## 2022
|  | ERCOT 2022 hourly simulaiton using 2022 data: 80 GW peak load, 5 GW nucl, 36 GW wind, 12 GW solar, and 61 GW fossil fuel capacity (calculated). Storm Elliott is modeled. Average energy cost is 7.3 c/kWh. | [20 empty] | Comments are shifted |  |  |  |  | Storm Elliott winter peak occurred 12/22 hour 21 with peak 91.8% of the summer peak.
[23 empty] | to the right because of |  |  |  |  | Input | Calculated | Yellow per unit (pu) header means the column is input data.
[23 empty] | a page width print |  |  |  |  | References:
[23 empty] | problem in Office 365. |  |  |  |  | 1 | https://www.ercot.com/mp/data-products/data-product-details?id=PG7-126-M
[28 empty] | 2 | https://www.futureofenergyinitiative.org/Pubs/46_CostInputsForToyModels.pdf
[28 empty] | 3 | https://egpreston.com/ExcelStorage.pdf |  |  | has more info on programming storage.
[28 empty] | 4 | battery must be charged up at end of period for total energies to agree.
[28 empty] | 5 | If storage drops down to the zero level gas generation will be automatically added.
[23 empty] | Total Energy = |  | 431527.2016 | GWh | System | U=Utilization C=Capacity Factor
[23 empty] | Nuclear Energy = |  | 43800 | GWh | 10.15 | % CF = | 100 | %
[23 empty] | Wind Energy = |  | 108664.6234 | GWh | 25.1814 | % UF = | 100 | %
[23 empty] | Solar Energy = |  | 24664.0933 | GWh | 5.7155 | % UF = | 100 | %
[23 empty] | Fossil Energy = |  | 254398.4849 | GWh | 58.9531 | % CF = | 47.7336 | %
[25 empty] | 431527.2016 | GWh (4) | 100 | %
|  | Hourly Demand and Variable Resources Input | [5 empty] | Hourly Dispatching of All Resources and Battery Storage | [15 empty] | Costs and Performance of Individual Sources
Base Nucl MW = |  | 5000 | [5 empty] | Base | Direct | Direct | Direct | Excess | Excess | Excess | Excess | Unserved | Maximum | Battery | Battery | Battery | Battery | Peaking | System Energy Cost |  | 7.3276 | cent/kWh | 60839.64 | MW Fossil Peaking
|  | PeakMW= | 80000 | WinPmx= | 36000 | SolPmax= | 12000 | Nuclear | Nuclear | Wind | Solar | Nuclear | Wind | Solar | Total | Load | Battery MWh | Discharge | Nuclear | Wind | Solar | Fossil | Hourly Load Stats
YYYYMMDDHH | D | load pu | loadMW | wind pu | windMW | solar pu | solarMW | Per Unit | MW | MW | MW | MW | MW | MW | MW | MW | 0 | MW | MW | Chg MW | Chg MW | MW | 80000 | MW Peak | 49.2611 | GW Avg | 10 | %Reserve
2022010101 | 7 | 0.47757 | 38205.6 | 0.35313 | 12712.68 | 0 | 0 | 1 | 5000 | 12712.68 | 0 | 0 | 0 | 0 | 0 | 20492.92 | 0 | 0 | 0 | 0 | 0 | 20492.92 | 32017.6 | MW Min | 431527.2016 | GWh | 61.5764 | %CF
2022010102 | 7 | 0.46503 | 37202.4 | 0.37703 | 13573.08 | 0 | 0 | 1 | 5000 | 13573.08 | 0 | 0 | 0 | 0 | 0 | 18629.32 | 0 | 0 | 0 | 0 | 0 | 18629.32 | Lithium Ion Battery |  |  | CAPEX M$
2022010103 | 7 | 0.45017 | 36013.6 | 0.42041 | 15134.76 | 0 | 0 | 1 | 5000 | 15134.76 | 0 | 0 | 0 | 0 | 0 | 15878.84 | 0 | 0 | 0 | 0 | 0 | 15878.84 | power | $/kW | 249 | 0 | 0 | MW | efficiency
2022010104 | 7 | 0.44009 | 35207.2 | 0.48177 | 17343.72 | 0 | 0 | 1 | 5000 | 17343.72 | 0 | 0 | 0 | 0 | 0 | 12863.48 | 0 | 0 | 0 | 0 | 0 | 12863.48 | energy | $/kWh | 369 | 0 | 0 | MWh | 0.85
2022010105 | 7 | 0.43346 | 34676.8 | 0.53661 | 19317.96 | 0 | 0 | 1 | 5000 | 19317.96 | 0 | 0 | 0 | 0 | 0 | 10358.84 | 0 | 0 | 0 | 0 | 0 | 10358.84 | total |  |  | 0 | 0 | Hours
2022010106 | 7 | 0.43155 | 34524 | 0.53149 | 19133.64 | 0 | 0 | 1 | 5000 | 19133.64 | 0 | 0 | 0 | 0 | 0 | 10390.36 | 0 | 0 | 0 | 0 | 0 | 10390.36 | Annual Costs |  |  |  | per year | annual | source
2022010107 | 7 | 0.43306 | 34644.8 | 0.54249 | 19529.64 | 0 | 0 | 1 | 5000 | 19529.64 | 0 | 0 | 0 | 0 | 0 | 10115.16 | 0 | 0 | 0 | 0 | 0 | 10115.16 | Base Loaded Nuclear |  |  |  | capt cost | cost M$ | cent/kWh
2022010108 | 7 | 0.43386 | 34708.8 | 0.53572 | 19285.92 | 0.0008 | 9.6 | 1 | 5000 | 19285.92 | 9.6 | 0 | 0 | 0 | 0 | 10413.28 | 0 | 0 | 0 | 0 | 0 | 10413.28 | 5000 | MW nucl | 7440 | $/kW | 0.064 | 2380.8 | 5.4356
2022010109 | 7 | 0.446 | 35680 | 0.50624 | 18224.64 | 0.14415 | 1729.8 | 1 | 5000 | 18224.64 | 1729.8 | 0 | 0 | 0 | 0 | 10725.56 | 0 | 0 | 0 | 0 | 0 | 10725.56 |  | Nucl O&M | 146 | $/kW/yr |  | 730 | 1.6667
2022010110 | 7 | 0.47494 | 37995.2 | 0.49502 | 17820.72 | 0.37098 | 4451.76 | 1 | 5000 | 17820.72 | 4451.76 | 0 | 0 | 0 | 0 | 10722.72 | 0 | 0 | 0 | 0 | 0 | 10722.72 |  | Vari O&M | 10 | $/MWh/yr |  | 438 | 1
2022010111 | 7 | 0.5009 | 40072 | 0.51769 | 18636.84 | 0.34787 | 4174.44 | 1 | 5000 | 18636.84 | 4174.44 | 0 | 0 | 0 | 0 | 12260.72 | 0 | 0 | 0 | 0 | 0 | 12260.72 | Wind
2022010112 | 7 | 0.52403 | 41922.4 | 0.52035 | 18732.6 | 0.28867 | 3464.04 | 1 | 5000 | 18732.6 | 3464.04 | 0 | 0 | 0 | 0 | 14725.76 | 0 | 0 | 0 | 0 | 0 | 14725.76 | 36000 | MW wind | 1460 | $/kW | 0.089 | 4677.84 | 4.3048
2022010113 | 7 | 0.54068 | 43254.4 | 0.47815 | 17213.4 | 0.38506 | 4620.72 | 1 | 5000 | 17213.4 | 4620.72 | 0 | 0 | 0 | 0 | 16420.28 | 0 | 0 | 0 | 0 | 0 | 16420.28 |  | WndO&M | 43 | $/kW/yr |  | 1548 | 1.4246
2022010114 | 7 | 0.55124 | 44099.2 | 0.4348 | 15652.8 | 0.50861 | 6103.32 | 1 | 5000 | 15652.8 | 6103.32 | 0 | 0 | 0 | 0 | 17343.08 | 0 | 0 | 0 | 0 | 0 | 17343.08 | Solar
2022010115 | 7 | 0.55428 | 44342.4 | 0.41077 | 14787.72 | 0.54386 | 6526.32 | 1 | 5000 | 14787.72 | 6526.32 | 0 | 0 | 0 | 0 | 18028.36 | 0 | 0 | 0 | 0 | 0 | 18028.36 | 12000 | MW solar | 1330 | $/kW | 0.074 | 1181.04 | 4.7885
2022010116 | 7 | 0.55378 | 44302.4 | 0.41978 | 15112.08 | 0.49681 | 5961.72 | 1 | 5000 | 15112.08 | 5961.72 | 0 | 0 | 0 | 0 | 18228.6 | 0 | 0 | 0 | 0 | 0 | 18228.6 |  | solarO&M | 23 | $/kW/yr |  | 276 | 1.119
2022010117 | 7 | 0.55539 | 44431.2 | 0.49428 | 17794.08 | 0.21587 | 2590.44 | 1 | 5000 | 17794.08 | 2590.44 | 0 | 0 | 0 | 0 | 19046.68 | 0 | 0 | 0 | 0 | 0 | 19046.68 | Lithium Ion Battery
2022010118 | 7 | 0.56347 | 45077.6 | 0.54996 | 19798.56 | 0.02487 | 298.44 | 1 | 5000 | 19798.56 | 298.44 | 0 | 0 | 0 | 0 | 19980.6 | 0 | 0 | 0 | 0 | 0 | 19980.6 | 0 | MW Batt | 0 | M$ capex | 0.104 | 0
2022010119 | 7 | 0.57757 | 46205.6 | 0.58111 | 20919.96 | 0 | 0 | 1 | 5000 | 20919.96 | 0 | 0 | 0 | 0 | 0 | 20285.64 | 0 | 0 | 0 | 0 | 0 | 20285.64 | 0 | MWh Batt | 0 | M$ capex |  | 0
2022010120 | 7 | 0.57553 | 46042.4 | 0.59821 | 21535.56 | 0 | 0 | 1 | 5000 | 21535.56 | 0 | 0 | 0 | 0 | 0 | 19506.84 | 0 | 0 | 0 | 0 | 0 | 19506.84 |  | Batt O&M | 43 | $/kW/yr |  | 0
2022010121 | 7 | 0.5732 | 45856 | 0.6104 | 21974.4 | 0 | 0 | 1 | 5000 | 21974.4 | 0 | 0 | 0 | 0 | 0 | 18881.6 | 0 | 0 | 0 | 0 | 0 | 18881.6 | Gas Peaking
2022010122 | 7 | 0.5702 | 45616 | 0.62561 | 22521.96 | 0 | 0 | 1 | 5000 | 22521.96 | 0 | 0 | 0 | 0 | 0 | 18094.04 | 0 | 0 | 0 | 0 | 0 | 18094.04 | 60839.64 | MW Gas | 922 | $/kW | 0.074 | 4150.967 | 1.6317
2022010123 | 7 | 0.56127 | 44901.6 | 0.63679 | 22924.44 | 0 | 0 | 1 | 5000 | 22924.44 | 0 | 0 | 0 | 0 | 0 | 16977.16 | 0 | 0 | 0 | 0 | 0 | 16977.16 |  | Gas O&M | 21 | $/kW/yr |  | 1277.6324 | 0.50222
2022010124 | 7 | 0.54944 | 43955.2 | 0.63059 | 22701.24 | 0 | 0 | 1 | 5000 | 22701.24 | 0 | 0 | 0 | 0 | 0 | 16253.96 | 0 | 0 | 0 | 0 | 0 | 16253.96 |  | Vari O&M | 16 | $/MWh/yr |  | 4070.3758 | 1.6
2022010201 | 1 | 0.53715 | 42972 | 0.6054 | 21794.4 | 0 | 0 | 1 | 5000 | 21794.4 | 0 | 0 | 0 | 0 | 0 | 16177.6 | 0 | 0 | 0 | 0 | 0 | 16177.6 | 29040.9229 | AvgGasMW | 40 | $/MWh fuel cost |  | 10175.9394 | 4
2022010202 | 1 | 0.52822 | 42257.6 | 0.58365 | 21011.4 | 0 | 0 | 1 | 5000 | 21011.4 | 0 | 0 | 0 | 0 | 0 | 16246.2 | 0 | 0 | 0 | 0 | 0 | 16246.2 | 8000 | MW Gas Reserve Capacity |  |  |  | 713.824 | 0.28059
2022010203 | 1 | 0.52689 | 42151.2 | 0.58429 | 21034.44 | 0 | 0 | 1 | 5000 | 21034.44 | 0 | 0 | 0 | 0 | 0 | 16116.76 | 0 | 0 | 0 | 0 | 0 | 16116.76 |  |  |  |  | total | 31620.4186 | 7.3276
2022010204 | 1 | 0.53254 | 42603.2 | 0.59276 | 21339.36 | 0 | 0 | 1 | 5000 | 21339.36 | 0 | 0 | 0 | 0 | 0 | 16263.84 | 0 | 0 | 0 | 0 | 0 | 16263.84 | Gas Peaking MWs |  |  |  | Storm Elliott
2022010205 | 1 | 0.54448 | 43558.4 | 0.60709 | 21855.24 | 0 | 0 | 1 | 5000 | 21855.24 | 0 | 0 | 0 | 0 | 0 | 16703.16 | 0 | 0 | 0 | 0 | 0 | 16703.16 | 60839.64 | Summer | 54731.76 | Winter 1 | 60308.56 | Winter 2 | ref (6) |  | (6) ERCOT with 120 GWh Battery Storage could serve 15 GW peak gas capacity.
2022010206 | 1 | 0.56207 | 44965.6 | 0.594 | 21384 | 0 | 0 | 1 | 5000 | 21384 | 0 | 0 | 0 | 0 | 0 | 18581.6 | 0 | 0 | 0 | 0 | 0 | 18581.6 | Annual Costs |  |  |  |  | annual | source | flat charge | However Storm Elliott requires almost the same peak gas capacity.
2022010207 | 1 | 0.58685 | 46948 | 0.58346 | 21004.56 | 0 | 0 | 1 | 5000 | 21004.56 | 0 | 0 | 0 | 0 | 0 | 20943.44 | 0 | 0 | 0 | 0 | 0 | 20943.44 |  | max %CF | load %CF | batt %CF | unused% | cost M$ | cent/kWh | cent/kWh | Winter peaking gas capacity must be able to run 24/7 for several days.
2022010208 | 1 | 0.6176 | 49408 | 0.56658 | 20396.88 | 0.00178 | 21.36 | 1 | 5000 | 20396.88 | 21.36 | 0 | 0 | 0 | 0 | 23989.76 | 0 | 0 | 0 | 0 | 0 | 23989.76 | Nuclear | 100 | 100 | 0 | 0 | 3548.8 | 8.1023 | 0.82238 | ERCOT should plan for both winter and summer generation capacities.
2022010209 | 1 | 0.64339 | 51471.2 | 0.52563 | 18922.68 | 0.19981 | 2397.72 | 1 | 5000 | 18922.68 | 2397.72 | 0 | 0 | 0 | 0 | 25150.8 | 0 | 0 | 0 | 0 | 0 | 25150.8 | Wind | 34.4573 | 34.4573 | 0 | 0 | 6225.84 | 5.7294 | 1.4427 | derivation | https://egpreston.com/BatteryPeakingCapacity.pdf
2022010210 | 1 | 0.65706 | 52564.8 | 0.46166 | 16619.76 | 0.58937 | 7072.44 | 1 | 5000 | 16619.76 | 7072.44 | 0 | 0 | 0 | 0 | 23872.6 | 0 | 0 | 0 | 0 | 0 | 23872.6 | Solar | 23.4628 | 23.4628 | 0 | 0 | 1457.04 | 5.9075 | 0.33765
2022010211 | 1 | 0.65519 | 52415.2 | 0.38041 | 13694.76 | 0.6689 | 8026.8 | 1 | 5000 | 13694.76 | 8026.8 | 0 | 0 | 0 | 0 | 25693.64 | 0 | 0 | 0 | 0 | 0 | 25693.64 | Fossil | 100 | 47.7336 |  | 52.2664 | 19674.9146 | 7.7339 | 4.5594
2022010212 | 1 | 0.64415 | 51532 | 0.31874 | 11474.64 | 0.64915 | 7789.8 | 1 | 5000 | 11474.64 | 7789.8 | 0 | 0 | 0 | 0 | 27267.56 | 0 | 0 | 0 | 0 | 0 | 27267.56 | Battery |  |  |  |  | 0 |  | 0
2022010213 | 1 | 0.62951 | 50360.8 | 0.30735 | 11064.6 | 0.66737 | 8008.44 | 1 | 5000 | 11064.6 | 8008.44 | 0 | 0 | 0 | 0 | 26287.76 | 0 | 0 | 0 | 0 | 0 | 26287.76 | Reserve |  |  |  |  | 713.824 | 0.28059 | 0.16542
2022010214 | 1 | 0.60784 | 48627.2 | 0.28154 | 10135.44 | 0.69465 | 8335.8 | 1 | 5000 | 10135.44 | 8335.8 | 0 | 0 | 0 | 0 | 25155.96 | 0 | 0 | 0 | 0 | 0 | 25155.96 |  |  |  |  | total | 31620.4186 | avg | 7.3276
2022010215 | 1 | 0.58894 | 47115.2 | 0.25397 | 9142.92 | 0.72893 | 8747.16 | 1 | 5000 | 9142.92 | 8747.16 | 0 | 0 | 0 | 0 | 24225.12 | 0 | 0 | 0 | 0 | 0 | 24225.12 |  |  |  | Wind Solar Batteries |  | 7682.88
2022010216 | 1 | 0.57791 | 46232.8 | 0.22273 | 8018.28 | 0.73272 | 8792.64 | 1 | 5000 | 8018.28 | 8792.64 | 0 | 0 | 0 | 0 | 24421.88 | 0 | 0 | 0 | 0 | 0 | 24421.88
2022010217 | 1 | 0.57907 | 46325.6 | 0.1807 | 6505.2 | 0.5544 | 6652.8 | 1 | 5000 | 6505.2 | 6652.8 | 0 | 0 | 0 | 0 | 28167.6 | 0 | 0 | 0 | 0 | 0 | 28167.6
2022010218 | 1 | 0.6104 | 48832 | 0.14866 | 5351.76 | 0.10251 | 1230.12 | 1 | 5000 | 5351.76 | 1230.12 | 0 | 0 | 0 | 0 | 37250.12 | 0 | 0 | 0 | 0 | 0 | 37250.12
2022010219 | 1 | 0.64731 | 51784.8 | 0.14265 | 5135.4 | 0 | 0 | 1 | 5000 | 5135.4 | 0 | 0 | 0 | 0 | 0 | 41649.4 | 0 | 0 | 0 | 0 | 0 | 41649.4
2022010220 | 1 | 0.6561 | 52488 | 0.14091 | 5072.76 | 0 | 0 | 1 | 5000 | 5072.76 | 0 | 0 | 0 | 0 | 0 | 42415.24 | 0 | 0 | 0 | 0 | 0 | 42415.24
2022010221 | 1 | 0.65547 | 52437.6 | 0.14422 | 5191.92 | 0 | 0 | 1 | 5000 | 5191.92 | 0 | 0 | 0 | 0 | 0 | 42245.68 | 0 | 0 | 0 | 0 | 0 | 42245.68
2022010222 | 1 | 0.65153 | 52122.4 | 0.14561 | 5241.96 | 0 | 0 | 1 | 5000 | 5241.96 | 0 | 0 | 0 | 0 | 0 | 41880.44 | 0 | 0 | 0 | 0 | 0 | 41880.44
2022010223 | 1 | 0.63521 | 50816.8 | 0.14364 | 5171.04 | 0 | 0 | 1 | 5000 | 5171.04 | 0 | 0 | 0 | 0 | 0 | 40645.76 | 0 | 0 | 0 | 0 | 0 | 40645.76
2022010224 | 1 | 0.61937 | 49549.6 | 0.14195 | 5110.2 | 0 | 0 | 1 | 5000 | 5110.2 | 0 | 0 | 0 | 0 | 0 | 39439.4 | 0 | 0 | 0 | 0 | 0 | 39439.4
2022010301 | 2 | 0.60764 | 48611.2 | 0.1436 | 5169.6 | 0 | 0 | 1 | 5000 | 5169.6 | 0 | 0 | 0 | 0 | 0 | 38441.6 | 0 | 0 | 0 | 0 | 0 | 38441.6
2022010302 | 2 | 0.60463 | 48370.4 | 0.14657 | 5276.52 | 0 | 0 | 1 | 5000 | 5276.52 | 0 | 0 | 0 | 0 | 0 | 38093.88 | 0 | 0 | 0 | 0 | 0 | 38093.88
2022010303 | 2 | 0.60608 | 48486.4 | 0.15007 | 5402.52 | 0 | 0 | 1 | 5000 | 5402.52 | 0 | 0 | 0 | 0 | 0 | 38083.88 | 0 | 0 | 0 | 0 | 0 | 38083.88
2022010304 | 2 | 0.61457 | 49165.6 | 0.15489 | 5576.04 | 0 | 0 | 1 | 5000 | 5576.04 | 0 | 0 | 0 | 0 | 0 | 38589.56 | 0 | 0 | 0 | 0 | 0 | 38589.56
2022010305 | 2 | 0.63087 | 50469.6 | 0.16599 | 5975.64 | 0 | 0 | 1 | 5000 | 5975.64 | 0 | 0 | 0 | 0 | 0 | 39493.96 | 0 | 0 | 0 | 0 | 0 | 39493.96
2022010306 | 2 | 0.6592 | 52736 | 0.18519 | 6666.84 | 0 | 0 | 1 | 5000 | 6666.84 | 0 | 0 | 0 | 0 | 0 | 41069.16 | 0 | 0 | 0 | 0 | 0 | 41069.16
2022010307 | 2 | 0.69698 | 55758.4 | 0.19196 | 6910.56 | 0 | 0 | 1 | 5000 | 6910.56 | 0 | 0 | 0 | 0 | 0 | 43847.84 | 0 | 0 | 0 | 0 | 0 | 43847.84
2022010308 | 2 | 0.72183 | 57746.4 | 0.2057 | 7405.2 | 0.00691 | 82.92 | 1 | 5000 | 7405.2 | 82.92 | 0 | 0 | 0 | 0 | 45258.28 | 0 | 0 | 0 | 0 | 0 | 45258.28
2022010309 | 2 | 0.7143 | 57144 | 0.22354 | 8047.44 | 0.27564 | 3307.68 | 1 | 5000 | 8047.44 | 3307.68 | 0 | 0 | 0 | 0 | 40788.88 | 0 | 0 | 0 | 0 | 0 | 40788.88
2022010310 | 2 | 0.68042 | 54433.6 | 0.16827 | 6057.72 | 0.71326 | 8559.12 | 1 | 5000 | 6057.72 | 8559.12 | 0 | 0 | 0 | 0 | 34816.76 | 0 | 0 | 0 | 0 | 0 | 34816.76
2022010311 | 2 | 0.645 | 51600 | 0.12364 | 4451.04 | 0.75983 | 9117.96 | 1 | 5000 | 4451.04 | 9117.96 | 0 | 0 | 0 | 0 | 33031 | 0 | 0 | 0 | 0 | 0 | 33031
2022010312 | 2 | 0.60996 | 48796.8 | 0.15141 | 5450.76 | 0.72612 | 8713.44 | 1 | 5000 | 5450.76 | 8713.44 | 0 | 0 | 0 | 0 | 29632.6 | 0 | 0 | 0 | 0 | 0 | 29632.6
2022010313 | 2 | 0.58021 | 46416.8 | 0.19036 | 6852.96 | 0.70442 | 8453.04 | 1 | 5000 | 6852.96 | 8453.04 | 0 | 0 | 0 | 0 | 26110.8 | 0 | 0 | 0 | 0 | 0 | 26110.8
2022010314 | 2 | 0.55632 | 44505.6 | 0.21292 | 7665.12 | 0.71519 | 8582.28 | 1 | 5000 | 7665.12 | 8582.28 | 0 | 0 | 0 | 0 | 23258.2 | 0 | 0 | 0 | 0 | 0 | 23258.2
2022010315 | 2 | 0.53846 | 43076.8 | 0.23557 | 8480.52 | 0.74852 | 8982.24 | 1 | 5000 | 8480.52 | 8982.24 | 0 | 0 | 0 | 0 | 20614.04 | 0 | 0 | 0 | 0 | 0 | 20614.04
2022010316 | 2 | 0.53059 | 42447.2 | 0.2686 | 9669.6 | 0.71808 | 8616.96 | 1 | 5000 | 9669.6 | 8616.96 | 0 | 0 | 0 | 0 | 19160.64 | 0 | 0 | 0 | 0 | 0 | 19160.64
2022010317 | 2 | 0.53341 | 42672.8 | 0.28035 | 10092.6 | 0.44425 | 5331 | 1 | 5000 | 10092.6 | 5331 | 0 | 0 | 0 | 0 | 22249.2 | 0 | 0 | 0 | 0 | 0 | 22249.2
2022010318 | 2 | 0.56288 | 45030.4 | 0.28179 | 10144.44 | 0.06108 | 732.96 | 1 | 5000 | 10144.44 | 732.96 | 0 | 0 | 0 | 0 | 29153 | 0 | 0 | 0 | 0 | 0 | 29153
2022010319 | 2 | 0.6025 | 48200 | 0.38975 | 14031 | 0 | 0 | 1 | 5000 | 14031 | 0 | 0 | 0 | 0 | 0 | 29169 | 0 | 0 | 0 | 0 | 0 | 29169
2022010320 | 2 | 0.61435 | 49148 | 0.51913 | 18688.68 | 0 | 0 | 1 | 5000 | 18688.68 | 0 | 0 | 0 | 0 | 0 | 25459.32 | 0 | 0 | 0 | 0 | 0 | 25459.32
2022010321 | 2 | 0.61832 | 49465.6 | 0.6015 | 21654 | 0 | 0 | 1 | 5000 | 21654 | 0 | 0 | 0 | 0 | 0 | 22811.6 | 0 | 0 | 0 | 0 | 0 | 22811.6
2022010322 | 2 | 0.61047 | 48837.6 | 0.60641 | 21830.76 | 0 | 0 | 1 | 5000 | 21830.76 | 0 | 0 | 0 | 0 | 0 | 22006.84 | 0 | 0 | 0 | 0 | 0 | 22006.84
2022010323 | 2 | 0.59106 | 47284.8 | 0.60471 | 21769.56 | 0 | 0 | 1 | 5000 | 21769.56 | 0 | 0 | 0 | 0 | 0 | 20515.24 | 0 | 0 | 0 | 0 | 0 | 20515.24
2022010324 | 2 | 0.57014 | 45611.2 | 0.60316 | 21713.76 | 0 | 0 | 1 | 5000 | 21713.76 | 0 | 0 | 0 | 0 | 0 | 18897.44 | 0 | 0 | 0 | 0 | 0 | 18897.44
2022010401 | 3 | 0.55636 | 44508.8 | 0.59894 | 21561.84 | 0 | 0 | 1 | 5000 | 21561.84 | 0 | 0 | 0 | 0 | 0 | 17946.96 | 0 | 0 | 0 | 0 | 0 | 17946.96
2022010402 | 3 | 0.55052 | 44041.6 | 0.59187 | 21307.32 | 0 | 0 | 1 | 5000 | 21307.32 | 0 | 0 | 0 | 0 | 0 | 17734.28 | 0 | 0 | 0 | 0 | 0 | 17734.28
2022010403 | 3 | 0.55048 | 44038.4 | 0.57574 | 20726.64 | 0 | 0 | 1 | 5000 | 20726.64 | 0 | 0 | 0 | 0 | 0 | 18311.76 | 0 | 0 | 0 | 0 | 0 | 18311.76
2022010404 | 3 | 0.55703 | 44562.4 | 0.56376 | 20295.36 | 0 | 0 | 1 | 5000 | 20295.36 | 0 | 0 | 0 | 0 | 0 | 19267.04 | 0 | 0 | 0 | 0 | 0 | 19267.04
2022010405 | 3 | 0.57318 | 45854.4 | 0.56625 | 20385 | 0 | 0 | 1 | 5000 | 20385 | 0 | 0 | 0 | 0 | 0 | 20469.4 | 0 | 0 | 0 | 0 | 0 | 20469.4
2022010406 | 3 | 0.60514 | 48411.2 | 0.58296 | 20986.56 | 0 | 0 | 1 | 5000 | 20986.56 | 0 | 0 | 0 | 0 | 0 | 22424.64 | 0 | 0 | 0 | 0 | 0 | 22424.64
2022010407 | 3 | 0.64916 | 51932.8 | 0.57942 | 20859.12 | 0 | 0 | 1 | 5000 | 20859.12 | 0 | 0 | 0 | 0 | 0 | 26073.68 | 0 | 0 | 0 | 0 | 0 | 26073.68
2022010408 | 3 | 0.67235 | 53788 | 0.57188 | 20587.68 | 0.0054 | 64.8 | 1 | 5000 | 20587.68 | 64.8 | 0 | 0 | 0 | 0 | 28135.52 | 0 | 0 | 0 | 0 | 0 | 28135.52
2022010409 | 3 | 0.65968 | 52774.4 | 0.54659 | 19677.24 | 0.1368 | 1641.6 | 1 | 5000 | 19677.24 | 1641.6 | 0 | 0 | 0 | 0 | 26455.56 | 0 | 0 | 0 | 0 | 0 | 26455.56
2022010410 | 3 | 0.62828 | 50262.4 | 0.50122 | 18043.92 | 0.34842 | 4181.04 | 1 | 5000 | 18043.92 | 4181.04 | 0 | 0 | 0 | 0 | 23037.44 | 0 | 0 | 0 | 0 | 0 | 23037.44
2022010411 | 3 | 0.60042 | 48033.6 | 0.49452 | 17802.72 | 0.42653 | 5118.36 | 1 | 5000 | 17802.72 | 5118.36 | 0 | 0 | 0 | 0 | 20112.52 | 0 | 0 | 0 | 0 | 0 | 20112.52
2022010412 | 3 | 0.57371 | 45896.8 | 0.52668 | 18960.48 | 0.41488 | 4978.56 | 1 | 5000 | 18960.48 | 4978.56 | 0 | 0 | 0 | 0 | 16957.76 | 0 | 0 | 0 | 0 | 0 | 16957.76
2022010413 | 3 | 0.55268 | 44214.4 | 0.53609 | 19299.24 | 0.40206 | 4824.72 | 1 | 5000 | 19299.24 | 4824.72 | 0 | 0 | 0 | 0 | 15090.44 | 0 | 0 | 0 | 0 | 0 | 15090.44
2022010414 | 3 | 0.53596 | 42876.8 | 0.52981 | 19073.16 | 0.41692 | 5003.04 | 1 | 5000 | 19073.16 | 5003.04 | 0 | 0 | 0 | 0 | 13800.6 | 0 | 0 | 0 | 0 | 0 | 13800.6
2022010415 | 3 | 0.52256 | 41804.8 | 0.51598 | 18575.28 | 0.43 | 5160 | 1 | 5000 | 18575.28 | 5160 | 0 | 0 | 0 | 0 | 13069.52 | 0 | 0 | 0 | 0 | 0 | 13069.52
2022010416 | 3 | 0.51647 | 41317.6 | 0.49874 | 17954.64 | 0.46933 | 5631.96 | 1 | 5000 | 17954.64 | 5631.96 | 0 | 0 | 0 | 0 | 12731 | 0 | 0 | 0 | 0 | 0 | 12731
2022010417 | 3 | 0.51813 | 41450.4 | 0.4542 | 16351.2 | 0.48399 | 5807.88 | 1 | 5000 | 16351.2 | 5807.88 | 0 | 0 | 0 | 0 | 14291.32 | 0 | 0 | 0 | 0 | 0 | 14291.32
2022010418 | 3 | 0.53249 | 42599.2 | 0.40924 | 14732.64 | 0.10021 | 1202.52 | 1 | 5000 | 14732.64 | 1202.52 | 0 | 0 | 0 | 0 | 21664.04 | 0 | 0 | 0 | 0 | 0 | 21664.04
2022010419 | 3 | 0.55817 | 44653.6 | 0.43165 | 15539.4 | 0 | 0 | 1 | 5000 | 15539.4 | 0 | 0 | 0 | 0 | 0 | 24114.2 | 0 | 0 | 0 | 0 | 0 | 24114.2
2022010420 | 3 | 0.55639 | 44511.2 | 0.50108 | 18038.88 | 0 | 0 | 1 | 5000 | 18038.88 | 0 | 0 | 0 | 0 | 0 | 21472.32 | 0 | 0 | 0 | 0 | 0 | 21472.32
2022010421 | 3 | 0.55069 | 44055.2 | 0.52326 | 18837.36 | 0 | 0 | 1 | 5000 | 18837.36 | 0 | 0 | 0 | 0 | 0 | 20217.84 | 0 | 0 | 0 | 0 | 0 | 20217.84
2022010422 | 3 | 0.53491 | 42792.8 | 0.5209 | 18752.4 | 0 | 0 | 1 | 5000 | 18752.4 | 0 | 0 | 0 | 0 | 0 | 19040.4 | 0 | 0 | 0 | 0 | 0 | 19040.4
2022010423 | 3 | 0.51076 | 40860.8 | 0.51082 | 18389.52 | 0 | 0 | 1 | 5000 | 18389.52 | 0 | 0 | 0 | 0 | 0 | 17471.28 | 0 | 0 | 0 | 0 | 0 | 17471.28
2022010424 | 3 | 0.48777 | 39021.6 | 0.47088 | 16951.68 | 0 | 0 | 1 | 5000 | 16951.68 | 0 | 0 | 0 | 0 | 0 | 17069.92 | 0 | 0 | 0 | 0 | 0 | 17069.92
2022010501 | 4 | 0.47259 | 37807.2 | 0.4446 | 16005.6 | 0 | 0 | 1 | 5000 | 16005.6 | 0 | 0 | 0 | 0 | 0 | 16801.6 | 0 | 0 | 0 | 0 | 0 | 16801.6
2022010502 | 4 | 0.46655 | 37324 | 0.43209 | 15555.24 | 0 | 0 | 1 | 5000 | 15555.24 | 0 | 0 | 0 | 0 | 0 | 16768.76 | 0 | 0 | 0 | 0 | 0 | 16768.76
2022010503 | 4 | 0.46688 | 37350.4 | 0.42818 | 15414.48 | 0 | 0 | 1 | 5000 | 15414.48 | 0 | 0 | 0 | 0 | 0 | 16935.92 | 0 | 0 | 0 | 0 | 0 | 16935.92
2022010504 | 4 | 0.47322 | 37857.6 | 0.47859 | 17229.24 | 0 | 0 | 1 | 5000 | 17229.24 | 0 | 0 | 0 | 0 | 0 | 15628.36 | 0 | 0 | 0 | 0 | 0 | 15628.36
2022010505 | 4 | 0.48888 | 39110.4 | 0.50781 | 18281.16 | 0 | 0 | 1 | 5000 | 18281.16 | 0 | 0 | 0 | 0 | 0 | 15829.24 | 0 | 0 | 0 | 0 | 0 | 15829.24
2022010506 | 4 | 0.51974 | 41579.2 | 0.5221 | 18795.6 | 0 | 0 | 1 | 5000 | 18795.6 | 0 | 0 | 0 | 0 | 0 | 17783.6 | 0 | 0 | 0 | 0 | 0 | 17783.6
2022010507 | 4 | 0.56468 | 45174.4 | 0.53246 | 19168.56 | 0 | 0 | 1 | 5000 | 19168.56 | 0 | 0 | 0 | 0 | 0 | 21005.84 | 0 | 0 | 0 | 0 | 0 | 21005.84
2022010508 | 4 | 0.58747 | 46997.6 | 0.53666 | 19319.76 | 0.00388 | 46.56 | 1 | 5000 | 19319.76 | 46.56 | 0 | 0 | 0 | 0 | 22631.28 | 0 | 0 | 0 | 0 | 0 | 22631.28
2022010509 | 4 | 0.57663 | 46130.4 | 0.48474 | 17450.64 | 0.23604 | 2832.48 | 1 | 5000 | 17450.64 | 2832.48 | 0 | 0 | 0 | 0 | 20847.28 | 0 | 0 | 0 | 0 | 0 | 20847.28
2022010510 | 4 | 0.55902 | 44721.6 | 0.39487 | 14215.32 | 0.65407 | 7848.84 | 1 | 5000 | 14215.32 | 7848.84 | 0 | 0 | 0 | 0 | 17657.44 | 0 | 0 | 0 | 0 | 0 | 17657.44
2022010511 | 4 | 0.54359 | 43487.2 | 0.32134 | 11568.24 | 0.71174 | 8540.88 | 1 | 5000 | 11568.24 | 8540.88 | 0 | 0 | 0 | 0 | 18378.08 | 0 | 0 | 0 | 0 | 0 | 18378.08
2022010512 | 4 | 0.52678 | 42142.4 | 0.22283 | 8021.88 | 0.69885 | 8386.2 | 1 | 5000 | 8021.88 | 8386.2 | 0 | 0 | 0 | 0 | 20734.32 | 0 | 0 | 0 | 0 | 0 | 20734.32
2022010513 | 4 | 0.51545 | 41236 | 0.14339 | 5162.04 | 0.68534 | 8224.08 | 1 | 5000 | 5162.04 | 8224.08 | 0 | 0 | 0 | 0 | 22849.88 | 0 | 0 | 0 | 0 | 0 | 22849.88
2022010514 | 4 | 0.50948 | 40758.4 | 0.09841 | 3542.76 | 0.69353 | 8322.36 | 1 | 5000 | 3542.76 | 8322.36 | 0 | 0 | 0 | 0 | 23893.28 | 0 | 0 | 0 | 0 | 0 | 23893.28
2022010515 | 4 | 0.50818 | 40654.4 | 0.09058 | 3260.88 | 0.72225 | 8667 | 1 | 5000 | 3260.88 | 8667 | 0 | 0 | 0 | 0 | 23726.52 | 0 | 0 | 0 | 0 | 0 | 23726.52
2022010516 | 4 | 0.50828 | 40662.4 | 0.09594 | 3453.84 | 0.72334 | 8680.08 | 1 | 5000 | 3453.84 | 8680.08 | 0 | 0 | 0 | 0 | 23528.48 | 0 | 0 | 0 | 0 | 0 | 23528.48
2022010517 | 4 | 0.51143 | 40914.4 | 0.12188 | 4387.68 | 0.55665 | 6679.8 | 1 | 5000 | 4387.68 | 6679.8 | 0 | 0 | 0 | 0 | 24846.92 | 0 | 0 | 0 | 0 | 0 | 24846.92
2022010518 | 4 | 0.52645 | 42116 | 0.133 | 4788 | 0.1105 | 1326 | 1 | 5000 | 4788 | 1326 | 0 | 0 | 0 | 0 | 31002 | 0 | 0 | 0 | 0 | 0 | 31002
2022010519 | 4 | 0.54817 | 43853.6 | 0.16463 | 5926.68 | 0 | 0 | 1 | 5000 | 5926.68 | 0 | 0 | 0 | 0 | 0 | 32926.92 | 0 | 0 | 0 | 0 | 0 | 32926.92
2022010520 | 4 | 0.54569 | 43655.2 | 0.19062 | 6862.32 | 0 | 0 | 1 | 5000 | 6862.32 | 0 | 0 | 0 | 0 | 0 | 31792.88 | 0 | 0 | 0 | 0 | 0 | 31792.88
2022010521 | 4 | 0.53979 | 43183.2 | 0.23184 | 8346.24 | 0 | 0 | 1 | 5000 | 8346.24 | 0 | 0 | 0 | 0 | 0 | 29836.96 | 0 | 0 | 0 | 0 | 0 | 29836.96
2022010522 | 4 | 0.52665 | 42132 | 0.28004 | 10081.44 | 0 | 0 | 1 | 5000 | 10081.44 | 0 | 0 | 0 | 0 | 0 | 27050.56 | 0 | 0 | 0 | 0 | 0 | 27050.56
2022010523 | 4 | 0.50467 | 40373.6 | 0.34716 | 12497.76 | 0 | 0 | 1 | 5000 | 12497.76 | 0 | 0 | 0 | 0 | 0 | 22875.84 | 0 | 0 | 0 | 0 | 0 | 22875.84
2022010524 | 4 | 0.48256 | 38604.8 | 0.41695 | 15010.2 | 0 | 0 | 1 | 5000 | 15010.2 | 0 | 0 | 0 | 0 | 0 | 18594.6 | 0 | 0 | 0 | 0 | 0 | 18594.6
2022010601 | 5 | 0.46938 | 37550.4 | 0.43334 | 15600.24 | 0 | 0 | 1 | 5000 | 15600.24 | 0 | 0 | 0 | 0 | 0 | 16950.16 | 0 | 0 | 0 | 0 | 0 | 16950.16
2022010602 | 5 | 0.46467 | 37173.6 | 0.44907 | 16166.52 | 0 | 0 | 1 | 5000 | 16166.52 | 0 | 0 | 0 | 0 | 0 | 16007.08 | 0 | 0 | 0 | 0 | 0 | 16007.08
2022010603 | 5 | 0.46721 | 37376.8 | 0.46328 | 16678.08 | 0 | 0 | 1 | 5000 | 16678.08 | 0 | 0 | 0 | 0 | 0 | 15698.72 | 0 | 0 | 0 | 0 | 0 | 15698.72
2022010604 | 5 | 0.47419 | 37935.2 | 0.43692 | 15729.12 | 0 | 0 | 1 | 5000 | 15729.12 | 0 | 0 | 0 | 0 | 0 | 17206.08 | 0 | 0 | 0 | 0 | 0 | 17206.08
2022010605 | 5 | 0.49017 | 39213.6 | 0.48463 | 17446.68 | 0 | 0 | 1 | 5000 | 17446.68 | 0 | 0 | 0 | 0 | 0 | 16766.92 | 0 | 0 | 0 | 0 | 0 | 16766.92
2022010606 | 5 | 0.52636 | 42108.8 | 0.53376 | 19215.36 | 0 | 0 | 1 | 5000 | 19215.36 | 0 | 0 | 0 | 0 | 0 | 17893.44 | 0 | 0 | 0 | 0 | 0 | 17893.44
2022010607 | 5 | 0.57531 | 46024.8 | 0.57179 | 20584.44 | 0 | 0 | 1 | 5000 | 20584.44 | 0 | 0 | 0 | 0 | 0 | 20440.36 | 0 | 0 | 0 | 0 | 0 | 20440.36
2022010608 | 5 | 0.6048 | 48384 | 0.59376 | 21375.36 | 0.00374 | 44.88 | 1 | 5000 | 21375.36 | 44.88 | 0 | 0 | 0 | 0 | 21963.76 | 0 | 0 | 0 | 0 | 0 | 21963.76
2022010609 | 5 | 0.60699 | 48559.2 | 0.57294 | 20625.84 | 0.14311 | 1717.32 | 1 | 5000 | 20625.84 | 1717.32 | 0 | 0 | 0 | 0 | 21216.04 | 0 | 0 | 0 | 0 | 0 | 21216.04
2022010610 | 5 | 0.60339 | 48271.2 | 0.53261 | 19173.96 | 0.32911 | 3949.32 | 1 | 5000 | 19173.96 | 3949.32 | 0 | 0 | 0 | 0 | 20147.92 | 0 | 0 | 0 | 0 | 0 | 20147.92
2022010611 | 5 | 0.59792 | 47833.6 | 0.50041 | 18014.76 | 0.45868 | 5504.16 | 1 | 5000 | 18014.76 | 5504.16 | 0 | 0 | 0 | 0 | 19314.68 | 0 | 0 | 0 | 0 | 0 | 19314.68
2022010612 | 5 | 0.59083 | 47266.4 | 0.45285 | 16302.6 | 0.60042 | 7205.04 | 1 | 5000 | 16302.6 | 7205.04 | 0 | 0 | 0 | 0 | 18758.76 | 0 | 0 | 0 | 0 | 0 | 18758.76
2022010613 | 5 | 0.58181 | 46544.8 | 0.4081 | 14691.6 | 0.6901 | 8281.2 | 1 | 5000 | 14691.6 | 8281.2 | 0 | 0 | 0 | 0 | 18572 | 0 | 0 | 0 | 0 | 0 | 18572
2022010614 | 5 | 0.57344 | 45875.2 | 0.31856 | 11468.16 | 0.71467 | 8576.04 | 1 | 5000 | 11468.16 | 8576.04 | 0 | 0 | 0 | 0 | 20831 | 0 | 0 | 0 | 0 | 0 | 20831
2022010615 | 5 | 0.56747 | 45397.6 | 0.23731 | 8543.16 | 0.74839 | 8980.68 | 1 | 5000 | 8543.16 | 8980.68 | 0 | 0 | 0 | 0 | 22873.76 | 0 | 0 | 0 | 0 | 0 | 22873.76
2022010616 | 5 | 0.56517 | 45213.6 | 0.2006 | 7221.6 | 0.73887 | 8866.44 | 1 | 5000 | 7221.6 | 8866.44 | 0 | 0 | 0 | 0 | 24125.56 | 0 | 0 | 0 | 0 | 0 | 24125.56
2022010617 | 5 | 0.57441 | 45952.8 | 0.17672 | 6361.92 | 0.55097 | 6611.64 | 1 | 5000 | 6361.92 | 6611.64 | 0 | 0 | 0 | 0 | 27979.24 | 0 | 0 | 0 | 0 | 0 | 27979.24
2022010618 | 5 | 0.60116 | 48092.8 | 0.17775 | 6399 | 0.11669 | 1400.28 | 1 | 5000 | 6399 | 1400.28 | 0 | 0 | 0 | 0 | 35293.52 | 0 | 0 | 0 | 0 | 0 | 35293.52
2022010619 | 5 | 0.63522 | 50817.6 | 0.21454 | 7723.44 | 7e-05 | 0.84 | 1 | 5000 | 7723.44 | 0.84 | 0 | 0 | 0 | 0 | 38093.32 | 0 | 0 | 0 | 0 | 0 | 38093.32
2022010620 | 5 | 0.64013 | 51210.4 | 0.25706 | 9254.16 | 0 | 0 | 1 | 5000 | 9254.16 | 0 | 0 | 0 | 0 | 0 | 36956.24 | 0 | 0 | 0 | 0 | 0 | 36956.24
2022010621 | 5 | 0.63978 | 51182.4 | 0.27986 | 10074.96 | 0 | 0 | 1 | 5000 | 10074.96 | 0 | 0 | 0 | 0 | 0 | 36107.44 | 0 | 0 | 0 | 0 | 0 | 36107.44
2022010622 | 5 | 0.63114 | 50491.2 | 0.29415 | 10589.4 | 0 | 0 | 1 | 5000 | 10589.4 | 0 | 0 | 0 | 0 | 0 | 34901.8 | 0 | 0 | 0 | 0 | 0 | 34901.8
2022010623 | 5 | 0.61124 | 48899.2 | 0.28612 | 10300.32 | 0 | 0 | 1 | 5000 | 10300.32 | 0 | 0 | 0 | 0 | 0 | 33598.88 | 0 | 0 | 0 | 0 | 0 | 33598.88
2022010624 | 5 | 0.59533 | 47626.4 | 0.27991 | 10076.76 | 0 | 0 | 1 | 5000 | 10076.76 | 0 | 0 | 0 | 0 | 0 | 32549.64 | 0 | 0 | 0 | 0 | 0 | 32549.64
2022010701 | 6 | 0.58485 | 46788 | 0.2689 | 9680.4 | 0 | 0 | 1 | 5000 | 9680.4 | 0 | 0 | 0 | 0 | 0 | 32107.6 | 0 | 0 | 0 | 0 | 0 | 32107.6
2022010702 | 6 | 0.58259 | 46607.2 | 0.26463 | 9526.68 | 0 | 0 | 1 | 5000 | 9526.68 | 0 | 0 | 0 | 0 | 0 | 32080.52 | 0 | 0 | 0 | 0 | 0 | 32080.52
2022010703 | 6 | 0.58472 | 46777.6 | 0.26121 | 9403.56 | 0 | 0 | 1 | 5000 | 9403.56 | 0 | 0 | 0 | 0 | 0 | 32374.04 | 0 | 0 | 0 | 0 | 0 | 32374.04
2022010704 | 6 | 0.59424 | 47539.2 | 0.25053 | 9019.08 | 0 | 0 | 1 | 5000 | 9019.08 | 0 | 0 | 0 | 0 | 0 | 33520.12 | 0 | 0 | 0 | 0 | 0 | 33520.12
2022010705 | 6 | 0.61062 | 48849.6 | 0.25205 | 9073.8 | 0 | 0 | 1 | 5000 | 9073.8 | 0 | 0 | 0 | 0 | 0 | 34775.8 | 0 | 0 | 0 | 0 | 0 | 34775.8
2022010706 | 6 | 0.6437 | 51496 | 0.26041 | 9374.76 | 0 | 0 | 1 | 5000 | 9374.76 | 0 | 0 | 0 | 0 | 0 | 37121.24 | 0 | 0 | 0 | 0 | 0 | 37121.24
2022010707 | 6 | 0.68858 | 55086.4 | 0.25838 | 9301.68 | 0 | 0 | 1 | 5000 | 9301.68 | 0 | 0 | 0 | 0 | 0 | 40784.72 | 0 | 0 | 0 | 0 | 0 | 40784.72
2022010708 | 6 | 0.71202 | 56961.6 | 0.2584 | 9302.4 | 0.0029 | 34.8 | 1 | 5000 | 9302.4 | 34.8 | 0 | 0 | 0 | 0 | 42624.4 | 0 | 0 | 0 | 0 | 0 | 42624.4
2022010709 | 6 | 0.70991 | 56792.8 | 0.23175 | 8343 | 0.20939 | 2512.68 | 1 | 5000 | 8343 | 2512.68 | 0 | 0 | 0 | 0 | 40937.12 | 0 | 0 | 0 | 0 | 0 | 40937.12
2022010710 | 6 | 0.69669 | 55735.2 | 0.18403 | 6625.08 | 0.60885 | 7306.2 | 1 | 5000 | 6625.08 | 7306.2 | 0 | 0 | 0 | 0 | 36803.92 | 0 | 0 | 0 | 0 | 0 | 36803.92
2022010711 | 6 | 0.67827 | 54261.6 | 0.18092 | 6513.12 | 0.66993 | 8039.16 | 1 | 5000 | 6513.12 | 8039.16 | 0 | 0 | 0 | 0 | 34709.32 | 0 | 0 | 0 | 0 | 0 | 34709.32
2022010712 | 6 | 0.65522 | 52417.6 | 0.20451 | 7362.36 | 0.64978 | 7797.36 | 1 | 5000 | 7362.36 | 7797.36 | 0 | 0 | 0 | 0 | 32257.88 | 0 | 0 | 0 | 0 | 0 | 32257.88
2022010713 | 6 | 0.63208 | 50566.4 | 0.24803 | 8929.08 | 0.63638 | 7636.56 | 1 | 5000 | 8929.08 | 7636.56 | 0 | 0 | 0 | 0 | 29000.76 | 0 | 0 | 0 | 0 | 0 | 29000.76
2022010714 | 6 | 0.616 | 49280 | 0.29461 | 10605.96 | 0.62728 | 7527.36 | 1 | 5000 | 10605.96 | 7527.36 | 0 | 0 | 0 | 0 | 26146.68 | 0 | 0 | 0 | 0 | 0 | 26146.68
2022010715 | 6 | 0.60507 | 48405.6 | 0.32405 | 11665.8 | 0.63264 | 7591.68 | 1 | 5000 | 11665.8 | 7591.68 | 0 | 0 | 0 | 0 | 24148.12 | 0 | 0 | 0 | 0 | 0 | 24148.12
2022010716 | 6 | 0.60758 | 48606.4 | 0.35278 | 12700.08 | 0.62321 | 7478.52 | 1 | 5000 | 12700.08 | 7478.52 | 0 | 0 | 0 | 0 | 23427.8 | 0 | 0 | 0 | 0 | 0 | 23427.8
2022010717 | 6 | 0.61528 | 49222.4 | 0.38388 | 13819.68 | 0.48484 | 5818.08 | 1 | 5000 | 13819.68 | 5818.08 | 0 | 0 | 0 | 0 | 24584.64 | 0 | 0 | 0 | 0 | 0 | 24584.64
2022010718 | 6 | 0.62665 | 50132 | 0.40896 | 14722.56 | 0.11119 | 1334.28 | 1 | 5000 | 14722.56 | 1334.28 | 0 | 0 | 0 | 0 | 29075.16 | 0 | 0 | 0 | 0 | 0 | 29075.16
2022010719 | 6 | 0.64017 | 51213.6 | 0.50167 | 18060.12 | 9e-05 | 1.08 | 1 | 5000 | 18060.12 | 1.08 | 0 | 0 | 0 | 0 | 28152.4 | 0 | 0 | 0 | 0 | 0 | 28152.4
2022010720 | 6 | 0.6328 | 50624 | 0.57189 | 20588.04 | 0 | 0 | 1 | 5000 | 20588.04 | 0 | 0 | 0 | 0 | 0 | 25035.96 | 0 | 0 | 0 | 0 | 0 | 25035.96
2022010721 | 6 | 0.61957 | 49565.6 | 0.56964 | 20507.04 | 0 | 0 | 1 | 5000 | 20507.04 | 0 | 0 | 0 | 0 | 0 | 24058.56 | 0 | 0 | 0 | 0 | 0 | 24058.56
2022010722 | 6 | 0.60063 | 48050.4 | 0.57402 | 20664.72 | 0 | 0 | 1 | 5000 | 20664.72 | 0 | 0 | 0 | 0 | 0 | 22385.68 | 0 | 0 | 0 | 0 | 0 | 22385.68
2022010723 | 6 | 0.57512 | 46009.6 | 0.57121 | 20563.56 | 0 | 0 | 1 | 5000 | 20563.56 | 0 | 0 | 0 | 0 | 0 | 20446.04 | 0 | 0 | 0 | 0 | 0 | 20446.04
2022010724 | 6 | 0.55 | 44000 | 0.56851 | 20466.36 | 0 | 0 | 1 | 5000 | 20466.36 | 0 | 0 | 0 | 0 | 0 | 18533.64 | 0 | 0 | 0 | 0 | 0 | 18533.64
2022010801 | 7 | 0.52779 | 42223.2 | 0.56389 | 20300.04 | 0 | 0 | 1 | 5000 | 20300.04 | 0 | 0 | 0 | 0 | 0 | 16923.16 | 0 | 0 | 0 | 0 | 0 | 16923.16
2022010802 | 7 | 0.51423 | 41138.4 | 0.55874 | 20114.64 | 0 | 0 | 1 | 5000 | 20114.64 | 0 | 0 | 0 | 0 | 0 | 16023.76 | 0 | 0 | 0 | 0 | 0 | 16023.76
2022010803 | 7 | 0.50499 | 40399.2 | 0.55732 | 20063.52 | 0 | 0 | 1 | 5000 | 20063.52 | 0 | 0 | 0 | 0 | 0 | 15335.68 | 0 | 0 | 0 | 0 | 0 | 15335.68
2022010804 | 7 | 0.50118 | 40094.4 | 0.55606 | 20018.16 | 0 | 0 | 1 | 5000 | 20018.16 | 0 | 0 | 0 | 0 | 0 | 15076.24 | 0 | 0 | 0 | 0 | 0 | 15076.24
2022010805 | 7 | 0.50042 | 40033.6 | 0.5556 | 20001.6 | 0 | 0 | 1 | 5000 | 20001.6 | 0 | 0 | 0 | 0 | 0 | 15032 | 0 | 0 | 0 | 0 | 0 | 15032
2022010806 | 7 | 0.50747 | 40597.6 | 0.54638 | 19669.68 | 0 | 0 | 1 | 5000 | 19669.68 | 0 | 0 | 0 | 0 | 0 | 15927.92 | 0 | 0 | 0 | 0 | 0 | 15927.92
2022010807 | 7 | 0.51935 | 41548 | 0.52416 | 18869.76 | 0 | 0 | 1 | 5000 | 18869.76 | 0 | 0 | 0 | 0 | 0 | 17678.24 | 0 | 0 | 0 | 0 | 0 | 17678.24
2022010808 | 7 | 0.53227 | 42581.6 | 0.51296 | 18466.56 | 0.00058 | 6.96 | 1 | 5000 | 18466.56 | 6.96 | 0 | 0 | 0 | 0 | 19108.08 | 0 | 0 | 0 | 0 | 0 | 19108.08
2022010809 | 7 | 0.54664 | 43731.2 | 0.51136 | 18408.96 | 0.13418 | 1610.16 | 1 | 5000 | 18408.96 | 1610.16 | 0 | 0 | 0 | 0 | 18712.08 | 0 | 0 | 0 | 0 | 0 | 18712.08
2022010810 | 7 | 0.55593 | 44474.4 | 0.45729 | 16462.44 | 0.33434 | 4012.08 | 1 | 5000 | 16462.44 | 4012.08 | 0 | 0 | 0 | 0 | 18999.88 | 0 | 0 | 0 | 0 | 0 | 18999.88
2022010811 | 7 | 0.56022 | 44817.6 | 0.42901 | 15444.36 | 0.46122 | 5534.64 | 1 | 5000 | 15444.36 | 5534.64 | 0 | 0 | 0 | 0 | 18838.6 | 0 | 0 | 0 | 0 | 0 | 18838.6
2022010812 | 7 | 0.55682 | 44545.6 | 0.41683 | 15005.88 | 0.51149 | 6137.88 | 1 | 5000 | 15005.88 | 6137.88 | 0 | 0 | 0 | 0 | 18401.84 | 0 | 0 | 0 | 0 | 0 | 18401.84
2022010813 | 7 | 0.5501 | 44008 | 0.41724 | 15020.64 | 0.51636 | 6196.32 | 1 | 5000 | 15020.64 | 6196.32 | 0 | 0 | 0 | 0 | 17791.04 | 0 | 0 | 0 | 0 | 0 | 17791.04
2022010814 | 7 | 0.54064 | 43251.2 | 0.41573 | 14966.28 | 0.49328 | 5919.36 | 1 | 5000 | 14966.28 | 5919.36 | 0 | 0 | 0 | 0 | 17365.56 | 0 | 0 | 0 | 0 | 0 | 17365.56
2022010815 | 7 | 0.53087 | 42469.6 | 0.40179 | 14464.44 | 0.53532 | 6423.84 | 1 | 5000 | 14464.44 | 6423.84 | 0 | 0 | 0 | 0 | 16581.32 | 0 | 0 | 0 | 0 | 0 | 16581.32
2022010816 | 7 | 0.52363 | 41890.4 | 0.39404 | 14185.44 | 0.56412 | 6769.44 | 1 | 5000 | 14185.44 | 6769.44 | 0 | 0 | 0 | 0 | 15935.52 | 0 | 0 | 0 | 0 | 0 | 15935.52
2022010817 | 7 | 0.52128 | 41702.4 | 0.4025 | 14490 | 0.46423 | 5570.76 | 1 | 5000 | 14490 | 5570.76 | 0 | 0 | 0 | 0 | 16641.64 | 0 | 0 | 0 | 0 | 0 | 16641.64
2022010818 | 7 | 0.52614 | 42091.2 | 0.36453 | 13123.08 | 0.12758 | 1530.96 | 1 | 5000 | 13123.08 | 1530.96 | 0 | 0 | 0 | 0 | 22437.16 | 0 | 0 | 0 | 0 | 0 | 22437.16
2022010819 | 7 | 0.53425 | 42740 | 0.35636 | 12828.96 | 0.02108 | 252.96 | 1 | 5000 | 12828.96 | 252.96 | 0 | 0 | 0 | 0 | 24658.08 | 0 | 0 | 0 | 0 | 0 | 24658.08
2022010820 | 7 | 0.52696 | 42156.8 | 0.39954 | 14383.44 | 0.00608 | 72.96 | 1 | 5000 | 14383.44 | 72.96 | 0 | 0 | 0 | 0 | 22700.4 | 0 | 0 | 0 | 0 | 0 | 22700.4
2022010821 | 7 | 0.51602 | 41281.6 | 0.45898 | 16523.28 | 0 | 0 | 1 | 5000 | 16523.28 | 0 | 0 | 0 | 0 | 0 | 19758.32 | 0 | 0 | 0 | 0 | 0 | 19758.32
2022010822 | 7 | 0.50474 | 40379.2 | 0.50275 | 18099 | 0 | 0 | 1 | 5000 | 18099 | 0 | 0 | 0 | 0 | 0 | 17280.2 | 0 | 0 | 0 | 0 | 0 | 17280.2
2022010823 | 7 | 0.48837 | 39069.6 | 0.53517 | 19266.12 | 0 | 0 | 1 | 5000 | 19266.12 | 0 | 0 | 0 | 0 | 0 | 14803.48 | 0 | 0 | 0 | 0 | 0 | 14803.48
2022010824 | 7 | 0.46887 | 37509.6 | 0.51555 | 18559.8 | 0 | 0 | 1 | 5000 | 18559.8 | 0 | 0 | 0 | 0 | 0 | 13949.8 | 0 | 0 | 0 | 0 | 0 | 13949.8
2022010901 | 1 | 0.45116 | 36092.8 | 0.49398 | 17783.28 | 0 | 0 | 1 | 5000 | 17783.28 | 0 | 0 | 0 | 0 | 0 | 13309.52 | 0 | 0 | 0 | 0 | 0 | 13309.52
2022010902 | 1 | 0.43923 | 35138.4 | 0.50027 | 18009.72 | 0 | 0 | 1 | 5000 | 18009.72 | 0 | 0 | 0 | 0 | 0 | 12128.68 | 0 | 0 | 0 | 0 | 0 | 12128.68
2022010903 | 1 | 0.4333 | 34664 | 0.52784 | 19002.24 | 0 | 0 | 1 | 5000 | 19002.24 | 0 | 0 | 0 | 0 | 0 | 10661.76 | 0 | 0 | 0 | 0 | 0 | 10661.76
2022010904 | 1 | 0.43208 | 34566.4 | 0.55528 | 19990.08 | 0 | 0 | 1 | 5000 | 19990.08 | 0 | 0 | 0 | 0 | 0 | 9576.32 | 0 | 0 | 0 | 0 | 0 | 9576.32
2022010905 | 1 | 0.43289 | 34631.2 | 0.5665 | 20394 | 0 | 0 | 1 | 5000 | 20394 | 0 | 0 | 0 | 0 | 0 | 9237.2 | 0 | 0 | 0 | 0 | 0 | 9237.2
2022010906 | 1 | 0.4399 | 35192 | 0.58852 | 21186.72 | 0 | 0 | 1 | 5000 | 21186.72 | 0 | 0 | 0 | 0 | 0 | 9005.28 | 0 | 0 | 0 | 0 | 0 | 9005.28
2022010907 | 1 | 0.45152 | 36121.6 | 0.59525 | 21429 | 0 | 0 | 1 | 5000 | 21429 | 0 | 0 | 0 | 0 | 0 | 9692.6 | 0 | 0 | 0 | 0 | 0 | 9692.6
2022010908 | 1 | 0.46606 | 37284.8 | 0.59738 | 21505.68 | 0.00135 | 16.2 | 1 | 5000 | 21505.68 | 16.2 | 0 | 0 | 0 | 0 | 10762.92 | 0 | 0 | 0 | 0 | 0 | 10762.92
2022010909 | 1 | 0.48308 | 38646.4 | 0.58704 | 21133.44 | 0.05031 | 603.72 | 1 | 5000 | 21133.44 | 603.72 | 0 | 0 | 0 | 0 | 11909.24 | 0 | 0 | 0 | 0 | 0 | 11909.24
2022010910 | 1 | 0.50299 | 40239.2 | 0.56178 | 20224.08 | 0.11767 | 1412.04 | 1 | 5000 | 20224.08 | 1412.04 | 0 | 0 | 0 | 0 | 13603.08 | 0 | 0 | 0 | 0 | 0 | 13603.08
2022010911 | 1 | 0.51795 | 41436 | 0.5616 | 20217.6 | 0.16042 | 1925.04 | 1 | 5000 | 20217.6 | 1925.04 | 0 | 0 | 0 | 0 | 14293.36 | 0 | 0 | 0 | 0 | 0 | 14293.36
2022010912 | 1 | 0.52877 | 42301.6 | 0.55322 | 19915.92 | 0.24336 | 2920.32 | 1 | 5000 | 19915.92 | 2920.32 | 0 | 0 | 0 | 0 | 14465.36 | 0 | 0 | 0 | 0 | 0 | 14465.36
2022010913 | 1 | 0.5316 | 42528 | 0.51374 | 18494.64 | 0.35837 | 4300.44 | 1 | 5000 | 18494.64 | 4300.44 | 0 | 0 | 0 | 0 | 14732.92 | 0 | 0 | 0 | 0 | 0 | 14732.92
2022010914 | 1 | 0.53366 | 42692.8 | 0.50723 | 18260.28 | 0.42775 | 5133 | 1 | 5000 | 18260.28 | 5133 | 0 | 0 | 0 | 0 | 14299.52 | 0 | 0 | 0 | 0 | 0 | 14299.52
2022010915 | 1 | 0.53116 | 42492.8 | 0.49061 | 17661.96 | 0.43372 | 5204.64 | 1 | 5000 | 17661.96 | 5204.64 | 0 | 0 | 0 | 0 | 14626.2 | 0 | 0 | 0 | 0 | 0 | 14626.2
2022010916 | 1 | 0.52676 | 42140.8 | 0.49973 | 17990.28 | 0.36632 | 4395.84 | 1 | 5000 | 17990.28 | 4395.84 | 0 | 0 | 0 | 0 | 14754.68 | 0 | 0 | 0 | 0 | 0 | 14754.68
2022010917 | 1 | 0.52776 | 42220.8 | 0.4939 | 17780.4 | 0.23419 | 2810.28 | 1 | 5000 | 17780.4 | 2810.28 | 0 | 0 | 0 | 0 | 16630.12 | 0 | 0 | 0 | 0 | 0 | 16630.12
2022010918 | 1 | 0.54314 | 43451.2 | 0.47054 | 16939.44 | 0.04226 | 507.12 | 1 | 5000 | 16939.44 | 507.12 | 0 | 0 | 0 | 0 | 21004.64 | 0 | 0 | 0 | 0 | 0 | 21004.64
2022010919 | 1 | 0.56608 | 45286.4 | 0.4538 | 16336.8 | 0 | 0 | 1 | 5000 | 16336.8 | 0 | 0 | 0 | 0 | 0 | 23949.6 | 0 | 0 | 0 | 0 | 0 | 23949.6
2022010920 | 1 | 0.56886 | 45508.8 | 0.47963 | 17266.68 | 0 | 0 | 1 | 5000 | 17266.68 | 0 | 0 | 0 | 0 | 0 | 23242.12 | 0 | 0 | 0 | 0 | 0 | 23242.12
2022010921 | 1 | 0.56273 | 45018.4 | 0.48162 | 17338.32 | 0 | 0 | 1 | 5000 | 17338.32 | 0 | 0 | 0 | 0 | 0 | 22680.08 | 0 | 0 | 0 | 0 | 0 | 22680.08
2022010922 | 1 | 0.55094 | 44075.2 | 0.50316 | 18113.76 | 0 | 0 | 1 | 5000 | 18113.76 | 0 | 0 | 0 | 0 | 0 | 20961.44 | 0 | 0 | 0 | 0 | 0 | 20961.44
2022010923 | 1 | 0.52934 | 42347.2 | 0.47255 | 17011.8 | 0 | 0 | 1 | 5000 | 17011.8 | 0 | 0 | 0 | 0 | 0 | 20335.4 | 0 | 0 | 0 | 0 | 0 | 20335.4
2022010924 | 1 | 0.50858 | 40686.4 | 0.44659 | 16077.24 | 0 | 0 | 1 | 5000 | 16077.24 | 0 | 0 | 0 | 0 | 0 | 19609.16 | 0 | 0 | 0 | 0 | 0 | 19609.16
2022011001 | 2 | 0.49479 | 39583.2 | 0.42945 | 15460.2 | 0 | 0 | 1 | 5000 | 15460.2 | 0 | 0 | 0 | 0 | 0 | 19123 | 0 | 0 | 0 | 0 | 0 | 19123
2022011002 | 2 | 0.49103 | 39282.4 | 0.41829 | 15058.44 | 0 | 0 | 1 | 5000 | 15058.44 | 0 | 0 | 0 | 0 | 0 | 19223.96 | 0 | 0 | 0 | 0 | 0 | 19223.96
2022011003 | 2 | 0.49345 | 39476 | 0.40851 | 14706.36 | 0 | 0 | 1 | 5000 | 14706.36 | 0 | 0 | 0 | 0 | 0 | 19769.64 | 0 | 0 | 0 | 0 | 0 | 19769.64
2022011004 | 2 | 0.50022 | 40017.6 | 0.40016 | 14405.76 | 0 | 0 | 1 | 5000 | 14405.76 | 0 | 0 | 0 | 0 | 0 | 20611.84 | 0 | 0 | 0 | 0 | 0 | 20611.84
2022011005 | 2 | 0.51712 | 41369.6 | 0.34294 | 12345.84 | 0 | 0 | 1 | 5000 | 12345.84 | 0 | 0 | 0 | 0 | 0 | 24023.76 | 0 | 0 | 0 | 0 | 0 | 24023.76
2022011006 | 2 | 0.55359 | 44287.2 | 0.32968 | 11868.48 | 0 | 0 | 1 | 5000 | 11868.48 | 0 | 0 | 0 | 0 | 0 | 27418.72 | 0 | 0 | 0 | 0 | 0 | 27418.72
2022011007 | 2 | 0.60716 | 48572.8 | 0.32267 | 11616.12 | 0 | 0 | 1 | 5000 | 11616.12 | 0 | 0 | 0 | 0 | 0 | 31956.68 | 0 | 0 | 0 | 0 | 0 | 31956.68
2022011008 | 2 | 0.63906 | 51124.8 | 0.27499 | 9899.64 | 0.00343 | 41.16 | 1 | 5000 | 9899.64 | 41.16 | 0 | 0 | 0 | 0 | 36184 | 0 | 0 | 0 | 0 | 0 | 36184
2022011009 | 2 | 0.64012 | 51209.6 | 0.23003 | 8281.08 | 0.11373 | 1364.76 | 1 | 5000 | 8281.08 | 1364.76 | 0 | 0 | 0 | 0 | 36563.76 | 0 | 0 | 0 | 0 | 0 | 36563.76
2022011010 | 2 | 0.62526 | 50020.8 | 0.18591 | 6692.76 | 0.3229 | 3874.8 | 1 | 5000 | 6692.76 | 3874.8 | 0 | 0 | 0 | 0 | 34453.24 | 0 | 0 | 0 | 0 | 0 | 34453.24
2022011011 | 2 | 0.60658 | 48526.4 | 0.15808 | 5690.88 | 0.40032 | 4803.84 | 1 | 5000 | 5690.88 | 4803.84 | 0 | 0 | 0 | 0 | 33031.68 | 0 | 0 | 0 | 0 | 0 | 33031.68
2022011012 | 2 | 0.58501 | 46800.8 | 0.14008 | 5042.88 | 0.49136 | 5896.32 | 1 | 5000 | 5042.88 | 5896.32 | 0 | 0 | 0 | 0 | 30861.6 | 0 | 0 | 0 | 0 | 0 | 30861.6
2022011013 | 2 | 0.56504 | 45203.2 | 0.11889 | 4280.04 | 0.49715 | 5965.8 | 1 | 5000 | 4280.04 | 5965.8 | 0 | 0 | 0 | 0 | 29957.36 | 0 | 0 | 0 | 0 | 0 | 29957.36
2022011014 | 2 | 0.54923 | 43938.4 | 0.11353 | 4087.08 | 0.50225 | 6027 | 1 | 5000 | 4087.08 | 6027 | 0 | 0 | 0 | 0 | 28824.32 | 0 | 0 | 0 | 0 | 0 | 28824.32
2022011015 | 2 | 0.534 | 42720 | 0.1129 | 4064.4 | 0.51852 | 6222.24 | 1 | 5000 | 4064.4 | 6222.24 | 0 | 0 | 0 | 0 | 27433.36 | 0 | 0 | 0 | 0 | 0 | 27433.36
2022011016 | 2 | 0.52596 | 42076.8 | 0.10656 | 3836.16 | 0.41455 | 4974.6 | 1 | 5000 | 3836.16 | 4974.6 | 0 | 0 | 0 | 0 | 28266.04 | 0 | 0 | 0 | 0 | 0 | 28266.04
2022011017 | 2 | 0.53356 | 42684.8 | 0.09115 | 3281.4 | 0.28413 | 3409.56 | 1 | 5000 | 3281.4 | 3409.56 | 0 | 0 | 0 | 0 | 30993.84 | 0 | 0 | 0 | 0 | 0 | 30993.84
2022011018 | 2 | 0.56093 | 44874.4 | 0.08063 | 2902.68 | 0.04311 | 517.32 | 1 | 5000 | 2902.68 | 517.32 | 0 | 0 | 0 | 0 | 36454.4 | 0 | 0 | 0 | 0 | 0 | 36454.4
2022011019 | 2 | 0.59521 | 47616.8 | 0.09564 | 3443.04 | 0 | 0 | 1 | 5000 | 3443.04 | 0 | 0 | 0 | 0 | 0 | 39173.76 | 0 | 0 | 0 | 0 | 0 | 39173.76
2022011020 | 2 | 0.59962 | 47969.6 | 0.13359 | 4809.24 | 0 | 0 | 1 | 5000 | 4809.24 | 0 | 0 | 0 | 0 | 0 | 38160.36 | 0 | 0 | 0 | 0 | 0 | 38160.36
2022011021 | 2 | 0.59874 | 47899.2 | 0.15336 | 5520.96 | 0 | 0 | 1 | 5000 | 5520.96 | 0 | 0 | 0 | 0 | 0 | 37378.24 | 0 | 0 | 0 | 0 | 0 | 37378.24
2022011022 | 2 | 0.58797 | 47037.6 | 0.17149 | 6173.64 | 0 | 0 | 1 | 5000 | 6173.64 | 0 | 0 | 0 | 0 | 0 | 35863.96 | 0 | 0 | 0 | 0 | 0 | 35863.96
2022011023 | 2 | 0.56541 | 45232.8 | 0.18238 | 6565.68 | 0 | 0 | 1 | 5000 | 6565.68 | 0 | 0 | 0 | 0 | 0 | 33667.12 | 0 | 0 | 0 | 0 | 0 | 33667.12
2022011024 | 2 | 0.54649 | 43719.2 | 0.20122 | 7243.92 | 0 | 0 | 1 | 5000 | 7243.92 | 0 | 0 | 0 | 0 | 0 | 31475.28 | 0 | 0 | 0 | 0 | 0 | 31475.28
2022011101 | 3 | 0.53341 | 42672.8 | 0.21655 | 7795.8 | 0 | 0 | 1 | 5000 | 7795.8 | 0 | 0 | 0 | 0 | 0 | 29877 | 0 | 0 | 0 | 0 | 0 | 29877
2022011102 | 3 | 0.53186 | 42548.8 | 0.26195 | 9430.2 | 0 | 0 | 1 | 5000 | 9430.2 | 0 | 0 | 0 | 0 | 0 | 28118.6 | 0 | 0 | 0 | 0 | 0 | 28118.6
2022011103 | 3 | 0.53393 | 42714.4 | 0.28614 | 10301.04 | 0 | 0 | 1 | 5000 | 10301.04 | 0 | 0 | 0 | 0 | 0 | 27413.36 | 0 | 0 | 0 | 0 | 0 | 27413.36
2022011104 | 3 | 0.54224 | 43379.2 | 0.30118 | 10842.48 | 0 | 0 | 1 | 5000 | 10842.48 | 0 | 0 | 0 | 0 | 0 | 27536.72 | 0 | 0 | 0 | 0 | 0 | 27536.72
2022011105 | 3 | 0.55631 | 44504.8 | 0.28956 | 10424.16 | 0 | 0 | 1 | 5000 | 10424.16 | 0 | 0 | 0 | 0 | 0 | 29080.64 | 0 | 0 | 0 | 0 | 0 | 29080.64
2022011106 | 3 | 0.59234 | 47387.2 | 0.28439 | 10238.04 | 0 | 0 | 1 | 5000 | 10238.04 | 0 | 0 | 0 | 0 | 0 | 32149.16 | 0 | 0 | 0 | 0 | 0 | 32149.16
2022011107 | 3 | 0.64194 | 51355.2 | 0.2951 | 10623.6 | 0 | 0 | 1 | 5000 | 10623.6 | 0 | 0 | 0 | 0 | 0 | 35731.6 | 0 | 0 | 0 | 0 | 0 | 35731.6
2022011108 | 3 | 0.66541 | 53232.8 | 0.30919 | 11130.84 | 0.00463 | 55.56 | 1 | 5000 | 11130.84 | 55.56 | 0 | 0 | 0 | 0 | 37046.4 | 0 | 0 | 0 | 0 | 0 | 37046.4
2022011109 | 3 | 0.65497 | 52397.6 | 0.28956 | 10424.16 | 0.10511 | 1261.32 | 1 | 5000 | 10424.16 | 1261.32 | 0 | 0 | 0 | 0 | 35712.12 | 0 | 0 | 0 | 0 | 0 | 35712.12
2022011110 | 3 | 0.63188 | 50550.4 | 0.24622 | 8863.92 | 0.32642 | 3917.04 | 1 | 5000 | 8863.92 | 3917.04 | 0 | 0 | 0 | 0 | 32769.44 | 0 | 0 | 0 | 0 | 0 | 32769.44
2022011111 | 3 | 0.6094 | 48752 | 0.25071 | 9025.56 | 0.41488 | 4978.56 | 1 | 5000 | 9025.56 | 4978.56 | 0 | 0 | 0 | 0 | 29747.88 | 0 | 0 | 0 | 0 | 0 | 29747.88
2022011112 | 3 | 0.59371 | 47496.8 | 0.29531 | 10631.16 | 0.51618 | 6194.16 | 1 | 5000 | 10631.16 | 6194.16 | 0 | 0 | 0 | 0 | 25671.48 | 0 | 0 | 0 | 0 | 0 | 25671.48
2022011113 | 3 | 0.57866 | 46292.8 | 0.29648 | 10673.28 | 0.53312 | 6397.44 | 1 | 5000 | 10673.28 | 6397.44 | 0 | 0 | 0 | 0 | 24222.08 | 0 | 0 | 0 | 0 | 0 | 24222.08
2022011114 | 3 | 0.56651 | 45320.8 | 0.31478 | 11332.08 | 0.53103 | 6372.36 | 1 | 5000 | 11332.08 | 6372.36 | 0 | 0 | 0 | 0 | 22616.36 | 0 | 0 | 0 | 0 | 0 | 22616.36
2022011115 | 3 | 0.5573 | 44584 | 0.32964 | 11867.04 | 0.57562 | 6907.44 | 1 | 5000 | 11867.04 | 6907.44 | 0 | 0 | 0 | 0 | 20809.52 | 0 | 0 | 0 | 0 | 0 | 20809.52
2022011116 | 3 | 0.55656 | 44524.8 | 0.30524 | 10988.64 | 0.5475 | 6570 | 1 | 5000 | 10988.64 | 6570 | 0 | 0 | 0 | 0 | 21966.16 | 0 | 0 | 0 | 0 | 0 | 21966.16
2022011117 | 3 | 0.56657 | 45325.6 | 0.25514 | 9185.04 | 0.33952 | 4074.24 | 1 | 5000 | 9185.04 | 4074.24 | 0 | 0 | 0 | 0 | 27066.32 | 0 | 0 | 0 | 0 | 0 | 27066.32
2022011118 | 3 | 0.58724 | 46979.2 | 0.21008 | 7562.88 | 0.07152 | 858.24 | 1 | 5000 | 7562.88 | 858.24 | 0 | 0 | 0 | 0 | 33558.08 | 0 | 0 | 0 | 0 | 0 | 33558.08
2022011119 | 3 | 0.60572 | 48457.6 | 0.25595 | 9214.2 | 0.00026 | 3.12 | 1 | 5000 | 9214.2 | 3.12 | 0 | 0 | 0 | 0 | 34240.28 | 0 | 0 | 0 | 0 | 0 | 34240.28
2022011120 | 3 | 0.60356 | 48284.8 | 0.33679 | 12124.44 | 0 | 0 | 1 | 5000 | 12124.44 | 0 | 0 | 0 | 0 | 0 | 31160.36 | 0 | 0 | 0 | 0 | 0 | 31160.36
2022011121 | 3 | 0.59739 | 47791.2 | 0.39771 | 14317.56 | 0 | 0 | 1 | 5000 | 14317.56 | 0 | 0 | 0 | 0 | 0 | 28473.64 | 0 | 0 | 0 | 0 | 0 | 28473.64
2022011122 | 3 | 0.57923 | 46338.4 | 0.41142 | 14811.12 | 0 | 0 | 1 | 5000 | 14811.12 | 0 | 0 | 0 | 0 | 0 | 26527.28 | 0 | 0 | 0 | 0 | 0 | 26527.28
2022011123 | 3 | 0.54956 | 43964.8 | 0.4088 | 14716.8 | 0 | 0 | 1 | 5000 | 14716.8 | 0 | 0 | 0 | 0 | 0 | 24248 | 0 | 0 | 0 | 0 | 0 | 24248
2022011124 | 3 | 0.52311 | 41848.8 | 0.40946 | 14740.56 | 0 | 0 | 1 | 5000 | 14740.56 | 0 | 0 | 0 | 0 | 0 | 22108.24 | 0 | 0 | 0 | 0 | 0 | 22108.24
2022011201 | 4 | 0.50715 | 40572 | 0.39785 | 14322.6 | 0 | 0 | 1 | 5000 | 14322.6 | 0 | 0 | 0 | 0 | 0 | 21249.4 | 0 | 0 | 0 | 0 | 0 | 21249.4
2022011202 | 4 | 0.49972 | 39977.6 | 0.37416 | 13469.76 | 0 | 0 | 1 | 5000 | 13469.76 | 0 | 0 | 0 | 0 | 0 | 21507.84 | 0 | 0 | 0 | 0 | 0 | 21507.84
2022011203 | 4 | 0.49596 | 39676.8 | 0.35619 | 12822.84 | 0 | 0 | 1 | 5000 | 12822.84 | 0 | 0 | 0 | 0 | 0 | 21853.96 | 0 | 0 | 0 | 0 | 0 | 21853.96
2022011204 | 4 | 0.50032 | 40025.6 | 0.33063 | 11902.68 | 0 | 0 | 1 | 5000 | 11902.68 | 0 | 0 | 0 | 0 | 0 | 23122.92 | 0 | 0 | 0 | 0 | 0 | 23122.92
2022011205 | 4 | 0.51409 | 41127.2 | 0.2951 | 10623.6 | 0 | 0 | 1 | 5000 | 10623.6 | 0 | 0 | 0 | 0 | 0 | 25503.6 | 0 | 0 | 0 | 0 | 0 | 25503.6
2022011206 | 4 | 0.54515 | 43612 | 0.25562 | 9202.32 | 0 | 0 | 1 | 5000 | 9202.32 | 0 | 0 | 0 | 0 | 0 | 29409.68 | 0 | 0 | 0 | 0 | 0 | 29409.68
2022011207 | 4 | 0.58954 | 47163.2 | 0.23353 | 8407.08 | 0 | 0 | 1 | 5000 | 8407.08 | 0 | 0 | 0 | 0 | 0 | 33756.12 | 0 | 0 | 0 | 0 | 0 | 33756.12
2022011208 | 4 | 0.61428 | 49142.4 | 0.19859 | 7149.24 | 0.00136 | 16.32 | 1 | 5000 | 7149.24 | 16.32 | 0 | 0 | 0 | 0 | 36976.84 | 0 | 0 | 0 | 0 | 0 | 36976.84
2022011209 | 4 | 0.60955 | 48764 | 0.17275 | 6219 | 0.20424 | 2450.88 | 1 | 5000 | 6219 | 2450.88 | 0 | 0 | 0 | 0 | 35094.12 | 0 | 0 | 0 | 0 | 0 | 35094.12
2022011210 | 4 | 0.59382 | 47505.6 | 0.10943 | 3939.48 | 0.6113 | 7335.6 | 1 | 5000 | 3939.48 | 7335.6 | 0 | 0 | 0 | 0 | 31230.52 | 0 | 0 | 0 | 0 | 0 | 31230.52
2022011211 | 4 | 0.57731 | 46184.8 | 0.07156 | 2576.16 | 0.67101 | 8052.12 | 1 | 5000 | 2576.16 | 8052.12 | 0 | 0 | 0 | 0 | 30556.52 | 0 | 0 | 0 | 0 | 0 | 30556.52
2022011212 | 4 | 0.5579 | 44632 | 0.05723 | 2060.28 | 0.67133 | 8055.96 | 1 | 5000 | 2060.28 | 8055.96 | 0 | 0 | 0 | 0 | 29515.76 | 0 | 0 | 0 | 0 | 0 | 29515.76
2022011213 | 4 | 0.53874 | 43099.2 | 0.05782 | 2081.52 | 0.65504 | 7860.48 | 1 | 5000 | 2081.52 | 7860.48 | 0 | 0 | 0 | 0 | 28157.2 | 0 | 0 | 0 | 0 | 0 | 28157.2
2022011214 | 4 | 0.52102 | 41681.6 | 0.06738 | 2425.68 | 0.6748 | 8097.6 | 1 | 5000 | 2425.68 | 8097.6 | 0 | 0 | 0 | 0 | 26158.32 | 0 | 0 | 0 | 0 | 0 | 26158.32
2022011215 | 4 | 0.50862 | 40689.6 | 0.0532 | 1915.2 | 0.69551 | 8346.12 | 1 | 5000 | 1915.2 | 8346.12 | 0 | 0 | 0 | 0 | 25428.28 | 0 | 0 | 0 | 0 | 0 | 25428.28
2022011216 | 4 | 0.50379 | 40303.2 | 0.03379 | 1216.44 | 0.72545 | 8705.4 | 1 | 5000 | 1216.44 | 8705.4 | 0 | 0 | 0 | 0 | 25381.36 | 0 | 0 | 0 | 0 | 0 | 25381.36
2022011217 | 4 | 0.50796 | 40636.8 | 0.02284 | 822.24 | 0.58879 | 7065.48 | 1 | 5000 | 822.24 | 7065.48 | 0 | 0 | 0 | 0 | 27749.08 | 0 | 0 | 0 | 0 | 0 | 27749.08
2022011218 | 4 | 0.52654 | 42123.2 | 0.02504 | 901.44 | 0.1457 | 1748.4 | 1 | 5000 | 901.44 | 1748.4 | 0 | 0 | 0 | 0 | 34473.36 | 0 | 0 | 0 | 0 | 0 | 34473.36
2022011219 | 4 | 0.55246 | 44196.8 | 0.02487 | 895.32 | 0 | 0 | 1 | 5000 | 895.32 | 0 | 0 | 0 | 0 | 0 | 38301.48 | 0 | 0 | 0 | 0 | 0 | 38301.48
2022011220 | 4 | 0.55401 | 44320.8 | 0.03045 | 1096.2 | 0 | 0 | 1 | 5000 | 1096.2 | 0 | 0 | 0 | 0 | 0 | 38224.6 | 0 | 0 | 0 | 0 | 0 | 38224.6
2022011221 | 4 | 0.55109 | 44087.2 | 0.03511 | 1263.96 | 0 | 0 | 1 | 5000 | 1263.96 | 0 | 0 | 0 | 0 | 0 | 37823.24 | 0 | 0 | 0 | 0 | 0 | 37823.24
2022011222 | 4 | 0.53998 | 43198.4 | 0.03511 | 1263.96 | 0 | 0 | 1 | 5000 | 1263.96 | 0 | 0 | 0 | 0 | 0 | 36934.44 | 0 | 0 | 0 | 0 | 0 | 36934.44
2022011223 | 4 | 0.51868 | 41494.4 | 0.03755 | 1351.8 | 0 | 0 | 1 | 5000 | 1351.8 | 0 | 0 | 0 | 0 | 0 | 35142.6 | 0 | 0 | 0 | 0 | 0 | 35142.6
2022011224 | 4 | 0.49963 | 39970.4 | 0.05239 | 1886.04 | 0 | 0 | 1 | 5000 | 1886.04 | 0 | 0 | 0 | 0 | 0 | 33084.36 | 0 | 0 | 0 | 0 | 0 | 33084.36
2022011301 | 5 | 0.48912 | 39129.6 | 0.06838 | 2461.68 | 0 | 0 | 1 | 5000 | 2461.68 | 0 | 0 | 0 | 0 | 0 | 31667.92 | 0 | 0 | 0 | 0 | 0 | 31667.92
2022011302 | 5 | 0.48515 | 38812 | 0.08516 | 3065.76 | 0 | 0 | 1 | 5000 | 3065.76 | 0 | 0 | 0 | 0 | 0 | 30746.24 | 0 | 0 | 0 | 0 | 0 | 30746.24
2022011303 | 5 | 0.48889 | 39111.2 | 0.08507 | 3062.52 | 0 | 0 | 1 | 5000 | 3062.52 | 0 | 0 | 0 | 0 | 0 | 31048.68 | 0 | 0 | 0 | 0 | 0 | 31048.68
2022011304 | 5 | 0.49706 | 39764.8 | 0.08799 | 3167.64 | 0 | 0 | 1 | 5000 | 3167.64 | 0 | 0 | 0 | 0 | 0 | 31597.16 | 0 | 0 | 0 | 0 | 0 | 31597.16
2022011305 | 5 | 0.51443 | 41154.4 | 0.09972 | 3589.92 | 0 | 0 | 1 | 5000 | 3589.92 | 0 | 0 | 0 | 0 | 0 | 32564.48 | 0 | 0 | 0 | 0 | 0 | 32564.48
2022011306 | 5 | 0.54853 | 43882.4 | 0.13188 | 4747.68 | 0 | 0 | 1 | 5000 | 4747.68 | 0 | 0 | 0 | 0 | 0 | 34134.72 | 0 | 0 | 0 | 0 | 0 | 34134.72
2022011307 | 5 | 0.59752 | 47801.6 | 0.15113 | 5440.68 | 0 | 0 | 1 | 5000 | 5440.68 | 0 | 0 | 0 | 0 | 0 | 37360.92 | 0 | 0 | 0 | 0 | 0 | 37360.92
2022011308 | 5 | 0.62121 | 49696.8 | 0.15223 | 5480.28 | 0.0061 | 73.2 | 1 | 5000 | 5480.28 | 73.2 | 0 | 0 | 0 | 0 | 39143.32 | 0 | 0 | 0 | 0 | 0 | 39143.32
2022011309 | 5 | 0.60527 | 48421.6 | 0.13874 | 4994.64 | 0.27477 | 3297.24 | 1 | 5000 | 4994.64 | 3297.24 | 0 | 0 | 0 | 0 | 35129.72 | 0 | 0 | 0 | 0 | 0 | 35129.72
2022011310 | 5 | 0.57416 | 45932.8 | 0.07623 | 2744.28 | 0.69948 | 8393.76 | 1 | 5000 | 2744.28 | 8393.76 | 0 | 0 | 0 | 0 | 29794.76 | 0 | 0 | 0 | 0 | 0 | 29794.76
2022011311 | 5 | 0.5467 | 43736 | 0.02029 | 730.44 | 0.74219 | 8906.28 | 1 | 5000 | 730.44 | 8906.28 | 0 | 0 | 0 | 0 | 29099.28 | 0 | 0 | 0 | 0 | 0 | 29099.28
2022011312 | 5 | 0.52471 | 41976.8 | 0.01158 | 416.88 | 0.71187 | 8542.44 | 1 | 5000 | 416.88 | 8542.44 | 0 | 0 | 0 | 0 | 28017.48 | 0 | 0 | 0 | 0 | 0 | 28017.48
2022011313 | 5 | 0.5098 | 40784 | 0.01056 | 380.16 | 0.6863 | 8235.6 | 1 | 5000 | 380.16 | 8235.6 | 0 | 0 | 0 | 0 | 27168.24 | 0 | 0 | 0 | 0 | 0 | 27168.24
2022011314 | 5 | 0.50274 | 40219.2 | 0.00909 | 327.24 | 0.69265 | 8311.8 | 1 | 5000 | 327.24 | 8311.8 | 0 | 0 | 0 | 0 | 26580.16 | 0 | 0 | 0 | 0 | 0 | 26580.16
2022011315 | 5 | 0.4987 | 39896 | 0.01321 | 475.56 | 0.71443 | 8573.16 | 1 | 5000 | 475.56 | 8573.16 | 0 | 0 | 0 | 0 | 25847.28 | 0 | 0 | 0 | 0 | 0 | 25847.28
2022011316 | 5 | 0.4984 | 39872 | 0.01123 | 404.28 | 0.72941 | 8752.92 | 1 | 5000 | 404.28 | 8752.92 | 0 | 0 | 0 | 0 | 25714.8 | 0 | 0 | 0 | 0 | 0 | 25714.8
2022011317 | 5 | 0.50162 | 40129.6 | 0.00892 | 321.12 | 0.60235 | 7228.2 | 1 | 5000 | 321.12 | 7228.2 | 0 | 0 | 0 | 0 | 27580.28 | 0 | 0 | 0 | 0 | 0 | 27580.28
2022011318 | 5 | 0.50913 | 40730.4 | 0.01268 | 456.48 | 0.15314 | 1837.68 | 1 | 5000 | 456.48 | 1837.68 | 0 | 0 | 0 | 0 | 33436.24 | 0 | 0 | 0 | 0 | 0 | 33436.24
2022011319 | 5 | 0.52656 | 42124.8 | 0.02282 | 821.52 | 0.00036 | 4.32 | 1 | 5000 | 821.52 | 4.32 | 0 | 0 | 0 | 0 | 36298.96 | 0 | 0 | 0 | 0 | 0 | 36298.96
2022011320 | 5 | 0.52381 | 41904.8 | 0.03655 | 1315.8 | 0 | 0 | 1 | 5000 | 1315.8 | 0 | 0 | 0 | 0 | 0 | 35589 | 0 | 0 | 0 | 0 | 0 | 35589
2022011321 | 5 | 0.51649 | 41319.2 | 0.06431 | 2315.16 | 0 | 0 | 1 | 5000 | 2315.16 | 0 | 0 | 0 | 0 | 0 | 34004.04 | 0 | 0 | 0 | 0 | 0 | 34004.04
2022011322 | 5 | 0.50451 | 40360.8 | 0.11398 | 4103.28 | 0 | 0 | 1 | 5000 | 4103.28 | 0 | 0 | 0 | 0 | 0 | 31257.52 | 0 | 0 | 0 | 0 | 0 | 31257.52
2022011323 | 5 | 0.48369 | 38695.2 | 0.18052 | 6498.72 | 0 | 0 | 1 | 5000 | 6498.72 | 0 | 0 | 0 | 0 | 0 | 27196.48 | 0 | 0 | 0 | 0 | 0 | 27196.48
2022011324 | 5 | 0.46249 | 36999.2 | 0.23399 | 8423.64 | 0 | 0 | 1 | 5000 | 8423.64 | 0 | 0 | 0 | 0 | 0 | 23575.56 | 0 | 0 | 0 | 0 | 0 | 23575.56
2022011401 | 6 | 0.45162 | 36129.6 | 0.29469 | 10608.84 | 0 | 0 | 1 | 5000 | 10608.84 | 0 | 0 | 0 | 0 | 0 | 20520.76 | 0 | 0 | 0 | 0 | 0 | 20520.76
2022011402 | 6 | 0.44982 | 35985.6 | 0.36609 | 13179.24 | 0 | 0 | 1 | 5000 | 13179.24 | 0 | 0 | 0 | 0 | 0 | 17806.36 | 0 | 0 | 0 | 0 | 0 | 17806.36
2022011403 | 6 | 0.45294 | 36235.2 | 0.39642 | 14271.12 | 0 | 0 | 1 | 5000 | 14271.12 | 0 | 0 | 0 | 0 | 0 | 16964.08 | 0 | 0 | 0 | 0 | 0 | 16964.08
2022011404 | 6 | 0.46142 | 36913.6 | 0.39913 | 14368.68 | 0 | 0 | 1 | 5000 | 14368.68 | 0 | 0 | 0 | 0 | 0 | 17544.92 | 0 | 0 | 0 | 0 | 0 | 17544.92
2022011405 | 6 | 0.47793 | 38234.4 | 0.4282 | 15415.2 | 0 | 0 | 1 | 5000 | 15415.2 | 0 | 0 | 0 | 0 | 0 | 17819.2 | 0 | 0 | 0 | 0 | 0 | 17819.2
2022011406 | 6 | 0.51261 | 41008.8 | 0.46941 | 16898.76 | 0 | 0 | 1 | 5000 | 16898.76 | 0 | 0 | 0 | 0 | 0 | 19110.04 | 0 | 0 | 0 | 0 | 0 | 19110.04
2022011407 | 6 | 0.56183 | 44946.4 | 0.49301 | 17748.36 | 0 | 0 | 1 | 5000 | 17748.36 | 0 | 0 | 0 | 0 | 0 | 22198.04 | 0 | 0 | 0 | 0 | 0 | 22198.04
2022011408 | 6 | 0.59042 | 47233.6 | 0.52862 | 19030.32 | 0.00505 | 60.6 | 1 | 5000 | 19030.32 | 60.6 | 0 | 0 | 0 | 0 | 23142.68 | 0 | 0 | 0 | 0 | 0 | 23142.68
2022011409 | 6 | 0.58554 | 46843.2 | 0.52786 | 19002.96 | 0.21295 | 2555.4 | 1 | 5000 | 19002.96 | 2555.4 | 0 | 0 | 0 | 0 | 20284.84 | 0 | 0 | 0 | 0 | 0 | 20284.84
2022011410 | 6 | 0.56289 | 45031.2 | 0.44345 | 15964.2 | 0.50933 | 6111.96 | 1 | 5000 | 15964.2 | 6111.96 | 0 | 0 | 0 | 0 | 17955.04 | 0 | 0 | 0 | 0 | 0 | 17955.04
2022011411 | 6 | 0.54203 | 43362.4 | 0.40089 | 14432.04 | 0.61597 | 7391.64 | 1 | 5000 | 14432.04 | 7391.64 | 0 | 0 | 0 | 0 | 16538.72 | 0 | 0 | 0 | 0 | 0 | 16538.72
2022011412 | 6 | 0.52667 | 42133.6 | 0.43914 | 15809.04 | 0.58194 | 6983.28 | 1 | 5000 | 15809.04 | 6983.28 | 0 | 0 | 0 | 0 | 14341.28 | 0 | 0 | 0 | 0 | 0 | 14341.28
2022011413 | 6 | 0.51857 | 41485.6 | 0.50876 | 18315.36 | 0.41766 | 5011.92 | 1 | 5000 | 18315.36 | 5011.92 | 0 | 0 | 0 | 0 | 13158.32 | 0 | 0 | 0 | 0 | 0 | 13158.32
2022011414 | 6 | 0.51483 | 41186.4 | 0.51341 | 18482.76 | 0.45386 | 5446.32 | 1 | 5000 | 18482.76 | 5446.32 | 0 | 0 | 0 | 0 | 12257.32 | 0 | 0 | 0 | 0 | 0 | 12257.32
2022011415 | 6 | 0.51232 | 40985.6 | 0.48509 | 17463.24 | 0.55262 | 6631.44 | 1 | 5000 | 17463.24 | 6631.44 | 0 | 0 | 0 | 0 | 11890.92 | 0 | 0 | 0 | 0 | 0 | 11890.92
2022011416 | 6 | 0.50928 | 40742.4 | 0.46265 | 16655.4 | 0.5321 | 6385.2 | 1 | 5000 | 16655.4 | 6385.2 | 0 | 0 | 0 | 0 | 12701.8 | 0 | 0 | 0 | 0 | 0 | 12701.8
2022011417 | 6 | 0.51039 | 40831.2 | 0.47653 | 17155.08 | 0.4081 | 4897.2 | 1 | 5000 | 17155.08 | 4897.2 | 0 | 0 | 0 | 0 | 13778.92 | 0 | 0 | 0 | 0 | 0 | 13778.92
2022011418 | 6 | 0.5138 | 41104 | 0.50045 | 18016.2 | 0.09704 | 1164.48 | 1 | 5000 | 18016.2 | 1164.48 | 0 | 0 | 0 | 0 | 16923.32 | 0 | 0 | 0 | 0 | 0 | 16923.32
2022011419 | 6 | 0.52638 | 42110.4 | 0.58521 | 21067.56 | 0.00025 | 3 | 1 | 5000 | 21067.56 | 3 | 0 | 0 | 0 | 0 | 16039.84 | 0 | 0 | 0 | 0 | 0 | 16039.84
2022011420 | 6 | 0.51979 | 41583.2 | 0.65356 | 23528.16 | 0 | 0 | 1 | 5000 | 23528.16 | 0 | 0 | 0 | 0 | 0 | 13055.04 | 0 | 0 | 0 | 0 | 0 | 13055.04
2022011421 | 6 | 0.51132 | 40905.6 | 0.66848 | 24065.28 | 0 | 0 | 1 | 5000 | 24065.28 | 0 | 0 | 0 | 0 | 0 | 11840.32 | 0 | 0 | 0 | 0 | 0 | 11840.32
2022011422 | 6 | 0.49808 | 39846.4 | 0.66491 | 23936.76 | 0 | 0 | 1 | 5000 | 23936.76 | 0 | 0 | 0 | 0 | 0 | 10909.64 | 0 | 0 | 0 | 0 | 0 | 10909.64
2022011423 | 6 | 0.48123 | 38498.4 | 0.666 | 23976 | 0 | 0 | 1 | 5000 | 23976 | 0 | 0 | 0 | 0 | 0 | 9522.4 | 0 | 0 | 0 | 0 | 0 | 9522.4
2022011424 | 6 | 0.46582 | 37265.6 | 0.65456 | 23564.16 | 0 | 0 | 1 | 5000 | 23564.16 | 0 | 0 | 0 | 0 | 0 | 8701.44 | 0 | 0 | 0 | 0 | 0 | 8701.44
2022011501 | 7 | 0.45227 | 36181.6 | 0.6313 | 22726.8 | 0 | 0 | 1 | 5000 | 22726.8 | 0 | 0 | 0 | 0 | 0 | 8454.8 | 0 | 0 | 0 | 0 | 0 | 8454.8
2022011502 | 7 | 0.44708 | 35766.4 | 0.63586 | 22890.96 | 0 | 0 | 1 | 5000 | 22890.96 | 0 | 0 | 0 | 0 | 0 | 7875.44 | 0 | 0 | 0 | 0 | 0 | 7875.44
2022011503 | 7 | 0.44851 | 35880.8 | 0.64358 | 23168.88 | 0 | 0 | 1 | 5000 | 23168.88 | 0 | 0 | 0 | 0 | 0 | 7711.92 | 0 | 0 | 0 | 0 | 0 | 7711.92
2022011504 | 7 | 0.45577 | 36461.6 | 0.64279 | 23140.44 | 0 | 0 | 1 | 5000 | 23140.44 | 0 | 0 | 0 | 0 | 0 | 8321.16 | 0 | 0 | 0 | 0 | 0 | 8321.16
2022011505 | 7 | 0.46819 | 37455.2 | 0.66935 | 24096.6 | 0 | 0 | 1 | 5000 | 24096.6 | 0 | 0 | 0 | 0 | 0 | 8358.6 | 0 | 0 | 0 | 0 | 0 | 8358.6
2022011506 | 7 | 0.49018 | 39214.4 | 0.68071 | 24505.56 | 0 | 0 | 1 | 5000 | 24505.56 | 0 | 0 | 0 | 0 | 0 | 9708.84 | 0 | 0 | 0 | 0 | 0 | 9708.84
2022011507 | 7 | 0.52037 | 41629.6 | 0.69134 | 24888.24 | 0 | 0 | 1 | 5000 | 24888.24 | 0 | 0 | 0 | 0 | 0 | 11741.36 | 0 | 0 | 0 | 0 | 0 | 11741.36
2022011508 | 7 | 0.55448 | 44358.4 | 0.69662 | 25078.32 | 0.00145 | 17.4 | 1 | 5000 | 25078.32 | 17.4 | 0 | 0 | 0 | 0 | 14262.68 | 0 | 0 | 0 | 0 | 0 | 14262.68
2022011509 | 7 | 0.58333 | 46666.4 | 0.68634 | 24708.24 | 0.08771 | 1052.52 | 1 | 5000 | 24708.24 | 1052.52 | 0 | 0 | 0 | 0 | 15905.64 | 0 | 0 | 0 | 0 | 0 | 15905.64
2022011510 | 7 | 0.60596 | 48476.8 | 0.66207 | 23834.52 | 0.22537 | 2704.44 | 1 | 5000 | 23834.52 | 2704.44 | 0 | 0 | 0 | 0 | 16937.84 | 0 | 0 | 0 | 0 | 0 | 16937.84
2022011511 | 7 | 0.61569 | 49255.2 | 0.66117 | 23802.12 | 0.26315 | 3157.8 | 1 | 5000 | 23802.12 | 3157.8 | 0 | 0 | 0 | 0 | 17295.28 | 0 | 0 | 0 | 0 | 0 | 17295.28
2022011512 | 7 | 0.6178 | 49424 | 0.6637 | 23893.2 | 0.286 | 3432 | 1 | 5000 | 23893.2 | 3432 | 0 | 0 | 0 | 0 | 17098.8 | 0 | 0 | 0 | 0 | 0 | 17098.8
2022011513 | 7 | 0.61481 | 49184.8 | 0.66801 | 24048.36 | 0.2876 | 3451.2 | 1 | 5000 | 24048.36 | 3451.2 | 0 | 0 | 0 | 0 | 16685.24 | 0 | 0 | 0 | 0 | 0 | 16685.24
2022011514 | 7 | 0.61093 | 48874.4 | 0.66551 | 23958.36 | 0.29747 | 3569.64 | 1 | 5000 | 23958.36 | 3569.64 | 0 | 0 | 0 | 0 | 16346.4 | 0 | 0 | 0 | 0 | 0 | 16346.4
2022011515 | 7 | 0.60779 | 48623.2 | 0.66338 | 23881.68 | 0.28455 | 3414.6 | 1 | 5000 | 23881.68 | 3414.6 | 0 | 0 | 0 | 0 | 16326.92 | 0 | 0 | 0 | 0 | 0 | 16326.92
2022011516 | 7 | 0.60869 | 48695.2 | 0.65749 | 23669.64 | 0.25604 | 3072.48 | 1 | 5000 | 23669.64 | 3072.48 | 0 | 0 | 0 | 0 | 16953.08 | 0 | 0 | 0 | 0 | 0 | 16953.08
2022011517 | 7 | 0.61725 | 49380 | 0.65626 | 23625.36 | 0.22978 | 2757.36 | 1 | 5000 | 23625.36 | 2757.36 | 0 | 0 | 0 | 0 | 17997.28 | 0 | 0 | 0 | 0 | 0 | 17997.28
2022011518 | 7 | 0.63901 | 51120.8 | 0.6593 | 23734.8 | 0.07749 | 929.88 | 1 | 5000 | 23734.8 | 929.88 | 0 | 0 | 0 | 0 | 21456.12 | 0 | 0 | 0 | 0 | 0 | 21456.12
2022011519 | 7 | 0.66386 | 53108.8 | 0.59569 | 21444.84 | 0.00016 | 1.92 | 1 | 5000 | 21444.84 | 1.92 | 0 | 0 | 0 | 0 | 26662.04 | 0 | 0 | 0 | 0 | 0 | 26662.04
2022011520 | 7 | 0.66565 | 53252 | 0.52662 | 18958.32 | 0 | 0 | 1 | 5000 | 18958.32 | 0 | 0 | 0 | 0 | 0 | 29293.68 | 0 | 0 | 0 | 0 | 0 | 29293.68
2022011521 | 7 | 0.66202 | 52961.6 | 0.49602 | 17856.72 | 0 | 0 | 1 | 5000 | 17856.72 | 0 | 0 | 0 | 0 | 0 | 30104.88 | 0 | 0 | 0 | 0 | 0 | 30104.88
2022011522 | 7 | 0.65286 | 52228.8 | 0.44715 | 16097.4 | 0 | 0 | 1 | 5000 | 16097.4 | 0 | 0 | 0 | 0 | 0 | 31131.4 | 0 | 0 | 0 | 0 | 0 | 31131.4
2022011523 | 7 | 0.63666 | 50932.8 | 0.39348 | 14165.28 | 0 | 0 | 1 | 5000 | 14165.28 | 0 | 0 | 0 | 0 | 0 | 31767.52 | 0 | 0 | 0 | 0 | 0 | 31767.52
2022011524 | 7 | 0.62087 | 49669.6 | 0.34366 | 12371.76 | 0 | 0 | 1 | 5000 | 12371.76 | 0 | 0 | 0 | 0 | 0 | 32297.84 | 0 | 0 | 0 | 0 | 0 | 32297.84
2022011601 | 1 | 0.60801 | 48640.8 | 0.30827 | 11097.72 | 0 | 0 | 1 | 5000 | 11097.72 | 0 | 0 | 0 | 0 | 0 | 32543.08 | 0 | 0 | 0 | 0 | 0 | 32543.08
2022011602 | 1 | 0.60182 | 48145.6 | 0.28555 | 10279.8 | 0 | 0 | 1 | 5000 | 10279.8 | 0 | 0 | 0 | 0 | 0 | 32865.8 | 0 | 0 | 0 | 0 | 0 | 32865.8
2022011603 | 1 | 0.59991 | 47992.8 | 0.26935 | 9696.6 | 0 | 0 | 1 | 5000 | 9696.6 | 0 | 0 | 0 | 0 | 0 | 33296.2 | 0 | 0 | 0 | 0 | 0 | 33296.2
2022011604 | 1 | 0.60385 | 48308 | 0.27203 | 9793.08 | 0 | 0 | 1 | 5000 | 9793.08 | 0 | 0 | 0 | 0 | 0 | 33514.92 | 0 | 0 | 0 | 0 | 0 | 33514.92
2022011605 | 1 | 0.61163 | 48930.4 | 0.27794 | 10005.84 | 0 | 0 | 1 | 5000 | 10005.84 | 0 | 0 | 0 | 0 | 0 | 33924.56 | 0 | 0 | 0 | 0 | 0 | 33924.56
2022011606 | 1 | 0.62513 | 50010.4 | 0.28523 | 10268.28 | 0 | 0 | 1 | 5000 | 10268.28 | 0 | 0 | 0 | 0 | 0 | 34742.12 | 0 | 0 | 0 | 0 | 0 | 34742.12
2022011607 | 1 | 0.64278 | 51422.4 | 0.26926 | 9693.36 | 0 | 0 | 1 | 5000 | 9693.36 | 0 | 0 | 0 | 0 | 0 | 36729.04 | 0 | 0 | 0 | 0 | 0 | 36729.04
2022011608 | 1 | 0.66183 | 52946.4 | 0.28886 | 10398.96 | 0.00644 | 77.28 | 1 | 5000 | 10398.96 | 77.28 | 0 | 0 | 0 | 0 | 37470.16 | 0 | 0 | 0 | 0 | 0 | 37470.16
2022011609 | 1 | 0.66397 | 53117.6 | 0.28989 | 10436.04 | 0.2813 | 3375.6 | 1 | 5000 | 10436.04 | 3375.6 | 0 | 0 | 0 | 0 | 34305.96 | 0 | 0 | 0 | 0 | 0 | 34305.96
2022011610 | 1 | 0.64599 | 51679.2 | 0.22942 | 8259.12 | 0.72548 | 8705.76 | 1 | 5000 | 8259.12 | 8705.76 | 0 | 0 | 0 | 0 | 29714.32 | 0 | 0 | 0 | 0 | 0 | 29714.32
2022011611 | 1 | 0.61513 | 49210.4 | 0.15705 | 5653.8 | 0.77287 | 9274.44 | 1 | 5000 | 5653.8 | 9274.44 | 0 | 0 | 0 | 0 | 29282.16 | 0 | 0 | 0 | 0 | 0 | 29282.16
2022011612 | 1 | 0.5828 | 46624 | 0.12321 | 4435.56 | 0.74401 | 8928.12 | 1 | 5000 | 4435.56 | 8928.12 | 0 | 0 | 0 | 0 | 28260.32 | 0 | 0 | 0 | 0 | 0 | 28260.32
2022011613 | 1 | 0.5519 | 44152 | 0.12182 | 4385.52 | 0.719 | 8628 | 1 | 5000 | 4385.52 | 8628 | 0 | 0 | 0 | 0 | 26138.48 | 0 | 0 | 0 | 0 | 0 | 26138.48
2022011614 | 1 | 0.52626 | 42100.8 | 0.14343 | 5163.48 | 0.71902 | 8628.24 | 1 | 5000 | 5163.48 | 8628.24 | 0 | 0 | 0 | 0 | 23309.08 | 0 | 0 | 0 | 0 | 0 | 23309.08
2022011615 | 1 | 0.50762 | 40609.6 | 0.13834 | 4980.24 | 0.74722 | 8966.64 | 1 | 5000 | 4980.24 | 8966.64 | 0 | 0 | 0 | 0 | 21662.72 | 0 | 0 | 0 | 0 | 0 | 21662.72
2022011616 | 1 | 0.49729 | 39783.2 | 0.11237 | 4045.32 | 0.76119 | 9134.28 | 1 | 5000 | 4045.32 | 9134.28 | 0 | 0 | 0 | 0 | 21603.6 | 0 | 0 | 0 | 0 | 0 | 21603.6
2022011617 | 1 | 0.49505 | 39604 | 0.08808 | 3170.88 | 0.63101 | 7572.12 | 1 | 5000 | 3170.88 | 7572.12 | 0 | 0 | 0 | 0 | 23861 | 0 | 0 | 0 | 0 | 0 | 23861
2022011618 | 1 | 0.51363 | 41090.4 | 0.05384 | 1938.24 | 0.16338 | 1960.56 | 1 | 5000 | 1938.24 | 1960.56 | 0 | 0 | 0 | 0 | 32191.6 | 0 | 0 | 0 | 0 | 0 | 32191.6
2022011619 | 1 | 0.54504 | 43603.2 | 0.05646 | 2032.56 | 0.00024 | 2.88 | 1 | 5000 | 2032.56 | 2.88 | 0 | 0 | 0 | 0 | 36567.76 | 0 | 0 | 0 | 0 | 0 | 36567.76
2022011620 | 1 | 0.56094 | 44875.2 | 0.0768 | 2764.8 | 0 | 0 | 1 | 5000 | 2764.8 | 0 | 0 | 0 | 0 | 0 | 37110.4 | 0 | 0 | 0 | 0 | 0 | 37110.4
2022011621 | 1 | 0.56499 | 45199.2 | 0.09613 | 3460.68 | 0 | 0 | 1 | 5000 | 3460.68 | 0 | 0 | 0 | 0 | 0 | 36738.52 | 0 | 0 | 0 | 0 | 0 | 36738.52
2022011622 | 1 | 0.56436 | 45148.8 | 0.12157 | 4376.52 | 0 | 0 | 1 | 5000 | 4376.52 | 0 | 0 | 0 | 0 | 0 | 35772.28 | 0 | 0 | 0 | 0 | 0 | 35772.28
2022011623 | 1 | 0.5547 | 44376 | 0.1516 | 5457.6 | 0 | 0 | 1 | 5000 | 5457.6 | 0 | 0 | 0 | 0 | 0 | 33918.4 | 0 | 0 | 0 | 0 | 0 | 33918.4
2022011624 | 1 | 0.54487 | 43589.6 | 0.16976 | 6111.36 | 0 | 0 | 1 | 5000 | 6111.36 | 0 | 0 | 0 | 0 | 0 | 32478.24 | 0 | 0 | 0 | 0 | 0 | 32478.24
2022011701 | 2 | 0.54086 | 43268.8 | 0.15483 | 5573.88 | 0 | 0 | 1 | 5000 | 5573.88 | 0 | 0 | 0 | 0 | 0 | 32694.92 | 0 | 0 | 0 | 0 | 0 | 32694.92
2022011702 | 2 | 0.54101 | 43280.8 | 0.15955 | 5743.8 | 0 | 0 | 1 | 5000 | 5743.8 | 0 | 0 | 0 | 0 | 0 | 32537 | 0 | 0 | 0 | 0 | 0 | 32537
2022011703 | 2 | 0.54662 | 43729.6 | 0.16056 | 5780.16 | 0 | 0 | 1 | 5000 | 5780.16 | 0 | 0 | 0 | 0 | 0 | 32949.44 | 0 | 0 | 0 | 0 | 0 | 32949.44
2022011704 | 2 | 0.55836 | 44668.8 | 0.16785 | 6042.6 | 0 | 0 | 1 | 5000 | 6042.6 | 0 | 0 | 0 | 0 | 0 | 33626.2 | 0 | 0 | 0 | 0 | 0 | 33626.2
2022011705 | 2 | 0.57624 | 46099.2 | 0.16405 | 5905.8 | 0 | 0 | 1 | 5000 | 5905.8 | 0 | 0 | 0 | 0 | 0 | 35193.4 | 0 | 0 | 0 | 0 | 0 | 35193.4
2022011706 | 2 | 0.60777 | 48621.6 | 0.15527 | 5589.72 | 0 | 0 | 1 | 5000 | 5589.72 | 0 | 0 | 0 | 0 | 0 | 38031.88 | 0 | 0 | 0 | 0 | 0 | 38031.88
2022011707 | 2 | 0.64506 | 51604.8 | 0.14645 | 5272.2 | 0 | 0 | 1 | 5000 | 5272.2 | 0 | 0 | 0 | 0 | 0 | 41332.6 | 0 | 0 | 0 | 0 | 0 | 41332.6
2022011708 | 2 | 0.6713 | 53704 | 0.14444 | 5199.84 | 0.00731 | 87.72 | 1 | 5000 | 5199.84 | 87.72 | 0 | 0 | 0 | 0 | 43416.44 | 0 | 0 | 0 | 0 | 0 | 43416.44
2022011709 | 2 | 0.66246 | 52996.8 | 0.15279 | 5500.44 | 0.27272 | 3272.64 | 1 | 5000 | 5500.44 | 3272.64 | 0 | 0 | 0 | 0 | 39223.72 | 0 | 0 | 0 | 0 | 0 | 39223.72
2022011710 | 2 | 0.62885 | 50308 | 0.11573 | 4166.28 | 0.68042 | 8165.04 | 1 | 5000 | 4166.28 | 8165.04 | 0 | 0 | 0 | 0 | 32976.68 | 0 | 0 | 0 | 0 | 0 | 32976.68
2022011711 | 2 | 0.59322 | 47457.6 | 0.13433 | 4835.88 | 0.72329 | 8679.48 | 1 | 5000 | 4835.88 | 8679.48 | 0 | 0 | 0 | 0 | 28942.24 | 0 | 0 | 0 | 0 | 0 | 28942.24
2022011712 | 2 | 0.56374 | 45099.2 | 0.17346 | 6244.56 | 0.69438 | 8332.56 | 1 | 5000 | 6244.56 | 8332.56 | 0 | 0 | 0 | 0 | 25522.08 | 0 | 0 | 0 | 0 | 0 | 25522.08
2022011713 | 2 | 0.54002 | 43201.6 | 0.18829 | 6778.44 | 0.67013 | 8041.56 | 1 | 5000 | 6778.44 | 8041.56 | 0 | 0 | 0 | 0 | 23381.6 | 0 | 0 | 0 | 0 | 0 | 23381.6
2022011714 | 2 | 0.52154 | 41723.2 | 0.22976 | 8271.36 | 0.66172 | 7940.64 | 1 | 5000 | 8271.36 | 7940.64 | 0 | 0 | 0 | 0 | 20511.2 | 0 | 0 | 0 | 0 | 0 | 20511.2
2022011715 | 2 | 0.51025 | 40820 | 0.27878 | 10036.08 | 0.66342 | 7961.04 | 1 | 5000 | 10036.08 | 7961.04 | 0 | 0 | 0 | 0 | 17822.88 | 0 | 0 | 0 | 0 | 0 | 17822.88
2022011716 | 2 | 0.5053 | 40424 | 0.33107 | 11918.52 | 0.57477 | 6897.24 | 1 | 5000 | 11918.52 | 6897.24 | 0 | 0 | 0 | 0 | 16608.24 | 0 | 0 | 0 | 0 | 0 | 16608.24
2022011717 | 2 | 0.50704 | 40563.2 | 0.36758 | 13232.88 | 0.4047 | 4856.4 | 1 | 5000 | 13232.88 | 4856.4 | 0 | 0 | 0 | 0 | 17473.92 | 0 | 0 | 0 | 0 | 0 | 17473.92
2022011718 | 2 | 0.5189 | 41512 | 0.37775 | 13599 | 0.1353 | 1623.6 | 1 | 5000 | 13599 | 1623.6 | 0 | 0 | 0 | 0 | 21289.4 | 0 | 0 | 0 | 0 | 0 | 21289.4
2022011719 | 2 | 0.54779 | 43823.2 | 0.47235 | 17004.6 | 0.00123 | 14.76 | 1 | 5000 | 17004.6 | 14.76 | 0 | 0 | 0 | 0 | 21803.84 | 0 | 0 | 0 | 0 | 0 | 21803.84
2022011720 | 2 | 0.55398 | 44318.4 | 0.53992 | 19437.12 | 0 | 0 | 1 | 5000 | 19437.12 | 0 | 0 | 0 | 0 | 0 | 19881.28 | 0 | 0 | 0 | 0 | 0 | 19881.28
2022011721 | 2 | 0.55066 | 44052.8 | 0.55733 | 20063.88 | 0 | 0 | 1 | 5000 | 20063.88 | 0 | 0 | 0 | 0 | 0 | 18988.92 | 0 | 0 | 0 | 0 | 0 | 18988.92
2022011722 | 2 | 0.53986 | 43188.8 | 0.57432 | 20675.52 | 0 | 0 | 1 | 5000 | 20675.52 | 0 | 0 | 0 | 0 | 0 | 17513.28 | 0 | 0 | 0 | 0 | 0 | 17513.28
2022011723 | 2 | 0.51971 | 41576.8 | 0.57849 | 20825.64 | 0 | 0 | 1 | 5000 | 20825.64 | 0 | 0 | 0 | 0 | 0 | 15751.16 | 0 | 0 | 0 | 0 | 0 | 15751.16
2022011724 | 2 | 0.49876 | 39900.8 | 0.58271 | 20977.56 | 0 | 0 | 1 | 5000 | 20977.56 | 0 | 0 | 0 | 0 | 0 | 13923.24 | 0 | 0 | 0 | 0 | 0 | 13923.24
2022011801 | 3 | 0.48684 | 38947.2 | 0.58259 | 20973.24 | 0 | 0 | 1 | 5000 | 20973.24 | 0 | 0 | 0 | 0 | 0 | 12973.96 | 0 | 0 | 0 | 0 | 0 | 12973.96
2022011802 | 3 | 0.48165 | 38532 | 0.581 | 20916 | 0 | 0 | 1 | 5000 | 20916 | 0 | 0 | 0 | 0 | 0 | 12616 | 0 | 0 | 0 | 0 | 0 | 12616
2022011803 | 3 | 0.48248 | 38598.4 | 0.58294 | 20985.84 | 0 | 0 | 1 | 5000 | 20985.84 | 0 | 0 | 0 | 0 | 0 | 12612.56 | 0 | 0 | 0 | 0 | 0 | 12612.56
2022011804 | 3 | 0.4887 | 39096 | 0.58228 | 20962.08 | 0 | 0 | 1 | 5000 | 20962.08 | 0 | 0 | 0 | 0 | 0 | 13133.92 | 0 | 0 | 0 | 0 | 0 | 13133.92
2022011805 | 3 | 0.5028 | 40224 | 0.58669 | 21120.84 | 0 | 0 | 1 | 5000 | 21120.84 | 0 | 0 | 0 | 0 | 0 | 14103.16 | 0 | 0 | 0 | 0 | 0 | 14103.16
2022011806 | 3 | 0.5345 | 42760 | 0.60275 | 21699 | 0 | 0 | 1 | 5000 | 21699 | 0 | 0 | 0 | 0 | 0 | 16061 | 0 | 0 | 0 | 0 | 0 | 16061
2022011807 | 3 | 0.58194 | 46555.2 | 0.6403 | 23050.8 | 0 | 0 | 1 | 5000 | 23050.8 | 0 | 0 | 0 | 0 | 0 | 18504.4 | 0 | 0 | 0 | 0 | 0 | 18504.4
2022011808 | 3 | 0.60087 | 48069.6 | 0.64226 | 23121.36 | 0.00397 | 47.64 | 1 | 5000 | 23121.36 | 47.64 | 0 | 0 | 0 | 0 | 19900.6 | 0 | 0 | 0 | 0 | 0 | 19900.6
2022011809 | 3 | 0.58729 | 46983.2 | 0.5906 | 21261.6 | 0.20348 | 2441.76 | 1 | 5000 | 21261.6 | 2441.76 | 0 | 0 | 0 | 0 | 18279.84 | 0 | 0 | 0 | 0 | 0 | 18279.84
2022011810 | 3 | 0.56531 | 45224.8 | 0.48489 | 17456.04 | 0.48452 | 5814.24 | 1 | 5000 | 17456.04 | 5814.24 | 0 | 0 | 0 | 0 | 16954.52 | 0 | 0 | 0 | 0 | 0 | 16954.52
2022011811 | 3 | 0.54478 | 43582.4 | 0.50517 | 18186.12 | 0.58099 | 6971.88 | 1 | 5000 | 18186.12 | 6971.88 | 0 | 0 | 0 | 0 | 13424.4 | 0 | 0 | 0 | 0 | 0 | 13424.4
2022011812 | 3 | 0.52944 | 42355.2 | 0.54199 | 19511.64 | 0.52613 | 6313.56 | 1 | 5000 | 19511.64 | 6313.56 | 0 | 0 | 0 | 0 | 11530 | 0 | 0 | 0 | 0 | 0 | 11530
2022011813 | 3 | 0.51711 | 41368.8 | 0.57573 | 20726.28 | 0.3764 | 4516.8 | 1 | 5000 | 20726.28 | 4516.8 | 0 | 0 | 0 | 0 | 11125.72 | 0 | 0 | 0 | 0 | 0 | 11125.72
2022011814 | 3 | 0.51117 | 40893.6 | 0.57271 | 20617.56 | 0.35366 | 4243.92 | 1 | 5000 | 20617.56 | 4243.92 | 0 | 0 | 0 | 0 | 11032.12 | 0 | 0 | 0 | 0 | 0 | 11032.12
2022011815 | 3 | 0.50862 | 40689.6 | 0.57083 | 20549.88 | 0.34997 | 4199.64 | 1 | 5000 | 20549.88 | 4199.64 | 0 | 0 | 0 | 0 | 10940.08 | 0 | 0 | 0 | 0 | 0 | 10940.08
2022011816 | 3 | 0.50891 | 40712.8 | 0.56602 | 20376.72 | 0.36161 | 4339.32 | 1 | 5000 | 20376.72 | 4339.32 | 0 | 0 | 0 | 0 | 10996.76 | 0 | 0 | 0 | 0 | 0 | 10996.76
2022011817 | 3 | 0.51173 | 40938.4 | 0.55404 | 19945.44 | 0.32793 | 3935.16 | 1 | 5000 | 19945.44 | 3935.16 | 0 | 0 | 0 | 0 | 12057.8 | 0 | 0 | 0 | 0 | 0 | 12057.8
2022011818 | 3 | 0.51759 | 41407.2 | 0.50049 | 18017.64 | 0.09998 | 1199.76 | 1 | 5000 | 18017.64 | 1199.76 | 0 | 0 | 0 | 0 | 17189.8 | 0 | 0 | 0 | 0 | 0 | 17189.8
2022011819 | 3 | 0.53535 | 42828 | 0.43664 | 15719.04 | 0.00059 | 7.08 | 1 | 5000 | 15719.04 | 7.08 | 0 | 0 | 0 | 0 | 22101.88 | 0 | 0 | 0 | 0 | 0 | 22101.88
2022011820 | 3 | 0.53178 | 42542.4 | 0.46342 | 16683.12 | 0 | 0 | 1 | 5000 | 16683.12 | 0 | 0 | 0 | 0 | 0 | 20859.28 | 0 | 0 | 0 | 0 | 0 | 20859.28
2022011821 | 3 | 0.52148 | 41718.4 | 0.51393 | 18501.48 | 0 | 0 | 1 | 5000 | 18501.48 | 0 | 0 | 0 | 0 | 0 | 18216.92 | 0 | 0 | 0 | 0 | 0 | 18216.92
2022011822 | 3 | 0.5031 | 40248 | 0.5456 | 19641.6 | 0 | 0 | 1 | 5000 | 19641.6 | 0 | 0 | 0 | 0 | 0 | 15606.4 | 0 | 0 | 0 | 0 | 0 | 15606.4
2022011823 | 3 | 0.47725 | 38180 | 0.52811 | 19011.96 | 0 | 0 | 1 | 5000 | 19011.96 | 0 | 0 | 0 | 0 | 0 | 14168.04 | 0 | 0 | 0 | 0 | 0 | 14168.04
2022011824 | 3 | 0.45037 | 36029.6 | 0.52929 | 19054.44 | 0 | 0 | 1 | 5000 | 19054.44 | 0 | 0 | 0 | 0 | 0 | 11975.16 | 0 | 0 | 0 | 0 | 0 | 11975.16
2022011901 | 4 | 0.43155 | 34524 | 0.49645 | 17872.2 | 0 | 0 | 1 | 5000 | 17872.2 | 0 | 0 | 0 | 0 | 0 | 11651.8 | 0 | 0 | 0 | 0 | 0 | 11651.8
2022011902 | 4 | 0.41947 | 33557.6 | 0.47911 | 17247.96 | 0 | 0 | 1 | 5000 | 17247.96 | 0 | 0 | 0 | 0 | 0 | 11309.64 | 0 | 0 | 0 | 0 | 0 | 11309.64
2022011903 | 4 | 0.4152 | 33216 | 0.46147 | 16612.92 | 0 | 0 | 1 | 5000 | 16612.92 | 0 | 0 | 0 | 0 | 0 | 11603.08 | 0 | 0 | 0 | 0 | 0 | 11603.08
2022011904 | 4 | 0.41719 | 33375.2 | 0.49055 | 17659.8 | 0 | 0 | 1 | 5000 | 17659.8 | 0 | 0 | 0 | 0 | 0 | 10715.4 | 0 | 0 | 0 | 0 | 0 | 10715.4
2022011905 | 4 | 0.42441 | 33952.8 | 0.48976 | 17631.36 | 0 | 0 | 1 | 5000 | 17631.36 | 0 | 0 | 0 | 0 | 0 | 11321.44 | 0 | 0 | 0 | 0 | 0 | 11321.44
2022011906 | 4 | 0.44773 | 35818.4 | 0.47412 | 17068.32 | 0 | 0 | 1 | 5000 | 17068.32 | 0 | 0 | 0 | 0 | 0 | 13750.08 | 0 | 0 | 0 | 0 | 0 | 13750.08
2022011907 | 4 | 0.48755 | 39004 | 0.49804 | 17929.44 | 0 | 0 | 1 | 5000 | 17929.44 | 0 | 0 | 0 | 0 | 0 | 16074.56 | 0 | 0 | 0 | 0 | 0 | 16074.56
2022011908 | 4 | 0.50798 | 40638.4 | 0.53184 | 19146.24 | 0.00289 | 34.68 | 1 | 5000 | 19146.24 | 34.68 | 0 | 0 | 0 | 0 | 16457.48 | 0 | 0 | 0 | 0 | 0 | 16457.48
2022011909 | 4 | 0.51177 | 40941.6 | 0.51355 | 18487.8 | 0.1946 | 2335.2 | 1 | 5000 | 18487.8 | 2335.2 | 0 | 0 | 0 | 0 | 15118.6 | 0 | 0 | 0 | 0 | 0 | 15118.6
2022011910 | 4 | 0.51865 | 41492 | 0.46897 | 16882.92 | 0.56233 | 6747.96 | 1 | 5000 | 16882.92 | 6747.96 | 0 | 0 | 0 | 0 | 12861.12 | 0 | 0 | 0 | 0 | 0 | 12861.12
2022011911 | 4 | 0.52397 | 41917.6 | 0.51289 | 18464.04 | 0.45916 | 5509.92 | 1 | 5000 | 18464.04 | 5509.92 | 0 | 0 | 0 | 0 | 12943.64 | 0 | 0 | 0 | 0 | 0 | 12943.64
2022011912 | 4 | 0.52538 | 42030.4 | 0.54383 | 19577.88 | 0.34034 | 4084.08 | 1 | 5000 | 19577.88 | 4084.08 | 0 | 0 | 0 | 0 | 13368.44 | 0 | 0 | 0 | 0 | 0 | 13368.44
2022011913 | 4 | 0.52843 | 42274.4 | 0.52318 | 18834.48 | 0.31487 | 3778.44 | 1 | 5000 | 18834.48 | 3778.44 | 0 | 0 | 0 | 0 | 14661.48 | 0 | 0 | 0 | 0 | 0 | 14661.48
2022011914 | 4 | 0.53371 | 42696.8 | 0.53549 | 19277.64 | 0.29605 | 3552.6 | 1 | 5000 | 19277.64 | 3552.6 | 0 | 0 | 0 | 0 | 14866.56 | 0 | 0 | 0 | 0 | 0 | 14866.56
2022011915 | 4 | 0.53707 | 42965.6 | 0.54347 | 19564.92 | 0.27231 | 3267.72 | 1 | 5000 | 19564.92 | 3267.72 | 0 | 0 | 0 | 0 | 15132.96 | 0 | 0 | 0 | 0 | 0 | 15132.96
2022011916 | 4 | 0.53987 | 43189.6 | 0.58186 | 20946.96 | 0.18862 | 2263.44 | 1 | 5000 | 20946.96 | 2263.44 | 0 | 0 | 0 | 0 | 14979.2 | 0 | 0 | 0 | 0 | 0 | 14979.2
2022011917 | 4 | 0.54565 | 43652 | 0.60894 | 21921.84 | 0.0961 | 1153.2 | 1 | 5000 | 21921.84 | 1153.2 | 0 | 0 | 0 | 0 | 15576.96 | 0 | 0 | 0 | 0 | 0 | 15576.96
2022011918 | 4 | 0.56254 | 45003.2 | 0.61587 | 22171.32 | 0.04195 | 503.4 | 1 | 5000 | 22171.32 | 503.4 | 0 | 0 | 0 | 0 | 17328.48 | 0 | 0 | 0 | 0 | 0 | 17328.48
2022011919 | 4 | 0.58351 | 46680.8 | 0.64454 | 23203.44 | 0.00025 | 3 | 1 | 5000 | 23203.44 | 3 | 0 | 0 | 0 | 0 | 18474.36 | 0 | 0 | 0 | 0 | 0 | 18474.36
2022011920 | 4 | 0.58669 | 46935.2 | 0.64773 | 23318.28 | 0 | 0 | 1 | 5000 | 23318.28 | 0 | 0 | 0 | 0 | 0 | 18616.92 | 0 | 0 | 0 | 0 | 0 | 18616.92
2022011921 | 4 | 0.584 | 46720 | 0.62892 | 22641.12 | 0 | 0 | 1 | 5000 | 22641.12 | 0 | 0 | 0 | 0 | 0 | 19078.88 | 0 | 0 | 0 | 0 | 0 | 19078.88
2022011922 | 4 | 0.57477 | 45981.6 | 0.6044 | 21758.4 | 0 | 0 | 1 | 5000 | 21758.4 | 0 | 0 | 0 | 0 | 0 | 19223.2 | 0 | 0 | 0 | 0 | 0 | 19223.2
2022011923 | 4 | 0.55323 | 44258.4 | 0.58661 | 21117.96 | 0 | 0 | 1 | 5000 | 21117.96 | 0 | 0 | 0 | 0 | 0 | 18140.44 | 0 | 0 | 0 | 0 | 0 | 18140.44
2022011924 | 4 | 0.53553 | 42842.4 | 0.58893 | 21201.48 | 0 | 0 | 1 | 5000 | 21201.48 | 0 | 0 | 0 | 0 | 0 | 16640.92 | 0 | 0 | 0 | 0 | 0 | 16640.92
2022012001 | 5 | 0.52786 | 42228.8 | 0.6052 | 21787.2 | 0 | 0 | 1 | 5000 | 21787.2 | 0 | 0 | 0 | 0 | 0 | 15441.6 | 0 | 0 | 0 | 0 | 0 | 15441.6
2022012002 | 5 | 0.52793 | 42234.4 | 0.6044 | 21758.4 | 0 | 0 | 1 | 5000 | 21758.4 | 0 | 0 | 0 | 0 | 0 | 15476 | 0 | 0 | 0 | 0 | 0 | 15476
2022012003 | 5 | 0.53472 | 42777.6 | 0.61468 | 22128.48 | 0 | 0 | 1 | 5000 | 22128.48 | 0 | 0 | 0 | 0 | 0 | 15649.12 | 0 | 0 | 0 | 0 | 0 | 15649.12
2022012004 | 5 | 0.55034 | 44027.2 | 0.62988 | 22675.68 | 0 | 0 | 1 | 5000 | 22675.68 | 0 | 0 | 0 | 0 | 0 | 16351.52 | 0 | 0 | 0 | 0 | 0 | 16351.52
2022012005 | 5 | 0.57247 | 45797.6 | 0.64419 | 23190.84 | 0 | 0 | 1 | 5000 | 23190.84 | 0 | 0 | 0 | 0 | 0 | 17606.76 | 0 | 0 | 0 | 0 | 0 | 17606.76
2022012006 | 5 | 0.61214 | 48971.2 | 0.64809 | 23331.24 | 0 | 0 | 1 | 5000 | 23331.24 | 0 | 0 | 0 | 0 | 0 | 20639.96 | 0 | 0 | 0 | 0 | 0 | 20639.96
2022012007 | 5 | 0.66987 | 53589.6 | 0.63835 | 22980.6 | 0 | 0 | 1 | 5000 | 22980.6 | 0 | 0 | 0 | 0 | 0 | 25609 | 0 | 0 | 0 | 0 | 0 | 25609
2022012008 | 5 | 0.70905 | 56724 | 0.63118 | 22722.48 | 0.00078 | 9.36 | 1 | 5000 | 22722.48 | 9.36 | 0 | 0 | 0 | 0 | 28992.16 | 0 | 0 | 0 | 0 | 0 | 28992.16
2022012009 | 5 | 0.72637 | 58109.6 | 0.6092 | 21931.2 | 0.03403 | 408.36 | 1 | 5000 | 21931.2 | 408.36 | 0 | 0 | 0 | 0 | 30770.04 | 0 | 0 | 0 | 0 | 0 | 30770.04
2022012010 | 5 | 0.74046 | 59236.8 | 0.57289 | 20624.04 | 0.11448 | 1373.76 | 1 | 5000 | 20624.04 | 1373.76 | 0 | 0 | 0 | 0 | 32239 | 0 | 0 | 0 | 0 | 0 | 32239
2022012011 | 5 | 0.74597 | 59677.6 | 0.54664 | 19679.04 | 0.1804 | 2164.8 | 1 | 5000 | 19679.04 | 2164.8 | 0 | 0 | 0 | 0 | 32833.76 | 0 | 0 | 0 | 0 | 0 | 32833.76
2022012012 | 5 | 0.74371 | 59496.8 | 0.52692 | 18969.12 | 0.25905 | 3108.6 | 1 | 5000 | 18969.12 | 3108.6 | 0 | 0 | 0 | 0 | 32419.08 | 0 | 0 | 0 | 0 | 0 | 32419.08
2022012013 | 5 | 0.73312 | 58649.6 | 0.50478 | 18172.08 | 0.29979 | 3597.48 | 1 | 5000 | 18172.08 | 3597.48 | 0 | 0 | 0 | 0 | 31880.04 | 0 | 0 | 0 | 0 | 0 | 31880.04
2022012014 | 5 | 0.72292 | 57833.6 | 0.47083 | 16949.88 | 0.33787 | 4054.44 | 1 | 5000 | 16949.88 | 4054.44 | 0 | 0 | 0 | 0 | 31829.28 | 0 | 0 | 0 | 0 | 0 | 31829.28
2022012015 | 5 | 0.7122 | 56976 | 0.43848 | 15785.28 | 0.34922 | 4190.64 | 1 | 5000 | 15785.28 | 4190.64 | 0 | 0 | 0 | 0 | 32000.08 | 0 | 0 | 0 | 0 | 0 | 32000.08
2022012016 | 5 | 0.71289 | 57031.2 | 0.42528 | 15310.08 | 0.27388 | 3286.56 | 1 | 5000 | 15310.08 | 3286.56 | 0 | 0 | 0 | 0 | 33434.56 | 0 | 0 | 0 | 0 | 0 | 33434.56
2022012017 | 5 | 0.7279 | 58232 | 0.39201 | 14112.36 | 0.17055 | 2046.6 | 1 | 5000 | 14112.36 | 2046.6 | 0 | 0 | 0 | 0 | 37073.04 | 0 | 0 | 0 | 0 | 0 | 37073.04
2022012018 | 5 | 0.75263 | 60210.4 | 0.33387 | 12019.32 | 0.05029 | 603.48 | 1 | 5000 | 12019.32 | 603.48 | 0 | 0 | 0 | 0 | 42587.6 | 0 | 0 | 0 | 0 | 0 | 42587.6
2022012019 | 5 | 0.77695 | 62156 | 0.2811 | 10119.6 | 0.00049 | 5.88 | 1 | 5000 | 10119.6 | 5.88 | 0 | 0 | 0 | 0 | 47030.52 | 0 | 0 | 0 | 0 | 0 | 47030.52
2022012020 | 5 | 0.77522 | 62017.6 | 0.26939 | 9698.04 | 0 | 0 | 1 | 5000 | 9698.04 | 0 | 0 | 0 | 0 | 0 | 47319.56 | 0 | 0 | 0 | 0 | 0 | 47319.56
2022012021 | 5 | 0.76644 | 61315.2 | 0.24251 | 8730.36 | 0 | 0 | 1 | 5000 | 8730.36 | 0 | 0 | 0 | 0 | 0 | 47584.84 | 0 | 0 | 0 | 0 | 0 | 47584.84
2022012022 | 5 | 0.74711 | 59768.8 | 0.21329 | 7678.44 | 0 | 0 | 1 | 5000 | 7678.44 | 0 | 0 | 0 | 0 | 0 | 47090.36 | 0 | 0 | 0 | 0 | 0 | 47090.36
2022012023 | 5 | 0.71737 | 57389.6 | 0.19792 | 7125.12 | 0 | 0 | 1 | 5000 | 7125.12 | 0 | 0 | 0 | 0 | 0 | 45264.48 | 0 | 0 | 0 | 0 | 0 | 45264.48
2022012024 | 5 | 0.69313 | 55450.4 | 0.19836 | 7140.96 | 0 | 0 | 1 | 5000 | 7140.96 | 0 | 0 | 0 | 0 | 0 | 43309.44 | 0 | 0 | 0 | 0 | 0 | 43309.44
2022012101 | 6 | 0.67865 | 54292 | 0.20034 | 7212.24 | 0 | 0 | 1 | 5000 | 7212.24 | 0 | 0 | 0 | 0 | 0 | 42079.76 | 0 | 0 | 0 | 0 | 0 | 42079.76
2022012102 | 6 | 0.67184 | 53747.2 | 0.20902 | 7524.72 | 0 | 0 | 1 | 5000 | 7524.72 | 0 | 0 | 0 | 0 | 0 | 41222.48 | 0 | 0 | 0 | 0 | 0 | 41222.48
2022012103 | 6 | 0.67074 | 53659.2 | 0.19977 | 7191.72 | 0 | 0 | 1 | 5000 | 7191.72 | 0 | 0 | 0 | 0 | 0 | 41467.48 | 0 | 0 | 0 | 0 | 0 | 41467.48
2022012104 | 6 | 0.67867 | 54293.6 | 0.17616 | 6341.76 | 0 | 0 | 1 | 5000 | 6341.76 | 0 | 0 | 0 | 0 | 0 | 42951.84 | 0 | 0 | 0 | 0 | 0 | 42951.84
2022012105 | 6 | 0.69337 | 55469.6 | 0.16332 | 5879.52 | 0 | 0 | 1 | 5000 | 5879.52 | 0 | 0 | 0 | 0 | 0 | 44590.08 | 0 | 0 | 0 | 0 | 0 | 44590.08
2022012106 | 6 | 0.72506 | 58004.8 | 0.16275 | 5859 | 0 | 0 | 1 | 5000 | 5859 | 0 | 0 | 0 | 0 | 0 | 47145.8 | 0 | 0 | 0 | 0 | 0 | 47145.8
2022012107 | 6 | 0.77053 | 61642.4 | 0.16199 | 5831.64 | 0 | 0 | 1 | 5000 | 5831.64 | 0 | 0 | 0 | 0 | 0 | 50810.76 | 0 | 0 | 0 | 0 | 0 | 50810.76
2022012108 | 6 | 0.79549 | 63639.2 | 0.16647 | 5992.92 | 0.00345 | 41.4 | 1 | 5000 | 5992.92 | 41.4 | 0 | 0 | 0 | 0 | 52604.88 | 0 | 0 | 0 | 0 | 0 | 52604.88
2022012109 | 6 | 0.78776 | 63020.8 | 0.16977 | 6111.72 | 0.2218 | 2661.6 | 1 | 5000 | 6111.72 | 2661.6 | 0 | 0 | 0 | 0 | 49247.48 | 0 | 0 | 0 | 0 | 0 | 49247.48
2022012110 | 6 | 0.76802 | 61441.6 | 0.13229 | 4762.44 | 0.61192 | 7343.04 | 1 | 5000 | 4762.44 | 7343.04 | 0 | 0 | 0 | 0 | 44336.12 | 0 | 0 | 0 | 0 | 0 | 44336.12
2022012111 | 6 | 0.74251 | 59400.8 | 0.13495 | 4858.2 | 0.67915 | 8149.8 | 1 | 5000 | 4858.2 | 8149.8 | 0 | 0 | 0 | 0 | 41392.8 | 0 | 0 | 0 | 0 | 0 | 41392.8
2022012112 | 6 | 0.7078 | 56624 | 0.14693 | 5289.48 | 0.68082 | 8169.84 | 1 | 5000 | 5289.48 | 8169.84 | 0 | 0 | 0 | 0 | 38164.68 | 0 | 0 | 0 | 0 | 0 | 38164.68
2022012113 | 6 | 0.67036 | 53628.8 | 0.17372 | 6253.92 | 0.6858 | 8229.6 | 1 | 5000 | 6253.92 | 8229.6 | 0 | 0 | 0 | 0 | 34145.28 | 0 | 0 | 0 | 0 | 0 | 34145.28
2022012114 | 6 | 0.63964 | 51171.2 | 0.17671 | 6361.56 | 0.69455 | 8334.6 | 1 | 5000 | 6361.56 | 8334.6 | 0 | 0 | 0 | 0 | 31475.04 | 0 | 0 | 0 | 0 | 0 | 31475.04
2022012115 | 6 | 0.61137 | 48909.6 | 0.19448 | 7001.28 | 0.7099 | 8518.8 | 1 | 5000 | 7001.28 | 8518.8 | 0 | 0 | 0 | 0 | 28389.52 | 0 | 0 | 0 | 0 | 0 | 28389.52
2022012116 | 6 | 0.59624 | 47699.2 | 0.20807 | 7490.52 | 0.74246 | 8909.52 | 1 | 5000 | 7490.52 | 8909.52 | 0 | 0 | 0 | 0 | 26299.16 | 0 | 0 | 0 | 0 | 0 | 26299.16
2022012117 | 6 | 0.59546 | 47636.8 | 0.21087 | 7591.32 | 0.62751 | 7530.12 | 1 | 5000 | 7591.32 | 7530.12 | 0 | 0 | 0 | 0 | 27515.36 | 0 | 0 | 0 | 0 | 0 | 27515.36
2022012118 | 6 | 0.61543 | 49234.4 | 0.20779 | 7480.44 | 0.19106 | 2292.72 | 1 | 5000 | 7480.44 | 2292.72 | 0 | 0 | 0 | 0 | 34461.24 | 0 | 0 | 0 | 0 | 0 | 34461.24
2022012119 | 6 | 0.65445 | 52356 | 0.25192 | 9069.12 | 0.00187 | 22.44 | 1 | 5000 | 9069.12 | 22.44 | 0 | 0 | 0 | 0 | 38264.44 | 0 | 0 | 0 | 0 | 0 | 38264.44
2022012120 | 6 | 0.66781 | 53424.8 | 0.34073 | 12266.28 | 0 | 0 | 1 | 5000 | 12266.28 | 0 | 0 | 0 | 0 | 0 | 36158.52 | 0 | 0 | 0 | 0 | 0 | 36158.52
2022012121 | 6 | 0.67447 | 53957.6 | 0.40536 | 14592.96 | 0 | 0 | 1 | 5000 | 14592.96 | 0 | 0 | 0 | 0 | 0 | 34364.64 | 0 | 0 | 0 | 0 | 0 | 34364.64
2022012122 | 6 | 0.67336 | 53868.8 | 0.44387 | 15979.32 | 0 | 0 | 1 | 5000 | 15979.32 | 0 | 0 | 0 | 0 | 0 | 32889.48 | 0 | 0 | 0 | 0 | 0 | 32889.48
2022012123 | 6 | 0.66206 | 52964.8 | 0.43229 | 15562.44 | 0 | 0 | 1 | 5000 | 15562.44 | 0 | 0 | 0 | 0 | 0 | 32402.36 | 0 | 0 | 0 | 0 | 0 | 32402.36
2022012124 | 6 | 0.64688 | 51750.4 | 0.41327 | 14877.72 | 0 | 0 | 1 | 5000 | 14877.72 | 0 | 0 | 0 | 0 | 0 | 31872.68 | 0 | 0 | 0 | 0 | 0 | 31872.68
2022012201 | 7 | 0.63693 | 50954.4 | 0.3754 | 13514.4 | 0 | 0 | 1 | 5000 | 13514.4 | 0 | 0 | 0 | 0 | 0 | 32440 | 0 | 0 | 0 | 0 | 0 | 32440
2022012202 | 7 | 0.6348 | 50784 | 0.32936 | 11856.96 | 0 | 0 | 1 | 5000 | 11856.96 | 0 | 0 | 0 | 0 | 0 | 33927.04 | 0 | 0 | 0 | 0 | 0 | 33927.04
2022012203 | 7 | 0.6371 | 50968 | 0.27891 | 10040.76 | 0 | 0 | 1 | 5000 | 10040.76 | 0 | 0 | 0 | 0 | 0 | 35927.24 | 0 | 0 | 0 | 0 | 0 | 35927.24
2022012204 | 7 | 0.64572 | 51657.6 | 0.23631 | 8507.16 | 0 | 0 | 1 | 5000 | 8507.16 | 0 | 0 | 0 | 0 | 0 | 38150.44 | 0 | 0 | 0 | 0 | 0 | 38150.44
2022012205 | 7 | 0.65817 | 52653.6 | 0.20841 | 7502.76 | 0 | 0 | 1 | 5000 | 7502.76 | 0 | 0 | 0 | 0 | 0 | 40150.84 | 0 | 0 | 0 | 0 | 0 | 40150.84
2022012206 | 7 | 0.6786 | 54288 | 0.1839 | 6620.4 | 0 | 0 | 1 | 5000 | 6620.4 | 0 | 0 | 0 | 0 | 0 | 42667.6 | 0 | 0 | 0 | 0 | 0 | 42667.6
2022012207 | 7 | 0.70499 | 56399.2 | 0.18632 | 6707.52 | 0 | 0 | 1 | 5000 | 6707.52 | 0 | 0 | 0 | 0 | 0 | 44691.68 | 0 | 0 | 0 | 0 | 0 | 44691.68
2022012208 | 7 | 0.72647 | 58117.6 | 0.1802 | 6487.2 | 0.00691 | 82.92 | 1 | 5000 | 6487.2 | 82.92 | 0 | 0 | 0 | 0 | 46547.48 | 0 | 0 | 0 | 0 | 0 | 46547.48
2022012209 | 7 | 0.72418 | 57934.4 | 0.13532 | 4871.52 | 0.2321 | 2785.2 | 1 | 5000 | 4871.52 | 2785.2 | 0 | 0 | 0 | 0 | 45277.68 | 0 | 0 | 0 | 0 | 0 | 45277.68
2022012210 | 7 | 0.6992 | 55936 | 0.08976 | 3231.36 | 0.49476 | 5937.12 | 1 | 5000 | 3231.36 | 5937.12 | 0 | 0 | 0 | 0 | 41767.52 | 0 | 0 | 0 | 0 | 0 | 41767.52
2022012211 | 7 | 0.66893 | 53514.4 | 0.06581 | 2369.16 | 0.45158 | 5418.96 | 1 | 5000 | 2369.16 | 5418.96 | 0 | 0 | 0 | 0 | 40726.28 | 0 | 0 | 0 | 0 | 0 | 40726.28
2022012212 | 7 | 0.63904 | 51123.2 | 0.05506 | 1982.16 | 0.42541 | 5104.92 | 1 | 5000 | 1982.16 | 5104.92 | 0 | 0 | 0 | 0 | 39036.12 | 0 | 0 | 0 | 0 | 0 | 39036.12
2022012213 | 7 | 0.60626 | 48500.8 | 0.05536 | 1992.96 | 0.42846 | 5141.52 | 1 | 5000 | 1992.96 | 5141.52 | 0 | 0 | 0 | 0 | 36366.32 | 0 | 0 | 0 | 0 | 0 | 36366.32
2022012214 | 7 | 0.57618 | 46094.4 | 0.0498 | 1792.8 | 0.41087 | 4930.44 | 1 | 5000 | 1792.8 | 4930.44 | 0 | 0 | 0 | 0 | 34371.16 | 0 | 0 | 0 | 0 | 0 | 34371.16
2022012215 | 7 | 0.55407 | 44325.6 | 0.04792 | 1725.12 | 0.4053 | 4863.6 | 1 | 5000 | 1725.12 | 4863.6 | 0 | 0 | 0 | 0 | 32736.88 | 0 | 0 | 0 | 0 | 0 | 32736.88
2022012216 | 7 | 0.54363 | 43490.4 | 0.05459 | 1965.24 | 0.34249 | 4109.88 | 1 | 5000 | 1965.24 | 4109.88 | 0 | 0 | 0 | 0 | 32415.28 | 0 | 0 | 0 | 0 | 0 | 32415.28
2022012217 | 7 | 0.5447 | 43576 | 0.064 | 2304 | 0.24648 | 2957.76 | 1 | 5000 | 2304 | 2957.76 | 0 | 0 | 0 | 0 | 33314.24 | 0 | 0 | 0 | 0 | 0 | 33314.24
2022012218 | 7 | 0.56372 | 45097.6 | 0.06817 | 2454.12 | 0.06379 | 765.48 | 1 | 5000 | 2454.12 | 765.48 | 0 | 0 | 0 | 0 | 36878 | 0 | 0 | 0 | 0 | 0 | 36878
2022012219 | 7 | 0.59815 | 47852 | 0.06982 | 2513.52 | 0.00059 | 7.08 | 1 | 5000 | 2513.52 | 7.08 | 0 | 0 | 0 | 0 | 40331.4 | 0 | 0 | 0 | 0 | 0 | 40331.4
2022012220 | 7 | 0.60868 | 48694.4 | 0.08009 | 2883.24 | 0 | 0 | 1 | 5000 | 2883.24 | 0 | 0 | 0 | 0 | 0 | 40811.16 | 0 | 0 | 0 | 0 | 0 | 40811.16
2022012221 | 7 | 0.61139 | 48911.2 | 0.09634 | 3468.24 | 0 | 0 | 1 | 5000 | 3468.24 | 0 | 0 | 0 | 0 | 0 | 40442.96 | 0 | 0 | 0 | 0 | 0 | 40442.96
2022012222 | 7 | 0.60779 | 48623.2 | 0.12314 | 4433.04 | 0 | 0 | 1 | 5000 | 4433.04 | 0 | 0 | 0 | 0 | 0 | 39190.16 | 0 | 0 | 0 | 0 | 0 | 39190.16
2022012223 | 7 | 0.59752 | 47801.6 | 0.1702 | 6127.2 | 0 | 0 | 1 | 5000 | 6127.2 | 0 | 0 | 0 | 0 | 0 | 36674.4 | 0 | 0 | 0 | 0 | 0 | 36674.4
2022012224 | 7 | 0.58465 | 46772 | 0.19926 | 7173.36 | 0 | 0 | 1 | 5000 | 7173.36 | 0 | 0 | 0 | 0 | 0 | 34598.64 | 0 | 0 | 0 | 0 | 0 | 34598.64
2022012301 | 1 | 0.57474 | 45979.2 | 0.20277 | 7299.72 | 0 | 0 | 1 | 5000 | 7299.72 | 0 | 0 | 0 | 0 | 0 | 33679.48 | 0 | 0 | 0 | 0 | 0 | 33679.48
2022012302 | 1 | 0.56784 | 45427.2 | 0.19948 | 7181.28 | 0 | 0 | 1 | 5000 | 7181.28 | 0 | 0 | 0 | 0 | 0 | 33245.92 | 0 | 0 | 0 | 0 | 0 | 33245.92
2022012303 | 1 | 0.56521 | 45216.8 | 0.20655 | 7435.8 | 0 | 0 | 1 | 5000 | 7435.8 | 0 | 0 | 0 | 0 | 0 | 32781 | 0 | 0 | 0 | 0 | 0 | 32781
2022012304 | 1 | 0.56625 | 45300 | 0.21686 | 7806.96 | 0 | 0 | 1 | 5000 | 7806.96 | 0 | 0 | 0 | 0 | 0 | 32493.04 | 0 | 0 | 0 | 0 | 0 | 32493.04
2022012305 | 1 | 0.56979 | 45583.2 | 0.2197 | 7909.2 | 0 | 0 | 1 | 5000 | 7909.2 | 0 | 0 | 0 | 0 | 0 | 32674 | 0 | 0 | 0 | 0 | 0 | 32674
2022012306 | 1 | 0.57978 | 46382.4 | 0.21246 | 7648.56 | 0 | 0 | 1 | 5000 | 7648.56 | 0 | 0 | 0 | 0 | 0 | 33733.84 | 0 | 0 | 0 | 0 | 0 | 33733.84
2022012307 | 1 | 0.59432 | 47545.6 | 0.20199 | 7271.64 | 0 | 0 | 1 | 5000 | 7271.64 | 0 | 0 | 0 | 0 | 0 | 35273.96 | 0 | 0 | 0 | 0 | 0 | 35273.96
2022012308 | 1 | 0.60887 | 48709.6 | 0.18307 | 6590.52 | 0.004 | 48 | 1 | 5000 | 6590.52 | 48 | 0 | 0 | 0 | 0 | 37071.08 | 0 | 0 | 0 | 0 | 0 | 37071.08
2022012309 | 1 | 0.61424 | 49139.2 | 0.16843 | 6063.48 | 0.11774 | 1412.88 | 1 | 5000 | 6063.48 | 1412.88 | 0 | 0 | 0 | 0 | 36662.84 | 0 | 0 | 0 | 0 | 0 | 36662.84
2022012310 | 1 | 0.60169 | 48135.2 | 0.11024 | 3968.64 | 0.31666 | 3799.92 | 1 | 5000 | 3968.64 | 3799.92 | 0 | 0 | 0 | 0 | 35366.64 | 0 | 0 | 0 | 0 | 0 | 35366.64
2022012311 | 1 | 0.57924 | 46339.2 | 0.06841 | 2462.76 | 0.40515 | 4861.8 | 1 | 5000 | 2462.76 | 4861.8 | 0 | 0 | 0 | 0 | 34014.64 | 0 | 0 | 0 | 0 | 0 | 34014.64
2022012312 | 1 | 0.55176 | 44140.8 | 0.04901 | 1764.36 | 0.46127 | 5535.24 | 1 | 5000 | 1764.36 | 5535.24 | 0 | 0 | 0 | 0 | 31841.2 | 0 | 0 | 0 | 0 | 0 | 31841.2
2022012313 | 1 | 0.53218 | 42574.4 | 0.04595 | 1654.2 | 0.49051 | 5886.12 | 1 | 5000 | 1654.2 | 5886.12 | 0 | 0 | 0 | 0 | 30034.08 | 0 | 0 | 0 | 0 | 0 | 30034.08
2022012314 | 1 | 0.51421 | 41136.8 | 0.04882 | 1757.52 | 0.52202 | 6264.24 | 1 | 5000 | 1757.52 | 6264.24 | 0 | 0 | 0 | 0 | 28115.04 | 0 | 0 | 0 | 0 | 0 | 28115.04
2022012315 | 1 | 0.49983 | 39986.4 | 0.04551 | 1638.36 | 0.50216 | 6025.92 | 1 | 5000 | 1638.36 | 6025.92 | 0 | 0 | 0 | 0 | 27322.12 | 0 | 0 | 0 | 0 | 0 | 27322.12
2022012316 | 1 | 0.4948 | 39584 | 0.03998 | 1439.28 | 0.49912 | 5989.44 | 1 | 5000 | 1439.28 | 5989.44 | 0 | 0 | 0 | 0 | 27155.28 | 0 | 0 | 0 | 0 | 0 | 27155.28
2022012317 | 1 | 0.49884 | 39907.2 | 0.04517 | 1626.12 | 0.38687 | 4642.44 | 1 | 5000 | 1626.12 | 4642.44 | 0 | 0 | 0 | 0 | 28638.64 | 0 | 0 | 0 | 0 | 0 | 28638.64
2022012318 | 1 | 0.51706 | 41364.8 | 0.05342 | 1923.12 | 0.10733 | 1287.96 | 1 | 5000 | 1923.12 | 1287.96 | 0 | 0 | 0 | 0 | 33153.72 | 0 | 0 | 0 | 0 | 0 | 33153.72
2022012319 | 1 | 0.54751 | 43800.8 | 0.07855 | 2827.8 | 0.00097 | 11.64 | 1 | 5000 | 2827.8 | 11.64 | 0 | 0 | 0 | 0 | 35961.36 | 0 | 0 | 0 | 0 | 0 | 35961.36
2022012320 | 1 | 0.55244 | 44195.2 | 0.12184 | 4386.24 | 0 | 0 | 1 | 5000 | 4386.24 | 0 | 0 | 0 | 0 | 0 | 34808.96 | 0 | 0 | 0 | 0 | 0 | 34808.96
2022012321 | 1 | 0.54557 | 43645.6 | 0.15092 | 5433.12 | 0 | 0 | 1 | 5000 | 5433.12 | 0 | 0 | 0 | 0 | 0 | 33212.48 | 0 | 0 | 0 | 0 | 0 | 33212.48
2022012322 | 1 | 0.53713 | 42970.4 | 0.17971 | 6469.56 | 0 | 0 | 1 | 5000 | 6469.56 | 0 | 0 | 0 | 0 | 0 | 31500.84 | 0 | 0 | 0 | 0 | 0 | 31500.84
2022012323 | 1 | 0.51407 | 41125.6 | 0.23073 | 8306.28 | 0 | 0 | 1 | 5000 | 8306.28 | 0 | 0 | 0 | 0 | 0 | 27819.32 | 0 | 0 | 0 | 0 | 0 | 27819.32
2022012324 | 1 | 0.49236 | 39388.8 | 0.27756 | 9992.16 | 0 | 0 | 1 | 5000 | 9992.16 | 0 | 0 | 0 | 0 | 0 | 24396.64 | 0 | 0 | 0 | 0 | 0 | 24396.64
2022012401 | 2 | 0.47897 | 38317.6 | 0.31528 | 11350.08 | 0 | 0 | 1 | 5000 | 11350.08 | 0 | 0 | 0 | 0 | 0 | 21967.52 | 0 | 0 | 0 | 0 | 0 | 21967.52
2022012402 | 2 | 0.47258 | 37806.4 | 0.35012 | 12604.32 | 0 | 0 | 1 | 5000 | 12604.32 | 0 | 0 | 0 | 0 | 0 | 20202.08 | 0 | 0 | 0 | 0 | 0 | 20202.08
2022012403 | 2 | 0.47155 | 37724 | 0.36034 | 12972.24 | 0 | 0 | 1 | 5000 | 12972.24 | 0 | 0 | 0 | 0 | 0 | 19751.76 | 0 | 0 | 0 | 0 | 0 | 19751.76
2022012404 | 2 | 0.47727 | 38181.6 | 0.35742 | 12867.12 | 0 | 0 | 1 | 5000 | 12867.12 | 0 | 0 | 0 | 0 | 0 | 20314.48 | 0 | 0 | 0 | 0 | 0 | 20314.48
2022012405 | 2 | 0.4901 | 39208 | 0.34324 | 12356.64 | 0 | 0 | 1 | 5000 | 12356.64 | 0 | 0 | 0 | 0 | 0 | 21851.36 | 0 | 0 | 0 | 0 | 0 | 21851.36
2022012406 | 2 | 0.51779 | 41423.2 | 0.32435 | 11676.6 | 0 | 0 | 1 | 5000 | 11676.6 | 0 | 0 | 0 | 0 | 0 | 24746.6 | 0 | 0 | 0 | 0 | 0 | 24746.6
2022012407 | 2 | 0.56115 | 44892 | 0.28319 | 10194.84 | 0 | 0 | 1 | 5000 | 10194.84 | 0 | 0 | 0 | 0 | 0 | 29697.16 | 0 | 0 | 0 | 0 | 0 | 29697.16
2022012408 | 2 | 0.58516 | 46812.8 | 0.26643 | 9591.48 | 0.00065 | 7.8 | 1 | 5000 | 9591.48 | 7.8 | 0 | 0 | 0 | 0 | 32213.52 | 0 | 0 | 0 | 0 | 0 | 32213.52
2022012409 | 2 | 0.58598 | 46878.4 | 0.23479 | 8452.44 | 0.13321 | 1598.52 | 1 | 5000 | 8452.44 | 1598.52 | 0 | 0 | 0 | 0 | 31827.44 | 0 | 0 | 0 | 0 | 0 | 31827.44
2022012410 | 2 | 0.58671 | 46936.8 | 0.16508 | 5942.88 | 0.45399 | 5447.88 | 1 | 5000 | 5942.88 | 5447.88 | 0 | 0 | 0 | 0 | 30546.04 | 0 | 0 | 0 | 0 | 0 | 30546.04
2022012411 | 2 | 0.58819 | 47055.2 | 0.12305 | 4429.8 | 0.55256 | 6630.72 | 1 | 5000 | 4429.8 | 6630.72 | 0 | 0 | 0 | 0 | 30994.68 | 0 | 0 | 0 | 0 | 0 | 30994.68
2022012412 | 2 | 0.58634 | 46907.2 | 0.13771 | 4957.56 | 0.55393 | 6647.16 | 1 | 5000 | 4957.56 | 6647.16 | 0 | 0 | 0 | 0 | 30302.48 | 0 | 0 | 0 | 0 | 0 | 30302.48
2022012413 | 2 | 0.58054 | 46443.2 | 0.14263 | 5134.68 | 0.54414 | 6529.68 | 1 | 5000 | 5134.68 | 6529.68 | 0 | 0 | 0 | 0 | 29778.84 | 0 | 0 | 0 | 0 | 0 | 29778.84
2022012414 | 2 | 0.57473 | 45978.4 | 0.13477 | 4851.72 | 0.56525 | 6783 | 1 | 5000 | 4851.72 | 6783 | 0 | 0 | 0 | 0 | 29343.68 | 0 | 0 | 0 | 0 | 0 | 29343.68
2022012415 | 2 | 0.56827 | 45461.6 | 0.14363 | 5170.68 | 0.58313 | 6997.56 | 1 | 5000 | 5170.68 | 6997.56 | 0 | 0 | 0 | 0 | 28293.36 | 0 | 0 | 0 | 0 | 0 | 28293.36
2022012416 | 2 | 0.56264 | 45011.2 | 0.15467 | 5568.12 | 0.57504 | 6900.48 | 1 | 5000 | 5568.12 | 6900.48 | 0 | 0 | 0 | 0 | 27542.6 | 0 | 0 | 0 | 0 | 0 | 27542.6
2022012417 | 2 | 0.56781 | 45424.8 | 0.12664 | 4559.04 | 0.52852 | 6342.24 | 1 | 5000 | 4559.04 | 6342.24 | 0 | 0 | 0 | 0 | 29523.52 | 0 | 0 | 0 | 0 | 0 | 29523.52
2022012418 | 2 | 0.58375 | 46700 | 0.10493 | 3777.48 | 0.19403 | 2328.36 | 1 | 5000 | 3777.48 | 2328.36 | 0 | 0 | 0 | 0 | 35594.16 | 0 | 0 | 0 | 0 | 0 | 35594.16
2022012419 | 2 | 0.60369 | 48295.2 | 0.08583 | 3089.88 | 0.00241 | 28.92 | 1 | 5000 | 3089.88 | 28.92 | 0 | 0 | 0 | 0 | 40176.4 | 0 | 0 | 0 | 0 | 0 | 40176.4
2022012420 | 2 | 0.59913 | 47930.4 | 0.09318 | 3354.48 | 0 | 0 | 1 | 5000 | 3354.48 | 0 | 0 | 0 | 0 | 0 | 39575.92 | 0 | 0 | 0 | 0 | 0 | 39575.92
2022012421 | 2 | 0.58885 | 47108 | 0.1029 | 3704.4 | 0 | 0 | 1 | 5000 | 3704.4 | 0 | 0 | 0 | 0 | 0 | 38403.6 | 0 | 0 | 0 | 0 | 0 | 38403.6
2022012422 | 2 | 0.57086 | 45668.8 | 0.11657 | 4196.52 | 0 | 0 | 1 | 5000 | 4196.52 | 0 | 0 | 0 | 0 | 0 | 36472.28 | 0 | 0 | 0 | 0 | 0 | 36472.28
2022012423 | 2 | 0.54318 | 43454.4 | 0.1073 | 3862.8 | 0 | 0 | 1 | 5000 | 3862.8 | 0 | 0 | 0 | 0 | 0 | 34591.6 | 0 | 0 | 0 | 0 | 0 | 34591.6
2022012424 | 2 | 0.51848 | 41478.4 | 0.11275 | 4059 | 0 | 0 | 1 | 5000 | 4059 | 0 | 0 | 0 | 0 | 0 | 32419.4 | 0 | 0 | 0 | 0 | 0 | 32419.4
2022012501 | 3 | 0.50184 | 40147.2 | 0.13397 | 4822.92 | 0 | 0 | 1 | 5000 | 4822.92 | 0 | 0 | 0 | 0 | 0 | 30324.28 | 0 | 0 | 0 | 0 | 0 | 30324.28
2022012502 | 3 | 0.49349 | 39479.2 | 0.17251 | 6210.36 | 0 | 0 | 1 | 5000 | 6210.36 | 0 | 0 | 0 | 0 | 0 | 28268.84 | 0 | 0 | 0 | 0 | 0 | 28268.84
2022012503 | 3 | 0.48977 | 39181.6 | 0.2234 | 8042.4 | 0 | 0 | 1 | 5000 | 8042.4 | 0 | 0 | 0 | 0 | 0 | 26139.2 | 0 | 0 | 0 | 0 | 0 | 26139.2
2022012504 | 3 | 0.49388 | 39510.4 | 0.27121 | 9763.56 | 0 | 0 | 1 | 5000 | 9763.56 | 0 | 0 | 0 | 0 | 0 | 24746.84 | 0 | 0 | 0 | 0 | 0 | 24746.84
2022012505 | 3 | 0.5072 | 40576 | 0.3075 | 11070 | 0 | 0 | 1 | 5000 | 11070 | 0 | 0 | 0 | 0 | 0 | 24506 | 0 | 0 | 0 | 0 | 0 | 24506
2022012506 | 3 | 0.53937 | 43149.6 | 0.3374 | 12146.4 | 0 | 0 | 1 | 5000 | 12146.4 | 0 | 0 | 0 | 0 | 0 | 26003.2 | 0 | 0 | 0 | 0 | 0 | 26003.2
2022012507 | 3 | 0.58989 | 47191.2 | 0.37823 | 13616.28 | 0 | 0 | 1 | 5000 | 13616.28 | 0 | 0 | 0 | 0 | 0 | 28574.92 | 0 | 0 | 0 | 0 | 0 | 28574.92
2022012508 | 3 | 0.61386 | 49108.8 | 0.38441 | 13838.76 | 0.00402 | 48.24 | 1 | 5000 | 13838.76 | 48.24 | 0 | 0 | 0 | 0 | 30221.8 | 0 | 0 | 0 | 0 | 0 | 30221.8
2022012509 | 3 | 0.607 | 48560 | 0.34303 | 12349.08 | 0.23873 | 2864.76 | 1 | 5000 | 12349.08 | 2864.76 | 0 | 0 | 0 | 0 | 28346.16 | 0 | 0 | 0 | 0 | 0 | 28346.16
2022012510 | 3 | 0.59526 | 47620.8 | 0.29668 | 10680.48 | 0.61942 | 7433.04 | 1 | 5000 | 10680.48 | 7433.04 | 0 | 0 | 0 | 0 | 24507.28 | 0 | 0 | 0 | 0 | 0 | 24507.28
2022012511 | 3 | 0.58005 | 46404 | 0.29755 | 10711.8 | 0.67625 | 8115 | 1 | 5000 | 10711.8 | 8115 | 0 | 0 | 0 | 0 | 22577.2 | 0 | 0 | 0 | 0 | 0 | 22577.2
2022012512 | 3 | 0.56424 | 45139.2 | 0.26515 | 9545.4 | 0.66686 | 8002.32 | 1 | 5000 | 9545.4 | 8002.32 | 0 | 0 | 0 | 0 | 22591.48 | 0 | 0 | 0 | 0 | 0 | 22591.48
2022012513 | 3 | 0.54681 | 43744.8 | 0.23796 | 8566.56 | 0.65315 | 7837.8 | 1 | 5000 | 8566.56 | 7837.8 | 0 | 0 | 0 | 0 | 22340.44 | 0 | 0 | 0 | 0 | 0 | 22340.44
2022012514 | 3 | 0.53387 | 42709.6 | 0.21327 | 7677.72 | 0.65934 | 7912.08 | 1 | 5000 | 7677.72 | 7912.08 | 0 | 0 | 0 | 0 | 22119.8 | 0 | 0 | 0 | 0 | 0 | 22119.8
2022012515 | 3 | 0.52655 | 42124 | 0.20837 | 7501.32 | 0.68237 | 8188.44 | 1 | 5000 | 7501.32 | 8188.44 | 0 | 0 | 0 | 0 | 21434.24 | 0 | 0 | 0 | 0 | 0 | 21434.24
2022012516 | 3 | 0.52261 | 41808.8 | 0.22429 | 8074.44 | 0.69485 | 8338.2 | 1 | 5000 | 8074.44 | 8338.2 | 0 | 0 | 0 | 0 | 20396.16 | 0 | 0 | 0 | 0 | 0 | 20396.16
2022012517 | 3 | 0.52776 | 42220.8 | 0.26572 | 9565.92 | 0.60819 | 7298.28 | 1 | 5000 | 9565.92 | 7298.28 | 0 | 0 | 0 | 0 | 20356.6 | 0 | 0 | 0 | 0 | 0 | 20356.6
2022012518 | 3 | 0.54673 | 43738.4 | 0.34644 | 12471.84 | 0.21865 | 2623.8 | 1 | 5000 | 12471.84 | 2623.8 | 0 | 0 | 0 | 0 | 23642.76 | 0 | 0 | 0 | 0 | 0 | 23642.76
2022012519 | 3 | 0.57486 | 45988.8 | 0.4419 | 15908.4 | 0.00768 | 92.16 | 1 | 5000 | 15908.4 | 92.16 | 0 | 0 | 0 | 0 | 24988.24 | 0 | 0 | 0 | 0 | 0 | 24988.24
2022012520 | 3 | 0.58065 | 46452 | 0.51647 | 18592.92 | 0.00485 | 58.2 | 1 | 5000 | 18592.92 | 58.2 | 0 | 0 | 0 | 0 | 22800.88 | 0 | 0 | 0 | 0 | 0 | 22800.88
2022012521 | 3 | 0.5783 | 46264 | 0.54269 | 19536.84 | 0.00485 | 58.2 | 1 | 5000 | 19536.84 | 58.2 | 0 | 0 | 0 | 0 | 21668.96 | 0 | 0 | 0 | 0 | 0 | 21668.96
2022012522 | 3 | 0.56854 | 45483.2 | 0.55402 | 19944.72 | 0.00485 | 58.2 | 1 | 5000 | 19944.72 | 58.2 | 0 | 0 | 0 | 0 | 20480.28 | 0 | 0 | 0 | 0 | 0 | 20480.28
2022012523 | 3 | 0.54736 | 43788.8 | 0.56045 | 20176.2 | 0.00485 | 58.2 | 1 | 5000 | 20176.2 | 58.2 | 0 | 0 | 0 | 0 | 18554.4 | 0 | 0 | 0 | 0 | 0 | 18554.4
2022012524 | 3 | 0.52793 | 42234.4 | 0.55884 | 20118.24 | 0.00486 | 58.32 | 1 | 5000 | 20118.24 | 58.32 | 0 | 0 | 0 | 0 | 17057.84 | 0 | 0 | 0 | 0 | 0 | 17057.84
2022012601 | 4 | 0.51655 | 41324 | 0.50629 | 18226.44 | 0.00485 | 58.2 | 1 | 5000 | 18226.44 | 58.2 | 0 | 0 | 0 | 0 | 18039.36 | 0 | 0 | 0 | 0 | 0 | 18039.36
2022012602 | 4 | 0.51545 | 41236 | 0.47225 | 17001 | 0.00485 | 58.2 | 1 | 5000 | 17001 | 58.2 | 0 | 0 | 0 | 0 | 19176.8 | 0 | 0 | 0 | 0 | 0 | 19176.8
2022012603 | 4 | 0.52091 | 41672.8 | 0.44277 | 15939.72 | 0.00485 | 58.2 | 1 | 5000 | 15939.72 | 58.2 | 0 | 0 | 0 | 0 | 20674.88 | 0 | 0 | 0 | 0 | 0 | 20674.88
2022012604 | 4 | 0.53224 | 42579.2 | 0.40026 | 14409.36 | 0.00485 | 58.2 | 1 | 5000 | 14409.36 | 58.2 | 0 | 0 | 0 | 0 | 23111.64 | 0 | 0 | 0 | 0 | 0 | 23111.64
2022012605 | 4 | 0.55371 | 44296.8 | 0.38252 | 13770.72 | 0.00485 | 58.2 | 1 | 5000 | 13770.72 | 58.2 | 0 | 0 | 0 | 0 | 25467.88 | 0 | 0 | 0 | 0 | 0 | 25467.88
2022012606 | 4 | 0.59247 | 47397.6 | 0.35448 | 12761.28 | 0.00485 | 58.2 | 1 | 5000 | 12761.28 | 58.2 | 0 | 0 | 0 | 0 | 29578.12 | 0 | 0 | 0 | 0 | 0 | 29578.12
2022012607 | 4 | 0.64753 | 51802.4 | 0.3312 | 11923.2 | 0.00368 | 44.16 | 1 | 5000 | 11923.2 | 44.16 | 0 | 0 | 0 | 0 | 34835.04 | 0 | 0 | 0 | 0 | 0 | 34835.04
2022012608 | 4 | 0.6741 | 53928 | 0.2854 | 10274.4 | 0.00425 | 51 | 1 | 5000 | 10274.4 | 51 | 0 | 0 | 0 | 0 | 38602.6 | 0 | 0 | 0 | 0 | 0 | 38602.6
2022012609 | 4 | 0.6676 | 53408 | 0.21147 | 7612.92 | 0.06936 | 832.32 | 1 | 5000 | 7612.92 | 832.32 | 0 | 0 | 0 | 0 | 39962.76 | 0 | 0 | 0 | 0 | 0 | 39962.76
2022012610 | 4 | 0.65127 | 52101.6 | 0.16046 | 5776.56 | 0.14809 | 1777.08 | 1 | 5000 | 5776.56 | 1777.08 | 0 | 0 | 0 | 0 | 39547.96 | 0 | 0 | 0 | 0 | 0 | 39547.96
2022012611 | 4 | 0.63253 | 50602.4 | 0.1311 | 4719.6 | 0.19458 | 2334.96 | 1 | 5000 | 4719.6 | 2334.96 | 0 | 0 | 0 | 0 | 38547.84 | 0 | 0 | 0 | 0 | 0 | 38547.84
2022012612 | 4 | 0.61049 | 48839.2 | 0.11133 | 4007.88 | 0.23941 | 2872.92 | 1 | 5000 | 4007.88 | 2872.92 | 0 | 0 | 0 | 0 | 36958.4 | 0 | 0 | 0 | 0 | 0 | 36958.4
2022012613 | 4 | 0.58706 | 46964.8 | 0.09593 | 3453.48 | 0.27798 | 3335.76 | 1 | 5000 | 3453.48 | 3335.76 | 0 | 0 | 0 | 0 | 35175.56 | 0 | 0 | 0 | 0 | 0 | 35175.56
2022012614 | 4 | 0.56791 | 45432.8 | 0.09119 | 3282.84 | 0.30596 | 3671.52 | 1 | 5000 | 3282.84 | 3671.52 | 0 | 0 | 0 | 0 | 33478.44 | 0 | 0 | 0 | 0 | 0 | 33478.44
2022012615 | 4 | 0.55322 | 44257.6 | 0.0958 | 3448.8 | 0.28551 | 3426.12 | 1 | 5000 | 3448.8 | 3426.12 | 0 | 0 | 0 | 0 | 32382.68 | 0 | 0 | 0 | 0 | 0 | 32382.68
2022012616 | 4 | 0.54547 | 43637.6 | 0.10038 | 3613.68 | 0.25214 | 3025.68 | 1 | 5000 | 3613.68 | 3025.68 | 0 | 0 | 0 | 0 | 31998.24 | 0 | 0 | 0 | 0 | 0 | 31998.24
2022012617 | 4 | 0.55232 | 44185.6 | 0.10324 | 3716.64 | 0.18419 | 2210.28 | 1 | 5000 | 3716.64 | 2210.28 | 0 | 0 | 0 | 0 | 33258.68 | 0 | 0 | 0 | 0 | 0 | 33258.68
2022012618 | 4 | 0.57567 | 46053.6 | 0.09738 | 3505.68 | 0.06177 | 741.24 | 1 | 5000 | 3505.68 | 741.24 | 0 | 0 | 0 | 0 | 36806.68 | 0 | 0 | 0 | 0 | 0 | 36806.68
2022012619 | 4 | 0.60919 | 48735.2 | 0.11001 | 3960.36 | 0.00626 | 75.12 | 1 | 5000 | 3960.36 | 75.12 | 0 | 0 | 0 | 0 | 39699.72 | 0 | 0 | 0 | 0 | 0 | 39699.72
2022012620 | 4 | 0.61434 | 49147.2 | 0.11884 | 4278.24 | 0.00536 | 64.32 | 1 | 5000 | 4278.24 | 64.32 | 0 | 0 | 0 | 0 | 39804.64 | 0 | 0 | 0 | 0 | 0 | 39804.64
2022012621 | 4 | 0.60999 | 48799.2 | 0.10924 | 3932.64 | 0.00537 | 64.44 | 1 | 5000 | 3932.64 | 64.44 | 0 | 0 | 0 | 0 | 39802.12 | 0 | 0 | 0 | 0 | 0 | 39802.12
2022012622 | 4 | 0.59367 | 47493.6 | 0.1049 | 3776.4 | 0.00537 | 64.44 | 1 | 5000 | 3776.4 | 64.44 | 0 | 0 | 0 | 0 | 38652.76 | 0 | 0 | 0 | 0 | 0 | 38652.76
2022012623 | 4 | 0.56513 | 45210.4 | 0.11149 | 4013.64 | 0.00537 | 64.44 | 1 | 5000 | 4013.64 | 64.44 | 0 | 0 | 0 | 0 | 36132.32 | 0 | 0 | 0 | 0 | 0 | 36132.32
2022012624 | 4 | 0.53936 | 43148.8 | 0.12268 | 4416.48 | 0.00537 | 64.44 | 1 | 5000 | 4416.48 | 64.44 | 0 | 0 | 0 | 0 | 33667.88 | 0 | 0 | 0 | 0 | 0 | 33667.88
2022012701 | 5 | 0.52374 | 41899.2 | 0.14061 | 5061.96 | 0.00537 | 64.44 | 1 | 5000 | 5061.96 | 64.44 | 0 | 0 | 0 | 0 | 31772.8 | 0 | 0 | 0 | 0 | 0 | 31772.8
2022012702 | 5 | 0.51593 | 41274.4 | 0.14118 | 5082.48 | 0.00537 | 64.44 | 1 | 5000 | 5082.48 | 64.44 | 0 | 0 | 0 | 0 | 31127.48 | 0 | 0 | 0 | 0 | 0 | 31127.48
2022012703 | 5 | 0.514 | 41120 | 0.14299 | 5147.64 | 0.00537 | 64.44 | 1 | 5000 | 5147.64 | 64.44 | 0 | 0 | 0 | 0 | 30907.92 | 0 | 0 | 0 | 0 | 0 | 30907.92
2022012704 | 5 | 0.51813 | 41450.4 | 0.14484 | 5214.24 | 0.00537 | 64.44 | 1 | 5000 | 5214.24 | 64.44 | 0 | 0 | 0 | 0 | 31171.72 | 0 | 0 | 0 | 0 | 0 | 31171.72
2022012705 | 5 | 0.53219 | 42575.2 | 0.14615 | 5261.4 | 0.00193 | 23.16 | 1 | 5000 | 5261.4 | 23.16 | 0 | 0 | 0 | 0 | 32290.64 | 0 | 0 | 0 | 0 | 0 | 32290.64
2022012706 | 5 | 0.56516 | 45212.8 | 0.14281 | 5141.16 | 0 | 0 | 1 | 5000 | 5141.16 | 0 | 0 | 0 | 0 | 0 | 35071.64 | 0 | 0 | 0 | 0 | 0 | 35071.64
2022012707 | 5 | 0.61342 | 49073.6 | 0.13334 | 4800.24 | 0 | 0 | 1 | 5000 | 4800.24 | 0 | 0 | 0 | 0 | 0 | 39273.36 | 0 | 0 | 0 | 0 | 0 | 39273.36
2022012708 | 5 | 0.63683 | 50946.4 | 0.13353 | 4807.08 | 0.00397 | 47.64 | 1 | 5000 | 4807.08 | 47.64 | 0 | 0 | 0 | 0 | 41091.68 | 0 | 0 | 0 | 0 | 0 | 41091.68
2022012709 | 5 | 0.62713 | 50170.4 | 0.10674 | 3842.64 | 0.07574 | 908.88 | 1 | 5000 | 3842.64 | 908.88 | 0 | 0 | 0 | 0 | 40418.88 | 0 | 0 | 0 | 0 | 0 | 40418.88
2022012710 | 5 | 0.6084 | 48672 | 0.0885 | 3186 | 0.20662 | 2479.44 | 1 | 5000 | 3186 | 2479.44 | 0 | 0 | 0 | 0 | 38006.56 | 0 | 0 | 0 | 0 | 0 | 38006.56
2022012711 | 5 | 0.59156 | 47324.8 | 0.0668 | 2404.8 | 0.29407 | 3528.84 | 1 | 5000 | 2404.8 | 3528.84 | 0 | 0 | 0 | 0 | 36391.16 | 0 | 0 | 0 | 0 | 0 | 36391.16
2022012712 | 5 | 0.57327 | 45861.6 | 0.05435 | 1956.6 | 0.40788 | 4894.56 | 1 | 5000 | 1956.6 | 4894.56 | 0 | 0 | 0 | 0 | 34010.44 | 0 | 0 | 0 | 0 | 0 | 34010.44
2022012713 | 5 | 0.55459 | 44367.2 | 0.06124 | 2204.64 | 0.44474 | 5336.88 | 1 | 5000 | 2204.64 | 5336.88 | 0 | 0 | 0 | 0 | 31825.68 | 0 | 0 | 0 | 0 | 0 | 31825.68
2022012714 | 5 | 0.5413 | 43304 | 0.08207 | 2954.52 | 0.48654 | 5838.48 | 1 | 5000 | 2954.52 | 5838.48 | 0 | 0 | 0 | 0 | 29511 | 0 | 0 | 0 | 0 | 0 | 29511
2022012715 | 5 | 0.52975 | 42380 | 0.11043 | 3975.48 | 0.51649 | 6197.88 | 1 | 5000 | 3975.48 | 6197.88 | 0 | 0 | 0 | 0 | 27206.64 | 0 | 0 | 0 | 0 | 0 | 27206.64
2022012716 | 5 | 0.52238 | 41790.4 | 0.14103 | 5077.08 | 0.53347 | 6401.64 | 1 | 5000 | 5077.08 | 6401.64 | 0 | 0 | 0 | 0 | 25311.68 | 0 | 0 | 0 | 0 | 0 | 25311.68
2022012717 | 5 | 0.52586 | 42068.8 | 0.16365 | 5891.4 | 0.45844 | 5501.28 | 1 | 5000 | 5891.4 | 5501.28 | 0 | 0 | 0 | 0 | 25676.12 | 0 | 0 | 0 | 0 | 0 | 25676.12
2022012718 | 5 | 0.54295 | 43436 | 0.19854 | 7147.44 | 0.17354 | 2082.48 | 1 | 5000 | 7147.44 | 2082.48 | 0 | 0 | 0 | 0 | 29206.08 | 0 | 0 | 0 | 0 | 0 | 29206.08
2022012719 | 5 | 0.571 | 45680 | 0.26646 | 9592.56 | 0.00326 | 39.12 | 1 | 5000 | 9592.56 | 39.12 | 0 | 0 | 0 | 0 | 31048.32 | 0 | 0 | 0 | 0 | 0 | 31048.32
2022012720 | 5 | 0.57709 | 46167.2 | 0.34055 | 12259.8 | 7e-05 | 0.84 | 1 | 5000 | 12259.8 | 0.84 | 0 | 0 | 0 | 0 | 28906.56 | 0 | 0 | 0 | 0 | 0 | 28906.56
2022012721 | 5 | 0.57603 | 46082.4 | 0.41797 | 15046.92 | 0 | 0 | 1 | 5000 | 15046.92 | 0 | 0 | 0 | 0 | 0 | 26035.48 | 0 | 0 | 0 | 0 | 0 | 26035.48
2022012722 | 5 | 0.5641 | 45128 | 0.47491 | 17096.76 | 0 | 0 | 1 | 5000 | 17096.76 | 0 | 0 | 0 | 0 | 0 | 23031.24 | 0 | 0 | 0 | 0 | 0 | 23031.24
2022012723 | 5 | 0.54209 | 43367.2 | 0.4808 | 17308.8 | 0 | 0 | 1 | 5000 | 17308.8 | 0 | 0 | 0 | 0 | 0 | 21058.4 | 0 | 0 | 0 | 0 | 0 | 21058.4
2022012724 | 5 | 0.52095 | 41676 | 0.47536 | 17112.96 | 0 | 0 | 1 | 5000 | 17112.96 | 0 | 0 | 0 | 0 | 0 | 19563.04 | 0 | 0 | 0 | 0 | 0 | 19563.04
2022012801 | 6 | 0.50937 | 40749.6 | 0.47781 | 17201.16 | 0 | 0 | 1 | 5000 | 17201.16 | 0 | 0 | 0 | 0 | 0 | 18548.44 | 0 | 0 | 0 | 0 | 0 | 18548.44
2022012802 | 6 | 0.5047 | 40376 | 0.48053 | 17299.08 | 0 | 0 | 1 | 5000 | 17299.08 | 0 | 0 | 0 | 0 | 0 | 18076.92 | 0 | 0 | 0 | 0 | 0 | 18076.92
2022012803 | 6 | 0.50906 | 40724.8 | 0.4605 | 16578 | 0 | 0 | 1 | 5000 | 16578 | 0 | 0 | 0 | 0 | 0 | 19146.8 | 0 | 0 | 0 | 0 | 0 | 19146.8
2022012804 | 6 | 0.52097 | 41677.6 | 0.46389 | 16700.04 | 0 | 0 | 1 | 5000 | 16700.04 | 0 | 0 | 0 | 0 | 0 | 19977.56 | 0 | 0 | 0 | 0 | 0 | 19977.56
2022012805 | 6 | 0.54068 | 43254.4 | 0.47415 | 17069.4 | 0 | 0 | 1 | 5000 | 17069.4 | 0 | 0 | 0 | 0 | 0 | 21185 | 0 | 0 | 0 | 0 | 0 | 21185
2022012806 | 6 | 0.57894 | 46315.2 | 0.46044 | 16575.84 | 0 | 0 | 1 | 5000 | 16575.84 | 0 | 0 | 0 | 0 | 0 | 24739.36 | 0 | 0 | 0 | 0 | 0 | 24739.36
2022012807 | 6 | 0.63236 | 50588.8 | 0.43625 | 15705 | 0 | 0 | 1 | 5000 | 15705 | 0 | 0 | 0 | 0 | 0 | 29883.8 | 0 | 0 | 0 | 0 | 0 | 29883.8
2022012808 | 6 | 0.66271 | 53016.8 | 0.4077 | 14677.2 | 0.00656 | 78.72 | 1 | 5000 | 14677.2 | 78.72 | 0 | 0 | 0 | 0 | 33260.88 | 0 | 0 | 0 | 0 | 0 | 33260.88
2022012809 | 6 | 0.65782 | 52625.6 | 0.34848 | 12545.28 | 0.27776 | 3333.12 | 1 | 5000 | 12545.28 | 3333.12 | 0 | 0 | 0 | 0 | 31747.2 | 0 | 0 | 0 | 0 | 0 | 31747.2
2022012810 | 6 | 0.63861 | 51088.8 | 0.2538 | 9136.8 | 0.69755 | 8370.6 | 1 | 5000 | 9136.8 | 8370.6 | 0 | 0 | 0 | 0 | 28581.4 | 0 | 0 | 0 | 0 | 0 | 28581.4
2022012811 | 6 | 0.61601 | 49280.8 | 0.21892 | 7881.12 | 0.75283 | 9033.96 | 1 | 5000 | 7881.12 | 9033.96 | 0 | 0 | 0 | 0 | 27365.72 | 0 | 0 | 0 | 0 | 0 | 27365.72
2022012812 | 6 | 0.59186 | 47348.8 | 0.25073 | 9026.28 | 0.75461 | 9055.32 | 1 | 5000 | 9026.28 | 9055.32 | 0 | 0 | 0 | 0 | 24267.2 | 0 | 0 | 0 | 0 | 0 | 24267.2
2022012813 | 6 | 0.57002 | 45601.6 | 0.27811 | 10011.96 | 0.75423 | 9050.76 | 1 | 5000 | 10011.96 | 9050.76 | 0 | 0 | 0 | 0 | 21538.88 | 0 | 0 | 0 | 0 | 0 | 21538.88
2022012814 | 6 | 0.55334 | 44267.2 | 0.28099 | 10115.64 | 0.76784 | 9214.08 | 1 | 5000 | 10115.64 | 9214.08 | 0 | 0 | 0 | 0 | 19937.48 | 0 | 0 | 0 | 0 | 0 | 19937.48
2022012815 | 6 | 0.53842 | 43073.6 | 0.2646 | 9525.6 | 0.78991 | 9478.92 | 1 | 5000 | 9525.6 | 9478.92 | 0 | 0 | 0 | 0 | 19069.08 | 0 | 0 | 0 | 0 | 0 | 19069.08
2022012816 | 6 | 0.52913 | 42330.4 | 0.24253 | 8731.08 | 0.81275 | 9753 | 1 | 5000 | 8731.08 | 9753 | 0 | 0 | 0 | 0 | 18846.32 | 0 | 0 | 0 | 0 | 0 | 18846.32
2022012817 | 6 | 0.52831 | 42264.8 | 0.20351 | 7326.36 | 0.71996 | 8639.52 | 1 | 5000 | 7326.36 | 8639.52 | 0 | 0 | 0 | 0 | 21298.92 | 0 | 0 | 0 | 0 | 0 | 21298.92
2022012818 | 6 | 0.54278 | 43422.4 | 0.12921 | 4651.56 | 0.26314 | 3157.68 | 1 | 5000 | 4651.56 | 3157.68 | 0 | 0 | 0 | 0 | 30613.16 | 0 | 0 | 0 | 0 | 0 | 30613.16
2022012819 | 6 | 0.57587 | 46069.6 | 0.07706 | 2774.16 | 0.00488 | 58.56 | 1 | 5000 | 2774.16 | 58.56 | 0 | 0 | 0 | 0 | 38236.88 | 0 | 0 | 0 | 0 | 0 | 38236.88
2022012820 | 6 | 0.58782 | 47025.6 | 0.06244 | 2247.84 | 6e-05 | 0.72 | 1 | 5000 | 2247.84 | 0.72 | 0 | 0 | 0 | 0 | 39777.04 | 0 | 0 | 0 | 0 | 0 | 39777.04
2022012821 | 6 | 0.59357 | 47485.6 | 0.06522 | 2347.92 | 6e-05 | 0.72 | 1 | 5000 | 2347.92 | 0.72 | 0 | 0 | 0 | 0 | 40136.96 | 0 | 0 | 0 | 0 | 0 | 40136.96
2022012822 | 6 | 0.59242 | 47393.6 | 0.08062 | 2902.32 | 6e-05 | 0.72 | 1 | 5000 | 2902.32 | 0.72 | 0 | 0 | 0 | 0 | 39490.56 | 0 | 0 | 0 | 0 | 0 | 39490.56
2022012823 | 6 | 0.58184 | 46547.2 | 0.10536 | 3792.96 | 6e-05 | 0.72 | 1 | 5000 | 3792.96 | 0.72 | 0 | 0 | 0 | 0 | 37753.52 | 0 | 0 | 0 | 0 | 0 | 37753.52
2022012824 | 6 | 0.57143 | 45714.4 | 0.13632 | 4907.52 | 6e-05 | 0.72 | 1 | 5000 | 4907.52 | 0.72 | 0 | 0 | 0 | 0 | 35806.16 | 0 | 0 | 0 | 0 | 0 | 35806.16
2022012901 | 7 | 0.56318 | 45054.4 | 0.16733 | 6023.88 | 6e-05 | 0.72 | 1 | 5000 | 6023.88 | 0.72 | 0 | 0 | 0 | 0 | 34029.8 | 0 | 0 | 0 | 0 | 0 | 34029.8
2022012902 | 7 | 0.56496 | 45196.8 | 0.22028 | 7930.08 | 6e-05 | 0.72 | 1 | 5000 | 7930.08 | 0.72 | 0 | 0 | 0 | 0 | 32266 | 0 | 0 | 0 | 0 | 0 | 32266
2022012903 | 7 | 0.56987 | 45589.6 | 0.27262 | 9814.32 | 6e-05 | 0.72 | 1 | 5000 | 9814.32 | 0.72 | 0 | 0 | 0 | 0 | 30774.56 | 0 | 0 | 0 | 0 | 0 | 30774.56
2022012904 | 7 | 0.57865 | 46292 | 0.30802 | 11088.72 | 6e-05 | 0.72 | 1 | 5000 | 11088.72 | 0.72 | 0 | 0 | 0 | 0 | 30202.56 | 0 | 0 | 0 | 0 | 0 | 30202.56
2022012905 | 7 | 0.59253 | 47402.4 | 0.32355 | 11647.8 | 0 | 0 | 1 | 5000 | 11647.8 | 0 | 0 | 0 | 0 | 0 | 30754.6 | 0 | 0 | 0 | 0 | 0 | 30754.6
2022012906 | 7 | 0.61192 | 48953.6 | 0.33157 | 11936.52 | 0 | 0 | 1 | 5000 | 11936.52 | 0 | 0 | 0 | 0 | 0 | 32017.08 | 0 | 0 | 0 | 0 | 0 | 32017.08
2022012907 | 7 | 0.63861 | 51088.8 | 0.31806 | 11450.16 | 0 | 0 | 1 | 5000 | 11450.16 | 0 | 0 | 0 | 0 | 0 | 34638.64 | 0 | 0 | 0 | 0 | 0 | 34638.64
2022012908 | 7 | 0.66177 | 52941.6 | 0.32298 | 11627.28 | 0.01304 | 156.48 | 1 | 5000 | 11627.28 | 156.48 | 0 | 0 | 0 | 0 | 36157.84 | 0 | 0 | 0 | 0 | 0 | 36157.84
2022012909 | 7 | 0.65696 | 52556.8 | 0.31905 | 11485.8 | 0.33532 | 4023.84 | 1 | 5000 | 11485.8 | 4023.84 | 0 | 0 | 0 | 0 | 32047.16 | 0 | 0 | 0 | 0 | 0 | 32047.16
2022012910 | 7 | 0.62529 | 50023.2 | 0.22094 | 7953.84 | 0.75286 | 9034.32 | 1 | 5000 | 7953.84 | 9034.32 | 0 | 0 | 0 | 0 | 28035.04 | 0 | 0 | 0 | 0 | 0 | 28035.04
2022012911 | 7 | 0.58747 | 46997.6 | 0.16836 | 6060.96 | 0.77474 | 9296.88 | 1 | 5000 | 6060.96 | 9296.88 | 0 | 0 | 0 | 0 | 26639.76 | 0 | 0 | 0 | 0 | 0 | 26639.76
2022012912 | 7 | 0.5525 | 44200 | 0.22837 | 8221.32 | 0.7673 | 9207.6 | 1 | 5000 | 8221.32 | 9207.6 | 0 | 0 | 0 | 0 | 21771.08 | 0 | 0 | 0 | 0 | 0 | 21771.08
2022012913 | 7 | 0.52336 | 41868.8 | 0.27962 | 10066.32 | 0.70289 | 8434.68 | 1 | 5000 | 10066.32 | 8434.68 | 0 | 0 | 0 | 0 | 18367.8 | 0 | 0 | 0 | 0 | 0 | 18367.8
2022012914 | 7 | 0.4994 | 39952 | 0.27693 | 9969.48 | 0.68189 | 8182.68 | 1 | 5000 | 9969.48 | 8182.68 | 0 | 0 | 0 | 0 | 16799.84 | 0 | 0 | 0 | 0 | 0 | 16799.84
2022012915 | 7 | 0.48333 | 38666.4 | 0.24737 | 8905.32 | 0.75177 | 9021.24 | 1 | 5000 | 8905.32 | 9021.24 | 0 | 0 | 0 | 0 | 15739.84 | 0 | 0 | 0 | 0 | 0 | 15739.84
2022012916 | 7 | 0.47545 | 38036 | 0.23359 | 8409.24 | 0.80283 | 9633.96 | 1 | 5000 | 8409.24 | 9633.96 | 0 | 0 | 0 | 0 | 14992.8 | 0 | 0 | 0 | 0 | 0 | 14992.8
2022012917 | 7 | 0.475 | 38000 | 0.22237 | 8005.32 | 0.71389 | 8566.68 | 1 | 5000 | 8005.32 | 8566.68 | 0 | 0 | 0 | 0 | 16428 | 0 | 0 | 0 | 0 | 0 | 16428
2022012918 | 7 | 0.48446 | 38756.8 | 0.20843 | 7503.48 | 0.26767 | 3212.04 | 1 | 5000 | 7503.48 | 3212.04 | 0 | 0 | 0 | 0 | 23041.28 | 0 | 0 | 0 | 0 | 0 | 23041.28
2022012919 | 7 | 0.51236 | 40988.8 | 0.2223 | 8002.8 | 0.00564 | 67.68 | 1 | 5000 | 8002.8 | 67.68 | 0 | 0 | 0 | 0 | 27918.32 | 0 | 0 | 0 | 0 | 0 | 27918.32
2022012920 | 7 | 0.52211 | 41768.8 | 0.2681 | 9651.6 | 0 | 0 | 1 | 5000 | 9651.6 | 0 | 0 | 0 | 0 | 0 | 27117.2 | 0 | 0 | 0 | 0 | 0 | 27117.2
2022012921 | 7 | 0.52646 | 42116.8 | 0.34554 | 12439.44 | 0 | 0 | 1 | 5000 | 12439.44 | 0 | 0 | 0 | 0 | 0 | 24677.36 | 0 | 0 | 0 | 0 | 0 | 24677.36
2022012922 | 7 | 0.52778 | 42222.4 | 0.46408 | 16706.88 | 0 | 0 | 1 | 5000 | 16706.88 | 0 | 0 | 0 | 0 | 0 | 20515.52 | 0 | 0 | 0 | 0 | 0 | 20515.52
2022012923 | 7 | 0.52253 | 41802.4 | 0.50149 | 18053.64 | 0 | 0 | 1 | 5000 | 18053.64 | 0 | 0 | 0 | 0 | 0 | 18748.76 | 0 | 0 | 0 | 0 | 0 | 18748.76
2022012924 | 7 | 0.51369 | 41095.2 | 0.51094 | 18393.84 | 0 | 0 | 1 | 5000 | 18393.84 | 0 | 0 | 0 | 0 | 0 | 17701.36 | 0 | 0 | 0 | 0 | 0 | 17701.36
2022013001 | 1 | 0.50758 | 40606.4 | 0.51636 | 18588.96 | 0 | 0 | 1 | 5000 | 18588.96 | 0 | 0 | 0 | 0 | 0 | 17017.44 | 0 | 0 | 0 | 0 | 0 | 17017.44
2022013002 | 1 | 0.5042 | 40336 | 0.51619 | 18582.84 | 0 | 0 | 1 | 5000 | 18582.84 | 0 | 0 | 0 | 0 | 0 | 16753.16 | 0 | 0 | 0 | 0 | 0 | 16753.16
2022013003 | 1 | 0.50797 | 40637.6 | 0.50739 | 18266.04 | 0 | 0 | 1 | 5000 | 18266.04 | 0 | 0 | 0 | 0 | 0 | 17371.56 | 0 | 0 | 0 | 0 | 0 | 17371.56
2022013004 | 1 | 0.51458 | 41166.4 | 0.49953 | 17983.08 | 0 | 0 | 1 | 5000 | 17983.08 | 0 | 0 | 0 | 0 | 0 | 18183.32 | 0 | 0 | 0 | 0 | 0 | 18183.32
2022013005 | 1 | 0.52392 | 41913.6 | 0.46304 | 16669.44 | 0 | 0 | 1 | 5000 | 16669.44 | 0 | 0 | 0 | 0 | 0 | 20244.16 | 0 | 0 | 0 | 0 | 0 | 20244.16
2022013006 | 1 | 0.53756 | 43004.8 | 0.38512 | 13864.32 | 0 | 0 | 1 | 5000 | 13864.32 | 0 | 0 | 0 | 0 | 0 | 24140.48 | 0 | 0 | 0 | 0 | 0 | 24140.48
2022013007 | 1 | 0.55951 | 44760.8 | 0.34306 | 12350.16 | 0 | 0 | 1 | 5000 | 12350.16 | 0 | 0 | 0 | 0 | 0 | 27410.64 | 0 | 0 | 0 | 0 | 0 | 27410.64
2022013008 | 1 | 0.58125 | 46500 | 0.30842 | 11103.12 | 0.01223 | 146.76 | 1 | 5000 | 11103.12 | 146.76 | 0 | 0 | 0 | 0 | 30250.12 | 0 | 0 | 0 | 0 | 0 | 30250.12
2022013009 | 1 | 0.58041 | 46432.8 | 0.25684 | 9246.24 | 0.31483 | 3777.96 | 1 | 5000 | 9246.24 | 3777.96 | 0 | 0 | 0 | 0 | 28408.6 | 0 | 0 | 0 | 0 | 0 | 28408.6
2022013010 | 1 | 0.55679 | 44543.2 | 0.14961 | 5385.96 | 0.70431 | 8451.72 | 1 | 5000 | 5385.96 | 8451.72 | 0 | 0 | 0 | 0 | 25705.52 | 0 | 0 | 0 | 0 | 0 | 25705.52
2022013011 | 1 | 0.5291 | 42328 | 0.12075 | 4347 | 0.76321 | 9158.52 | 1 | 5000 | 4347 | 9158.52 | 0 | 0 | 0 | 0 | 23822.48 | 0 | 0 | 0 | 0 | 0 | 23822.48
2022013012 | 1 | 0.50637 | 40509.6 | 0.14632 | 5267.52 | 0.73556 | 8826.72 | 1 | 5000 | 5267.52 | 8826.72 | 0 | 0 | 0 | 0 | 21415.36 | 0 | 0 | 0 | 0 | 0 | 21415.36
2022013013 | 1 | 0.48994 | 39195.2 | 0.14235 | 5124.6 | 0.70177 | 8421.24 | 1 | 5000 | 5124.6 | 8421.24 | 0 | 0 | 0 | 0 | 20649.36 | 0 | 0 | 0 | 0 | 0 | 20649.36
2022013014 | 1 | 0.47811 | 38248.8 | 0.17206 | 6194.16 | 0.70158 | 8418.96 | 1 | 5000 | 6194.16 | 8418.96 | 0 | 0 | 0 | 0 | 18635.68 | 0 | 0 | 0 | 0 | 0 | 18635.68
2022013015 | 1 | 0.47143 | 37714.4 | 0.20098 | 7235.28 | 0.65211 | 7825.32 | 1 | 5000 | 7235.28 | 7825.32 | 0 | 0 | 0 | 0 | 17653.8 | 0 | 0 | 0 | 0 | 0 | 17653.8
2022013016 | 1 | 0.46907 | 37525.6 | 0.21299 | 7667.64 | 0.55507 | 6660.84 | 1 | 5000 | 7667.64 | 6660.84 | 0 | 0 | 0 | 0 | 18197.12 | 0 | 0 | 0 | 0 | 0 | 18197.12
2022013017 | 1 | 0.47118 | 37694.4 | 0.20133 | 7247.88 | 0.4527 | 5432.4 | 1 | 5000 | 7247.88 | 5432.4 | 0 | 0 | 0 | 0 | 20014.12 | 0 | 0 | 0 | 0 | 0 | 20014.12
2022013018 | 1 | 0.4856 | 38848 | 0.19753 | 7111.08 | 0.13084 | 1570.08 | 1 | 5000 | 7111.08 | 1570.08 | 0 | 0 | 0 | 0 | 25166.84 | 0 | 0 | 0 | 0 | 0 | 25166.84
2022013019 | 1 | 0.51179 | 40943.2 | 0.23319 | 8394.84 | 0.00234 | 28.08 | 1 | 5000 | 8394.84 | 28.08 | 0 | 0 | 0 | 0 | 27520.28 | 0 | 0 | 0 | 0 | 0 | 27520.28
2022013020 | 1 | 0.51891 | 41512.8 | 0.29153 | 10495.08 | 0 | 0 | 1 | 5000 | 10495.08 | 0 | 0 | 0 | 0 | 0 | 26017.72 | 0 | 0 | 0 | 0 | 0 | 26017.72
2022013021 | 1 | 0.51246 | 40996.8 | 0.31331 | 11279.16 | 0 | 0 | 1 | 5000 | 11279.16 | 0 | 0 | 0 | 0 | 0 | 24717.64 | 0 | 0 | 0 | 0 | 0 | 24717.64
2022013022 | 1 | 0.50413 | 40330.4 | 0.305 | 10980 | 0 | 0 | 1 | 5000 | 10980 | 0 | 0 | 0 | 0 | 0 | 24350.4 | 0 | 0 | 0 | 0 | 0 | 24350.4
2022013023 | 1 | 0.48175 | 38540 | 0.30065 | 10823.4 | 0 | 0 | 1 | 5000 | 10823.4 | 0 | 0 | 0 | 0 | 0 | 22716.6 | 0 | 0 | 0 | 0 | 0 | 22716.6
2022013024 | 1 | 0.45946 | 36756.8 | 0.33726 | 12141.36 | 0 | 0 | 1 | 5000 | 12141.36 | 0 | 0 | 0 | 0 | 0 | 19615.44 | 0 | 0 | 0 | 0 | 0 | 19615.44
2022013101 | 2 | 0.44404 | 35523.2 | 0.39855 | 14347.8 | 0 | 0 | 1 | 5000 | 14347.8 | 0 | 0 | 0 | 0 | 0 | 16175.4 | 0 | 0 | 0 | 0 | 0 | 16175.4
2022013102 | 2 | 0.43733 | 34986.4 | 0.42247 | 15208.92 | 0 | 0 | 1 | 5000 | 15208.92 | 0 | 0 | 0 | 0 | 0 | 14777.48 | 0 | 0 | 0 | 0 | 0 | 14777.48
2022013103 | 2 | 0.43492 | 34793.6 | 0.40565 | 14603.4 | 0 | 0 | 1 | 5000 | 14603.4 | 0 | 0 | 0 | 0 | 0 | 15190.2 | 0 | 0 | 0 | 0 | 0 | 15190.2
2022013104 | 2 | 0.43883 | 35106.4 | 0.36518 | 13146.48 | 0 | 0 | 1 | 5000 | 13146.48 | 0 | 0 | 0 | 0 | 0 | 16959.92 | 0 | 0 | 0 | 0 | 0 | 16959.92
2022013105 | 2 | 0.45145 | 36116 | 0.32195 | 11590.2 | 0 | 0 | 1 | 5000 | 11590.2 | 0 | 0 | 0 | 0 | 0 | 19525.8 | 0 | 0 | 0 | 0 | 0 | 19525.8
2022013106 | 2 | 0.48077 | 38461.6 | 0.30303 | 10909.08 | 0 | 0 | 1 | 5000 | 10909.08 | 0 | 0 | 0 | 0 | 0 | 22552.52 | 0 | 0 | 0 | 0 | 0 | 22552.52
2022013107 | 2 | 0.52365 | 41892 | 0.23968 | 8628.48 | 0 | 0 | 1 | 5000 | 8628.48 | 0 | 0 | 0 | 0 | 0 | 28263.52 | 0 | 0 | 0 | 0 | 0 | 28263.52
2022013108 | 2 | 0.5454 | 43632 | 0.19739 | 7106.04 | 0.00394 | 47.28 | 1 | 5000 | 7106.04 | 47.28 | 0 | 0 | 0 | 0 | 31478.68 | 0 | 0 | 0 | 0 | 0 | 31478.68
2022013109 | 2 | 0.54123 | 43298.4 | 0.14881 | 5357.16 | 0.1568 | 1881.6 | 1 | 5000 | 5357.16 | 1881.6 | 0 | 0 | 0 | 0 | 31059.64 | 0 | 0 | 0 | 0 | 0 | 31059.64
2022013110 | 2 | 0.53787 | 43029.6 | 0.10081 | 3629.16 | 0.41411 | 4969.32 | 1 | 5000 | 3629.16 | 4969.32 | 0 | 0 | 0 | 0 | 29431.12 | 0 | 0 | 0 | 0 | 0 | 29431.12
2022013111 | 2 | 0.53297 | 42637.6 | 0.08637 | 3109.32 | 0.50965 | 6115.8 | 1 | 5000 | 3109.32 | 6115.8 | 0 | 0 | 0 | 0 | 28412.48 | 0 | 0 | 0 | 0 | 0 | 28412.48
2022013112 | 2 | 0.52791 | 42232.8 | 0.11905 | 4285.8 | 0.59142 | 7097.04 | 1 | 5000 | 4285.8 | 7097.04 | 0 | 0 | 0 | 0 | 25849.96 | 0 | 0 | 0 | 0 | 0 | 25849.96
2022013113 | 2 | 0.52489 | 41991.2 | 0.14184 | 5106.24 | 0.62333 | 7479.96 | 1 | 5000 | 5106.24 | 7479.96 | 0 | 0 | 0 | 0 | 24405 | 0 | 0 | 0 | 0 | 0 | 24405
2022013114 | 2 | 0.52272 | 41817.6 | 0.15231 | 5483.16 | 0.62687 | 7522.44 | 1 | 5000 | 5483.16 | 7522.44 | 0 | 0 | 0 | 0 | 23812 | 0 | 0 | 0 | 0 | 0 | 23812
2022013115 | 2 | 0.51736 | 41388.8 | 0.19375 | 6975 | 0.65806 | 7896.72 | 1 | 5000 | 6975 | 7896.72 | 0 | 0 | 0 | 0 | 21517.08 | 0 | 0 | 0 | 0 | 0 | 21517.08
2022013116 | 2 | 0.51529 | 41223.2 | 0.21559 | 7761.24 | 0.64636 | 7756.32 | 1 | 5000 | 7761.24 | 7756.32 | 0 | 0 | 0 | 0 | 20705.64 | 0 | 0 | 0 | 0 | 0 | 20705.64
2022013117 | 2 | 0.51942 | 41553.6 | 0.21707 | 7814.52 | 0.59026 | 7083.12 | 1 | 5000 | 7814.52 | 7083.12 | 0 | 0 | 0 | 0 | 21655.96 | 0 | 0 | 0 | 0 | 0 | 21655.96
2022013118 | 2 | 0.52955 | 42364 | 0.2079 | 7484.4 | 0.26025 | 3123 | 1 | 5000 | 7484.4 | 3123 | 0 | 0 | 0 | 0 | 26756.6 | 0 | 0 | 0 | 0 | 0 | 26756.6
2022013119 | 2 | 0.54715 | 43772 | 0.25246 | 9088.56 | 0.00635 | 76.2 | 1 | 5000 | 9088.56 | 76.2 | 0 | 0 | 0 | 0 | 29607.24 | 0 | 0 | 0 | 0 | 0 | 29607.24
2022013120 | 2 | 0.5468 | 43744 | 0.3643 | 13114.8 | 0 | 0 | 1 | 5000 | 13114.8 | 0 | 0 | 0 | 0 | 0 | 25629.2 | 0 | 0 | 0 | 0 | 0 | 25629.2
2022013121 | 2 | 0.53841 | 43072.8 | 0.42942 | 15459.12 | 0 | 0 | 1 | 5000 | 15459.12 | 0 | 0 | 0 | 0 | 0 | 22613.68 | 0 | 0 | 0 | 0 | 0 | 22613.68
2022013122 | 2 | 0.5196 | 41568 | 0.43758 | 15752.88 | 0 | 0 | 1 | 5000 | 15752.88 | 0 | 0 | 0 | 0 | 0 | 20815.12 | 0 | 0 | 0 | 0 | 0 | 20815.12
2022013123 | 2 | 0.49115 | 39292 | 0.43141 | 15530.76 | 0 | 0 | 1 | 5000 | 15530.76 | 0 | 0 | 0 | 0 | 0 | 18761.24 | 0 | 0 | 0 | 0 | 0 | 18761.24
2022013124 | 2 | 0.46493 | 37194.4 | 0.42674 | 15362.64 | 0 | 0 | 1 | 5000 | 15362.64 | 0 | 0 | 0 | 0 | 0 | 16831.76 | 0 | 0 | 0 | 0 | 0 | 16831.76
2022020101 | 3 | 0.44689 | 35751.2 | 0.42076 | 15147.36 | 0 | 0 | 1 | 5000 | 15147.36 | 0 | 0 | 0 | 0 | 0 | 15603.84 | 0 | 0 | 0 | 0 | 0 | 15603.84
2022020102 | 3 | 0.43492 | 34793.6 | 0.4054 | 14594.4 | 0 | 0 | 1 | 5000 | 14594.4 | 0 | 0 | 0 | 0 | 0 | 15199.2 | 0 | 0 | 0 | 0 | 0 | 15199.2
2022020103 | 3 | 0.43147 | 34517.6 | 0.39675 | 14283 | 0 | 0 | 1 | 5000 | 14283 | 0 | 0 | 0 | 0 | 0 | 15234.6 | 0 | 0 | 0 | 0 | 0 | 15234.6
2022020104 | 3 | 0.43184 | 34547.2 | 0.39322 | 14155.92 | 0 | 0 | 1 | 5000 | 14155.92 | 0 | 0 | 0 | 0 | 0 | 15391.28 | 0 | 0 | 0 | 0 | 0 | 15391.28
2022020105 | 3 | 0.44046 | 35236.8 | 0.3874 | 13946.4 | 0 | 0 | 1 | 5000 | 13946.4 | 0 | 0 | 0 | 0 | 0 | 16290.4 | 0 | 0 | 0 | 0 | 0 | 16290.4
2022020106 | 3 | 0.46646 | 37316.8 | 0.38949 | 14021.64 | 0 | 0 | 1 | 5000 | 14021.64 | 0 | 0 | 0 | 0 | 0 | 18295.16 | 0 | 0 | 0 | 0 | 0 | 18295.16
2022020107 | 3 | 0.50606 | 40484.8 | 0.40644 | 14631.84 | 0 | 0 | 1 | 5000 | 14631.84 | 0 | 0 | 0 | 0 | 0 | 20852.96 | 0 | 0 | 0 | 0 | 0 | 20852.96
2022020108 | 3 | 0.52514 | 42011.2 | 0.41174 | 14822.64 | 0.00213 | 25.56 | 1 | 5000 | 14822.64 | 25.56 | 0 | 0 | 0 | 0 | 22163 | 0 | 0 | 0 | 0 | 0 | 22163
2022020109 | 3 | 0.52433 | 41946.4 | 0.39023 | 14048.28 | 0.08536 | 1024.32 | 1 | 5000 | 14048.28 | 1024.32 | 0 | 0 | 0 | 0 | 21873.8 | 0 | 0 | 0 | 0 | 0 | 21873.8
2022020110 | 3 | 0.52436 | 41948.8 | 0.35483 | 12773.88 | 0.23478 | 2817.36 | 1 | 5000 | 12773.88 | 2817.36 | 0 | 0 | 0 | 0 | 21357.56 | 0 | 0 | 0 | 0 | 0 | 21357.56
2022020111 | 3 | 0.52033 | 41626.4 | 0.32041 | 11534.76 | 0.31844 | 3821.28 | 1 | 5000 | 11534.76 | 3821.28 | 0 | 0 | 0 | 0 | 21270.36 | 0 | 0 | 0 | 0 | 0 | 21270.36
2022020112 | 3 | 0.51329 | 41063.2 | 0.28751 | 10350.36 | 0.40246 | 4829.52 | 1 | 5000 | 10350.36 | 4829.52 | 0 | 0 | 0 | 0 | 20883.32 | 0 | 0 | 0 | 0 | 0 | 20883.32
2022020113 | 3 | 0.50756 | 40604.8 | 0.25192 | 9069.12 | 0.49158 | 5898.96 | 1 | 5000 | 9069.12 | 5898.96 | 0 | 0 | 0 | 0 | 20636.72 | 0 | 0 | 0 | 0 | 0 | 20636.72
2022020114 | 3 | 0.50254 | 40203.2 | 0.21085 | 7590.6 | 0.55051 | 6606.12 | 1 | 5000 | 7590.6 | 6606.12 | 0 | 0 | 0 | 0 | 21006.48 | 0 | 0 | 0 | 0 | 0 | 21006.48
2022020115 | 3 | 0.49906 | 39924.8 | 0.18126 | 6525.36 | 0.63268 | 7592.16 | 1 | 5000 | 6525.36 | 7592.16 | 0 | 0 | 0 | 0 | 20807.28 | 0 | 0 | 0 | 0 | 0 | 20807.28
2022020116 | 3 | 0.49641 | 39712.8 | 0.18457 | 6644.52 | 0.54777 | 6573.24 | 1 | 5000 | 6644.52 | 6573.24 | 0 | 0 | 0 | 0 | 21495.04 | 0 | 0 | 0 | 0 | 0 | 21495.04
2022020117 | 3 | 0.49885 | 39908 | 0.19228 | 6922.08 | 0.47063 | 5647.56 | 1 | 5000 | 6922.08 | 5647.56 | 0 | 0 | 0 | 0 | 22338.36 | 0 | 0 | 0 | 0 | 0 | 22338.36
2022020118 | 3 | 0.50733 | 40586.4 | 0.19442 | 6999.12 | 0.18337 | 2200.44 | 1 | 5000 | 6999.12 | 2200.44 | 0 | 0 | 0 | 0 | 26386.84 | 0 | 0 | 0 | 0 | 0 | 26386.84
2022020119 | 3 | 0.52642 | 42113.6 | 0.23456 | 8444.16 | 0.00196 | 23.52 | 1 | 5000 | 8444.16 | 23.52 | 0 | 0 | 0 | 0 | 28645.92 | 0 | 0 | 0 | 0 | 0 | 28645.92
2022020120 | 3 | 0.52914 | 42331.2 | 0.32405 | 11665.8 | 6e-05 | 0.72 | 1 | 5000 | 11665.8 | 0.72 | 0 | 0 | 0 | 0 | 25664.68 | 0 | 0 | 0 | 0 | 0 | 25664.68
2022020121 | 3 | 0.52087 | 41669.6 | 0.3893 | 14014.8 | 6e-05 | 0.72 | 1 | 5000 | 14014.8 | 0.72 | 0 | 0 | 0 | 0 | 22654.08 | 0 | 0 | 0 | 0 | 0 | 22654.08
2022020122 | 3 | 0.50522 | 40417.6 | 0.42343 | 15243.48 | 6e-05 | 0.72 | 1 | 5000 | 15243.48 | 0.72 | 0 | 0 | 0 | 0 | 20173.4 | 0 | 0 | 0 | 0 | 0 | 20173.4
2022020123 | 3 | 0.48061 | 38448.8 | 0.45722 | 16459.92 | 6e-05 | 0.72 | 1 | 5000 | 16459.92 | 0.72 | 0 | 0 | 0 | 0 | 16988.16 | 0 | 0 | 0 | 0 | 0 | 16988.16
2022020124 | 3 | 0.45598 | 36478.4 | 0.44595 | 16054.2 | 0 | 0 | 1 | 5000 | 16054.2 | 0 | 0 | 0 | 0 | 0 | 15424.2 | 0 | 0 | 0 | 0 | 0 | 15424.2
2022020201 | 4 | 0.43828 | 35062.4 | 0.43453 | 15643.08 | 0 | 0 | 1 | 5000 | 15643.08 | 0 | 0 | 0 | 0 | 0 | 14419.32 | 0 | 0 | 0 | 0 | 0 | 14419.32
2022020202 | 4 | 0.42815 | 34252 | 0.42775 | 15399 | 0 | 0 | 1 | 5000 | 15399 | 0 | 0 | 0 | 0 | 0 | 13853 | 0 | 0 | 0 | 0 | 0 | 13853
2022020203 | 4 | 0.42465 | 33972 | 0.42621 | 15343.56 | 0 | 0 | 1 | 5000 | 15343.56 | 0 | 0 | 0 | 0 | 0 | 13628.44 | 0 | 0 | 0 | 0 | 0 | 13628.44
2022020204 | 4 | 0.42516 | 34012.8 | 0.42518 | 15306.48 | 0 | 0 | 1 | 5000 | 15306.48 | 0 | 0 | 0 | 0 | 0 | 13706.32 | 0 | 0 | 0 | 0 | 0 | 13706.32
2022020205 | 4 | 0.43653 | 34922.4 | 0.43945 | 15820.2 | 0 | 0 | 1 | 5000 | 15820.2 | 0 | 0 | 0 | 0 | 0 | 14102.2 | 0 | 0 | 0 | 0 | 0 | 14102.2
2022020206 | 4 | 0.46518 | 37214.4 | 0.48089 | 17312.04 | 0 | 0 | 1 | 5000 | 17312.04 | 0 | 0 | 0 | 0 | 0 | 14902.36 | 0 | 0 | 0 | 0 | 0 | 14902.36
2022020207 | 4 | 0.5089 | 40712 | 0.51682 | 18605.52 | 0 | 0 | 1 | 5000 | 18605.52 | 0 | 0 | 0 | 0 | 0 | 17106.48 | 0 | 0 | 0 | 0 | 0 | 17106.48
2022020208 | 4 | 0.53486 | 42788.8 | 0.54148 | 19493.28 | 0.00104 | 12.48 | 1 | 5000 | 19493.28 | 12.48 | 0 | 0 | 0 | 0 | 18283.04 | 0 | 0 | 0 | 0 | 0 | 18283.04
2022020209 | 4 | 0.54297 | 43437.6 | 0.53648 | 19313.28 | 0.01074 | 128.88 | 1 | 5000 | 19313.28 | 128.88 | 0 | 0 | 0 | 0 | 18995.44 | 0 | 0 | 0 | 0 | 0 | 18995.44
2022020210 | 4 | 0.55145 | 44116 | 0.54612 | 19660.32 | 0.03143 | 377.16 | 1 | 5000 | 19660.32 | 377.16 | 0 | 0 | 0 | 0 | 19078.52 | 0 | 0 | 0 | 0 | 0 | 19078.52
2022020211 | 4 | 0.56059 | 44847.2 | 0.55174 | 19862.64 | 0.079 | 948 | 1 | 5000 | 19862.64 | 948 | 0 | 0 | 0 | 0 | 19036.56 | 0 | 0 | 0 | 0 | 0 | 19036.56
2022020212 | 4 | 0.56722 | 45377.6 | 0.51584 | 18570.24 | 0.12801 | 1536.12 | 1 | 5000 | 18570.24 | 1536.12 | 0 | 0 | 0 | 0 | 20271.24 | 0 | 0 | 0 | 0 | 0 | 20271.24
2022020213 | 4 | 0.57384 | 45907.2 | 0.50544 | 18195.84 | 0.16296 | 1955.52 | 1 | 5000 | 18195.84 | 1955.52 | 0 | 0 | 0 | 0 | 20755.84 | 0 | 0 | 0 | 0 | 0 | 20755.84
2022020214 | 4 | 0.57933 | 46346.4 | 0.50915 | 18329.4 | 0.1801 | 2161.2 | 1 | 5000 | 18329.4 | 2161.2 | 0 | 0 | 0 | 0 | 20855.8 | 0 | 0 | 0 | 0 | 0 | 20855.8
2022020215 | 4 | 0.58183 | 46546.4 | 0.49982 | 17993.52 | 0.15715 | 1885.8 | 1 | 5000 | 17993.52 | 1885.8 | 0 | 0 | 0 | 0 | 21667.08 | 0 | 0 | 0 | 0 | 0 | 21667.08
2022020216 | 4 | 0.58713 | 46970.4 | 0.4944 | 17798.4 | 0.10392 | 1247.04 | 1 | 5000 | 17798.4 | 1247.04 | 0 | 0 | 0 | 0 | 22924.96 | 0 | 0 | 0 | 0 | 0 | 22924.96
2022020217 | 4 | 0.60367 | 48293.6 | 0.49908 | 17966.88 | 0.05785 | 694.2 | 1 | 5000 | 17966.88 | 694.2 | 0 | 0 | 0 | 0 | 24632.52 | 0 | 0 | 0 | 0 | 0 | 24632.52
2022020218 | 4 | 0.62933 | 50346.4 | 0.49169 | 17700.84 | 0.0147 | 176.4 | 1 | 5000 | 17700.84 | 176.4 | 0 | 0 | 0 | 0 | 27469.16 | 0 | 0 | 0 | 0 | 0 | 27469.16
2022020219 | 4 | 0.65293 | 52234.4 | 0.4919 | 17708.4 | 0.00013 | 1.56 | 1 | 5000 | 17708.4 | 1.56 | 0 | 0 | 0 | 0 | 29524.44 | 0 | 0 | 0 | 0 | 0 | 29524.44
2022020220 | 4 | 0.65787 | 52629.6 | 0.50331 | 18119.16 | 0 | 0 | 1 | 5000 | 18119.16 | 0 | 0 | 0 | 0 | 0 | 29510.44 | 0 | 0 | 0 | 0 | 0 | 29510.44
2022020221 | 4 | 0.65401 | 52320.8 | 0.50297 | 18106.92 | 0 | 0 | 1 | 5000 | 18106.92 | 0 | 0 | 0 | 0 | 0 | 29213.88 | 0 | 0 | 0 | 0 | 0 | 29213.88
2022020222 | 4 | 0.64459 | 51567.2 | 0.50226 | 18081.36 | 0 | 0 | 1 | 5000 | 18081.36 | 0 | 0 | 0 | 0 | 0 | 28485.84 | 0 | 0 | 0 | 0 | 0 | 28485.84
2022020223 | 4 | 0.62549 | 50039.2 | 0.50631 | 18227.16 | 0 | 0 | 1 | 5000 | 18227.16 | 0 | 0 | 0 | 0 | 0 | 26812.04 | 0 | 0 | 0 | 0 | 0 | 26812.04
2022020224 | 4 | 0.60616 | 48492.8 | 0.50774 | 18278.64 | 0 | 0 | 1 | 5000 | 18278.64 | 0 | 0 | 0 | 0 | 0 | 25214.16 | 0 | 0 | 0 | 0 | 0 | 25214.16
2022020301 | 5 | 0.59344 | 47475.2 | 0.49973 | 17990.28 | 0 | 0 | 1 | 5000 | 17990.28 | 0 | 0 | 0 | 0 | 0 | 24484.92 | 0 | 0 | 0 | 0 | 0 | 24484.92
2022020302 | 5 | 0.592 | 47360 | 0.48533 | 17471.88 | 0 | 0 | 1 | 5000 | 17471.88 | 0 | 0 | 0 | 0 | 0 | 24888.12 | 0 | 0 | 0 | 0 | 0 | 24888.12
2022020303 | 5 | 0.60021 | 48016.8 | 0.5036 | 18129.6 | 0 | 0 | 1 | 5000 | 18129.6 | 0 | 0 | 0 | 0 | 0 | 24887.2 | 0 | 0 | 0 | 0 | 0 | 24887.2
2022020304 | 5 | 0.61454 | 49163.2 | 0.5298 | 19072.8 | 0 | 0 | 1 | 5000 | 19072.8 | 0 | 0 | 0 | 0 | 0 | 25090.4 | 0 | 0 | 0 | 0 | 0 | 25090.4
2022020305 | 5 | 0.63467 | 50773.6 | 0.53851 | 19386.36 | 0 | 0 | 1 | 5000 | 19386.36 | 0 | 0 | 0 | 0 | 0 | 26387.24 | 0 | 0 | 0 | 0 | 0 | 26387.24
2022020306 | 5 | 0.66578 | 53262.4 | 0.53875 | 19395 | 0 | 0 | 1 | 5000 | 19395 | 0 | 0 | 0 | 0 | 0 | 28867.4 | 0 | 0 | 0 | 0 | 0 | 28867.4
2022020307 | 5 | 0.70634 | 56507.2 | 0.53668 | 19320.48 | 0 | 0 | 1 | 5000 | 19320.48 | 0 | 0 | 0 | 0 | 0 | 32186.72 | 0 | 0 | 0 | 0 | 0 | 32186.72
2022020308 | 5 | 0.73775 | 59020 | 0.52419 | 18870.84 | 0.00101 | 12.12 | 1 | 5000 | 18870.84 | 12.12 | 0 | 0 | 0 | 0 | 35137.04 | 0 | 0 | 0 | 0 | 0 | 35137.04
2022020309 | 5 | 0.75723 | 60578.4 | 0.50264 | 18095.04 | 0.04024 | 482.88 | 1 | 5000 | 18095.04 | 482.88 | 0 | 0 | 0 | 0 | 37000.48 | 0 | 0 | 0 | 0 | 0 | 37000.48
2022020310 | 5 | 0.7778 | 62224 | 0.50196 | 18070.56 | 0.1278 | 1533.6 | 1 | 5000 | 18070.56 | 1533.6 | 0 | 0 | 0 | 0 | 37619.84 | 0 | 0 | 0 | 0 | 0 | 37619.84
2022020311 | 5 | 0.79275 | 63420 | 0.5051 | 18183.6 | 0.23704 | 2844.48 | 1 | 5000 | 18183.6 | 2844.48 | 0 | 0 | 0 | 0 | 37391.92 | 0 | 0 | 0 | 0 | 0 | 37391.92
2022020312 | 5 | 0.80065 | 64052 | 0.49979 | 17992.44 | 0.33381 | 4005.72 | 1 | 5000 | 17992.44 | 4005.72 | 0 | 0 | 0 | 0 | 37053.84 | 0 | 0 | 0 | 0 | 0 | 37053.84
2022020313 | 5 | 0.80239 | 64191.2 | 0.50342 | 18123.12 | 0.36217 | 4346.04 | 1 | 5000 | 18123.12 | 4346.04 | 0 | 0 | 0 | 0 | 36722.04 | 0 | 0 | 0 | 0 | 0 | 36722.04
2022020314 | 5 | 0.80062 | 64049.6 | 0.51039 | 18374.04 | 0.37449 | 4493.88 | 1 | 5000 | 18374.04 | 4493.88 | 0 | 0 | 0 | 0 | 36181.68 | 0 | 0 | 0 | 0 | 0 | 36181.68
2022020315 | 5 | 0.79794 | 63835.2 | 0.51028 | 18370.08 | 0.33906 | 4068.72 | 1 | 5000 | 18370.08 | 4068.72 | 0 | 0 | 0 | 0 | 36396.4 | 0 | 0 | 0 | 0 | 0 | 36396.4
2022020316 | 5 | 0.80031 | 64024.8 | 0.50179 | 18064.44 | 0.32035 | 3844.2 | 1 | 5000 | 18064.44 | 3844.2 | 0 | 0 | 0 | 0 | 37116.16 | 0 | 0 | 0 | 0 | 0 | 37116.16
2022020317 | 5 | 0.80996 | 64796.8 | 0.482 | 17352 | 0.3004 | 3604.8 | 1 | 5000 | 17352 | 3604.8 | 0 | 0 | 0 | 0 | 38840 | 0 | 0 | 0 | 0 | 0 | 38840
2022020318 | 5 | 0.82784 | 66227.2 | 0.45728 | 16462.08 | 0.16103 | 1932.36 | 1 | 5000 | 16462.08 | 1932.36 | 0 | 0 | 0 | 0 | 42832.76 | 0 | 0 | 0 | 0 | 0 | 42832.76
2022020319 | 5 | 0.85002 | 68001.6 | 0.43146 | 15532.56 | 0.00651 | 78.12 | 1 | 5000 | 15532.56 | 78.12 | 0 | 0 | 0 | 0 | 47390.92 | 0 | 0 | 0 | 0 | 0 | 47390.92
2022020320 | 5 | 0.84989 | 67991.2 | 0.42691 | 15368.76 | 6e-05 | 0.72 | 1 | 5000 | 15368.76 | 0.72 | 0 | 0 | 0 | 0 | 47621.72 | 0 | 0 | 0 | 0 | 0 | 47621.72
2022020321 | 5 | 0.84311 | 67448.8 | 0.43076 | 15507.36 | 0 | 0 | 1 | 5000 | 15507.36 | 0 | 0 | 0 | 0 | 0 | 46941.44 | 0 | 0 | 0 | 0 | 0 | 46941.44
2022020322 | 5 | 0.82964 | 66371.2 | 0.44502 | 16020.72 | 0 | 0 | 1 | 5000 | 16020.72 | 0 | 0 | 0 | 0 | 0 | 45350.48 | 0 | 0 | 0 | 0 | 0 | 45350.48
2022020323 | 5 | 0.80757 | 64605.6 | 0.45951 | 16542.36 | 0 | 0 | 1 | 5000 | 16542.36 | 0 | 0 | 0 | 0 | 0 | 43063.24 | 0 | 0 | 0 | 0 | 0 | 43063.24
2022020324 | 5 | 0.79074 | 63259.2 | 0.46754 | 16831.44 | 0 | 0 | 1 | 5000 | 16831.44 | 0 | 0 | 0 | 0 | 0 | 41427.76 | 0 | 0 | 0 | 0 | 0 | 41427.76
2022020401 | 6 | 0.77975 | 62380 | 0.47113 | 16960.68 | 0 | 0 | 1 | 5000 | 16960.68 | 0 | 0 | 0 | 0 | 0 | 40419.32 | 0 | 0 | 0 | 0 | 0 | 40419.32
2022020402 | 6 | 0.77547 | 62037.6 | 0.46188 | 16627.68 | 0 | 0 | 1 | 5000 | 16627.68 | 0 | 0 | 0 | 0 | 0 | 40409.92 | 0 | 0 | 0 | 0 | 0 | 40409.92
2022020403 | 6 | 0.77532 | 62025.6 | 0.42779 | 15400.44 | 0 | 0 | 1 | 5000 | 15400.44 | 0 | 0 | 0 | 0 | 0 | 41625.16 | 0 | 0 | 0 | 0 | 0 | 41625.16
2022020404 | 6 | 0.77757 | 62205.6 | 0.39545 | 14236.2 | 0 | 0 | 1 | 5000 | 14236.2 | 0 | 0 | 0 | 0 | 0 | 42969.4 | 0 | 0 | 0 | 0 | 0 | 42969.4
2022020405 | 6 | 0.78604 | 62883.2 | 0.39044 | 14055.84 | 0 | 0 | 1 | 5000 | 14055.84 | 0 | 0 | 0 | 0 | 0 | 43827.36 | 0 | 0 | 0 | 0 | 0 | 43827.36
2022020406 | 6 | 0.8053 | 64424 | 0.37933 | 13655.88 | 0 | 0 | 1 | 5000 | 13655.88 | 0 | 0 | 0 | 0 | 0 | 45768.12 | 0 | 0 | 0 | 0 | 0 | 45768.12
2022020407 | 6 | 0.82904 | 66323.2 | 0.37756 | 13592.16 | 0 | 0 | 1 | 5000 | 13592.16 | 0 | 0 | 0 | 0 | 0 | 47731.04 | 0 | 0 | 0 | 0 | 0 | 47731.04
2022020408 | 6 | 0.84894 | 67915.2 | 0.39239 | 14126.04 | 0.00504 | 60.48 | 1 | 5000 | 14126.04 | 60.48 | 0 | 0 | 0 | 0 | 48728.68 | 0 | 0 | 0 | 0 | 0 | 48728.68
2022020409 | 6 | 0.85946 | 68756.8 | 0.37951 | 13662.36 | 0.23608 | 2832.96 | 1 | 5000 | 13662.36 | 2832.96 | 0 | 0 | 0 | 0 | 47261.48 | 0 | 0 | 0 | 0 | 0 | 47261.48
2022020410 | 6 | 0.86262 | 69009.6 | 0.32102 | 11556.72 | 0.57447 | 6893.64 | 1 | 5000 | 11556.72 | 6893.64 | 0 | 0 | 0 | 0 | 45559.24 | 0 | 0 | 0 | 0 | 0 | 45559.24
2022020411 | 6 | 0.8503 | 68024 | 0.28393 | 10221.48 | 0.67244 | 8069.28 | 1 | 5000 | 10221.48 | 8069.28 | 0 | 0 | 0 | 0 | 44733.24 | 0 | 0 | 0 | 0 | 0 | 44733.24
2022020412 | 6 | 0.82657 | 66125.6 | 0.27682 | 9965.52 | 0.70721 | 8486.52 | 1 | 5000 | 9965.52 | 8486.52 | 0 | 0 | 0 | 0 | 42673.56 | 0 | 0 | 0 | 0 | 0 | 42673.56
2022020413 | 6 | 0.79753 | 63802.4 | 0.29106 | 10478.16 | 0.71271 | 8552.52 | 1 | 5000 | 10478.16 | 8552.52 | 0 | 0 | 0 | 0 | 39771.72 | 0 | 0 | 0 | 0 | 0 | 39771.72
2022020414 | 6 | 0.76711 | 61368.8 | 0.29345 | 10564.2 | 0.72261 | 8671.32 | 1 | 5000 | 10564.2 | 8671.32 | 0 | 0 | 0 | 0 | 37133.28 | 0 | 0 | 0 | 0 | 0 | 37133.28
2022020415 | 6 | 0.73992 | 59193.6 | 0.27841 | 10022.76 | 0.74839 | 8980.68 | 1 | 5000 | 10022.76 | 8980.68 | 0 | 0 | 0 | 0 | 35190.16 | 0 | 0 | 0 | 0 | 0 | 35190.16
2022020416 | 6 | 0.72084 | 57667.2 | 0.25881 | 9317.16 | 0.76648 | 9197.76 | 1 | 5000 | 9317.16 | 9197.76 | 0 | 0 | 0 | 0 | 34152.28 | 0 | 0 | 0 | 0 | 0 | 34152.28
2022020417 | 6 | 0.71458 | 57166.4 | 0.23403 | 8425.08 | 0.73586 | 8830.32 | 1 | 5000 | 8425.08 | 8830.32 | 0 | 0 | 0 | 0 | 34911 | 0 | 0 | 0 | 0 | 0 | 34911
2022020418 | 6 | 0.72842 | 58273.6 | 0.2018 | 7264.8 | 0.33628 | 4035.36 | 1 | 5000 | 7264.8 | 4035.36 | 0 | 0 | 0 | 0 | 41973.44 | 0 | 0 | 0 | 0 | 0 | 41973.44
2022020419 | 6 | 0.76406 | 61124.8 | 0.16046 | 5776.56 | 0.01181 | 141.72 | 1 | 5000 | 5776.56 | 141.72 | 0 | 0 | 0 | 0 | 50206.52 | 0 | 0 | 0 | 0 | 0 | 50206.52
2022020420 | 6 | 0.77266 | 61812.8 | 0.13395 | 4822.2 | 0 | 0 | 1 | 5000 | 4822.2 | 0 | 0 | 0 | 0 | 0 | 51990.6 | 0 | 0 | 0 | 0 | 0 | 51990.6
2022020421 | 6 | 0.76979 | 61583.2 | 0.13873 | 4994.28 | 0 | 0 | 1 | 5000 | 4994.28 | 0 | 0 | 0 | 0 | 0 | 51588.92 | 0 | 0 | 0 | 0 | 0 | 51588.92
2022020422 | 6 | 0.76342 | 61073.6 | 0.15229 | 5482.44 | 0 | 0 | 1 | 5000 | 5482.44 | 0 | 0 | 0 | 0 | 0 | 50591.16 | 0 | 0 | 0 | 0 | 0 | 50591.16
2022020423 | 6 | 0.75012 | 60009.6 | 0.1695 | 6102 | 0 | 0 | 1 | 5000 | 6102 | 0 | 0 | 0 | 0 | 0 | 48907.6 | 0 | 0 | 0 | 0 | 0 | 48907.6
2022020424 | 6 | 0.73327 | 58661.6 | 0.18724 | 6740.64 | 0 | 0 | 1 | 5000 | 6740.64 | 0 | 0 | 0 | 0 | 0 | 46920.96 | 0 | 0 | 0 | 0 | 0 | 46920.96
2022020501 | 7 | 0.7239 | 57912 | 0.20756 | 7472.16 | 0 | 0 | 1 | 5000 | 7472.16 | 0 | 0 | 0 | 0 | 0 | 45439.84 | 0 | 0 | 0 | 0 | 0 | 45439.84
2022020502 | 7 | 0.72183 | 57746.4 | 0.21943 | 7899.48 | 0 | 0 | 1 | 5000 | 7899.48 | 0 | 0 | 0 | 0 | 0 | 44846.92 | 0 | 0 | 0 | 0 | 0 | 44846.92
2022020503 | 7 | 0.72449 | 57959.2 | 0.21861 | 7869.96 | 0 | 0 | 1 | 5000 | 7869.96 | 0 | 0 | 0 | 0 | 0 | 45089.24 | 0 | 0 | 0 | 0 | 0 | 45089.24
2022020504 | 7 | 0.73103 | 58482.4 | 0.22014 | 7925.04 | 0 | 0 | 1 | 5000 | 7925.04 | 0 | 0 | 0 | 0 | 0 | 45557.36 | 0 | 0 | 0 | 0 | 0 | 45557.36
2022020505 | 7 | 0.74566 | 59652.8 | 0.22227 | 8001.72 | 0 | 0 | 1 | 5000 | 8001.72 | 0 | 0 | 0 | 0 | 0 | 46651.08 | 0 | 0 | 0 | 0 | 0 | 46651.08
2022020506 | 7 | 0.76343 | 61074.4 | 0.22779 | 8200.44 | 0 | 0 | 1 | 5000 | 8200.44 | 0 | 0 | 0 | 0 | 0 | 47873.96 | 0 | 0 | 0 | 0 | 0 | 47873.96
2022020507 | 7 | 0.78666 | 62932.8 | 0.21509 | 7743.24 | 0 | 0 | 1 | 5000 | 7743.24 | 0 | 0 | 0 | 0 | 0 | 50189.56 | 0 | 0 | 0 | 0 | 0 | 50189.56
2022020508 | 7 | 0.80394 | 64315.2 | 0.2118 | 7624.8 | 0.01839 | 220.68 | 1 | 5000 | 7624.8 | 220.68 | 0 | 0 | 0 | 0 | 51469.72 | 0 | 0 | 0 | 0 | 0 | 51469.72
2022020509 | 7 | 0.78989 | 63191.2 | 0.20296 | 7306.56 | 0.38218 | 4586.16 | 1 | 5000 | 7306.56 | 4586.16 | 0 | 0 | 0 | 0 | 46298.48 | 0 | 0 | 0 | 0 | 0 | 46298.48
2022020510 | 7 | 0.75185 | 60148 | 0.17614 | 6341.04 | 0.80385 | 9646.2 | 1 | 5000 | 6341.04 | 9646.2 | 0 | 0 | 0 | 0 | 39160.76 | 0 | 0 | 0 | 0 | 0 | 39160.76
2022020511 | 7 | 0.70605 | 56484 | 0.1598 | 5752.8 | 0.84717 | 10166.04 | 1 | 5000 | 5752.8 | 10166.04 | 0 | 0 | 0 | 0 | 35565.16 | 0 | 0 | 0 | 0 | 0 | 35565.16
2022020512 | 7 | 0.66493 | 53194.4 | 0.22587 | 8131.32 | 0.8283 | 9939.6 | 1 | 5000 | 8131.32 | 9939.6 | 0 | 0 | 0 | 0 | 30123.48 | 0 | 0 | 0 | 0 | 0 | 30123.48
2022020513 | 7 | 0.6274 | 50192 | 0.29667 | 10680.12 | 0.7917 | 9500.4 | 1 | 5000 | 10680.12 | 9500.4 | 0 | 0 | 0 | 0 | 25011.48 | 0 | 0 | 0 | 0 | 0 | 25011.48
2022020514 | 7 | 0.59443 | 47554.4 | 0.31886 | 11478.96 | 0.71603 | 8592.36 | 1 | 5000 | 11478.96 | 8592.36 | 0 | 0 | 0 | 0 | 22483.08 | 0 | 0 | 0 | 0 | 0 | 22483.08
2022020515 | 7 | 0.56603 | 45282.4 | 0.33081 | 11909.16 | 0.56095 | 6731.4 | 1 | 5000 | 11909.16 | 6731.4 | 0 | 0 | 0 | 0 | 21641.84 | 0 | 0 | 0 | 0 | 0 | 21641.84
2022020516 | 7 | 0.54739 | 43791.2 | 0.33283 | 11981.88 | 0.45684 | 5482.08 | 1 | 5000 | 11981.88 | 5482.08 | 0 | 0 | 0 | 0 | 21327.24 | 0 | 0 | 0 | 0 | 0 | 21327.24
2022020517 | 7 | 0.54421 | 43536.8 | 0.33949 | 12221.64 | 0.44825 | 5379 | 1 | 5000 | 12221.64 | 5379 | 0 | 0 | 0 | 0 | 20936.16 | 0 | 0 | 0 | 0 | 0 | 20936.16
2022020518 | 7 | 0.56392 | 45113.6 | 0.35895 | 12922.2 | 0.31146 | 3737.52 | 1 | 5000 | 12922.2 | 3737.52 | 0 | 0 | 0 | 0 | 23453.88 | 0 | 0 | 0 | 0 | 0 | 23453.88
2022020519 | 7 | 0.6101 | 48808 | 0.42211 | 15195.96 | 0.01326 | 159.12 | 1 | 5000 | 15195.96 | 159.12 | 0 | 0 | 0 | 0 | 28452.92 | 0 | 0 | 0 | 0 | 0 | 28452.92
2022020520 | 7 | 0.63689 | 50951.2 | 0.52688 | 18967.68 | 0 | 0 | 1 | 5000 | 18967.68 | 0 | 0 | 0 | 0 | 0 | 26983.52 | 0 | 0 | 0 | 0 | 0 | 26983.52
2022020521 | 7 | 0.65308 | 52246.4 | 0.57297 | 20626.92 | 0 | 0 | 1 | 5000 | 20626.92 | 0 | 0 | 0 | 0 | 0 | 26619.48 | 0 | 0 | 0 | 0 | 0 | 26619.48
2022020522 | 7 | 0.66044 | 52835.2 | 0.57312 | 20632.32 | 0 | 0 | 1 | 5000 | 20632.32 | 0 | 0 | 0 | 0 | 0 | 27202.88 | 0 | 0 | 0 | 0 | 0 | 27202.88
2022020523 | 7 | 0.65671 | 52536.8 | 0.57612 | 20740.32 | 0 | 0 | 1 | 5000 | 20740.32 | 0 | 0 | 0 | 0 | 0 | 26796.48 | 0 | 0 | 0 | 0 | 0 | 26796.48
2022020524 | 7 | 0.65027 | 52021.6 | 0.56937 | 20497.32 | 0 | 0 | 1 | 5000 | 20497.32 | 0 | 0 | 0 | 0 | 0 | 26524.28 | 0 | 0 | 0 | 0 | 0 | 26524.28
2022020601 | 1 | 0.64653 | 51722.4 | 0.55057 | 19820.52 | 0 | 0 | 1 | 5000 | 19820.52 | 0 | 0 | 0 | 0 | 0 | 26901.88 | 0 | 0 | 0 | 0 | 0 | 26901.88
2022020602 | 1 | 0.64822 | 51857.6 | 0.54125 | 19485 | 0 | 0 | 1 | 5000 | 19485 | 0 | 0 | 0 | 0 | 0 | 27372.6 | 0 | 0 | 0 | 0 | 0 | 27372.6
2022020603 | 1 | 0.65303 | 52242.4 | 0.52409 | 18867.24 | 0 | 0 | 1 | 5000 | 18867.24 | 0 | 0 | 0 | 0 | 0 | 28375.16 | 0 | 0 | 0 | 0 | 0 | 28375.16
2022020604 | 1 | 0.66 | 52800 | 0.4907 | 17665.2 | 0 | 0 | 1 | 5000 | 17665.2 | 0 | 0 | 0 | 0 | 0 | 30134.8 | 0 | 0 | 0 | 0 | 0 | 30134.8
2022020605 | 1 | 0.66978 | 53582.4 | 0.4629 | 16664.4 | 0 | 0 | 1 | 5000 | 16664.4 | 0 | 0 | 0 | 0 | 0 | 31918 | 0 | 0 | 0 | 0 | 0 | 31918
2022020606 | 1 | 0.68341 | 54672.8 | 0.43805 | 15769.8 | 0 | 0 | 1 | 5000 | 15769.8 | 0 | 0 | 0 | 0 | 0 | 33903 | 0 | 0 | 0 | 0 | 0 | 33903
2022020607 | 1 | 0.70124 | 56099.2 | 0.40934 | 14736.24 | 0 | 0 | 1 | 5000 | 14736.24 | 0 | 0 | 0 | 0 | 0 | 36362.96 | 0 | 0 | 0 | 0 | 0 | 36362.96
2022020608 | 1 | 0.71607 | 57285.6 | 0.39156 | 14096.16 | 0.0209 | 250.8 | 1 | 5000 | 14096.16 | 250.8 | 0 | 0 | 0 | 0 | 37938.64 | 0 | 0 | 0 | 0 | 0 | 37938.64
2022020609 | 1 | 0.70009 | 56007.2 | 0.33292 | 11985.12 | 0.39711 | 4765.32 | 1 | 5000 | 11985.12 | 4765.32 | 0 | 0 | 0 | 0 | 34256.76 | 0 | 0 | 0 | 0 | 0 | 34256.76
2022020610 | 1 | 0.66415 | 53132 | 0.23614 | 8501.04 | 0.82211 | 9865.32 | 1 | 5000 | 8501.04 | 9865.32 | 0 | 0 | 0 | 0 | 29765.64 | 0 | 0 | 0 | 0 | 0 | 29765.64
2022020611 | 1 | 0.62453 | 49962.4 | 0.21191 | 7628.76 | 0.84253 | 10110.36 | 1 | 5000 | 7628.76 | 10110.36 | 0 | 0 | 0 | 0 | 27223.28 | 0 | 0 | 0 | 0 | 0 | 27223.28
2022020612 | 1 | 0.58561 | 46848.8 | 0.21908 | 7886.88 | 0.81357 | 9762.84 | 1 | 5000 | 7886.88 | 9762.84 | 0 | 0 | 0 | 0 | 24199.08 | 0 | 0 | 0 | 0 | 0 | 24199.08
2022020613 | 1 | 0.55374 | 44299.2 | 0.23279 | 8380.44 | 0.78734 | 9448.08 | 1 | 5000 | 8380.44 | 9448.08 | 0 | 0 | 0 | 0 | 21470.68 | 0 | 0 | 0 | 0 | 0 | 21470.68
2022020614 | 1 | 0.52722 | 42177.6 | 0.2504 | 9014.4 | 0.73213 | 8785.56 | 1 | 5000 | 9014.4 | 8785.56 | 0 | 0 | 0 | 0 | 19377.64 | 0 | 0 | 0 | 0 | 0 | 19377.64
2022020615 | 1 | 0.50974 | 40779.2 | 0.27625 | 9945 | 0.70158 | 8418.96 | 1 | 5000 | 9945 | 8418.96 | 0 | 0 | 0 | 0 | 17415.24 | 0 | 0 | 0 | 0 | 0 | 17415.24
2022020616 | 1 | 0.49985 | 39988 | 0.31292 | 11265.12 | 0.53846 | 6461.52 | 1 | 5000 | 11265.12 | 6461.52 | 0 | 0 | 0 | 0 | 17261.36 | 0 | 0 | 0 | 0 | 0 | 17261.36
2022020617 | 1 | 0.50143 | 40114.4 | 0.3442 | 12391.2 | 0.38829 | 4659.48 | 1 | 5000 | 12391.2 | 4659.48 | 0 | 0 | 0 | 0 | 18063.72 | 0 | 0 | 0 | 0 | 0 | 18063.72
2022020618 | 1 | 0.51965 | 41572 | 0.35581 | 12809.16 | 0.23091 | 2770.92 | 1 | 5000 | 12809.16 | 2770.92 | 0 | 0 | 0 | 0 | 20991.92 | 0 | 0 | 0 | 0 | 0 | 20991.92
2022020619 | 1 | 0.55452 | 44361.6 | 0.35387 | 12739.32 | 0.01136 | 136.32 | 1 | 5000 | 12739.32 | 136.32 | 0 | 0 | 0 | 0 | 26485.96 | 0 | 0 | 0 | 0 | 0 | 26485.96
2022020620 | 1 | 0.57313 | 45850.4 | 0.3825 | 13770 | 0.00015 | 1.8 | 1 | 5000 | 13770 | 1.8 | 0 | 0 | 0 | 0 | 27078.6 | 0 | 0 | 0 | 0 | 0 | 27078.6
2022020621 | 1 | 0.57975 | 46380 | 0.39287 | 14143.32 | 0.00015 | 1.8 | 1 | 5000 | 14143.32 | 1.8 | 0 | 0 | 0 | 0 | 27234.88 | 0 | 0 | 0 | 0 | 0 | 27234.88
2022020622 | 1 | 0.57659 | 46127.2 | 0.38184 | 13746.24 | 0.00015 | 1.8 | 1 | 5000 | 13746.24 | 1.8 | 0 | 0 | 0 | 0 | 27379.16 | 0 | 0 | 0 | 0 | 0 | 27379.16
2022020623 | 1 | 0.5604 | 44832 | 0.37605 | 13537.8 | 0.00015 | 1.8 | 1 | 5000 | 13537.8 | 1.8 | 0 | 0 | 0 | 0 | 26292.4 | 0 | 0 | 0 | 0 | 0 | 26292.4
2022020624 | 1 | 0.54378 | 43502.4 | 0.36712 | 13216.32 | 0.00015 | 1.8 | 1 | 5000 | 13216.32 | 1.8 | 0 | 0 | 0 | 0 | 25284.28 | 0 | 0 | 0 | 0 | 0 | 25284.28
2022020701 | 2 | 0.53377 | 42701.6 | 0.34945 | 12580.2 | 0.00015 | 1.8 | 1 | 5000 | 12580.2 | 1.8 | 0 | 0 | 0 | 0 | 25119.6 | 0 | 0 | 0 | 0 | 0 | 25119.6
2022020702 | 2 | 0.53051 | 42440.8 | 0.35168 | 12660.48 | 0.00015 | 1.8 | 1 | 5000 | 12660.48 | 1.8 | 0 | 0 | 0 | 0 | 24778.52 | 0 | 0 | 0 | 0 | 0 | 24778.52
2022020703 | 2 | 0.53462 | 42769.6 | 0.34253 | 12331.08 | 0.00015 | 1.8 | 1 | 5000 | 12331.08 | 1.8 | 0 | 0 | 0 | 0 | 25436.72 | 0 | 0 | 0 | 0 | 0 | 25436.72
2022020704 | 2 | 0.54514 | 43611.2 | 0.33084 | 11910.24 | 0.00015 | 1.8 | 1 | 5000 | 11910.24 | 1.8 | 0 | 0 | 0 | 0 | 26699.16 | 0 | 0 | 0 | 0 | 0 | 26699.16
2022020705 | 2 | 0.56536 | 45228.8 | 0.31006 | 11162.16 | 0.00015 | 1.8 | 1 | 5000 | 11162.16 | 1.8 | 0 | 0 | 0 | 0 | 29064.84 | 0 | 0 | 0 | 0 | 0 | 29064.84
2022020706 | 2 | 0.6017 | 48136 | 0.28367 | 10212.12 | 0.00015 | 1.8 | 1 | 5000 | 10212.12 | 1.8 | 0 | 0 | 0 | 0 | 32922.08 | 0 | 0 | 0 | 0 | 0 | 32922.08
2022020707 | 2 | 0.65342 | 52273.6 | 0.26891 | 9680.76 | 0.00015 | 1.8 | 1 | 5000 | 9680.76 | 1.8 | 0 | 0 | 0 | 0 | 37591.04 | 0 | 0 | 0 | 0 | 0 | 37591.04
2022020708 | 2 | 0.67837 | 54269.6 | 0.26535 | 9552.6 | 0.01665 | 199.8 | 1 | 5000 | 9552.6 | 199.8 | 0 | 0 | 0 | 0 | 39517.2 | 0 | 0 | 0 | 0 | 0 | 39517.2
2022020709 | 2 | 0.6588 | 52704 | 0.22577 | 8127.72 | 0.37111 | 4453.32 | 1 | 5000 | 8127.72 | 4453.32 | 0 | 0 | 0 | 0 | 35122.96 | 0 | 0 | 0 | 0 | 0 | 35122.96
2022020710 | 2 | 0.62668 | 50134.4 | 0.14831 | 5339.16 | 0.78551 | 9426.12 | 1 | 5000 | 5339.16 | 9426.12 | 0 | 0 | 0 | 0 | 30369.12 | 0 | 0 | 0 | 0 | 0 | 30369.12
2022020711 | 2 | 0.59797 | 47837.6 | 0.12756 | 4592.16 | 0.83196 | 9983.52 | 1 | 5000 | 4592.16 | 9983.52 | 0 | 0 | 0 | 0 | 28261.92 | 0 | 0 | 0 | 0 | 0 | 28261.92
2022020712 | 2 | 0.5718 | 45744 | 0.14893 | 5361.48 | 0.81211 | 9745.32 | 1 | 5000 | 5361.48 | 9745.32 | 0 | 0 | 0 | 0 | 25637.2 | 0 | 0 | 0 | 0 | 0 | 25637.2
2022020713 | 2 | 0.54905 | 43924 | 0.16448 | 5921.28 | 0.80054 | 9606.48 | 1 | 5000 | 5921.28 | 9606.48 | 0 | 0 | 0 | 0 | 23396.24 | 0 | 0 | 0 | 0 | 0 | 23396.24
2022020714 | 2 | 0.53116 | 42492.8 | 0.1572 | 5659.2 | 0.80478 | 9657.36 | 1 | 5000 | 5659.2 | 9657.36 | 0 | 0 | 0 | 0 | 22176.24 | 0 | 0 | 0 | 0 | 0 | 22176.24
2022020715 | 2 | 0.51761 | 41408.8 | 0.16009 | 5763.24 | 0.82267 | 9872.04 | 1 | 5000 | 5763.24 | 9872.04 | 0 | 0 | 0 | 0 | 20773.52 | 0 | 0 | 0 | 0 | 0 | 20773.52
2022020716 | 2 | 0.51031 | 40824.8 | 0.15789 | 5684.04 | 0.83624 | 10034.88 | 1 | 5000 | 5684.04 | 10034.88 | 0 | 0 | 0 | 0 | 20105.88 | 0 | 0 | 0 | 0 | 0 | 20105.88
2022020717 | 2 | 0.5134 | 41072 | 0.15216 | 5477.76 | 0.77216 | 9265.92 | 1 | 5000 | 5477.76 | 9265.92 | 0 | 0 | 0 | 0 | 21328.32 | 0 | 0 | 0 | 0 | 0 | 21328.32
2022020718 | 2 | 0.52782 | 42225.6 | 0.10856 | 3908.16 | 0.35874 | 4304.88 | 1 | 5000 | 3908.16 | 4304.88 | 0 | 0 | 0 | 0 | 29012.56 | 0 | 0 | 0 | 0 | 0 | 29012.56
2022020719 | 2 | 0.56555 | 45244 | 0.07919 | 2850.84 | 0.0151 | 181.2 | 1 | 5000 | 2850.84 | 181.2 | 0 | 0 | 0 | 0 | 37211.96 | 0 | 0 | 0 | 0 | 0 | 37211.96
2022020720 | 2 | 0.58288 | 46630.4 | 0.08309 | 2991.24 | 0 | 0 | 1 | 5000 | 2991.24 | 0 | 0 | 0 | 0 | 0 | 38639.16 | 0 | 0 | 0 | 0 | 0 | 38639.16
2022020721 | 2 | 0.5889 | 47112 | 0.12095 | 4354.2 | 0 | 0 | 1 | 5000 | 4354.2 | 0 | 0 | 0 | 0 | 0 | 37757.8 | 0 | 0 | 0 | 0 | 0 | 37757.8
2022020722 | 2 | 0.58486 | 46788.8 | 0.16593 | 5973.48 | 0 | 0 | 1 | 5000 | 5973.48 | 0 | 0 | 0 | 0 | 0 | 35815.32 | 0 | 0 | 0 | 0 | 0 | 35815.32
2022020723 | 2 | 0.56811 | 45448.8 | 0.23244 | 8367.84 | 0 | 0 | 1 | 5000 | 8367.84 | 0 | 0 | 0 | 0 | 0 | 32080.96 | 0 | 0 | 0 | 0 | 0 | 32080.96
2022020724 | 2 | 0.55169 | 44135.2 | 0.30923 | 11132.28 | 0 | 0 | 1 | 5000 | 11132.28 | 0 | 0 | 0 | 0 | 0 | 28002.92 | 0 | 0 | 0 | 0 | 0 | 28002.92
2022020801 | 3 | 0.54522 | 43617.6 | 0.36449 | 13121.64 | 0 | 0 | 1 | 5000 | 13121.64 | 0 | 0 | 0 | 0 | 0 | 25495.96 | 0 | 0 | 0 | 0 | 0 | 25495.96
2022020802 | 3 | 0.54817 | 43853.6 | 0.39156 | 14096.16 | 0 | 0 | 1 | 5000 | 14096.16 | 0 | 0 | 0 | 0 | 0 | 24757.44 | 0 | 0 | 0 | 0 | 0 | 24757.44
2022020803 | 3 | 0.55715 | 44572 | 0.41795 | 15046.2 | 0 | 0 | 1 | 5000 | 15046.2 | 0 | 0 | 0 | 0 | 0 | 24525.8 | 0 | 0 | 0 | 0 | 0 | 24525.8
2022020804 | 3 | 0.57013 | 45610.4 | 0.4407 | 15865.2 | 0 | 0 | 1 | 5000 | 15865.2 | 0 | 0 | 0 | 0 | 0 | 24745.2 | 0 | 0 | 0 | 0 | 0 | 24745.2
2022020805 | 3 | 0.59363 | 47490.4 | 0.45692 | 16449.12 | 0 | 0 | 1 | 5000 | 16449.12 | 0 | 0 | 0 | 0 | 0 | 26041.28 | 0 | 0 | 0 | 0 | 0 | 26041.28
2022020806 | 3 | 0.63429 | 50743.2 | 0.45653 | 16435.08 | 0 | 0 | 1 | 5000 | 16435.08 | 0 | 0 | 0 | 0 | 0 | 29308.12 | 0 | 0 | 0 | 0 | 0 | 29308.12
2022020807 | 3 | 0.68925 | 55140 | 0.45695 | 16450.2 | 0 | 0 | 1 | 5000 | 16450.2 | 0 | 0 | 0 | 0 | 0 | 33689.8 | 0 | 0 | 0 | 0 | 0 | 33689.8
2022020808 | 3 | 0.70933 | 56746.4 | 0.45443 | 16359.48 | 0.02292 | 275.04 | 1 | 5000 | 16359.48 | 275.04 | 0 | 0 | 0 | 0 | 35111.88 | 0 | 0 | 0 | 0 | 0 | 35111.88
2022020809 | 3 | 0.67779 | 54223.2 | 0.42278 | 15220.08 | 0.39739 | 4768.68 | 1 | 5000 | 15220.08 | 4768.68 | 0 | 0 | 0 | 0 | 29234.44 | 0 | 0 | 0 | 0 | 0 | 29234.44
2022020810 | 3 | 0.6296 | 50368 | 0.30606 | 11018.16 | 0.78163 | 9379.56 | 1 | 5000 | 11018.16 | 9379.56 | 0 | 0 | 0 | 0 | 24970.28 | 0 | 0 | 0 | 0 | 0 | 24970.28
2022020811 | 3 | 0.5887 | 47096 | 0.26845 | 9664.2 | 0.85897 | 10307.64 | 1 | 5000 | 9664.2 | 10307.64 | 0 | 0 | 0 | 0 | 22124.16 | 0 | 0 | 0 | 0 | 0 | 22124.16
2022020812 | 3 | 0.55634 | 44507.2 | 0.28015 | 10085.4 | 0.80361 | 9643.32 | 1 | 5000 | 10085.4 | 9643.32 | 0 | 0 | 0 | 0 | 19778.48 | 0 | 0 | 0 | 0 | 0 | 19778.48
2022020813 | 3 | 0.53122 | 42497.6 | 0.32183 | 11585.88 | 0.639 | 7668 | 1 | 5000 | 11585.88 | 7668 | 0 | 0 | 0 | 0 | 18243.72 | 0 | 0 | 0 | 0 | 0 | 18243.72
2022020814 | 3 | 0.5153 | 41224 | 0.36516 | 13145.76 | 0.45555 | 5466.6 | 1 | 5000 | 13145.76 | 5466.6 | 0 | 0 | 0 | 0 | 17611.64 | 0 | 0 | 0 | 0 | 0 | 17611.64
2022020815 | 3 | 0.50278 | 40222.4 | 0.37325 | 13437 | 0.42457 | 5094.84 | 1 | 5000 | 13437 | 5094.84 | 0 | 0 | 0 | 0 | 16690.56 | 0 | 0 | 0 | 0 | 0 | 16690.56
2022020816 | 3 | 0.49706 | 39764.8 | 0.3917 | 14101.2 | 0.4532 | 5438.4 | 1 | 5000 | 14101.2 | 5438.4 | 0 | 0 | 0 | 0 | 15225.2 | 0 | 0 | 0 | 0 | 0 | 15225.2
2022020817 | 3 | 0.50016 | 40012.8 | 0.3743 | 13474.8 | 0.53843 | 6461.16 | 1 | 5000 | 13474.8 | 6461.16 | 0 | 0 | 0 | 0 | 15076.84 | 0 | 0 | 0 | 0 | 0 | 15076.84
2022020818 | 3 | 0.50936 | 40748.8 | 0.32892 | 11841.12 | 0.34161 | 4099.32 | 1 | 5000 | 11841.12 | 4099.32 | 0 | 0 | 0 | 0 | 19808.36 | 0 | 0 | 0 | 0 | 0 | 19808.36
2022020819 | 3 | 0.53869 | 43095.2 | 0.28385 | 10218.6 | 0.01642 | 197.04 | 1 | 5000 | 10218.6 | 197.04 | 0 | 0 | 0 | 0 | 27679.56 | 0 | 0 | 0 | 0 | 0 | 27679.56
2022020820 | 3 | 0.55277 | 44221.6 | 0.32493 | 11697.48 | 9e-05 | 1.08 | 1 | 5000 | 11697.48 | 1.08 | 0 | 0 | 0 | 0 | 27523.04 | 0 | 0 | 0 | 0 | 0 | 27523.04
2022020821 | 3 | 0.55505 | 44404 | 0.36903 | 13285.08 | 9e-05 | 1.08 | 1 | 5000 | 13285.08 | 1.08 | 0 | 0 | 0 | 0 | 26117.84 | 0 | 0 | 0 | 0 | 0 | 26117.84
2022020822 | 3 | 0.54917 | 43933.6 | 0.38574 | 13886.64 | 9e-05 | 1.08 | 1 | 5000 | 13886.64 | 1.08 | 0 | 0 | 0 | 0 | 25045.88 | 0 | 0 | 0 | 0 | 0 | 25045.88
2022020823 | 3 | 0.53296 | 42636.8 | 0.38639 | 13910.04 | 9e-05 | 1.08 | 1 | 5000 | 13910.04 | 1.08 | 0 | 0 | 0 | 0 | 23725.68 | 0 | 0 | 0 | 0 | 0 | 23725.68
2022020824 | 3 | 0.5136 | 41088 | 0.38392 | 13821.12 | 8e-05 | 0.96 | 1 | 5000 | 13821.12 | 0.96 | 0 | 0 | 0 | 0 | 22265.92 | 0 | 0 | 0 | 0 | 0 | 22265.92
2022020901 | 4 | 0.50455 | 40364 | 0.34859 | 12549.24 | 8e-05 | 0.96 | 1 | 5000 | 12549.24 | 0.96 | 0 | 0 | 0 | 0 | 22813.8 | 0 | 0 | 0 | 0 | 0 | 22813.8
2022020902 | 4 | 0.50398 | 40318.4 | 0.29023 | 10448.28 | 8e-05 | 0.96 | 1 | 5000 | 10448.28 | 0.96 | 0 | 0 | 0 | 0 | 24869.16 | 0 | 0 | 0 | 0 | 0 | 24869.16
2022020903 | 4 | 0.51001 | 40800.8 | 0.24038 | 8653.68 | 8e-05 | 0.96 | 1 | 5000 | 8653.68 | 0.96 | 0 | 0 | 0 | 0 | 27146.16 | 0 | 0 | 0 | 0 | 0 | 27146.16
2022020904 | 4 | 0.52197 | 41757.6 | 0.19787 | 7123.32 | 8e-05 | 0.96 | 1 | 5000 | 7123.32 | 0.96 | 0 | 0 | 0 | 0 | 29633.32 | 0 | 0 | 0 | 0 | 0 | 29633.32
2022020905 | 4 | 0.54581 | 43664.8 | 0.16859 | 6069.24 | 8e-05 | 0.96 | 1 | 5000 | 6069.24 | 0.96 | 0 | 0 | 0 | 0 | 32594.6 | 0 | 0 | 0 | 0 | 0 | 32594.6
2022020906 | 4 | 0.58421 | 46736.8 | 0.1402 | 5047.2 | 8e-05 | 0.96 | 1 | 5000 | 5047.2 | 0.96 | 0 | 0 | 0 | 0 | 36688.64 | 0 | 0 | 0 | 0 | 0 | 36688.64
2022020907 | 4 | 0.64016 | 51212.8 | 0.12116 | 4361.76 | 8e-05 | 0.96 | 1 | 5000 | 4361.76 | 0.96 | 0 | 0 | 0 | 0 | 41850.08 | 0 | 0 | 0 | 0 | 0 | 41850.08
2022020908 | 4 | 0.66094 | 52875.2 | 0.10817 | 3894.12 | 0.02174 | 260.88 | 1 | 5000 | 3894.12 | 260.88 | 0 | 0 | 0 | 0 | 43720.2 | 0 | 0 | 0 | 0 | 0 | 43720.2
2022020909 | 4 | 0.63535 | 50828 | 0.09902 | 3564.72 | 0.39751 | 4770.12 | 1 | 5000 | 3564.72 | 4770.12 | 0 | 0 | 0 | 0 | 37493.16 | 0 | 0 | 0 | 0 | 0 | 37493.16
2022020910 | 4 | 0.59477 | 47581.6 | 0.05678 | 2044.08 | 0.76867 | 9224.04 | 1 | 5000 | 2044.08 | 9224.04 | 0 | 0 | 0 | 0 | 31313.48 | 0 | 0 | 0 | 0 | 0 | 31313.48
2022020911 | 4 | 0.56 | 44800 | 0.04386 | 1578.96 | 0.8038 | 9645.6 | 1 | 5000 | 1578.96 | 9645.6 | 0 | 0 | 0 | 0 | 28575.44 | 0 | 0 | 0 | 0 | 0 | 28575.44
2022020912 | 4 | 0.53071 | 42456.8 | 0.04651 | 1674.36 | 0.78602 | 9432.24 | 1 | 5000 | 1674.36 | 9432.24 | 0 | 0 | 0 | 0 | 26350.2 | 0 | 0 | 0 | 0 | 0 | 26350.2
2022020913 | 4 | 0.51057 | 40845.6 | 0.04569 | 1644.84 | 0.76995 | 9239.4 | 1 | 5000 | 1644.84 | 9239.4 | 0 | 0 | 0 | 0 | 24961.36 | 0 | 0 | 0 | 0 | 0 | 24961.36
2022020914 | 4 | 0.50079 | 40063.2 | 0.0438 | 1576.8 | 0.76998 | 9239.76 | 1 | 5000 | 1576.8 | 9239.76 | 0 | 0 | 0 | 0 | 24246.64 | 0 | 0 | 0 | 0 | 0 | 24246.64
2022020915 | 4 | 0.49383 | 39506.4 | 0.03627 | 1305.72 | 0.78498 | 9419.76 | 1 | 5000 | 1305.72 | 9419.76 | 0 | 0 | 0 | 0 | 23780.92 | 0 | 0 | 0 | 0 | 0 | 23780.92
2022020916 | 4 | 0.49028 | 39222.4 | 0.03919 | 1410.84 | 0.80005 | 9600.6 | 1 | 5000 | 1410.84 | 9600.6 | 0 | 0 | 0 | 0 | 23210.96 | 0 | 0 | 0 | 0 | 0 | 23210.96
2022020917 | 4 | 0.49324 | 39459.2 | 0.05193 | 1869.48 | 0.73514 | 8821.68 | 1 | 5000 | 1869.48 | 8821.68 | 0 | 0 | 0 | 0 | 23768.04 | 0 | 0 | 0 | 0 | 0 | 23768.04
2022020918 | 4 | 0.50127 | 40101.6 | 0.06765 | 2435.4 | 0.35122 | 4214.64 | 1 | 5000 | 2435.4 | 4214.64 | 0 | 0 | 0 | 0 | 28451.56 | 0 | 0 | 0 | 0 | 0 | 28451.56
2022020919 | 4 | 0.52276 | 41820.8 | 0.11121 | 4003.56 | 0.01689 | 202.68 | 1 | 5000 | 4003.56 | 202.68 | 0 | 0 | 0 | 0 | 32614.56 | 0 | 0 | 0 | 0 | 0 | 32614.56
2022020920 | 4 | 0.53068 | 42454.4 | 0.19361 | 6969.96 | 6e-05 | 0.72 | 1 | 5000 | 6969.96 | 0.72 | 0 | 0 | 0 | 0 | 30483.72 | 0 | 0 | 0 | 0 | 0 | 30483.72
2022020921 | 4 | 0.53041 | 42432.8 | 0.24156 | 8696.16 | 6e-05 | 0.72 | 1 | 5000 | 8696.16 | 0.72 | 0 | 0 | 0 | 0 | 28735.92 | 0 | 0 | 0 | 0 | 0 | 28735.92
2022020922 | 4 | 0.52142 | 41713.6 | 0.27068 | 9744.48 | 5e-05 | 0.6 | 1 | 5000 | 9744.48 | 0.6 | 0 | 0 | 0 | 0 | 26968.52 | 0 | 0 | 0 | 0 | 0 | 26968.52
2022020923 | 4 | 0.50457 | 40365.6 | 0.28142 | 10131.12 | 5e-05 | 0.6 | 1 | 5000 | 10131.12 | 0.6 | 0 | 0 | 0 | 0 | 25233.88 | 0 | 0 | 0 | 0 | 0 | 25233.88
2022020924 | 4 | 0.48687 | 38949.6 | 0.28955 | 10423.8 | 5e-05 | 0.6 | 1 | 5000 | 10423.8 | 0.6 | 0 | 0 | 0 | 0 | 23525.2 | 0 | 0 | 0 | 0 | 0 | 23525.2
2022021001 | 5 | 0.47749 | 38199.2 | 0.29616 | 10661.76 | 5e-05 | 0.6 | 1 | 5000 | 10661.76 | 0.6 | 0 | 0 | 0 | 0 | 22536.84 | 0 | 0 | 0 | 0 | 0 | 22536.84
2022021002 | 5 | 0.4763 | 38104 | 0.28379 | 10216.44 | 5e-05 | 0.6 | 1 | 5000 | 10216.44 | 0.6 | 0 | 0 | 0 | 0 | 22886.96 | 0 | 0 | 0 | 0 | 0 | 22886.96
2022021003 | 5 | 0.48144 | 38515.2 | 0.26986 | 9714.96 | 5e-05 | 0.6 | 1 | 5000 | 9714.96 | 0.6 | 0 | 0 | 0 | 0 | 23799.64 | 0 | 0 | 0 | 0 | 0 | 23799.64
2022021004 | 5 | 0.49184 | 39347.2 | 0.22801 | 8208.36 | 5e-05 | 0.6 | 1 | 5000 | 8208.36 | 0.6 | 0 | 0 | 0 | 0 | 26138.24 | 0 | 0 | 0 | 0 | 0 | 26138.24
2022021005 | 5 | 0.51124 | 40899.2 | 0.19404 | 6985.44 | 5e-05 | 0.6 | 1 | 5000 | 6985.44 | 0.6 | 0 | 0 | 0 | 0 | 28913.16 | 0 | 0 | 0 | 0 | 0 | 28913.16
2022021006 | 5 | 0.55053 | 44042.4 | 0.17538 | 6313.68 | 5e-05 | 0.6 | 1 | 5000 | 6313.68 | 0.6 | 0 | 0 | 0 | 0 | 32728.12 | 0 | 0 | 0 | 0 | 0 | 32728.12
2022021007 | 5 | 0.60617 | 48493.6 | 0.15904 | 5725.44 | 6e-05 | 0.72 | 1 | 5000 | 5725.44 | 0.72 | 0 | 0 | 0 | 0 | 37767.44 | 0 | 0 | 0 | 0 | 0 | 37767.44
2022021008 | 5 | 0.62844 | 50275.2 | 0.178 | 6408 | 0.02301 | 276.12 | 1 | 5000 | 6408 | 276.12 | 0 | 0 | 0 | 0 | 38591.08 | 0 | 0 | 0 | 0 | 0 | 38591.08
2022021009 | 5 | 0.6051 | 48408 | 0.16655 | 5995.8 | 0.34358 | 4122.96 | 1 | 5000 | 5995.8 | 4122.96 | 0 | 0 | 0 | 0 | 33289.24 | 0 | 0 | 0 | 0 | 0 | 33289.24
2022021010 | 5 | 0.57015 | 45612 | 0.10551 | 3798.36 | 0.71612 | 8593.44 | 1 | 5000 | 3798.36 | 8593.44 | 0 | 0 | 0 | 0 | 28220.2 | 0 | 0 | 0 | 0 | 0 | 28220.2
2022021011 | 5 | 0.54046 | 43236.8 | 0.08135 | 2928.6 | 0.78606 | 9432.72 | 1 | 5000 | 2928.6 | 9432.72 | 0 | 0 | 0 | 0 | 25875.48 | 0 | 0 | 0 | 0 | 0 | 25875.48
2022021012 | 5 | 0.51653 | 41322.4 | 0.0549 | 1976.4 | 0.74207 | 8904.84 | 1 | 5000 | 1976.4 | 8904.84 | 0 | 0 | 0 | 0 | 25441.16 | 0 | 0 | 0 | 0 | 0 | 25441.16
2022021013 | 5 | 0.50257 | 40205.6 | 0.03103 | 1117.08 | 0.72513 | 8701.56 | 1 | 5000 | 1117.08 | 8701.56 | 0 | 0 | 0 | 0 | 25386.96 | 0 | 0 | 0 | 0 | 0 | 25386.96
2022021014 | 5 | 0.49604 | 39683.2 | 0.01912 | 688.32 | 0.72886 | 8746.32 | 1 | 5000 | 688.32 | 8746.32 | 0 | 0 | 0 | 0 | 25248.56 | 0 | 0 | 0 | 0 | 0 | 25248.56
2022021015 | 5 | 0.49275 | 39420 | 0.02733 | 983.88 | 0.75638 | 9076.56 | 1 | 5000 | 983.88 | 9076.56 | 0 | 0 | 0 | 0 | 24359.56 | 0 | 0 | 0 | 0 | 0 | 24359.56
2022021016 | 5 | 0.49055 | 39244 | 0.03721 | 1339.56 | 0.77149 | 9257.88 | 1 | 5000 | 1339.56 | 9257.88 | 0 | 0 | 0 | 0 | 23646.56 | 0 | 0 | 0 | 0 | 0 | 23646.56
2022021017 | 5 | 0.49263 | 39410.4 | 0.03696 | 1330.56 | 0.70836 | 8500.32 | 1 | 5000 | 1330.56 | 8500.32 | 0 | 0 | 0 | 0 | 24579.52 | 0 | 0 | 0 | 0 | 0 | 24579.52
2022021018 | 5 | 0.49897 | 39917.6 | 0.04543 | 1635.48 | 0.33769 | 4052.28 | 1 | 5000 | 1635.48 | 4052.28 | 0 | 0 | 0 | 0 | 29229.84 | 0 | 0 | 0 | 0 | 0 | 29229.84
2022021019 | 5 | 0.51825 | 41460 | 0.06775 | 2439 | 0.0164 | 196.8 | 1 | 5000 | 2439 | 196.8 | 0 | 0 | 0 | 0 | 33824.2 | 0 | 0 | 0 | 0 | 0 | 33824.2
2022021020 | 5 | 0.52582 | 42065.6 | 0.10804 | 3889.44 | 0 | 0 | 1 | 5000 | 3889.44 | 0 | 0 | 0 | 0 | 0 | 33176.16 | 0 | 0 | 0 | 0 | 0 | 33176.16
2022021021 | 5 | 0.52231 | 41784.8 | 0.15221 | 5479.56 | 0 | 0 | 1 | 5000 | 5479.56 | 0 | 0 | 0 | 0 | 0 | 31305.24 | 0 | 0 | 0 | 0 | 0 | 31305.24
2022021022 | 5 | 0.51231 | 40984.8 | 0.19916 | 7169.76 | 0 | 0 | 1 | 5000 | 7169.76 | 0 | 0 | 0 | 0 | 0 | 28815.04 | 0 | 0 | 0 | 0 | 0 | 28815.04
2022021023 | 5 | 0.49211 | 39368.8 | 0.27554 | 9919.44 | 0 | 0 | 1 | 5000 | 9919.44 | 0 | 0 | 0 | 0 | 0 | 24449.36 | 0 | 0 | 0 | 0 | 0 | 24449.36
2022021024 | 5 | 0.47268 | 37814.4 | 0.37895 | 13642.2 | 0 | 0 | 1 | 5000 | 13642.2 | 0 | 0 | 0 | 0 | 0 | 19172.2 | 0 | 0 | 0 | 0 | 0 | 19172.2
2022021101 | 6 | 0.46218 | 36974.4 | 0.46373 | 16694.28 | 0 | 0 | 1 | 5000 | 16694.28 | 0 | 0 | 0 | 0 | 0 | 15280.12 | 0 | 0 | 0 | 0 | 0 | 15280.12
2022021102 | 6 | 0.4605 | 36840 | 0.51234 | 18444.24 | 0 | 0 | 1 | 5000 | 18444.24 | 0 | 0 | 0 | 0 | 0 | 13395.76 | 0 | 0 | 0 | 0 | 0 | 13395.76
2022021103 | 6 | 0.46338 | 37070.4 | 0.53585 | 19290.6 | 0 | 0 | 1 | 5000 | 19290.6 | 0 | 0 | 0 | 0 | 0 | 12779.8 | 0 | 0 | 0 | 0 | 0 | 12779.8
2022021104 | 6 | 0.47006 | 37604.8 | 0.54378 | 19576.08 | 0 | 0 | 1 | 5000 | 19576.08 | 0 | 0 | 0 | 0 | 0 | 13028.72 | 0 | 0 | 0 | 0 | 0 | 13028.72
2022021105 | 6 | 0.486 | 38880 | 0.54383 | 19577.88 | 0 | 0 | 1 | 5000 | 19577.88 | 0 | 0 | 0 | 0 | 0 | 14302.12 | 0 | 0 | 0 | 0 | 0 | 14302.12
2022021106 | 6 | 0.52007 | 41605.6 | 0.54363 | 19570.68 | 0 | 0 | 1 | 5000 | 19570.68 | 0 | 0 | 0 | 0 | 0 | 17034.92 | 0 | 0 | 0 | 0 | 0 | 17034.92
2022021107 | 6 | 0.56775 | 45420 | 0.53664 | 19319.04 | 0 | 0 | 1 | 5000 | 19319.04 | 0 | 0 | 0 | 0 | 0 | 21100.96 | 0 | 0 | 0 | 0 | 0 | 21100.96
2022021108 | 6 | 0.58869 | 47095.2 | 0.53438 | 19237.68 | 0.01854 | 222.48 | 1 | 5000 | 19237.68 | 222.48 | 0 | 0 | 0 | 0 | 22635.04 | 0 | 0 | 0 | 0 | 0 | 22635.04
2022021109 | 6 | 0.57365 | 45892 | 0.48897 | 17602.92 | 0.23933 | 2871.96 | 1 | 5000 | 17602.92 | 2871.96 | 0 | 0 | 0 | 0 | 20417.12 | 0 | 0 | 0 | 0 | 0 | 20417.12
2022021110 | 6 | 0.54879 | 43903.2 | 0.3991 | 14367.6 | 0.58257 | 6990.84 | 1 | 5000 | 14367.6 | 6990.84 | 0 | 0 | 0 | 0 | 17544.76 | 0 | 0 | 0 | 0 | 0 | 17544.76
2022021111 | 6 | 0.52853 | 42282.4 | 0.39343 | 14163.48 | 0.65104 | 7812.48 | 1 | 5000 | 14163.48 | 7812.48 | 0 | 0 | 0 | 0 | 15306.44 | 0 | 0 | 0 | 0 | 0 | 15306.44
2022021112 | 6 | 0.51213 | 40970.4 | 0.38154 | 13735.44 | 0.67001 | 8040.12 | 1 | 5000 | 13735.44 | 8040.12 | 0 | 0 | 0 | 0 | 14194.84 | 0 | 0 | 0 | 0 | 0 | 14194.84
2022021113 | 6 | 0.50223 | 40178.4 | 0.36234 | 13044.24 | 0.74543 | 8945.16 | 1 | 5000 | 13044.24 | 8945.16 | 0 | 0 | 0 | 0 | 13189 | 0 | 0 | 0 | 0 | 0 | 13189
2022021114 | 6 | 0.49937 | 39949.6 | 0.34459 | 12405.24 | 0.74672 | 8960.64 | 1 | 5000 | 12405.24 | 8960.64 | 0 | 0 | 0 | 0 | 13583.72 | 0 | 0 | 0 | 0 | 0 | 13583.72
2022021115 | 6 | 0.49751 | 39800.8 | 0.34016 | 12245.76 | 0.76501 | 9180.12 | 1 | 5000 | 12245.76 | 9180.12 | 0 | 0 | 0 | 0 | 13374.92 | 0 | 0 | 0 | 0 | 0 | 13374.92
2022021116 | 6 | 0.49947 | 39957.6 | 0.37669 | 13560.84 | 0.77576 | 9309.12 | 1 | 5000 | 13560.84 | 9309.12 | 0 | 0 | 0 | 0 | 12087.64 | 0 | 0 | 0 | 0 | 0 | 12087.64
2022021117 | 6 | 0.50231 | 40184.8 | 0.43467 | 15648.12 | 0.6281 | 7537.2 | 1 | 5000 | 15648.12 | 7537.2 | 0 | 0 | 0 | 0 | 11999.48 | 0 | 0 | 0 | 0 | 0 | 11999.48
2022021118 | 6 | 0.50492 | 40393.6 | 0.52827 | 19017.72 | 0.29435 | 3532.2 | 1 | 5000 | 19017.72 | 3532.2 | 0 | 0 | 0 | 0 | 12843.68 | 0 | 0 | 0 | 0 | 0 | 12843.68
2022021119 | 6 | 0.51308 | 41046.4 | 0.59753 | 21511.08 | 0.01602 | 192.24 | 1 | 5000 | 21511.08 | 192.24 | 0 | 0 | 0 | 0 | 14343.08 | 0 | 0 | 0 | 0 | 0 | 14343.08
2022021120 | 6 | 0.51418 | 41134.4 | 0.6285 | 22626 | 0 | 0 | 1 | 5000 | 22626 | 0 | 0 | 0 | 0 | 0 | 13508.4 | 0 | 0 | 0 | 0 | 0 | 13508.4
2022021121 | 6 | 0.50704 | 40563.2 | 0.65359 | 23529.24 | 0 | 0 | 1 | 5000 | 23529.24 | 0 | 0 | 0 | 0 | 0 | 12033.96 | 0 | 0 | 0 | 0 | 0 | 12033.96
2022021122 | 6 | 0.49611 | 39688.8 | 0.64405 | 23185.8 | 0 | 0 | 1 | 5000 | 23185.8 | 0 | 0 | 0 | 0 | 0 | 11503 | 0 | 0 | 0 | 0 | 0 | 11503
2022021123 | 6 | 0.4798 | 38384 | 0.62875 | 22635 | 0 | 0 | 1 | 5000 | 22635 | 0 | 0 | 0 | 0 | 0 | 10749 | 0 | 0 | 0 | 0 | 0 | 10749
2022021124 | 6 | 0.46056 | 36844.8 | 0.61229 | 22042.44 | 0 | 0 | 1 | 5000 | 22042.44 | 0 | 0 | 0 | 0 | 0 | 9802.36 | 0 | 0 | 0 | 0 | 0 | 9802.36
2022021201 | 7 | 0.44319 | 35455.2 | 0.59871 | 21553.56 | 0 | 0 | 1 | 5000 | 21553.56 | 0 | 0 | 0 | 0 | 0 | 8901.64 | 0 | 0 | 0 | 0 | 0 | 8901.64
2022021202 | 7 | 0.43497 | 34797.6 | 0.581 | 20916 | 0 | 0 | 1 | 5000 | 20916 | 0 | 0 | 0 | 0 | 0 | 8881.6 | 0 | 0 | 0 | 0 | 0 | 8881.6
2022021203 | 7 | 0.43286 | 34628.8 | 0.58274 | 20978.64 | 0 | 0 | 1 | 5000 | 20978.64 | 0 | 0 | 0 | 0 | 0 | 8650.16 | 0 | 0 | 0 | 0 | 0 | 8650.16
2022021204 | 7 | 0.43536 | 34828.8 | 0.59124 | 21284.64 | 0 | 0 | 1 | 5000 | 21284.64 | 0 | 0 | 0 | 0 | 0 | 8544.16 | 0 | 0 | 0 | 0 | 0 | 8544.16
2022021205 | 7 | 0.44099 | 35279.2 | 0.59183 | 21305.88 | 0 | 0 | 1 | 5000 | 21305.88 | 0 | 0 | 0 | 0 | 0 | 8973.32 | 0 | 0 | 0 | 0 | 0 | 8973.32
2022021206 | 7 | 0.45685 | 36548 | 0.59578 | 21448.08 | 0 | 0 | 1 | 5000 | 21448.08 | 0 | 0 | 0 | 0 | 0 | 10099.92 | 0 | 0 | 0 | 0 | 0 | 10099.92
2022021207 | 7 | 0.4797 | 38376 | 0.59948 | 21581.28 | 0 | 0 | 1 | 5000 | 21581.28 | 0 | 0 | 0 | 0 | 0 | 11794.72 | 0 | 0 | 0 | 0 | 0 | 11794.72
2022021208 | 7 | 0.50787 | 40629.6 | 0.59485 | 21414.6 | 0.0041 | 49.2 | 1 | 5000 | 21414.6 | 49.2 | 0 | 0 | 0 | 0 | 14165.8 | 0 | 0 | 0 | 0 | 0 | 14165.8
2022021209 | 7 | 0.53556 | 42844.8 | 0.57748 | 20789.28 | 0.08297 | 995.64 | 1 | 5000 | 20789.28 | 995.64 | 0 | 0 | 0 | 0 | 16059.88 | 0 | 0 | 0 | 0 | 0 | 16059.88
2022021210 | 7 | 0.55897 | 44717.6 | 0.54785 | 19722.6 | 0.20132 | 2415.84 | 1 | 5000 | 19722.6 | 2415.84 | 0 | 0 | 0 | 0 | 17579.16 | 0 | 0 | 0 | 0 | 0 | 17579.16
2022021211 | 7 | 0.57341 | 45872.8 | 0.53707 | 19334.52 | 0.28914 | 3469.68 | 1 | 5000 | 19334.52 | 3469.68 | 0 | 0 | 0 | 0 | 18068.6 | 0 | 0 | 0 | 0 | 0 | 18068.6
2022021212 | 7 | 0.57643 | 46114.4 | 0.51843 | 18663.48 | 0.49054 | 5886.48 | 1 | 5000 | 18663.48 | 5886.48 | 0 | 0 | 0 | 0 | 16564.44 | 0 | 0 | 0 | 0 | 0 | 16564.44
2022021213 | 7 | 0.57601 | 46080.8 | 0.46248 | 16649.28 | 0.60775 | 7293 | 1 | 5000 | 16649.28 | 7293 | 0 | 0 | 0 | 0 | 17138.52 | 0 | 0 | 0 | 0 | 0 | 17138.52
2022021214 | 7 | 0.56875 | 45500 | 0.38831 | 13979.16 | 0.68665 | 8239.8 | 1 | 5000 | 13979.16 | 8239.8 | 0 | 0 | 0 | 0 | 18281.04 | 0 | 0 | 0 | 0 | 0 | 18281.04
2022021215 | 7 | 0.55317 | 44253.6 | 0.31844 | 11463.84 | 0.73198 | 8783.76 | 1 | 5000 | 11463.84 | 8783.76 | 0 | 0 | 0 | 0 | 19006 | 0 | 0 | 0 | 0 | 0 | 19006
2022021216 | 7 | 0.54172 | 43337.6 | 0.27776 | 9999.36 | 0.79478 | 9537.36 | 1 | 5000 | 9999.36 | 9537.36 | 0 | 0 | 0 | 0 | 18800.88 | 0 | 0 | 0 | 0 | 0 | 18800.88
2022021217 | 7 | 0.53986 | 43188.8 | 0.25448 | 9161.28 | 0.75254 | 9030.48 | 1 | 5000 | 9161.28 | 9030.48 | 0 | 0 | 0 | 0 | 19997.04 | 0 | 0 | 0 | 0 | 0 | 19997.04
2022021218 | 7 | 0.55383 | 44306.4 | 0.22944 | 8259.84 | 0.3768 | 4521.6 | 1 | 5000 | 8259.84 | 4521.6 | 0 | 0 | 0 | 0 | 26524.96 | 0 | 0 | 0 | 0 | 0 | 26524.96
2022021219 | 7 | 0.5899 | 47192 | 0.19383 | 6977.88 | 0.02146 | 257.52 | 1 | 5000 | 6977.88 | 257.52 | 0 | 0 | 0 | 0 | 34956.6 | 0 | 0 | 0 | 0 | 0 | 34956.6
2022021220 | 7 | 0.60789 | 48631.2 | 0.18828 | 6778.08 | 6e-05 | 0.72 | 1 | 5000 | 6778.08 | 0.72 | 0 | 0 | 0 | 0 | 36852.4 | 0 | 0 | 0 | 0 | 0 | 36852.4
2022021221 | 7 | 0.61462 | 49169.6 | 0.19397 | 6982.92 | 6e-05 | 0.72 | 1 | 5000 | 6982.92 | 0.72 | 0 | 0 | 0 | 0 | 37185.96 | 0 | 0 | 0 | 0 | 0 | 37185.96
2022021222 | 7 | 0.61686 | 49348.8 | 0.20413 | 7348.68 | 6e-05 | 0.72 | 1 | 5000 | 7348.68 | 0.72 | 0 | 0 | 0 | 0 | 36999.4 | 0 | 0 | 0 | 0 | 0 | 36999.4
2022021223 | 7 | 0.61144 | 48915.2 | 0.24208 | 8714.88 | 6e-05 | 0.72 | 1 | 5000 | 8714.88 | 0.72 | 0 | 0 | 0 | 0 | 35199.6 | 0 | 0 | 0 | 0 | 0 | 35199.6
2022021224 | 7 | 0.60394 | 48315.2 | 0.29556 | 10640.16 | 6e-05 | 0.72 | 1 | 5000 | 10640.16 | 0.72 | 0 | 0 | 0 | 0 | 32674.32 | 0 | 0 | 0 | 0 | 0 | 32674.32
2022021301 | 1 | 0.59953 | 47962.4 | 0.36567 | 13164.12 | 6e-05 | 0.72 | 1 | 5000 | 13164.12 | 0.72 | 0 | 0 | 0 | 0 | 29797.56 | 0 | 0 | 0 | 0 | 0 | 29797.56
2022021302 | 1 | 0.59952 | 47961.6 | 0.40125 | 14445 | 6e-05 | 0.72 | 1 | 5000 | 14445 | 0.72 | 0 | 0 | 0 | 0 | 28515.88 | 0 | 0 | 0 | 0 | 0 | 28515.88
2022021303 | 1 | 0.60284 | 48227.2 | 0.41651 | 14994.36 | 6e-05 | 0.72 | 1 | 5000 | 14994.36 | 0.72 | 0 | 0 | 0 | 0 | 28232.12 | 0 | 0 | 0 | 0 | 0 | 28232.12
2022021304 | 1 | 0.6098 | 48784 | 0.41699 | 15011.64 | 6e-05 | 0.72 | 1 | 5000 | 15011.64 | 0.72 | 0 | 0 | 0 | 0 | 28771.64 | 0 | 0 | 0 | 0 | 0 | 28771.64
2022021305 | 1 | 0.62 | 49600 | 0.4066 | 14637.6 | 6e-05 | 0.72 | 1 | 5000 | 14637.6 | 0.72 | 0 | 0 | 0 | 0 | 29961.68 | 0 | 0 | 0 | 0 | 0 | 29961.68
2022021306 | 1 | 0.6356 | 50848 | 0.38932 | 14015.52 | 6e-05 | 0.72 | 1 | 5000 | 14015.52 | 0.72 | 0 | 0 | 0 | 0 | 31831.76 | 0 | 0 | 0 | 0 | 0 | 31831.76
2022021307 | 1 | 0.65756 | 52604.8 | 0.3841 | 13827.6 | 6e-05 | 0.72 | 1 | 5000 | 13827.6 | 0.72 | 0 | 0 | 0 | 0 | 33776.48 | 0 | 0 | 0 | 0 | 0 | 33776.48
2022021308 | 1 | 0.67385 | 53908 | 0.34983 | 12593.88 | 0.03377 | 405.24 | 1 | 5000 | 12593.88 | 405.24 | 0 | 0 | 0 | 0 | 35908.88 | 0 | 0 | 0 | 0 | 0 | 35908.88
2022021309 | 1 | 0.66194 | 52955.2 | 0.27327 | 9837.72 | 0.47364 | 5683.68 | 1 | 5000 | 9837.72 | 5683.68 | 0 | 0 | 0 | 0 | 32433.8 | 0 | 0 | 0 | 0 | 0 | 32433.8
2022021310 | 1 | 0.63131 | 50504.8 | 0.14212 | 5116.32 | 0.84384 | 10126.08 | 1 | 5000 | 5116.32 | 10126.08 | 0 | 0 | 0 | 0 | 30262.4 | 0 | 0 | 0 | 0 | 0 | 30262.4
2022021311 | 1 | 0.59468 | 47574.4 | 0.11652 | 4194.72 | 0.86653 | 10398.36 | 1 | 5000 | 4194.72 | 10398.36 | 0 | 0 | 0 | 0 | 27981.32 | 0 | 0 | 0 | 0 | 0 | 27981.32
2022021312 | 1 | 0.55913 | 44730.4 | 0.08552 | 3078.72 | 0.84764 | 10171.68 | 1 | 5000 | 3078.72 | 10171.68 | 0 | 0 | 0 | 0 | 26480 | 0 | 0 | 0 | 0 | 0 | 26480
2022021313 | 1 | 0.52875 | 42300 | 0.05458 | 1964.88 | 0.82739 | 9928.68 | 1 | 5000 | 1964.88 | 9928.68 | 0 | 0 | 0 | 0 | 25406.44 | 0 | 0 | 0 | 0 | 0 | 25406.44
2022021314 | 1 | 0.50517 | 40413.6 | 0.04988 | 1795.68 | 0.83002 | 9960.24 | 1 | 5000 | 1795.68 | 9960.24 | 0 | 0 | 0 | 0 | 23657.68 | 0 | 0 | 0 | 0 | 0 | 23657.68
2022021315 | 1 | 0.48831 | 39064.8 | 0.05918 | 2130.48 | 0.85129 | 10215.48 | 1 | 5000 | 2130.48 | 10215.48 | 0 | 0 | 0 | 0 | 21718.84 | 0 | 0 | 0 | 0 | 0 | 21718.84
2022021316 | 1 | 0.4808 | 38464 | 0.07485 | 2694.6 | 0.86783 | 10413.96 | 1 | 5000 | 2694.6 | 10413.96 | 0 | 0 | 0 | 0 | 20355.44 | 0 | 0 | 0 | 0 | 0 | 20355.44
2022021317 | 1 | 0.48251 | 38600.8 | 0.09179 | 3304.44 | 0.81188 | 9742.56 | 1 | 5000 | 3304.44 | 9742.56 | 0 | 0 | 0 | 0 | 20553.8 | 0 | 0 | 0 | 0 | 0 | 20553.8
2022021318 | 1 | 0.48766 | 39012.8 | 0.09991 | 3596.76 | 0.41799 | 5015.88 | 1 | 5000 | 3596.76 | 5015.88 | 0 | 0 | 0 | 0 | 25400.16 | 0 | 0 | 0 | 0 | 0 | 25400.16
2022021319 | 1 | 0.50682 | 40545.6 | 0.11048 | 3977.28 | 0.02462 | 295.44 | 1 | 5000 | 3977.28 | 295.44 | 0 | 0 | 0 | 0 | 31272.88 | 0 | 0 | 0 | 0 | 0 | 31272.88
2022021320 | 1 | 0.5203 | 41624 | 0.17886 | 6438.96 | 0 | 0 | 1 | 5000 | 6438.96 | 0 | 0 | 0 | 0 | 0 | 30185.04 | 0 | 0 | 0 | 0 | 0 | 30185.04
2022021321 | 1 | 0.52945 | 42356 | 0.27727 | 9981.72 | 0 | 0 | 1 | 5000 | 9981.72 | 0 | 0 | 0 | 0 | 0 | 27374.28 | 0 | 0 | 0 | 0 | 0 | 27374.28
2022021322 | 1 | 0.54098 | 43278.4 | 0.38822 | 13975.92 | 0 | 0 | 1 | 5000 | 13975.92 | 0 | 0 | 0 | 0 | 0 | 24302.48 | 0 | 0 | 0 | 0 | 0 | 24302.48
2022021323 | 1 | 0.53589 | 42871.2 | 0.48516 | 17465.76 | 0 | 0 | 1 | 5000 | 17465.76 | 0 | 0 | 0 | 0 | 0 | 20405.44 | 0 | 0 | 0 | 0 | 0 | 20405.44
2022021324 | 1 | 0.52271 | 41816.8 | 0.54413 | 19588.68 | 0 | 0 | 1 | 5000 | 19588.68 | 0 | 0 | 0 | 0 | 0 | 17228.12 | 0 | 0 | 0 | 0 | 0 | 17228.12
2022021401 | 2 | 0.51443 | 41154.4 | 0.58878 | 21196.08 | 0 | 0 | 1 | 5000 | 21196.08 | 0 | 0 | 0 | 0 | 0 | 14958.32 | 0 | 0 | 0 | 0 | 0 | 14958.32
2022021402 | 2 | 0.51474 | 41179.2 | 0.59691 | 21488.76 | 0 | 0 | 1 | 5000 | 21488.76 | 0 | 0 | 0 | 0 | 0 | 14690.44 | 0 | 0 | 0 | 0 | 0 | 14690.44
2022021403 | 2 | 0.51874 | 41499.2 | 0.5951 | 21423.6 | 0 | 0 | 1 | 5000 | 21423.6 | 0 | 0 | 0 | 0 | 0 | 15075.6 | 0 | 0 | 0 | 0 | 0 | 15075.6
2022021404 | 2 | 0.52981 | 42384.8 | 0.5926 | 21333.6 | 0 | 0 | 1 | 5000 | 21333.6 | 0 | 0 | 0 | 0 | 0 | 16051.2 | 0 | 0 | 0 | 0 | 0 | 16051.2
2022021405 | 2 | 0.55015 | 44012 | 0.57958 | 20864.88 | 0 | 0 | 1 | 5000 | 20864.88 | 0 | 0 | 0 | 0 | 0 | 18147.12 | 0 | 0 | 0 | 0 | 0 | 18147.12
2022021406 | 2 | 0.58823 | 47058.4 | 0.54036 | 19452.96 | 0 | 0 | 1 | 5000 | 19452.96 | 0 | 0 | 0 | 0 | 0 | 22605.44 | 0 | 0 | 0 | 0 | 0 | 22605.44
2022021407 | 2 | 0.64399 | 51519.2 | 0.50733 | 18263.88 | 0 | 0 | 1 | 5000 | 18263.88 | 0 | 0 | 0 | 0 | 0 | 28255.32 | 0 | 0 | 0 | 0 | 0 | 28255.32
2022021408 | 2 | 0.66569 | 53255.2 | 0.47899 | 17243.64 | 0.03528 | 423.36 | 1 | 5000 | 17243.64 | 423.36 | 0 | 0 | 0 | 0 | 30588.2 | 0 | 0 | 0 | 0 | 0 | 30588.2
2022021409 | 2 | 0.63959 | 51167.2 | 0.41536 | 14952.96 | 0.48548 | 5825.76 | 1 | 5000 | 14952.96 | 5825.76 | 0 | 0 | 0 | 0 | 25388.48 | 0 | 0 | 0 | 0 | 0 | 25388.48
2022021410 | 2 | 0.59951 | 47960.8 | 0.26818 | 9654.48 | 0.84791 | 10174.92 | 1 | 5000 | 9654.48 | 10174.92 | 0 | 0 | 0 | 0 | 23131.4 | 0 | 0 | 0 | 0 | 0 | 23131.4
2022021411 | 2 | 0.56514 | 45211.2 | 0.23232 | 8363.52 | 0.87127 | 10455.24 | 1 | 5000 | 8363.52 | 10455.24 | 0 | 0 | 0 | 0 | 21392.44 | 0 | 0 | 0 | 0 | 0 | 21392.44
2022021412 | 2 | 0.5368 | 42944 | 0.23154 | 8335.44 | 0.8522 | 10226.4 | 1 | 5000 | 8335.44 | 10226.4 | 0 | 0 | 0 | 0 | 19382.16 | 0 | 0 | 0 | 0 | 0 | 19382.16
2022021413 | 2 | 0.51571 | 41256.8 | 0.23758 | 8552.88 | 0.83422 | 10010.64 | 1 | 5000 | 8552.88 | 10010.64 | 0 | 0 | 0 | 0 | 17693.28 | 0 | 0 | 0 | 0 | 0 | 17693.28
2022021414 | 2 | 0.50439 | 40351.2 | 0.2693 | 9694.8 | 0.8316 | 9979.2 | 1 | 5000 | 9694.8 | 9979.2 | 0 | 0 | 0 | 0 | 15677.2 | 0 | 0 | 0 | 0 | 0 | 15677.2
2022021415 | 2 | 0.49484 | 39587.2 | 0.29877 | 10755.72 | 0.85024 | 10202.88 | 1 | 5000 | 10755.72 | 10202.88 | 0 | 0 | 0 | 0 | 13628.6 | 0 | 0 | 0 | 0 | 0 | 13628.6
2022021416 | 2 | 0.49083 | 39266.4 | 0.32581 | 11729.16 | 0.85552 | 10266.24 | 1 | 5000 | 11729.16 | 10266.24 | 0 | 0 | 0 | 0 | 12271 | 0 | 0 | 0 | 0 | 0 | 12271
2022021417 | 2 | 0.49316 | 39452.8 | 0.34831 | 12539.16 | 0.78862 | 9463.44 | 1 | 5000 | 12539.16 | 9463.44 | 0 | 0 | 0 | 0 | 12450.2 | 0 | 0 | 0 | 0 | 0 | 12450.2
2022021418 | 2 | 0.49843 | 39874.4 | 0.37844 | 13623.84 | 0.40812 | 4897.44 | 1 | 5000 | 13623.84 | 4897.44 | 0 | 0 | 0 | 0 | 16353.12 | 0 | 0 | 0 | 0 | 0 | 16353.12
2022021419 | 2 | 0.52055 | 41644 | 0.42355 | 15247.8 | 0.02551 | 306.12 | 1 | 5000 | 15247.8 | 306.12 | 0 | 0 | 0 | 0 | 21090.08 | 0 | 0 | 0 | 0 | 0 | 21090.08
2022021420 | 2 | 0.53358 | 42686.4 | 0.56378 | 20296.08 | 6e-05 | 0.72 | 1 | 5000 | 20296.08 | 0.72 | 0 | 0 | 0 | 0 | 17389.6 | 0 | 0 | 0 | 0 | 0 | 17389.6
2022021421 | 2 | 0.53365 | 42692 | 0.63514 | 22865.04 | 6e-05 | 0.72 | 1 | 5000 | 22865.04 | 0.72 | 0 | 0 | 0 | 0 | 14826.24 | 0 | 0 | 0 | 0 | 0 | 14826.24
2022021422 | 2 | 0.52423 | 41938.4 | 0.64312 | 23152.32 | 6e-05 | 0.72 | 1 | 5000 | 23152.32 | 0.72 | 0 | 0 | 0 | 0 | 13785.36 | 0 | 0 | 0 | 0 | 0 | 13785.36
2022021423 | 2 | 0.50429 | 40343.2 | 0.63754 | 22951.44 | 6e-05 | 0.72 | 1 | 5000 | 22951.44 | 0.72 | 0 | 0 | 0 | 0 | 12391.04 | 0 | 0 | 0 | 0 | 0 | 12391.04
2022021424 | 2 | 0.48353 | 38682.4 | 0.63229 | 22762.44 | 6e-05 | 0.72 | 1 | 5000 | 22762.44 | 0.72 | 0 | 0 | 0 | 0 | 10919.24 | 0 | 0 | 0 | 0 | 0 | 10919.24
2022021501 | 3 | 0.47229 | 37783.2 | 0.63836 | 22980.96 | 6e-05 | 0.72 | 1 | 5000 | 22980.96 | 0.72 | 0 | 0 | 0 | 0 | 9801.52 | 0 | 0 | 0 | 0 | 0 | 9801.52
2022021502 | 3 | 0.46857 | 37485.6 | 0.63642 | 22911.12 | 6e-05 | 0.72 | 1 | 5000 | 22911.12 | 0.72 | 0 | 0 | 0 | 0 | 9573.76 | 0 | 0 | 0 | 0 | 0 | 9573.76
2022021503 | 3 | 0.47017 | 37613.6 | 0.63983 | 23033.88 | 6e-05 | 0.72 | 1 | 5000 | 23033.88 | 0.72 | 0 | 0 | 0 | 0 | 9579 | 0 | 0 | 0 | 0 | 0 | 9579
2022021504 | 3 | 0.47883 | 38306.4 | 0.64015 | 23045.4 | 6e-05 | 0.72 | 1 | 5000 | 23045.4 | 0.72 | 0 | 0 | 0 | 0 | 10260.28 | 0 | 0 | 0 | 0 | 0 | 10260.28
2022021505 | 3 | 0.49606 | 39684.8 | 0.64339 | 23162.04 | 6e-05 | 0.72 | 1 | 5000 | 23162.04 | 0.72 | 0 | 0 | 0 | 0 | 11522.04 | 0 | 0 | 0 | 0 | 0 | 11522.04
2022021506 | 3 | 0.53087 | 42469.6 | 0.64877 | 23355.72 | 6e-05 | 0.72 | 1 | 5000 | 23355.72 | 0.72 | 0 | 0 | 0 | 0 | 14113.16 | 0 | 0 | 0 | 0 | 0 | 14113.16
2022021507 | 3 | 0.58274 | 46619.2 | 0.65563 | 23602.68 | 6e-05 | 0.72 | 1 | 5000 | 23602.68 | 0.72 | 0 | 0 | 0 | 0 | 18015.8 | 0 | 0 | 0 | 0 | 0 | 18015.8
2022021508 | 3 | 0.59974 | 47979.2 | 0.64157 | 23096.52 | 0.02394 | 287.28 | 1 | 5000 | 23096.52 | 287.28 | 0 | 0 | 0 | 0 | 19595.4 | 0 | 0 | 0 | 0 | 0 | 19595.4
2022021509 | 3 | 0.57855 | 46284 | 0.59291 | 21344.76 | 0.24632 | 2955.84 | 1 | 5000 | 21344.76 | 2955.84 | 0 | 0 | 0 | 0 | 16983.4 | 0 | 0 | 0 | 0 | 0 | 16983.4
2022021510 | 3 | 0.55247 | 44197.6 | 0.55274 | 19898.64 | 0.40253 | 4830.36 | 1 | 5000 | 19898.64 | 4830.36 | 0 | 0 | 0 | 0 | 14468.6 | 0 | 0 | 0 | 0 | 0 | 14468.6
2022021511 | 3 | 0.53183 | 42546.4 | 0.59362 | 21370.32 | 0.33227 | 3987.24 | 1 | 5000 | 21370.32 | 3987.24 | 0 | 0 | 0 | 0 | 12188.84 | 0 | 0 | 0 | 0 | 0 | 12188.84
2022021512 | 3 | 0.51759 | 41407.2 | 0.61712 | 22216.32 | 0.18967 | 2276.04 | 1 | 5000 | 22216.32 | 2276.04 | 0 | 0 | 0 | 0 | 11914.84 | 0 | 0 | 0 | 0 | 0 | 11914.84
2022021513 | 3 | 0.50546 | 40436.8 | 0.60555 | 21799.8 | 0.15736 | 1888.32 | 1 | 5000 | 21799.8 | 1888.32 | 0 | 0 | 0 | 0 | 11748.68 | 0 | 0 | 0 | 0 | 0 | 11748.68
2022021514 | 3 | 0.50045 | 40036 | 0.60233 | 21683.88 | 0.15582 | 1869.84 | 1 | 5000 | 21683.88 | 1869.84 | 0 | 0 | 0 | 0 | 11482.28 | 0 | 0 | 0 | 0 | 0 | 11482.28
2022021515 | 3 | 0.49756 | 39804.8 | 0.61635 | 22188.6 | 0.14637 | 1756.44 | 1 | 5000 | 22188.6 | 1756.44 | 0 | 0 | 0 | 0 | 10859.76 | 0 | 0 | 0 | 0 | 0 | 10859.76
2022021516 | 3 | 0.49772 | 39817.6 | 0.62158 | 22376.88 | 0.14553 | 1746.36 | 1 | 5000 | 22376.88 | 1746.36 | 0 | 0 | 0 | 0 | 10694.36 | 0 | 0 | 0 | 0 | 0 | 10694.36
2022021517 | 3 | 0.50035 | 40028 | 0.6236 | 22449.6 | 0.11928 | 1431.36 | 1 | 5000 | 22449.6 | 1431.36 | 0 | 0 | 0 | 0 | 11147.04 | 0 | 0 | 0 | 0 | 0 | 11147.04
2022021518 | 3 | 0.50711 | 40568.8 | 0.64088 | 23071.68 | 0.03989 | 478.68 | 1 | 5000 | 23071.68 | 478.68 | 0 | 0 | 0 | 0 | 12018.44 | 0 | 0 | 0 | 0 | 0 | 12018.44
2022021519 | 3 | 0.52513 | 42010.4 | 0.65786 | 23682.96 | 0.00202 | 24.24 | 1 | 5000 | 23682.96 | 24.24 | 0 | 0 | 0 | 0 | 13303.2 | 0 | 0 | 0 | 0 | 0 | 13303.2
2022021520 | 3 | 0.5326 | 42608 | 0.67768 | 24396.48 | 0.00014 | 1.68 | 1 | 5000 | 24396.48 | 1.68 | 0 | 0 | 0 | 0 | 13209.84 | 0 | 0 | 0 | 0 | 0 | 13209.84
2022021521 | 3 | 0.52502 | 42001.6 | 0.67983 | 24473.88 | 0.00014 | 1.68 | 1 | 5000 | 24473.88 | 1.68 | 0 | 0 | 0 | 0 | 12526.04 | 0 | 0 | 0 | 0 | 0 | 12526.04
2022021522 | 3 | 0.50875 | 40700 | 0.66937 | 24097.32 | 0.00014 | 1.68 | 1 | 5000 | 24097.32 | 1.68 | 0 | 0 | 0 | 0 | 11601 | 0 | 0 | 0 | 0 | 0 | 11601
2022021523 | 3 | 0.48048 | 38438.4 | 0.64558 | 23240.88 | 0.00014 | 1.68 | 1 | 5000 | 23240.88 | 1.68 | 0 | 0 | 0 | 0 | 10195.84 | 0 | 0 | 0 | 0 | 0 | 10195.84
2022021524 | 3 | 0.45163 | 36130.4 | 0.60595 | 21814.2 | 0.00014 | 1.68 | 1 | 5000 | 21814.2 | 1.68 | 0 | 0 | 0 | 0 | 9314.52 | 0 | 0 | 0 | 0 | 0 | 9314.52
2022021601 | 4 | 0.43189 | 34551.2 | 0.57596 | 20734.56 | 0.00014 | 1.68 | 1 | 5000 | 20734.56 | 1.68 | 0 | 0 | 0 | 0 | 8814.96 | 0 | 0 | 0 | 0 | 0 | 8814.96
2022021602 | 4 | 0.4211 | 33688 | 0.57132 | 20567.52 | 0.00014 | 1.68 | 1 | 5000 | 20567.52 | 1.68 | 0 | 0 | 0 | 0 | 8118.8 | 0 | 0 | 0 | 0 | 0 | 8118.8
2022021603 | 4 | 0.41427 | 33141.6 | 0.56411 | 20307.96 | 0.00014 | 1.68 | 1 | 5000 | 20307.96 | 1.68 | 0 | 0 | 0 | 0 | 7831.96 | 0 | 0 | 0 | 0 | 0 | 7831.96
2022021604 | 4 | 0.41403 | 33122.4 | 0.56792 | 20445.12 | 0.00014 | 1.68 | 1 | 5000 | 20445.12 | 1.68 | 0 | 0 | 0 | 0 | 7675.6 | 0 | 0 | 0 | 0 | 0 | 7675.6
2022021605 | 4 | 0.42205 | 33764 | 0.57305 | 20629.8 | 0.00014 | 1.68 | 1 | 5000 | 20629.8 | 1.68 | 0 | 0 | 0 | 0 | 8132.52 | 0 | 0 | 0 | 0 | 0 | 8132.52
2022021606 | 4 | 0.44543 | 35634.4 | 0.59136 | 21288.96 | 0.00014 | 1.68 | 1 | 5000 | 21288.96 | 1.68 | 0 | 0 | 0 | 0 | 9343.76 | 0 | 0 | 0 | 0 | 0 | 9343.76
2022021607 | 4 | 0.48532 | 38825.6 | 0.62755 | 22591.8 | 0.00014 | 1.68 | 1 | 5000 | 22591.8 | 1.68 | 0 | 0 | 0 | 0 | 11232.12 | 0 | 0 | 0 | 0 | 0 | 11232.12
2022021608 | 4 | 0.50193 | 40154.4 | 0.6415 | 23094 | 0.00599 | 71.88 | 1 | 5000 | 23094 | 71.88 | 0 | 0 | 0 | 0 | 11988.52 | 0 | 0 | 0 | 0 | 0 | 11988.52
2022021609 | 4 | 0.50503 | 40402.4 | 0.61872 | 22273.92 | 0.08693 | 1043.16 | 1 | 5000 | 22273.92 | 1043.16 | 0 | 0 | 0 | 0 | 12085.32 | 0 | 0 | 0 | 0 | 0 | 12085.32
2022021610 | 4 | 0.50852 | 40681.6 | 0.59956 | 21584.16 | 0.21541 | 2584.92 | 1 | 5000 | 21584.16 | 2584.92 | 0 | 0 | 0 | 0 | 11512.52 | 0 | 0 | 0 | 0 | 0 | 11512.52
2022021611 | 4 | 0.51398 | 41118.4 | 0.59658 | 21476.88 | 0.2499 | 2998.8 | 1 | 5000 | 21476.88 | 2998.8 | 0 | 0 | 0 | 0 | 11642.72 | 0 | 0 | 0 | 0 | 0 | 11642.72
2022021612 | 4 | 0.51788 | 41430.4 | 0.58608 | 21098.88 | 0.28465 | 3415.8 | 1 | 5000 | 21098.88 | 3415.8 | 0 | 0 | 0 | 0 | 11915.72 | 0 | 0 | 0 | 0 | 0 | 11915.72
2022021613 | 4 | 0.51708 | 41366.4 | 0.55676 | 20043.36 | 0.35766 | 4291.92 | 1 | 5000 | 20043.36 | 4291.92 | 0 | 0 | 0 | 0 | 12031.12 | 0 | 0 | 0 | 0 | 0 | 12031.12
2022021614 | 4 | 0.51714 | 41371.2 | 0.53288 | 19183.68 | 0.43079 | 5169.48 | 1 | 5000 | 19183.68 | 5169.48 | 0 | 0 | 0 | 0 | 12018.04 | 0 | 0 | 0 | 0 | 0 | 12018.04
2022021615 | 4 | 0.51817 | 41453.6 | 0.52927 | 19053.72 | 0.45218 | 5426.16 | 1 | 5000 | 19053.72 | 5426.16 | 0 | 0 | 0 | 0 | 11973.72 | 0 | 0 | 0 | 0 | 0 | 11973.72
2022021616 | 4 | 0.5188 | 41504 | 0.54588 | 19651.68 | 0.39203 | 4704.36 | 1 | 5000 | 19651.68 | 4704.36 | 0 | 0 | 0 | 0 | 12147.96 | 0 | 0 | 0 | 0 | 0 | 12147.96
2022021617 | 4 | 0.52348 | 41878.4 | 0.601 | 21636 | 0.23989 | 2878.68 | 1 | 5000 | 21636 | 2878.68 | 0 | 0 | 0 | 0 | 12363.72 | 0 | 0 | 0 | 0 | 0 | 12363.72
2022021618 | 4 | 0.53033 | 42426.4 | 0.64688 | 23287.68 | 0.10249 | 1229.88 | 1 | 5000 | 23287.68 | 1229.88 | 0 | 0 | 0 | 0 | 12908.84 | 0 | 0 | 0 | 0 | 0 | 12908.84
2022021619 | 4 | 0.54211 | 43368.8 | 0.67362 | 24250.32 | 0.00829 | 99.48 | 1 | 5000 | 24250.32 | 99.48 | 0 | 0 | 0 | 0 | 14019 | 0 | 0 | 0 | 0 | 0 | 14019
2022021620 | 4 | 0.54454 | 43563.2 | 0.69912 | 25168.32 | 0 | 0 | 1 | 5000 | 25168.32 | 0 | 0 | 0 | 0 | 0 | 13394.88 | 0 | 0 | 0 | 0 | 0 | 13394.88
2022021621 | 4 | 0.53435 | 42748 | 0.6938 | 24976.8 | 0 | 0 | 1 | 5000 | 24976.8 | 0 | 0 | 0 | 0 | 0 | 12771.2 | 0 | 0 | 0 | 0 | 0 | 12771.2
2022021622 | 4 | 0.51563 | 41250.4 | 0.68511 | 24663.96 | 0 | 0 | 1 | 5000 | 24663.96 | 0 | 0 | 0 | 0 | 0 | 11586.44 | 0 | 0 | 0 | 0 | 0 | 11586.44
2022021623 | 4 | 0.48605 | 38884 | 0.6477 | 23317.2 | 0 | 0 | 1 | 5000 | 23317.2 | 0 | 0 | 0 | 0 | 0 | 10566.8 | 0 | 0 | 0 | 0 | 0 | 10566.8
2022021624 | 4 | 0.45721 | 36576.8 | 0.60683 | 21845.88 | 0 | 0 | 1 | 5000 | 21845.88 | 0 | 0 | 0 | 0 | 0 | 9730.92 | 0 | 0 | 0 | 0 | 0 | 9730.92
2022021701 | 5 | 0.43527 | 34821.6 | 0.5717 | 20581.2 | 0 | 0 | 1 | 5000 | 20581.2 | 0 | 0 | 0 | 0 | 0 | 9240.4 | 0 | 0 | 0 | 0 | 0 | 9240.4
2022021702 | 5 | 0.42142 | 33713.6 | 0.54092 | 19473.12 | 0 | 0 | 1 | 5000 | 19473.12 | 0 | 0 | 0 | 0 | 0 | 9240.48 | 0 | 0 | 0 | 0 | 0 | 9240.48
2022021703 | 5 | 0.41457 | 33165.6 | 0.52597 | 18934.92 | 0 | 0 | 1 | 5000 | 18934.92 | 0 | 0 | 0 | 0 | 0 | 9230.68 | 0 | 0 | 0 | 0 | 0 | 9230.68
2022021704 | 5 | 0.41173 | 32938.4 | 0.53891 | 19400.76 | 0 | 0 | 1 | 5000 | 19400.76 | 0 | 0 | 0 | 0 | 0 | 8537.64 | 0 | 0 | 0 | 0 | 0 | 8537.64
2022021705 | 5 | 0.41832 | 33465.6 | 0.55849 | 20105.64 | 0 | 0 | 1 | 5000 | 20105.64 | 0 | 0 | 0 | 0 | 0 | 8359.96 | 0 | 0 | 0 | 0 | 0 | 8359.96
2022021706 | 5 | 0.44132 | 35305.6 | 0.58673 | 21122.28 | 0 | 0 | 1 | 5000 | 21122.28 | 0 | 0 | 0 | 0 | 0 | 9183.32 | 0 | 0 | 0 | 0 | 0 | 9183.32
2022021707 | 5 | 0.48089 | 38471.2 | 0.63636 | 22908.96 | 0 | 0 | 1 | 5000 | 22908.96 | 0 | 0 | 0 | 0 | 0 | 10562.24 | 0 | 0 | 0 | 0 | 0 | 10562.24
2022021708 | 5 | 0.5032 | 40256 | 0.63784 | 22962.24 | 0.00694 | 83.28 | 1 | 5000 | 22962.24 | 83.28 | 0 | 0 | 0 | 0 | 12210.48 | 0 | 0 | 0 | 0 | 0 | 12210.48
2022021709 | 5 | 0.51162 | 40929.6 | 0.61667 | 22200.12 | 0.1144 | 1372.8 | 1 | 5000 | 22200.12 | 1372.8 | 0 | 0 | 0 | 0 | 12356.68 | 0 | 0 | 0 | 0 | 0 | 12356.68
2022021710 | 5 | 0.52662 | 42129.6 | 0.61358 | 22088.88 | 0.15832 | 1899.84 | 1 | 5000 | 22088.88 | 1899.84 | 0 | 0 | 0 | 0 | 13140.88 | 0 | 0 | 0 | 0 | 0 | 13140.88
2022021711 | 5 | 0.5411 | 43288 | 0.63565 | 22883.4 | 0.17152 | 2058.24 | 1 | 5000 | 22883.4 | 2058.24 | 0 | 0 | 0 | 0 | 13346.36 | 0 | 0 | 0 | 0 | 0 | 13346.36
2022021712 | 5 | 0.55511 | 44408.8 | 0.65005 | 23401.8 | 0.18614 | 2233.68 | 1 | 5000 | 23401.8 | 2233.68 | 0 | 0 | 0 | 0 | 13773.32 | 0 | 0 | 0 | 0 | 0 | 13773.32
2022021713 | 5 | 0.56509 | 45207.2 | 0.64846 | 23344.56 | 0.20133 | 2415.96 | 1 | 5000 | 23344.56 | 2415.96 | 0 | 0 | 0 | 0 | 14446.68 | 0 | 0 | 0 | 0 | 0 | 14446.68
2022021714 | 5 | 0.57144 | 45715.2 | 0.63419 | 22830.84 | 0.27918 | 3350.16 | 1 | 5000 | 22830.84 | 3350.16 | 0 | 0 | 0 | 0 | 14534.2 | 0 | 0 | 0 | 0 | 0 | 14534.2
2022021715 | 5 | 0.57634 | 46107.2 | 0.61776 | 22239.36 | 0.33392 | 4007.04 | 1 | 5000 | 22239.36 | 4007.04 | 0 | 0 | 0 | 0 | 14860.8 | 0 | 0 | 0 | 0 | 0 | 14860.8
2022021716 | 5 | 0.58057 | 46445.6 | 0.59348 | 21365.28 | 0.39446 | 4733.52 | 1 | 5000 | 21365.28 | 4733.52 | 0 | 0 | 0 | 0 | 15346.8 | 0 | 0 | 0 | 0 | 0 | 15346.8
2022021717 | 5 | 0.58937 | 47149.6 | 0.54902 | 19764.72 | 0.51024 | 6122.88 | 1 | 5000 | 19764.72 | 6122.88 | 0 | 0 | 0 | 0 | 16262 | 0 | 0 | 0 | 0 | 0 | 16262
2022021718 | 5 | 0.5954 | 47632 | 0.48164 | 17339.04 | 0.34574 | 4148.88 | 1 | 5000 | 17339.04 | 4148.88 | 0 | 0 | 0 | 0 | 21144.08 | 0 | 0 | 0 | 0 | 0 | 21144.08
2022021719 | 5 | 0.61435 | 49148 | 0.38511 | 13863.96 | 0.02498 | 299.76 | 1 | 5000 | 13863.96 | 299.76 | 0 | 0 | 0 | 0 | 29984.28 | 0 | 0 | 0 | 0 | 0 | 29984.28
2022021720 | 5 | 0.62553 | 50042.4 | 0.33409 | 12027.24 | 0 | 0 | 1 | 5000 | 12027.24 | 0 | 0 | 0 | 0 | 0 | 33015.16 | 0 | 0 | 0 | 0 | 0 | 33015.16
2022021721 | 5 | 0.62689 | 50151.2 | 0.32628 | 11746.08 | 0 | 0 | 1 | 5000 | 11746.08 | 0 | 0 | 0 | 0 | 0 | 33405.12 | 0 | 0 | 0 | 0 | 0 | 33405.12
2022021722 | 5 | 0.61959 | 49567.2 | 0.32236 | 11604.96 | 0 | 0 | 1 | 5000 | 11604.96 | 0 | 0 | 0 | 0 | 0 | 32962.24 | 0 | 0 | 0 | 0 | 0 | 32962.24
2022021723 | 5 | 0.59913 | 47930.4 | 0.30783 | 11081.88 | 0 | 0 | 1 | 5000 | 11081.88 | 0 | 0 | 0 | 0 | 0 | 31848.52 | 0 | 0 | 0 | 0 | 0 | 31848.52
2022021724 | 5 | 0.58191 | 46552.8 | 0.29689 | 10688.04 | 0 | 0 | 1 | 5000 | 10688.04 | 0 | 0 | 0 | 0 | 0 | 30864.76 | 0 | 0 | 0 | 0 | 0 | 30864.76
2022021801 | 6 | 0.57386 | 45908.8 | 0.28836 | 10380.96 | 0 | 0 | 1 | 5000 | 10380.96 | 0 | 0 | 0 | 0 | 0 | 30527.84 | 0 | 0 | 0 | 0 | 0 | 30527.84
2022021802 | 6 | 0.57207 | 45765.6 | 0.2514 | 9050.4 | 0 | 0 | 1 | 5000 | 9050.4 | 0 | 0 | 0 | 0 | 0 | 31715.2 | 0 | 0 | 0 | 0 | 0 | 31715.2
2022021803 | 6 | 0.57803 | 46242.4 | 0.23144 | 8331.84 | 0 | 0 | 1 | 5000 | 8331.84 | 0 | 0 | 0 | 0 | 0 | 32910.56 | 0 | 0 | 0 | 0 | 0 | 32910.56
2022021804 | 6 | 0.59005 | 47204 | 0.21507 | 7742.52 | 0 | 0 | 1 | 5000 | 7742.52 | 0 | 0 | 0 | 0 | 0 | 34461.48 | 0 | 0 | 0 | 0 | 0 | 34461.48
2022021805 | 6 | 0.60829 | 48663.2 | 0.20505 | 7381.8 | 0 | 0 | 1 | 5000 | 7381.8 | 0 | 0 | 0 | 0 | 0 | 36281.4 | 0 | 0 | 0 | 0 | 0 | 36281.4
2022021806 | 6 | 0.64318 | 51454.4 | 0.1995 | 7182 | 0 | 0 | 1 | 5000 | 7182 | 0 | 0 | 0 | 0 | 0 | 39272.4 | 0 | 0 | 0 | 0 | 0 | 39272.4
2022021807 | 6 | 0.69702 | 55761.6 | 0.21176 | 7623.36 | 5e-05 | 0.6 | 1 | 5000 | 7623.36 | 0.6 | 0 | 0 | 0 | 0 | 43137.64 | 0 | 0 | 0 | 0 | 0 | 43137.64
2022021808 | 6 | 0.72354 | 57883.2 | 0.22961 | 8265.96 | 0.03514 | 421.68 | 1 | 5000 | 8265.96 | 421.68 | 0 | 0 | 0 | 0 | 44195.56 | 0 | 0 | 0 | 0 | 0 | 44195.56
2022021809 | 6 | 0.71216 | 56972.8 | 0.23277 | 8379.72 | 0.45107 | 5412.84 | 1 | 5000 | 8379.72 | 5412.84 | 0 | 0 | 0 | 0 | 38180.24 | 0 | 0 | 0 | 0 | 0 | 38180.24
2022021810 | 6 | 0.68334 | 54667.2 | 0.17709 | 6375.24 | 0.7934 | 9520.8 | 1 | 5000 | 6375.24 | 9520.8 | 0 | 0 | 0 | 0 | 33771.16 | 0 | 0 | 0 | 0 | 0 | 33771.16
2022021811 | 6 | 0.65102 | 52081.6 | 0.1321 | 4755.6 | 0.84648 | 10157.76 | 1 | 5000 | 4755.6 | 10157.76 | 0 | 0 | 0 | 0 | 32168.24 | 0 | 0 | 0 | 0 | 0 | 32168.24
2022021812 | 6 | 0.6157 | 49256 | 0.09668 | 3480.48 | 0.84356 | 10122.72 | 1 | 5000 | 3480.48 | 10122.72 | 0 | 0 | 0 | 0 | 30652.8 | 0 | 0 | 0 | 0 | 0 | 30652.8
2022021813 | 6 | 0.58087 | 46469.6 | 0.07456 | 2684.16 | 0.82882 | 9945.84 | 1 | 5000 | 2684.16 | 9945.84 | 0 | 0 | 0 | 0 | 28839.6 | 0 | 0 | 0 | 0 | 0 | 28839.6
2022021814 | 6 | 0.55471 | 44376.8 | 0.0637 | 2293.2 | 0.82802 | 9936.24 | 1 | 5000 | 2293.2 | 9936.24 | 0 | 0 | 0 | 0 | 27147.36 | 0 | 0 | 0 | 0 | 0 | 27147.36
2022021815 | 6 | 0.53322 | 42657.6 | 0.0549 | 1976.4 | 0.84515 | 10141.8 | 1 | 5000 | 1976.4 | 10141.8 | 0 | 0 | 0 | 0 | 25539.4 | 0 | 0 | 0 | 0 | 0 | 25539.4
2022021816 | 6 | 0.51894 | 41515.2 | 0.05139 | 1850.04 | 0.85522 | 10262.64 | 1 | 5000 | 1850.04 | 10262.64 | 0 | 0 | 0 | 0 | 24402.52 | 0 | 0 | 0 | 0 | 0 | 24402.52
2022021817 | 6 | 0.51518 | 41214.4 | 0.04969 | 1788.84 | 0.81238 | 9748.56 | 1 | 5000 | 1788.84 | 9748.56 | 0 | 0 | 0 | 0 | 24677 | 0 | 0 | 0 | 0 | 0 | 24677
2022021818 | 6 | 0.52294 | 41835.2 | 0.0459 | 1652.4 | 0.44444 | 5333.28 | 1 | 5000 | 1652.4 | 5333.28 | 0 | 0 | 0 | 0 | 29849.52 | 0 | 0 | 0 | 0 | 0 | 29849.52
2022021819 | 6 | 0.55217 | 44173.6 | 0.05726 | 2061.36 | 0.03331 | 399.72 | 1 | 5000 | 2061.36 | 399.72 | 0 | 0 | 0 | 0 | 36712.52 | 0 | 0 | 0 | 0 | 0 | 36712.52
2022021820 | 6 | 0.56883 | 45506.4 | 0.09554 | 3439.44 | 6e-05 | 0.72 | 1 | 5000 | 3439.44 | 0.72 | 0 | 0 | 0 | 0 | 37066.24 | 0 | 0 | 0 | 0 | 0 | 37066.24
2022021821 | 6 | 0.57378 | 45902.4 | 0.15576 | 5607.36 | 6e-05 | 0.72 | 1 | 5000 | 5607.36 | 0.72 | 0 | 0 | 0 | 0 | 35294.32 | 0 | 0 | 0 | 0 | 0 | 35294.32
2022021822 | 6 | 0.57348 | 45878.4 | 0.21665 | 7799.4 | 6e-05 | 0.72 | 1 | 5000 | 7799.4 | 0.72 | 0 | 0 | 0 | 0 | 33078.28 | 0 | 0 | 0 | 0 | 0 | 33078.28
2022021823 | 6 | 0.56666 | 45332.8 | 0.24863 | 8950.68 | 6e-05 | 0.72 | 1 | 5000 | 8950.68 | 0.72 | 0 | 0 | 0 | 0 | 31381.4 | 0 | 0 | 0 | 0 | 0 | 31381.4
2022021824 | 6 | 0.55612 | 44489.6 | 0.25499 | 9179.64 | 6e-05 | 0.72 | 1 | 5000 | 9179.64 | 0.72 | 0 | 0 | 0 | 0 | 30309.24 | 0 | 0 | 0 | 0 | 0 | 30309.24
2022021901 | 7 | 0.54906 | 43924.8 | 0.25601 | 9216.36 | 6e-05 | 0.72 | 1 | 5000 | 9216.36 | 0.72 | 0 | 0 | 0 | 0 | 29707.72 | 0 | 0 | 0 | 0 | 0 | 29707.72
2022021902 | 7 | 0.54758 | 43806.4 | 0.26808 | 9650.88 | 6e-05 | 0.72 | 1 | 5000 | 9650.88 | 0.72 | 0 | 0 | 0 | 0 | 29154.8 | 0 | 0 | 0 | 0 | 0 | 29154.8
2022021903 | 7 | 0.55035 | 44028 | 0.26792 | 9645.12 | 6e-05 | 0.72 | 1 | 5000 | 9645.12 | 0.72 | 0 | 0 | 0 | 0 | 29382.16 | 0 | 0 | 0 | 0 | 0 | 29382.16
2022021904 | 7 | 0.55628 | 44502.4 | 0.26566 | 9563.76 | 6e-05 | 0.72 | 1 | 5000 | 9563.76 | 0.72 | 0 | 0 | 0 | 0 | 29937.92 | 0 | 0 | 0 | 0 | 0 | 29937.92
2022021905 | 7 | 0.56761 | 45408.8 | 0.24953 | 8983.08 | 6e-05 | 0.72 | 1 | 5000 | 8983.08 | 0.72 | 0 | 0 | 0 | 0 | 31425 | 0 | 0 | 0 | 0 | 0 | 31425
2022021906 | 7 | 0.58792 | 47033.6 | 0.22905 | 8245.8 | 6e-05 | 0.72 | 1 | 5000 | 8245.8 | 0.72 | 0 | 0 | 0 | 0 | 33787.08 | 0 | 0 | 0 | 0 | 0 | 33787.08
2022021907 | 7 | 0.61522 | 49217.6 | 0.20515 | 7385.4 | 6e-05 | 0.72 | 1 | 5000 | 7385.4 | 0.72 | 0 | 0 | 0 | 0 | 36831.48 | 0 | 0 | 0 | 0 | 0 | 36831.48
2022021908 | 7 | 0.63445 | 50756 | 0.20156 | 7256.16 | 0.04317 | 518.04 | 1 | 5000 | 7256.16 | 518.04 | 0 | 0 | 0 | 0 | 37981.8 | 0 | 0 | 0 | 0 | 0 | 37981.8
2022021909 | 7 | 0.62246 | 49796.8 | 0.15821 | 5695.56 | 0.47243 | 5669.16 | 1 | 5000 | 5695.56 | 5669.16 | 0 | 0 | 0 | 0 | 33432.08 | 0 | 0 | 0 | 0 | 0 | 33432.08
2022021910 | 7 | 0.59185 | 47348 | 0.10556 | 3800.16 | 0.78538 | 9424.56 | 1 | 5000 | 3800.16 | 9424.56 | 0 | 0 | 0 | 0 | 29123.28 | 0 | 0 | 0 | 0 | 0 | 29123.28
2022021911 | 7 | 0.561 | 44880 | 0.11252 | 4050.72 | 0.81797 | 9815.64 | 1 | 5000 | 4050.72 | 9815.64 | 0 | 0 | 0 | 0 | 26013.64 | 0 | 0 | 0 | 0 | 0 | 26013.64
2022021912 | 7 | 0.5299 | 42392 | 0.136 | 4896 | 0.81706 | 9804.72 | 1 | 5000 | 4896 | 9804.72 | 0 | 0 | 0 | 0 | 22691.28 | 0 | 0 | 0 | 0 | 0 | 22691.28
2022021913 | 7 | 0.50466 | 40372.8 | 0.17892 | 6441.12 | 0.81578 | 9789.36 | 1 | 5000 | 6441.12 | 9789.36 | 0 | 0 | 0 | 0 | 19142.32 | 0 | 0 | 0 | 0 | 0 | 19142.32
2022021914 | 7 | 0.48672 | 38937.6 | 0.21211 | 7635.96 | 0.82314 | 9877.68 | 1 | 5000 | 7635.96 | 9877.68 | 0 | 0 | 0 | 0 | 16423.96 | 0 | 0 | 0 | 0 | 0 | 16423.96
2022021915 | 7 | 0.47496 | 37996.8 | 0.2421 | 8715.6 | 0.82137 | 9856.44 | 1 | 5000 | 8715.6 | 9856.44 | 0 | 0 | 0 | 0 | 14424.76 | 0 | 0 | 0 | 0 | 0 | 14424.76
2022021916 | 7 | 0.47108 | 37686.4 | 0.26676 | 9603.36 | 0.83532 | 10023.84 | 1 | 5000 | 9603.36 | 10023.84 | 0 | 0 | 0 | 0 | 13059.2 | 0 | 0 | 0 | 0 | 0 | 13059.2
2022021917 | 7 | 0.47344 | 37875.2 | 0.30014 | 10805.04 | 0.78957 | 9474.84 | 1 | 5000 | 10805.04 | 9474.84 | 0 | 0 | 0 | 0 | 12595.32 | 0 | 0 | 0 | 0 | 0 | 12595.32
2022021918 | 7 | 0.47883 | 38306.4 | 0.32633 | 11747.88 | 0.44114 | 5293.68 | 1 | 5000 | 11747.88 | 5293.68 | 0 | 0 | 0 | 0 | 16264.84 | 0 | 0 | 0 | 0 | 0 | 16264.84
2022021919 | 7 | 0.49769 | 39815.2 | 0.34318 | 12354.48 | 0.03475 | 417 | 1 | 5000 | 12354.48 | 417 | 0 | 0 | 0 | 0 | 22043.72 | 0 | 0 | 0 | 0 | 0 | 22043.72
2022021920 | 7 | 0.51079 | 40863.2 | 0.45459 | 16365.24 | 8e-05 | 0.96 | 1 | 5000 | 16365.24 | 0.96 | 0 | 0 | 0 | 0 | 19497 | 0 | 0 | 0 | 0 | 0 | 19497
2022021921 | 7 | 0.51471 | 41176.8 | 0.57019 | 20526.84 | 8e-05 | 0.96 | 1 | 5000 | 20526.84 | 0.96 | 0 | 0 | 0 | 0 | 15649 | 0 | 0 | 0 | 0 | 0 | 15649
2022021922 | 7 | 0.51447 | 41157.6 | 0.6083 | 21898.8 | 8e-05 | 0.96 | 1 | 5000 | 21898.8 | 0.96 | 0 | 0 | 0 | 0 | 14257.84 | 0 | 0 | 0 | 0 | 0 | 14257.84
2022021923 | 7 | 0.50914 | 40731.2 | 0.6105 | 21978 | 8e-05 | 0.96 | 1 | 5000 | 21978 | 0.96 | 0 | 0 | 0 | 0 | 13752.24 | 0 | 0 | 0 | 0 | 0 | 13752.24
2022021924 | 7 | 0.49952 | 39961.6 | 0.60516 | 21785.76 | 8e-05 | 0.96 | 1 | 5000 | 21785.76 | 0.96 | 0 | 0 | 0 | 0 | 13174.88 | 0 | 0 | 0 | 0 | 0 | 13174.88
2022022001 | 1 | 0.4923 | 39384 | 0.59837 | 21541.32 | 8e-05 | 0.96 | 1 | 5000 | 21541.32 | 0.96 | 0 | 0 | 0 | 0 | 12841.72 | 0 | 0 | 0 | 0 | 0 | 12841.72
2022022002 | 1 | 0.48845 | 39076 | 0.60089 | 21632.04 | 8e-05 | 0.96 | 1 | 5000 | 21632.04 | 0.96 | 0 | 0 | 0 | 0 | 12443 | 0 | 0 | 0 | 0 | 0 | 12443
2022022003 | 1 | 0.48735 | 38988 | 0.60499 | 21779.64 | 8e-05 | 0.96 | 1 | 5000 | 21779.64 | 0.96 | 0 | 0 | 0 | 0 | 12207.4 | 0 | 0 | 0 | 0 | 0 | 12207.4
2022022004 | 1 | 0.4892 | 39136 | 0.60565 | 21803.4 | 8e-05 | 0.96 | 1 | 5000 | 21803.4 | 0.96 | 0 | 0 | 0 | 0 | 12331.64 | 0 | 0 | 0 | 0 | 0 | 12331.64
2022022005 | 1 | 0.49433 | 39546.4 | 0.59968 | 21588.48 | 8e-05 | 0.96 | 1 | 5000 | 21588.48 | 0.96 | 0 | 0 | 0 | 0 | 12956.96 | 0 | 0 | 0 | 0 | 0 | 12956.96
2022022006 | 1 | 0.50662 | 40529.6 | 0.59788 | 21523.68 | 8e-05 | 0.96 | 1 | 5000 | 21523.68 | 0.96 | 0 | 0 | 0 | 0 | 14004.96 | 0 | 0 | 0 | 0 | 0 | 14004.96
2022022007 | 1 | 0.52277 | 41821.6 | 0.59439 | 21398.04 | 9e-05 | 1.08 | 1 | 5000 | 21398.04 | 1.08 | 0 | 0 | 0 | 0 | 15422.48 | 0 | 0 | 0 | 0 | 0 | 15422.48
2022022008 | 1 | 0.53772 | 43017.6 | 0.59554 | 21439.44 | 0.02156 | 258.72 | 1 | 5000 | 21439.44 | 258.72 | 0 | 0 | 0 | 0 | 16319.44 | 0 | 0 | 0 | 0 | 0 | 16319.44
2022022009 | 1 | 0.5422 | 43376 | 0.55863 | 20110.68 | 0.18357 | 2202.84 | 1 | 5000 | 20110.68 | 2202.84 | 0 | 0 | 0 | 0 | 16062.48 | 0 | 0 | 0 | 0 | 0 | 16062.48
2022022010 | 1 | 0.53563 | 42850.4 | 0.5204 | 18734.4 | 0.29784 | 3574.08 | 1 | 5000 | 18734.4 | 3574.08 | 0 | 0 | 0 | 0 | 15541.92 | 0 | 0 | 0 | 0 | 0 | 15541.92
2022022011 | 1 | 0.51262 | 41009.6 | 0.50739 | 18266.04 | 0.36329 | 4359.48 | 1 | 5000 | 18266.04 | 4359.48 | 0 | 0 | 0 | 0 | 13384.08 | 0 | 0 | 0 | 0 | 0 | 13384.08
2022022012 | 1 | 0.49258 | 39406.4 | 0.48696 | 17530.56 | 0.45596 | 5471.52 | 1 | 5000 | 17530.56 | 5471.52 | 0 | 0 | 0 | 0 | 11404.32 | 0 | 0 | 0 | 0 | 0 | 11404.32
2022022013 | 1 | 0.47902 | 38321.6 | 0.46927 | 16893.72 | 0.51763 | 6211.56 | 1 | 5000 | 16893.72 | 6211.56 | 0 | 0 | 0 | 0 | 10216.32 | 0 | 0 | 0 | 0 | 0 | 10216.32
2022022014 | 1 | 0.46943 | 37554.4 | 0.45746 | 16468.56 | 0.57565 | 6907.8 | 1 | 5000 | 16468.56 | 6907.8 | 0 | 0 | 0 | 0 | 9178.04 | 0 | 0 | 0 | 0 | 0 | 9178.04
2022022015 | 1 | 0.46855 | 37484 | 0.46909 | 16887.24 | 0.56413 | 6769.56 | 1 | 5000 | 16887.24 | 6769.56 | 0 | 0 | 0 | 0 | 8827.2 | 0 | 0 | 0 | 0 | 0 | 8827.2
2022022016 | 1 | 0.46861 | 37488.8 | 0.48793 | 17565.48 | 0.51764 | 6211.68 | 1 | 5000 | 17565.48 | 6211.68 | 0 | 0 | 0 | 0 | 8711.64 | 0 | 0 | 0 | 0 | 0 | 8711.64
2022022017 | 1 | 0.4736 | 37888 | 0.49543 | 17835.48 | 0.45855 | 5502.6 | 1 | 5000 | 17835.48 | 5502.6 | 0 | 0 | 0 | 0 | 9549.92 | 0 | 0 | 0 | 0 | 0 | 9549.92
2022022018 | 1 | 0.48322 | 38657.6 | 0.51402 | 18504.72 | 0.30101 | 3612.12 | 1 | 5000 | 18504.72 | 3612.12 | 0 | 0 | 0 | 0 | 11540.76 | 0 | 0 | 0 | 0 | 0 | 11540.76
2022022019 | 1 | 0.49989 | 39991.2 | 0.53985 | 19434.6 | 0.03363 | 403.56 | 1 | 5000 | 19434.6 | 403.56 | 0 | 0 | 0 | 0 | 15153.04 | 0 | 0 | 0 | 0 | 0 | 15153.04
2022022020 | 1 | 0.50924 | 40739.2 | 0.59323 | 21356.28 | 7e-05 | 0.84 | 1 | 5000 | 21356.28 | 0.84 | 0 | 0 | 0 | 0 | 14382.08 | 0 | 0 | 0 | 0 | 0 | 14382.08
2022022021 | 1 | 0.50397 | 40317.6 | 0.60822 | 21895.92 | 7e-05 | 0.84 | 1 | 5000 | 21895.92 | 0.84 | 0 | 0 | 0 | 0 | 13420.84 | 0 | 0 | 0 | 0 | 0 | 13420.84
2022022022 | 1 | 0.49203 | 39362.4 | 0.61137 | 22009.32 | 7e-05 | 0.84 | 1 | 5000 | 22009.32 | 0.84 | 0 | 0 | 0 | 0 | 12352.24 | 0 | 0 | 0 | 0 | 0 | 12352.24
2022022023 | 1 | 0.47242 | 37793.6 | 0.63105 | 22717.8 | 7e-05 | 0.84 | 1 | 5000 | 22717.8 | 0.84 | 0 | 0 | 0 | 0 | 10074.96 | 0 | 0 | 0 | 0 | 0 | 10074.96
2022022024 | 1 | 0.44996 | 35996.8 | 0.62772 | 22597.92 | 7e-05 | 0.84 | 1 | 5000 | 22597.92 | 0.84 | 0 | 0 | 0 | 0 | 8398.04 | 0 | 0 | 0 | 0 | 0 | 8398.04
2022022101 | 2 | 0.43223 | 34578.4 | 0.60889 | 21920.04 | 7e-05 | 0.84 | 1 | 5000 | 21920.04 | 0.84 | 0 | 0 | 0 | 0 | 7657.52 | 0 | 0 | 0 | 0 | 0 | 7657.52
2022022102 | 2 | 0.42209 | 33767.2 | 0.59881 | 21557.16 | 7e-05 | 0.84 | 1 | 5000 | 21557.16 | 0.84 | 0 | 0 | 0 | 0 | 7209.2 | 0 | 0 | 0 | 0 | 0 | 7209.2
2022022103 | 2 | 0.41686 | 33348.8 | 0.59012 | 21244.32 | 7e-05 | 0.84 | 1 | 5000 | 21244.32 | 0.84 | 0 | 0 | 0 | 0 | 7103.64 | 0 | 0 | 0 | 0 | 0 | 7103.64
2022022104 | 2 | 0.4162 | 33296 | 0.58739 | 21146.04 | 7e-05 | 0.84 | 1 | 5000 | 21146.04 | 0.84 | 0 | 0 | 0 | 0 | 7149.12 | 0 | 0 | 0 | 0 | 0 | 7149.12
2022022105 | 2 | 0.42448 | 33958.4 | 0.59463 | 21406.68 | 7e-05 | 0.84 | 1 | 5000 | 21406.68 | 0.84 | 0 | 0 | 0 | 0 | 7550.88 | 0 | 0 | 0 | 0 | 0 | 7550.88
2022022106 | 2 | 0.4442 | 35536 | 0.62615 | 22541.4 | 7e-05 | 0.84 | 1 | 5000 | 22541.4 | 0.84 | 0 | 0 | 0 | 0 | 7993.76 | 0 | 0 | 0 | 0 | 0 | 7993.76
2022022107 | 2 | 0.47576 | 38060.8 | 0.65867 | 23712.12 | 7e-05 | 0.84 | 1 | 5000 | 23712.12 | 0.84 | 0 | 0 | 0 | 0 | 9347.84 | 0 | 0 | 0 | 0 | 0 | 9347.84
2022022108 | 2 | 0.49362 | 39489.6 | 0.67018 | 24126.48 | 0.0183 | 219.6 | 1 | 5000 | 24126.48 | 219.6 | 0 | 0 | 0 | 0 | 10143.52 | 0 | 0 | 0 | 0 | 0 | 10143.52
2022022109 | 2 | 0.50386 | 40308.8 | 0.61559 | 22161.24 | 0.20708 | 2484.96 | 1 | 5000 | 22161.24 | 2484.96 | 0 | 0 | 0 | 0 | 10662.6 | 0 | 0 | 0 | 0 | 0 | 10662.6
2022022110 | 2 | 0.51275 | 41020 | 0.55856 | 20108.16 | 0.38689 | 4642.68 | 1 | 5000 | 20108.16 | 4642.68 | 0 | 0 | 0 | 0 | 11269.16 | 0 | 0 | 0 | 0 | 0 | 11269.16
2022022111 | 2 | 0.51941 | 41552.8 | 0.56131 | 20207.16 | 0.37449 | 4493.88 | 1 | 5000 | 20207.16 | 4493.88 | 0 | 0 | 0 | 0 | 11851.76 | 0 | 0 | 0 | 0 | 0 | 11851.76
2022022112 | 2 | 0.52473 | 41978.4 | 0.5531 | 19911.6 | 0.40328 | 4839.36 | 1 | 5000 | 19911.6 | 4839.36 | 0 | 0 | 0 | 0 | 12227.44 | 0 | 0 | 0 | 0 | 0 | 12227.44
2022022113 | 2 | 0.52993 | 42394.4 | 0.57599 | 20735.64 | 0.35247 | 4229.64 | 1 | 5000 | 20735.64 | 4229.64 | 0 | 0 | 0 | 0 | 12429.12 | 0 | 0 | 0 | 0 | 0 | 12429.12
2022022114 | 2 | 0.53982 | 43185.6 | 0.59842 | 21543.12 | 0.34399 | 4127.88 | 1 | 5000 | 21543.12 | 4127.88 | 0 | 0 | 0 | 0 | 12514.6 | 0 | 0 | 0 | 0 | 0 | 12514.6
2022022115 | 2 | 0.54787 | 43829.6 | 0.59248 | 21329.28 | 0.30245 | 3629.4 | 1 | 5000 | 21329.28 | 3629.4 | 0 | 0 | 0 | 0 | 13870.92 | 0 | 0 | 0 | 0 | 0 | 13870.92
2022022116 | 2 | 0.55541 | 44432.8 | 0.56792 | 20445.12 | 0.27548 | 3305.76 | 1 | 5000 | 20445.12 | 3305.76 | 0 | 0 | 0 | 0 | 15681.92 | 0 | 0 | 0 | 0 | 0 | 15681.92
2022022117 | 2 | 0.56129 | 44903.2 | 0.5602 | 20167.2 | 0.21774 | 2612.88 | 1 | 5000 | 20167.2 | 2612.88 | 0 | 0 | 0 | 0 | 17123.12 | 0 | 0 | 0 | 0 | 0 | 17123.12
2022022118 | 2 | 0.56378 | 45102.4 | 0.59419 | 21390.84 | 0.11972 | 1436.64 | 1 | 5000 | 21390.84 | 1436.64 | 0 | 0 | 0 | 0 | 17274.92 | 0 | 0 | 0 | 0 | 0 | 17274.92
2022022119 | 2 | 0.5719 | 45752 | 0.59942 | 21579.12 | 0.00862 | 103.44 | 1 | 5000 | 21579.12 | 103.44 | 0 | 0 | 0 | 0 | 19069.44 | 0 | 0 | 0 | 0 | 0 | 19069.44
2022022120 | 2 | 0.57299 | 45839.2 | 0.61213 | 22036.68 | 0 | 0 | 1 | 5000 | 22036.68 | 0 | 0 | 0 | 0 | 0 | 18802.52 | 0 | 0 | 0 | 0 | 0 | 18802.52
2022022121 | 2 | 0.56141 | 44912.8 | 0.64595 | 23254.2 | 0 | 0 | 1 | 5000 | 23254.2 | 0 | 0 | 0 | 0 | 0 | 16658.6 | 0 | 0 | 0 | 0 | 0 | 16658.6
2022022122 | 2 | 0.54172 | 43337.6 | 0.64859 | 23349.24 | 5e-05 | 0.6 | 1 | 5000 | 23349.24 | 0.6 | 0 | 0 | 0 | 0 | 14987.76 | 0 | 0 | 0 | 0 | 0 | 14987.76
2022022123 | 2 | 0.51293 | 41034.4 | 0.6563 | 23626.8 | 5e-05 | 0.6 | 1 | 5000 | 23626.8 | 0.6 | 0 | 0 | 0 | 0 | 12407 | 0 | 0 | 0 | 0 | 0 | 12407
2022022124 | 2 | 0.4812 | 38496 | 0.63911 | 23007.96 | 5e-05 | 0.6 | 1 | 5000 | 23007.96 | 0.6 | 0 | 0 | 0 | 0 | 10487.44 | 0 | 0 | 0 | 0 | 0 | 10487.44
2022022201 | 3 | 0.45323 | 36258.4 | 0.6029 | 21704.4 | 0 | 0 | 1 | 5000 | 21704.4 | 0 | 0 | 0 | 0 | 0 | 9554 | 0 | 0 | 0 | 0 | 0 | 9554
2022022202 | 3 | 0.43523 | 34818.4 | 0.57692 | 20769.12 | 0 | 0 | 1 | 5000 | 20769.12 | 0 | 0 | 0 | 0 | 0 | 9049.28 | 0 | 0 | 0 | 0 | 0 | 9049.28
2022022203 | 3 | 0.42417 | 33933.6 | 0.55714 | 20057.04 | 5e-05 | 0.6 | 1 | 5000 | 20057.04 | 0.6 | 0 | 0 | 0 | 0 | 8875.96 | 0 | 0 | 0 | 0 | 0 | 8875.96
2022022204 | 3 | 0.41893 | 33514.4 | 0.55034 | 19812.24 | 0 | 0 | 1 | 5000 | 19812.24 | 0 | 0 | 0 | 0 | 0 | 8702.16 | 0 | 0 | 0 | 0 | 0 | 8702.16
2022022205 | 3 | 0.42363 | 33890.4 | 0.54879 | 19756.44 | 0 | 0 | 1 | 5000 | 19756.44 | 0 | 0 | 0 | 0 | 0 | 9133.96 | 0 | 0 | 0 | 0 | 0 | 9133.96
2022022206 | 3 | 0.44323 | 35458.4 | 0.5619 | 20228.4 | 0 | 0 | 1 | 5000 | 20228.4 | 0 | 0 | 0 | 0 | 0 | 10230 | 0 | 0 | 0 | 0 | 0 | 10230
2022022207 | 3 | 0.48065 | 38452 | 0.54981 | 19793.16 | 6e-05 | 0.72 | 1 | 5000 | 19793.16 | 0.72 | 0 | 0 | 0 | 0 | 13658.12 | 0 | 0 | 0 | 0 | 0 | 13658.12
2022022208 | 3 | 0.49699 | 39759.2 | 0.53353 | 19207.08 | 0.01924 | 230.88 | 1 | 5000 | 19207.08 | 230.88 | 0 | 0 | 0 | 0 | 15321.24 | 0 | 0 | 0 | 0 | 0 | 15321.24
2022022209 | 3 | 0.505 | 40400 | 0.49525 | 17829 | 0.26046 | 3125.52 | 1 | 5000 | 17829 | 3125.52 | 0 | 0 | 0 | 0 | 14445.48 | 0 | 0 | 0 | 0 | 0 | 14445.48
2022022210 | 3 | 0.5158 | 41264 | 0.43963 | 15826.68 | 0.51843 | 6221.16 | 1 | 5000 | 15826.68 | 6221.16 | 0 | 0 | 0 | 0 | 14216.16 | 0 | 0 | 0 | 0 | 0 | 14216.16
2022022211 | 3 | 0.53022 | 42417.6 | 0.38761 | 13953.96 | 0.63012 | 7561.44 | 1 | 5000 | 13953.96 | 7561.44 | 0 | 0 | 0 | 0 | 15902.2 | 0 | 0 | 0 | 0 | 0 | 15902.2
2022022212 | 3 | 0.54291 | 43432.8 | 0.34016 | 12245.76 | 0.68808 | 8256.96 | 1 | 5000 | 12245.76 | 8256.96 | 0 | 0 | 0 | 0 | 17930.08 | 0 | 0 | 0 | 0 | 0 | 17930.08
2022022213 | 3 | 0.55095 | 44076 | 0.32241 | 11606.76 | 0.72613 | 8713.56 | 1 | 5000 | 11606.76 | 8713.56 | 0 | 0 | 0 | 0 | 18755.68 | 0 | 0 | 0 | 0 | 0 | 18755.68
2022022214 | 3 | 0.55729 | 44583.2 | 0.31636 | 11388.96 | 0.75262 | 9031.44 | 1 | 5000 | 11388.96 | 9031.44 | 0 | 0 | 0 | 0 | 19162.8 | 0 | 0 | 0 | 0 | 0 | 19162.8
2022022215 | 3 | 0.56269 | 45015.2 | 0.32426 | 11673.36 | 0.75589 | 9070.68 | 1 | 5000 | 11673.36 | 9070.68 | 0 | 0 | 0 | 0 | 19271.16 | 0 | 0 | 0 | 0 | 0 | 19271.16
2022022216 | 3 | 0.569 | 45520 | 0.36419 | 13110.84 | 0.72677 | 8721.24 | 1 | 5000 | 13110.84 | 8721.24 | 0 | 0 | 0 | 0 | 18687.92 | 0 | 0 | 0 | 0 | 0 | 18687.92
2022022217 | 3 | 0.57509 | 46007.2 | 0.42777 | 15399.72 | 0.62637 | 7516.44 | 1 | 5000 | 15399.72 | 7516.44 | 0 | 0 | 0 | 0 | 18091.04 | 0 | 0 | 0 | 0 | 0 | 18091.04
2022022218 | 3 | 0.58106 | 46484.8 | 0.52825 | 19017 | 0.33409 | 4009.08 | 1 | 5000 | 19017 | 4009.08 | 0 | 0 | 0 | 0 | 18458.72 | 0 | 0 | 0 | 0 | 0 | 18458.72
2022022219 | 3 | 0.59778 | 47822.4 | 0.63766 | 22955.76 | 0.02736 | 328.32 | 1 | 5000 | 22955.76 | 328.32 | 0 | 0 | 0 | 0 | 19538.32 | 0 | 0 | 0 | 0 | 0 | 19538.32
2022022220 | 3 | 0.60799 | 48639.2 | 0.69824 | 25136.64 | 6e-05 | 0.72 | 1 | 5000 | 25136.64 | 0.72 | 0 | 0 | 0 | 0 | 18501.84 | 0 | 0 | 0 | 0 | 0 | 18501.84
2022022221 | 3 | 0.60447 | 48357.6 | 0.71898 | 25883.28 | 6e-05 | 0.72 | 1 | 5000 | 25883.28 | 0.72 | 0 | 0 | 0 | 0 | 17473.6 | 0 | 0 | 0 | 0 | 0 | 17473.6
2022022222 | 3 | 0.59117 | 47293.6 | 0.72192 | 25989.12 | 6e-05 | 0.72 | 1 | 5000 | 25989.12 | 0.72 | 0 | 0 | 0 | 0 | 16303.76 | 0 | 0 | 0 | 0 | 0 | 16303.76
2022022223 | 3 | 0.56839 | 45471.2 | 0.72309 | 26031.24 | 6e-05 | 0.72 | 1 | 5000 | 26031.24 | 0.72 | 0 | 0 | 0 | 0 | 14439.24 | 0 | 0 | 0 | 0 | 0 | 14439.24
2022022224 | 3 | 0.54558 | 43646.4 | 0.71883 | 25877.88 | 6e-05 | 0.72 | 1 | 5000 | 25877.88 | 0.72 | 0 | 0 | 0 | 0 | 12767.8 | 0 | 0 | 0 | 0 | 0 | 12767.8
2022022301 | 4 | 0.52973 | 42378.4 | 0.71186 | 25626.96 | 6e-05 | 0.72 | 1 | 5000 | 25626.96 | 0.72 | 0 | 0 | 0 | 0 | 11750.72 | 0 | 0 | 0 | 0 | 0 | 11750.72
2022022302 | 4 | 0.52103 | 41682.4 | 0.70402 | 25344.72 | 6e-05 | 0.72 | 1 | 5000 | 25344.72 | 0.72 | 0 | 0 | 0 | 0 | 11336.96 | 0 | 0 | 0 | 0 | 0 | 11336.96
2022022303 | 4 | 0.51765 | 41412 | 0.69771 | 25117.56 | 6e-05 | 0.72 | 1 | 5000 | 25117.56 | 0.72 | 0 | 0 | 0 | 0 | 11293.72 | 0 | 0 | 0 | 0 | 0 | 11293.72
2022022304 | 4 | 0.5211 | 41688 | 0.68565 | 24683.4 | 6e-05 | 0.72 | 1 | 5000 | 24683.4 | 0.72 | 0 | 0 | 0 | 0 | 12003.88 | 0 | 0 | 0 | 0 | 0 | 12003.88
2022022305 | 4 | 0.53634 | 42907.2 | 0.66007 | 23762.52 | 6e-05 | 0.72 | 1 | 5000 | 23762.52 | 0.72 | 0 | 0 | 0 | 0 | 14143.96 | 0 | 0 | 0 | 0 | 0 | 14143.96
2022022306 | 4 | 0.5689 | 45512 | 0.6349 | 22856.4 | 6e-05 | 0.72 | 1 | 5000 | 22856.4 | 0.72 | 0 | 0 | 0 | 0 | 17654.88 | 0 | 0 | 0 | 0 | 0 | 17654.88
2022022307 | 4 | 0.61983 | 49586.4 | 0.59983 | 21593.88 | 6e-05 | 0.72 | 1 | 5000 | 21593.88 | 0.72 | 0 | 0 | 0 | 0 | 22991.8 | 0 | 0 | 0 | 0 | 0 | 22991.8
2022022308 | 4 | 0.65151 | 52120.8 | 0.53879 | 19396.44 | 0.00522 | 62.64 | 1 | 5000 | 19396.44 | 62.64 | 0 | 0 | 0 | 0 | 27661.72 | 0 | 0 | 0 | 0 | 0 | 27661.72
2022022309 | 4 | 0.66755 | 53404 | 0.48105 | 17317.8 | 0.05613 | 673.56 | 1 | 5000 | 17317.8 | 673.56 | 0 | 0 | 0 | 0 | 30412.64 | 0 | 0 | 0 | 0 | 0 | 30412.64
2022022310 | 4 | 0.68374 | 54699.2 | 0.43199 | 15551.64 | 0.13965 | 1675.8 | 1 | 5000 | 15551.64 | 1675.8 | 0 | 0 | 0 | 0 | 32471.76 | 0 | 0 | 0 | 0 | 0 | 32471.76
2022022311 | 4 | 0.69774 | 55819.2 | 0.36339 | 13082.04 | 0.26069 | 3128.28 | 1 | 5000 | 13082.04 | 3128.28 | 0 | 0 | 0 | 0 | 34608.88 | 0 | 0 | 0 | 0 | 0 | 34608.88
2022022312 | 4 | 0.70789 | 56631.2 | 0.31009 | 11163.24 | 0.3617 | 4340.4 | 1 | 5000 | 11163.24 | 4340.4 | 0 | 0 | 0 | 0 | 36127.56 | 0 | 0 | 0 | 0 | 0 | 36127.56
2022022313 | 4 | 0.71483 | 57186.4 | 0.28292 | 10185.12 | 0.40988 | 4918.56 | 1 | 5000 | 10185.12 | 4918.56 | 0 | 0 | 0 | 0 | 37082.72 | 0 | 0 | 0 | 0 | 0 | 37082.72
2022022314 | 4 | 0.71934 | 57547.2 | 0.26753 | 9631.08 | 0.44071 | 5288.52 | 1 | 5000 | 9631.08 | 5288.52 | 0 | 0 | 0 | 0 | 37627.6 | 0 | 0 | 0 | 0 | 0 | 37627.6
2022022315 | 4 | 0.7181 | 57448 | 0.26417 | 9510.12 | 0.44219 | 5306.28 | 1 | 5000 | 9510.12 | 5306.28 | 0 | 0 | 0 | 0 | 37631.6 | 0 | 0 | 0 | 0 | 0 | 37631.6
2022022316 | 4 | 0.71999 | 57599.2 | 0.24302 | 8748.72 | 0.42562 | 5107.44 | 1 | 5000 | 8748.72 | 5107.44 | 0 | 0 | 0 | 0 | 38743.04 | 0 | 0 | 0 | 0 | 0 | 38743.04
2022022317 | 4 | 0.7327 | 58616 | 0.22848 | 8225.28 | 0.34587 | 4150.44 | 1 | 5000 | 8225.28 | 4150.44 | 0 | 0 | 0 | 0 | 41240.28 | 0 | 0 | 0 | 0 | 0 | 41240.28
2022022318 | 4 | 0.75193 | 60154.4 | 0.21018 | 7566.48 | 0.19899 | 2387.88 | 1 | 5000 | 7566.48 | 2387.88 | 0 | 0 | 0 | 0 | 45200.04 | 0 | 0 | 0 | 0 | 0 | 45200.04
2022022319 | 4 | 0.77077 | 61661.6 | 0.20448 | 7361.28 | 0.02288 | 274.56 | 1 | 5000 | 7361.28 | 274.56 | 0 | 0 | 0 | 0 | 49025.76 | 0 | 0 | 0 | 0 | 0 | 49025.76
2022022320 | 4 | 0.77219 | 61775.2 | 0.22117 | 7962.12 | 0 | 0 | 1 | 5000 | 7962.12 | 0 | 0 | 0 | 0 | 0 | 48813.08 | 0 | 0 | 0 | 0 | 0 | 48813.08
2022022321 | 4 | 0.76359 | 61087.2 | 0.20905 | 7525.8 | 0 | 0 | 1 | 5000 | 7525.8 | 0 | 0 | 0 | 0 | 0 | 48561.4 | 0 | 0 | 0 | 0 | 0 | 48561.4
2022022322 | 4 | 0.74111 | 59288.8 | 0.15892 | 5721.12 | 0 | 0 | 1 | 5000 | 5721.12 | 0 | 0 | 0 | 0 | 0 | 48567.68 | 0 | 0 | 0 | 0 | 0 | 48567.68
2022022323 | 4 | 0.71625 | 57300 | 0.11214 | 4037.04 | 0 | 0 | 1 | 5000 | 4037.04 | 0 | 0 | 0 | 0 | 0 | 48262.96 | 0 | 0 | 0 | 0 | 0 | 48262.96
2022022324 | 4 | 0.69029 | 55223.2 | 0.08283 | 2981.88 | 0 | 0 | 1 | 5000 | 2981.88 | 0 | 0 | 0 | 0 | 0 | 47241.32 | 0 | 0 | 0 | 0 | 0 | 47241.32
2022022401 | 5 | 0.67659 | 54127.2 | 0.06403 | 2305.08 | 0 | 0 | 1 | 5000 | 2305.08 | 0 | 0 | 0 | 0 | 0 | 46822.12 | 0 | 0 | 0 | 0 | 0 | 46822.12
2022022402 | 5 | 0.67088 | 53670.4 | 0.04958 | 1784.88 | 0 | 0 | 1 | 5000 | 1784.88 | 0 | 0 | 0 | 0 | 0 | 46885.52 | 0 | 0 | 0 | 0 | 0 | 46885.52
2022022403 | 5 | 0.67161 | 53728.8 | 0.04267 | 1536.12 | 0 | 0 | 1 | 5000 | 1536.12 | 0 | 0 | 0 | 0 | 0 | 47192.68 | 0 | 0 | 0 | 0 | 0 | 47192.68
2022022404 | 5 | 0.67588 | 54070.4 | 0.04525 | 1629 | 0 | 0 | 1 | 5000 | 1629 | 0 | 0 | 0 | 0 | 0 | 47441.4 | 0 | 0 | 0 | 0 | 0 | 47441.4
2022022405 | 5 | 0.68761 | 55008.8 | 0.03603 | 1297.08 | 0 | 0 | 1 | 5000 | 1297.08 | 0 | 0 | 0 | 0 | 0 | 48711.72 | 0 | 0 | 0 | 0 | 0 | 48711.72
2022022406 | 5 | 0.71207 | 56965.6 | 0.03433 | 1235.88 | 0 | 0 | 1 | 5000 | 1235.88 | 0 | 0 | 0 | 0 | 0 | 50729.72 | 0 | 0 | 0 | 0 | 0 | 50729.72
2022022407 | 5 | 0.74462 | 59569.6 | 0.0363 | 1306.8 | 0 | 0 | 1 | 5000 | 1306.8 | 0 | 0 | 0 | 0 | 0 | 53262.8 | 0 | 0 | 0 | 0 | 0 | 53262.8
2022022408 | 5 | 0.759 | 60720 | 0.03315 | 1193.4 | 0.00339 | 40.68 | 1 | 5000 | 1193.4 | 40.68 | 0 | 0 | 0 | 0 | 54485.92 | 0 | 0 | 0 | 0 | 0 | 54485.92
2022022409 | 5 | 0.76357 | 61085.6 | 0.02418 | 870.48 | 0.04028 | 483.36 | 1 | 5000 | 870.48 | 483.36 | 0 | 0 | 0 | 0 | 54731.76 | 0 | 0 | 0 | 0 | 0 | 54731.76
2022022410 | 5 | 0.76479 | 61183.2 | 0.01964 | 707.04 | 0.12159 | 1459.08 | 1 | 5000 | 707.04 | 1459.08 | 0 | 0 | 0 | 0 | 54017.08 | 0 | 0 | 0 | 0 | 0 | 54017.08
2022022411 | 5 | 0.76111 | 60888.8 | 0.01647 | 592.92 | 0.21834 | 2620.08 | 1 | 5000 | 592.92 | 2620.08 | 0 | 0 | 0 | 0 | 52675.8 | 0 | 0 | 0 | 0 | 0 | 52675.8
2022022412 | 5 | 0.75776 | 60620.8 | 0.0216 | 777.6 | 0.37837 | 4540.44 | 1 | 5000 | 777.6 | 4540.44 | 0 | 0 | 0 | 0 | 50302.76 | 0 | 0 | 0 | 0 | 0 | 50302.76
2022022413 | 5 | 0.74795 | 59836 | 0.03577 | 1287.72 | 0.5324 | 6388.8 | 1 | 5000 | 1287.72 | 6388.8 | 0 | 0 | 0 | 0 | 47159.48 | 0 | 0 | 0 | 0 | 0 | 47159.48
2022022414 | 5 | 0.73471 | 58776.8 | 0.05821 | 2095.56 | 0.5737 | 6884.4 | 1 | 5000 | 2095.56 | 6884.4 | 0 | 0 | 0 | 0 | 44796.84 | 0 | 0 | 0 | 0 | 0 | 44796.84
2022022415 | 5 | 0.72263 | 57810.4 | 0.07784 | 2802.24 | 0.5781 | 6937.2 | 1 | 5000 | 2802.24 | 6937.2 | 0 | 0 | 0 | 0 | 43070.96 | 0 | 0 | 0 | 0 | 0 | 43070.96
2022022416 | 5 | 0.7181 | 57448 | 0.11666 | 4199.76 | 0.57332 | 6879.84 | 1 | 5000 | 4199.76 | 6879.84 | 0 | 0 | 0 | 0 | 41368.4 | 0 | 0 | 0 | 0 | 0 | 41368.4
2022022417 | 5 | 0.72214 | 57771.2 | 0.13536 | 4872.96 | 0.56641 | 6796.92 | 1 | 5000 | 4872.96 | 6796.92 | 0 | 0 | 0 | 0 | 41101.32 | 0 | 0 | 0 | 0 | 0 | 41101.32
2022022418 | 5 | 0.73432 | 58745.6 | 0.14114 | 5081.04 | 0.3294 | 3952.8 | 1 | 5000 | 5081.04 | 3952.8 | 0 | 0 | 0 | 0 | 44711.76 | 0 | 0 | 0 | 0 | 0 | 44711.76
2022022419 | 5 | 0.75484 | 60387.2 | 0.14054 | 5059.44 | 0.02977 | 357.24 | 1 | 5000 | 5059.44 | 357.24 | 0 | 0 | 0 | 0 | 49970.52 | 0 | 0 | 0 | 0 | 0 | 49970.52
2022022420 | 5 | 0.75948 | 60758.4 | 0.15051 | 5418.36 | 0 | 0 | 1 | 5000 | 5418.36 | 0 | 0 | 0 | 0 | 0 | 50340.04 | 0 | 0 | 0 | 0 | 0 | 50340.04
2022022421 | 5 | 0.75503 | 60402.4 | 0.16269 | 5856.84 | 0 | 0 | 1 | 5000 | 5856.84 | 0 | 0 | 0 | 0 | 0 | 49545.56 | 0 | 0 | 0 | 0 | 0 | 49545.56
2022022422 | 5 | 0.7398 | 59184 | 0.18314 | 6593.04 | 0 | 0 | 1 | 5000 | 6593.04 | 0 | 0 | 0 | 0 | 0 | 47590.96 | 0 | 0 | 0 | 0 | 0 | 47590.96
2022022423 | 5 | 0.71252 | 57001.6 | 0.19654 | 7075.44 | 0 | 0 | 1 | 5000 | 7075.44 | 0 | 0 | 0 | 0 | 0 | 44926.16 | 0 | 0 | 0 | 0 | 0 | 44926.16
2022022424 | 5 | 0.68986 | 55188.8 | 0.18716 | 6737.76 | 0 | 0 | 1 | 5000 | 6737.76 | 0 | 0 | 0 | 0 | 0 | 43451.04 | 0 | 0 | 0 | 0 | 0 | 43451.04
2022022501 | 6 | 0.67695 | 54156 | 0.15685 | 5646.6 | 0 | 0 | 1 | 5000 | 5646.6 | 0 | 0 | 0 | 0 | 0 | 43509.4 | 0 | 0 | 0 | 0 | 0 | 43509.4
2022022502 | 6 | 0.67093 | 53674.4 | 0.14157 | 5096.52 | 0 | 0 | 1 | 5000 | 5096.52 | 0 | 0 | 0 | 0 | 0 | 43577.88 | 0 | 0 | 0 | 0 | 0 | 43577.88
2022022503 | 6 | 0.67444 | 53955.2 | 0.12534 | 4512.24 | 0 | 0 | 1 | 5000 | 4512.24 | 0 | 0 | 0 | 0 | 0 | 44442.96 | 0 | 0 | 0 | 0 | 0 | 44442.96
2022022504 | 6 | 0.68302 | 54641.6 | 0.12792 | 4605.12 | 0 | 0 | 1 | 5000 | 4605.12 | 0 | 0 | 0 | 0 | 0 | 45036.48 | 0 | 0 | 0 | 0 | 0 | 45036.48
2022022505 | 6 | 0.70084 | 56067.2 | 0.15066 | 5423.76 | 0 | 0 | 1 | 5000 | 5423.76 | 0 | 0 | 0 | 0 | 0 | 45643.44 | 0 | 0 | 0 | 0 | 0 | 45643.44
2022022506 | 6 | 0.73298 | 58638.4 | 0.19383 | 6977.88 | 0 | 0 | 1 | 5000 | 6977.88 | 0 | 0 | 0 | 0 | 0 | 46660.52 | 0 | 0 | 0 | 0 | 0 | 46660.52
2022022507 | 6 | 0.77966 | 62372.8 | 0.2082 | 7495.2 | 0 | 0 | 1 | 5000 | 7495.2 | 0 | 0 | 0 | 0 | 0 | 49877.6 | 0 | 0 | 0 | 0 | 0 | 49877.6
2022022508 | 6 | 0.79981 | 63984.8 | 0.20634 | 7428.24 | 0.03479 | 417.48 | 1 | 5000 | 7428.24 | 417.48 | 0 | 0 | 0 | 0 | 51139.08 | 0 | 0 | 0 | 0 | 0 | 51139.08
2022022509 | 6 | 0.7959 | 63672 | 0.19377 | 6975.72 | 0.24372 | 2924.64 | 1 | 5000 | 6975.72 | 2924.64 | 0 | 0 | 0 | 0 | 48771.64 | 0 | 0 | 0 | 0 | 0 | 48771.64
2022022510 | 6 | 0.78601 | 62880.8 | 0.21784 | 7842.24 | 0.47718 | 5726.16 | 1 | 5000 | 7842.24 | 5726.16 | 0 | 0 | 0 | 0 | 44312.4 | 0 | 0 | 0 | 0 | 0 | 44312.4
2022022511 | 6 | 0.76809 | 61447.2 | 0.2189 | 7880.4 | 0.56196 | 6743.52 | 1 | 5000 | 7880.4 | 6743.52 | 0 | 0 | 0 | 0 | 41823.28 | 0 | 0 | 0 | 0 | 0 | 41823.28
2022022512 | 6 | 0.74774 | 59819.2 | 0.211 | 7596 | 0.62419 | 7490.28 | 1 | 5000 | 7596 | 7490.28 | 0 | 0 | 0 | 0 | 39732.92 | 0 | 0 | 0 | 0 | 0 | 39732.92
2022022513 | 6 | 0.7257 | 58056 | 0.20388 | 7339.68 | 0.61133 | 7335.96 | 1 | 5000 | 7339.68 | 7335.96 | 0 | 0 | 0 | 0 | 38380.36 | 0 | 0 | 0 | 0 | 0 | 38380.36
2022022514 | 6 | 0.70917 | 56733.6 | 0.21385 | 7698.6 | 0.61782 | 7413.84 | 1 | 5000 | 7698.6 | 7413.84 | 0 | 0 | 0 | 0 | 36621.16 | 0 | 0 | 0 | 0 | 0 | 36621.16
2022022515 | 6 | 0.69797 | 55837.6 | 0.20787 | 7483.32 | 0.52075 | 6249 | 1 | 5000 | 7483.32 | 6249 | 0 | 0 | 0 | 0 | 37105.28 | 0 | 0 | 0 | 0 | 0 | 37105.28
2022022516 | 6 | 0.69788 | 55830.4 | 0.22071 | 7945.56 | 0.49313 | 5917.56 | 1 | 5000 | 7945.56 | 5917.56 | 0 | 0 | 0 | 0 | 36967.28 | 0 | 0 | 0 | 0 | 0 | 36967.28
2022022517 | 6 | 0.70622 | 56497.6 | 0.22758 | 8192.88 | 0.41043 | 4925.16 | 1 | 5000 | 8192.88 | 4925.16 | 0 | 0 | 0 | 0 | 38379.56 | 0 | 0 | 0 | 0 | 0 | 38379.56
2022022518 | 6 | 0.71576 | 57260.8 | 0.26185 | 9426.6 | 0.21194 | 2543.28 | 1 | 5000 | 9426.6 | 2543.28 | 0 | 0 | 0 | 0 | 40290.92 | 0 | 0 | 0 | 0 | 0 | 40290.92
2022022519 | 6 | 0.72768 | 58214.4 | 0.27727 | 9981.72 | 0.01262 | 151.44 | 1 | 5000 | 9981.72 | 151.44 | 0 | 0 | 0 | 0 | 43081.24 | 0 | 0 | 0 | 0 | 0 | 43081.24
2022022520 | 6 | 0.72602 | 58081.6 | 0.26191 | 9428.76 | 0 | 0 | 1 | 5000 | 9428.76 | 0 | 0 | 0 | 0 | 0 | 43652.84 | 0 | 0 | 0 | 0 | 0 | 43652.84
2022022521 | 6 | 0.71567 | 57253.6 | 0.25848 | 9305.28 | 0 | 0 | 1 | 5000 | 9305.28 | 0 | 0 | 0 | 0 | 0 | 42948.32 | 0 | 0 | 0 | 0 | 0 | 42948.32
2022022522 | 6 | 0.69941 | 55952.8 | 0.24897 | 8962.92 | 0 | 0 | 1 | 5000 | 8962.92 | 0 | 0 | 0 | 0 | 0 | 41989.88 | 0 | 0 | 0 | 0 | 0 | 41989.88
2022022523 | 6 | 0.67401 | 53920.8 | 0.21913 | 7888.68 | 0 | 0 | 1 | 5000 | 7888.68 | 0 | 0 | 0 | 0 | 0 | 41032.12 | 0 | 0 | 0 | 0 | 0 | 41032.12
2022022524 | 6 | 0.65094 | 52075.2 | 0.18096 | 6514.56 | 0 | 0 | 1 | 5000 | 6514.56 | 0 | 0 | 0 | 0 | 0 | 40560.64 | 0 | 0 | 0 | 0 | 0 | 40560.64
2022022601 | 7 | 0.63428 | 50742.4 | 0.14784 | 5322.24 | 0 | 0 | 1 | 5000 | 5322.24 | 0 | 0 | 0 | 0 | 0 | 40420.16 | 0 | 0 | 0 | 0 | 0 | 40420.16
2022022602 | 7 | 0.62475 | 49980 | 0.13387 | 4819.32 | 0 | 0 | 1 | 5000 | 4819.32 | 0 | 0 | 0 | 0 | 0 | 40160.68 | 0 | 0 | 0 | 0 | 0 | 40160.68
2022022603 | 7 | 0.61908 | 49526.4 | 0.13441 | 4838.76 | 0 | 0 | 1 | 5000 | 4838.76 | 0 | 0 | 0 | 0 | 0 | 39687.64 | 0 | 0 | 0 | 0 | 0 | 39687.64
2022022604 | 7 | 0.61877 | 49501.6 | 0.12784 | 4602.24 | 0 | 0 | 1 | 5000 | 4602.24 | 0 | 0 | 0 | 0 | 0 | 39899.36 | 0 | 0 | 0 | 0 | 0 | 39899.36
2022022605 | 7 | 0.62566 | 50052.8 | 0.12148 | 4373.28 | 0 | 0 | 1 | 5000 | 4373.28 | 0 | 0 | 0 | 0 | 0 | 40679.52 | 0 | 0 | 0 | 0 | 0 | 40679.52
2022022606 | 7 | 0.63911 | 51128.8 | 0.12173 | 4382.28 | 0 | 0 | 1 | 5000 | 4382.28 | 0 | 0 | 0 | 0 | 0 | 41746.52 | 0 | 0 | 0 | 0 | 0 | 41746.52
2022022607 | 7 | 0.66013 | 52810.4 | 0.12811 | 4611.96 | 0 | 0 | 1 | 5000 | 4611.96 | 0 | 0 | 0 | 0 | 0 | 43198.44 | 0 | 0 | 0 | 0 | 0 | 43198.44
2022022608 | 7 | 0.67803 | 54242.4 | 0.12241 | 4406.76 | 0.00619 | 74.28 | 1 | 5000 | 4406.76 | 74.28 | 0 | 0 | 0 | 0 | 44761.36 | 0 | 0 | 0 | 0 | 0 | 44761.36
2022022609 | 7 | 0.69688 | 55750.4 | 0.09989 | 3596.04 | 0.10493 | 1259.16 | 1 | 5000 | 3596.04 | 1259.16 | 0 | 0 | 0 | 0 | 45895.2 | 0 | 0 | 0 | 0 | 0 | 45895.2
2022022610 | 7 | 0.71126 | 56900.8 | 0.0739 | 2660.4 | 0.28118 | 3374.16 | 1 | 5000 | 2660.4 | 3374.16 | 0 | 0 | 0 | 0 | 45866.24 | 0 | 0 | 0 | 0 | 0 | 45866.24
2022022611 | 7 | 0.71541 | 57232.8 | 0.05453 | 1963.08 | 0.41299 | 4955.88 | 1 | 5000 | 1963.08 | 4955.88 | 0 | 0 | 0 | 0 | 45313.84 | 0 | 0 | 0 | 0 | 0 | 45313.84
2022022612 | 7 | 0.70707 | 56565.6 | 0.04285 | 1542.6 | 0.52628 | 6315.36 | 1 | 5000 | 1542.6 | 6315.36 | 0 | 0 | 0 | 0 | 43707.64 | 0 | 0 | 0 | 0 | 0 | 43707.64
2022022613 | 7 | 0.69262 | 55409.6 | 0.04132 | 1487.52 | 0.58671 | 7040.52 | 1 | 5000 | 1487.52 | 7040.52 | 0 | 0 | 0 | 0 | 41881.56 | 0 | 0 | 0 | 0 | 0 | 41881.56
2022022614 | 7 | 0.67927 | 54341.6 | 0.04301 | 1548.36 | 0.58534 | 7024.08 | 1 | 5000 | 1548.36 | 7024.08 | 0 | 0 | 0 | 0 | 40769.16 | 0 | 0 | 0 | 0 | 0 | 40769.16
2022022615 | 7 | 0.66788 | 53430.4 | 0.04917 | 1770.12 | 0.57733 | 6927.96 | 1 | 5000 | 1770.12 | 6927.96 | 0 | 0 | 0 | 0 | 39732.32 | 0 | 0 | 0 | 0 | 0 | 39732.32
2022022616 | 7 | 0.664 | 53120 | 0.06513 | 2344.68 | 0.55402 | 6648.24 | 1 | 5000 | 2344.68 | 6648.24 | 0 | 0 | 0 | 0 | 39127.08 | 0 | 0 | 0 | 0 | 0 | 39127.08
2022022617 | 7 | 0.66511 | 53208.8 | 0.07974 | 2870.64 | 0.52932 | 6351.84 | 1 | 5000 | 2870.64 | 6351.84 | 0 | 0 | 0 | 0 | 38986.32 | 0 | 0 | 0 | 0 | 0 | 38986.32
2022022618 | 7 | 0.6698 | 53584 | 0.08958 | 3224.88 | 0.35312 | 4237.44 | 1 | 5000 | 3224.88 | 4237.44 | 0 | 0 | 0 | 0 | 41121.68 | 0 | 0 | 0 | 0 | 0 | 41121.68
2022022619 | 7 | 0.68294 | 54635.2 | 0.09444 | 3399.84 | 0.04239 | 508.68 | 1 | 5000 | 3399.84 | 508.68 | 0 | 0 | 0 | 0 | 45726.68 | 0 | 0 | 0 | 0 | 0 | 45726.68
2022022620 | 7 | 0.685 | 54800 | 0.09936 | 3576.96 | 0.00012 | 1.44 | 1 | 5000 | 3576.96 | 1.44 | 0 | 0 | 0 | 0 | 46221.6 | 0 | 0 | 0 | 0 | 0 | 46221.6
2022022621 | 7 | 0.67773 | 54218.4 | 0.09106 | 3278.16 | 0.00012 | 1.44 | 1 | 5000 | 3278.16 | 1.44 | 0 | 0 | 0 | 0 | 45938.8 | 0 | 0 | 0 | 0 | 0 | 45938.8
2022022622 | 7 | 0.66472 | 53177.6 | 0.08867 | 3192.12 | 0.00012 | 1.44 | 1 | 5000 | 3192.12 | 1.44 | 0 | 0 | 0 | 0 | 44984.04 | 0 | 0 | 0 | 0 | 0 | 44984.04
2022022623 | 7 | 0.64518 | 51614.4 | 0.08964 | 3227.04 | 0.00012 | 1.44 | 1 | 5000 | 3227.04 | 1.44 | 0 | 0 | 0 | 0 | 43385.92 | 0 | 0 | 0 | 0 | 0 | 43385.92
2022022624 | 7 | 0.62485 | 49988 | 0.08722 | 3139.92 | 0.00012 | 1.44 | 1 | 5000 | 3139.92 | 1.44 | 0 | 0 | 0 | 0 | 41846.64 | 0 | 0 | 0 | 0 | 0 | 41846.64
2022022701 | 1 | 0.60976 | 48780.8 | 0.11167 | 4020.12 | 0.00012 | 1.44 | 1 | 5000 | 4020.12 | 1.44 | 0 | 0 | 0 | 0 | 39759.24 | 0 | 0 | 0 | 0 | 0 | 39759.24
2022022702 | 1 | 0.60043 | 48034.4 | 0.14401 | 5184.36 | 0.00012 | 1.44 | 1 | 5000 | 5184.36 | 1.44 | 0 | 0 | 0 | 0 | 37848.6 | 0 | 0 | 0 | 0 | 0 | 37848.6
2022022703 | 1 | 0.59887 | 47909.6 | 0.18345 | 6604.2 | 0.00012 | 1.44 | 1 | 5000 | 6604.2 | 1.44 | 0 | 0 | 0 | 0 | 36303.96 | 0 | 0 | 0 | 0 | 0 | 36303.96
2022022704 | 1 | 0.60246 | 48196.8 | 0.22871 | 8233.56 | 0.00011 | 1.32 | 1 | 5000 | 8233.56 | 1.32 | 0 | 0 | 0 | 0 | 34961.92 | 0 | 0 | 0 | 0 | 0 | 34961.92
2022022705 | 1 | 0.61088 | 48870.4 | 0.26594 | 9573.84 | 0.00011 | 1.32 | 1 | 5000 | 9573.84 | 1.32 | 0 | 0 | 0 | 0 | 34295.24 | 0 | 0 | 0 | 0 | 0 | 34295.24
2022022706 | 1 | 0.62611 | 50088.8 | 0.29816 | 10733.76 | 0.00011 | 1.32 | 1 | 5000 | 10733.76 | 1.32 | 0 | 0 | 0 | 0 | 34353.72 | 0 | 0 | 0 | 0 | 0 | 34353.72
2022022707 | 1 | 0.64762 | 51809.6 | 0.30479 | 10972.44 | 0.00013 | 1.56 | 1 | 5000 | 10972.44 | 1.56 | 0 | 0 | 0 | 0 | 35835.6 | 0 | 0 | 0 | 0 | 0 | 35835.6
2022022708 | 1 | 0.66211 | 52968.8 | 0.2958 | 10648.8 | 0.06704 | 804.48 | 1 | 5000 | 10648.8 | 804.48 | 0 | 0 | 0 | 0 | 36515.52 | 0 | 0 | 0 | 0 | 0 | 36515.52
2022022709 | 1 | 0.65733 | 52586.4 | 0.24316 | 8753.76 | 0.5372 | 6446.4 | 1 | 5000 | 8753.76 | 6446.4 | 0 | 0 | 0 | 0 | 32386.24 | 0 | 0 | 0 | 0 | 0 | 32386.24
2022022710 | 1 | 0.64147 | 51317.6 | 0.17644 | 6351.84 | 0.80043 | 9605.16 | 1 | 5000 | 6351.84 | 9605.16 | 0 | 0 | 0 | 0 | 30360.6 | 0 | 0 | 0 | 0 | 0 | 30360.6
2022022711 | 1 | 0.61858 | 49486.4 | 0.18707 | 6734.52 | 0.82955 | 9954.6 | 1 | 5000 | 6734.52 | 9954.6 | 0 | 0 | 0 | 0 | 27797.28 | 0 | 0 | 0 | 0 | 0 | 27797.28
2022022712 | 1 | 0.59181 | 47344.8 | 0.17734 | 6384.24 | 0.83698 | 10043.76 | 1 | 5000 | 6384.24 | 10043.76 | 0 | 0 | 0 | 0 | 25916.8 | 0 | 0 | 0 | 0 | 0 | 25916.8
2022022713 | 1 | 0.56634 | 45307.2 | 0.16132 | 5807.52 | 0.84488 | 10138.56 | 1 | 5000 | 5807.52 | 10138.56 | 0 | 0 | 0 | 0 | 24361.12 | 0 | 0 | 0 | 0 | 0 | 24361.12
2022022714 | 1 | 0.54065 | 43252 | 0.15337 | 5521.32 | 0.85268 | 10232.16 | 1 | 5000 | 5521.32 | 10232.16 | 0 | 0 | 0 | 0 | 22498.52 | 0 | 0 | 0 | 0 | 0 | 22498.52
2022022715 | 1 | 0.5183 | 41464 | 0.13341 | 4802.76 | 0.85989 | 10318.68 | 1 | 5000 | 4802.76 | 10318.68 | 0 | 0 | 0 | 0 | 21342.56 | 0 | 0 | 0 | 0 | 0 | 21342.56
2022022716 | 1 | 0.50636 | 40508.8 | 0.11422 | 4111.92 | 0.87263 | 10471.56 | 1 | 5000 | 4111.92 | 10471.56 | 0 | 0 | 0 | 0 | 20925.32 | 0 | 0 | 0 | 0 | 0 | 20925.32
2022022717 | 1 | 0.5041 | 40328 | 0.09629 | 3466.44 | 0.8363 | 10035.6 | 1 | 5000 | 3466.44 | 10035.6 | 0 | 0 | 0 | 0 | 21825.96 | 0 | 0 | 0 | 0 | 0 | 21825.96
2022022718 | 1 | 0.51529 | 41223.2 | 0.07792 | 2805.12 | 0.51496 | 6179.52 | 1 | 5000 | 2805.12 | 6179.52 | 0 | 0 | 0 | 0 | 27238.56 | 0 | 0 | 0 | 0 | 0 | 27238.56
2022022719 | 1 | 0.55097 | 44077.6 | 0.05911 | 2127.96 | 0.05469 | 656.28 | 1 | 5000 | 2127.96 | 656.28 | 0 | 0 | 0 | 0 | 36293.36 | 0 | 0 | 0 | 0 | 0 | 36293.36
2022022720 | 1 | 0.58071 | 46456.8 | 0.07073 | 2546.28 | 6e-05 | 0.72 | 1 | 5000 | 2546.28 | 0.72 | 0 | 0 | 0 | 0 | 38909.8 | 0 | 0 | 0 | 0 | 0 | 38909.8
2022022721 | 1 | 0.59054 | 47243.2 | 0.10148 | 3653.28 | 6e-05 | 0.72 | 1 | 5000 | 3653.28 | 0.72 | 0 | 0 | 0 | 0 | 38589.2 | 0 | 0 | 0 | 0 | 0 | 38589.2
2022022722 | 1 | 0.59135 | 47308 | 0.12789 | 4604.04 | 6e-05 | 0.72 | 1 | 5000 | 4604.04 | 0.72 | 0 | 0 | 0 | 0 | 37703.24 | 0 | 0 | 0 | 0 | 0 | 37703.24
2022022723 | 1 | 0.57944 | 46355.2 | 0.1628 | 5860.8 | 6e-05 | 0.72 | 1 | 5000 | 5860.8 | 0.72 | 0 | 0 | 0 | 0 | 35493.68 | 0 | 0 | 0 | 0 | 0 | 35493.68
2022022724 | 1 | 0.56677 | 45341.6 | 0.20181 | 7265.16 | 6e-05 | 0.72 | 1 | 5000 | 7265.16 | 0.72 | 0 | 0 | 0 | 0 | 33075.72 | 0 | 0 | 0 | 0 | 0 | 33075.72
2022022801 | 2 | 0.56108 | 44886.4 | 0.24305 | 8749.8 | 6e-05 | 0.72 | 1 | 5000 | 8749.8 | 0.72 | 0 | 0 | 0 | 0 | 31135.88 | 0 | 0 | 0 | 0 | 0 | 31135.88
2022022802 | 2 | 0.56499 | 45199.2 | 0.27897 | 10042.92 | 6e-05 | 0.72 | 1 | 5000 | 10042.92 | 0.72 | 0 | 0 | 0 | 0 | 30155.56 | 0 | 0 | 0 | 0 | 0 | 30155.56
2022022803 | 2 | 0.57431 | 45944.8 | 0.30888 | 11119.68 | 6e-05 | 0.72 | 1 | 5000 | 11119.68 | 0.72 | 0 | 0 | 0 | 0 | 29824.4 | 0 | 0 | 0 | 0 | 0 | 29824.4
2022022804 | 2 | 0.58903 | 47122.4 | 0.32821 | 11815.56 | 6e-05 | 0.72 | 1 | 5000 | 11815.56 | 0.72 | 0 | 0 | 0 | 0 | 30306.12 | 0 | 0 | 0 | 0 | 0 | 30306.12
2022022805 | 2 | 0.61574 | 49259.2 | 0.3307 | 11905.2 | 6e-05 | 0.72 | 1 | 5000 | 11905.2 | 0.72 | 0 | 0 | 0 | 0 | 32353.28 | 0 | 0 | 0 | 0 | 0 | 32353.28
2022022806 | 2 | 0.66045 | 52836 | 0.31472 | 11329.92 | 6e-05 | 0.72 | 1 | 5000 | 11329.92 | 0.72 | 0 | 0 | 0 | 0 | 36505.36 | 0 | 0 | 0 | 0 | 0 | 36505.36
2022022807 | 2 | 0.72104 | 57683.2 | 0.31206 | 11234.16 | 0.00015 | 1.8 | 1 | 5000 | 11234.16 | 1.8 | 0 | 0 | 0 | 0 | 41447.24 | 0 | 0 | 0 | 0 | 0 | 41447.24
2022022808 | 2 | 0.73408 | 58726.4 | 0.31155 | 11215.8 | 0.09233 | 1107.96 | 1 | 5000 | 11215.8 | 1107.96 | 0 | 0 | 0 | 0 | 41402.64 | 0 | 0 | 0 | 0 | 0 | 41402.64
2022022809 | 2 | 0.68635 | 54908 | 0.26276 | 9459.36 | 0.52165 | 6259.8 | 1 | 5000 | 9459.36 | 6259.8 | 0 | 0 | 0 | 0 | 34188.84 | 0 | 0 | 0 | 0 | 0 | 34188.84
2022022810 | 2 | 0.63304 | 50643.2 | 0.15434 | 5556.24 | 0.74412 | 8929.44 | 1 | 5000 | 5556.24 | 8929.44 | 0 | 0 | 0 | 0 | 31157.52 | 0 | 0 | 0 | 0 | 0 | 31157.52
2022022811 | 2 | 0.59142 | 47313.6 | 0.13718 | 4938.48 | 0.79565 | 9547.8 | 1 | 5000 | 4938.48 | 9547.8 | 0 | 0 | 0 | 0 | 27827.32 | 0 | 0 | 0 | 0 | 0 | 27827.32
2022022812 | 2 | 0.55875 | 44700 | 0.12024 | 4328.64 | 0.77458 | 9294.96 | 1 | 5000 | 4328.64 | 9294.96 | 0 | 0 | 0 | 0 | 26076.4 | 0 | 0 | 0 | 0 | 0 | 26076.4
2022022813 | 2 | 0.5302 | 42416 | 0.10156 | 3656.16 | 0.75361 | 9043.32 | 1 | 5000 | 3656.16 | 9043.32 | 0 | 0 | 0 | 0 | 24716.52 | 0 | 0 | 0 | 0 | 0 | 24716.52
2022022814 | 2 | 0.5124 | 40992 | 0.0937 | 3373.2 | 0.70928 | 8511.36 | 1 | 5000 | 3373.2 | 8511.36 | 0 | 0 | 0 | 0 | 24107.44 | 0 | 0 | 0 | 0 | 0 | 24107.44
2022022815 | 2 | 0.49923 | 39938.4 | 0.08131 | 2927.16 | 0.61015 | 7321.8 | 1 | 5000 | 2927.16 | 7321.8 | 0 | 0 | 0 | 0 | 24689.44 | 0 | 0 | 0 | 0 | 0 | 24689.44
2022022816 | 2 | 0.49412 | 39529.6 | 0.07097 | 2554.92 | 0.44308 | 5316.96 | 1 | 5000 | 2554.92 | 5316.96 | 0 | 0 | 0 | 0 | 26657.72 | 0 | 0 | 0 | 0 | 0 | 26657.72
2022022817 | 2 | 0.49745 | 39796 | 0.06488 | 2335.68 | 0.32873 | 3944.76 | 1 | 5000 | 2335.68 | 3944.76 | 0 | 0 | 0 | 0 | 28515.56 | 0 | 0 | 0 | 0 | 0 | 28515.56
2022022818 | 2 | 0.5059 | 40472 | 0.07136 | 2568.96 | 0.16998 | 2039.76 | 1 | 5000 | 2568.96 | 2039.76 | 0 | 0 | 0 | 0 | 30863.28 | 0 | 0 | 0 | 0 | 0 | 30863.28
2022022819 | 2 | 0.52966 | 42372.8 | 0.10197 | 3670.92 | 0.02129 | 255.48 | 1 | 5000 | 3670.92 | 255.48 | 0 | 0 | 0 | 0 | 33446.4 | 0 | 0 | 0 | 0 | 0 | 33446.4
2022022820 | 2 | 0.54639 | 43711.2 | 0.15273 | 5498.28 | 0 | 0 | 1 | 5000 | 5498.28 | 0 | 0 | 0 | 0 | 0 | 33212.92 | 0 | 0 | 0 | 0 | 0 | 33212.92
2022022821 | 2 | 0.54715 | 43772 | 0.22239 | 8006.04 | 0 | 0 | 1 | 5000 | 8006.04 | 0 | 0 | 0 | 0 | 0 | 30765.96 | 0 | 0 | 0 | 0 | 0 | 30765.96
2022022822 | 2 | 0.53868 | 43094.4 | 0.27887 | 10039.32 | 0 | 0 | 1 | 5000 | 10039.32 | 0 | 0 | 0 | 0 | 0 | 28055.08 | 0 | 0 | 0 | 0 | 0 | 28055.08
2022022823 | 2 | 0.51889 | 41511.2 | 0.32457 | 11684.52 | 0 | 0 | 1 | 5000 | 11684.52 | 0 | 0 | 0 | 0 | 0 | 24826.68 | 0 | 0 | 0 | 0 | 0 | 24826.68
2022022824 | 2 | 0.50023 | 40018.4 | 0.34824 | 12536.64 | 0 | 0 | 1 | 5000 | 12536.64 | 0 | 0 | 0 | 0 | 0 | 22481.76 | 0 | 0 | 0 | 0 | 0 | 22481.76
2022030101 | 3 | 0.49045 | 39236 | 0.36388 | 13099.68 | 0 | 0 | 1 | 5000 | 13099.68 | 0 | 0 | 0 | 0 | 0 | 21136.32 | 0 | 0 | 0 | 0 | 0 | 21136.32
2022030102 | 3 | 0.4915 | 39320 | 0.3645 | 13122 | 0 | 0 | 1 | 5000 | 13122 | 0 | 0 | 0 | 0 | 0 | 21198 | 0 | 0 | 0 | 0 | 0 | 21198
2022030103 | 3 | 0.49652 | 39721.6 | 0.34252 | 12330.72 | 0 | 0 | 1 | 5000 | 12330.72 | 0 | 0 | 0 | 0 | 0 | 22390.88 | 0 | 0 | 0 | 0 | 0 | 22390.88
2022030104 | 3 | 0.50844 | 40675.2 | 0.30389 | 10940.04 | 0 | 0 | 1 | 5000 | 10940.04 | 0 | 0 | 0 | 0 | 0 | 24735.16 | 0 | 0 | 0 | 0 | 0 | 24735.16
2022030105 | 3 | 0.53038 | 42430.4 | 0.26175 | 9423 | 0 | 0 | 1 | 5000 | 9423 | 0 | 0 | 0 | 0 | 0 | 28007.4 | 0 | 0 | 0 | 0 | 0 | 28007.4
2022030106 | 3 | 0.57286 | 45828.8 | 0.22343 | 8043.48 | 0 | 0 | 1 | 5000 | 8043.48 | 0 | 0 | 0 | 0 | 0 | 32785.32 | 0 | 0 | 0 | 0 | 0 | 32785.32
2022030107 | 3 | 0.63075 | 50460 | 0.19607 | 7058.52 | 0.00012 | 1.44 | 1 | 5000 | 7058.52 | 1.44 | 0 | 0 | 0 | 0 | 38400.04 | 0 | 0 | 0 | 0 | 0 | 38400.04
2022030108 | 3 | 0.64507 | 51605.6 | 0.16207 | 5834.52 | 0.06279 | 753.48 | 1 | 5000 | 5834.52 | 753.48 | 0 | 0 | 0 | 0 | 40017.6 | 0 | 0 | 0 | 0 | 0 | 40017.6
2022030109 | 3 | 0.6113 | 48904 | 0.11276 | 4059.36 | 0.32114 | 3853.68 | 1 | 5000 | 4059.36 | 3853.68 | 0 | 0 | 0 | 0 | 35990.96 | 0 | 0 | 0 | 0 | 0 | 35990.96
2022030110 | 3 | 0.5713 | 45704 | 0.07511 | 2703.96 | 0.50185 | 6022.2 | 1 | 5000 | 2703.96 | 6022.2 | 0 | 0 | 0 | 0 | 31977.84 | 0 | 0 | 0 | 0 | 0 | 31977.84
2022030111 | 3 | 0.54109 | 43287.2 | 0.067 | 2412 | 0.58955 | 7074.6 | 1 | 5000 | 2412 | 7074.6 | 0 | 0 | 0 | 0 | 28800.6 | 0 | 0 | 0 | 0 | 0 | 28800.6
2022030112 | 3 | 0.51828 | 41462.4 | 0.043 | 1548 | 0.63904 | 7668.48 | 1 | 5000 | 1548 | 7668.48 | 0 | 0 | 0 | 0 | 27245.92 | 0 | 0 | 0 | 0 | 0 | 27245.92
2022030113 | 3 | 0.50316 | 40252.8 | 0.03557 | 1280.52 | 0.63638 | 7636.56 | 1 | 5000 | 1280.52 | 7636.56 | 0 | 0 | 0 | 0 | 26335.72 | 0 | 0 | 0 | 0 | 0 | 26335.72
2022030114 | 3 | 0.49561 | 39648.8 | 0.03954 | 1423.44 | 0.62744 | 7529.28 | 1 | 5000 | 1423.44 | 7529.28 | 0 | 0 | 0 | 0 | 25696.08 | 0 | 0 | 0 | 0 | 0 | 25696.08
2022030115 | 3 | 0.49209 | 39367.2 | 0.04946 | 1780.56 | 0.57299 | 6875.88 | 1 | 5000 | 1780.56 | 6875.88 | 0 | 0 | 0 | 0 | 25710.76 | 0 | 0 | 0 | 0 | 0 | 25710.76
2022030116 | 3 | 0.49002 | 39201.6 | 0.05659 | 2037.24 | 0.516 | 6192 | 1 | 5000 | 2037.24 | 6192 | 0 | 0 | 0 | 0 | 25972.36 | 0 | 0 | 0 | 0 | 0 | 25972.36
2022030117 | 3 | 0.49588 | 39670.4 | 0.05558 | 2000.88 | 0.35572 | 4268.64 | 1 | 5000 | 2000.88 | 4268.64 | 0 | 0 | 0 | 0 | 28400.88 | 0 | 0 | 0 | 0 | 0 | 28400.88
2022030118 | 3 | 0.50104 | 40083.2 | 0.06243 | 2247.48 | 0.14397 | 1727.64 | 1 | 5000 | 2247.48 | 1727.64 | 0 | 0 | 0 | 0 | 31108.08 | 0 | 0 | 0 | 0 | 0 | 31108.08
2022030119 | 3 | 0.51643 | 41314.4 | 0.08935 | 3216.6 | 0.01515 | 181.8 | 1 | 5000 | 3216.6 | 181.8 | 0 | 0 | 0 | 0 | 32916 | 0 | 0 | 0 | 0 | 0 | 32916
2022030120 | 3 | 0.52783 | 42226.4 | 0.14846 | 5344.56 | 0 | 0 | 1 | 5000 | 5344.56 | 0 | 0 | 0 | 0 | 0 | 31881.84 | 0 | 0 | 0 | 0 | 0 | 31881.84
2022030121 | 3 | 0.52039 | 41631.2 | 0.19868 | 7152.48 | 0 | 0 | 1 | 5000 | 7152.48 | 0 | 0 | 0 | 0 | 0 | 29478.72 | 0 | 0 | 0 | 0 | 0 | 29478.72
2022030122 | 3 | 0.50845 | 40676 | 0.21926 | 7893.36 | 0 | 0 | 1 | 5000 | 7893.36 | 0 | 0 | 0 | 0 | 0 | 27782.64 | 0 | 0 | 0 | 0 | 0 | 27782.64
2022030123 | 3 | 0.48684 | 38947.2 | 0.23616 | 8501.76 | 0 | 0 | 1 | 5000 | 8501.76 | 0 | 0 | 0 | 0 | 0 | 25445.44 | 0 | 0 | 0 | 0 | 0 | 25445.44
2022030124 | 3 | 0.46351 | 37080.8 | 0.24711 | 8895.96 | 0 | 0 | 1 | 5000 | 8895.96 | 0 | 0 | 0 | 0 | 0 | 23184.84 | 0 | 0 | 0 | 0 | 0 | 23184.84
2022030201 | 4 | 0.44867 | 35893.6 | 0.25308 | 9110.88 | 0 | 0 | 1 | 5000 | 9110.88 | 0 | 0 | 0 | 0 | 0 | 21782.72 | 0 | 0 | 0 | 0 | 0 | 21782.72
2022030202 | 4 | 0.443 | 35440 | 0.24003 | 8641.08 | 0 | 0 | 1 | 5000 | 8641.08 | 0 | 0 | 0 | 0 | 0 | 21798.92 | 0 | 0 | 0 | 0 | 0 | 21798.92
2022030203 | 4 | 0.44394 | 35515.2 | 0.21364 | 7691.04 | 0 | 0 | 1 | 5000 | 7691.04 | 0 | 0 | 0 | 0 | 0 | 22824.16 | 0 | 0 | 0 | 0 | 0 | 22824.16
2022030204 | 4 | 0.4532 | 36256 | 0.18695 | 6730.2 | 0 | 0 | 1 | 5000 | 6730.2 | 0 | 0 | 0 | 0 | 0 | 24525.8 | 0 | 0 | 0 | 0 | 0 | 24525.8
2022030205 | 4 | 0.47137 | 37709.6 | 0.17655 | 6355.8 | 0 | 0 | 1 | 5000 | 6355.8 | 0 | 0 | 0 | 0 | 0 | 26353.8 | 0 | 0 | 0 | 0 | 0 | 26353.8
2022030206 | 4 | 0.50832 | 40665.6 | 0.16059 | 5781.24 | 0 | 0 | 1 | 5000 | 5781.24 | 0 | 0 | 0 | 0 | 0 | 29884.36 | 0 | 0 | 0 | 0 | 0 | 29884.36
2022030207 | 4 | 0.56281 | 45024.8 | 0.14113 | 5080.68 | 0.00012 | 1.44 | 1 | 5000 | 5080.68 | 1.44 | 0 | 0 | 0 | 0 | 34942.68 | 0 | 0 | 0 | 0 | 0 | 34942.68
2022030208 | 4 | 0.5791 | 46328 | 0.12576 | 4527.36 | 0.07821 | 938.52 | 1 | 5000 | 4527.36 | 938.52 | 0 | 0 | 0 | 0 | 35862.12 | 0 | 0 | 0 | 0 | 0 | 35862.12
2022030209 | 4 | 0.55599 | 44479.2 | 0.09044 | 3255.84 | 0.49064 | 5887.68 | 1 | 5000 | 3255.84 | 5887.68 | 0 | 0 | 0 | 0 | 30335.68 | 0 | 0 | 0 | 0 | 0 | 30335.68
2022030210 | 4 | 0.52984 | 42387.2 | 0.04615 | 1661.4 | 0.74948 | 8993.76 | 1 | 5000 | 1661.4 | 8993.76 | 0 | 0 | 0 | 0 | 26732.04 | 0 | 0 | 0 | 0 | 0 | 26732.04
2022030211 | 4 | 0.51005 | 40804 | 0.04281 | 1541.16 | 0.79194 | 9503.28 | 1 | 5000 | 1541.16 | 9503.28 | 0 | 0 | 0 | 0 | 24759.56 | 0 | 0 | 0 | 0 | 0 | 24759.56
2022030212 | 4 | 0.49966 | 39972.8 | 0.03684 | 1326.24 | 0.77189 | 9262.68 | 1 | 5000 | 1326.24 | 9262.68 | 0 | 0 | 0 | 0 | 24383.88 | 0 | 0 | 0 | 0 | 0 | 24383.88
2022030213 | 4 | 0.4932 | 39456 | 0.04066 | 1463.76 | 0.77505 | 9300.6 | 1 | 5000 | 1463.76 | 9300.6 | 0 | 0 | 0 | 0 | 23691.64 | 0 | 0 | 0 | 0 | 0 | 23691.64
2022030214 | 4 | 0.49352 | 39481.6 | 0.05635 | 2028.6 | 0.77448 | 9293.76 | 1 | 5000 | 2028.6 | 9293.76 | 0 | 0 | 0 | 0 | 23159.24 | 0 | 0 | 0 | 0 | 0 | 23159.24
2022030215 | 4 | 0.49547 | 39637.6 | 0.06745 | 2428.2 | 0.76042 | 9125.04 | 1 | 5000 | 2428.2 | 9125.04 | 0 | 0 | 0 | 0 | 23084.36 | 0 | 0 | 0 | 0 | 0 | 23084.36
2022030216 | 4 | 0.49851 | 39880.8 | 0.07766 | 2795.76 | 0.7404 | 8884.8 | 1 | 5000 | 2795.76 | 8884.8 | 0 | 0 | 0 | 0 | 23200.24 | 0 | 0 | 0 | 0 | 0 | 23200.24
2022030217 | 4 | 0.50346 | 40276.8 | 0.08782 | 3161.52 | 0.65162 | 7819.44 | 1 | 5000 | 3161.52 | 7819.44 | 0 | 0 | 0 | 0 | 24295.84 | 0 | 0 | 0 | 0 | 0 | 24295.84
2022030218 | 4 | 0.50684 | 40547.2 | 0.09839 | 3542.04 | 0.37668 | 4520.16 | 1 | 5000 | 3542.04 | 4520.16 | 0 | 0 | 0 | 0 | 27485 | 0 | 0 | 0 | 0 | 0 | 27485
2022030219 | 4 | 0.51582 | 41265.6 | 0.12593 | 4533.48 | 0.04813 | 577.56 | 1 | 5000 | 4533.48 | 577.56 | 0 | 0 | 0 | 0 | 31154.56 | 0 | 0 | 0 | 0 | 0 | 31154.56
2022030220 | 4 | 0.52328 | 41862.4 | 0.18639 | 6710.04 | 6e-05 | 0.72 | 1 | 5000 | 6710.04 | 0.72 | 0 | 0 | 0 | 0 | 30151.64 | 0 | 0 | 0 | 0 | 0 | 30151.64
2022030221 | 4 | 0.51511 | 41208.8 | 0.26249 | 9449.64 | 6e-05 | 0.72 | 1 | 5000 | 9449.64 | 0.72 | 0 | 0 | 0 | 0 | 26758.44 | 0 | 0 | 0 | 0 | 0 | 26758.44
2022030222 | 4 | 0.49902 | 39921.6 | 0.32148 | 11573.28 | 0 | 0 | 1 | 5000 | 11573.28 | 0 | 0 | 0 | 0 | 0 | 23348.32 | 0 | 0 | 0 | 0 | 0 | 23348.32
2022030223 | 4 | 0.47276 | 37820.8 | 0.35349 | 12725.64 | 0 | 0 | 1 | 5000 | 12725.64 | 0 | 0 | 0 | 0 | 0 | 20095.16 | 0 | 0 | 0 | 0 | 0 | 20095.16
2022030224 | 4 | 0.44617 | 35693.6 | 0.37012 | 13324.32 | 0 | 0 | 1 | 5000 | 13324.32 | 0 | 0 | 0 | 0 | 0 | 17369.28 | 0 | 0 | 0 | 0 | 0 | 17369.28
2022030301 | 5 | 0.42723 | 34178.4 | 0.35863 | 12910.68 | 0 | 0 | 1 | 5000 | 12910.68 | 0 | 0 | 0 | 0 | 0 | 16267.72 | 0 | 0 | 0 | 0 | 0 | 16267.72
2022030302 | 5 | 0.41755 | 33404 | 0.34059 | 12261.24 | 0 | 0 | 1 | 5000 | 12261.24 | 0 | 0 | 0 | 0 | 0 | 16142.76 | 0 | 0 | 0 | 0 | 0 | 16142.76
2022030303 | 5 | 0.4152 | 33216 | 0.29872 | 10753.92 | 0 | 0 | 1 | 5000 | 10753.92 | 0 | 0 | 0 | 0 | 0 | 17462.08 | 0 | 0 | 0 | 0 | 0 | 17462.08
2022030304 | 5 | 0.41846 | 33476.8 | 0.26379 | 9496.44 | 0 | 0 | 1 | 5000 | 9496.44 | 0 | 0 | 0 | 0 | 0 | 18980.36 | 0 | 0 | 0 | 0 | 0 | 18980.36
2022030305 | 5 | 0.43152 | 34521.6 | 0.24805 | 8929.8 | 0 | 0 | 1 | 5000 | 8929.8 | 0 | 0 | 0 | 0 | 0 | 20591.8 | 0 | 0 | 0 | 0 | 0 | 20591.8
2022030306 | 5 | 0.46244 | 36995.2 | 0.21095 | 7594.2 | 0 | 0 | 1 | 5000 | 7594.2 | 0 | 0 | 0 | 0 | 0 | 24401 | 0 | 0 | 0 | 0 | 0 | 24401
2022030307 | 5 | 0.50815 | 40652 | 0.17536 | 6312.96 | 6e-05 | 0.72 | 1 | 5000 | 6312.96 | 0.72 | 0 | 0 | 0 | 0 | 29338.32 | 0 | 0 | 0 | 0 | 0 | 29338.32
2022030308 | 5 | 0.52253 | 41802.4 | 0.15743 | 5667.48 | 0.07484 | 898.08 | 1 | 5000 | 5667.48 | 898.08 | 0 | 0 | 0 | 0 | 30236.84 | 0 | 0 | 0 | 0 | 0 | 30236.84
2022030309 | 5 | 0.51696 | 41356.8 | 0.12414 | 4469.04 | 0.52476 | 6297.12 | 1 | 5000 | 4469.04 | 6297.12 | 0 | 0 | 0 | 0 | 25590.64 | 0 | 0 | 0 | 0 | 0 | 25590.64
2022030310 | 5 | 0.50785 | 40628 | 0.06912 | 2488.32 | 0.75454 | 9054.48 | 1 | 5000 | 2488.32 | 9054.48 | 0 | 0 | 0 | 0 | 24085.2 | 0 | 0 | 0 | 0 | 0 | 24085.2
2022030311 | 5 | 0.50206 | 40164.8 | 0.07532 | 2711.52 | 0.75343 | 9041.16 | 1 | 5000 | 2711.52 | 9041.16 | 0 | 0 | 0 | 0 | 23412.12 | 0 | 0 | 0 | 0 | 0 | 23412.12
2022030312 | 5 | 0.50148 | 40118.4 | 0.06834 | 2460.24 | 0.76217 | 9146.04 | 1 | 5000 | 2460.24 | 9146.04 | 0 | 0 | 0 | 0 | 23512.12 | 0 | 0 | 0 | 0 | 0 | 23512.12
2022030313 | 5 | 0.50377 | 40301.6 | 0.08953 | 3223.08 | 0.75517 | 9062.04 | 1 | 5000 | 3223.08 | 9062.04 | 0 | 0 | 0 | 0 | 23016.48 | 0 | 0 | 0 | 0 | 0 | 23016.48
2022030314 | 5 | 0.50918 | 40734.4 | 0.13003 | 4681.08 | 0.70692 | 8483.04 | 1 | 5000 | 4681.08 | 8483.04 | 0 | 0 | 0 | 0 | 22570.28 | 0 | 0 | 0 | 0 | 0 | 22570.28
2022030315 | 5 | 0.51585 | 41268 | 0.15753 | 5671.08 | 0.70945 | 8513.4 | 1 | 5000 | 5671.08 | 8513.4 | 0 | 0 | 0 | 0 | 22083.52 | 0 | 0 | 0 | 0 | 0 | 22083.52
2022030316 | 5 | 0.52102 | 41681.6 | 0.1768 | 6364.8 | 0.67547 | 8105.64 | 1 | 5000 | 6364.8 | 8105.64 | 0 | 0 | 0 | 0 | 22211.16 | 0 | 0 | 0 | 0 | 0 | 22211.16
2022030317 | 5 | 0.52482 | 41985.6 | 0.20566 | 7403.76 | 0.54028 | 6483.36 | 1 | 5000 | 7403.76 | 6483.36 | 0 | 0 | 0 | 0 | 23098.48 | 0 | 0 | 0 | 0 | 0 | 23098.48
2022030318 | 5 | 0.52534 | 42027.2 | 0.21952 | 7902.72 | 0.2357 | 2828.4 | 1 | 5000 | 7902.72 | 2828.4 | 0 | 0 | 0 | 0 | 26296.08 | 0 | 0 | 0 | 0 | 0 | 26296.08
2022030319 | 5 | 0.53039 | 42431.2 | 0.24003 | 8641.08 | 0.02356 | 282.72 | 1 | 5000 | 8641.08 | 282.72 | 0 | 0 | 0 | 0 | 28507.4 | 0 | 0 | 0 | 0 | 0 | 28507.4
2022030320 | 5 | 0.53565 | 42852 | 0.31477 | 11331.72 | 0 | 0 | 1 | 5000 | 11331.72 | 0 | 0 | 0 | 0 | 0 | 26520.28 | 0 | 0 | 0 | 0 | 0 | 26520.28
2022030321 | 5 | 0.5276 | 42208 | 0.4328 | 15580.8 | 0 | 0 | 1 | 5000 | 15580.8 | 0 | 0 | 0 | 0 | 0 | 21627.2 | 0 | 0 | 0 | 0 | 0 | 21627.2
2022030322 | 5 | 0.51015 | 40812 | 0.50678 | 18244.08 | 0 | 0 | 1 | 5000 | 18244.08 | 0 | 0 | 0 | 0 | 0 | 17567.92 | 0 | 0 | 0 | 0 | 0 | 17567.92
2022030323 | 5 | 0.4839 | 38712 | 0.52471 | 18889.56 | 0 | 0 | 1 | 5000 | 18889.56 | 0 | 0 | 0 | 0 | 0 | 14822.44 | 0 | 0 | 0 | 0 | 0 | 14822.44
2022030324 | 5 | 0.4549 | 36392 | 0.51479 | 18532.44 | 0 | 0 | 1 | 5000 | 18532.44 | 0 | 0 | 0 | 0 | 0 | 12859.56 | 0 | 0 | 0 | 0 | 0 | 12859.56
2022030401 | 6 | 0.43322 | 34657.6 | 0.51744 | 18627.84 | 0 | 0 | 1 | 5000 | 18627.84 | 0 | 0 | 0 | 0 | 0 | 11029.76 | 0 | 0 | 0 | 0 | 0 | 11029.76
2022030402 | 6 | 0.41905 | 33524 | 0.51761 | 18633.96 | 0 | 0 | 1 | 5000 | 18633.96 | 0 | 0 | 0 | 0 | 0 | 9890.04 | 0 | 0 | 0 | 0 | 0 | 9890.04
2022030403 | 6 | 0.41252 | 33001.6 | 0.51449 | 18521.64 | 0 | 0 | 1 | 5000 | 18521.64 | 0 | 0 | 0 | 0 | 0 | 9479.96 | 0 | 0 | 0 | 0 | 0 | 9479.96
2022030404 | 6 | 0.41183 | 32946.4 | 0.5146 | 18525.6 | 0 | 0 | 1 | 5000 | 18525.6 | 0 | 0 | 0 | 0 | 0 | 9420.8 | 0 | 0 | 0 | 0 | 0 | 9420.8
2022030405 | 6 | 0.41974 | 33579.2 | 0.51938 | 18697.68 | 0 | 0 | 1 | 5000 | 18697.68 | 0 | 0 | 0 | 0 | 0 | 9881.52 | 0 | 0 | 0 | 0 | 0 | 9881.52
2022030406 | 6 | 0.44303 | 35442.4 | 0.53828 | 19378.08 | 0 | 0 | 1 | 5000 | 19378.08 | 0 | 0 | 0 | 0 | 0 | 11064.32 | 0 | 0 | 0 | 0 | 0 | 11064.32
2022030407 | 6 | 0.48199 | 38559.2 | 0.56712 | 20416.32 | 6e-05 | 0.72 | 1 | 5000 | 20416.32 | 0.72 | 0 | 0 | 0 | 0 | 13142.16 | 0 | 0 | 0 | 0 | 0 | 13142.16
2022030408 | 6 | 0.49967 | 39973.6 | 0.56105 | 20197.8 | 0.03595 | 431.4 | 1 | 5000 | 20197.8 | 431.4 | 0 | 0 | 0 | 0 | 14344.4 | 0 | 0 | 0 | 0 | 0 | 14344.4
2022030409 | 6 | 0.50672 | 40537.6 | 0.51816 | 18653.76 | 0.25483 | 3057.96 | 1 | 5000 | 18653.76 | 3057.96 | 0 | 0 | 0 | 0 | 13825.88 | 0 | 0 | 0 | 0 | 0 | 13825.88
2022030410 | 6 | 0.51617 | 41293.6 | 0.54852 | 19746.72 | 0.30847 | 3701.64 | 1 | 5000 | 19746.72 | 3701.64 | 0 | 0 | 0 | 0 | 12845.24 | 0 | 0 | 0 | 0 | 0 | 12845.24
2022030411 | 6 | 0.51888 | 41510.4 | 0.56958 | 20504.88 | 0.27013 | 3241.56 | 1 | 5000 | 20504.88 | 3241.56 | 0 | 0 | 0 | 0 | 12763.96 | 0 | 0 | 0 | 0 | 0 | 12763.96
2022030412 | 6 | 0.52263 | 41810.4 | 0.56856 | 20468.16 | 0.23712 | 2845.44 | 1 | 5000 | 20468.16 | 2845.44 | 0 | 0 | 0 | 0 | 13496.8 | 0 | 0 | 0 | 0 | 0 | 13496.8
2022030413 | 6 | 0.52442 | 41953.6 | 0.57407 | 20666.52 | 0.24979 | 2997.48 | 1 | 5000 | 20666.52 | 2997.48 | 0 | 0 | 0 | 0 | 13289.6 | 0 | 0 | 0 | 0 | 0 | 13289.6
2022030414 | 6 | 0.52744 | 42195.2 | 0.57107 | 20558.52 | 0.29326 | 3519.12 | 1 | 5000 | 20558.52 | 3519.12 | 0 | 0 | 0 | 0 | 13117.56 | 0 | 0 | 0 | 0 | 0 | 13117.56
2022030415 | 6 | 0.52899 | 42319.2 | 0.5738 | 20656.8 | 0.3147 | 3776.4 | 1 | 5000 | 20656.8 | 3776.4 | 0 | 0 | 0 | 0 | 12886 | 0 | 0 | 0 | 0 | 0 | 12886
2022030416 | 6 | 0.53017 | 42413.6 | 0.58838 | 21181.68 | 0.24723 | 2966.76 | 1 | 5000 | 21181.68 | 2966.76 | 0 | 0 | 0 | 0 | 13265.16 | 0 | 0 | 0 | 0 | 0 | 13265.16
2022030417 | 6 | 0.53099 | 42479.2 | 0.60569 | 21804.84 | 0.13648 | 1637.76 | 1 | 5000 | 21804.84 | 1637.76 | 0 | 0 | 0 | 0 | 14036.6 | 0 | 0 | 0 | 0 | 0 | 14036.6
2022030418 | 6 | 0.52961 | 42368.8 | 0.62302 | 22428.72 | 0.06731 | 807.72 | 1 | 5000 | 22428.72 | 807.72 | 0 | 0 | 0 | 0 | 14132.36 | 0 | 0 | 0 | 0 | 0 | 14132.36
2022030419 | 6 | 0.53148 | 42518.4 | 0.61845 | 22264.2 | 0.01192 | 143.04 | 1 | 5000 | 22264.2 | 143.04 | 0 | 0 | 0 | 0 | 15111.16 | 0 | 0 | 0 | 0 | 0 | 15111.16
2022030420 | 6 | 0.53207 | 42565.6 | 0.63239 | 22766.04 | 0 | 0 | 1 | 5000 | 22766.04 | 0 | 0 | 0 | 0 | 0 | 14799.56 | 0 | 0 | 0 | 0 | 0 | 14799.56
2022030421 | 6 | 0.5209 | 41672 | 0.63467 | 22848.12 | 0 | 0 | 1 | 5000 | 22848.12 | 0 | 0 | 0 | 0 | 0 | 13823.88 | 0 | 0 | 0 | 0 | 0 | 13823.88
2022030422 | 6 | 0.50822 | 40657.6 | 0.64519 | 23226.84 | 0 | 0 | 1 | 5000 | 23226.84 | 0 | 0 | 0 | 0 | 0 | 12430.76 | 0 | 0 | 0 | 0 | 0 | 12430.76
2022030423 | 6 | 0.48875 | 39100 | 0.63017 | 22686.12 | 0 | 0 | 1 | 5000 | 22686.12 | 0 | 0 | 0 | 0 | 0 | 11413.88 | 0 | 0 | 0 | 0 | 0 | 11413.88
2022030424 | 6 | 0.46498 | 37198.4 | 0.6188 | 22276.8 | 0 | 0 | 1 | 5000 | 22276.8 | 0 | 0 | 0 | 0 | 0 | 9921.6 | 0 | 0 | 0 | 0 | 0 | 9921.6
2022030501 | 7 | 0.44424 | 35539.2 | 0.6124 | 22046.4 | 0 | 0 | 1 | 5000 | 22046.4 | 0 | 0 | 0 | 0 | 0 | 8492.8 | 0 | 0 | 0 | 0 | 0 | 8492.8
2022030502 | 7 | 0.4295 | 34360 | 0.60622 | 21823.92 | 0 | 0 | 1 | 5000 | 21823.92 | 0 | 0 | 0 | 0 | 0 | 7536.08 | 0 | 0 | 0 | 0 | 0 | 7536.08
2022030503 | 7 | 0.42046 | 33636.8 | 0.59715 | 21497.4 | 0 | 0 | 1 | 5000 | 21497.4 | 0 | 0 | 0 | 0 | 0 | 7139.4 | 0 | 0 | 0 | 0 | 0 | 7139.4
2022030504 | 7 | 0.4153 | 33224 | 0.58634 | 21108.24 | 0 | 0 | 1 | 5000 | 21108.24 | 0 | 0 | 0 | 0 | 0 | 7115.76 | 0 | 0 | 0 | 0 | 0 | 7115.76
2022030505 | 7 | 0.41444 | 33155.2 | 0.57306 | 20630.16 | 0 | 0 | 1 | 5000 | 20630.16 | 0 | 0 | 0 | 0 | 0 | 7525.04 | 0 | 0 | 0 | 0 | 0 | 7525.04
2022030506 | 7 | 0.42165 | 33732 | 0.57004 | 20521.44 | 0 | 0 | 1 | 5000 | 20521.44 | 0 | 0 | 0 | 0 | 0 | 8210.56 | 0 | 0 | 0 | 0 | 0 | 8210.56
2022030507 | 7 | 0.43456 | 34764.8 | 0.56996 | 20518.56 | 0.0001 | 1.2 | 1 | 5000 | 20518.56 | 1.2 | 0 | 0 | 0 | 0 | 9245.04 | 0 | 0 | 0 | 0 | 0 | 9245.04
2022030508 | 7 | 0.44942 | 35953.6 | 0.54574 | 19646.64 | 0.05993 | 719.16 | 1 | 5000 | 19646.64 | 719.16 | 0 | 0 | 0 | 0 | 10587.8 | 0 | 0 | 0 | 0 | 0 | 10587.8
2022030509 | 7 | 0.47248 | 37798.4 | 0.47871 | 17233.56 | 0.40553 | 4866.36 | 1 | 5000 | 17233.56 | 4866.36 | 0 | 0 | 0 | 0 | 10698.48 | 0 | 0 | 0 | 0 | 0 | 10698.48
2022030510 | 7 | 0.49416 | 39532.8 | 0.49132 | 17687.52 | 0.53097 | 6371.64 | 1 | 5000 | 17687.52 | 6371.64 | 0 | 0 | 0 | 0 | 10473.64 | 0 | 0 | 0 | 0 | 0 | 10473.64
2022030511 | 7 | 0.51103 | 40882.4 | 0.53561 | 19281.96 | 0.44679 | 5361.48 | 1 | 5000 | 19281.96 | 5361.48 | 0 | 0 | 0 | 0 | 11238.96 | 0 | 0 | 0 | 0 | 0 | 11238.96
2022030512 | 7 | 0.52356 | 41884.8 | 0.55274 | 19898.64 | 0.38233 | 4587.96 | 1 | 5000 | 19898.64 | 4587.96 | 0 | 0 | 0 | 0 | 12398.2 | 0 | 0 | 0 | 0 | 0 | 12398.2
2022030513 | 7 | 0.52872 | 42297.6 | 0.55676 | 20043.36 | 0.33446 | 4013.52 | 1 | 5000 | 20043.36 | 4013.52 | 0 | 0 | 0 | 0 | 13240.72 | 0 | 0 | 0 | 0 | 0 | 13240.72
2022030514 | 7 | 0.53031 | 42424.8 | 0.5501 | 19803.6 | 0.33176 | 3981.12 | 1 | 5000 | 19803.6 | 3981.12 | 0 | 0 | 0 | 0 | 13640.08 | 0 | 0 | 0 | 0 | 0 | 13640.08
2022030515 | 7 | 0.53149 | 42519.2 | 0.52221 | 18799.56 | 0.38316 | 4597.92 | 1 | 5000 | 18799.56 | 4597.92 | 0 | 0 | 0 | 0 | 14121.72 | 0 | 0 | 0 | 0 | 0 | 14121.72
2022030516 | 7 | 0.53571 | 42856.8 | 0.50699 | 18251.64 | 0.35618 | 4274.16 | 1 | 5000 | 18251.64 | 4274.16 | 0 | 0 | 0 | 0 | 15331 | 0 | 0 | 0 | 0 | 0 | 15331
2022030517 | 7 | 0.53852 | 43081.6 | 0.50479 | 18172.44 | 0.29858 | 3582.96 | 1 | 5000 | 18172.44 | 3582.96 | 0 | 0 | 0 | 0 | 16326.2 | 0 | 0 | 0 | 0 | 0 | 16326.2
2022030518 | 7 | 0.53521 | 42816.8 | 0.47123 | 16964.28 | 0.29242 | 3509.04 | 1 | 5000 | 16964.28 | 3509.04 | 0 | 0 | 0 | 0 | 17343.48 | 0 | 0 | 0 | 0 | 0 | 17343.48
2022030519 | 7 | 0.5348 | 42784 | 0.39197 | 14110.92 | 0.06636 | 796.32 | 1 | 5000 | 14110.92 | 796.32 | 0 | 0 | 0 | 0 | 22876.76 | 0 | 0 | 0 | 0 | 0 | 22876.76
2022030520 | 7 | 0.53641 | 42912.8 | 0.35404 | 12745.44 | 0 | 0 | 1 | 5000 | 12745.44 | 0 | 0 | 0 | 0 | 0 | 25167.36 | 0 | 0 | 0 | 0 | 0 | 25167.36
2022030521 | 7 | 0.52337 | 41869.6 | 0.34292 | 12345.12 | 0 | 0 | 1 | 5000 | 12345.12 | 0 | 0 | 0 | 0 | 0 | 24524.48 | 0 | 0 | 0 | 0 | 0 | 24524.48
2022030522 | 7 | 0.50941 | 40752.8 | 0.3571 | 12855.6 | 0 | 0 | 1 | 5000 | 12855.6 | 0 | 0 | 0 | 0 | 0 | 22897.2 | 0 | 0 | 0 | 0 | 0 | 22897.2
2022030523 | 7 | 0.4923 | 39384 | 0.40762 | 14674.32 | 0 | 0 | 1 | 5000 | 14674.32 | 0 | 0 | 0 | 0 | 0 | 19709.68 | 0 | 0 | 0 | 0 | 0 | 19709.68
2022030524 | 7 | 0.47398 | 37918.4 | 0.51389 | 18500.04 | 0 | 0 | 1 | 5000 | 18500.04 | 0 | 0 | 0 | 0 | 0 | 14418.36 | 0 | 0 | 0 | 0 | 0 | 14418.36
2022030601 | 1 | 0.45575 | 36460 | 0.59235 | 21324.6 | 0 | 0 | 1 | 5000 | 21324.6 | 0 | 0 | 0 | 0 | 0 | 10135.4 | 0 | 0 | 0 | 0 | 0 | 10135.4
2022030602 | 1 | 0.43988 | 35190.4 | 0.60972 | 21949.92 | 0 | 0 | 1 | 5000 | 21949.92 | 0 | 0 | 0 | 0 | 0 | 8240.48 | 0 | 0 | 0 | 0 | 0 | 8240.48
2022030603 | 1 | 0.42897 | 34317.6 | 0.60705 | 21853.8 | 0 | 0 | 1 | 5000 | 21853.8 | 0 | 0 | 0 | 0 | 0 | 7463.8 | 0 | 0 | 0 | 0 | 0 | 7463.8
2022030604 | 1 | 0.42184 | 33747.2 | 0.59932 | 21575.52 | 0 | 0 | 1 | 5000 | 21575.52 | 0 | 0 | 0 | 0 | 0 | 7171.68 | 0 | 0 | 0 | 0 | 0 | 7171.68
2022030605 | 1 | 0.41913 | 33530.4 | 0.58424 | 21032.64 | 0 | 0 | 1 | 5000 | 21032.64 | 0 | 0 | 0 | 0 | 0 | 7497.76 | 0 | 0 | 0 | 0 | 0 | 7497.76
2022030606 | 1 | 0.42133 | 33706.4 | 0.57657 | 20756.52 | 0 | 0 | 1 | 5000 | 20756.52 | 0 | 0 | 0 | 0 | 0 | 7949.88 | 0 | 0 | 0 | 0 | 0 | 7949.88
2022030607 | 1 | 0.42766 | 34212.8 | 0.5523 | 19882.8 | 0 | 0 | 1 | 5000 | 19882.8 | 0 | 0 | 0 | 0 | 0 | 9330 | 0 | 0 | 0 | 0 | 0 | 9330
2022030608 | 1 | 0.43713 | 34970.4 | 0.56147 | 20212.92 | 0.03339 | 400.68 | 1 | 5000 | 20212.92 | 400.68 | 0 | 0 | 0 | 0 | 9356.8 | 0 | 0 | 0 | 0 | 0 | 9356.8
2022030609 | 1 | 0.46321 | 37056.8 | 0.56812 | 20452.32 | 0.2423 | 2907.6 | 1 | 5000 | 20452.32 | 2907.6 | 0 | 0 | 0 | 0 | 8696.88 | 0 | 0 | 0 | 0 | 0 | 8696.88
2022030610 | 1 | 0.48839 | 39071.2 | 0.55321 | 19915.56 | 0.38015 | 4561.8 | 1 | 5000 | 19915.56 | 4561.8 | 0 | 0 | 0 | 0 | 9593.84 | 0 | 0 | 0 | 0 | 0 | 9593.84
2022030611 | 1 | 0.50742 | 40593.6 | 0.49998 | 17999.28 | 0.53907 | 6468.84 | 1 | 5000 | 17999.28 | 6468.84 | 0 | 0 | 0 | 0 | 11125.48 | 0 | 0 | 0 | 0 | 0 | 11125.48
2022030612 | 1 | 0.52195 | 41756 | 0.46715 | 16817.4 | 0.57447 | 6893.64 | 1 | 5000 | 16817.4 | 6893.64 | 0 | 0 | 0 | 0 | 13044.96 | 0 | 0 | 0 | 0 | 0 | 13044.96
2022030613 | 1 | 0.53169 | 42535.2 | 0.44321 | 15955.56 | 0.60779 | 7293.48 | 1 | 5000 | 15955.56 | 7293.48 | 0 | 0 | 0 | 0 | 14286.16 | 0 | 0 | 0 | 0 | 0 | 14286.16
2022030614 | 1 | 0.53815 | 43052 | 0.43799 | 15767.64 | 0.60983 | 7317.96 | 1 | 5000 | 15767.64 | 7317.96 | 0 | 0 | 0 | 0 | 14966.4 | 0 | 0 | 0 | 0 | 0 | 14966.4
2022030615 | 1 | 0.54081 | 43264.8 | 0.45822 | 16495.92 | 0.58489 | 7018.68 | 1 | 5000 | 16495.92 | 7018.68 | 0 | 0 | 0 | 0 | 14750.2 | 0 | 0 | 0 | 0 | 0 | 14750.2
2022030616 | 1 | 0.54364 | 43491.2 | 0.50932 | 18335.52 | 0.44288 | 5314.56 | 1 | 5000 | 18335.52 | 5314.56 | 0 | 0 | 0 | 0 | 14841.12 | 0 | 0 | 0 | 0 | 0 | 14841.12
2022030617 | 1 | 0.54663 | 43730.4 | 0.5513 | 19846.8 | 0.30234 | 3628.08 | 1 | 5000 | 19846.8 | 3628.08 | 0 | 0 | 0 | 0 | 15255.52 | 0 | 0 | 0 | 0 | 0 | 15255.52
2022030618 | 1 | 0.54758 | 43806.4 | 0.57796 | 20806.56 | 0.17566 | 2107.92 | 1 | 5000 | 20806.56 | 2107.92 | 0 | 0 | 0 | 0 | 15891.92 | 0 | 0 | 0 | 0 | 0 | 15891.92
2022030619 | 1 | 0.55224 | 44179.2 | 0.59825 | 21537 | 0.04334 | 520.08 | 1 | 5000 | 21537 | 520.08 | 0 | 0 | 0 | 0 | 17122.12 | 0 | 0 | 0 | 0 | 0 | 17122.12
2022030620 | 1 | 0.55865 | 44692 | 0.61169 | 22020.84 | 0 | 0 | 1 | 5000 | 22020.84 | 0 | 0 | 0 | 0 | 0 | 17671.16 | 0 | 0 | 0 | 0 | 0 | 17671.16
2022030621 | 1 | 0.55027 | 44021.6 | 0.61908 | 22286.88 | 0 | 0 | 1 | 5000 | 22286.88 | 0 | 0 | 0 | 0 | 0 | 16734.72 | 0 | 0 | 0 | 0 | 0 | 16734.72
2022030622 | 1 | 0.53396 | 42716.8 | 0.6038 | 21736.8 | 0 | 0 | 1 | 5000 | 21736.8 | 0 | 0 | 0 | 0 | 0 | 15980 | 0 | 0 | 0 | 0 | 0 | 15980
2022030623 | 1 | 0.50962 | 40769.6 | 0.59062 | 21262.32 | 0 | 0 | 1 | 5000 | 21262.32 | 0 | 0 | 0 | 0 | 0 | 14507.28 | 0 | 0 | 0 | 0 | 0 | 14507.28
2022030624 | 1 | 0.48314 | 38651.2 | 0.58724 | 21140.64 | 0 | 0 | 1 | 5000 | 21140.64 | 0 | 0 | 0 | 0 | 0 | 12510.56 | 0 | 0 | 0 | 0 | 0 | 12510.56
2022030701 | 2 | 0.46147 | 36917.6 | 0.58102 | 20916.72 | 0 | 0 | 1 | 5000 | 20916.72 | 0 | 0 | 0 | 0 | 0 | 11000.88 | 0 | 0 | 0 | 0 | 0 | 11000.88
2022030702 | 2 | 0.4478 | 35824 | 0.58907 | 21206.52 | 0 | 0 | 1 | 5000 | 21206.52 | 0 | 0 | 0 | 0 | 0 | 9617.48 | 0 | 0 | 0 | 0 | 0 | 9617.48
2022030703 | 2 | 0.44169 | 35335.2 | 0.5916 | 21297.6 | 0 | 0 | 1 | 5000 | 21297.6 | 0 | 0 | 0 | 0 | 0 | 9037.6 | 0 | 0 | 0 | 0 | 0 | 9037.6
2022030704 | 2 | 0.44539 | 35631.2 | 0.58908 | 21206.88 | 0 | 0 | 1 | 5000 | 21206.88 | 0 | 0 | 0 | 0 | 0 | 9424.32 | 0 | 0 | 0 | 0 | 0 | 9424.32
2022030705 | 2 | 0.45776 | 36620.8 | 0.57555 | 20719.8 | 0 | 0 | 1 | 5000 | 20719.8 | 0 | 0 | 0 | 0 | 0 | 10901 | 0 | 0 | 0 | 0 | 0 | 10901
2022030706 | 2 | 0.48621 | 38896.8 | 0.54722 | 19699.92 | 0 | 0 | 1 | 5000 | 19699.92 | 0 | 0 | 0 | 0 | 0 | 14196.88 | 0 | 0 | 0 | 0 | 0 | 14196.88
2022030707 | 2 | 0.53334 | 42667.2 | 0.53052 | 19098.72 | 0 | 0 | 1 | 5000 | 19098.72 | 0 | 0 | 0 | 0 | 0 | 18568.48 | 0 | 0 | 0 | 0 | 0 | 18568.48
2022030708 | 2 | 0.56127 | 44901.6 | 0.53473 | 19250.28 | 0.06254 | 750.48 | 1 | 5000 | 19250.28 | 750.48 | 0 | 0 | 0 | 0 | 19900.84 | 0 | 0 | 0 | 0 | 0 | 19900.84
2022030709 | 2 | 0.57557 | 46045.6 | 0.5232 | 18835.2 | 0.3588 | 4305.6 | 1 | 5000 | 18835.2 | 4305.6 | 0 | 0 | 0 | 0 | 17904.8 | 0 | 0 | 0 | 0 | 0 | 17904.8
2022030710 | 2 | 0.58428 | 46742.4 | 0.54662 | 19678.32 | 0.346 | 4152 | 1 | 5000 | 19678.32 | 4152 | 0 | 0 | 0 | 0 | 17912.08 | 0 | 0 | 0 | 0 | 0 | 17912.08
2022030711 | 2 | 0.58566 | 46852.8 | 0.48798 | 17567.28 | 0.55163 | 6619.56 | 1 | 5000 | 17567.28 | 6619.56 | 0 | 0 | 0 | 0 | 17665.96 | 0 | 0 | 0 | 0 | 0 | 17665.96
2022030712 | 2 | 0.58084 | 46467.2 | 0.42359 | 15249.24 | 0.71908 | 8628.96 | 1 | 5000 | 15249.24 | 8628.96 | 0 | 0 | 0 | 0 | 17589 | 0 | 0 | 0 | 0 | 0 | 17589
2022030713 | 2 | 0.57063 | 45650.4 | 0.34414 | 12389.04 | 0.72571 | 8708.52 | 1 | 5000 | 12389.04 | 8708.52 | 0 | 0 | 0 | 0 | 19552.84 | 0 | 0 | 0 | 0 | 0 | 19552.84
2022030714 | 2 | 0.55877 | 44701.6 | 0.29431 | 10595.16 | 0.72021 | 8642.52 | 1 | 5000 | 10595.16 | 8642.52 | 0 | 0 | 0 | 0 | 20463.92 | 0 | 0 | 0 | 0 | 0 | 20463.92
2022030715 | 2 | 0.54528 | 43622.4 | 0.26133 | 9407.88 | 0.70853 | 8502.36 | 1 | 5000 | 9407.88 | 8502.36 | 0 | 0 | 0 | 0 | 20712.16 | 0 | 0 | 0 | 0 | 0 | 20712.16
2022030716 | 2 | 0.53646 | 42916.8 | 0.24966 | 8987.76 | 0.6847 | 8216.4 | 1 | 5000 | 8987.76 | 8216.4 | 0 | 0 | 0 | 0 | 20712.64 | 0 | 0 | 0 | 0 | 0 | 20712.64
2022030717 | 2 | 0.53922 | 43137.6 | 0.23996 | 8638.56 | 0.61789 | 7414.68 | 1 | 5000 | 8638.56 | 7414.68 | 0 | 0 | 0 | 0 | 22084.36 | 0 | 0 | 0 | 0 | 0 | 22084.36
2022030718 | 2 | 0.55048 | 44038.4 | 0.23269 | 8376.84 | 0.39526 | 4743.12 | 1 | 5000 | 8376.84 | 4743.12 | 0 | 0 | 0 | 0 | 25918.44 | 0 | 0 | 0 | 0 | 0 | 25918.44
2022030719 | 2 | 0.57804 | 46243.2 | 0.21848 | 7865.28 | 0.05446 | 653.52 | 1 | 5000 | 7865.28 | 653.52 | 0 | 0 | 0 | 0 | 32724.4 | 0 | 0 | 0 | 0 | 0 | 32724.4
2022030720 | 2 | 0.59508 | 47606.4 | 0.23938 | 8617.68 | 0 | 0 | 1 | 5000 | 8617.68 | 0 | 0 | 0 | 0 | 0 | 33988.72 | 0 | 0 | 0 | 0 | 0 | 33988.72
2022030721 | 2 | 0.5912 | 47296 | 0.28581 | 10289.16 | 0 | 0 | 1 | 5000 | 10289.16 | 0 | 0 | 0 | 0 | 0 | 32006.84 | 0 | 0 | 0 | 0 | 0 | 32006.84
2022030722 | 2 | 0.57558 | 46046.4 | 0.31566 | 11363.76 | 0 | 0 | 1 | 5000 | 11363.76 | 0 | 0 | 0 | 0 | 0 | 29682.64 | 0 | 0 | 0 | 0 | 0 | 29682.64
2022030723 | 2 | 0.55093 | 44074.4 | 0.3402 | 12247.2 | 0 | 0 | 1 | 5000 | 12247.2 | 0 | 0 | 0 | 0 | 0 | 26827.2 | 0 | 0 | 0 | 0 | 0 | 26827.2
2022030724 | 2 | 0.52836 | 42268.8 | 0.3368 | 12124.8 | 0 | 0 | 1 | 5000 | 12124.8 | 0 | 0 | 0 | 0 | 0 | 25144 | 0 | 0 | 0 | 0 | 0 | 25144
2022030801 | 3 | 0.51421 | 41136.8 | 0.2903 | 10450.8 | 0 | 0 | 1 | 5000 | 10450.8 | 0 | 0 | 0 | 0 | 0 | 25686 | 0 | 0 | 0 | 0 | 0 | 25686
2022030802 | 3 | 0.51001 | 40800.8 | 0.25647 | 9232.92 | 0 | 0 | 1 | 5000 | 9232.92 | 0 | 0 | 0 | 0 | 0 | 26567.88 | 0 | 0 | 0 | 0 | 0 | 26567.88
2022030803 | 3 | 0.50831 | 40664.8 | 0.23747 | 8548.92 | 0 | 0 | 1 | 5000 | 8548.92 | 0 | 0 | 0 | 0 | 0 | 27115.88 | 0 | 0 | 0 | 0 | 0 | 27115.88
2022030804 | 3 | 0.51442 | 41153.6 | 0.21295 | 7666.2 | 0 | 0 | 1 | 5000 | 7666.2 | 0 | 0 | 0 | 0 | 0 | 28487.4 | 0 | 0 | 0 | 0 | 0 | 28487.4
2022030805 | 3 | 0.53039 | 42431.2 | 0.21253 | 7651.08 | 0 | 0 | 1 | 5000 | 7651.08 | 0 | 0 | 0 | 0 | 0 | 29780.12 | 0 | 0 | 0 | 0 | 0 | 29780.12
2022030806 | 3 | 0.56359 | 45087.2 | 0.2047 | 7369.2 | 0 | 0 | 1 | 5000 | 7369.2 | 0 | 0 | 0 | 0 | 0 | 32718 | 0 | 0 | 0 | 0 | 0 | 32718
2022030807 | 3 | 0.61356 | 49084.8 | 0.17261 | 6213.96 | 0.00022 | 2.64 | 1 | 5000 | 6213.96 | 2.64 | 0 | 0 | 0 | 0 | 37868.2 | 0 | 0 | 0 | 0 | 0 | 37868.2
2022030808 | 3 | 0.63452 | 50761.6 | 0.1426 | 5133.6 | 0.03867 | 464.04 | 1 | 5000 | 5133.6 | 464.04 | 0 | 0 | 0 | 0 | 40163.96 | 0 | 0 | 0 | 0 | 0 | 40163.96
2022030809 | 3 | 0.63481 | 50784.8 | 0.09499 | 3419.64 | 0.31248 | 3749.76 | 1 | 5000 | 3419.64 | 3749.76 | 0 | 0 | 0 | 0 | 38615.4 | 0 | 0 | 0 | 0 | 0 | 38615.4
2022030810 | 3 | 0.63543 | 50834.4 | 0.06731 | 2423.16 | 0.52608 | 6312.96 | 1 | 5000 | 2423.16 | 6312.96 | 0 | 0 | 0 | 0 | 37098.28 | 0 | 0 | 0 | 0 | 0 | 37098.28
2022030811 | 3 | 0.63482 | 50785.6 | 0.04975 | 1791 | 0.61028 | 7323.36 | 1 | 5000 | 1791 | 7323.36 | 0 | 0 | 0 | 0 | 36671.24 | 0 | 0 | 0 | 0 | 0 | 36671.24
2022030812 | 3 | 0.62582 | 50065.6 | 0.05449 | 1961.64 | 0.67233 | 8067.96 | 1 | 5000 | 1961.64 | 8067.96 | 0 | 0 | 0 | 0 | 35036 | 0 | 0 | 0 | 0 | 0 | 35036
2022030813 | 3 | 0.61313 | 49050.4 | 0.06465 | 2327.4 | 0.71247 | 8549.64 | 1 | 5000 | 2327.4 | 8549.64 | 0 | 0 | 0 | 0 | 33173.36 | 0 | 0 | 0 | 0 | 0 | 33173.36
2022030814 | 3 | 0.59988 | 47990.4 | 0.06105 | 2197.8 | 0.73189 | 8782.68 | 1 | 5000 | 2197.8 | 8782.68 | 0 | 0 | 0 | 0 | 32009.92 | 0 | 0 | 0 | 0 | 0 | 32009.92
2022030815 | 3 | 0.58113 | 46490.4 | 0.05588 | 2011.68 | 0.74468 | 8936.16 | 1 | 5000 | 2011.68 | 8936.16 | 0 | 0 | 0 | 0 | 30542.56 | 0 | 0 | 0 | 0 | 0 | 30542.56
2022030816 | 3 | 0.56782 | 45425.6 | 0.06793 | 2445.48 | 0.75731 | 9087.72 | 1 | 5000 | 2445.48 | 9087.72 | 0 | 0 | 0 | 0 | 28892.4 | 0 | 0 | 0 | 0 | 0 | 28892.4
2022030817 | 3 | 0.56452 | 45161.6 | 0.07857 | 2828.52 | 0.7652 | 9182.4 | 1 | 5000 | 2828.52 | 9182.4 | 0 | 0 | 0 | 0 | 28150.68 | 0 | 0 | 0 | 0 | 0 | 28150.68
2022030818 | 3 | 0.57277 | 45821.6 | 0.07134 | 2568.24 | 0.54073 | 6488.76 | 1 | 5000 | 2568.24 | 6488.76 | 0 | 0 | 0 | 0 | 31764.6 | 0 | 0 | 0 | 0 | 0 | 31764.6
2022030819 | 3 | 0.5976 | 47808 | 0.05743 | 2067.48 | 0.07921 | 950.52 | 1 | 5000 | 2067.48 | 950.52 | 0 | 0 | 0 | 0 | 39790 | 0 | 0 | 0 | 0 | 0 | 39790
2022030820 | 3 | 0.61823 | 49458.4 | 0.07197 | 2590.92 | 0 | 0 | 1 | 5000 | 2590.92 | 0 | 0 | 0 | 0 | 0 | 41867.48 | 0 | 0 | 0 | 0 | 0 | 41867.48
2022030821 | 3 | 0.61825 | 49460 | 0.10392 | 3741.12 | 0 | 0 | 1 | 5000 | 3741.12 | 0 | 0 | 0 | 0 | 0 | 40718.88 | 0 | 0 | 0 | 0 | 0 | 40718.88
2022030822 | 3 | 0.60639 | 48511.2 | 0.15205 | 5473.8 | 0 | 0 | 1 | 5000 | 5473.8 | 0 | 0 | 0 | 0 | 0 | 38037.4 | 0 | 0 | 0 | 0 | 0 | 38037.4
2022030823 | 3 | 0.58414 | 46731.2 | 0.18293 | 6585.48 | 0 | 0 | 1 | 5000 | 6585.48 | 0 | 0 | 0 | 0 | 0 | 35145.72 | 0 | 0 | 0 | 0 | 0 | 35145.72
2022030824 | 3 | 0.56298 | 45038.4 | 0.21121 | 7603.56 | 0 | 0 | 1 | 5000 | 7603.56 | 0 | 0 | 0 | 0 | 0 | 32434.84 | 0 | 0 | 0 | 0 | 0 | 32434.84
2022030901 | 4 | 0.55161 | 44128.8 | 0.21483 | 7733.88 | 0 | 0 | 1 | 5000 | 7733.88 | 0 | 0 | 0 | 0 | 0 | 31394.92 | 0 | 0 | 0 | 0 | 0 | 31394.92
2022030902 | 4 | 0.54762 | 43809.6 | 0.19616 | 7061.76 | 0 | 0 | 1 | 5000 | 7061.76 | 0 | 0 | 0 | 0 | 0 | 31747.84 | 0 | 0 | 0 | 0 | 0 | 31747.84
2022030903 | 4 | 0.55008 | 44006.4 | 0.18747 | 6748.92 | 0 | 0 | 1 | 5000 | 6748.92 | 0 | 0 | 0 | 0 | 0 | 32257.48 | 0 | 0 | 0 | 0 | 0 | 32257.48
2022030904 | 4 | 0.55861 | 44688.8 | 0.20136 | 7248.96 | 0 | 0 | 1 | 5000 | 7248.96 | 0 | 0 | 0 | 0 | 0 | 32439.84 | 0 | 0 | 0 | 0 | 0 | 32439.84
2022030905 | 4 | 0.57496 | 45996.8 | 0.21275 | 7659 | 0 | 0 | 1 | 5000 | 7659 | 0 | 0 | 0 | 0 | 0 | 33337.8 | 0 | 0 | 0 | 0 | 0 | 33337.8
2022030906 | 4 | 0.61281 | 49024.8 | 0.23315 | 8393.4 | 0 | 0 | 1 | 5000 | 8393.4 | 0 | 0 | 0 | 0 | 0 | 35631.4 | 0 | 0 | 0 | 0 | 0 | 35631.4
2022030907 | 4 | 0.66254 | 53003.2 | 0.25016 | 9005.76 | 0.0003 | 3.6 | 1 | 5000 | 9005.76 | 3.6 | 0 | 0 | 0 | 0 | 38993.84 | 0 | 0 | 0 | 0 | 0 | 38993.84
2022030908 | 4 | 0.67374 | 53899.2 | 0.24927 | 8973.72 | 0.12182 | 1461.84 | 1 | 5000 | 8973.72 | 1461.84 | 0 | 0 | 0 | 0 | 38463.64 | 0 | 0 | 0 | 0 | 0 | 38463.64
2022030909 | 4 | 0.64659 | 51727.2 | 0.20067 | 7224.12 | 0.63016 | 7561.92 | 1 | 5000 | 7224.12 | 7561.92 | 0 | 0 | 0 | 0 | 31941.16 | 0 | 0 | 0 | 0 | 0 | 31941.16
2022030910 | 4 | 0.61669 | 49335.2 | 0.21691 | 7808.76 | 0.83956 | 10074.72 | 1 | 5000 | 7808.76 | 10074.72 | 0 | 0 | 0 | 0 | 26451.72 | 0 | 0 | 0 | 0 | 0 | 26451.72
2022030911 | 4 | 0.59148 | 47318.4 | 0.25386 | 9138.96 | 0.84661 | 10159.32 | 1 | 5000 | 9138.96 | 10159.32 | 0 | 0 | 0 | 0 | 23020.12 | 0 | 0 | 0 | 0 | 0 | 23020.12
2022030912 | 4 | 0.56686 | 45348.8 | 0.26458 | 9524.88 | 0.84373 | 10124.76 | 1 | 5000 | 9524.88 | 10124.76 | 0 | 0 | 0 | 0 | 20699.16 | 0 | 0 | 0 | 0 | 0 | 20699.16
2022030913 | 4 | 0.54548 | 43638.4 | 0.27198 | 9791.28 | 0.84192 | 10103.04 | 1 | 5000 | 9791.28 | 10103.04 | 0 | 0 | 0 | 0 | 18744.08 | 0 | 0 | 0 | 0 | 0 | 18744.08
2022030914 | 4 | 0.52871 | 42296.8 | 0.28376 | 10215.36 | 0.81994 | 9839.28 | 1 | 5000 | 10215.36 | 9839.28 | 0 | 0 | 0 | 0 | 17242.16 | 0 | 0 | 0 | 0 | 0 | 17242.16
2022030915 | 4 | 0.51593 | 41274.4 | 0.29848 | 10745.28 | 0.76654 | 9198.48 | 1 | 5000 | 10745.28 | 9198.48 | 0 | 0 | 0 | 0 | 16330.64 | 0 | 0 | 0 | 0 | 0 | 16330.64
2022030916 | 4 | 0.50885 | 40708 | 0.31893 | 11481.48 | 0.70864 | 8503.68 | 1 | 5000 | 11481.48 | 8503.68 | 0 | 0 | 0 | 0 | 15722.84 | 0 | 0 | 0 | 0 | 0 | 15722.84
2022030917 | 4 | 0.50836 | 40668.8 | 0.34416 | 12389.76 | 0.61793 | 7415.16 | 1 | 5000 | 12389.76 | 7415.16 | 0 | 0 | 0 | 0 | 15863.88 | 0 | 0 | 0 | 0 | 0 | 15863.88
2022030918 | 4 | 0.51502 | 41201.6 | 0.3575 | 12870 | 0.44183 | 5301.96 | 1 | 5000 | 12870 | 5301.96 | 0 | 0 | 0 | 0 | 18029.64 | 0 | 0 | 0 | 0 | 0 | 18029.64
2022030919 | 4 | 0.53396 | 42716.8 | 0.40412 | 14548.32 | 0.08058 | 966.96 | 1 | 5000 | 14548.32 | 966.96 | 0 | 0 | 0 | 0 | 22201.52 | 0 | 0 | 0 | 0 | 0 | 22201.52
2022030920 | 4 | 0.55581 | 44464.8 | 0.47314 | 17033.04 | 0 | 0 | 1 | 5000 | 17033.04 | 0 | 0 | 0 | 0 | 0 | 22431.76 | 0 | 0 | 0 | 0 | 0 | 22431.76
2022030921 | 4 | 0.5607 | 44856 | 0.50879 | 18316.44 | 0 | 0 | 1 | 5000 | 18316.44 | 0 | 0 | 0 | 0 | 0 | 21539.56 | 0 | 0 | 0 | 0 | 0 | 21539.56
2022030922 | 4 | 0.55328 | 44262.4 | 0.52855 | 19027.8 | 0 | 0 | 1 | 5000 | 19027.8 | 0 | 0 | 0 | 0 | 0 | 20234.6 | 0 | 0 | 0 | 0 | 0 | 20234.6
2022030923 | 4 | 0.53456 | 42764.8 | 0.51672 | 18601.92 | 0 | 0 | 1 | 5000 | 18601.92 | 0 | 0 | 0 | 0 | 0 | 19162.88 | 0 | 0 | 0 | 0 | 0 | 19162.88
2022030924 | 4 | 0.5165 | 41320 | 0.50479 | 18172.44 | 0 | 0 | 1 | 5000 | 18172.44 | 0 | 0 | 0 | 0 | 0 | 18147.56 | 0 | 0 | 0 | 0 | 0 | 18147.56
2022031001 | 5 | 0.50665 | 40532 | 0.48839 | 17582.04 | 0 | 0 | 1 | 5000 | 17582.04 | 0 | 0 | 0 | 0 | 0 | 17949.96 | 0 | 0 | 0 | 0 | 0 | 17949.96
2022031002 | 5 | 0.50414 | 40331.2 | 0.48083 | 17309.88 | 0 | 0 | 1 | 5000 | 17309.88 | 0 | 0 | 0 | 0 | 0 | 18021.32 | 0 | 0 | 0 | 0 | 0 | 18021.32
2022031003 | 5 | 0.5064 | 40512 | 0.47621 | 17143.56 | 0 | 0 | 1 | 5000 | 17143.56 | 0 | 0 | 0 | 0 | 0 | 18368.44 | 0 | 0 | 0 | 0 | 0 | 18368.44
2022031004 | 5 | 0.51519 | 41215.2 | 0.48218 | 17358.48 | 0 | 0 | 1 | 5000 | 17358.48 | 0 | 0 | 0 | 0 | 0 | 18856.72 | 0 | 0 | 0 | 0 | 0 | 18856.72
2022031005 | 5 | 0.531 | 42480 | 0.4818 | 17344.8 | 0 | 0 | 1 | 5000 | 17344.8 | 0 | 0 | 0 | 0 | 0 | 20135.2 | 0 | 0 | 0 | 0 | 0 | 20135.2
2022031006 | 5 | 0.56573 | 45258.4 | 0.47837 | 17221.32 | 0 | 0 | 1 | 5000 | 17221.32 | 0 | 0 | 0 | 0 | 0 | 23037.08 | 0 | 0 | 0 | 0 | 0 | 23037.08
2022031007 | 5 | 0.6154 | 49232 | 0.47616 | 17141.76 | 0.00062 | 7.44 | 1 | 5000 | 17141.76 | 7.44 | 0 | 0 | 0 | 0 | 27082.8 | 0 | 0 | 0 | 0 | 0 | 27082.8
2022031008 | 5 | 0.62219 | 49775.2 | 0.46099 | 16595.64 | 0.12689 | 1522.68 | 1 | 5000 | 16595.64 | 1522.68 | 0 | 0 | 0 | 0 | 26656.88 | 0 | 0 | 0 | 0 | 0 | 26656.88
2022031009 | 5 | 0.59258 | 47406.4 | 0.33851 | 12186.36 | 0.57646 | 6917.52 | 1 | 5000 | 12186.36 | 6917.52 | 0 | 0 | 0 | 0 | 23302.52 | 0 | 0 | 0 | 0 | 0 | 23302.52
2022031010 | 5 | 0.56525 | 45220 | 0.26076 | 9387.36 | 0.8255 | 9906 | 1 | 5000 | 9387.36 | 9906 | 0 | 0 | 0 | 0 | 20926.64 | 0 | 0 | 0 | 0 | 0 | 20926.64
2022031011 | 5 | 0.54172 | 43337.6 | 0.21999 | 7919.64 | 0.87172 | 10460.64 | 1 | 5000 | 7919.64 | 10460.64 | 0 | 0 | 0 | 0 | 19957.32 | 0 | 0 | 0 | 0 | 0 | 19957.32
2022031012 | 5 | 0.52319 | 41855.2 | 0.17012 | 6124.32 | 0.86699 | 10403.88 | 1 | 5000 | 6124.32 | 10403.88 | 0 | 0 | 0 | 0 | 20327 | 0 | 0 | 0 | 0 | 0 | 20327
2022031013 | 5 | 0.50615 | 40492 | 0.13589 | 4892.04 | 0.86204 | 10344.48 | 1 | 5000 | 4892.04 | 10344.48 | 0 | 0 | 0 | 0 | 20255.48 | 0 | 0 | 0 | 0 | 0 | 20255.48
2022031014 | 5 | 0.49861 | 39888.8 | 0.13832 | 4979.52 | 0.85597 | 10271.64 | 1 | 5000 | 4979.52 | 10271.64 | 0 | 0 | 0 | 0 | 19637.64 | 0 | 0 | 0 | 0 | 0 | 19637.64
2022031015 | 5 | 0.4953 | 39624 | 0.15514 | 5585.04 | 0.85786 | 10294.32 | 1 | 5000 | 5585.04 | 10294.32 | 0 | 0 | 0 | 0 | 18744.64 | 0 | 0 | 0 | 0 | 0 | 18744.64
2022031016 | 5 | 0.4962 | 39696 | 0.19481 | 7013.16 | 0.85921 | 10310.52 | 1 | 5000 | 7013.16 | 10310.52 | 0 | 0 | 0 | 0 | 17372.32 | 0 | 0 | 0 | 0 | 0 | 17372.32
2022031017 | 5 | 0.50152 | 40121.6 | 0.24127 | 8685.72 | 0.82561 | 9907.32 | 1 | 5000 | 8685.72 | 9907.32 | 0 | 0 | 0 | 0 | 16528.56 | 0 | 0 | 0 | 0 | 0 | 16528.56
2022031018 | 5 | 0.50583 | 40466.4 | 0.31135 | 11208.6 | 0.53783 | 6453.96 | 1 | 5000 | 11208.6 | 6453.96 | 0 | 0 | 0 | 0 | 17803.84 | 0 | 0 | 0 | 0 | 0 | 17803.84
2022031019 | 5 | 0.5172 | 41376 | 0.43306 | 15590.16 | 0.08305 | 996.6 | 1 | 5000 | 15590.16 | 996.6 | 0 | 0 | 0 | 0 | 19789.24 | 0 | 0 | 0 | 0 | 0 | 19789.24
2022031020 | 5 | 0.5315 | 42520 | 0.49196 | 17710.56 | 0 | 0 | 1 | 5000 | 17710.56 | 0 | 0 | 0 | 0 | 0 | 19809.44 | 0 | 0 | 0 | 0 | 0 | 19809.44
2022031021 | 5 | 0.52845 | 42276 | 0.50396 | 18142.56 | 0 | 0 | 1 | 5000 | 18142.56 | 0 | 0 | 0 | 0 | 0 | 19133.44 | 0 | 0 | 0 | 0 | 0 | 19133.44
2022031022 | 5 | 0.51722 | 41377.6 | 0.51279 | 18460.44 | 0 | 0 | 1 | 5000 | 18460.44 | 0 | 0 | 0 | 0 | 0 | 17917.16 | 0 | 0 | 0 | 0 | 0 | 17917.16
2022031023 | 5 | 0.49707 | 39765.6 | 0.51703 | 18613.08 | 0 | 0 | 1 | 5000 | 18613.08 | 0 | 0 | 0 | 0 | 0 | 16152.52 | 0 | 0 | 0 | 0 | 0 | 16152.52
2022031024 | 5 | 0.47648 | 38118.4 | 0.52142 | 18771.12 | 0 | 0 | 1 | 5000 | 18771.12 | 0 | 0 | 0 | 0 | 0 | 14347.28 | 0 | 0 | 0 | 0 | 0 | 14347.28
2022031101 | 6 | 0.46239 | 36991.2 | 0.52009 | 18723.24 | 0 | 0 | 1 | 5000 | 18723.24 | 0 | 0 | 0 | 0 | 0 | 13267.96 | 0 | 0 | 0 | 0 | 0 | 13267.96
2022031102 | 6 | 0.45856 | 36684.8 | 0.54613 | 19660.68 | 0 | 0 | 1 | 5000 | 19660.68 | 0 | 0 | 0 | 0 | 0 | 12024.12 | 0 | 0 | 0 | 0 | 0 | 12024.12
2022031103 | 6 | 0.46238 | 36990.4 | 0.55803 | 20089.08 | 0 | 0 | 1 | 5000 | 20089.08 | 0 | 0 | 0 | 0 | 0 | 11901.32 | 0 | 0 | 0 | 0 | 0 | 11901.32
2022031104 | 6 | 0.47088 | 37670.4 | 0.56638 | 20389.68 | 0 | 0 | 1 | 5000 | 20389.68 | 0 | 0 | 0 | 0 | 0 | 12280.72 | 0 | 0 | 0 | 0 | 0 | 12280.72
2022031105 | 6 | 0.48894 | 39115.2 | 0.57427 | 20673.72 | 0 | 0 | 1 | 5000 | 20673.72 | 0 | 0 | 0 | 0 | 0 | 13441.48 | 0 | 0 | 0 | 0 | 0 | 13441.48
2022031106 | 6 | 0.52109 | 41687.2 | 0.58511 | 21063.96 | 0 | 0 | 1 | 5000 | 21063.96 | 0 | 0 | 0 | 0 | 0 | 15623.24 | 0 | 0 | 0 | 0 | 0 | 15623.24
2022031107 | 6 | 0.56885 | 45508 | 0.58816 | 21173.76 | 0.00013 | 1.56 | 1 | 5000 | 21173.76 | 1.56 | 0 | 0 | 0 | 0 | 19332.68 | 0 | 0 | 0 | 0 | 0 | 19332.68
2022031108 | 6 | 0.59363 | 47490.4 | 0.5779 | 20804.4 | 0.02259 | 271.08 | 1 | 5000 | 20804.4 | 271.08 | 0 | 0 | 0 | 0 | 21414.92 | 0 | 0 | 0 | 0 | 0 | 21414.92
2022031109 | 6 | 0.61026 | 48820.8 | 0.55473 | 19970.28 | 0.09864 | 1183.68 | 1 | 5000 | 19970.28 | 1183.68 | 0 | 0 | 0 | 0 | 22666.84 | 0 | 0 | 0 | 0 | 0 | 22666.84
2022031110 | 6 | 0.62521 | 50016.8 | 0.53383 | 19217.88 | 0.20709 | 2485.08 | 1 | 5000 | 19217.88 | 2485.08 | 0 | 0 | 0 | 0 | 23313.84 | 0 | 0 | 0 | 0 | 0 | 23313.84
2022031111 | 6 | 0.63451 | 50760.8 | 0.52538 | 18913.68 | 0.25365 | 3043.8 | 1 | 5000 | 18913.68 | 3043.8 | 0 | 0 | 0 | 0 | 23803.32 | 0 | 0 | 0 | 0 | 0 | 23803.32
2022031112 | 6 | 0.64017 | 51213.6 | 0.53019 | 19086.84 | 0.29184 | 3502.08 | 1 | 5000 | 19086.84 | 3502.08 | 0 | 0 | 0 | 0 | 23624.68 | 0 | 0 | 0 | 0 | 0 | 23624.68
2022031113 | 6 | 0.64267 | 51413.6 | 0.56463 | 20326.68 | 0.26331 | 3159.72 | 1 | 5000 | 20326.68 | 3159.72 | 0 | 0 | 0 | 0 | 22927.2 | 0 | 0 | 0 | 0 | 0 | 22927.2
2022031114 | 6 | 0.64649 | 51719.2 | 0.59379 | 21376.44 | 0.26258 | 3150.96 | 1 | 5000 | 21376.44 | 3150.96 | 0 | 0 | 0 | 0 | 22191.8 | 0 | 0 | 0 | 0 | 0 | 22191.8
2022031115 | 6 | 0.64562 | 51649.6 | 0.61712 | 22216.32 | 0.33662 | 4039.44 | 1 | 5000 | 22216.32 | 4039.44 | 0 | 0 | 0 | 0 | 20393.84 | 0 | 0 | 0 | 0 | 0 | 20393.84
2022031116 | 6 | 0.64232 | 51385.6 | 0.61959 | 22305.24 | 0.36958 | 4434.96 | 1 | 5000 | 22305.24 | 4434.96 | 0 | 0 | 0 | 0 | 19645.4 | 0 | 0 | 0 | 0 | 0 | 19645.4
2022031117 | 6 | 0.64437 | 51549.6 | 0.58591 | 21092.76 | 0.41179 | 4941.48 | 1 | 5000 | 21092.76 | 4941.48 | 0 | 0 | 0 | 0 | 20515.36 | 0 | 0 | 0 | 0 | 0 | 20515.36
2022031118 | 6 | 0.64957 | 51965.6 | 0.511 | 18396 | 0.42351 | 5082.12 | 1 | 5000 | 18396 | 5082.12 | 0 | 0 | 0 | 0 | 23487.48 | 0 | 0 | 0 | 0 | 0 | 23487.48
2022031119 | 6 | 0.66566 | 53252.8 | 0.41237 | 14845.32 | 0.0877 | 1052.4 | 1 | 5000 | 14845.32 | 1052.4 | 0 | 0 | 0 | 0 | 32355.08 | 0 | 0 | 0 | 0 | 0 | 32355.08
2022031120 | 6 | 0.6805 | 54440 | 0.35189 | 12668.04 | 0.00014 | 1.68 | 1 | 5000 | 12668.04 | 1.68 | 0 | 0 | 0 | 0 | 36770.28 | 0 | 0 | 0 | 0 | 0 | 36770.28
2022031121 | 6 | 0.67881 | 54304.8 | 0.34061 | 12261.96 | 0 | 0 | 1 | 5000 | 12261.96 | 0 | 0 | 0 | 0 | 0 | 37042.84 | 0 | 0 | 0 | 0 | 0 | 37042.84
2022031122 | 6 | 0.67327 | 53861.6 | 0.31626 | 11385.36 | 0 | 0 | 1 | 5000 | 11385.36 | 0 | 0 | 0 | 0 | 0 | 37476.24 | 0 | 0 | 0 | 0 | 0 | 37476.24
2022031123 | 6 | 0.66026 | 52820.8 | 0.29712 | 10696.32 | 0 | 0 | 1 | 5000 | 10696.32 | 0 | 0 | 0 | 0 | 0 | 37124.48 | 0 | 0 | 0 | 0 | 0 | 37124.48
2022031124 | 6 | 0.64638 | 51710.4 | 0.26548 | 9557.28 | 0 | 0 | 1 | 5000 | 9557.28 | 0 | 0 | 0 | 0 | 0 | 37153.12 | 0 | 0 | 0 | 0 | 0 | 37153.12
2022031201 | 7 | 0.63757 | 51005.6 | 0.23948 | 8621.28 | 0 | 0 | 1 | 5000 | 8621.28 | 0 | 0 | 0 | 0 | 0 | 37384.32 | 0 | 0 | 0 | 0 | 0 | 37384.32
2022031202 | 7 | 0.63475 | 50780 | 0.22912 | 8248.32 | 0 | 0 | 1 | 5000 | 8248.32 | 0 | 0 | 0 | 0 | 0 | 37531.68 | 0 | 0 | 0 | 0 | 0 | 37531.68
2022031203 | 7 | 0.63662 | 50929.6 | 0.23473 | 8450.28 | 0 | 0 | 1 | 5000 | 8450.28 | 0 | 0 | 0 | 0 | 0 | 37479.32 | 0 | 0 | 0 | 0 | 0 | 37479.32
2022031204 | 7 | 0.64209 | 51367.2 | 0.26439 | 9518.04 | 0 | 0 | 1 | 5000 | 9518.04 | 0 | 0 | 0 | 0 | 0 | 36849.16 | 0 | 0 | 0 | 0 | 0 | 36849.16
2022031205 | 7 | 0.65422 | 52337.6 | 0.28154 | 10135.44 | 0 | 0 | 1 | 5000 | 10135.44 | 0 | 0 | 0 | 0 | 0 | 37202.16 | 0 | 0 | 0 | 0 | 0 | 37202.16
2022031206 | 7 | 0.67367 | 53893.6 | 0.31864 | 11471.04 | 0 | 0 | 1 | 5000 | 11471.04 | 0 | 0 | 0 | 0 | 0 | 37422.56 | 0 | 0 | 0 | 0 | 0 | 37422.56
2022031207 | 7 | 0.69936 | 55948.8 | 0.36972 | 13309.92 | 0.00139 | 16.68 | 1 | 5000 | 13309.92 | 16.68 | 0 | 0 | 0 | 0 | 37622.2 | 0 | 0 | 0 | 0 | 0 | 37622.2
2022031208 | 7 | 0.70653 | 56522.4 | 0.40119 | 14442.84 | 0.17235 | 2068.2 | 1 | 5000 | 14442.84 | 2068.2 | 0 | 0 | 0 | 0 | 35011.36 | 0 | 0 | 0 | 0 | 0 | 35011.36
2022031209 | 7 | 0.68425 | 54740 | 0.36085 | 12990.6 | 0.72447 | 8693.64 | 1 | 5000 | 12990.6 | 8693.64 | 0 | 0 | 0 | 0 | 28055.76 | 0 | 0 | 0 | 0 | 0 | 28055.76
2022031210 | 7 | 0.65255 | 52204 | 0.35145 | 12652.2 | 0.8823 | 10587.6 | 1 | 5000 | 12652.2 | 10587.6 | 0 | 0 | 0 | 0 | 23964.2 | 0 | 0 | 0 | 0 | 0 | 23964.2
2022031211 | 7 | 0.61798 | 49438.4 | 0.33737 | 12145.32 | 0.89085 | 10690.2 | 1 | 5000 | 12145.32 | 10690.2 | 0 | 0 | 0 | 0 | 21602.88 | 0 | 0 | 0 | 0 | 0 | 21602.88
2022031212 | 7 | 0.58364 | 46691.2 | 0.31607 | 11378.52 | 0.88779 | 10653.48 | 1 | 5000 | 11378.52 | 10653.48 | 0 | 0 | 0 | 0 | 19659.2 | 0 | 0 | 0 | 0 | 0 | 19659.2
2022031213 | 7 | 0.55309 | 44247.2 | 0.33296 | 11986.56 | 0.85694 | 10283.28 | 1 | 5000 | 11986.56 | 10283.28 | 0 | 0 | 0 | 0 | 16977.36 | 0 | 0 | 0 | 0 | 0 | 16977.36
2022031214 | 7 | 0.52598 | 42078.4 | 0.35748 | 12869.28 | 0.81461 | 9775.32 | 1 | 5000 | 12869.28 | 9775.32 | 0 | 0 | 0 | 0 | 14433.8 | 0 | 0 | 0 | 0 | 0 | 14433.8
2022031215 | 7 | 0.50369 | 40295.2 | 0.3715 | 13374 | 0.72366 | 8683.92 | 1 | 5000 | 13374 | 8683.92 | 0 | 0 | 0 | 0 | 13237.28 | 0 | 0 | 0 | 0 | 0 | 13237.28
2022031216 | 7 | 0.49077 | 39261.6 | 0.37906 | 13646.16 | 0.63556 | 7626.72 | 1 | 5000 | 13646.16 | 7626.72 | 0 | 0 | 0 | 0 | 12988.72 | 0 | 0 | 0 | 0 | 0 | 12988.72
2022031217 | 7 | 0.48918 | 39134.4 | 0.36632 | 13187.52 | 0.64564 | 7747.68 | 1 | 5000 | 13187.52 | 7747.68 | 0 | 0 | 0 | 0 | 13199.2 | 0 | 0 | 0 | 0 | 0 | 13199.2
2022031218 | 7 | 0.49616 | 39692.8 | 0.39044 | 14055.84 | 0.52446 | 6293.52 | 1 | 5000 | 14055.84 | 6293.52 | 0 | 0 | 0 | 0 | 14343.44 | 0 | 0 | 0 | 0 | 0 | 14343.44
2022031219 | 7 | 0.51596 | 41276.8 | 0.39476 | 14211.36 | 0.10228 | 1227.36 | 1 | 5000 | 14211.36 | 1227.36 | 0 | 0 | 0 | 0 | 20838.08 | 0 | 0 | 0 | 0 | 0 | 20838.08
2022031220 | 7 | 0.54483 | 43586.4 | 0.49975 | 17991 | 0 | 0 | 1 | 5000 | 17991 | 0 | 0 | 0 | 0 | 0 | 20595.4 | 0 | 0 | 0 | 0 | 0 | 20595.4
2022031221 | 7 | 0.55966 | 44772.8 | 0.62469 | 22488.84 | 0 | 0 | 1 | 5000 | 22488.84 | 0 | 0 | 0 | 0 | 0 | 17283.96 | 0 | 0 | 0 | 0 | 0 | 17283.96
2022031222 | 7 | 0.56594 | 45275.2 | 0.63334 | 22800.24 | 0 | 0 | 1 | 5000 | 22800.24 | 0 | 0 | 0 | 0 | 0 | 17474.96 | 0 | 0 | 0 | 0 | 0 | 17474.96
2022031223 | 7 | 0.56224 | 44979.2 | 0.63435 | 22836.6 | 0 | 0 | 1 | 5000 | 22836.6 | 0 | 0 | 0 | 0 | 0 | 17142.6 | 0 | 0 | 0 | 0 | 0 | 17142.6
2022031224 | 7 | 0.55712 | 44569.6 | 0.63348 | 22805.28 | 0 | 0 | 1 | 5000 | 22805.28 | 0 | 0 | 0 | 0 | 0 | 16764.32 | 0 | 0 | 0 | 0 | 0 | 16764.32
2022031301 | 1 | 0.55332 | 44265.6 | 0.61975 | 22311 | 0 | 0 | 1 | 5000 | 22311 | 0 | 0 | 0 | 0 | 0 | 16954.6 | 0 | 0 | 0 | 0 | 0 | 16954.6
2022031303 | 1 | 0.552 | 44160 | 0.61296 | 22066.56 | 0 | 0 | 1 | 5000 | 22066.56 | 0 | 0 | 0 | 0 | 0 | 17093.44 | 0 | 0 | 0 | 0 | 0 | 17093.44
2022031304 | 1 | 0.55724 | 44579.2 | 0.61275 | 22059 | 0 | 0 | 1 | 5000 | 22059 | 0 | 0 | 0 | 0 | 0 | 17520.2 | 0 | 0 | 0 | 0 | 0 | 17520.2
2022031305 | 1 | 0.56709 | 45367.2 | 0.61263 | 22054.68 | 0 | 0 | 1 | 5000 | 22054.68 | 0 | 0 | 0 | 0 | 0 | 18312.52 | 0 | 0 | 0 | 0 | 0 | 18312.52
2022031306 | 1 | 0.57936 | 46348.8 | 0.60294 | 21705.84 | 0 | 0 | 1 | 5000 | 21705.84 | 0 | 0 | 0 | 0 | 0 | 19642.96 | 0 | 0 | 0 | 0 | 0 | 19642.96
2022031307 | 1 | 0.59655 | 47724 | 0.59713 | 21496.68 | 0 | 0 | 1 | 5000 | 21496.68 | 0 | 0 | 0 | 0 | 0 | 21227.32 | 0 | 0 | 0 | 0 | 0 | 21227.32
2022031308 | 1 | 0.61756 | 49404.8 | 0.59706 | 21494.16 | 0.0015 | 18 | 1 | 5000 | 21494.16 | 18 | 0 | 0 | 0 | 0 | 22892.64 | 0 | 0 | 0 | 0 | 0 | 22892.64
2022031309 | 1 | 0.61948 | 49558.4 | 0.57296 | 20626.56 | 0.12372 | 1484.64 | 1 | 5000 | 20626.56 | 1484.64 | 0 | 0 | 0 | 0 | 22447.2 | 0 | 0 | 0 | 0 | 0 | 22447.2
2022031310 | 1 | 0.59725 | 47780 | 0.50472 | 18169.92 | 0.39805 | 4776.6 | 1 | 5000 | 18169.92 | 4776.6 | 0 | 0 | 0 | 0 | 19833.48 | 0 | 0 | 0 | 0 | 0 | 19833.48
2022031311 | 1 | 0.57102 | 45681.6 | 0.57348 | 20645.28 | 0.41531 | 4983.72 | 1 | 5000 | 20645.28 | 4983.72 | 0 | 0 | 0 | 0 | 15052.6 | 0 | 0 | 0 | 0 | 0 | 15052.6
2022031312 | 1 | 0.54598 | 43678.4 | 0.62316 | 22433.76 | 0.3708 | 4449.6 | 1 | 5000 | 22433.76 | 4449.6 | 0 | 0 | 0 | 0 | 11795.04 | 0 | 0 | 0 | 0 | 0 | 11795.04
2022031313 | 1 | 0.5233 | 41864 | 0.62973 | 22670.28 | 0.35308 | 4236.96 | 1 | 5000 | 22670.28 | 4236.96 | 0 | 0 | 0 | 0 | 9956.76 | 0 | 0 | 0 | 0 | 0 | 9956.76
2022031314 | 1 | 0.5037 | 40296 | 0.62619 | 22542.84 | 0.34816 | 4177.92 | 1 | 5000 | 22542.84 | 4177.92 | 0 | 0 | 0 | 0 | 8575.24 | 0 | 0 | 0 | 0 | 0 | 8575.24
2022031315 | 1 | 0.48811 | 39048.8 | 0.63012 | 22684.32 | 0.29838 | 3580.56 | 1 | 5000 | 22684.32 | 3580.56 | 0 | 0 | 0 | 0 | 7783.92 | 0 | 0 | 0 | 0 | 0 | 7783.92
2022031316 | 1 | 0.47927 | 38341.6 | 0.63668 | 22920.48 | 0.24958 | 2994.96 | 1 | 5000 | 22920.48 | 2994.96 | 0 | 0 | 0 | 0 | 7426.16 | 0 | 0 | 0 | 0 | 0 | 7426.16
2022031317 | 1 | 0.47576 | 38060.8 | 0.64293 | 23145.48 | 0.2006 | 2407.2 | 1 | 5000 | 23145.48 | 2407.2 | 0 | 0 | 0 | 0 | 7508.12 | 0 | 0 | 0 | 0 | 0 | 7508.12
2022031318 | 1 | 0.47991 | 38392.8 | 0.65229 | 23482.44 | 0.1649 | 1978.8 | 1 | 5000 | 23482.44 | 1978.8 | 0 | 0 | 0 | 0 | 7931.56 | 0 | 0 | 0 | 0 | 0 | 7931.56
2022031319 | 1 | 0.48709 | 38967.2 | 0.65121 | 23443.56 | 0.09476 | 1137.12 | 1 | 5000 | 23443.56 | 1137.12 | 0 | 0 | 0 | 0 | 9386.52 | 0 | 0 | 0 | 0 | 0 | 9386.52
2022031320 | 1 | 0.50324 | 40259.2 | 0.63817 | 22974.12 | 0.01805 | 216.6 | 1 | 5000 | 22974.12 | 216.6 | 0 | 0 | 0 | 0 | 12068.48 | 0 | 0 | 0 | 0 | 0 | 12068.48
2022031321 | 1 | 0.5209 | 41672 | 0.64113 | 23080.68 | 0 | 0 | 1 | 5000 | 23080.68 | 0 | 0 | 0 | 0 | 0 | 13591.32 | 0 | 0 | 0 | 0 | 0 | 13591.32
2022031322 | 1 | 0.51633 | 41306.4 | 0.64535 | 23232.6 | 0 | 0 | 1 | 5000 | 23232.6 | 0 | 0 | 0 | 0 | 0 | 13073.8 | 0 | 0 | 0 | 0 | 0 | 13073.8
2022031323 | 1 | 0.5011 | 40088 | 0.64949 | 23381.64 | 0 | 0 | 1 | 5000 | 23381.64 | 0 | 0 | 0 | 0 | 0 | 11706.36 | 0 | 0 | 0 | 0 | 0 | 11706.36
2022031324 | 1 | 0.48092 | 38473.6 | 0.64442 | 23199.12 | 0 | 0 | 1 | 5000 | 23199.12 | 0 | 0 | 0 | 0 | 0 | 10274.48 | 0 | 0 | 0 | 0 | 0 | 10274.48
2022031401 | 2 | 0.46536 | 37228.8 | 0.65104 | 23437.44 | 0 | 0 | 1 | 5000 | 23437.44 | 0 | 0 | 0 | 0 | 0 | 8791.36 | 0 | 0 | 0 | 0 | 0 | 8791.36
2022031402 | 2 | 0.45565 | 36452 | 0.64367 | 23172.12 | 0 | 0 | 1 | 5000 | 23172.12 | 0 | 0 | 0 | 0 | 0 | 8279.88 | 0 | 0 | 0 | 0 | 0 | 8279.88
2022031403 | 2 | 0.45219 | 36175.2 | 0.63539 | 22874.04 | 0 | 0 | 1 | 5000 | 22874.04 | 0 | 0 | 0 | 0 | 0 | 8301.16 | 0 | 0 | 0 | 0 | 0 | 8301.16
2022031404 | 2 | 0.45348 | 36278.4 | 0.6249 | 22496.4 | 0 | 0 | 1 | 5000 | 22496.4 | 0 | 0 | 0 | 0 | 0 | 8782 | 0 | 0 | 0 | 0 | 0 | 8782
2022031405 | 2 | 0.4624 | 36992 | 0.61839 | 22262.04 | 0 | 0 | 1 | 5000 | 22262.04 | 0 | 0 | 0 | 0 | 0 | 9729.96 | 0 | 0 | 0 | 0 | 0 | 9729.96
2022031406 | 2 | 0.48307 | 38645.6 | 0.62127 | 22365.72 | 0 | 0 | 1 | 5000 | 22365.72 | 0 | 0 | 0 | 0 | 0 | 11279.88 | 0 | 0 | 0 | 0 | 0 | 11279.88
2022031407 | 2 | 0.51609 | 41287.2 | 0.62523 | 22508.28 | 0 | 0 | 1 | 5000 | 22508.28 | 0 | 0 | 0 | 0 | 0 | 13778.92 | 0 | 0 | 0 | 0 | 0 | 13778.92
2022031408 | 2 | 0.53917 | 43133.6 | 0.62677 | 22563.72 | 0.0006 | 7.2 | 1 | 5000 | 22563.72 | 7.2 | 0 | 0 | 0 | 0 | 15562.68 | 0 | 0 | 0 | 0 | 0 | 15562.68
2022031409 | 2 | 0.54368 | 43494.4 | 0.59778 | 21520.08 | 0.12176 | 1461.12 | 1 | 5000 | 21520.08 | 1461.12 | 0 | 0 | 0 | 0 | 15513.2 | 0 | 0 | 0 | 0 | 0 | 15513.2
2022031410 | 2 | 0.54136 | 43308.8 | 0.52103 | 18757.08 | 0.38013 | 4561.56 | 1 | 5000 | 18757.08 | 4561.56 | 0 | 0 | 0 | 0 | 14990.16 | 0 | 0 | 0 | 0 | 0 | 14990.16
2022031411 | 2 | 0.53608 | 42886.4 | 0.53614 | 19301.04 | 0.42105 | 5052.6 | 1 | 5000 | 19301.04 | 5052.6 | 0 | 0 | 0 | 0 | 13532.76 | 0 | 0 | 0 | 0 | 0 | 13532.76
2022031412 | 2 | 0.53078 | 42462.4 | 0.55342 | 19923.12 | 0.44664 | 5359.68 | 1 | 5000 | 19923.12 | 5359.68 | 0 | 0 | 0 | 0 | 12179.6 | 0 | 0 | 0 | 0 | 0 | 12179.6
2022031413 | 2 | 0.52466 | 41972.8 | 0.54997 | 19798.92 | 0.48684 | 5842.08 | 1 | 5000 | 19798.92 | 5842.08 | 0 | 0 | 0 | 0 | 11331.8 | 0 | 0 | 0 | 0 | 0 | 11331.8
2022031414 | 2 | 0.52187 | 41749.6 | 0.5691 | 20487.6 | 0.40834 | 4900.08 | 1 | 5000 | 20487.6 | 4900.08 | 0 | 0 | 0 | 0 | 11361.92 | 0 | 0 | 0 | 0 | 0 | 11361.92
2022031415 | 2 | 0.51869 | 41495.2 | 0.5714 | 20570.4 | 0.40603 | 4872.36 | 1 | 5000 | 20570.4 | 4872.36 | 0 | 0 | 0 | 0 | 11052.44 | 0 | 0 | 0 | 0 | 0 | 11052.44
2022031416 | 2 | 0.5192 | 41536 | 0.57854 | 20827.44 | 0.35188 | 4222.56 | 1 | 5000 | 20827.44 | 4222.56 | 0 | 0 | 0 | 0 | 11486 | 0 | 0 | 0 | 0 | 0 | 11486
2022031417 | 2 | 0.52356 | 41884.8 | 0.57829 | 20818.44 | 0.35716 | 4285.92 | 1 | 5000 | 20818.44 | 4285.92 | 0 | 0 | 0 | 0 | 11780.44 | 0 | 0 | 0 | 0 | 0 | 11780.44
2022031418 | 2 | 0.52889 | 42311.2 | 0.57999 | 20879.64 | 0.28211 | 3385.32 | 1 | 5000 | 20879.64 | 3385.32 | 0 | 0 | 0 | 0 | 13046.24 | 0 | 0 | 0 | 0 | 0 | 13046.24
2022031419 | 2 | 0.53122 | 42497.6 | 0.59368 | 21372.48 | 0.17763 | 2131.56 | 1 | 5000 | 21372.48 | 2131.56 | 0 | 0 | 0 | 0 | 13993.56 | 0 | 0 | 0 | 0 | 0 | 13993.56
2022031420 | 2 | 0.53254 | 42603.2 | 0.61065 | 21983.4 | 0.03925 | 471 | 1 | 5000 | 21983.4 | 471 | 0 | 0 | 0 | 0 | 15148.8 | 0 | 0 | 0 | 0 | 0 | 15148.8
2022031421 | 2 | 0.53374 | 42699.2 | 0.57716 | 20777.76 | 0 | 0 | 1 | 5000 | 20777.76 | 0 | 0 | 0 | 0 | 0 | 16921.44 | 0 | 0 | 0 | 0 | 0 | 16921.44
2022031422 | 2 | 0.51975 | 41580 | 0.58974 | 21230.64 | 0 | 0 | 1 | 5000 | 21230.64 | 0 | 0 | 0 | 0 | 0 | 15349.36 | 0 | 0 | 0 | 0 | 0 | 15349.36
2022031423 | 2 | 0.49508 | 39606.4 | 0.55442 | 19959.12 | 0 | 0 | 1 | 5000 | 19959.12 | 0 | 0 | 0 | 0 | 0 | 14647.28 | 0 | 0 | 0 | 0 | 0 | 14647.28
2022031424 | 2 | 0.46763 | 37410.4 | 0.49132 | 17687.52 | 0 | 0 | 1 | 5000 | 17687.52 | 0 | 0 | 0 | 0 | 0 | 14722.88 | 0 | 0 | 0 | 0 | 0 | 14722.88
2022031501 | 3 | 0.44534 | 35627.2 | 0.4201 | 15123.6 | 0 | 0 | 1 | 5000 | 15123.6 | 0 | 0 | 0 | 0 | 0 | 15503.6 | 0 | 0 | 0 | 0 | 0 | 15503.6
2022031502 | 3 | 0.42914 | 34331.2 | 0.37998 | 13679.28 | 0 | 0 | 1 | 5000 | 13679.28 | 0 | 0 | 0 | 0 | 0 | 15651.92 | 0 | 0 | 0 | 0 | 0 | 15651.92
2022031503 | 3 | 0.42048 | 33638.4 | 0.34444 | 12399.84 | 0 | 0 | 1 | 5000 | 12399.84 | 0 | 0 | 0 | 0 | 0 | 16238.56 | 0 | 0 | 0 | 0 | 0 | 16238.56
2022031504 | 3 | 0.41783 | 33426.4 | 0.36509 | 13143.24 | 0 | 0 | 1 | 5000 | 13143.24 | 0 | 0 | 0 | 0 | 0 | 15283.16 | 0 | 0 | 0 | 0 | 0 | 15283.16
2022031505 | 3 | 0.42714 | 34171.2 | 0.40931 | 14735.16 | 0 | 0 | 1 | 5000 | 14735.16 | 0 | 0 | 0 | 0 | 0 | 14436.04 | 0 | 0 | 0 | 0 | 0 | 14436.04
2022031506 | 3 | 0.44963 | 35970.4 | 0.43344 | 15603.84 | 0 | 0 | 1 | 5000 | 15603.84 | 0 | 0 | 0 | 0 | 0 | 15366.56 | 0 | 0 | 0 | 0 | 0 | 15366.56
2022031507 | 3 | 0.48422 | 38737.6 | 0.45451 | 16362.36 | 0 | 0 | 1 | 5000 | 16362.36 | 0 | 0 | 0 | 0 | 0 | 17375.24 | 0 | 0 | 0 | 0 | 0 | 17375.24
2022031508 | 3 | 0.5114 | 40912 | 0.46385 | 16698.6 | 0.00117 | 14.04 | 1 | 5000 | 16698.6 | 14.04 | 0 | 0 | 0 | 0 | 19199.36 | 0 | 0 | 0 | 0 | 0 | 19199.36
2022031509 | 3 | 0.51969 | 41575.2 | 0.46463 | 16726.68 | 0.1669 | 2002.8 | 1 | 5000 | 16726.68 | 2002.8 | 0 | 0 | 0 | 0 | 17845.72 | 0 | 0 | 0 | 0 | 0 | 17845.72
2022031510 | 3 | 0.51744 | 41395.2 | 0.36751 | 13230.36 | 0.65249 | 7829.88 | 1 | 5000 | 13230.36 | 7829.88 | 0 | 0 | 0 | 0 | 15334.96 | 0 | 0 | 0 | 0 | 0 | 15334.96
2022031511 | 3 | 0.51351 | 41080.8 | 0.34253 | 12331.08 | 0.81132 | 9735.84 | 1 | 5000 | 12331.08 | 9735.84 | 0 | 0 | 0 | 0 | 14013.88 | 0 | 0 | 0 | 0 | 0 | 14013.88
2022031512 | 3 | 0.50714 | 40571.2 | 0.30305 | 10909.8 | 0.82028 | 9843.36 | 1 | 5000 | 10909.8 | 9843.36 | 0 | 0 | 0 | 0 | 14818.04 | 0 | 0 | 0 | 0 | 0 | 14818.04
2022031513 | 3 | 0.50021 | 40016.8 | 0.24803 | 8929.08 | 0.84362 | 10123.44 | 1 | 5000 | 8929.08 | 10123.44 | 0 | 0 | 0 | 0 | 15964.28 | 0 | 0 | 0 | 0 | 0 | 15964.28
2022031514 | 3 | 0.49871 | 39896.8 | 0.21623 | 7784.28 | 0.84155 | 10098.6 | 1 | 5000 | 7784.28 | 10098.6 | 0 | 0 | 0 | 0 | 17013.92 | 0 | 0 | 0 | 0 | 0 | 17013.92
2022031515 | 3 | 0.49984 | 39987.2 | 0.20612 | 7420.32 | 0.83135 | 9976.2 | 1 | 5000 | 7420.32 | 9976.2 | 0 | 0 | 0 | 0 | 17590.68 | 0 | 0 | 0 | 0 | 0 | 17590.68
2022031516 | 3 | 0.50199 | 40159.2 | 0.18468 | 6648.48 | 0.83908 | 10068.96 | 1 | 5000 | 6648.48 | 10068.96 | 0 | 0 | 0 | 0 | 18441.76 | 0 | 0 | 0 | 0 | 0 | 18441.76
2022031517 | 3 | 0.50651 | 40520.8 | 0.16836 | 6060.96 | 0.82874 | 9944.88 | 1 | 5000 | 6060.96 | 9944.88 | 0 | 0 | 0 | 0 | 19514.96 | 0 | 0 | 0 | 0 | 0 | 19514.96
2022031518 | 3 | 0.51001 | 40800.8 | 0.13637 | 4909.32 | 0.82478 | 9897.36 | 1 | 5000 | 4909.32 | 9897.36 | 0 | 0 | 0 | 0 | 20994.12 | 0 | 0 | 0 | 0 | 0 | 20994.12
2022031519 | 3 | 0.51137 | 40909.6 | 0.10433 | 3755.88 | 0.60133 | 7215.96 | 1 | 5000 | 3755.88 | 7215.96 | 0 | 0 | 0 | 0 | 24937.76 | 0 | 0 | 0 | 0 | 0 | 24937.76
2022031520 | 3 | 0.51338 | 41070.4 | 0.07996 | 2878.56 | 0.10795 | 1295.4 | 1 | 5000 | 2878.56 | 1295.4 | 0 | 0 | 0 | 0 | 31896.44 | 0 | 0 | 0 | 0 | 0 | 31896.44
2022031521 | 3 | 0.51796 | 41436.8 | 0.10264 | 3695.04 | 0 | 0 | 1 | 5000 | 3695.04 | 0 | 0 | 0 | 0 | 0 | 32741.76 | 0 | 0 | 0 | 0 | 0 | 32741.76
2022031522 | 3 | 0.50579 | 40463.2 | 0.15805 | 5689.8 | 0 | 0 | 1 | 5000 | 5689.8 | 0 | 0 | 0 | 0 | 0 | 29773.4 | 0 | 0 | 0 | 0 | 0 | 29773.4
2022031523 | 3 | 0.48147 | 38517.6 | 0.21798 | 7847.28 | 0 | 0 | 1 | 5000 | 7847.28 | 0 | 0 | 0 | 0 | 0 | 25670.32 | 0 | 0 | 0 | 0 | 0 | 25670.32
2022031524 | 3 | 0.45513 | 36410.4 | 0.28315 | 10193.4 | 0 | 0 | 1 | 5000 | 10193.4 | 0 | 0 | 0 | 0 | 0 | 21217 | 0 | 0 | 0 | 0 | 0 | 21217
2022031601 | 4 | 0.43518 | 34814.4 | 0.36698 | 13211.28 | 0 | 0 | 1 | 5000 | 13211.28 | 0 | 0 | 0 | 0 | 0 | 16603.12 | 0 | 0 | 0 | 0 | 0 | 16603.12
2022031602 | 4 | 0.42435 | 33948 | 0.4417 | 15901.2 | 0 | 0 | 1 | 5000 | 15901.2 | 0 | 0 | 0 | 0 | 0 | 13046.8 | 0 | 0 | 0 | 0 | 0 | 13046.8
2022031603 | 4 | 0.41958 | 33566.4 | 0.48344 | 17403.84 | 0 | 0 | 1 | 5000 | 17403.84 | 0 | 0 | 0 | 0 | 0 | 11162.56 | 0 | 0 | 0 | 0 | 0 | 11162.56
2022031604 | 4 | 0.42094 | 33675.2 | 0.50182 | 18065.52 | 0 | 0 | 1 | 5000 | 18065.52 | 0 | 0 | 0 | 0 | 0 | 10609.68 | 0 | 0 | 0 | 0 | 0 | 10609.68
2022031605 | 4 | 0.43184 | 34547.2 | 0.52038 | 18733.68 | 0 | 0 | 1 | 5000 | 18733.68 | 0 | 0 | 0 | 0 | 0 | 10813.52 | 0 | 0 | 0 | 0 | 0 | 10813.52
2022031606 | 4 | 0.45765 | 36612 | 0.54993 | 19797.48 | 0 | 0 | 1 | 5000 | 19797.48 | 0 | 0 | 0 | 0 | 0 | 11814.52 | 0 | 0 | 0 | 0 | 0 | 11814.52
2022031607 | 4 | 0.49366 | 39492.8 | 0.56557 | 20360.52 | 0 | 0 | 1 | 5000 | 20360.52 | 0 | 0 | 0 | 0 | 0 | 14132.28 | 0 | 0 | 0 | 0 | 0 | 14132.28
2022031608 | 4 | 0.52265 | 41812 | 0.57437 | 20677.32 | 0.00212 | 25.44 | 1 | 5000 | 20677.32 | 25.44 | 0 | 0 | 0 | 0 | 16109.24 | 0 | 0 | 0 | 0 | 0 | 16109.24
2022031609 | 4 | 0.52806 | 42244.8 | 0.54098 | 19475.28 | 0.18233 | 2187.96 | 1 | 5000 | 19475.28 | 2187.96 | 0 | 0 | 0 | 0 | 15581.56 | 0 | 0 | 0 | 0 | 0 | 15581.56
2022031610 | 4 | 0.51504 | 41203.2 | 0.46945 | 16900.2 | 0.45211 | 5425.32 | 1 | 5000 | 16900.2 | 5425.32 | 0 | 0 | 0 | 0 | 13877.68 | 0 | 0 | 0 | 0 | 0 | 13877.68
2022031611 | 4 | 0.50624 | 40499.2 | 0.45029 | 16210.44 | 0.56618 | 6794.16 | 1 | 5000 | 16210.44 | 6794.16 | 0 | 0 | 0 | 0 | 12494.6 | 0 | 0 | 0 | 0 | 0 | 12494.6
2022031612 | 4 | 0.50082 | 40065.6 | 0.46105 | 16597.8 | 0.52703 | 6324.36 | 1 | 5000 | 16597.8 | 6324.36 | 0 | 0 | 0 | 0 | 12143.44 | 0 | 0 | 0 | 0 | 0 | 12143.44
2022031613 | 4 | 0.49926 | 39940.8 | 0.43871 | 15793.56 | 0.57396 | 6887.52 | 1 | 5000 | 15793.56 | 6887.52 | 0 | 0 | 0 | 0 | 12259.72 | 0 | 0 | 0 | 0 | 0 | 12259.72
2022031614 | 4 | 0.50481 | 40384.8 | 0.40587 | 14611.32 | 0.70842 | 8501.04 | 1 | 5000 | 14611.32 | 8501.04 | 0 | 0 | 0 | 0 | 12272.44 | 0 | 0 | 0 | 0 | 0 | 12272.44
2022031615 | 4 | 0.51347 | 41077.6 | 0.38759 | 13953.24 | 0.8058 | 9669.6 | 1 | 5000 | 13953.24 | 9669.6 | 0 | 0 | 0 | 0 | 12454.76 | 0 | 0 | 0 | 0 | 0 | 12454.76
2022031616 | 4 | 0.52446 | 41956.8 | 0.40581 | 14609.16 | 0.81821 | 9818.52 | 1 | 5000 | 14609.16 | 9818.52 | 0 | 0 | 0 | 0 | 12529.12 | 0 | 0 | 0 | 0 | 0 | 12529.12
2022031617 | 4 | 0.53634 | 42907.2 | 0.45628 | 16426.08 | 0.78394 | 9407.28 | 1 | 5000 | 16426.08 | 9407.28 | 0 | 0 | 0 | 0 | 12073.84 | 0 | 0 | 0 | 0 | 0 | 12073.84
2022031618 | 4 | 0.54482 | 43585.6 | 0.50062 | 18022.32 | 0.68596 | 8231.52 | 1 | 5000 | 18022.32 | 8231.52 | 0 | 0 | 0 | 0 | 12331.76 | 0 | 0 | 0 | 0 | 0 | 12331.76
2022031619 | 4 | 0.54245 | 43396 | 0.52507 | 18902.52 | 0.45599 | 5471.88 | 1 | 5000 | 18902.52 | 5471.88 | 0 | 0 | 0 | 0 | 14021.6 | 0 | 0 | 0 | 0 | 0 | 14021.6
2022031620 | 4 | 0.53226 | 42580.8 | 0.51549 | 18557.64 | 0.08875 | 1065 | 1 | 5000 | 18557.64 | 1065 | 0 | 0 | 0 | 0 | 17958.16 | 0 | 0 | 0 | 0 | 0 | 17958.16
2022031621 | 4 | 0.53508 | 42806.4 | 0.57707 | 20774.52 | 0 | 0 | 1 | 5000 | 20774.52 | 0 | 0 | 0 | 0 | 0 | 17031.88 | 0 | 0 | 0 | 0 | 0 | 17031.88
2022031622 | 4 | 0.52059 | 41647.2 | 0.64335 | 23160.6 | 0 | 0 | 1 | 5000 | 23160.6 | 0 | 0 | 0 | 0 | 0 | 13486.6 | 0 | 0 | 0 | 0 | 0 | 13486.6
2022031623 | 4 | 0.49601 | 39680.8 | 0.66015 | 23765.4 | 0 | 0 | 1 | 5000 | 23765.4 | 0 | 0 | 0 | 0 | 0 | 10915.4 | 0 | 0 | 0 | 0 | 0 | 10915.4
2022031624 | 4 | 0.46533 | 37226.4 | 0.63846 | 22984.56 | 0 | 0 | 1 | 5000 | 22984.56 | 0 | 0 | 0 | 0 | 0 | 9241.84 | 0 | 0 | 0 | 0 | 0 | 9241.84
2022031701 | 5 | 0.43998 | 35198.4 | 0.60893 | 21921.48 | 0 | 0 | 1 | 5000 | 21921.48 | 0 | 0 | 0 | 0 | 0 | 8276.92 | 0 | 0 | 0 | 0 | 0 | 8276.92
2022031702 | 5 | 0.42409 | 33927.2 | 0.59422 | 21391.92 | 0 | 0 | 1 | 5000 | 21391.92 | 0 | 0 | 0 | 0 | 0 | 7535.28 | 0 | 0 | 0 | 0 | 0 | 7535.28
2022031703 | 5 | 0.41335 | 33068 | 0.58294 | 20985.84 | 0 | 0 | 1 | 5000 | 20985.84 | 0 | 0 | 0 | 0 | 0 | 7082.16 | 0 | 0 | 0 | 0 | 0 | 7082.16
2022031704 | 5 | 0.41025 | 32820 | 0.58265 | 20975.4 | 0 | 0 | 1 | 5000 | 20975.4 | 0 | 0 | 0 | 0 | 0 | 6844.6 | 0 | 0 | 0 | 0 | 0 | 6844.6
2022031705 | 5 | 0.41576 | 33260.8 | 0.58546 | 21076.56 | 0 | 0 | 1 | 5000 | 21076.56 | 0 | 0 | 0 | 0 | 0 | 7184.24 | 0 | 0 | 0 | 0 | 0 | 7184.24
2022031706 | 5 | 0.43474 | 34779.2 | 0.61451 | 22122.36 | 0 | 0 | 1 | 5000 | 22122.36 | 0 | 0 | 0 | 0 | 0 | 7656.84 | 0 | 0 | 0 | 0 | 0 | 7656.84
2022031707 | 5 | 0.46362 | 37089.6 | 0.64729 | 23302.44 | 0 | 0 | 1 | 5000 | 23302.44 | 0 | 0 | 0 | 0 | 0 | 8787.16 | 0 | 0 | 0 | 0 | 0 | 8787.16
2022031708 | 5 | 0.48708 | 38966.4 | 0.65477 | 23571.72 | 0.00206 | 24.72 | 1 | 5000 | 23571.72 | 24.72 | 0 | 0 | 0 | 0 | 10369.96 | 0 | 0 | 0 | 0 | 0 | 10369.96
2022031709 | 5 | 0.49686 | 39748.8 | 0.63012 | 22684.32 | 0.16365 | 1963.8 | 1 | 5000 | 22684.32 | 1963.8 | 0 | 0 | 0 | 0 | 10100.68 | 0 | 0 | 0 | 0 | 0 | 10100.68
2022031710 | 5 | 0.50389 | 40311.2 | 0.57258 | 20612.88 | 0.4527 | 5432.4 | 1 | 5000 | 20612.88 | 5432.4 | 0 | 0 | 0 | 0 | 9265.92 | 0 | 0 | 0 | 0 | 0 | 9265.92
2022031711 | 5 | 0.51007 | 40805.6 | 0.59707 | 21494.52 | 0.41845 | 5021.4 | 1 | 5000 | 21494.52 | 5021.4 | 0 | 0 | 0 | 0 | 9289.68 | 0 | 0 | 0 | 0 | 0 | 9289.68
2022031712 | 5 | 0.51347 | 41077.6 | 0.61017 | 21966.12 | 0.36908 | 4428.96 | 1 | 5000 | 21966.12 | 4428.96 | 0 | 0 | 0 | 0 | 9682.52 | 0 | 0 | 0 | 0 | 0 | 9682.52
2022031713 | 5 | 0.51888 | 41510.4 | 0.59841 | 21542.76 | 0.35766 | 4291.92 | 1 | 5000 | 21542.76 | 4291.92 | 0 | 0 | 0 | 0 | 10675.72 | 0 | 0 | 0 | 0 | 0 | 10675.72
2022031714 | 5 | 0.52534 | 42027.2 | 0.57883 | 20837.88 | 0.35795 | 4295.4 | 1 | 5000 | 20837.88 | 4295.4 | 0 | 0 | 0 | 0 | 11893.92 | 0 | 0 | 0 | 0 | 0 | 11893.92
2022031715 | 5 | 0.52873 | 42298.4 | 0.58751 | 21150.36 | 0.28643 | 3437.16 | 1 | 5000 | 21150.36 | 3437.16 | 0 | 0 | 0 | 0 | 12710.88 | 0 | 0 | 0 | 0 | 0 | 12710.88
2022031716 | 5 | 0.53162 | 42529.6 | 0.60001 | 21600.36 | 0.25123 | 3014.76 | 1 | 5000 | 21600.36 | 3014.76 | 0 | 0 | 0 | 0 | 12914.48 | 0 | 0 | 0 | 0 | 0 | 12914.48
2022031717 | 5 | 0.5336 | 42688 | 0.59937 | 21577.32 | 0.18631 | 2235.72 | 1 | 5000 | 21577.32 | 2235.72 | 0 | 0 | 0 | 0 | 13874.96 | 0 | 0 | 0 | 0 | 0 | 13874.96
2022031718 | 5 | 0.53565 | 42852 | 0.60263 | 21694.68 | 0.20289 | 2434.68 | 1 | 5000 | 21694.68 | 2434.68 | 0 | 0 | 0 | 0 | 13722.64 | 0 | 0 | 0 | 0 | 0 | 13722.64
2022031719 | 5 | 0.53586 | 42868.8 | 0.61527 | 22149.72 | 0.1539 | 1846.8 | 1 | 5000 | 22149.72 | 1846.8 | 0 | 0 | 0 | 0 | 13872.28 | 0 | 0 | 0 | 0 | 0 | 13872.28
2022031720 | 5 | 0.53496 | 42796.8 | 0.63155 | 22735.8 | 0.02728 | 327.36 | 1 | 5000 | 22735.8 | 327.36 | 0 | 0 | 0 | 0 | 14733.64 | 0 | 0 | 0 | 0 | 0 | 14733.64
2022031721 | 5 | 0.53597 | 42877.6 | 0.65011 | 23403.96 | 0 | 0 | 1 | 5000 | 23403.96 | 0 | 0 | 0 | 0 | 0 | 14473.64 | 0 | 0 | 0 | 0 | 0 | 14473.64
2022031722 | 5 | 0.52521 | 42016.8 | 0.64057 | 23060.52 | 0 | 0 | 1 | 5000 | 23060.52 | 0 | 0 | 0 | 0 | 0 | 13956.28 | 0 | 0 | 0 | 0 | 0 | 13956.28
2022031723 | 5 | 0.50316 | 40252.8 | 0.60414 | 21749.04 | 0 | 0 | 1 | 5000 | 21749.04 | 0 | 0 | 0 | 0 | 0 | 13503.76 | 0 | 0 | 0 | 0 | 0 | 13503.76
2022031724 | 5 | 0.47628 | 38102.4 | 0.57777 | 20799.72 | 0 | 0 | 1 | 5000 | 20799.72 | 0 | 0 | 0 | 0 | 0 | 12302.68 | 0 | 0 | 0 | 0 | 0 | 12302.68
2022031801 | 6 | 0.45321 | 36256.8 | 0.55681 | 20045.16 | 0 | 0 | 1 | 5000 | 20045.16 | 0 | 0 | 0 | 0 | 0 | 11211.64 | 0 | 0 | 0 | 0 | 0 | 11211.64
2022031802 | 6 | 0.43686 | 34948.8 | 0.53599 | 19295.64 | 0 | 0 | 1 | 5000 | 19295.64 | 0 | 0 | 0 | 0 | 0 | 10653.16 | 0 | 0 | 0 | 0 | 0 | 10653.16
2022031803 | 6 | 0.42654 | 34123.2 | 0.51644 | 18591.84 | 0 | 0 | 1 | 5000 | 18591.84 | 0 | 0 | 0 | 0 | 0 | 10531.36 | 0 | 0 | 0 | 0 | 0 | 10531.36
2022031804 | 6 | 0.42355 | 33884 | 0.51376 | 18495.36 | 0 | 0 | 1 | 5000 | 18495.36 | 0 | 0 | 0 | 0 | 0 | 10388.64 | 0 | 0 | 0 | 0 | 0 | 10388.64
2022031805 | 6 | 0.4292 | 34336 | 0.5219 | 18788.4 | 0 | 0 | 1 | 5000 | 18788.4 | 0 | 0 | 0 | 0 | 0 | 10547.6 | 0 | 0 | 0 | 0 | 0 | 10547.6
2022031806 | 6 | 0.44739 | 35791.2 | 0.54853 | 19747.08 | 0 | 0 | 1 | 5000 | 19747.08 | 0 | 0 | 0 | 0 | 0 | 11044.12 | 0 | 0 | 0 | 0 | 0 | 11044.12
2022031807 | 6 | 0.47702 | 38161.6 | 0.57905 | 20845.8 | 0 | 0 | 1 | 5000 | 20845.8 | 0 | 0 | 0 | 0 | 0 | 12315.8 | 0 | 0 | 0 | 0 | 0 | 12315.8
2022031808 | 6 | 0.50195 | 40156 | 0.59681 | 21485.16 | 0.00103 | 12.36 | 1 | 5000 | 21485.16 | 12.36 | 0 | 0 | 0 | 0 | 13658.48 | 0 | 0 | 0 | 0 | 0 | 13658.48
2022031809 | 6 | 0.51406 | 41124.8 | 0.57975 | 20871 | 0.16924 | 2030.88 | 1 | 5000 | 20871 | 2030.88 | 0 | 0 | 0 | 0 | 13222.92 | 0 | 0 | 0 | 0 | 0 | 13222.92
2022031810 | 6 | 0.52329 | 41863.2 | 0.55776 | 20079.36 | 0.49764 | 5971.68 | 1 | 5000 | 20079.36 | 5971.68 | 0 | 0 | 0 | 0 | 10812.16 | 0 | 0 | 0 | 0 | 0 | 10812.16
2022031811 | 6 | 0.5227 | 41816 | 0.58164 | 20939.04 | 0.4461 | 5353.2 | 1 | 5000 | 20939.04 | 5353.2 | 0 | 0 | 0 | 0 | 10523.76 | 0 | 0 | 0 | 0 | 0 | 10523.76
2022031812 | 6 | 0.5183 | 41464 | 0.55708 | 20054.88 | 0.51936 | 6232.32 | 1 | 5000 | 20054.88 | 6232.32 | 0 | 0 | 0 | 0 | 10176.8 | 0 | 0 | 0 | 0 | 0 | 10176.8
2022031813 | 6 | 0.50969 | 40775.2 | 0.47035 | 16932.6 | 0.71976 | 8637.12 | 1 | 5000 | 16932.6 | 8637.12 | 0 | 0 | 0 | 0 | 10205.48 | 0 | 0 | 0 | 0 | 0 | 10205.48
2022031814 | 6 | 0.50306 | 40244.8 | 0.38796 | 13966.56 | 0.80981 | 9717.72 | 1 | 5000 | 13966.56 | 9717.72 | 0 | 0 | 0 | 0 | 11560.52 | 0 | 0 | 0 | 0 | 0 | 11560.52
2022031815 | 6 | 0.4984 | 39872 | 0.32667 | 11760.12 | 0.78356 | 9402.72 | 1 | 5000 | 11760.12 | 9402.72 | 0 | 0 | 0 | 0 | 13709.16 | 0 | 0 | 0 | 0 | 0 | 13709.16
2022031816 | 6 | 0.49746 | 39796.8 | 0.28781 | 10361.16 | 0.75667 | 9080.04 | 1 | 5000 | 10361.16 | 9080.04 | 0 | 0 | 0 | 0 | 15355.6 | 0 | 0 | 0 | 0 | 0 | 15355.6
2022031817 | 6 | 0.49825 | 39860 | 0.25435 | 9156.6 | 0.73069 | 8768.28 | 1 | 5000 | 9156.6 | 8768.28 | 0 | 0 | 0 | 0 | 16935.12 | 0 | 0 | 0 | 0 | 0 | 16935.12
2022031818 | 6 | 0.49896 | 39916.8 | 0.21497 | 7738.92 | 0.6661 | 7993.2 | 1 | 5000 | 7738.92 | 7993.2 | 0 | 0 | 0 | 0 | 19184.68 | 0 | 0 | 0 | 0 | 0 | 19184.68
2022031819 | 6 | 0.49541 | 39632.8 | 0.15824 | 5696.64 | 0.35823 | 4298.76 | 1 | 5000 | 5696.64 | 4298.76 | 0 | 0 | 0 | 0 | 24637.4 | 0 | 0 | 0 | 0 | 0 | 24637.4
2022031820 | 6 | 0.49669 | 39735.2 | 0.09257 | 3332.52 | 0.06991 | 838.92 | 1 | 5000 | 3332.52 | 838.92 | 0 | 0 | 0 | 0 | 30563.76 | 0 | 0 | 0 | 0 | 0 | 30563.76
2022031821 | 6 | 0.50522 | 40417.6 | 0.06887 | 2479.32 | 8e-05 | 0.96 | 1 | 5000 | 2479.32 | 0.96 | 0 | 0 | 0 | 0 | 32937.32 | 0 | 0 | 0 | 0 | 0 | 32937.32
2022031822 | 6 | 0.4965 | 39720 | 0.06765 | 2435.4 | 0 | 0 | 1 | 5000 | 2435.4 | 0 | 0 | 0 | 0 | 0 | 32284.6 | 0 | 0 | 0 | 0 | 0 | 32284.6
2022031823 | 6 | 0.48237 | 38589.6 | 0.06143 | 2211.48 | 0 | 0 | 1 | 5000 | 2211.48 | 0 | 0 | 0 | 0 | 0 | 31378.12 | 0 | 0 | 0 | 0 | 0 | 31378.12
2022031824 | 6 | 0.46459 | 37167.2 | 0.0685 | 2466 | 0 | 0 | 1 | 5000 | 2466 | 0 | 0 | 0 | 0 | 0 | 29701.2 | 0 | 0 | 0 | 0 | 0 | 29701.2
2022031901 | 7 | 0.44954 | 35963.2 | 0.098 | 3528 | 0 | 0 | 1 | 5000 | 3528 | 0 | 0 | 0 | 0 | 0 | 27435.2 | 0 | 0 | 0 | 0 | 0 | 27435.2
2022031902 | 7 | 0.44022 | 35217.6 | 0.11787 | 4243.32 | 0 | 0 | 1 | 5000 | 4243.32 | 0 | 0 | 0 | 0 | 0 | 25974.28 | 0 | 0 | 0 | 0 | 0 | 25974.28
2022031903 | 7 | 0.43532 | 34825.6 | 0.14558 | 5240.88 | 0 | 0 | 1 | 5000 | 5240.88 | 0 | 0 | 0 | 0 | 0 | 24584.72 | 0 | 0 | 0 | 0 | 0 | 24584.72
2022031904 | 7 | 0.4346 | 34768 | 0.17127 | 6165.72 | 0 | 0 | 1 | 5000 | 6165.72 | 0 | 0 | 0 | 0 | 0 | 23602.28 | 0 | 0 | 0 | 0 | 0 | 23602.28
2022031905 | 7 | 0.44095 | 35276 | 0.19986 | 7194.96 | 0 | 0 | 1 | 5000 | 7194.96 | 0 | 0 | 0 | 0 | 0 | 23081.04 | 0 | 0 | 0 | 0 | 0 | 23081.04
2022031906 | 7 | 0.45437 | 36349.6 | 0.23783 | 8561.88 | 0 | 0 | 1 | 5000 | 8561.88 | 0 | 0 | 0 | 0 | 0 | 22787.72 | 0 | 0 | 0 | 0 | 0 | 22787.72
2022031907 | 7 | 0.47674 | 38139.2 | 0.27229 | 9802.44 | 0 | 0 | 1 | 5000 | 9802.44 | 0 | 0 | 0 | 0 | 0 | 23336.76 | 0 | 0 | 0 | 0 | 0 | 23336.76
2022031908 | 7 | 0.49826 | 39860.8 | 0.31757 | 11432.52 | 0.00391 | 46.92 | 1 | 5000 | 11432.52 | 46.92 | 0 | 0 | 0 | 0 | 23381.36 | 0 | 0 | 0 | 0 | 0 | 23381.36
2022031909 | 7 | 0.51224 | 40979.2 | 0.34538 | 12433.68 | 0.23567 | 2828.04 | 1 | 5000 | 12433.68 | 2828.04 | 0 | 0 | 0 | 0 | 20717.48 | 0 | 0 | 0 | 0 | 0 | 20717.48
2022031910 | 7 | 0.50871 | 40696.8 | 0.28694 | 10329.84 | 0.75191 | 9022.92 | 1 | 5000 | 10329.84 | 9022.92 | 0 | 0 | 0 | 0 | 16344.04 | 0 | 0 | 0 | 0 | 0 | 16344.04
2022031911 | 7 | 0.50045 | 40036 | 0.32466 | 11687.76 | 0.85844 | 10301.28 | 1 | 5000 | 11687.76 | 10301.28 | 0 | 0 | 0 | 0 | 13046.96 | 0 | 0 | 0 | 0 | 0 | 13046.96
2022031912 | 7 | 0.4874 | 38992 | 0.32568 | 11724.48 | 0.86894 | 10427.28 | 1 | 5000 | 11724.48 | 10427.28 | 0 | 0 | 0 | 0 | 11840.24 | 0 | 0 | 0 | 0 | 0 | 11840.24
2022031913 | 7 | 0.47789 | 38231.2 | 0.27282 | 9821.52 | 0.87767 | 10532.04 | 1 | 5000 | 9821.52 | 10532.04 | 0 | 0 | 0 | 0 | 12877.64 | 0 | 0 | 0 | 0 | 0 | 12877.64
2022031914 | 7 | 0.47132 | 37705.6 | 0.20626 | 7425.36 | 0.87481 | 10497.72 | 1 | 5000 | 7425.36 | 10497.72 | 0 | 0 | 0 | 0 | 14782.52 | 0 | 0 | 0 | 0 | 0 | 14782.52
2022031915 | 7 | 0.47089 | 37671.2 | 0.18128 | 6526.08 | 0.87362 | 10483.44 | 1 | 5000 | 6526.08 | 10483.44 | 0 | 0 | 0 | 0 | 15661.68 | 0 | 0 | 0 | 0 | 0 | 15661.68
2022031916 | 7 | 0.47457 | 37965.6 | 0.19403 | 6985.08 | 0.87425 | 10491 | 1 | 5000 | 6985.08 | 10491 | 0 | 0 | 0 | 0 | 15489.52 | 0 | 0 | 0 | 0 | 0 | 15489.52
2022031917 | 7 | 0.48342 | 38673.6 | 0.21115 | 7601.4 | 0.86782 | 10413.84 | 1 | 5000 | 7601.4 | 10413.84 | 0 | 0 | 0 | 0 | 15658.36 | 0 | 0 | 0 | 0 | 0 | 15658.36
2022031918 | 7 | 0.49158 | 39326.4 | 0.21819 | 7854.84 | 0.80543 | 9665.16 | 1 | 5000 | 7854.84 | 9665.16 | 0 | 0 | 0 | 0 | 16806.4 | 0 | 0 | 0 | 0 | 0 | 16806.4
2022031919 | 7 | 0.49282 | 39425.6 | 0.22227 | 8001.72 | 0.5197 | 6236.4 | 1 | 5000 | 8001.72 | 6236.4 | 0 | 0 | 0 | 0 | 20187.48 | 0 | 0 | 0 | 0 | 0 | 20187.48
2022031920 | 7 | 0.49126 | 39300.8 | 0.21867 | 7872.12 | 0.07396 | 887.52 | 1 | 5000 | 7872.12 | 887.52 | 0 | 0 | 0 | 0 | 25541.16 | 0 | 0 | 0 | 0 | 0 | 25541.16
2022031921 | 7 | 0.49312 | 39449.6 | 0.26488 | 9535.68 | 0 | 0 | 1 | 5000 | 9535.68 | 0 | 0 | 0 | 0 | 0 | 24913.92 | 0 | 0 | 0 | 0 | 0 | 24913.92
2022031922 | 7 | 0.48275 | 38620 | 0.37942 | 13659.12 | 0 | 0 | 1 | 5000 | 13659.12 | 0 | 0 | 0 | 0 | 0 | 19960.88 | 0 | 0 | 0 | 0 | 0 | 19960.88
2022031923 | 7 | 0.46705 | 37364 | 0.48181 | 17345.16 | 0 | 0 | 1 | 5000 | 17345.16 | 0 | 0 | 0 | 0 | 0 | 15018.84 | 0 | 0 | 0 | 0 | 0 | 15018.84
2022031924 | 7 | 0.44948 | 35958.4 | 0.55133 | 19847.88 | 0 | 0 | 1 | 5000 | 19847.88 | 0 | 0 | 0 | 0 | 0 | 11110.52 | 0 | 0 | 0 | 0 | 0 | 11110.52
2022032001 | 1 | 0.43274 | 34619.2 | 0.57623 | 20744.28 | 0 | 0 | 1 | 5000 | 20744.28 | 0 | 0 | 0 | 0 | 0 | 8874.92 | 0 | 0 | 0 | 0 | 0 | 8874.92
2022032002 | 1 | 0.42062 | 33649.6 | 0.56784 | 20442.24 | 0 | 0 | 1 | 5000 | 20442.24 | 0 | 0 | 0 | 0 | 0 | 8207.36 | 0 | 0 | 0 | 0 | 0 | 8207.36
2022032003 | 1 | 0.41222 | 32977.6 | 0.55518 | 19986.48 | 0 | 0 | 1 | 5000 | 19986.48 | 0 | 0 | 0 | 0 | 0 | 7991.12 | 0 | 0 | 0 | 0 | 0 | 7991.12
2022032004 | 1 | 0.41104 | 32883.2 | 0.55319 | 19914.84 | 0 | 0 | 1 | 5000 | 19914.84 | 0 | 0 | 0 | 0 | 0 | 7968.36 | 0 | 0 | 0 | 0 | 0 | 7968.36
2022032005 | 1 | 0.41332 | 33065.6 | 0.5491 | 19767.6 | 0 | 0 | 1 | 5000 | 19767.6 | 0 | 0 | 0 | 0 | 0 | 8298 | 0 | 0 | 0 | 0 | 0 | 8298
2022032006 | 1 | 0.42055 | 33644 | 0.54482 | 19613.52 | 0 | 0 | 1 | 5000 | 19613.52 | 0 | 0 | 0 | 0 | 0 | 9030.48 | 0 | 0 | 0 | 0 | 0 | 9030.48
2022032007 | 1 | 0.43506 | 34804.8 | 0.55423 | 19952.28 | 0 | 0 | 1 | 5000 | 19952.28 | 0 | 0 | 0 | 0 | 0 | 9852.52 | 0 | 0 | 0 | 0 | 0 | 9852.52
2022032008 | 1 | 0.45301 | 36240.8 | 0.56244 | 20247.84 | 0.00324 | 38.88 | 1 | 5000 | 20247.84 | 38.88 | 0 | 0 | 0 | 0 | 10954.08 | 0 | 0 | 0 | 0 | 0 | 10954.08
2022032009 | 1 | 0.46702 | 37361.6 | 0.55026 | 19809.36 | 0.1457 | 1748.4 | 1 | 5000 | 19809.36 | 1748.4 | 0 | 0 | 0 | 0 | 10803.84 | 0 | 0 | 0 | 0 | 0 | 10803.84
2022032010 | 1 | 0.47142 | 37713.6 | 0.51511 | 18543.96 | 0.36347 | 4361.64 | 1 | 5000 | 18543.96 | 4361.64 | 0 | 0 | 0 | 0 | 9808 | 0 | 0 | 0 | 0 | 0 | 9808
2022032011 | 1 | 0.47225 | 37780 | 0.57329 | 20638.44 | 0.31524 | 3782.88 | 1 | 5000 | 20638.44 | 3782.88 | 0 | 0 | 0 | 0 | 8358.68 | 0 | 0 | 0 | 0 | 0 | 8358.68
2022032012 | 1 | 0.47148 | 37718.4 | 0.61894 | 22281.84 | 0.2583 | 3099.6 | 1 | 5000 | 22281.84 | 3099.6 | 0 | 0 | 0 | 0 | 7336.96 | 0 | 0 | 0 | 0 | 0 | 7336.96
2022032013 | 1 | 0.47243 | 37794.4 | 0.63638 | 22909.68 | 0.23458 | 2814.96 | 1 | 5000 | 22909.68 | 2814.96 | 0 | 0 | 0 | 0 | 7069.76 | 0 | 0 | 0 | 0 | 0 | 7069.76
2022032014 | 1 | 0.47501 | 38000.8 | 0.64289 | 23144.04 | 0.23955 | 2874.6 | 1 | 5000 | 23144.04 | 2874.6 | 0 | 0 | 0 | 0 | 6982.16 | 0 | 0 | 0 | 0 | 0 | 6982.16
2022032015 | 1 | 0.47982 | 38385.6 | 0.64624 | 23264.64 | 0.25144 | 3017.28 | 1 | 5000 | 23264.64 | 3017.28 | 0 | 0 | 0 | 0 | 7103.68 | 0 | 0 | 0 | 0 | 0 | 7103.68
2022032016 | 1 | 0.48809 | 39047.2 | 0.65222 | 23479.92 | 0.24898 | 2987.76 | 1 | 5000 | 23479.92 | 2987.76 | 0 | 0 | 0 | 0 | 7579.52 | 0 | 0 | 0 | 0 | 0 | 7579.52
2022032017 | 1 | 0.49751 | 39800.8 | 0.65898 | 23723.28 | 0.24615 | 2953.8 | 1 | 5000 | 23723.28 | 2953.8 | 0 | 0 | 0 | 0 | 8123.72 | 0 | 0 | 0 | 0 | 0 | 8123.72
2022032018 | 1 | 0.50692 | 40553.6 | 0.66193 | 23829.48 | 0.26085 | 3130.2 | 1 | 5000 | 23829.48 | 3130.2 | 0 | 0 | 0 | 0 | 8593.92 | 0 | 0 | 0 | 0 | 0 | 8593.92
2022032019 | 1 | 0.51101 | 40880.8 | 0.67232 | 24203.52 | 0.16208 | 1944.96 | 1 | 5000 | 24203.52 | 1944.96 | 0 | 0 | 0 | 0 | 9732.32 | 0 | 0 | 0 | 0 | 0 | 9732.32
2022032020 | 1 | 0.5156 | 41248 | 0.68646 | 24712.56 | 0.03046 | 365.52 | 1 | 5000 | 24712.56 | 365.52 | 0 | 0 | 0 | 0 | 11169.92 | 0 | 0 | 0 | 0 | 0 | 11169.92
2022032021 | 1 | 0.5265 | 42120 | 0.6921 | 24915.6 | 0 | 0 | 1 | 5000 | 24915.6 | 0 | 0 | 0 | 0 | 0 | 12204.4 | 0 | 0 | 0 | 0 | 0 | 12204.4
2022032022 | 1 | 0.51517 | 41213.6 | 0.69397 | 24982.92 | 0 | 0 | 1 | 5000 | 24982.92 | 0 | 0 | 0 | 0 | 0 | 11230.68 | 0 | 0 | 0 | 0 | 0 | 11230.68
2022032023 | 1 | 0.48987 | 39189.6 | 0.68084 | 24510.24 | 0 | 0 | 1 | 5000 | 24510.24 | 0 | 0 | 0 | 0 | 0 | 9679.36 | 0 | 0 | 0 | 0 | 0 | 9679.36
2022032024 | 1 | 0.4587 | 36696 | 0.65097 | 23434.92 | 0 | 0 | 1 | 5000 | 23434.92 | 0 | 0 | 0 | 0 | 0 | 8261.08 | 0 | 0 | 0 | 0 | 0 | 8261.08
2022032101 | 2 | 0.43385 | 34708 | 0.62875 | 22635 | 0 | 0 | 1 | 5000 | 22635 | 0 | 0 | 0 | 0 | 0 | 7073 | 0 | 0 | 0 | 0 | 0 | 7073
2022032102 | 2 | 0.41796 | 33436.8 | 0.61499 | 22139.64 | 0 | 0 | 1 | 5000 | 22139.64 | 0 | 0 | 0 | 0 | 0 | 6297.16 | 0 | 0 | 0 | 0 | 0 | 6297.16
2022032103 | 2 | 0.41143 | 32914.4 | 0.60516 | 21785.76 | 0 | 0 | 1 | 5000 | 21785.76 | 0 | 0 | 0 | 0 | 0 | 6128.64 | 0 | 0 | 0 | 0 | 0 | 6128.64
2022032104 | 2 | 0.41104 | 32883.2 | 0.60721 | 21859.56 | 0 | 0 | 1 | 5000 | 21859.56 | 0 | 0 | 0 | 0 | 0 | 6023.64 | 0 | 0 | 0 | 0 | 0 | 6023.64
2022032105 | 2 | 0.41711 | 33368.8 | 0.60934 | 21936.24 | 0 | 0 | 1 | 5000 | 21936.24 | 0 | 0 | 0 | 0 | 0 | 6432.56 | 0 | 0 | 0 | 0 | 0 | 6432.56
2022032106 | 2 | 0.43785 | 35028 | 0.61671 | 22201.56 | 0 | 0 | 1 | 5000 | 22201.56 | 0 | 0 | 0 | 0 | 0 | 7826.44 | 0 | 0 | 0 | 0 | 0 | 7826.44
2022032107 | 2 | 0.4755 | 38040 | 0.6493 | 23374.8 | 0 | 0 | 1 | 5000 | 23374.8 | 0 | 0 | 0 | 0 | 0 | 9665.2 | 0 | 0 | 0 | 0 | 0 | 9665.2
2022032108 | 2 | 0.49952 | 39961.6 | 0.63567 | 22884.12 | 0.00018 | 2.16 | 1 | 5000 | 22884.12 | 2.16 | 0 | 0 | 0 | 0 | 12075.32 | 0 | 0 | 0 | 0 | 0 | 12075.32
2022032109 | 2 | 0.50486 | 40388.8 | 0.56407 | 20306.52 | 0.0779 | 934.8 | 1 | 5000 | 20306.52 | 934.8 | 0 | 0 | 0 | 0 | 14147.48 | 0 | 0 | 0 | 0 | 0 | 14147.48
2022032110 | 2 | 0.51521 | 41216.8 | 0.53467 | 19248.12 | 0.24772 | 2972.64 | 1 | 5000 | 19248.12 | 2972.64 | 0 | 0 | 0 | 0 | 13996.04 | 0 | 0 | 0 | 0 | 0 | 13996.04
2022032111 | 2 | 0.52921 | 42336.8 | 0.5813 | 20926.8 | 0.32099 | 3851.88 | 1 | 5000 | 20926.8 | 3851.88 | 0 | 0 | 0 | 0 | 12558.12 | 0 | 0 | 0 | 0 | 0 | 12558.12
2022032112 | 2 | 0.54076 | 43260.8 | 0.56607 | 20378.52 | 0.34618 | 4154.16 | 1 | 5000 | 20378.52 | 4154.16 | 0 | 0 | 0 | 0 | 13728.12 | 0 | 0 | 0 | 0 | 0 | 13728.12
2022032113 | 2 | 0.54478 | 43582.4 | 0.51838 | 18661.68 | 0.4555 | 5466 | 1 | 5000 | 18661.68 | 5466 | 0 | 0 | 0 | 0 | 14454.72 | 0 | 0 | 0 | 0 | 0 | 14454.72
2022032114 | 2 | 0.5475 | 43800 | 0.50056 | 18020.16 | 0.46733 | 5607.96 | 1 | 5000 | 18020.16 | 5607.96 | 0 | 0 | 0 | 0 | 15171.88 | 0 | 0 | 0 | 0 | 0 | 15171.88
2022032115 | 2 | 0.54749 | 43799.2 | 0.49433 | 17795.88 | 0.43479 | 5217.48 | 1 | 5000 | 17795.88 | 5217.48 | 0 | 0 | 0 | 0 | 15785.84 | 0 | 0 | 0 | 0 | 0 | 15785.84
2022032116 | 2 | 0.55002 | 44001.6 | 0.52023 | 18728.28 | 0.41444 | 4973.28 | 1 | 5000 | 18728.28 | 4973.28 | 0 | 0 | 0 | 0 | 15300.04 | 0 | 0 | 0 | 0 | 0 | 15300.04
2022032117 | 2 | 0.55619 | 44495.2 | 0.54325 | 19557 | 0.3436 | 4123.2 | 1 | 5000 | 19557 | 4123.2 | 0 | 0 | 0 | 0 | 15815 | 0 | 0 | 0 | 0 | 0 | 15815
2022032118 | 2 | 0.56335 | 45068 | 0.58895 | 21202.2 | 0.23543 | 2825.16 | 1 | 5000 | 21202.2 | 2825.16 | 0 | 0 | 0 | 0 | 16040.64 | 0 | 0 | 0 | 0 | 0 | 16040.64
2022032119 | 2 | 0.55859 | 44687.2 | 0.59945 | 21580.2 | 0.17078 | 2049.36 | 1 | 5000 | 21580.2 | 2049.36 | 0 | 0 | 0 | 0 | 16057.64 | 0 | 0 | 0 | 0 | 0 | 16057.64
2022032120 | 2 | 0.55288 | 44230.4 | 0.62545 | 22516.2 | 0.0432 | 518.4 | 1 | 5000 | 22516.2 | 518.4 | 0 | 0 | 0 | 0 | 16195.8 | 0 | 0 | 0 | 0 | 0 | 16195.8
2022032121 | 2 | 0.5521 | 44168 | 0.599 | 21564 | 0 | 0 | 1 | 5000 | 21564 | 0 | 0 | 0 | 0 | 0 | 17604 | 0 | 0 | 0 | 0 | 0 | 17604
2022032122 | 2 | 0.53871 | 43096.8 | 0.60709 | 21855.24 | 0 | 0 | 1 | 5000 | 21855.24 | 0 | 0 | 0 | 0 | 0 | 16241.56 | 0 | 0 | 0 | 0 | 0 | 16241.56
2022032123 | 2 | 0.51332 | 41065.6 | 0.59244 | 21327.84 | 0 | 0 | 1 | 5000 | 21327.84 | 0 | 0 | 0 | 0 | 0 | 14737.76 | 0 | 0 | 0 | 0 | 0 | 14737.76
2022032124 | 2 | 0.48083 | 38466.4 | 0.5432 | 19555.2 | 0 | 0 | 1 | 5000 | 19555.2 | 0 | 0 | 0 | 0 | 0 | 13911.2 | 0 | 0 | 0 | 0 | 0 | 13911.2
2022032201 | 3 | 0.45287 | 36229.6 | 0.48684 | 17526.24 | 0 | 0 | 1 | 5000 | 17526.24 | 0 | 0 | 0 | 0 | 0 | 13703.36 | 0 | 0 | 0 | 0 | 0 | 13703.36
2022032202 | 3 | 0.43783 | 35026.4 | 0.47601 | 17136.36 | 0 | 0 | 1 | 5000 | 17136.36 | 0 | 0 | 0 | 0 | 0 | 12890.04 | 0 | 0 | 0 | 0 | 0 | 12890.04
2022032203 | 3 | 0.42948 | 34358.4 | 0.54479 | 19612.44 | 0 | 0 | 1 | 5000 | 19612.44 | 0 | 0 | 0 | 0 | 0 | 9745.96 | 0 | 0 | 0 | 0 | 0 | 9745.96
2022032204 | 3 | 0.42732 | 34185.6 | 0.56619 | 20382.84 | 0 | 0 | 1 | 5000 | 20382.84 | 0 | 0 | 0 | 0 | 0 | 8802.76 | 0 | 0 | 0 | 0 | 0 | 8802.76
2022032205 | 3 | 0.43178 | 34542.4 | 0.58163 | 20938.68 | 0 | 0 | 1 | 5000 | 20938.68 | 0 | 0 | 0 | 0 | 0 | 8603.72 | 0 | 0 | 0 | 0 | 0 | 8603.72
2022032206 | 3 | 0.45212 | 36169.6 | 0.57927 | 20853.72 | 0 | 0 | 1 | 5000 | 20853.72 | 0 | 0 | 0 | 0 | 0 | 10315.88 | 0 | 0 | 0 | 0 | 0 | 10315.88
2022032207 | 3 | 0.49 | 39200 | 0.59751 | 21510.36 | 0 | 0 | 1 | 5000 | 21510.36 | 0 | 0 | 0 | 0 | 0 | 12689.64 | 0 | 0 | 0 | 0 | 0 | 12689.64
2022032208 | 3 | 0.51144 | 40915.2 | 0.62495 | 22498.2 | 0.00062 | 7.44 | 1 | 5000 | 22498.2 | 7.44 | 0 | 0 | 0 | 0 | 13409.56 | 0 | 0 | 0 | 0 | 0 | 13409.56
2022032209 | 3 | 0.51111 | 40888.8 | 0.61224 | 22040.64 | 0.06094 | 731.28 | 1 | 5000 | 22040.64 | 731.28 | 0 | 0 | 0 | 0 | 13116.88 | 0 | 0 | 0 | 0 | 0 | 13116.88
2022032210 | 3 | 0.51618 | 41294.4 | 0.6115 | 22014 | 0.16636 | 1996.32 | 1 | 5000 | 22014 | 1996.32 | 0 | 0 | 0 | 0 | 12284.08 | 0 | 0 | 0 | 0 | 0 | 12284.08
2022032211 | 3 | 0.52201 | 41760.8 | 0.63666 | 22919.76 | 0.20501 | 2460.12 | 1 | 5000 | 22919.76 | 2460.12 | 0 | 0 | 0 | 0 | 11380.92 | 0 | 0 | 0 | 0 | 0 | 11380.92
2022032212 | 3 | 0.52825 | 42260 | 0.64751 | 23310.36 | 0.22752 | 2730.24 | 1 | 5000 | 23310.36 | 2730.24 | 0 | 0 | 0 | 0 | 11219.4 | 0 | 0 | 0 | 0 | 0 | 11219.4
2022032213 | 3 | 0.53182 | 42545.6 | 0.64925 | 23373 | 0.21864 | 2623.68 | 1 | 5000 | 23373 | 2623.68 | 0 | 0 | 0 | 0 | 11548.92 | 0 | 0 | 0 | 0 | 0 | 11548.92
2022032214 | 3 | 0.5355 | 42840 | 0.64351 | 23166.36 | 0.2378 | 2853.6 | 1 | 5000 | 23166.36 | 2853.6 | 0 | 0 | 0 | 0 | 11820.04 | 0 | 0 | 0 | 0 | 0 | 11820.04
2022032215 | 3 | 0.53591 | 42872.8 | 0.63806 | 22970.16 | 0.24448 | 2933.76 | 1 | 5000 | 22970.16 | 2933.76 | 0 | 0 | 0 | 0 | 11968.88 | 0 | 0 | 0 | 0 | 0 | 11968.88
2022032216 | 3 | 0.53728 | 42982.4 | 0.64622 | 23263.92 | 0.20657 | 2478.84 | 1 | 5000 | 23263.92 | 2478.84 | 0 | 0 | 0 | 0 | 12239.64 | 0 | 0 | 0 | 0 | 0 | 12239.64
2022032217 | 3 | 0.54419 | 43535.2 | 0.66237 | 23845.32 | 0.16049 | 1925.88 | 1 | 5000 | 23845.32 | 1925.88 | 0 | 0 | 0 | 0 | 12764 | 0 | 0 | 0 | 0 | 0 | 12764
2022032218 | 3 | 0.55169 | 44135.2 | 0.67108 | 24158.88 | 0.14707 | 1764.84 | 1 | 5000 | 24158.88 | 1764.84 | 0 | 0 | 0 | 0 | 13211.48 | 0 | 0 | 0 | 0 | 0 | 13211.48
2022032219 | 3 | 0.55254 | 44203.2 | 0.6587 | 23713.2 | 0.0957 | 1148.4 | 1 | 5000 | 23713.2 | 1148.4 | 0 | 0 | 0 | 0 | 14341.6 | 0 | 0 | 0 | 0 | 0 | 14341.6
2022032220 | 3 | 0.55672 | 44537.6 | 0.64909 | 23367.24 | 0.02372 | 284.64 | 1 | 5000 | 23367.24 | 284.64 | 0 | 0 | 0 | 0 | 15885.72 | 0 | 0 | 0 | 0 | 0 | 15885.72
2022032221 | 3 | 0.56235 | 44988 | 0.58349 | 21005.64 | 0 | 0 | 1 | 5000 | 21005.64 | 0 | 0 | 0 | 0 | 0 | 18982.36 | 0 | 0 | 0 | 0 | 0 | 18982.36
2022032222 | 3 | 0.54677 | 43741.6 | 0.5432 | 19555.2 | 0 | 0 | 1 | 5000 | 19555.2 | 0 | 0 | 0 | 0 | 0 | 19186.4 | 0 | 0 | 0 | 0 | 0 | 19186.4
2022032223 | 3 | 0.51812 | 41449.6 | 0.5383 | 19378.8 | 0 | 0 | 1 | 5000 | 19378.8 | 0 | 0 | 0 | 0 | 0 | 17070.8 | 0 | 0 | 0 | 0 | 0 | 17070.8
2022032224 | 3 | 0.48767 | 39013.6 | 0.5695 | 20502 | 0 | 0 | 1 | 5000 | 20502 | 0 | 0 | 0 | 0 | 0 | 13511.6 | 0 | 0 | 0 | 0 | 0 | 13511.6
2022032301 | 4 | 0.46731 | 37384.8 | 0.58702 | 21132.72 | 0 | 0 | 1 | 5000 | 21132.72 | 0 | 0 | 0 | 0 | 0 | 11252.08 | 0 | 0 | 0 | 0 | 0 | 11252.08
2022032302 | 4 | 0.45711 | 36568.8 | 0.5763 | 20746.8 | 0 | 0 | 1 | 5000 | 20746.8 | 0 | 0 | 0 | 0 | 0 | 10822 | 0 | 0 | 0 | 0 | 0 | 10822
2022032303 | 4 | 0.45314 | 36251.2 | 0.55877 | 20115.72 | 0 | 0 | 1 | 5000 | 20115.72 | 0 | 0 | 0 | 0 | 0 | 11135.48 | 0 | 0 | 0 | 0 | 0 | 11135.48
2022032304 | 4 | 0.45522 | 36417.6 | 0.54554 | 19639.44 | 0 | 0 | 1 | 5000 | 19639.44 | 0 | 0 | 0 | 0 | 0 | 11778.16 | 0 | 0 | 0 | 0 | 0 | 11778.16
2022032305 | 4 | 0.46719 | 37375.2 | 0.53147 | 19132.92 | 0 | 0 | 1 | 5000 | 19132.92 | 0 | 0 | 0 | 0 | 0 | 13242.28 | 0 | 0 | 0 | 0 | 0 | 13242.28
2022032306 | 4 | 0.49644 | 39715.2 | 0.52378 | 18856.08 | 0 | 0 | 1 | 5000 | 18856.08 | 0 | 0 | 0 | 0 | 0 | 15859.12 | 0 | 0 | 0 | 0 | 0 | 15859.12
2022032307 | 4 | 0.54642 | 43713.6 | 0.53128 | 19126.08 | 0 | 0 | 1 | 5000 | 19126.08 | 0 | 0 | 0 | 0 | 0 | 19587.52 | 0 | 0 | 0 | 0 | 0 | 19587.52
2022032308 | 4 | 0.57317 | 45853.6 | 0.52001 | 18720.36 | 0.00652 | 78.24 | 1 | 5000 | 18720.36 | 78.24 | 0 | 0 | 0 | 0 | 22055 | 0 | 0 | 0 | 0 | 0 | 22055
2022032309 | 4 | 0.56332 | 45065.6 | 0.45128 | 16246.08 | 0.26757 | 3210.84 | 1 | 5000 | 16246.08 | 3210.84 | 0 | 0 | 0 | 0 | 20608.68 | 0 | 0 | 0 | 0 | 0 | 20608.68
2022032310 | 4 | 0.55001 | 44000.8 | 0.38381 | 13817.16 | 0.69823 | 8378.76 | 1 | 5000 | 13817.16 | 8378.76 | 0 | 0 | 0 | 0 | 16804.88 | 0 | 0 | 0 | 0 | 0 | 16804.88
2022032311 | 4 | 0.53506 | 42804.8 | 0.38206 | 13754.16 | 0.75171 | 9020.52 | 1 | 5000 | 13754.16 | 9020.52 | 0 | 0 | 0 | 0 | 15030.12 | 0 | 0 | 0 | 0 | 0 | 15030.12
2022032312 | 4 | 0.52293 | 41834.4 | 0.40546 | 14596.56 | 0.75682 | 9081.84 | 1 | 5000 | 14596.56 | 9081.84 | 0 | 0 | 0 | 0 | 13156 | 0 | 0 | 0 | 0 | 0 | 13156
2022032313 | 4 | 0.51437 | 41149.6 | 0.45402 | 16344.72 | 0.60704 | 7284.48 | 1 | 5000 | 16344.72 | 7284.48 | 0 | 0 | 0 | 0 | 12520.4 | 0 | 0 | 0 | 0 | 0 | 12520.4
2022032314 | 4 | 0.50726 | 40580.8 | 0.48464 | 17447.04 | 0.44534 | 5344.08 | 1 | 5000 | 17447.04 | 5344.08 | 0 | 0 | 0 | 0 | 12789.68 | 0 | 0 | 0 | 0 | 0 | 12789.68
2022032315 | 4 | 0.50023 | 40018.4 | 0.49605 | 17857.8 | 0.40618 | 4874.16 | 1 | 5000 | 17857.8 | 4874.16 | 0 | 0 | 0 | 0 | 12286.44 | 0 | 0 | 0 | 0 | 0 | 12286.44
2022032316 | 4 | 0.49861 | 39888.8 | 0.49079 | 17668.44 | 0.40685 | 4882.2 | 1 | 5000 | 17668.44 | 4882.2 | 0 | 0 | 0 | 0 | 12338.16 | 0 | 0 | 0 | 0 | 0 | 12338.16
2022032317 | 4 | 0.49967 | 39973.6 | 0.4972 | 17899.2 | 0.36906 | 4428.72 | 1 | 5000 | 17899.2 | 4428.72 | 0 | 0 | 0 | 0 | 12645.68 | 0 | 0 | 0 | 0 | 0 | 12645.68
2022032318 | 4 | 0.50263 | 40210.4 | 0.48825 | 17577 | 0.3503 | 4203.6 | 1 | 5000 | 17577 | 4203.6 | 0 | 0 | 0 | 0 | 13429.8 | 0 | 0 | 0 | 0 | 0 | 13429.8
2022032319 | 4 | 0.50315 | 40252 | 0.47609 | 17139.24 | 0.23307 | 2796.84 | 1 | 5000 | 17139.24 | 2796.84 | 0 | 0 | 0 | 0 | 15315.92 | 0 | 0 | 0 | 0 | 0 | 15315.92
2022032320 | 4 | 0.5114 | 40912 | 0.41657 | 14996.52 | 0.07478 | 897.36 | 1 | 5000 | 14996.52 | 897.36 | 0 | 0 | 0 | 0 | 20018.12 | 0 | 0 | 0 | 0 | 0 | 20018.12
2022032321 | 4 | 0.52551 | 42040.8 | 0.32682 | 11765.52 | 0.00019 | 2.28 | 1 | 5000 | 11765.52 | 2.28 | 0 | 0 | 0 | 0 | 25273 | 0 | 0 | 0 | 0 | 0 | 25273
2022032322 | 4 | 0.51564 | 41251.2 | 0.25095 | 9034.2 | 0 | 0 | 1 | 5000 | 9034.2 | 0 | 0 | 0 | 0 | 0 | 27217 | 0 | 0 | 0 | 0 | 0 | 27217
2022032323 | 4 | 0.4937 | 39496 | 0.22641 | 8150.76 | 0 | 0 | 1 | 5000 | 8150.76 | 0 | 0 | 0 | 0 | 0 | 26345.24 | 0 | 0 | 0 | 0 | 0 | 26345.24
2022032324 | 4 | 0.46845 | 37476 | 0.18723 | 6740.28 | 0 | 0 | 1 | 5000 | 6740.28 | 0 | 0 | 0 | 0 | 0 | 25735.72 | 0 | 0 | 0 | 0 | 0 | 25735.72
2022032401 | 5 | 0.45257 | 36205.6 | 0.15054 | 5419.44 | 0 | 0 | 1 | 5000 | 5419.44 | 0 | 0 | 0 | 0 | 0 | 25786.16 | 0 | 0 | 0 | 0 | 0 | 25786.16
2022032402 | 5 | 0.4455 | 35640 | 0.14977 | 5391.72 | 0 | 0 | 1 | 5000 | 5391.72 | 0 | 0 | 0 | 0 | 0 | 25248.28 | 0 | 0 | 0 | 0 | 0 | 25248.28
2022032403 | 5 | 0.44545 | 35636 | 0.2148 | 7732.8 | 0 | 0 | 1 | 5000 | 7732.8 | 0 | 0 | 0 | 0 | 0 | 22903.2 | 0 | 0 | 0 | 0 | 0 | 22903.2
2022032404 | 5 | 0.4516 | 36128 | 0.27656 | 9956.16 | 0 | 0 | 1 | 5000 | 9956.16 | 0 | 0 | 0 | 0 | 0 | 21171.84 | 0 | 0 | 0 | 0 | 0 | 21171.84
2022032405 | 5 | 0.46613 | 37290.4 | 0.3268 | 11764.8 | 0 | 0 | 1 | 5000 | 11764.8 | 0 | 0 | 0 | 0 | 0 | 20525.6 | 0 | 0 | 0 | 0 | 0 | 20525.6
2022032406 | 5 | 0.49978 | 39982.4 | 0.37898 | 13643.28 | 0 | 0 | 1 | 5000 | 13643.28 | 0 | 0 | 0 | 0 | 0 | 21339.12 | 0 | 0 | 0 | 0 | 0 | 21339.12
2022032407 | 5 | 0.55306 | 44244.8 | 0.41039 | 14774.04 | 0 | 0 | 1 | 5000 | 14774.04 | 0 | 0 | 0 | 0 | 0 | 24470.76 | 0 | 0 | 0 | 0 | 0 | 24470.76
2022032408 | 5 | 0.58218 | 46574.4 | 0.41327 | 14877.72 | 0.0075 | 90 | 1 | 5000 | 14877.72 | 90 | 0 | 0 | 0 | 0 | 26606.68 | 0 | 0 | 0 | 0 | 0 | 26606.68
2022032409 | 5 | 0.57051 | 45640.8 | 0.3725 | 13410 | 0.29163 | 3499.56 | 1 | 5000 | 13410 | 3499.56 | 0 | 0 | 0 | 0 | 23731.24 | 0 | 0 | 0 | 0 | 0 | 23731.24
2022032410 | 5 | 0.54866 | 43892.8 | 0.22375 | 8055 | 0.78711 | 9445.32 | 1 | 5000 | 8055 | 9445.32 | 0 | 0 | 0 | 0 | 21392.48 | 0 | 0 | 0 | 0 | 0 | 21392.48
2022032411 | 5 | 0.5312 | 42496 | 0.20179 | 7264.44 | 0.86261 | 10351.32 | 1 | 5000 | 7264.44 | 10351.32 | 0 | 0 | 0 | 0 | 19880.24 | 0 | 0 | 0 | 0 | 0 | 19880.24
2022032412 | 5 | 0.51639 | 41311.2 | 0.30725 | 11061 | 0.84957 | 10194.84 | 1 | 5000 | 11061 | 10194.84 | 0 | 0 | 0 | 0 | 15055.36 | 0 | 0 | 0 | 0 | 0 | 15055.36
2022032413 | 5 | 0.50698 | 40558.4 | 0.42552 | 15318.72 | 0.66636 | 7996.32 | 1 | 5000 | 15318.72 | 7996.32 | 0 | 0 | 0 | 0 | 12243.36 | 0 | 0 | 0 | 0 | 0 | 12243.36
2022032414 | 5 | 0.50241 | 40192.8 | 0.47172 | 16981.92 | 0.56529 | 6783.48 | 1 | 5000 | 16981.92 | 6783.48 | 0 | 0 | 0 | 0 | 11427.4 | 0 | 0 | 0 | 0 | 0 | 11427.4
2022032415 | 5 | 0.49844 | 39875.2 | 0.47172 | 16981.92 | 0.52432 | 6291.84 | 1 | 5000 | 16981.92 | 6291.84 | 0 | 0 | 0 | 0 | 11601.44 | 0 | 0 | 0 | 0 | 0 | 11601.44
2022032416 | 5 | 0.49762 | 39809.6 | 0.45308 | 16310.88 | 0.53319 | 6398.28 | 1 | 5000 | 16310.88 | 6398.28 | 0 | 0 | 0 | 0 | 12100.44 | 0 | 0 | 0 | 0 | 0 | 12100.44
2022032417 | 5 | 0.50158 | 40126.4 | 0.41119 | 14802.84 | 0.67109 | 8053.08 | 1 | 5000 | 14802.84 | 8053.08 | 0 | 0 | 0 | 0 | 12270.48 | 0 | 0 | 0 | 0 | 0 | 12270.48
2022032418 | 5 | 0.50522 | 40417.6 | 0.33613 | 12100.68 | 0.79633 | 9555.96 | 1 | 5000 | 12100.68 | 9555.96 | 0 | 0 | 0 | 0 | 13760.96 | 0 | 0 | 0 | 0 | 0 | 13760.96
2022032419 | 5 | 0.50289 | 40231.2 | 0.21246 | 7648.56 | 0.63753 | 7650.36 | 1 | 5000 | 7648.56 | 7650.36 | 0 | 0 | 0 | 0 | 19932.28 | 0 | 0 | 0 | 0 | 0 | 19932.28
2022032420 | 5 | 0.50657 | 40525.6 | 0.08432 | 3035.52 | 0.14287 | 1714.44 | 1 | 5000 | 3035.52 | 1714.44 | 0 | 0 | 0 | 0 | 30775.64 | 0 | 0 | 0 | 0 | 0 | 30775.64
2022032421 | 5 | 0.51856 | 41484.8 | 0.05878 | 2116.08 | 0.00019 | 2.28 | 1 | 5000 | 2116.08 | 2.28 | 0 | 0 | 0 | 0 | 34366.44 | 0 | 0 | 0 | 0 | 0 | 34366.44
2022032422 | 5 | 0.50849 | 40679.2 | 0.08469 | 3048.84 | 0 | 0 | 1 | 5000 | 3048.84 | 0 | 0 | 0 | 0 | 0 | 32630.36 | 0 | 0 | 0 | 0 | 0 | 32630.36
2022032423 | 5 | 0.48589 | 38871.2 | 0.11808 | 4250.88 | 0 | 0 | 1 | 5000 | 4250.88 | 0 | 0 | 0 | 0 | 0 | 29620.32 | 0 | 0 | 0 | 0 | 0 | 29620.32
2022032424 | 5 | 0.46049 | 36839.2 | 0.16674 | 6002.64 | 0 | 0 | 1 | 5000 | 6002.64 | 0 | 0 | 0 | 0 | 0 | 25836.56 | 0 | 0 | 0 | 0 | 0 | 25836.56
2022032501 | 6 | 0.44188 | 35350.4 | 0.19616 | 7061.76 | 0 | 0 | 1 | 5000 | 7061.76 | 0 | 0 | 0 | 0 | 0 | 23288.64 | 0 | 0 | 0 | 0 | 0 | 23288.64
2022032502 | 6 | 0.43229 | 34583.2 | 0.22007 | 7922.52 | 0 | 0 | 1 | 5000 | 7922.52 | 0 | 0 | 0 | 0 | 0 | 21660.68 | 0 | 0 | 0 | 0 | 0 | 21660.68
2022032503 | 6 | 0.43105 | 34484 | 0.24069 | 8664.84 | 0 | 0 | 1 | 5000 | 8664.84 | 0 | 0 | 0 | 0 | 0 | 20819.16 | 0 | 0 | 0 | 0 | 0 | 20819.16
2022032504 | 6 | 0.43452 | 34761.6 | 0.24316 | 8753.76 | 0 | 0 | 1 | 5000 | 8753.76 | 0 | 0 | 0 | 0 | 0 | 21007.84 | 0 | 0 | 0 | 0 | 0 | 21007.84
2022032505 | 6 | 0.4461 | 35688 | 0.24149 | 8693.64 | 0 | 0 | 1 | 5000 | 8693.64 | 0 | 0 | 0 | 0 | 0 | 21994.36 | 0 | 0 | 0 | 0 | 0 | 21994.36
2022032506 | 6 | 0.47844 | 38275.2 | 0.22047 | 7936.92 | 0 | 0 | 1 | 5000 | 7936.92 | 0 | 0 | 0 | 0 | 0 | 25338.28 | 0 | 0 | 0 | 0 | 0 | 25338.28
2022032507 | 6 | 0.52818 | 42254.4 | 0.19918 | 7170.48 | 0 | 0 | 1 | 5000 | 7170.48 | 0 | 0 | 0 | 0 | 0 | 30083.92 | 0 | 0 | 0 | 0 | 0 | 30083.92
2022032508 | 6 | 0.5566 | 44528 | 0.18059 | 6501.24 | 0.00905 | 108.6 | 1 | 5000 | 6501.24 | 108.6 | 0 | 0 | 0 | 0 | 32918.16 | 0 | 0 | 0 | 0 | 0 | 32918.16
2022032509 | 6 | 0.54808 | 43846.4 | 0.14575 | 5247 | 0.31162 | 3739.44 | 1 | 5000 | 5247 | 3739.44 | 0 | 0 | 0 | 0 | 29859.96 | 0 | 0 | 0 | 0 | 0 | 29859.96
2022032510 | 6 | 0.52948 | 42358.4 | 0.06402 | 2304.72 | 0.78577 | 9429.24 | 1 | 5000 | 2304.72 | 9429.24 | 0 | 0 | 0 | 0 | 25624.44 | 0 | 0 | 0 | 0 | 0 | 25624.44
2022032511 | 6 | 0.51425 | 41140 | 0.03527 | 1269.72 | 0.85777 | 10293.24 | 1 | 5000 | 1269.72 | 10293.24 | 0 | 0 | 0 | 0 | 24577.04 | 0 | 0 | 0 | 0 | 0 | 24577.04
2022032512 | 6 | 0.50685 | 40548 | 0.05162 | 1858.32 | 0.86333 | 10359.96 | 1 | 5000 | 1858.32 | 10359.96 | 0 | 0 | 0 | 0 | 23329.72 | 0 | 0 | 0 | 0 | 0 | 23329.72
2022032513 | 6 | 0.5028 | 40224 | 0.04768 | 1716.48 | 0.86032 | 10323.84 | 1 | 5000 | 1716.48 | 10323.84 | 0 | 0 | 0 | 0 | 23183.68 | 0 | 0 | 0 | 0 | 0 | 23183.68
2022032514 | 6 | 0.51038 | 40830.4 | 0.0298 | 1072.8 | 0.85298 | 10235.76 | 1 | 5000 | 1072.8 | 10235.76 | 0 | 0 | 0 | 0 | 24521.84 | 0 | 0 | 0 | 0 | 0 | 24521.84
2022032515 | 6 | 0.52072 | 41657.6 | 0.0431 | 1551.6 | 0.85569 | 10268.28 | 1 | 5000 | 1551.6 | 10268.28 | 0 | 0 | 0 | 0 | 24837.72 | 0 | 0 | 0 | 0 | 0 | 24837.72
2022032516 | 6 | 0.53341 | 42672.8 | 0.06831 | 2459.16 | 0.85707 | 10284.84 | 1 | 5000 | 2459.16 | 10284.84 | 0 | 0 | 0 | 0 | 24928.8 | 0 | 0 | 0 | 0 | 0 | 24928.8
2022032517 | 6 | 0.54805 | 43844 | 0.10122 | 3643.92 | 0.85146 | 10217.52 | 1 | 5000 | 3643.92 | 10217.52 | 0 | 0 | 0 | 0 | 24982.56 | 0 | 0 | 0 | 0 | 0 | 24982.56
2022032518 | 6 | 0.55863 | 44690.4 | 0.14642 | 5271.12 | 0.81981 | 9837.72 | 1 | 5000 | 5271.12 | 9837.72 | 0 | 0 | 0 | 0 | 24581.56 | 0 | 0 | 0 | 0 | 0 | 24581.56
2022032519 | 6 | 0.55556 | 44444.8 | 0.15573 | 5606.28 | 0.60583 | 7269.96 | 1 | 5000 | 5606.28 | 7269.96 | 0 | 0 | 0 | 0 | 26568.56 | 0 | 0 | 0 | 0 | 0 | 26568.56
2022032520 | 6 | 0.54373 | 43498.4 | 0.18333 | 6599.88 | 0.12997 | 1559.64 | 1 | 5000 | 6599.88 | 1559.64 | 0 | 0 | 0 | 0 | 30338.88 | 0 | 0 | 0 | 0 | 0 | 30338.88
2022032521 | 6 | 0.53663 | 42930.4 | 0.28394 | 10221.84 | 0.0002 | 2.4 | 1 | 5000 | 10221.84 | 2.4 | 0 | 0 | 0 | 0 | 27706.16 | 0 | 0 | 0 | 0 | 0 | 27706.16
2022032522 | 6 | 0.51793 | 41434.4 | 0.38311 | 13791.96 | 0 | 0 | 1 | 5000 | 13791.96 | 0 | 0 | 0 | 0 | 0 | 22642.44 | 0 | 0 | 0 | 0 | 0 | 22642.44
2022032523 | 6 | 0.49226 | 39380.8 | 0.43492 | 15657.12 | 0 | 0 | 1 | 5000 | 15657.12 | 0 | 0 | 0 | 0 | 0 | 18723.68 | 0 | 0 | 0 | 0 | 0 | 18723.68
2022032524 | 6 | 0.4646 | 37168 | 0.48873 | 17594.28 | 0 | 0 | 1 | 5000 | 17594.28 | 0 | 0 | 0 | 0 | 0 | 14573.72 | 0 | 0 | 0 | 0 | 0 | 14573.72
2022032601 | 7 | 0.44092 | 35273.6 | 0.55296 | 19906.56 | 0 | 0 | 1 | 5000 | 19906.56 | 0 | 0 | 0 | 0 | 0 | 10367.04 | 0 | 0 | 0 | 0 | 0 | 10367.04
2022032602 | 7 | 0.42287 | 33829.6 | 0.53929 | 19414.44 | 0 | 0 | 1 | 5000 | 19414.44 | 0 | 0 | 0 | 0 | 0 | 9415.16 | 0 | 0 | 0 | 0 | 0 | 9415.16
2022032603 | 7 | 0.41123 | 32898.4 | 0.49209 | 17715.24 | 0 | 0 | 1 | 5000 | 17715.24 | 0 | 0 | 0 | 0 | 0 | 10183.16 | 0 | 0 | 0 | 0 | 0 | 10183.16
2022032604 | 7 | 0.40401 | 32320.8 | 0.42864 | 15431.04 | 0 | 0 | 1 | 5000 | 15431.04 | 0 | 0 | 0 | 0 | 0 | 11889.76 | 0 | 0 | 0 | 0 | 0 | 11889.76
2022032605 | 7 | 0.40507 | 32405.6 | 0.36827 | 13257.72 | 0 | 0 | 1 | 5000 | 13257.72 | 0 | 0 | 0 | 0 | 0 | 14147.88 | 0 | 0 | 0 | 0 | 0 | 14147.88
2022032606 | 7 | 0.41383 | 33106.4 | 0.38145 | 13732.2 | 0 | 0 | 1 | 5000 | 13732.2 | 0 | 0 | 0 | 0 | 0 | 14374.2 | 0 | 0 | 0 | 0 | 0 | 14374.2
2022032607 | 7 | 0.43036 | 34428.8 | 0.37677 | 13563.72 | 0 | 0 | 1 | 5000 | 13563.72 | 0 | 0 | 0 | 0 | 0 | 15865.08 | 0 | 0 | 0 | 0 | 0 | 15865.08
2022032608 | 7 | 0.44971 | 35976.8 | 0.35447 | 12760.92 | 0.00773 | 92.76 | 1 | 5000 | 12760.92 | 92.76 | 0 | 0 | 0 | 0 | 18123.12 | 0 | 0 | 0 | 0 | 0 | 18123.12
2022032609 | 7 | 0.46546 | 37236.8 | 0.30728 | 11062.08 | 0.3035 | 3642 | 1 | 5000 | 11062.08 | 3642 | 0 | 0 | 0 | 0 | 17532.72 | 0 | 0 | 0 | 0 | 0 | 17532.72
2022032610 | 7 | 0.47366 | 37892.8 | 0.20516 | 7385.76 | 0.78778 | 9453.36 | 1 | 5000 | 7385.76 | 9453.36 | 0 | 0 | 0 | 0 | 16053.68 | 0 | 0 | 0 | 0 | 0 | 16053.68
2022032611 | 7 | 0.48002 | 38401.6 | 0.18269 | 6576.84 | 0.87118 | 10454.16 | 1 | 5000 | 6576.84 | 10454.16 | 0 | 0 | 0 | 0 | 16370.6 | 0 | 0 | 0 | 0 | 0 | 16370.6
2022032612 | 7 | 0.48663 | 38930.4 | 0.19355 | 6967.8 | 0.87225 | 10467 | 1 | 5000 | 6967.8 | 10467 | 0 | 0 | 0 | 0 | 16495.6 | 0 | 0 | 0 | 0 | 0 | 16495.6
2022032613 | 7 | 0.49427 | 39541.6 | 0.17551 | 6318.36 | 0.87004 | 10440.48 | 1 | 5000 | 6318.36 | 10440.48 | 0 | 0 | 0 | 0 | 17782.76 | 0 | 0 | 0 | 0 | 0 | 17782.76
2022032614 | 7 | 0.50529 | 40423.2 | 0.15695 | 5650.2 | 0.868 | 10416 | 1 | 5000 | 5650.2 | 10416 | 0 | 0 | 0 | 0 | 19357 | 0 | 0 | 0 | 0 | 0 | 19357
2022032615 | 7 | 0.52308 | 41846.4 | 0.13779 | 4960.44 | 0.86383 | 10365.96 | 1 | 5000 | 4960.44 | 10365.96 | 0 | 0 | 0 | 0 | 21520 | 0 | 0 | 0 | 0 | 0 | 21520
2022032616 | 7 | 0.54431 | 43544.8 | 0.13462 | 4846.32 | 0.85931 | 10311.72 | 1 | 5000 | 4846.32 | 10311.72 | 0 | 0 | 0 | 0 | 23386.76 | 0 | 0 | 0 | 0 | 0 | 23386.76
2022032617 | 7 | 0.56316 | 45052.8 | 0.14831 | 5339.16 | 0.84616 | 10153.92 | 1 | 5000 | 5339.16 | 10153.92 | 0 | 0 | 0 | 0 | 24559.72 | 0 | 0 | 0 | 0 | 0 | 24559.72
2022032618 | 7 | 0.57364 | 45891.2 | 0.17316 | 6233.76 | 0.78884 | 9466.08 | 1 | 5000 | 6233.76 | 9466.08 | 0 | 0 | 0 | 0 | 25191.36 | 0 | 0 | 0 | 0 | 0 | 25191.36
2022032619 | 7 | 0.57028 | 45622.4 | 0.20325 | 7317 | 0.58448 | 7013.76 | 1 | 5000 | 7317 | 7013.76 | 0 | 0 | 0 | 0 | 26291.64 | 0 | 0 | 0 | 0 | 0 | 26291.64
2022032620 | 7 | 0.55102 | 44081.6 | 0.23584 | 8490.24 | 0.11432 | 1371.84 | 1 | 5000 | 8490.24 | 1371.84 | 0 | 0 | 0 | 0 | 29219.52 | 0 | 0 | 0 | 0 | 0 | 29219.52
2022032621 | 7 | 0.5459 | 43672 | 0.31895 | 11482.2 | 0.00013 | 1.56 | 1 | 5000 | 11482.2 | 1.56 | 0 | 0 | 0 | 0 | 27188.24 | 0 | 0 | 0 | 0 | 0 | 27188.24
2022032622 | 7 | 0.52648 | 42118.4 | 0.42775 | 15399 | 0 | 0 | 1 | 5000 | 15399 | 0 | 0 | 0 | 0 | 0 | 21719.4 | 0 | 0 | 0 | 0 | 0 | 21719.4
2022032623 | 7 | 0.50199 | 40159.2 | 0.51117 | 18402.12 | 0 | 0 | 1 | 5000 | 18402.12 | 0 | 0 | 0 | 0 | 0 | 16757.08 | 0 | 0 | 0 | 0 | 0 | 16757.08
2022032624 | 7 | 0.47517 | 38013.6 | 0.55671 | 20041.56 | 0 | 0 | 1 | 5000 | 20041.56 | 0 | 0 | 0 | 0 | 0 | 12972.04 | 0 | 0 | 0 | 0 | 0 | 12972.04
2022032701 | 1 | 0.44954 | 35963.2 | 0.56748 | 20429.28 | 0 | 0 | 1 | 5000 | 20429.28 | 0 | 0 | 0 | 0 | 0 | 10533.92 | 0 | 0 | 0 | 0 | 0 | 10533.92
2022032702 | 1 | 0.42826 | 34260.8 | 0.55586 | 20010.96 | 0 | 0 | 1 | 5000 | 20010.96 | 0 | 0 | 0 | 0 | 0 | 9249.84 | 0 | 0 | 0 | 0 | 0 | 9249.84
2022032703 | 1 | 0.41511 | 33208.8 | 0.56014 | 20165.04 | 0 | 0 | 1 | 5000 | 20165.04 | 0 | 0 | 0 | 0 | 0 | 8043.76 | 0 | 0 | 0 | 0 | 0 | 8043.76
2022032704 | 1 | 0.40753 | 32602.4 | 0.57231 | 20603.16 | 0 | 0 | 1 | 5000 | 20603.16 | 0 | 0 | 0 | 0 | 0 | 6999.24 | 0 | 0 | 0 | 0 | 0 | 6999.24
2022032705 | 1 | 0.4051 | 32408 | 0.57194 | 20589.84 | 0 | 0 | 1 | 5000 | 20589.84 | 0 | 0 | 0 | 0 | 0 | 6818.16 | 0 | 0 | 0 | 0 | 0 | 6818.16
2022032706 | 1 | 0.40782 | 32625.6 | 0.57424 | 20672.64 | 0 | 0 | 1 | 5000 | 20672.64 | 0 | 0 | 0 | 0 | 0 | 6952.96 | 0 | 0 | 0 | 0 | 0 | 6952.96
2022032707 | 1 | 0.41437 | 33149.6 | 0.57809 | 20811.24 | 0 | 0 | 1 | 5000 | 20811.24 | 0 | 0 | 0 | 0 | 0 | 7338.36 | 0 | 0 | 0 | 0 | 0 | 7338.36
2022032708 | 1 | 0.42371 | 33896.8 | 0.56836 | 20460.96 | 0.0087 | 104.4 | 1 | 5000 | 20460.96 | 104.4 | 0 | 0 | 0 | 0 | 8331.44 | 0 | 0 | 0 | 0 | 0 | 8331.44
2022032709 | 1 | 0.44063 | 35250.4 | 0.53571 | 19285.56 | 0.24622 | 2954.64 | 1 | 5000 | 19285.56 | 2954.64 | 0 | 0 | 0 | 0 | 8010.2 | 0 | 0 | 0 | 0 | 0 | 8010.2
2022032710 | 1 | 0.45928 | 36742.4 | 0.45558 | 16400.88 | 0.64035 | 7684.2 | 1 | 5000 | 16400.88 | 7684.2 | 0 | 0 | 0 | 0 | 7657.32 | 0 | 0 | 0 | 0 | 0 | 7657.32
2022032711 | 1 | 0.47333 | 37866.4 | 0.43922 | 15811.92 | 0.70482 | 8457.84 | 1 | 5000 | 15811.92 | 8457.84 | 0 | 0 | 0 | 0 | 8596.64 | 0 | 0 | 0 | 0 | 0 | 8596.64
2022032712 | 1 | 0.4881 | 39048 | 0.4212 | 15163.2 | 0.76013 | 9121.56 | 1 | 5000 | 15163.2 | 9121.56 | 0 | 0 | 0 | 0 | 9763.24 | 0 | 0 | 0 | 0 | 0 | 9763.24
2022032713 | 1 | 0.5057 | 40456 | 0.40428 | 14554.08 | 0.7949 | 9538.8 | 1 | 5000 | 14554.08 | 9538.8 | 0 | 0 | 0 | 0 | 11363.12 | 0 | 0 | 0 | 0 | 0 | 11363.12
2022032714 | 1 | 0.52447 | 41957.6 | 0.36378 | 13096.08 | 0.83323 | 9998.76 | 1 | 5000 | 13096.08 | 9998.76 | 0 | 0 | 0 | 0 | 13862.76 | 0 | 0 | 0 | 0 | 0 | 13862.76
2022032715 | 1 | 0.5464 | 43712 | 0.34317 | 12354.12 | 0.84281 | 10113.72 | 1 | 5000 | 12354.12 | 10113.72 | 0 | 0 | 0 | 0 | 16244.16 | 0 | 0 | 0 | 0 | 0 | 16244.16
2022032716 | 1 | 0.56995 | 45596 | 0.34309 | 12351.24 | 0.84061 | 10087.32 | 1 | 5000 | 12351.24 | 10087.32 | 0 | 0 | 0 | 0 | 18157.44 | 0 | 0 | 0 | 0 | 0 | 18157.44
2022032717 | 1 | 0.59199 | 47359.2 | 0.35608 | 12818.88 | 0.80698 | 9683.76 | 1 | 5000 | 12818.88 | 9683.76 | 0 | 0 | 0 | 0 | 19856.56 | 0 | 0 | 0 | 0 | 0 | 19856.56
2022032718 | 1 | 0.60643 | 48514.4 | 0.37764 | 13595.04 | 0.74765 | 8971.8 | 1 | 5000 | 13595.04 | 8971.8 | 0 | 0 | 0 | 0 | 20947.56 | 0 | 0 | 0 | 0 | 0 | 20947.56
2022032719 | 1 | 0.60261 | 48208.8 | 0.43335 | 15600.6 | 0.46523 | 5582.76 | 1 | 5000 | 15600.6 | 5582.76 | 0 | 0 | 0 | 0 | 22025.44 | 0 | 0 | 0 | 0 | 0 | 22025.44
2022032720 | 1 | 0.58849 | 47079.2 | 0.48001 | 17280.36 | 0.08411 | 1009.32 | 1 | 5000 | 17280.36 | 1009.32 | 0 | 0 | 0 | 0 | 23789.52 | 0 | 0 | 0 | 0 | 0 | 23789.52
2022032721 | 1 | 0.58616 | 46892.8 | 0.58043 | 20895.48 | 0.00029 | 3.48 | 1 | 5000 | 20895.48 | 3.48 | 0 | 0 | 0 | 0 | 20993.84 | 0 | 0 | 0 | 0 | 0 | 20993.84
2022032722 | 1 | 0.56639 | 45311.2 | 0.65529 | 23590.44 | 0 | 0 | 1 | 5000 | 23590.44 | 0 | 0 | 0 | 0 | 0 | 16720.76 | 0 | 0 | 0 | 0 | 0 | 16720.76
2022032723 | 1 | 0.53157 | 42525.6 | 0.66288 | 23863.68 | 0 | 0 | 1 | 5000 | 23863.68 | 0 | 0 | 0 | 0 | 0 | 13661.92 | 0 | 0 | 0 | 0 | 0 | 13661.92
2022032724 | 1 | 0.49091 | 39272.8 | 0.64494 | 23217.84 | 0 | 0 | 1 | 5000 | 23217.84 | 0 | 0 | 0 | 0 | 0 | 11054.96 | 0 | 0 | 0 | 0 | 0 | 11054.96
2022032801 | 2 | 0.4569 | 36552 | 0.6261 | 22539.6 | 0 | 0 | 1 | 5000 | 22539.6 | 0 | 0 | 0 | 0 | 0 | 9012.4 | 0 | 0 | 0 | 0 | 0 | 9012.4
2022032802 | 2 | 0.43555 | 34844 | 0.604 | 21744 | 0 | 0 | 1 | 5000 | 21744 | 0 | 0 | 0 | 0 | 0 | 8100 | 0 | 0 | 0 | 0 | 0 | 8100
2022032803 | 2 | 0.42268 | 33814.4 | 0.59513 | 21424.68 | 0 | 0 | 1 | 5000 | 21424.68 | 0 | 0 | 0 | 0 | 0 | 7389.72 | 0 | 0 | 0 | 0 | 0 | 7389.72
2022032804 | 2 | 0.41675 | 33340 | 0.57742 | 20787.12 | 0 | 0 | 1 | 5000 | 20787.12 | 0 | 0 | 0 | 0 | 0 | 7552.88 | 0 | 0 | 0 | 0 | 0 | 7552.88
2022032805 | 2 | 0.41915 | 33532 | 0.55649 | 20033.64 | 0 | 0 | 1 | 5000 | 20033.64 | 0 | 0 | 0 | 0 | 0 | 8498.36 | 0 | 0 | 0 | 0 | 0 | 8498.36
2022032806 | 2 | 0.43694 | 34955.2 | 0.55964 | 20147.04 | 0 | 0 | 1 | 5000 | 20147.04 | 0 | 0 | 0 | 0 | 0 | 9808.16 | 0 | 0 | 0 | 0 | 0 | 9808.16
2022032807 | 2 | 0.47188 | 37750.4 | 0.54502 | 19620.72 | 0 | 0 | 1 | 5000 | 19620.72 | 0 | 0 | 0 | 0 | 0 | 13129.68 | 0 | 0 | 0 | 0 | 0 | 13129.68
2022032808 | 2 | 0.48801 | 39040.8 | 0.52572 | 18925.92 | 0.00709 | 85.08 | 1 | 5000 | 18925.92 | 85.08 | 0 | 0 | 0 | 0 | 15029.8 | 0 | 0 | 0 | 0 | 0 | 15029.8
2022032809 | 2 | 0.49253 | 39402.4 | 0.48201 | 17352.36 | 0.26011 | 3121.32 | 1 | 5000 | 17352.36 | 3121.32 | 0 | 0 | 0 | 0 | 13928.72 | 0 | 0 | 0 | 0 | 0 | 13928.72
2022032810 | 2 | 0.50643 | 40514.4 | 0.44828 | 16138.08 | 0.62446 | 7493.52 | 1 | 5000 | 16138.08 | 7493.52 | 0 | 0 | 0 | 0 | 11882.8 | 0 | 0 | 0 | 0 | 0 | 11882.8
2022032811 | 2 | 0.52222 | 41777.6 | 0.44252 | 15930.72 | 0.71296 | 8555.52 | 1 | 5000 | 15930.72 | 8555.52 | 0 | 0 | 0 | 0 | 12291.36 | 0 | 0 | 0 | 0 | 0 | 12291.36
2022032812 | 2 | 0.53603 | 42882.4 | 0.42249 | 15209.64 | 0.74942 | 8993.04 | 1 | 5000 | 15209.64 | 8993.04 | 0 | 0 | 0 | 0 | 13679.72 | 0 | 0 | 0 | 0 | 0 | 13679.72
2022032813 | 2 | 0.55186 | 44148.8 | 0.39165 | 14099.4 | 0.77769 | 9332.28 | 1 | 5000 | 14099.4 | 9332.28 | 0 | 0 | 0 | 0 | 15717.12 | 0 | 0 | 0 | 0 | 0 | 15717.12
2022032814 | 2 | 0.57157 | 45725.6 | 0.38464 | 13847.04 | 0.77575 | 9309 | 1 | 5000 | 13847.04 | 9309 | 0 | 0 | 0 | 0 | 17569.56 | 0 | 0 | 0 | 0 | 0 | 17569.56
2022032815 | 2 | 0.59272 | 47417.6 | 0.40971 | 14749.56 | 0.74702 | 8964.24 | 1 | 5000 | 14749.56 | 8964.24 | 0 | 0 | 0 | 0 | 18703.8 | 0 | 0 | 0 | 0 | 0 | 18703.8
2022032816 | 2 | 0.61368 | 49094.4 | 0.47547 | 17116.92 | 0.67126 | 8055.12 | 1 | 5000 | 17116.92 | 8055.12 | 0 | 0 | 0 | 0 | 18922.36 | 0 | 0 | 0 | 0 | 0 | 18922.36
2022032817 | 2 | 0.63119 | 50495.2 | 0.51484 | 18534.24 | 0.5906 | 7087.2 | 1 | 5000 | 18534.24 | 7087.2 | 0 | 0 | 0 | 0 | 19873.76 | 0 | 0 | 0 | 0 | 0 | 19873.76
2022032818 | 2 | 0.63729 | 50983.2 | 0.53649 | 19313.64 | 0.47545 | 5705.4 | 1 | 5000 | 19313.64 | 5705.4 | 0 | 0 | 0 | 0 | 20964.16 | 0 | 0 | 0 | 0 | 0 | 20964.16
2022032819 | 2 | 0.62576 | 50060.8 | 0.56629 | 20386.44 | 0.29104 | 3492.48 | 1 | 5000 | 20386.44 | 3492.48 | 0 | 0 | 0 | 0 | 21181.88 | 0 | 0 | 0 | 0 | 0 | 21181.88
2022032820 | 2 | 0.60808 | 48646.4 | 0.57547 | 20716.92 | 0.03506 | 420.72 | 1 | 5000 | 20716.92 | 420.72 | 0 | 0 | 0 | 0 | 22508.76 | 0 | 0 | 0 | 0 | 0 | 22508.76
2022032821 | 2 | 0.60573 | 48458.4 | 0.61872 | 22273.92 | 6e-05 | 0.72 | 1 | 5000 | 22273.92 | 0.72 | 0 | 0 | 0 | 0 | 21183.76 | 0 | 0 | 0 | 0 | 0 | 21183.76
2022032822 | 2 | 0.58506 | 46804.8 | 0.66528 | 23950.08 | 0 | 0 | 1 | 5000 | 23950.08 | 0 | 0 | 0 | 0 | 0 | 17854.72 | 0 | 0 | 0 | 0 | 0 | 17854.72
2022032823 | 2 | 0.54898 | 43918.4 | 0.67199 | 24191.64 | 0 | 0 | 1 | 5000 | 24191.64 | 0 | 0 | 0 | 0 | 0 | 14726.76 | 0 | 0 | 0 | 0 | 0 | 14726.76
2022032824 | 2 | 0.50951 | 40760.8 | 0.67919 | 24450.84 | 0 | 0 | 1 | 5000 | 24450.84 | 0 | 0 | 0 | 0 | 0 | 11309.96 | 0 | 0 | 0 | 0 | 0 | 11309.96
2022032901 | 3 | 0.47964 | 38371.2 | 0.68567 | 24684.12 | 0 | 0 | 1 | 5000 | 24684.12 | 0 | 0 | 0 | 0 | 0 | 8687.08 | 0 | 0 | 0 | 0 | 0 | 8687.08
2022032902 | 3 | 0.45978 | 36782.4 | 0.67452 | 24282.72 | 0 | 0 | 1 | 5000 | 24282.72 | 0 | 0 | 0 | 0 | 0 | 7499.68 | 0 | 0 | 0 | 0 | 0 | 7499.68
2022032903 | 3 | 0.446 | 35680 | 0.66404 | 23905.44 | 0 | 0 | 1 | 5000 | 23905.44 | 0 | 0 | 0 | 0 | 0 | 6774.56 | 0 | 0 | 0 | 0 | 0 | 6774.56
2022032904 | 3 | 0.44017 | 35213.6 | 0.65986 | 23754.96 | 0 | 0 | 1 | 5000 | 23754.96 | 0 | 0 | 0 | 0 | 0 | 6458.64 | 0 | 0 | 0 | 0 | 0 | 6458.64
2022032905 | 3 | 0.44358 | 35486.4 | 0.66017 | 23766.12 | 0 | 0 | 1 | 5000 | 23766.12 | 0 | 0 | 0 | 0 | 0 | 6720.28 | 0 | 0 | 0 | 0 | 0 | 6720.28
2022032906 | 3 | 0.46326 | 37060.8 | 0.66586 | 23970.96 | 0 | 0 | 1 | 5000 | 23970.96 | 0 | 0 | 0 | 0 | 0 | 8089.84 | 0 | 0 | 0 | 0 | 0 | 8089.84
2022032907 | 3 | 0.50016 | 40012.8 | 0.66729 | 24022.44 | 0 | 0 | 1 | 5000 | 24022.44 | 0 | 0 | 0 | 0 | 0 | 10990.36 | 0 | 0 | 0 | 0 | 0 | 10990.36
2022032908 | 3 | 0.51725 | 41380 | 0.66425 | 23913 | 0.00162 | 19.44 | 1 | 5000 | 23913 | 19.44 | 0 | 0 | 0 | 0 | 12447.56 | 0 | 0 | 0 | 0 | 0 | 12447.56
2022032909 | 3 | 0.52303 | 41842.4 | 0.64628 | 23266.08 | 0.13036 | 1564.32 | 1 | 5000 | 23266.08 | 1564.32 | 0 | 0 | 0 | 0 | 12012 | 0 | 0 | 0 | 0 | 0 | 12012
2022032910 | 3 | 0.53458 | 42766.4 | 0.61944 | 22299.84 | 0.31275 | 3753 | 1 | 5000 | 22299.84 | 3753 | 0 | 0 | 0 | 0 | 11713.56 | 0 | 0 | 0 | 0 | 0 | 11713.56
2022032911 | 3 | 0.55036 | 44028.8 | 0.64077 | 23067.72 | 0.29161 | 3499.32 | 1 | 5000 | 23067.72 | 3499.32 | 0 | 0 | 0 | 0 | 12461.76 | 0 | 0 | 0 | 0 | 0 | 12461.76
2022032912 | 3 | 0.56522 | 45217.6 | 0.64703 | 23293.08 | 0.29884 | 3586.08 | 1 | 5000 | 23293.08 | 3586.08 | 0 | 0 | 0 | 0 | 13338.44 | 0 | 0 | 0 | 0 | 0 | 13338.44
2022032913 | 3 | 0.57861 | 46288.8 | 0.63787 | 22963.32 | 0.31411 | 3769.32 | 1 | 5000 | 22963.32 | 3769.32 | 0 | 0 | 0 | 0 | 14556.16 | 0 | 0 | 0 | 0 | 0 | 14556.16
2022032914 | 3 | 0.59003 | 47202.4 | 0.63561 | 22881.96 | 0.32265 | 3871.8 | 1 | 5000 | 22881.96 | 3871.8 | 0 | 0 | 0 | 0 | 15448.64 | 0 | 0 | 0 | 0 | 0 | 15448.64
2022032915 | 3 | 0.6016 | 48128 | 0.64322 | 23155.92 | 0.31727 | 3807.24 | 1 | 5000 | 23155.92 | 3807.24 | 0 | 0 | 0 | 0 | 16164.84 | 0 | 0 | 0 | 0 | 0 | 16164.84
2022032916 | 3 | 0.60872 | 48697.6 | 0.65432 | 23555.52 | 0.27131 | 3255.72 | 1 | 5000 | 23555.52 | 3255.72 | 0 | 0 | 0 | 0 | 16886.36 | 0 | 0 | 0 | 0 | 0 | 16886.36
2022032917 | 3 | 0.61347 | 49077.6 | 0.65617 | 23622.12 | 0.25932 | 3111.84 | 1 | 5000 | 23622.12 | 3111.84 | 0 | 0 | 0 | 0 | 17343.64 | 0 | 0 | 0 | 0 | 0 | 17343.64
2022032918 | 3 | 0.61215 | 48972 | 0.66548 | 23957.28 | 0.22196 | 2663.52 | 1 | 5000 | 23957.28 | 2663.52 | 0 | 0 | 0 | 0 | 17351.2 | 0 | 0 | 0 | 0 | 0 | 17351.2
2022032919 | 3 | 0.59901 | 47920.8 | 0.67249 | 24209.64 | 0.1474 | 1768.8 | 1 | 5000 | 24209.64 | 1768.8 | 0 | 0 | 0 | 0 | 16942.36 | 0 | 0 | 0 | 0 | 0 | 16942.36
2022032920 | 3 | 0.59523 | 47618.4 | 0.68044 | 24495.84 | 0.03635 | 436.2 | 1 | 5000 | 24495.84 | 436.2 | 0 | 0 | 0 | 0 | 17686.36 | 0 | 0 | 0 | 0 | 0 | 17686.36
2022032921 | 3 | 0.60137 | 48109.6 | 0.69816 | 25133.76 | 0.00014 | 1.68 | 1 | 5000 | 25133.76 | 1.68 | 0 | 0 | 0 | 0 | 17974.16 | 0 | 0 | 0 | 0 | 0 | 17974.16
2022032922 | 3 | 0.58642 | 46913.6 | 0.66843 | 24063.48 | 0 | 0 | 1 | 5000 | 24063.48 | 0 | 0 | 0 | 0 | 0 | 17850.12 | 0 | 0 | 0 | 0 | 0 | 17850.12
2022032923 | 3 | 0.55481 | 44384.8 | 0.63888 | 22999.68 | 0 | 0 | 1 | 5000 | 22999.68 | 0 | 0 | 0 | 0 | 0 | 16385.12 | 0 | 0 | 0 | 0 | 0 | 16385.12
2022032924 | 3 | 0.51911 | 41528.8 | 0.60925 | 21933 | 0 | 0 | 1 | 5000 | 21933 | 0 | 0 | 0 | 0 | 0 | 14595.8 | 0 | 0 | 0 | 0 | 0 | 14595.8
2022033001 | 4 | 0.4878 | 39024 | 0.56182 | 20225.52 | 0 | 0 | 1 | 5000 | 20225.52 | 0 | 0 | 0 | 0 | 0 | 13798.48 | 0 | 0 | 0 | 0 | 0 | 13798.48
2022033002 | 4 | 0.46798 | 37438.4 | 0.50822 | 18295.92 | 0 | 0 | 1 | 5000 | 18295.92 | 0 | 0 | 0 | 0 | 0 | 14142.48 | 0 | 0 | 0 | 0 | 0 | 14142.48
2022033003 | 4 | 0.45794 | 36635.2 | 0.54294 | 19545.84 | 0 | 0 | 1 | 5000 | 19545.84 | 0 | 0 | 0 | 0 | 0 | 12089.36 | 0 | 0 | 0 | 0 | 0 | 12089.36
2022033004 | 4 | 0.45121 | 36096.8 | 0.55612 | 20020.32 | 0 | 0 | 1 | 5000 | 20020.32 | 0 | 0 | 0 | 0 | 0 | 11076.48 | 0 | 0 | 0 | 0 | 0 | 11076.48
2022033005 | 4 | 0.45346 | 36276.8 | 0.59339 | 21362.04 | 0 | 0 | 1 | 5000 | 21362.04 | 0 | 0 | 0 | 0 | 0 | 9914.76 | 0 | 0 | 0 | 0 | 0 | 9914.76
2022033006 | 4 | 0.46937 | 37549.6 | 0.5974 | 21506.4 | 0 | 0 | 1 | 5000 | 21506.4 | 0 | 0 | 0 | 0 | 0 | 11043.2 | 0 | 0 | 0 | 0 | 0 | 11043.2
2022033007 | 4 | 0.49901 | 39920.8 | 0.59085 | 21270.6 | 0 | 0 | 1 | 5000 | 21270.6 | 0 | 0 | 0 | 0 | 0 | 13650.2 | 0 | 0 | 0 | 0 | 0 | 13650.2
2022033008 | 4 | 0.51686 | 41348.8 | 0.58199 | 20951.64 | 0.00249 | 29.88 | 1 | 5000 | 20951.64 | 29.88 | 0 | 0 | 0 | 0 | 15367.28 | 0 | 0 | 0 | 0 | 0 | 15367.28
2022033009 | 4 | 0.51956 | 41564.8 | 0.60973 | 21950.28 | 0.06782 | 813.84 | 1 | 5000 | 21950.28 | 813.84 | 0 | 0 | 0 | 0 | 13800.68 | 0 | 0 | 0 | 0 | 0 | 13800.68
2022033010 | 4 | 0.52553 | 42042.4 | 0.61818 | 22254.48 | 0.11648 | 1397.76 | 1 | 5000 | 22254.48 | 1397.76 | 0 | 0 | 0 | 0 | 13390.16 | 0 | 0 | 0 | 0 | 0 | 13390.16
2022033011 | 4 | 0.52989 | 42391.2 | 0.64634 | 23268.24 | 0.18849 | 2261.88 | 1 | 5000 | 23268.24 | 2261.88 | 0 | 0 | 0 | 0 | 11861.08 | 0 | 0 | 0 | 0 | 0 | 11861.08
2022033012 | 4 | 0.52995 | 42396 | 0.65933 | 23735.88 | 0.23744 | 2849.28 | 1 | 5000 | 23735.88 | 2849.28 | 0 | 0 | 0 | 0 | 10810.84 | 0 | 0 | 0 | 0 | 0 | 10810.84
2022033013 | 4 | 0.53606 | 42884.8 | 0.65788 | 23683.68 | 0.28495 | 3419.4 | 1 | 5000 | 23683.68 | 3419.4 | 0 | 0 | 0 | 0 | 10781.72 | 0 | 0 | 0 | 0 | 0 | 10781.72
2022033014 | 4 | 0.54634 | 43707.2 | 0.64837 | 23341.32 | 0.31555 | 3786.6 | 1 | 5000 | 23341.32 | 3786.6 | 0 | 0 | 0 | 0 | 11579.28 | 0 | 0 | 0 | 0 | 0 | 11579.28
2022033015 | 4 | 0.55407 | 44325.6 | 0.61246 | 22048.56 | 0.36636 | 4396.32 | 1 | 5000 | 22048.56 | 4396.32 | 0 | 0 | 0 | 0 | 12880.72 | 0 | 0 | 0 | 0 | 0 | 12880.72
2022033016 | 4 | 0.56114 | 44891.2 | 0.55526 | 19989.36 | 0.42505 | 5100.6 | 1 | 5000 | 19989.36 | 5100.6 | 0 | 0 | 0 | 0 | 14801.24 | 0 | 0 | 0 | 0 | 0 | 14801.24
2022033017 | 4 | 0.56928 | 45542.4 | 0.48716 | 17537.76 | 0.48902 | 5868.24 | 1 | 5000 | 17537.76 | 5868.24 | 0 | 0 | 0 | 0 | 17136.4 | 0 | 0 | 0 | 0 | 0 | 17136.4
2022033018 | 4 | 0.57265 | 45812 | 0.41248 | 14849.28 | 0.59399 | 7127.88 | 1 | 5000 | 14849.28 | 7127.88 | 0 | 0 | 0 | 0 | 18834.84 | 0 | 0 | 0 | 0 | 0 | 18834.84
2022033019 | 4 | 0.56343 | 45074.4 | 0.32302 | 11628.72 | 0.45048 | 5405.76 | 1 | 5000 | 11628.72 | 5405.76 | 0 | 0 | 0 | 0 | 23039.92 | 0 | 0 | 0 | 0 | 0 | 23039.92
2022033020 | 4 | 0.55171 | 44136.8 | 0.20479 | 7372.44 | 0.1018 | 1221.6 | 1 | 5000 | 7372.44 | 1221.6 | 0 | 0 | 0 | 0 | 30542.76 | 0 | 0 | 0 | 0 | 0 | 30542.76
2022033021 | 4 | 0.55381 | 44304.8 | 0.1534 | 5522.4 | 0.00018 | 2.16 | 1 | 5000 | 5522.4 | 2.16 | 0 | 0 | 0 | 0 | 33780.24 | 0 | 0 | 0 | 0 | 0 | 33780.24
2022033022 | 4 | 0.53488 | 42790.4 | 0.17547 | 6316.92 | 0 | 0 | 1 | 5000 | 6316.92 | 0 | 0 | 0 | 0 | 0 | 31473.48 | 0 | 0 | 0 | 0 | 0 | 31473.48
2022033023 | 4 | 0.50095 | 40076 | 0.21331 | 7679.16 | 0 | 0 | 1 | 5000 | 7679.16 | 0 | 0 | 0 | 0 | 0 | 27396.84 | 0 | 0 | 0 | 0 | 0 | 27396.84
2022033024 | 4 | 0.46318 | 37054.4 | 0.23257 | 8372.52 | 0 | 0 | 1 | 5000 | 8372.52 | 0 | 0 | 0 | 0 | 0 | 23681.88 | 0 | 0 | 0 | 0 | 0 | 23681.88
2022033101 | 5 | 0.43704 | 34963.2 | 0.23694 | 8529.84 | 0 | 0 | 1 | 5000 | 8529.84 | 0 | 0 | 0 | 0 | 0 | 21433.36 | 0 | 0 | 0 | 0 | 0 | 21433.36
2022033102 | 5 | 0.42279 | 33823.2 | 0.18355 | 6607.8 | 0 | 0 | 1 | 5000 | 6607.8 | 0 | 0 | 0 | 0 | 0 | 22215.4 | 0 | 0 | 0 | 0 | 0 | 22215.4
2022033103 | 5 | 0.41399 | 33119.2 | 0.19459 | 7005.24 | 0 | 0 | 1 | 5000 | 7005.24 | 0 | 0 | 0 | 0 | 0 | 21113.96 | 0 | 0 | 0 | 0 | 0 | 21113.96
2022033104 | 5 | 0.41097 | 32877.6 | 0.24623 | 8864.28 | 0 | 0 | 1 | 5000 | 8864.28 | 0 | 0 | 0 | 0 | 0 | 19013.32 | 0 | 0 | 0 | 0 | 0 | 19013.32
2022033105 | 5 | 0.41769 | 33415.2 | 0.3047 | 10969.2 | 0 | 0 | 1 | 5000 | 10969.2 | 0 | 0 | 0 | 0 | 0 | 17446 | 0 | 0 | 0 | 0 | 0 | 17446
2022033106 | 5 | 0.44163 | 35330.4 | 0.27755 | 9991.8 | 0 | 0 | 1 | 5000 | 9991.8 | 0 | 0 | 0 | 0 | 0 | 20338.6 | 0 | 0 | 0 | 0 | 0 | 20338.6
2022033107 | 5 | 0.48407 | 38725.6 | 0.25808 | 9290.88 | 0 | 0 | 1 | 5000 | 9290.88 | 0 | 0 | 0 | 0 | 0 | 24434.72 | 0 | 0 | 0 | 0 | 0 | 24434.72
2022033108 | 5 | 0.50481 | 40384.8 | 0.2278 | 8200.8 | 0.01003 | 120.36 | 1 | 5000 | 8200.8 | 120.36 | 0 | 0 | 0 | 0 | 27063.64 | 0 | 0 | 0 | 0 | 0 | 27063.64
2022033109 | 5 | 0.50484 | 40387.2 | 0.20325 | 7317 | 0.29278 | 3513.36 | 1 | 5000 | 7317 | 3513.36 | 0 | 0 | 0 | 0 | 24556.84 | 0 | 0 | 0 | 0 | 0 | 24556.84
2022033110 | 5 | 0.50671 | 40536.8 | 0.14085 | 5070.6 | 0.69266 | 8311.92 | 1 | 5000 | 5070.6 | 8311.92 | 0 | 0 | 0 | 0 | 22154.28 | 0 | 0 | 0 | 0 | 0 | 22154.28
2022033111 | 5 | 0.50279 | 40223.2 | 0.13268 | 4776.48 | 0.81474 | 9776.88 | 1 | 5000 | 4776.48 | 9776.88 | 0 | 0 | 0 | 0 | 20669.84 | 0 | 0 | 0 | 0 | 0 | 20669.84
2022033112 | 5 | 0.49941 | 39952.8 | 0.12239 | 4406.04 | 0.85595 | 10271.4 | 1 | 5000 | 4406.04 | 10271.4 | 0 | 0 | 0 | 0 | 20275.36 | 0 | 0 | 0 | 0 | 0 | 20275.36
2022033113 | 5 | 0.50009 | 40007.2 | 0.10866 | 3911.76 | 0.8697 | 10436.4 | 1 | 5000 | 3911.76 | 10436.4 | 0 | 0 | 0 | 0 | 20659.04 | 0 | 0 | 0 | 0 | 0 | 20659.04
2022033114 | 5 | 0.50454 | 40363.2 | 0.11501 | 4140.36 | 0.85383 | 10245.96 | 1 | 5000 | 4140.36 | 10245.96 | 0 | 0 | 0 | 0 | 20976.88 | 0 | 0 | 0 | 0 | 0 | 20976.88
2022033115 | 5 | 0.51143 | 40914.4 | 0.11786 | 4242.96 | 0.8479 | 10174.8 | 1 | 5000 | 4242.96 | 10174.8 | 0 | 0 | 0 | 0 | 21496.64 | 0 | 0 | 0 | 0 | 0 | 21496.64
2022033116 | 5 | 0.52067 | 41653.6 | 0.1083 | 3898.8 | 0.85138 | 10216.56 | 1 | 5000 | 3898.8 | 10216.56 | 0 | 0 | 0 | 0 | 22538.24 | 0 | 0 | 0 | 0 | 0 | 22538.24
2022033117 | 5 | 0.533 | 42640 | 0.09491 | 3416.76 | 0.84082 | 10089.84 | 1 | 5000 | 3416.76 | 10089.84 | 0 | 0 | 0 | 0 | 24133.4 | 0 | 0 | 0 | 0 | 0 | 24133.4
2022033118 | 5 | 0.54184 | 43347.2 | 0.09663 | 3478.68 | 0.80888 | 9706.56 | 1 | 5000 | 3478.68 | 9706.56 | 0 | 0 | 0 | 0 | 25161.96 | 0 | 0 | 0 | 0 | 0 | 25161.96
2022033119 | 5 | 0.53881 | 43104.8 | 0.0987 | 3553.2 | 0.58028 | 6963.36 | 1 | 5000 | 3553.2 | 6963.36 | 0 | 0 | 0 | 0 | 27588.24 | 0 | 0 | 0 | 0 | 0 | 27588.24
2022033120 | 5 | 0.5343 | 42744 | 0.10522 | 3787.92 | 0.12425 | 1491 | 1 | 5000 | 3787.92 | 1491 | 0 | 0 | 0 | 0 | 32465.08 | 0 | 0 | 0 | 0 | 0 | 32465.08
2022033121 | 5 | 0.53636 | 42908.8 | 0.09566 | 3443.76 | 0.00022 | 2.64 | 1 | 5000 | 3443.76 | 2.64 | 0 | 0 | 0 | 0 | 34462.4 | 0 | 0 | 0 | 0 | 0 | 34462.4
2022033122 | 5 | 0.52059 | 41647.2 | 0.13044 | 4695.84 | 0 | 0 | 1 | 5000 | 4695.84 | 0 | 0 | 0 | 0 | 0 | 31951.36 | 0 | 0 | 0 | 0 | 0 | 31951.36
2022033123 | 5 | 0.49119 | 39295.2 | 0.20521 | 7387.56 | 0 | 0 | 1 | 5000 | 7387.56 | 0 | 0 | 0 | 0 | 0 | 26907.64 | 0 | 0 | 0 | 0 | 0 | 26907.64
2022033124 | 5 | 0.45641 | 36512.8 | 0.29319 | 10554.84 | 0 | 0 | 1 | 5000 | 10554.84 | 0 | 0 | 0 | 0 | 0 | 20957.96 | 0 | 0 | 0 | 0 | 0 | 20957.96
2022040101 | 6 | 0.43352 | 34681.6 | 0.38518 | 13866.48 | 0 | 0 | 1 | 5000 | 13866.48 | 0 | 0 | 0 | 0 | 0 | 15815.12 | 0 | 0 | 0 | 0 | 0 | 15815.12
2022040102 | 6 | 0.42135 | 33708 | 0.44612 | 16060.32 | 0 | 0 | 1 | 5000 | 16060.32 | 0 | 0 | 0 | 0 | 0 | 12647.68 | 0 | 0 | 0 | 0 | 0 | 12647.68
2022040103 | 6 | 0.41476 | 33180.8 | 0.48127 | 17325.72 | 0 | 0 | 1 | 5000 | 17325.72 | 0 | 0 | 0 | 0 | 0 | 10855.08 | 0 | 0 | 0 | 0 | 0 | 10855.08
2022040104 | 6 | 0.41605 | 33284 | 0.51446 | 18520.56 | 0 | 0 | 1 | 5000 | 18520.56 | 0 | 0 | 0 | 0 | 0 | 9763.44 | 0 | 0 | 0 | 0 | 0 | 9763.44
2022040105 | 6 | 0.42416 | 33932.8 | 0.52971 | 19069.56 | 0 | 0 | 1 | 5000 | 19069.56 | 0 | 0 | 0 | 0 | 0 | 9863.24 | 0 | 0 | 0 | 0 | 0 | 9863.24
2022040106 | 6 | 0.44821 | 35856.8 | 0.53755 | 19351.8 | 0 | 0 | 1 | 5000 | 19351.8 | 0 | 0 | 0 | 0 | 0 | 11505 | 0 | 0 | 0 | 0 | 0 | 11505
2022040107 | 6 | 0.48568 | 38854.4 | 0.53526 | 19269.36 | 0 | 0 | 1 | 5000 | 19269.36 | 0 | 0 | 0 | 0 | 0 | 14585.04 | 0 | 0 | 0 | 0 | 0 | 14585.04
2022040108 | 6 | 0.50591 | 40472.8 | 0.54028 | 19450.08 | 0.01552 | 186.24 | 1 | 5000 | 19450.08 | 186.24 | 0 | 0 | 0 | 0 | 15836.48 | 0 | 0 | 0 | 0 | 0 | 15836.48
2022040109 | 6 | 0.50661 | 40528.8 | 0.50737 | 18265.32 | 0.2083 | 2499.6 | 1 | 5000 | 18265.32 | 2499.6 | 0 | 0 | 0 | 0 | 14763.88 | 0 | 0 | 0 | 0 | 0 | 14763.88
2022040110 | 6 | 0.50865 | 40692 | 0.49198 | 17711.28 | 0.38473 | 4616.76 | 1 | 5000 | 17711.28 | 4616.76 | 0 | 0 | 0 | 0 | 13363.96 | 0 | 0 | 0 | 0 | 0 | 13363.96
2022040111 | 6 | 0.50951 | 40760.8 | 0.55561 | 20001.96 | 0.3455 | 4146 | 1 | 5000 | 20001.96 | 4146 | 0 | 0 | 0 | 0 | 11612.84 | 0 | 0 | 0 | 0 | 0 | 11612.84
2022040112 | 6 | 0.51003 | 40802.4 | 0.58341 | 21002.76 | 0.34366 | 4123.92 | 1 | 5000 | 21002.76 | 4123.92 | 0 | 0 | 0 | 0 | 10675.72 | 0 | 0 | 0 | 0 | 0 | 10675.72
2022040113 | 6 | 0.5135 | 41080 | 0.6023 | 21682.8 | 0.33644 | 4037.28 | 1 | 5000 | 21682.8 | 4037.28 | 0 | 0 | 0 | 0 | 10359.92 | 0 | 0 | 0 | 0 | 0 | 10359.92
2022040114 | 6 | 0.52043 | 41634.4 | 0.61734 | 22224.24 | 0.3168 | 3801.6 | 1 | 5000 | 22224.24 | 3801.6 | 0 | 0 | 0 | 0 | 10608.56 | 0 | 0 | 0 | 0 | 0 | 10608.56
2022040115 | 6 | 0.52759 | 42207.2 | 0.62472 | 22489.92 | 0.31445 | 3773.4 | 1 | 5000 | 22489.92 | 3773.4 | 0 | 0 | 0 | 0 | 10943.88 | 0 | 0 | 0 | 0 | 0 | 10943.88
2022040116 | 6 | 0.53795 | 43036 | 0.62948 | 22661.28 | 0.31268 | 3752.16 | 1 | 5000 | 22661.28 | 3752.16 | 0 | 0 | 0 | 0 | 11622.56 | 0 | 0 | 0 | 0 | 0 | 11622.56
2022040117 | 6 | 0.54855 | 43884 | 0.62654 | 22555.44 | 0.33283 | 3993.96 | 1 | 5000 | 22555.44 | 3993.96 | 0 | 0 | 0 | 0 | 12334.6 | 0 | 0 | 0 | 0 | 0 | 12334.6
2022040118 | 6 | 0.55521 | 44416.8 | 0.61589 | 22172.04 | 0.33132 | 3975.84 | 1 | 5000 | 22172.04 | 3975.84 | 0 | 0 | 0 | 0 | 13268.92 | 0 | 0 | 0 | 0 | 0 | 13268.92
2022040119 | 6 | 0.54603 | 43682.4 | 0.59022 | 21247.92 | 0.25153 | 3018.36 | 1 | 5000 | 21247.92 | 3018.36 | 0 | 0 | 0 | 0 | 14416.12 | 0 | 0 | 0 | 0 | 0 | 14416.12
2022040120 | 6 | 0.53397 | 42717.6 | 0.55906 | 20126.16 | 0.1028 | 1233.6 | 1 | 5000 | 20126.16 | 1233.6 | 0 | 0 | 0 | 0 | 16357.84 | 0 | 0 | 0 | 0 | 0 | 16357.84
2022040121 | 6 | 0.53343 | 42674.4 | 0.53997 | 19438.92 | 0.0005 | 6 | 1 | 5000 | 19438.92 | 6 | 0 | 0 | 0 | 0 | 18229.48 | 0 | 0 | 0 | 0 | 0 | 18229.48
2022040122 | 6 | 0.51918 | 41534.4 | 0.52361 | 18849.96 | 0 | 0 | 1 | 5000 | 18849.96 | 0 | 0 | 0 | 0 | 0 | 17684.44 | 0 | 0 | 0 | 0 | 0 | 17684.44
2022040123 | 6 | 0.4932 | 39456 | 0.45572 | 16405.92 | 0 | 0 | 1 | 5000 | 16405.92 | 0 | 0 | 0 | 0 | 0 | 18050.08 | 0 | 0 | 0 | 0 | 0 | 18050.08
2022040124 | 6 | 0.46534 | 37227.2 | 0.38734 | 13944.24 | 0 | 0 | 1 | 5000 | 13944.24 | 0 | 0 | 0 | 0 | 0 | 18282.96 | 0 | 0 | 0 | 0 | 0 | 18282.96
2022040201 | 7 | 0.43953 | 35162.4 | 0.34073 | 12266.28 | 0 | 0 | 1 | 5000 | 12266.28 | 0 | 0 | 0 | 0 | 0 | 17896.12 | 0 | 0 | 0 | 0 | 0 | 17896.12
2022040202 | 7 | 0.42086 | 33668.8 | 0.28985 | 10434.6 | 0 | 0 | 1 | 5000 | 10434.6 | 0 | 0 | 0 | 0 | 0 | 18234.2 | 0 | 0 | 0 | 0 | 0 | 18234.2
2022040203 | 7 | 0.40858 | 32686.4 | 0.26398 | 9503.28 | 0 | 0 | 1 | 5000 | 9503.28 | 0 | 0 | 0 | 0 | 0 | 18183.12 | 0 | 0 | 0 | 0 | 0 | 18183.12
2022040204 | 7 | 0.4037 | 32296 | 0.2549 | 9176.4 | 0 | 0 | 1 | 5000 | 9176.4 | 0 | 0 | 0 | 0 | 0 | 18119.6 | 0 | 0 | 0 | 0 | 0 | 18119.6
2022040205 | 7 | 0.40364 | 32291.2 | 0.25719 | 9258.84 | 0 | 0 | 1 | 5000 | 9258.84 | 0 | 0 | 0 | 0 | 0 | 18032.36 | 0 | 0 | 0 | 0 | 0 | 18032.36
2022040206 | 7 | 0.41166 | 32932.8 | 0.22924 | 8252.64 | 0 | 0 | 1 | 5000 | 8252.64 | 0 | 0 | 0 | 0 | 0 | 19680.16 | 0 | 0 | 0 | 0 | 0 | 19680.16
2022040207 | 7 | 0.42459 | 33967.2 | 0.16246 | 5848.56 | 0 | 0 | 1 | 5000 | 5848.56 | 0 | 0 | 0 | 0 | 0 | 23118.64 | 0 | 0 | 0 | 0 | 0 | 23118.64
2022040208 | 7 | 0.43942 | 35153.6 | 0.11789 | 4244.04 | 0.01324 | 158.88 | 1 | 5000 | 4244.04 | 158.88 | 0 | 0 | 0 | 0 | 25750.68 | 0 | 0 | 0 | 0 | 0 | 25750.68
2022040209 | 7 | 0.45381 | 36304.8 | 0.09717 | 3498.12 | 0.32415 | 3889.8 | 1 | 5000 | 3498.12 | 3889.8 | 0 | 0 | 0 | 0 | 23916.88 | 0 | 0 | 0 | 0 | 0 | 23916.88
2022040210 | 7 | 0.4688 | 37504 | 0.07145 | 2572.2 | 0.72928 | 8751.36 | 1 | 5000 | 2572.2 | 8751.36 | 0 | 0 | 0 | 0 | 21180.44 | 0 | 0 | 0 | 0 | 0 | 21180.44
2022040211 | 7 | 0.48252 | 38601.6 | 0.06108 | 2198.88 | 0.80784 | 9694.08 | 1 | 5000 | 2198.88 | 9694.08 | 0 | 0 | 0 | 0 | 21708.64 | 0 | 0 | 0 | 0 | 0 | 21708.64
2022040212 | 7 | 0.49734 | 39787.2 | 0.06679 | 2404.44 | 0.82945 | 9953.4 | 1 | 5000 | 2404.44 | 9953.4 | 0 | 0 | 0 | 0 | 22429.36 | 0 | 0 | 0 | 0 | 0 | 22429.36
2022040213 | 7 | 0.50783 | 40626.4 | 0.0623 | 2242.8 | 0.83382 | 10005.84 | 1 | 5000 | 2242.8 | 10005.84 | 0 | 0 | 0 | 0 | 23377.76 | 0 | 0 | 0 | 0 | 0 | 23377.76
2022040214 | 7 | 0.52071 | 41656.8 | 0.06572 | 2365.92 | 0.83751 | 10050.12 | 1 | 5000 | 2365.92 | 10050.12 | 0 | 0 | 0 | 0 | 24240.76 | 0 | 0 | 0 | 0 | 0 | 24240.76
2022040215 | 7 | 0.538 | 43040 | 0.07621 | 2743.56 | 0.8383 | 10059.6 | 1 | 5000 | 2743.56 | 10059.6 | 0 | 0 | 0 | 0 | 25236.84 | 0 | 0 | 0 | 0 | 0 | 25236.84
2022040216 | 7 | 0.5586 | 44688 | 0.08758 | 3152.88 | 0.84197 | 10103.64 | 1 | 5000 | 3152.88 | 10103.64 | 0 | 0 | 0 | 0 | 26431.48 | 0 | 0 | 0 | 0 | 0 | 26431.48
2022040217 | 7 | 0.57789 | 46231.2 | 0.10068 | 3624.48 | 0.84276 | 10113.12 | 1 | 5000 | 3624.48 | 10113.12 | 0 | 0 | 0 | 0 | 27493.6 | 0 | 0 | 0 | 0 | 0 | 27493.6
2022040218 | 7 | 0.58863 | 47090.4 | 0.13107 | 4718.52 | 0.81492 | 9779.04 | 1 | 5000 | 4718.52 | 9779.04 | 0 | 0 | 0 | 0 | 27592.84 | 0 | 0 | 0 | 0 | 0 | 27592.84
2022040219 | 7 | 0.58408 | 46726.4 | 0.16228 | 5842.08 | 0.6307 | 7568.4 | 1 | 5000 | 5842.08 | 7568.4 | 0 | 0 | 0 | 0 | 28315.92 | 0 | 0 | 0 | 0 | 0 | 28315.92
2022040220 | 7 | 0.56393 | 45114.4 | 0.19371 | 6973.56 | 0.16017 | 1922.04 | 1 | 5000 | 6973.56 | 1922.04 | 0 | 0 | 0 | 0 | 31218.8 | 0 | 0 | 0 | 0 | 0 | 31218.8
2022040221 | 7 | 0.55111 | 44088.8 | 0.23869 | 8592.84 | 0.00056 | 6.72 | 1 | 5000 | 8592.84 | 6.72 | 0 | 0 | 0 | 0 | 30489.24 | 0 | 0 | 0 | 0 | 0 | 30489.24
2022040222 | 7 | 0.5316 | 42528 | 0.3163 | 11386.8 | 0 | 0 | 1 | 5000 | 11386.8 | 0 | 0 | 0 | 0 | 0 | 26141.2 | 0 | 0 | 0 | 0 | 0 | 26141.2
2022040223 | 7 | 0.50638 | 40510.4 | 0.39958 | 14384.88 | 0 | 0 | 1 | 5000 | 14384.88 | 0 | 0 | 0 | 0 | 0 | 21125.52 | 0 | 0 | 0 | 0 | 0 | 21125.52
2022040224 | 7 | 0.47849 | 38279.2 | 0.49896 | 17962.56 | 0 | 0 | 1 | 5000 | 17962.56 | 0 | 0 | 0 | 0 | 0 | 15316.64 | 0 | 0 | 0 | 0 | 0 | 15316.64
2022040301 | 1 | 0.45466 | 36372.8 | 0.55922 | 20131.92 | 0 | 0 | 1 | 5000 | 20131.92 | 0 | 0 | 0 | 0 | 0 | 11240.88 | 0 | 0 | 0 | 0 | 0 | 11240.88
2022040302 | 1 | 0.43415 | 34732 | 0.56987 | 20515.32 | 0 | 0 | 1 | 5000 | 20515.32 | 0 | 0 | 0 | 0 | 0 | 9216.68 | 0 | 0 | 0 | 0 | 0 | 9216.68
2022040303 | 1 | 0.42231 | 33784.8 | 0.56056 | 20180.16 | 0 | 0 | 1 | 5000 | 20180.16 | 0 | 0 | 0 | 0 | 0 | 8604.64 | 0 | 0 | 0 | 0 | 0 | 8604.64
2022040304 | 1 | 0.41378 | 33102.4 | 0.54521 | 19627.56 | 0 | 0 | 1 | 5000 | 19627.56 | 0 | 0 | 0 | 0 | 0 | 8474.84 | 0 | 0 | 0 | 0 | 0 | 8474.84
2022040305 | 1 | 0.41119 | 32895.2 | 0.53632 | 19307.52 | 0 | 0 | 1 | 5000 | 19307.52 | 0 | 0 | 0 | 0 | 0 | 8587.68 | 0 | 0 | 0 | 0 | 0 | 8587.68
2022040306 | 1 | 0.41381 | 33104.8 | 0.53555 | 19279.8 | 0 | 0 | 1 | 5000 | 19279.8 | 0 | 0 | 0 | 0 | 0 | 8825 | 0 | 0 | 0 | 0 | 0 | 8825
2022040307 | 1 | 0.42044 | 33635.2 | 0.53554 | 19279.44 | 0 | 0 | 1 | 5000 | 19279.44 | 0 | 0 | 0 | 0 | 0 | 9355.76 | 0 | 0 | 0 | 0 | 0 | 9355.76
2022040308 | 1 | 0.42901 | 34320.8 | 0.53395 | 19222.2 | 0.01508 | 180.96 | 1 | 5000 | 19222.2 | 180.96 | 0 | 0 | 0 | 0 | 9917.64 | 0 | 0 | 0 | 0 | 0 | 9917.64
2022040309 | 1 | 0.44736 | 35788.8 | 0.50644 | 18231.84 | 0.1737 | 2084.4 | 1 | 5000 | 18231.84 | 2084.4 | 0 | 0 | 0 | 0 | 10472.56 | 0 | 0 | 0 | 0 | 0 | 10472.56
2022040310 | 1 | 0.46641 | 37312.8 | 0.48623 | 17504.28 | 0.30343 | 3641.16 | 1 | 5000 | 17504.28 | 3641.16 | 0 | 0 | 0 | 0 | 11167.36 | 0 | 0 | 0 | 0 | 0 | 11167.36
2022040311 | 1 | 0.48758 | 39006.4 | 0.49291 | 17744.76 | 0.31218 | 3746.16 | 1 | 5000 | 17744.76 | 3746.16 | 0 | 0 | 0 | 0 | 12515.48 | 0 | 0 | 0 | 0 | 0 | 12515.48
2022040312 | 1 | 0.506 | 40480 | 0.49175 | 17703 | 0.37305 | 4476.6 | 1 | 5000 | 17703 | 4476.6 | 0 | 0 | 0 | 0 | 13300.4 | 0 | 0 | 0 | 0 | 0 | 13300.4
2022040313 | 1 | 0.5267 | 42136 | 0.49517 | 17826.12 | 0.41703 | 5004.36 | 1 | 5000 | 17826.12 | 5004.36 | 0 | 0 | 0 | 0 | 14305.52 | 0 | 0 | 0 | 0 | 0 | 14305.52
2022040314 | 1 | 0.54631 | 43704.8 | 0.46567 | 16764.12 | 0.5779 | 6934.8 | 1 | 5000 | 16764.12 | 6934.8 | 0 | 0 | 0 | 0 | 15005.88 | 0 | 0 | 0 | 0 | 0 | 15005.88
2022040315 | 1 | 0.56721 | 45376.8 | 0.426 | 15336 | 0.75721 | 9086.52 | 1 | 5000 | 15336 | 9086.52 | 0 | 0 | 0 | 0 | 15954.28 | 0 | 0 | 0 | 0 | 0 | 15954.28
2022040316 | 1 | 0.58855 | 47084 | 0.42563 | 15322.68 | 0.78179 | 9381.48 | 1 | 5000 | 15322.68 | 9381.48 | 0 | 0 | 0 | 0 | 17379.84 | 0 | 0 | 0 | 0 | 0 | 17379.84
2022040317 | 1 | 0.60611 | 48488.8 | 0.46433 | 16715.88 | 0.70177 | 8421.24 | 1 | 5000 | 16715.88 | 8421.24 | 0 | 0 | 0 | 0 | 18351.68 | 0 | 0 | 0 | 0 | 0 | 18351.68
2022040318 | 1 | 0.61703 | 49362.4 | 0.50794 | 18285.84 | 0.49512 | 5941.44 | 1 | 5000 | 18285.84 | 5941.44 | 0 | 0 | 0 | 0 | 20135.12 | 0 | 0 | 0 | 0 | 0 | 20135.12
2022040319 | 1 | 0.61384 | 49107.2 | 0.55306 | 19910.16 | 0.29167 | 3500.04 | 1 | 5000 | 19910.16 | 3500.04 | 0 | 0 | 0 | 0 | 20697 | 0 | 0 | 0 | 0 | 0 | 20697
2022040320 | 1 | 0.59646 | 47716.8 | 0.55116 | 19841.76 | 0.07019 | 842.28 | 1 | 5000 | 19841.76 | 842.28 | 0 | 0 | 0 | 0 | 22032.76 | 0 | 0 | 0 | 0 | 0 | 22032.76
2022040321 | 1 | 0.59197 | 47357.6 | 0.58734 | 21144.24 | 0.00046 | 5.52 | 1 | 5000 | 21144.24 | 5.52 | 0 | 0 | 0 | 0 | 21207.84 | 0 | 0 | 0 | 0 | 0 | 21207.84
2022040322 | 1 | 0.57349 | 45879.2 | 0.6175 | 22230 | 0 | 0 | 1 | 5000 | 22230 | 0 | 0 | 0 | 0 | 0 | 18649.2 | 0 | 0 | 0 | 0 | 0 | 18649.2
2022040323 | 1 | 0.53741 | 42992.8 | 0.60078 | 21628.08 | 0 | 0 | 1 | 5000 | 21628.08 | 0 | 0 | 0 | 0 | 0 | 16364.72 | 0 | 0 | 0 | 0 | 0 | 16364.72
2022040324 | 1 | 0.49584 | 39667.2 | 0.58321 | 20995.56 | 0 | 0 | 1 | 5000 | 20995.56 | 0 | 0 | 0 | 0 | 0 | 13671.64 | 0 | 0 | 0 | 0 | 0 | 13671.64
2022040401 | 2 | 0.46215 | 36972 | 0.56482 | 20333.52 | 0 | 0 | 1 | 5000 | 20333.52 | 0 | 0 | 0 | 0 | 0 | 11638.48 | 0 | 0 | 0 | 0 | 0 | 11638.48
2022040402 | 2 | 0.43906 | 35124.8 | 0.5465 | 19674 | 0 | 0 | 1 | 5000 | 19674 | 0 | 0 | 0 | 0 | 0 | 10450.8 | 0 | 0 | 0 | 0 | 0 | 10450.8
2022040403 | 2 | 0.4262 | 34096 | 0.50115 | 18041.4 | 0 | 0 | 1 | 5000 | 18041.4 | 0 | 0 | 0 | 0 | 0 | 11054.6 | 0 | 0 | 0 | 0 | 0 | 11054.6
2022040404 | 2 | 0.42194 | 33755.2 | 0.45816 | 16493.76 | 0 | 0 | 1 | 5000 | 16493.76 | 0 | 0 | 0 | 0 | 0 | 12261.44 | 0 | 0 | 0 | 0 | 0 | 12261.44
2022040405 | 2 | 0.42594 | 34075.2 | 0.40566 | 14603.76 | 0 | 0 | 1 | 5000 | 14603.76 | 0 | 0 | 0 | 0 | 0 | 14471.44 | 0 | 0 | 0 | 0 | 0 | 14471.44
2022040406 | 2 | 0.44534 | 35627.2 | 0.38594 | 13893.84 | 0 | 0 | 1 | 5000 | 13893.84 | 0 | 0 | 0 | 0 | 0 | 16733.36 | 0 | 0 | 0 | 0 | 0 | 16733.36
2022040407 | 2 | 0.47773 | 38218.4 | 0.35733 | 12863.88 | 0 | 0 | 1 | 5000 | 12863.88 | 0 | 0 | 0 | 0 | 0 | 20354.52 | 0 | 0 | 0 | 0 | 0 | 20354.52
2022040408 | 2 | 0.49646 | 39716.8 | 0.30398 | 10943.28 | 0.00701 | 84.12 | 1 | 5000 | 10943.28 | 84.12 | 0 | 0 | 0 | 0 | 23689.4 | 0 | 0 | 0 | 0 | 0 | 23689.4
2022040409 | 2 | 0.50342 | 40273.6 | 0.2569 | 9248.4 | 0.1534 | 1840.8 | 1 | 5000 | 9248.4 | 1840.8 | 0 | 0 | 0 | 0 | 24184.4 | 0 | 0 | 0 | 0 | 0 | 24184.4
2022040410 | 2 | 0.51592 | 41273.6 | 0.2518 | 9064.8 | 0.37503 | 4500.36 | 1 | 5000 | 9064.8 | 4500.36 | 0 | 0 | 0 | 0 | 22708.44 | 0 | 0 | 0 | 0 | 0 | 22708.44
2022040411 | 2 | 0.52862 | 42289.6 | 0.26068 | 9384.48 | 0.43518 | 5222.16 | 1 | 5000 | 9384.48 | 5222.16 | 0 | 0 | 0 | 0 | 22682.96 | 0 | 0 | 0 | 0 | 0 | 22682.96
2022040412 | 2 | 0.54533 | 43626.4 | 0.24441 | 8798.76 | 0.50859 | 6103.08 | 1 | 5000 | 8798.76 | 6103.08 | 0 | 0 | 0 | 0 | 23724.56 | 0 | 0 | 0 | 0 | 0 | 23724.56
2022040413 | 2 | 0.5587 | 44696 | 0.21876 | 7875.36 | 0.54462 | 6535.44 | 1 | 5000 | 7875.36 | 6535.44 | 0 | 0 | 0 | 0 | 25285.2 | 0 | 0 | 0 | 0 | 0 | 25285.2
2022040414 | 2 | 0.56936 | 45548.8 | 0.20159 | 7257.24 | 0.58071 | 6968.52 | 1 | 5000 | 7257.24 | 6968.52 | 0 | 0 | 0 | 0 | 26323.04 | 0 | 0 | 0 | 0 | 0 | 26323.04
2022040415 | 2 | 0.57517 | 46013.6 | 0.19422 | 6991.92 | 0.57526 | 6903.12 | 1 | 5000 | 6991.92 | 6903.12 | 0 | 0 | 0 | 0 | 27118.56 | 0 | 0 | 0 | 0 | 0 | 27118.56
2022040416 | 2 | 0.58081 | 46464.8 | 0.18684 | 6726.24 | 0.59734 | 7168.08 | 1 | 5000 | 6726.24 | 7168.08 | 0 | 0 | 0 | 0 | 27570.48 | 0 | 0 | 0 | 0 | 0 | 27570.48
2022040417 | 2 | 0.59079 | 47263.2 | 0.19203 | 6913.08 | 0.56161 | 6739.32 | 1 | 5000 | 6913.08 | 6739.32 | 0 | 0 | 0 | 0 | 28610.8 | 0 | 0 | 0 | 0 | 0 | 28610.8
2022040418 | 2 | 0.59537 | 47629.6 | 0.19709 | 7095.24 | 0.55177 | 6621.24 | 1 | 5000 | 7095.24 | 6621.24 | 0 | 0 | 0 | 0 | 28913.12 | 0 | 0 | 0 | 0 | 0 | 28913.12
2022040419 | 2 | 0.59041 | 47232.8 | 0.20445 | 7360.2 | 0.43167 | 5180.04 | 1 | 5000 | 7360.2 | 5180.04 | 0 | 0 | 0 | 0 | 29692.56 | 0 | 0 | 0 | 0 | 0 | 29692.56
2022040420 | 2 | 0.58713 | 46970.4 | 0.19709 | 7095.24 | 0.12474 | 1496.88 | 1 | 5000 | 7095.24 | 1496.88 | 0 | 0 | 0 | 0 | 33378.28 | 0 | 0 | 0 | 0 | 0 | 33378.28
2022040421 | 2 | 0.58644 | 46915.2 | 0.19628 | 7066.08 | 0.00066 | 7.92 | 1 | 5000 | 7066.08 | 7.92 | 0 | 0 | 0 | 0 | 34841.2 | 0 | 0 | 0 | 0 | 0 | 34841.2
2022040422 | 2 | 0.56842 | 45473.6 | 0.1716 | 6177.6 | 0 | 0 | 1 | 5000 | 6177.6 | 0 | 0 | 0 | 0 | 0 | 34296 | 0 | 0 | 0 | 0 | 0 | 34296
2022040423 | 2 | 0.53786 | 43028.8 | 0.15803 | 5689.08 | 0 | 0 | 1 | 5000 | 5689.08 | 0 | 0 | 0 | 0 | 0 | 32339.72 | 0 | 0 | 0 | 0 | 0 | 32339.72
2022040424 | 2 | 0.49826 | 39860.8 | 0.1658 | 5968.8 | 0 | 0 | 1 | 5000 | 5968.8 | 0 | 0 | 0 | 0 | 0 | 28892 | 0 | 0 | 0 | 0 | 0 | 28892
2022040501 | 3 | 0.46657 | 37325.6 | 0.16435 | 5916.6 | 0 | 0 | 1 | 5000 | 5916.6 | 0 | 0 | 0 | 0 | 0 | 26409 | 0 | 0 | 0 | 0 | 0 | 26409
2022040502 | 3 | 0.44667 | 35733.6 | 0.18179 | 6544.44 | 0 | 0 | 1 | 5000 | 6544.44 | 0 | 0 | 0 | 0 | 0 | 24189.16 | 0 | 0 | 0 | 0 | 0 | 24189.16
2022040503 | 3 | 0.43361 | 34688.8 | 0.1964 | 7070.4 | 0 | 0 | 1 | 5000 | 7070.4 | 0 | 0 | 0 | 0 | 0 | 22618.4 | 0 | 0 | 0 | 0 | 0 | 22618.4
2022040504 | 3 | 0.43123 | 34498.4 | 0.23551 | 8478.36 | 0 | 0 | 1 | 5000 | 8478.36 | 0 | 0 | 0 | 0 | 0 | 21020.04 | 0 | 0 | 0 | 0 | 0 | 21020.04
2022040505 | 3 | 0.43779 | 35023.2 | 0.28659 | 10317.24 | 0 | 0 | 1 | 5000 | 10317.24 | 0 | 0 | 0 | 0 | 0 | 19705.96 | 0 | 0 | 0 | 0 | 0 | 19705.96
2022040506 | 3 | 0.45881 | 36704.8 | 0.31887 | 11479.32 | 0 | 0 | 1 | 5000 | 11479.32 | 0 | 0 | 0 | 0 | 0 | 20225.48 | 0 | 0 | 0 | 0 | 0 | 20225.48
2022040507 | 3 | 0.49697 | 39757.6 | 0.3533 | 12718.8 | 0 | 0 | 1 | 5000 | 12718.8 | 0 | 0 | 0 | 0 | 0 | 22038.8 | 0 | 0 | 0 | 0 | 0 | 22038.8
2022040508 | 3 | 0.51536 | 41228.8 | 0.39278 | 14140.08 | 0.01447 | 173.64 | 1 | 5000 | 14140.08 | 173.64 | 0 | 0 | 0 | 0 | 21915.08 | 0 | 0 | 0 | 0 | 0 | 21915.08
2022040509 | 3 | 0.52572 | 42057.6 | 0.40349 | 14525.64 | 0.24993 | 2999.16 | 1 | 5000 | 14525.64 | 2999.16 | 0 | 0 | 0 | 0 | 19532.8 | 0 | 0 | 0 | 0 | 0 | 19532.8
2022040510 | 3 | 0.53972 | 43177.6 | 0.37123 | 13364.28 | 0.43429 | 5211.48 | 1 | 5000 | 13364.28 | 5211.48 | 0 | 0 | 0 | 0 | 19601.84 | 0 | 0 | 0 | 0 | 0 | 19601.84
2022040511 | 3 | 0.56185 | 44948 | 0.36616 | 13181.76 | 0.51874 | 6224.88 | 1 | 5000 | 13181.76 | 6224.88 | 0 | 0 | 0 | 0 | 20541.36 | 0 | 0 | 0 | 0 | 0 | 20541.36
2022040512 | 3 | 0.5855 | 46840 | 0.39409 | 14187.24 | 0.49015 | 5881.8 | 1 | 5000 | 14187.24 | 5881.8 | 0 | 0 | 0 | 0 | 21770.96 | 0 | 0 | 0 | 0 | 0 | 21770.96
2022040513 | 3 | 0.61866 | 49492.8 | 0.4381 | 15771.6 | 0.38927 | 4671.24 | 1 | 5000 | 15771.6 | 4671.24 | 0 | 0 | 0 | 0 | 24049.96 | 0 | 0 | 0 | 0 | 0 | 24049.96
2022040514 | 3 | 0.64995 | 51996 | 0.46172 | 16621.92 | 0.33823 | 4058.76 | 1 | 5000 | 16621.92 | 4058.76 | 0 | 0 | 0 | 0 | 26315.32 | 0 | 0 | 0 | 0 | 0 | 26315.32
2022040515 | 3 | 0.67731 | 54184.8 | 0.46342 | 16683.12 | 0.33083 | 3969.96 | 1 | 5000 | 16683.12 | 3969.96 | 0 | 0 | 0 | 0 | 28531.72 | 0 | 0 | 0 | 0 | 0 | 28531.72
2022040516 | 3 | 0.70424 | 56339.2 | 0.4653 | 16750.8 | 0.30745 | 3689.4 | 1 | 5000 | 16750.8 | 3689.4 | 0 | 0 | 0 | 0 | 30899 | 0 | 0 | 0 | 0 | 0 | 30899
2022040517 | 3 | 0.7261 | 58088 | 0.48158 | 17336.88 | 0.28502 | 3420.24 | 1 | 5000 | 17336.88 | 3420.24 | 0 | 0 | 0 | 0 | 32330.88 | 0 | 0 | 0 | 0 | 0 | 32330.88
2022040518 | 3 | 0.73253 | 58602.4 | 0.4985 | 17946 | 0.25967 | 3116.04 | 1 | 5000 | 17946 | 3116.04 | 0 | 0 | 0 | 0 | 32540.36 | 0 | 0 | 0 | 0 | 0 | 32540.36
2022040519 | 3 | 0.71719 | 57375.2 | 0.51156 | 18416.16 | 0.21256 | 2550.72 | 1 | 5000 | 18416.16 | 2550.72 | 0 | 0 | 0 | 0 | 31408.32 | 0 | 0 | 0 | 0 | 0 | 31408.32
2022040520 | 3 | 0.69328 | 55462.4 | 0.50792 | 18285.12 | 0.10554 | 1266.48 | 1 | 5000 | 18285.12 | 1266.48 | 0 | 0 | 0 | 0 | 30910.8 | 0 | 0 | 0 | 0 | 0 | 30910.8
2022040521 | 3 | 0.67586 | 54068.8 | 0.49303 | 17749.08 | 0.00067 | 8.04 | 1 | 5000 | 17749.08 | 8.04 | 0 | 0 | 0 | 0 | 31311.68 | 0 | 0 | 0 | 0 | 0 | 31311.68
2022040522 | 3 | 0.64703 | 51762.4 | 0.5432 | 19555.2 | 0 | 0 | 1 | 5000 | 19555.2 | 0 | 0 | 0 | 0 | 0 | 27207.2 | 0 | 0 | 0 | 0 | 0 | 27207.2
2022040523 | 3 | 0.60241 | 48192.8 | 0.57053 | 20539.08 | 0 | 0 | 1 | 5000 | 20539.08 | 0 | 0 | 0 | 0 | 0 | 22653.72 | 0 | 0 | 0 | 0 | 0 | 22653.72
2022040524 | 3 | 0.55511 | 44408.8 | 0.58305 | 20989.8 | 0 | 0 | 1 | 5000 | 20989.8 | 0 | 0 | 0 | 0 | 0 | 18419 | 0 | 0 | 0 | 0 | 0 | 18419
2022040601 | 4 | 0.51748 | 41398.4 | 0.59599 | 21455.64 | 0 | 0 | 1 | 5000 | 21455.64 | 0 | 0 | 0 | 0 | 0 | 14942.76 | 0 | 0 | 0 | 0 | 0 | 14942.76
2022040602 | 4 | 0.49182 | 39345.6 | 0.59511 | 21423.96 | 0 | 0 | 1 | 5000 | 21423.96 | 0 | 0 | 0 | 0 | 0 | 12921.64 | 0 | 0 | 0 | 0 | 0 | 12921.64
2022040603 | 4 | 0.47336 | 37868.8 | 0.58643 | 21111.48 | 0 | 0 | 1 | 5000 | 21111.48 | 0 | 0 | 0 | 0 | 0 | 11757.32 | 0 | 0 | 0 | 0 | 0 | 11757.32
2022040604 | 4 | 0.46145 | 36916 | 0.57783 | 20801.88 | 0 | 0 | 1 | 5000 | 20801.88 | 0 | 0 | 0 | 0 | 0 | 11114.12 | 0 | 0 | 0 | 0 | 0 | 11114.12
2022040605 | 4 | 0.45704 | 36563.2 | 0.57756 | 20792.16 | 0 | 0 | 1 | 5000 | 20792.16 | 0 | 0 | 0 | 0 | 0 | 10771.04 | 0 | 0 | 0 | 0 | 0 | 10771.04
2022040606 | 4 | 0.46949 | 37559.2 | 0.58164 | 20939.04 | 0 | 0 | 1 | 5000 | 20939.04 | 0 | 0 | 0 | 0 | 0 | 11620.16 | 0 | 0 | 0 | 0 | 0 | 11620.16
2022040607 | 4 | 0.50155 | 40124 | 0.5838 | 21016.8 | 0 | 0 | 1 | 5000 | 21016.8 | 0 | 0 | 0 | 0 | 0 | 14107.2 | 0 | 0 | 0 | 0 | 0 | 14107.2
2022040608 | 4 | 0.51542 | 41233.6 | 0.56294 | 20265.84 | 0.0165 | 198 | 1 | 5000 | 20265.84 | 198 | 0 | 0 | 0 | 0 | 15769.76 | 0 | 0 | 0 | 0 | 0 | 15769.76
2022040609 | 4 | 0.51922 | 41537.6 | 0.49966 | 17987.76 | 0.25701 | 3084.12 | 1 | 5000 | 17987.76 | 3084.12 | 0 | 0 | 0 | 0 | 15465.72 | 0 | 0 | 0 | 0 | 0 | 15465.72
2022040610 | 4 | 0.52733 | 42186.4 | 0.49829 | 17938.44 | 0.28996 | 3479.52 | 1 | 5000 | 17938.44 | 3479.52 | 0 | 0 | 0 | 0 | 15768.44 | 0 | 0 | 0 | 0 | 0 | 15768.44
2022040611 | 4 | 0.53935 | 43148 | 0.52117 | 18762.12 | 0.27638 | 3316.56 | 1 | 5000 | 18762.12 | 3316.56 | 0 | 0 | 0 | 0 | 16069.32 | 0 | 0 | 0 | 0 | 0 | 16069.32
2022040612 | 4 | 0.54894 | 43915.2 | 0.5204 | 18734.4 | 0.32508 | 3900.96 | 1 | 5000 | 18734.4 | 3900.96 | 0 | 0 | 0 | 0 | 16279.84 | 0 | 0 | 0 | 0 | 0 | 16279.84
2022040613 | 4 | 0.55603 | 44482.4 | 0.51653 | 18595.08 | 0.41577 | 4989.24 | 1 | 5000 | 18595.08 | 4989.24 | 0 | 0 | 0 | 0 | 15898.08 | 0 | 0 | 0 | 0 | 0 | 15898.08
2022040614 | 4 | 0.56741 | 45392.8 | 0.48741 | 17546.76 | 0.56375 | 6765 | 1 | 5000 | 17546.76 | 6765 | 0 | 0 | 0 | 0 | 16081.04 | 0 | 0 | 0 | 0 | 0 | 16081.04
2022040615 | 4 | 0.57716 | 46172.8 | 0.44312 | 15952.32 | 0.73762 | 8851.44 | 1 | 5000 | 15952.32 | 8851.44 | 0 | 0 | 0 | 0 | 16369.04 | 0 | 0 | 0 | 0 | 0 | 16369.04
2022040616 | 4 | 0.5868 | 46944 | 0.44589 | 16052.04 | 0.81474 | 9776.88 | 1 | 5000 | 16052.04 | 9776.88 | 0 | 0 | 0 | 0 | 16115.08 | 0 | 0 | 0 | 0 | 0 | 16115.08
2022040617 | 4 | 0.59647 | 47717.6 | 0.4535 | 16326 | 0.79508 | 9540.96 | 1 | 5000 | 16326 | 9540.96 | 0 | 0 | 0 | 0 | 16850.64 | 0 | 0 | 0 | 0 | 0 | 16850.64
2022040618 | 4 | 0.59911 | 47928.8 | 0.45794 | 16485.84 | 0.77346 | 9281.52 | 1 | 5000 | 16485.84 | 9281.52 | 0 | 0 | 0 | 0 | 17161.44 | 0 | 0 | 0 | 0 | 0 | 17161.44
2022040619 | 4 | 0.58563 | 46850.4 | 0.45652 | 16434.72 | 0.60932 | 7311.84 | 1 | 5000 | 16434.72 | 7311.84 | 0 | 0 | 0 | 0 | 18103.84 | 0 | 0 | 0 | 0 | 0 | 18103.84
2022040620 | 4 | 0.56623 | 45298.4 | 0.4379 | 15764.4 | 0.16105 | 1932.6 | 1 | 5000 | 15764.4 | 1932.6 | 0 | 0 | 0 | 0 | 22601.4 | 0 | 0 | 0 | 0 | 0 | 22601.4
2022040621 | 4 | 0.56378 | 45102.4 | 0.40807 | 14690.52 | 0.00097 | 11.64 | 1 | 5000 | 14690.52 | 11.64 | 0 | 0 | 0 | 0 | 25400.24 | 0 | 0 | 0 | 0 | 0 | 25400.24
2022040622 | 4 | 0.54093 | 43274.4 | 0.41704 | 15013.44 | 0 | 0 | 1 | 5000 | 15013.44 | 0 | 0 | 0 | 0 | 0 | 23260.96 | 0 | 0 | 0 | 0 | 0 | 23260.96
2022040623 | 4 | 0.50421 | 40336.8 | 0.43282 | 15581.52 | 0 | 0 | 1 | 5000 | 15581.52 | 0 | 0 | 0 | 0 | 0 | 19755.28 | 0 | 0 | 0 | 0 | 0 | 19755.28
2022040624 | 4 | 0.4626 | 37008 | 0.49079 | 17668.44 | 0 | 0 | 1 | 5000 | 17668.44 | 0 | 0 | 0 | 0 | 0 | 14339.56 | 0 | 0 | 0 | 0 | 0 | 14339.56
2022040701 | 5 | 0.43313 | 34650.4 | 0.48024 | 17288.64 | 0 | 0 | 1 | 5000 | 17288.64 | 0 | 0 | 0 | 0 | 0 | 12361.76 | 0 | 0 | 0 | 0 | 0 | 12361.76
2022040702 | 5 | 0.4151 | 33208 | 0.48127 | 17325.72 | 0 | 0 | 1 | 5000 | 17325.72 | 0 | 0 | 0 | 0 | 0 | 10882.28 | 0 | 0 | 0 | 0 | 0 | 10882.28
2022040703 | 5 | 0.40474 | 32379.2 | 0.49149 | 17693.64 | 0 | 0 | 1 | 5000 | 17693.64 | 0 | 0 | 0 | 0 | 0 | 9685.56 | 0 | 0 | 0 | 0 | 0 | 9685.56
2022040704 | 5 | 0.40022 | 32017.6 | 0.48013 | 17284.68 | 0 | 0 | 1 | 5000 | 17284.68 | 0 | 0 | 0 | 0 | 0 | 9732.92 | 0 | 0 | 0 | 0 | 0 | 9732.92
2022040705 | 5 | 0.40513 | 32410.4 | 0.45019 | 16206.84 | 0 | 0 | 1 | 5000 | 16206.84 | 0 | 0 | 0 | 0 | 0 | 11203.56 | 0 | 0 | 0 | 0 | 0 | 11203.56
2022040706 | 5 | 0.4282 | 34256 | 0.43132 | 15527.52 | 0 | 0 | 1 | 5000 | 15527.52 | 0 | 0 | 0 | 0 | 0 | 13728.48 | 0 | 0 | 0 | 0 | 0 | 13728.48
2022040707 | 5 | 0.46805 | 37444 | 0.42751 | 15390.36 | 0 | 0 | 1 | 5000 | 15390.36 | 0 | 0 | 0 | 0 | 0 | 17053.64 | 0 | 0 | 0 | 0 | 0 | 17053.64
2022040708 | 5 | 0.4856 | 38848 | 0.42033 | 15131.88 | 0.02858 | 342.96 | 1 | 5000 | 15131.88 | 342.96 | 0 | 0 | 0 | 0 | 18373.16 | 0 | 0 | 0 | 0 | 0 | 18373.16
2022040709 | 5 | 0.48762 | 39009.6 | 0.37657 | 13556.52 | 0.39467 | 4736.04 | 1 | 5000 | 13556.52 | 4736.04 | 0 | 0 | 0 | 0 | 15717.04 | 0 | 0 | 0 | 0 | 0 | 15717.04
2022040710 | 5 | 0.49261 | 39408.8 | 0.36994 | 13317.84 | 0.76221 | 9146.52 | 1 | 5000 | 13317.84 | 9146.52 | 0 | 0 | 0 | 0 | 11944.44 | 0 | 0 | 0 | 0 | 0 | 11944.44
2022040711 | 5 | 0.50033 | 40026.4 | 0.49499 | 17819.64 | 0.66916 | 8029.92 | 1 | 5000 | 17819.64 | 8029.92 | 0 | 0 | 0 | 0 | 9176.84 | 0 | 0 | 0 | 0 | 0 | 9176.84
2022040712 | 5 | 0.50222 | 40177.6 | 0.48746 | 17548.56 | 0.73599 | 8831.88 | 1 | 5000 | 17548.56 | 8831.88 | 0 | 0 | 0 | 0 | 8797.16 | 0 | 0 | 0 | 0 | 0 | 8797.16
2022040713 | 5 | 0.5041 | 40328 | 0.4358 | 15688.8 | 0.83313 | 9997.56 | 1 | 5000 | 15688.8 | 9997.56 | 0 | 0 | 0 | 0 | 9641.64 | 0 | 0 | 0 | 0 | 0 | 9641.64
2022040714 | 5 | 0.50791 | 40632.8 | 0.39685 | 14286.6 | 0.84913 | 10189.56 | 1 | 5000 | 14286.6 | 10189.56 | 0 | 0 | 0 | 0 | 11156.64 | 0 | 0 | 0 | 0 | 0 | 11156.64
2022040715 | 5 | 0.51102 | 40881.6 | 0.38619 | 13902.84 | 0.84518 | 10142.16 | 1 | 5000 | 13902.84 | 10142.16 | 0 | 0 | 0 | 0 | 11836.6 | 0 | 0 | 0 | 0 | 0 | 11836.6
2022040716 | 5 | 0.51792 | 41433.6 | 0.39066 | 14063.76 | 0.82309 | 9877.08 | 1 | 5000 | 14063.76 | 9877.08 | 0 | 0 | 0 | 0 | 12492.76 | 0 | 0 | 0 | 0 | 0 | 12492.76
2022040717 | 5 | 0.52666 | 42132.8 | 0.40269 | 14496.84 | 0.78547 | 9425.64 | 1 | 5000 | 14496.84 | 9425.64 | 0 | 0 | 0 | 0 | 13210.32 | 0 | 0 | 0 | 0 | 0 | 13210.32
2022040718 | 5 | 0.5327 | 42616 | 0.39574 | 14246.64 | 0.77003 | 9240.36 | 1 | 5000 | 14246.64 | 9240.36 | 0 | 0 | 0 | 0 | 14129 | 0 | 0 | 0 | 0 | 0 | 14129
2022040719 | 5 | 0.52758 | 42206.4 | 0.36135 | 13008.6 | 0.59745 | 7169.4 | 1 | 5000 | 13008.6 | 7169.4 | 0 | 0 | 0 | 0 | 17028.4 | 0 | 0 | 0 | 0 | 0 | 17028.4
2022040720 | 5 | 0.52221 | 41776.8 | 0.31189 | 11228.04 | 0.16944 | 2033.28 | 1 | 5000 | 11228.04 | 2033.28 | 0 | 0 | 0 | 0 | 23515.48 | 0 | 0 | 0 | 0 | 0 | 23515.48
2022040721 | 5 | 0.52428 | 41942.4 | 0.24667 | 8880.12 | 0.00097 | 11.64 | 1 | 5000 | 8880.12 | 11.64 | 0 | 0 | 0 | 0 | 28050.64 | 0 | 0 | 0 | 0 | 0 | 28050.64
2022040722 | 5 | 0.50972 | 40777.6 | 0.23628 | 8506.08 | 0 | 0 | 1 | 5000 | 8506.08 | 0 | 0 | 0 | 0 | 0 | 27271.52 | 0 | 0 | 0 | 0 | 0 | 27271.52
2022040723 | 5 | 0.48051 | 38440.8 | 0.25819 | 9294.84 | 0 | 0 | 1 | 5000 | 9294.84 | 0 | 0 | 0 | 0 | 0 | 24145.96 | 0 | 0 | 0 | 0 | 0 | 24145.96
2022040724 | 5 | 0.44937 | 35949.6 | 0.27043 | 9735.48 | 0 | 0 | 1 | 5000 | 9735.48 | 0 | 0 | 0 | 0 | 0 | 21214.12 | 0 | 0 | 0 | 0 | 0 | 21214.12
2022040801 | 6 | 0.42579 | 34063.2 | 0.28189 | 10148.04 | 0 | 0 | 1 | 5000 | 10148.04 | 0 | 0 | 0 | 0 | 0 | 18915.16 | 0 | 0 | 0 | 0 | 0 | 18915.16
2022040802 | 6 | 0.41148 | 32918.4 | 0.28337 | 10201.32 | 0 | 0 | 1 | 5000 | 10201.32 | 0 | 0 | 0 | 0 | 0 | 17717.08 | 0 | 0 | 0 | 0 | 0 | 17717.08
2022040803 | 6 | 0.4042 | 32336 | 0.29645 | 10672.2 | 0 | 0 | 1 | 5000 | 10672.2 | 0 | 0 | 0 | 0 | 0 | 16663.8 | 0 | 0 | 0 | 0 | 0 | 16663.8
2022040804 | 6 | 0.4041 | 32328 | 0.30098 | 10835.28 | 0 | 0 | 1 | 5000 | 10835.28 | 0 | 0 | 0 | 0 | 0 | 16492.72 | 0 | 0 | 0 | 0 | 0 | 16492.72
2022040805 | 6 | 0.41133 | 32906.4 | 0.31419 | 11310.84 | 0 | 0 | 1 | 5000 | 11310.84 | 0 | 0 | 0 | 0 | 0 | 16595.56 | 0 | 0 | 0 | 0 | 0 | 16595.56
2022040806 | 6 | 0.43448 | 34758.4 | 0.30385 | 10938.6 | 0 | 0 | 1 | 5000 | 10938.6 | 0 | 0 | 0 | 0 | 0 | 18819.8 | 0 | 0 | 0 | 0 | 0 | 18819.8
2022040807 | 6 | 0.47493 | 37994.4 | 0.28888 | 10399.68 | 0 | 0 | 1 | 5000 | 10399.68 | 0 | 0 | 0 | 0 | 0 | 22594.72 | 0 | 0 | 0 | 0 | 0 | 22594.72
2022040808 | 6 | 0.49539 | 39631.2 | 0.29375 | 10575 | 0.02996 | 359.52 | 1 | 5000 | 10575 | 359.52 | 0 | 0 | 0 | 0 | 23696.68 | 0 | 0 | 0 | 0 | 0 | 23696.68
2022040809 | 6 | 0.49832 | 39865.6 | 0.26026 | 9369.36 | 0.42582 | 5109.84 | 1 | 5000 | 9369.36 | 5109.84 | 0 | 0 | 0 | 0 | 20386.4 | 0 | 0 | 0 | 0 | 0 | 20386.4
2022040810 | 6 | 0.4994 | 39952 | 0.23262 | 8374.32 | 0.80046 | 9605.52 | 1 | 5000 | 8374.32 | 9605.52 | 0 | 0 | 0 | 0 | 16972.16 | 0 | 0 | 0 | 0 | 0 | 16972.16
2022040811 | 6 | 0.49963 | 39970.4 | 0.24489 | 8816.04 | 0.84417 | 10130.04 | 1 | 5000 | 8816.04 | 10130.04 | 0 | 0 | 0 | 0 | 16024.32 | 0 | 0 | 0 | 0 | 0 | 16024.32
2022040812 | 6 | 0.49822 | 39857.6 | 0.23914 | 8609.04 | 0.85127 | 10215.24 | 1 | 5000 | 8609.04 | 10215.24 | 0 | 0 | 0 | 0 | 16033.32 | 0 | 0 | 0 | 0 | 0 | 16033.32
2022040813 | 6 | 0.49738 | 39790.4 | 0.24562 | 8842.32 | 0.85206 | 10224.72 | 1 | 5000 | 8842.32 | 10224.72 | 0 | 0 | 0 | 0 | 15723.36 | 0 | 0 | 0 | 0 | 0 | 15723.36
2022040814 | 6 | 0.50021 | 40016.8 | 0.23328 | 8398.08 | 0.84319 | 10118.28 | 1 | 5000 | 8398.08 | 10118.28 | 0 | 0 | 0 | 0 | 16500.44 | 0 | 0 | 0 | 0 | 0 | 16500.44
2022040815 | 6 | 0.50394 | 40315.2 | 0.23227 | 8361.72 | 0.8534 | 10240.8 | 1 | 5000 | 8361.72 | 10240.8 | 0 | 0 | 0 | 0 | 16712.68 | 0 | 0 | 0 | 0 | 0 | 16712.68
2022040816 | 6 | 0.50911 | 40728.8 | 0.25793 | 9285.48 | 0.85176 | 10221.12 | 1 | 5000 | 9285.48 | 10221.12 | 0 | 0 | 0 | 0 | 16222.2 | 0 | 0 | 0 | 0 | 0 | 16222.2
2022040817 | 6 | 0.51572 | 41257.6 | 0.28844 | 10383.84 | 0.84682 | 10161.84 | 1 | 5000 | 10383.84 | 10161.84 | 0 | 0 | 0 | 0 | 15711.92 | 0 | 0 | 0 | 0 | 0 | 15711.92
2022040818 | 6 | 0.51883 | 41506.4 | 0.28525 | 10269 | 0.82633 | 9915.96 | 1 | 5000 | 10269 | 9915.96 | 0 | 0 | 0 | 0 | 16321.44 | 0 | 0 | 0 | 0 | 0 | 16321.44
2022040819 | 6 | 0.51396 | 41116.8 | 0.23324 | 8396.64 | 0.64888 | 7786.56 | 1 | 5000 | 8396.64 | 7786.56 | 0 | 0 | 0 | 0 | 19933.6 | 0 | 0 | 0 | 0 | 0 | 19933.6
2022040820 | 6 | 0.50621 | 40496.8 | 0.15424 | 5552.64 | 0.17522 | 2102.64 | 1 | 5000 | 5552.64 | 2102.64 | 0 | 0 | 0 | 0 | 27841.52 | 0 | 0 | 0 | 0 | 0 | 27841.52
2022040821 | 6 | 0.5075 | 40600 | 0.11998 | 4319.28 | 0.00128 | 15.36 | 1 | 5000 | 4319.28 | 15.36 | 0 | 0 | 0 | 0 | 31265.36 | 0 | 0 | 0 | 0 | 0 | 31265.36
2022040822 | 6 | 0.49788 | 39830.4 | 0.13326 | 4797.36 | 0 | 0 | 1 | 5000 | 4797.36 | 0 | 0 | 0 | 0 | 0 | 30033.04 | 0 | 0 | 0 | 0 | 0 | 30033.04
2022040823 | 6 | 0.47653 | 38122.4 | 0.16032 | 5771.52 | 0 | 0 | 1 | 5000 | 5771.52 | 0 | 0 | 0 | 0 | 0 | 27350.88 | 0 | 0 | 0 | 0 | 0 | 27350.88
2022040824 | 6 | 0.45218 | 36174.4 | 0.2002 | 7207.2 | 0 | 0 | 1 | 5000 | 7207.2 | 0 | 0 | 0 | 0 | 0 | 23967.2 | 0 | 0 | 0 | 0 | 0 | 23967.2
2022040901 | 7 | 0.43124 | 34499.2 | 0.25796 | 9286.56 | 0 | 0 | 1 | 5000 | 9286.56 | 0 | 0 | 0 | 0 | 0 | 20212.64 | 0 | 0 | 0 | 0 | 0 | 20212.64
2022040902 | 7 | 0.41869 | 33495.2 | 0.31023 | 11168.28 | 0 | 0 | 1 | 5000 | 11168.28 | 0 | 0 | 0 | 0 | 0 | 17326.92 | 0 | 0 | 0 | 0 | 0 | 17326.92
2022040903 | 7 | 0.41162 | 32929.6 | 0.37877 | 13635.72 | 0 | 0 | 1 | 5000 | 13635.72 | 0 | 0 | 0 | 0 | 0 | 14293.88 | 0 | 0 | 0 | 0 | 0 | 14293.88
2022040904 | 7 | 0.41013 | 32810.4 | 0.46822 | 16855.92 | 0 | 0 | 1 | 5000 | 16855.92 | 0 | 0 | 0 | 0 | 0 | 10954.48 | 0 | 0 | 0 | 0 | 0 | 10954.48
2022040905 | 7 | 0.41521 | 33216.8 | 0.55758 | 20072.88 | 0 | 0 | 1 | 5000 | 20072.88 | 0 | 0 | 0 | 0 | 0 | 8143.92 | 0 | 0 | 0 | 0 | 0 | 8143.92
2022040906 | 7 | 0.42789 | 34231.2 | 0.6083 | 21898.8 | 0 | 0 | 1 | 5000 | 21898.8 | 0 | 0 | 0 | 0 | 0 | 7332.4 | 0 | 0 | 0 | 0 | 0 | 7332.4
2022040907 | 7 | 0.4473 | 35784 | 0.64721 | 23299.56 | 0 | 0 | 1 | 5000 | 23299.56 | 0 | 0 | 0 | 0 | 0 | 7484.44 | 0 | 0 | 0 | 0 | 0 | 7484.44
2022040908 | 7 | 0.46535 | 37228 | 0.64036 | 23052.96 | 0.03543 | 425.16 | 1 | 5000 | 23052.96 | 425.16 | 0 | 0 | 0 | 0 | 8749.88 | 0 | 0 | 0 | 0 | 0 | 8749.88
2022040909 | 7 | 0.47782 | 38225.6 | 0.57993 | 20877.48 | 0.31116 | 3733.92 | 1 | 5000 | 20877.48 | 3733.92 | 0 | 0 | 0 | 0 | 8614.2 | 0 | 0 | 0 | 0 | 0 | 8614.2
2022040910 | 7 | 0.4851 | 38808 | 0.54606 | 19658.16 | 0.51473 | 6176.76 | 1 | 5000 | 19658.16 | 6176.76 | 0 | 0 | 0 | 0 | 7973.08 | 0 | 0 | 0 | 0 | 0 | 7973.08
2022040911 | 7 | 0.48697 | 38957.6 | 0.59922 | 21571.92 | 0.46237 | 5548.44 | 1 | 5000 | 21571.92 | 5548.44 | 0 | 0 | 0 | 0 | 6837.24 | 0 | 0 | 0 | 0 | 0 | 6837.24
2022040912 | 7 | 0.49111 | 39288.8 | 0.61435 | 22116.6 | 0.42842 | 5141.04 | 1 | 5000 | 22116.6 | 5141.04 | 0 | 0 | 0 | 0 | 7031.16 | 0 | 0 | 0 | 0 | 0 | 7031.16
2022040913 | 7 | 0.49615 | 39692 | 0.6298 | 22672.8 | 0.3982 | 4778.4 | 1 | 5000 | 22672.8 | 4778.4 | 0 | 0 | 0 | 0 | 7240.8 | 0 | 0 | 0 | 0 | 0 | 7240.8
2022040914 | 7 | 0.50774 | 40619.2 | 0.64305 | 23149.8 | 0.39713 | 4765.56 | 1 | 5000 | 23149.8 | 4765.56 | 0 | 0 | 0 | 0 | 7703.84 | 0 | 0 | 0 | 0 | 0 | 7703.84
2022040915 | 7 | 0.52259 | 41807.2 | 0.64703 | 23293.08 | 0.40729 | 4887.48 | 1 | 5000 | 23293.08 | 4887.48 | 0 | 0 | 0 | 0 | 8626.64 | 0 | 0 | 0 | 0 | 0 | 8626.64
2022040916 | 7 | 0.53959 | 43167.2 | 0.65765 | 23675.4 | 0.38819 | 4658.28 | 1 | 5000 | 23675.4 | 4658.28 | 0 | 0 | 0 | 0 | 9833.52 | 0 | 0 | 0 | 0 | 0 | 9833.52
2022040917 | 7 | 0.55879 | 44703.2 | 0.66609 | 23979.24 | 0.37163 | 4459.56 | 1 | 5000 | 23979.24 | 4459.56 | 0 | 0 | 0 | 0 | 11264.4 | 0 | 0 | 0 | 0 | 0 | 11264.4
2022040918 | 7 | 0.57171 | 45736.8 | 0.66364 | 23891.04 | 0.36964 | 4435.68 | 1 | 5000 | 23891.04 | 4435.68 | 0 | 0 | 0 | 0 | 12410.08 | 0 | 0 | 0 | 0 | 0 | 12410.08
2022040919 | 7 | 0.5706 | 45648 | 0.65794 | 23685.84 | 0.29835 | 3580.2 | 1 | 5000 | 23685.84 | 3580.2 | 0 | 0 | 0 | 0 | 13381.96 | 0 | 0 | 0 | 0 | 0 | 13381.96
2022040920 | 7 | 0.55619 | 44495.2 | 0.66313 | 23872.68 | 0.11791 | 1414.92 | 1 | 5000 | 23872.68 | 1414.92 | 0 | 0 | 0 | 0 | 14207.6 | 0 | 0 | 0 | 0 | 0 | 14207.6
2022040921 | 7 | 0.5517 | 44136 | 0.70707 | 25454.52 | 0.00125 | 15 | 1 | 5000 | 25454.52 | 15 | 0 | 0 | 0 | 0 | 13666.48 | 0 | 0 | 0 | 0 | 0 | 13666.48
2022040922 | 7 | 0.53689 | 42951.2 | 0.72134 | 25968.24 | 0 | 0 | 1 | 5000 | 25968.24 | 0 | 0 | 0 | 0 | 0 | 11982.96 | 0 | 0 | 0 | 0 | 0 | 11982.96
2022040923 | 7 | 0.51194 | 40955.2 | 0.70949 | 25541.64 | 0 | 0 | 1 | 5000 | 25541.64 | 0 | 0 | 0 | 0 | 0 | 10413.56 | 0 | 0 | 0 | 0 | 0 | 10413.56
2022040924 | 7 | 0.4837 | 38696 | 0.70319 | 25314.84 | 0 | 0 | 1 | 5000 | 25314.84 | 0 | 0 | 0 | 0 | 0 | 8381.16 | 0 | 0 | 0 | 0 | 0 | 8381.16
2022041001 | 1 | 0.45795 | 36636 | 0.69519 | 25026.84 | 0 | 0 | 1 | 5000 | 25026.84 | 0 | 0 | 0 | 0 | 0 | 6609.16 | 0 | 0 | 0 | 0 | 0 | 6609.16
2022041002 | 1 | 0.43864 | 35091.2 | 0.67671 | 24361.56 | 0 | 0 | 1 | 5000 | 24361.56 | 0 | 0 | 0 | 0 | 0 | 5729.64 | 0 | 0 | 0 | 0 | 0 | 5729.64
2022041003 | 1 | 0.42312 | 33849.6 | 0.64855 | 23347.8 | 0 | 0 | 1 | 5000 | 23347.8 | 0 | 0 | 0 | 0 | 0 | 5501.8 | 0 | 0 | 0 | 0 | 0 | 5501.8
2022041004 | 1 | 0.41312 | 33049.6 | 0.62475 | 22491 | 0 | 0 | 1 | 5000 | 22491 | 0 | 0 | 0 | 0 | 0 | 5558.6 | 0 | 0 | 0 | 0 | 0 | 5558.6
2022041005 | 1 | 0.40997 | 32797.6 | 0.61952 | 22302.72 | 0 | 0 | 1 | 5000 | 22302.72 | 0 | 0 | 0 | 0 | 0 | 5494.88 | 0 | 0 | 0 | 0 | 0 | 5494.88
2022041006 | 1 | 0.41119 | 32895.2 | 0.62491 | 22496.76 | 0 | 0 | 1 | 5000 | 22496.76 | 0 | 0 | 0 | 0 | 0 | 5398.44 | 0 | 0 | 0 | 0 | 0 | 5398.44
2022041007 | 1 | 0.41857 | 33485.6 | 0.63951 | 23022.36 | 0 | 0 | 1 | 5000 | 23022.36 | 0 | 0 | 0 | 0 | 0 | 5463.24 | 0 | 0 | 0 | 0 | 0 | 5463.24
2022041008 | 1 | 0.42636 | 34108.8 | 0.65089 | 23432.04 | 0.01648 | 197.76 | 1 | 5000 | 23432.04 | 197.76 | 0 | 0 | 0 | 0 | 5479 | 0 | 0 | 0 | 0 | 0 | 5479
2022041009 | 1 | 0.4493 | 35944 | 0.64551 | 23238.36 | 0.21771 | 2612.52 | 1 | 5000 | 23238.36 | 2612.52 | 0 | 0 | 0 | 0 | 5093.12 | 0 | 0 | 0 | 0 | 0 | 5093.12
2022041010 | 1 | 0.47453 | 37962.4 | 0.61579 | 22168.44 | 0.39106 | 4692.72 | 1 | 5000 | 22168.44 | 4692.72 | 0 | 0 | 0 | 0 | 6101.24 | 0 | 0 | 0 | 0 | 0 | 6101.24
2022041011 | 1 | 0.49842 | 39873.6 | 0.58645 | 21112.2 | 0.49879 | 5985.48 | 1 | 5000 | 21112.2 | 5985.48 | 0 | 0 | 0 | 0 | 7775.92 | 0 | 0 | 0 | 0 | 0 | 7775.92
2022041012 | 1 | 0.51897 | 41517.6 | 0.53449 | 19241.64 | 0.61844 | 7421.28 | 1 | 5000 | 19241.64 | 7421.28 | 0 | 0 | 0 | 0 | 9854.68 | 0 | 0 | 0 | 0 | 0 | 9854.68
2022041013 | 1 | 0.53402 | 42721.6 | 0.46601 | 16776.36 | 0.58669 | 7040.28 | 1 | 5000 | 16776.36 | 7040.28 | 0 | 0 | 0 | 0 | 13904.96 | 0 | 0 | 0 | 0 | 0 | 13904.96
2022041014 | 1 | 0.55174 | 44139.2 | 0.4167 | 15001.2 | 0.5759 | 6910.8 | 1 | 5000 | 15001.2 | 6910.8 | 0 | 0 | 0 | 0 | 17227.2 | 0 | 0 | 0 | 0 | 0 | 17227.2
2022041015 | 1 | 0.57067 | 45653.6 | 0.4128 | 14860.8 | 0.59835 | 7180.2 | 1 | 5000 | 14860.8 | 7180.2 | 0 | 0 | 0 | 0 | 18612.6 | 0 | 0 | 0 | 0 | 0 | 18612.6
2022041016 | 1 | 0.58962 | 47169.6 | 0.45115 | 16241.4 | 0.5914 | 7096.8 | 1 | 5000 | 16241.4 | 7096.8 | 0 | 0 | 0 | 0 | 18831.4 | 0 | 0 | 0 | 0 | 0 | 18831.4
2022041017 | 1 | 0.59849 | 47879.2 | 0.47771 | 17197.56 | 0.57772 | 6932.64 | 1 | 5000 | 17197.56 | 6932.64 | 0 | 0 | 0 | 0 | 18749 | 0 | 0 | 0 | 0 | 0 | 18749
2022041018 | 1 | 0.60304 | 48243.2 | 0.50228 | 18082.08 | 0.50367 | 6044.04 | 1 | 5000 | 18082.08 | 6044.04 | 0 | 0 | 0 | 0 | 19117.08 | 0 | 0 | 0 | 0 | 0 | 19117.08
2022041019 | 1 | 0.59758 | 47806.4 | 0.5091 | 18327.6 | 0.42876 | 5145.12 | 1 | 5000 | 18327.6 | 5145.12 | 0 | 0 | 0 | 0 | 19333.68 | 0 | 0 | 0 | 0 | 0 | 19333.68
2022041020 | 1 | 0.59133 | 47306.4 | 0.50634 | 18228.24 | 0.16034 | 1924.08 | 1 | 5000 | 18228.24 | 1924.08 | 0 | 0 | 0 | 0 | 22154.08 | 0 | 0 | 0 | 0 | 0 | 22154.08
2022041021 | 1 | 0.59211 | 47368.8 | 0.52041 | 18734.76 | 0.0058 | 69.6 | 1 | 5000 | 18734.76 | 69.6 | 0 | 0 | 0 | 0 | 23564.44 | 0 | 0 | 0 | 0 | 0 | 23564.44
2022041022 | 1 | 0.57748 | 46198.4 | 0.54305 | 19549.8 | 0 | 0 | 1 | 5000 | 19549.8 | 0 | 0 | 0 | 0 | 0 | 21648.6 | 0 | 0 | 0 | 0 | 0 | 21648.6
2022041023 | 1 | 0.54747 | 43797.6 | 0.54331 | 19559.16 | 0 | 0 | 1 | 5000 | 19559.16 | 0 | 0 | 0 | 0 | 0 | 19238.44 | 0 | 0 | 0 | 0 | 0 | 19238.44
2022041024 | 1 | 0.50978 | 40782.4 | 0.54226 | 19521.36 | 0 | 0 | 1 | 5000 | 19521.36 | 0 | 0 | 0 | 0 | 0 | 16261.04 | 0 | 0 | 0 | 0 | 0 | 16261.04
2022041101 | 2 | 0.47996 | 38396.8 | 0.574 | 20664 | 0 | 0 | 1 | 5000 | 20664 | 0 | 0 | 0 | 0 | 0 | 12732.8 | 0 | 0 | 0 | 0 | 0 | 12732.8
2022041102 | 2 | 0.46097 | 36877.6 | 0.59854 | 21547.44 | 0 | 0 | 1 | 5000 | 21547.44 | 0 | 0 | 0 | 0 | 0 | 10330.16 | 0 | 0 | 0 | 0 | 0 | 10330.16
2022041103 | 2 | 0.45196 | 36156.8 | 0.61604 | 22177.44 | 0 | 0 | 1 | 5000 | 22177.44 | 0 | 0 | 0 | 0 | 0 | 8979.36 | 0 | 0 | 0 | 0 | 0 | 8979.36
2022041104 | 2 | 0.44782 | 35825.6 | 0.61948 | 22301.28 | 0 | 0 | 1 | 5000 | 22301.28 | 0 | 0 | 0 | 0 | 0 | 8524.32 | 0 | 0 | 0 | 0 | 0 | 8524.32
2022041105 | 2 | 0.45398 | 36318.4 | 0.59953 | 21583.08 | 0 | 0 | 1 | 5000 | 21583.08 | 0 | 0 | 0 | 0 | 0 | 9735.32 | 0 | 0 | 0 | 0 | 0 | 9735.32
2022041106 | 2 | 0.47113 | 37690.4 | 0.53541 | 19274.76 | 0 | 0 | 1 | 5000 | 19274.76 | 0 | 0 | 0 | 0 | 0 | 13415.64 | 0 | 0 | 0 | 0 | 0 | 13415.64
2022041107 | 2 | 0.5022 | 40176 | 0.48363 | 17410.68 | 0 | 0 | 1 | 5000 | 17410.68 | 0 | 0 | 0 | 0 | 0 | 17765.32 | 0 | 0 | 0 | 0 | 0 | 17765.32
2022041108 | 2 | 0.51832 | 41465.6 | 0.44618 | 16062.48 | 0.02289 | 274.68 | 1 | 5000 | 16062.48 | 274.68 | 0 | 0 | 0 | 0 | 20128.44 | 0 | 0 | 0 | 0 | 0 | 20128.44
2022041109 | 2 | 0.52797 | 42237.6 | 0.38214 | 13757.04 | 0.35014 | 4201.68 | 1 | 5000 | 13757.04 | 4201.68 | 0 | 0 | 0 | 0 | 19278.88 | 0 | 0 | 0 | 0 | 0 | 19278.88
2022041110 | 2 | 0.54757 | 43805.6 | 0.3506 | 12621.6 | 0.64678 | 7761.36 | 1 | 5000 | 12621.6 | 7761.36 | 0 | 0 | 0 | 0 | 18422.64 | 0 | 0 | 0 | 0 | 0 | 18422.64
2022041111 | 2 | 0.56795 | 45436 | 0.35899 | 12923.64 | 0.72168 | 8660.16 | 1 | 5000 | 12923.64 | 8660.16 | 0 | 0 | 0 | 0 | 18852.2 | 0 | 0 | 0 | 0 | 0 | 18852.2
2022041112 | 2 | 0.58497 | 46797.6 | 0.32685 | 11766.6 | 0.74376 | 8925.12 | 1 | 5000 | 11766.6 | 8925.12 | 0 | 0 | 0 | 0 | 21105.88 | 0 | 0 | 0 | 0 | 0 | 21105.88
2022041113 | 2 | 0.60581 | 48464.8 | 0.24686 | 8886.96 | 0.77061 | 9247.32 | 1 | 5000 | 8886.96 | 9247.32 | 0 | 0 | 0 | 0 | 25330.52 | 0 | 0 | 0 | 0 | 0 | 25330.52
2022041114 | 2 | 0.62427 | 49941.6 | 0.18923 | 6812.28 | 0.77121 | 9254.52 | 1 | 5000 | 6812.28 | 9254.52 | 0 | 0 | 0 | 0 | 28874.8 | 0 | 0 | 0 | 0 | 0 | 28874.8
2022041115 | 2 | 0.64212 | 51369.6 | 0.16988 | 6115.68 | 0.76434 | 9172.08 | 1 | 5000 | 6115.68 | 9172.08 | 0 | 0 | 0 | 0 | 31081.84 | 0 | 0 | 0 | 0 | 0 | 31081.84
2022041116 | 2 | 0.65911 | 52728.8 | 0.17824 | 6416.64 | 0.761 | 9132 | 1 | 5000 | 6416.64 | 9132 | 0 | 0 | 0 | 0 | 32180.16 | 0 | 0 | 0 | 0 | 0 | 32180.16
2022041117 | 2 | 0.67648 | 54118.4 | 0.19987 | 7195.32 | 0.73939 | 8872.68 | 1 | 5000 | 7195.32 | 8872.68 | 0 | 0 | 0 | 0 | 33050.4 | 0 | 0 | 0 | 0 | 0 | 33050.4
2022041118 | 2 | 0.68235 | 54588 | 0.21787 | 7843.32 | 0.7374 | 8848.8 | 1 | 5000 | 7843.32 | 8848.8 | 0 | 0 | 0 | 0 | 32895.88 | 0 | 0 | 0 | 0 | 0 | 32895.88
2022041119 | 2 | 0.67275 | 53820 | 0.25562 | 9202.32 | 0.58092 | 6971.04 | 1 | 5000 | 9202.32 | 6971.04 | 0 | 0 | 0 | 0 | 32646.64 | 0 | 0 | 0 | 0 | 0 | 32646.64
2022041120 | 2 | 0.65659 | 52527.2 | 0.27868 | 10032.48 | 0.18379 | 2205.48 | 1 | 5000 | 10032.48 | 2205.48 | 0 | 0 | 0 | 0 | 35289.24 | 0 | 0 | 0 | 0 | 0 | 35289.24
2022041121 | 2 | 0.6494 | 51952 | 0.32239 | 11606.04 | 0.00192 | 23.04 | 1 | 5000 | 11606.04 | 23.04 | 0 | 0 | 0 | 0 | 35322.92 | 0 | 0 | 0 | 0 | 0 | 35322.92
2022041122 | 2 | 0.63191 | 50552.8 | 0.42026 | 15129.36 | 0 | 0 | 1 | 5000 | 15129.36 | 0 | 0 | 0 | 0 | 0 | 30423.44 | 0 | 0 | 0 | 0 | 0 | 30423.44
2022041123 | 2 | 0.59478 | 47582.4 | 0.5212 | 18763.2 | 0 | 0 | 1 | 5000 | 18763.2 | 0 | 0 | 0 | 0 | 0 | 23819.2 | 0 | 0 | 0 | 0 | 0 | 23819.2
2022041124 | 2 | 0.55258 | 44206.4 | 0.59475 | 21411 | 0 | 0 | 1 | 5000 | 21411 | 0 | 0 | 0 | 0 | 0 | 17795.4 | 0 | 0 | 0 | 0 | 0 | 17795.4
2022041201 | 3 | 0.52015 | 41612 | 0.61789 | 22244.04 | 0 | 0 | 1 | 5000 | 22244.04 | 0 | 0 | 0 | 0 | 0 | 14367.96 | 0 | 0 | 0 | 0 | 0 | 14367.96
2022041202 | 3 | 0.49788 | 39830.4 | 0.61109 | 21999.24 | 0 | 0 | 1 | 5000 | 21999.24 | 0 | 0 | 0 | 0 | 0 | 12831.16 | 0 | 0 | 0 | 0 | 0 | 12831.16
2022041203 | 3 | 0.48246 | 38596.8 | 0.5898 | 21232.8 | 0 | 0 | 1 | 5000 | 21232.8 | 0 | 0 | 0 | 0 | 0 | 12364 | 0 | 0 | 0 | 0 | 0 | 12364
2022041204 | 3 | 0.47685 | 38148 | 0.57472 | 20689.92 | 0 | 0 | 1 | 5000 | 20689.92 | 0 | 0 | 0 | 0 | 0 | 12458.08 | 0 | 0 | 0 | 0 | 0 | 12458.08
2022041205 | 3 | 0.48084 | 38467.2 | 0.57731 | 20783.16 | 0 | 0 | 1 | 5000 | 20783.16 | 0 | 0 | 0 | 0 | 0 | 12684.04 | 0 | 0 | 0 | 0 | 0 | 12684.04
2022041206 | 3 | 0.49921 | 39936.8 | 0.59634 | 21468.24 | 0 | 0 | 1 | 5000 | 21468.24 | 0 | 0 | 0 | 0 | 0 | 13468.56 | 0 | 0 | 0 | 0 | 0 | 13468.56
2022041207 | 3 | 0.53379 | 42703.2 | 0.60819 | 21894.84 | 0 | 0 | 1 | 5000 | 21894.84 | 0 | 0 | 0 | 0 | 0 | 15808.36 | 0 | 0 | 0 | 0 | 0 | 15808.36
2022041208 | 3 | 0.54965 | 43972 | 0.58996 | 21238.56 | 0.01007 | 120.84 | 1 | 5000 | 21238.56 | 120.84 | 0 | 0 | 0 | 0 | 17612.6 | 0 | 0 | 0 | 0 | 0 | 17612.6
2022041209 | 3 | 0.55607 | 44485.6 | 0.55192 | 19869.12 | 0.15893 | 1907.16 | 1 | 5000 | 19869.12 | 1907.16 | 0 | 0 | 0 | 0 | 17709.32 | 0 | 0 | 0 | 0 | 0 | 17709.32
2022041210 | 3 | 0.56815 | 45452 | 0.53535 | 19272.6 | 0.21901 | 2628.12 | 1 | 5000 | 19272.6 | 2628.12 | 0 | 0 | 0 | 0 | 18551.28 | 0 | 0 | 0 | 0 | 0 | 18551.28
2022041211 | 3 | 0.58262 | 46609.6 | 0.54191 | 19508.76 | 0.23469 | 2816.28 | 1 | 5000 | 19508.76 | 2816.28 | 0 | 0 | 0 | 0 | 19284.56 | 0 | 0 | 0 | 0 | 0 | 19284.56
2022041212 | 3 | 0.59681 | 47744.8 | 0.52871 | 19033.56 | 0.31631 | 3795.72 | 1 | 5000 | 19033.56 | 3795.72 | 0 | 0 | 0 | 0 | 19915.52 | 0 | 0 | 0 | 0 | 0 | 19915.52
2022041213 | 3 | 0.61294 | 49035.2 | 0.52548 | 18917.28 | 0.35626 | 4275.12 | 1 | 5000 | 18917.28 | 4275.12 | 0 | 0 | 0 | 0 | 20842.8 | 0 | 0 | 0 | 0 | 0 | 20842.8
2022041214 | 3 | 0.63532 | 50825.6 | 0.53737 | 19345.32 | 0.36556 | 4386.72 | 1 | 5000 | 19345.32 | 4386.72 | 0 | 0 | 0 | 0 | 22093.56 | 0 | 0 | 0 | 0 | 0 | 22093.56
2022041215 | 3 | 0.65378 | 52302.4 | 0.5669 | 20408.4 | 0.31323 | 3758.76 | 1 | 5000 | 20408.4 | 3758.76 | 0 | 0 | 0 | 0 | 23135.24 | 0 | 0 | 0 | 0 | 0 | 23135.24
2022041216 | 3 | 0.66642 | 53313.6 | 0.58558 | 21080.88 | 0.29689 | 3562.68 | 1 | 5000 | 21080.88 | 3562.68 | 0 | 0 | 0 | 0 | 23670.04 | 0 | 0 | 0 | 0 | 0 | 23670.04
2022041217 | 3 | 0.67648 | 54118.4 | 0.60799 | 21887.64 | 0.24113 | 2893.56 | 1 | 5000 | 21887.64 | 2893.56 | 0 | 0 | 0 | 0 | 24337.2 | 0 | 0 | 0 | 0 | 0 | 24337.2
2022041218 | 3 | 0.68178 | 54542.4 | 0.61864 | 22271.04 | 0.17494 | 2099.28 | 1 | 5000 | 22271.04 | 2099.28 | 0 | 0 | 0 | 0 | 25172.08 | 0 | 0 | 0 | 0 | 0 | 25172.08
2022041219 | 3 | 0.66973 | 53578.4 | 0.60527 | 21789.72 | 0.13386 | 1606.32 | 1 | 5000 | 21789.72 | 1606.32 | 0 | 0 | 0 | 0 | 25182.36 | 0 | 0 | 0 | 0 | 0 | 25182.36
2022041220 | 3 | 0.65006 | 52004.8 | 0.60506 | 21782.16 | 0.05816 | 697.92 | 1 | 5000 | 21782.16 | 697.92 | 0 | 0 | 0 | 0 | 24524.72 | 0 | 0 | 0 | 0 | 0 | 24524.72
2022041221 | 3 | 0.63845 | 51076 | 0.60301 | 21708.36 | 0.00139 | 16.68 | 1 | 5000 | 21708.36 | 16.68 | 0 | 0 | 0 | 0 | 24350.96 | 0 | 0 | 0 | 0 | 0 | 24350.96
2022041222 | 3 | 0.618 | 49440 | 0.60733 | 21863.88 | 0 | 0 | 1 | 5000 | 21863.88 | 0 | 0 | 0 | 0 | 0 | 22576.12 | 0 | 0 | 0 | 0 | 0 | 22576.12
2022041223 | 3 | 0.58208 | 46566.4 | 0.58227 | 20961.72 | 0 | 0 | 1 | 5000 | 20961.72 | 0 | 0 | 0 | 0 | 0 | 20604.68 | 0 | 0 | 0 | 0 | 0 | 20604.68
2022041224 | 3 | 0.54158 | 43326.4 | 0.57398 | 20663.28 | 0 | 0 | 1 | 5000 | 20663.28 | 0 | 0 | 0 | 0 | 0 | 17663.12 | 0 | 0 | 0 | 0 | 0 | 17663.12
2022041301 | 4 | 0.51321 | 41056.8 | 0.58219 | 20958.84 | 0 | 0 | 1 | 5000 | 20958.84 | 0 | 0 | 0 | 0 | 0 | 15097.96 | 0 | 0 | 0 | 0 | 0 | 15097.96
2022041302 | 4 | 0.49385 | 39508 | 0.57776 | 20799.36 | 0 | 0 | 1 | 5000 | 20799.36 | 0 | 0 | 0 | 0 | 0 | 13708.64 | 0 | 0 | 0 | 0 | 0 | 13708.64
2022041303 | 4 | 0.48278 | 38622.4 | 0.58225 | 20961 | 0 | 0 | 1 | 5000 | 20961 | 0 | 0 | 0 | 0 | 0 | 12661.4 | 0 | 0 | 0 | 0 | 0 | 12661.4
2022041304 | 4 | 0.4783 | 38264 | 0.59516 | 21425.76 | 0 | 0 | 1 | 5000 | 21425.76 | 0 | 0 | 0 | 0 | 0 | 11838.24 | 0 | 0 | 0 | 0 | 0 | 11838.24
2022041305 | 4 | 0.48443 | 38754.4 | 0.59487 | 21415.32 | 0 | 0 | 1 | 5000 | 21415.32 | 0 | 0 | 0 | 0 | 0 | 12339.08 | 0 | 0 | 0 | 0 | 0 | 12339.08
2022041306 | 4 | 0.50471 | 40376.8 | 0.58689 | 21128.04 | 0 | 0 | 1 | 5000 | 21128.04 | 0 | 0 | 0 | 0 | 0 | 14248.76 | 0 | 0 | 0 | 0 | 0 | 14248.76
2022041307 | 4 | 0.54054 | 43243.2 | 0.60783 | 21881.88 | 0 | 0 | 1 | 5000 | 21881.88 | 0 | 0 | 0 | 0 | 0 | 16361.32 | 0 | 0 | 0 | 0 | 0 | 16361.32
2022041308 | 4 | 0.55721 | 44576.8 | 0.61434 | 22116.24 | 0.0162 | 194.4 | 1 | 5000 | 22116.24 | 194.4 | 0 | 0 | 0 | 0 | 17266.16 | 0 | 0 | 0 | 0 | 0 | 17266.16
2022041309 | 4 | 0.56397 | 45117.6 | 0.5507 | 19825.2 | 0.2205 | 2646 | 1 | 5000 | 19825.2 | 2646 | 0 | 0 | 0 | 0 | 17646.4 | 0 | 0 | 0 | 0 | 0 | 17646.4
2022041310 | 4 | 0.57359 | 45887.2 | 0.4829 | 17384.4 | 0.39364 | 4723.68 | 1 | 5000 | 17384.4 | 4723.68 | 0 | 0 | 0 | 0 | 18779.12 | 0 | 0 | 0 | 0 | 0 | 18779.12
2022041311 | 4 | 0.59111 | 47288.8 | 0.39256 | 14132.16 | 0.66888 | 8026.56 | 1 | 5000 | 14132.16 | 8026.56 | 0 | 0 | 0 | 0 | 20130.08 | 0 | 0 | 0 | 0 | 0 | 20130.08
2022041312 | 4 | 0.60609 | 48487.2 | 0.405 | 14580 | 0.6695 | 8034 | 1 | 5000 | 14580 | 8034 | 0 | 0 | 0 | 0 | 20873.2 | 0 | 0 | 0 | 0 | 0 | 20873.2
2022041313 | 4 | 0.62206 | 49764.8 | 0.43836 | 15780.96 | 0.6011 | 7213.2 | 1 | 5000 | 15780.96 | 7213.2 | 0 | 0 | 0 | 0 | 21770.64 | 0 | 0 | 0 | 0 | 0 | 21770.64
2022041314 | 4 | 0.63494 | 50795.2 | 0.452 | 16272 | 0.521 | 6252 | 1 | 5000 | 16272 | 6252 | 0 | 0 | 0 | 0 | 23271.2 | 0 | 0 | 0 | 0 | 0 | 23271.2
2022041315 | 4 | 0.64323 | 51458.4 | 0.46341 | 16682.76 | 0.45316 | 5437.92 | 1 | 5000 | 16682.76 | 5437.92 | 0 | 0 | 0 | 0 | 24337.72 | 0 | 0 | 0 | 0 | 0 | 24337.72
2022041316 | 4 | 0.64949 | 51959.2 | 0.45829 | 16498.44 | 0.48815 | 5857.8 | 1 | 5000 | 16498.44 | 5857.8 | 0 | 0 | 0 | 0 | 24602.96 | 0 | 0 | 0 | 0 | 0 | 24602.96
2022041317 | 4 | 0.6613 | 52904 | 0.44043 | 15855.48 | 0.5388 | 6465.6 | 1 | 5000 | 15855.48 | 6465.6 | 0 | 0 | 0 | 0 | 25582.92 | 0 | 0 | 0 | 0 | 0 | 25582.92
2022041318 | 4 | 0.6681 | 53448 | 0.42302 | 15228.72 | 0.59171 | 7100.52 | 1 | 5000 | 15228.72 | 7100.52 | 0 | 0 | 0 | 0 | 26118.76 | 0 | 0 | 0 | 0 | 0 | 26118.76
2022041319 | 4 | 0.65614 | 52491.2 | 0.3534 | 12722.4 | 0.61075 | 7329 | 1 | 5000 | 12722.4 | 7329 | 0 | 0 | 0 | 0 | 27439.8 | 0 | 0 | 0 | 0 | 0 | 27439.8
2022041320 | 4 | 0.63035 | 50428 | 0.24997 | 8998.92 | 0.19771 | 2372.52 | 1 | 5000 | 8998.92 | 2372.52 | 0 | 0 | 0 | 0 | 34056.56 | 0 | 0 | 0 | 0 | 0 | 34056.56
2022041321 | 4 | 0.61561 | 49248.8 | 0.19319 | 6954.84 | 0.00231 | 27.72 | 1 | 5000 | 6954.84 | 27.72 | 0 | 0 | 0 | 0 | 37266.24 | 0 | 0 | 0 | 0 | 0 | 37266.24
2022041322 | 4 | 0.59217 | 47373.6 | 0.21002 | 7560.72 | 0 | 0 | 1 | 5000 | 7560.72 | 0 | 0 | 0 | 0 | 0 | 34812.88 | 0 | 0 | 0 | 0 | 0 | 34812.88
2022041323 | 4 | 0.54908 | 43926.4 | 0.21473 | 7730.28 | 0 | 0 | 1 | 5000 | 7730.28 | 0 | 0 | 0 | 0 | 0 | 31196.12 | 0 | 0 | 0 | 0 | 0 | 31196.12
2022041324 | 4 | 0.50358 | 40286.4 | 0.22268 | 8016.48 | 0 | 0 | 1 | 5000 | 8016.48 | 0 | 0 | 0 | 0 | 0 | 27269.92 | 0 | 0 | 0 | 0 | 0 | 27269.92
2022041401 | 5 | 0.46725 | 37380 | 0.23116 | 8321.76 | 0 | 0 | 1 | 5000 | 8321.76 | 0 | 0 | 0 | 0 | 0 | 24058.24 | 0 | 0 | 0 | 0 | 0 | 24058.24
2022041402 | 5 | 0.442 | 35360 | 0.25387 | 9139.32 | 0 | 0 | 1 | 5000 | 9139.32 | 0 | 0 | 0 | 0 | 0 | 21220.68 | 0 | 0 | 0 | 0 | 0 | 21220.68
2022041403 | 5 | 0.42632 | 34105.6 | 0.29455 | 10603.8 | 0 | 0 | 1 | 5000 | 10603.8 | 0 | 0 | 0 | 0 | 0 | 18501.8 | 0 | 0 | 0 | 0 | 0 | 18501.8
2022041404 | 5 | 0.4186 | 33488 | 0.34031 | 12251.16 | 0 | 0 | 1 | 5000 | 12251.16 | 0 | 0 | 0 | 0 | 0 | 16236.84 | 0 | 0 | 0 | 0 | 0 | 16236.84
2022041405 | 5 | 0.42062 | 33649.6 | 0.3892 | 14011.2 | 0 | 0 | 1 | 5000 | 14011.2 | 0 | 0 | 0 | 0 | 0 | 14638.4 | 0 | 0 | 0 | 0 | 0 | 14638.4
2022041406 | 5 | 0.4395 | 35160 | 0.41053 | 14779.08 | 0 | 0 | 1 | 5000 | 14779.08 | 0 | 0 | 0 | 0 | 0 | 15380.92 | 0 | 0 | 0 | 0 | 0 | 15380.92
2022041407 | 5 | 0.47508 | 38006.4 | 0.41756 | 15032.16 | 0 | 0 | 1 | 5000 | 15032.16 | 0 | 0 | 0 | 0 | 0 | 17974.24 | 0 | 0 | 0 | 0 | 0 | 17974.24
2022041408 | 5 | 0.49168 | 39334.4 | 0.38607 | 13898.52 | 0.05306 | 636.72 | 1 | 5000 | 13898.52 | 636.72 | 0 | 0 | 0 | 0 | 19799.16 | 0 | 0 | 0 | 0 | 0 | 19799.16
2022041409 | 5 | 0.49884 | 39907.2 | 0.31657 | 11396.52 | 0.46554 | 5586.48 | 1 | 5000 | 11396.52 | 5586.48 | 0 | 0 | 0 | 0 | 17924.2 | 0 | 0 | 0 | 0 | 0 | 17924.2
2022041410 | 5 | 0.50603 | 40482.4 | 0.32252 | 11610.72 | 0.71202 | 8544.24 | 1 | 5000 | 11610.72 | 8544.24 | 0 | 0 | 0 | 0 | 15327.44 | 0 | 0 | 0 | 0 | 0 | 15327.44
2022041411 | 5 | 0.51615 | 41292 | 0.37822 | 13615.92 | 0.70472 | 8456.64 | 1 | 5000 | 13615.92 | 8456.64 | 0 | 0 | 0 | 0 | 14219.44 | 0 | 0 | 0 | 0 | 0 | 14219.44
2022041412 | 5 | 0.52643 | 42114.4 | 0.37695 | 13570.2 | 0.75471 | 9056.52 | 1 | 5000 | 13570.2 | 9056.52 | 0 | 0 | 0 | 0 | 14487.68 | 0 | 0 | 0 | 0 | 0 | 14487.68
2022041413 | 5 | 0.53749 | 42999.2 | 0.38042 | 13695.12 | 0.80785 | 9694.2 | 1 | 5000 | 13695.12 | 9694.2 | 0 | 0 | 0 | 0 | 14609.88 | 0 | 0 | 0 | 0 | 0 | 14609.88
2022041414 | 5 | 0.55434 | 44347.2 | 0.39132 | 14087.52 | 0.81621 | 9794.52 | 1 | 5000 | 14087.52 | 9794.52 | 0 | 0 | 0 | 0 | 15465.16 | 0 | 0 | 0 | 0 | 0 | 15465.16
2022041415 | 5 | 0.56997 | 45597.6 | 0.42076 | 15147.36 | 0.78051 | 9366.12 | 1 | 5000 | 15147.36 | 9366.12 | 0 | 0 | 0 | 0 | 16084.12 | 0 | 0 | 0 | 0 | 0 | 16084.12
2022041416 | 5 | 0.58613 | 46890.4 | 0.45088 | 16231.68 | 0.68019 | 8162.28 | 1 | 5000 | 16231.68 | 8162.28 | 0 | 0 | 0 | 0 | 17496.44 | 0 | 0 | 0 | 0 | 0 | 17496.44
2022041417 | 5 | 0.60387 | 48309.6 | 0.49614 | 17861.04 | 0.54974 | 6596.88 | 1 | 5000 | 17861.04 | 6596.88 | 0 | 0 | 0 | 0 | 18851.68 | 0 | 0 | 0 | 0 | 0 | 18851.68
2022041418 | 5 | 0.61034 | 48827.2 | 0.52977 | 19071.72 | 0.4299 | 5158.8 | 1 | 5000 | 19071.72 | 5158.8 | 0 | 0 | 0 | 0 | 19596.68 | 0 | 0 | 0 | 0 | 0 | 19596.68
2022041419 | 5 | 0.60087 | 48069.6 | 0.54729 | 19702.44 | 0.28257 | 3390.84 | 1 | 5000 | 19702.44 | 3390.84 | 0 | 0 | 0 | 0 | 19976.32 | 0 | 0 | 0 | 0 | 0 | 19976.32
2022041420 | 5 | 0.58378 | 46702.4 | 0.55953 | 20143.08 | 0.09409 | 1129.08 | 1 | 5000 | 20143.08 | 1129.08 | 0 | 0 | 0 | 0 | 20430.24 | 0 | 0 | 0 | 0 | 0 | 20430.24
2022041421 | 5 | 0.5769 | 46152 | 0.58153 | 20935.08 | 0.00223 | 26.76 | 1 | 5000 | 20935.08 | 26.76 | 0 | 0 | 0 | 0 | 20190.16 | 0 | 0 | 0 | 0 | 0 | 20190.16
2022041422 | 5 | 0.55806 | 44644.8 | 0.5785 | 20826 | 0 | 0 | 1 | 5000 | 20826 | 0 | 0 | 0 | 0 | 0 | 18818.8 | 0 | 0 | 0 | 0 | 0 | 18818.8
2022041423 | 5 | 0.52762 | 42209.6 | 0.56904 | 20485.44 | 0 | 0 | 1 | 5000 | 20485.44 | 0 | 0 | 0 | 0 | 0 | 16724.16 | 0 | 0 | 0 | 0 | 0 | 16724.16
2022041424 | 5 | 0.49161 | 39328.8 | 0.55242 | 19887.12 | 0 | 0 | 1 | 5000 | 19887.12 | 0 | 0 | 0 | 0 | 0 | 14441.68 | 0 | 0 | 0 | 0 | 0 | 14441.68
2022041501 | 6 | 0.46018 | 36814.4 | 0.53962 | 19426.32 | 0 | 0 | 1 | 5000 | 19426.32 | 0 | 0 | 0 | 0 | 0 | 12388.08 | 0 | 0 | 0 | 0 | 0 | 12388.08
2022041502 | 6 | 0.4413 | 35304 | 0.51725 | 18621 | 0 | 0 | 1 | 5000 | 18621 | 0 | 0 | 0 | 0 | 0 | 11683 | 0 | 0 | 0 | 0 | 0 | 11683
2022041503 | 6 | 0.43156 | 34524.8 | 0.50127 | 18045.72 | 0 | 0 | 1 | 5000 | 18045.72 | 0 | 0 | 0 | 0 | 0 | 11479.08 | 0 | 0 | 0 | 0 | 0 | 11479.08
2022041504 | 6 | 0.42588 | 34070.4 | 0.49701 | 17892.36 | 0 | 0 | 1 | 5000 | 17892.36 | 0 | 0 | 0 | 0 | 0 | 11178.04 | 0 | 0 | 0 | 0 | 0 | 11178.04
2022041505 | 6 | 0.42852 | 34281.6 | 0.49667 | 17880.12 | 0 | 0 | 1 | 5000 | 17880.12 | 0 | 0 | 0 | 0 | 0 | 11401.48 | 0 | 0 | 0 | 0 | 0 | 11401.48
2022041506 | 6 | 0.44008 | 35206.4 | 0.49801 | 17928.36 | 0 | 0 | 1 | 5000 | 17928.36 | 0 | 0 | 0 | 0 | 0 | 12278.04 | 0 | 0 | 0 | 0 | 0 | 12278.04
2022041507 | 6 | 0.46055 | 36844 | 0.49554 | 17839.44 | 0 | 0 | 1 | 5000 | 17839.44 | 0 | 0 | 0 | 0 | 0 | 14004.56 | 0 | 0 | 0 | 0 | 0 | 14004.56
2022041508 | 6 | 0.47412 | 37929.6 | 0.49415 | 17789.4 | 0.02019 | 242.28 | 1 | 5000 | 17789.4 | 242.28 | 0 | 0 | 0 | 0 | 14897.92 | 0 | 0 | 0 | 0 | 0 | 14897.92
2022041509 | 6 | 0.49042 | 39233.6 | 0.46897 | 16882.92 | 0.13905 | 1668.6 | 1 | 5000 | 16882.92 | 1668.6 | 0 | 0 | 0 | 0 | 15682.08 | 0 | 0 | 0 | 0 | 0 | 15682.08
2022041510 | 6 | 0.50989 | 40791.2 | 0.46669 | 16800.84 | 0.18122 | 2174.64 | 1 | 5000 | 16800.84 | 2174.64 | 0 | 0 | 0 | 0 | 16815.72 | 0 | 0 | 0 | 0 | 0 | 16815.72
2022041511 | 6 | 0.52571 | 42056.8 | 0.46695 | 16810.2 | 0.23737 | 2848.44 | 1 | 5000 | 16810.2 | 2848.44 | 0 | 0 | 0 | 0 | 17398.16 | 0 | 0 | 0 | 0 | 0 | 17398.16
2022041512 | 6 | 0.54082 | 43265.6 | 0.43375 | 15615 | 0.39232 | 4707.84 | 1 | 5000 | 15615 | 4707.84 | 0 | 0 | 0 | 0 | 17942.76 | 0 | 0 | 0 | 0 | 0 | 17942.76
2022041513 | 6 | 0.55813 | 44650.4 | 0.39537 | 14233.32 | 0.5453 | 6543.6 | 1 | 5000 | 14233.32 | 6543.6 | 0 | 0 | 0 | 0 | 18873.48 | 0 | 0 | 0 | 0 | 0 | 18873.48
2022041514 | 6 | 0.57187 | 45749.6 | 0.34858 | 12548.88 | 0.68675 | 8241 | 1 | 5000 | 12548.88 | 8241 | 0 | 0 | 0 | 0 | 19959.72 | 0 | 0 | 0 | 0 | 0 | 19959.72
2022041515 | 6 | 0.58809 | 47047.2 | 0.33849 | 12185.64 | 0.64524 | 7742.88 | 1 | 5000 | 12185.64 | 7742.88 | 0 | 0 | 0 | 0 | 22118.68 | 0 | 0 | 0 | 0 | 0 | 22118.68
2022041516 | 6 | 0.60658 | 48526.4 | 0.36108 | 12998.88 | 0.61408 | 7368.96 | 1 | 5000 | 12998.88 | 7368.96 | 0 | 0 | 0 | 0 | 23158.56 | 0 | 0 | 0 | 0 | 0 | 23158.56
2022041517 | 6 | 0.6237 | 49896 | 0.37951 | 13662.36 | 0.61761 | 7411.32 | 1 | 5000 | 13662.36 | 7411.32 | 0 | 0 | 0 | 0 | 23822.32 | 0 | 0 | 0 | 0 | 0 | 23822.32
2022041518 | 6 | 0.63298 | 50638.4 | 0.38905 | 14005.8 | 0.59039 | 7084.68 | 1 | 5000 | 14005.8 | 7084.68 | 0 | 0 | 0 | 0 | 24547.92 | 0 | 0 | 0 | 0 | 0 | 24547.92
2022041519 | 6 | 0.62655 | 50124 | 0.38308 | 13790.88 | 0.42773 | 5132.76 | 1 | 5000 | 13790.88 | 5132.76 | 0 | 0 | 0 | 0 | 26200.36 | 0 | 0 | 0 | 0 | 0 | 26200.36
2022041520 | 6 | 0.61178 | 48942.4 | 0.3407 | 12265.2 | 0.10407 | 1248.84 | 1 | 5000 | 12265.2 | 1248.84 | 0 | 0 | 0 | 0 | 30428.36 | 0 | 0 | 0 | 0 | 0 | 30428.36
2022041521 | 6 | 0.60744 | 48595.2 | 0.36493 | 13137.48 | 0.00108 | 12.96 | 1 | 5000 | 13137.48 | 12.96 | 0 | 0 | 0 | 0 | 30444.76 | 0 | 0 | 0 | 0 | 0 | 30444.76
2022041522 | 6 | 0.59203 | 47362.4 | 0.4026 | 14493.6 | 0 | 0 | 1 | 5000 | 14493.6 | 0 | 0 | 0 | 0 | 0 | 27868.8 | 0 | 0 | 0 | 0 | 0 | 27868.8
2022041523 | 6 | 0.56854 | 45483.2 | 0.43811 | 15771.96 | 0 | 0 | 1 | 5000 | 15771.96 | 0 | 0 | 0 | 0 | 0 | 24711.24 | 0 | 0 | 0 | 0 | 0 | 24711.24
2022041524 | 6 | 0.54267 | 43413.6 | 0.48831 | 17579.16 | 0 | 0 | 1 | 5000 | 17579.16 | 0 | 0 | 0 | 0 | 0 | 20834.44 | 0 | 0 | 0 | 0 | 0 | 20834.44
2022041601 | 7 | 0.5146 | 41168 | 0.52244 | 18807.84 | 0 | 0 | 1 | 5000 | 18807.84 | 0 | 0 | 0 | 0 | 0 | 17360.16 | 0 | 0 | 0 | 0 | 0 | 17360.16
2022041602 | 7 | 0.4961 | 39688 | 0.53782 | 19361.52 | 0 | 0 | 1 | 5000 | 19361.52 | 0 | 0 | 0 | 0 | 0 | 15326.48 | 0 | 0 | 0 | 0 | 0 | 15326.48
2022041603 | 7 | 0.48134 | 38507.2 | 0.54122 | 19483.92 | 0 | 0 | 1 | 5000 | 19483.92 | 0 | 0 | 0 | 0 | 0 | 14023.28 | 0 | 0 | 0 | 0 | 0 | 14023.28
2022041604 | 7 | 0.47307 | 37845.6 | 0.51428 | 18514.08 | 0 | 0 | 1 | 5000 | 18514.08 | 0 | 0 | 0 | 0 | 0 | 14331.52 | 0 | 0 | 0 | 0 | 0 | 14331.52
2022041605 | 7 | 0.46893 | 37514.4 | 0.5074 | 18266.4 | 0 | 0 | 1 | 5000 | 18266.4 | 0 | 0 | 0 | 0 | 0 | 14248 | 0 | 0 | 0 | 0 | 0 | 14248
2022041606 | 7 | 0.47019 | 37615.2 | 0.48132 | 17327.52 | 0 | 0 | 1 | 5000 | 17327.52 | 0 | 0 | 0 | 0 | 0 | 15287.68 | 0 | 0 | 0 | 0 | 0 | 15287.68
2022041607 | 7 | 0.47464 | 37971.2 | 0.45623 | 16424.28 | 0 | 0 | 1 | 5000 | 16424.28 | 0 | 0 | 0 | 0 | 0 | 16546.92 | 0 | 0 | 0 | 0 | 0 | 16546.92
2022041608 | 7 | 0.48271 | 38616.8 | 0.46154 | 16615.44 | 0.02177 | 261.24 | 1 | 5000 | 16615.44 | 261.24 | 0 | 0 | 0 | 0 | 16740.12 | 0 | 0 | 0 | 0 | 0 | 16740.12
2022041609 | 7 | 0.50724 | 40579.2 | 0.43428 | 15634.08 | 0.25612 | 3073.44 | 1 | 5000 | 15634.08 | 3073.44 | 0 | 0 | 0 | 0 | 16871.68 | 0 | 0 | 0 | 0 | 0 | 16871.68
2022041610 | 7 | 0.53615 | 42892 | 0.44333 | 15959.88 | 0.35149 | 4217.88 | 1 | 5000 | 15959.88 | 4217.88 | 0 | 0 | 0 | 0 | 17714.24 | 0 | 0 | 0 | 0 | 0 | 17714.24
2022041611 | 7 | 0.55521 | 44416.8 | 0.46289 | 16664.04 | 0.33048 | 3965.76 | 1 | 5000 | 16664.04 | 3965.76 | 0 | 0 | 0 | 0 | 18787 | 0 | 0 | 0 | 0 | 0 | 18787
2022041612 | 7 | 0.57103 | 45682.4 | 0.43666 | 15719.76 | 0.43012 | 5161.44 | 1 | 5000 | 15719.76 | 5161.44 | 0 | 0 | 0 | 0 | 19801.2 | 0 | 0 | 0 | 0 | 0 | 19801.2
2022041613 | 7 | 0.58216 | 46572.8 | 0.36514 | 13145.04 | 0.60072 | 7208.64 | 1 | 5000 | 13145.04 | 7208.64 | 0 | 0 | 0 | 0 | 21219.12 | 0 | 0 | 0 | 0 | 0 | 21219.12
2022041614 | 7 | 0.59281 | 47424.8 | 0.31225 | 11241 | 0.65465 | 7855.8 | 1 | 5000 | 11241 | 7855.8 | 0 | 0 | 0 | 0 | 23328 | 0 | 0 | 0 | 0 | 0 | 23328
2022041615 | 7 | 0.60028 | 48022.4 | 0.25194 | 9069.84 | 0.65467 | 7856.04 | 1 | 5000 | 9069.84 | 7856.04 | 0 | 0 | 0 | 0 | 26096.52 | 0 | 0 | 0 | 0 | 0 | 26096.52
2022041616 | 7 | 0.60825 | 48660 | 0.19836 | 7140.96 | 0.64299 | 7715.88 | 1 | 5000 | 7140.96 | 7715.88 | 0 | 0 | 0 | 0 | 28803.16 | 0 | 0 | 0 | 0 | 0 | 28803.16
2022041617 | 7 | 0.61719 | 49375.2 | 0.18669 | 6720.84 | 0.59568 | 7148.16 | 1 | 5000 | 6720.84 | 7148.16 | 0 | 0 | 0 | 0 | 30506.2 | 0 | 0 | 0 | 0 | 0 | 30506.2
2022041618 | 7 | 0.6185 | 49480 | 0.17685 | 6366.6 | 0.47027 | 5643.24 | 1 | 5000 | 6366.6 | 5643.24 | 0 | 0 | 0 | 0 | 32470.16 | 0 | 0 | 0 | 0 | 0 | 32470.16
2022041619 | 7 | 0.60622 | 48497.6 | 0.18037 | 6493.32 | 0.35448 | 4253.76 | 1 | 5000 | 6493.32 | 4253.76 | 0 | 0 | 0 | 0 | 32750.52 | 0 | 0 | 0 | 0 | 0 | 32750.52
2022041620 | 7 | 0.58722 | 46977.6 | 0.19259 | 6933.24 | 0.08181 | 981.72 | 1 | 5000 | 6933.24 | 981.72 | 0 | 0 | 0 | 0 | 34062.64 | 0 | 0 | 0 | 0 | 0 | 34062.64
2022041621 | 7 | 0.58486 | 46788.8 | 0.22326 | 8037.36 | 0.00233 | 27.96 | 1 | 5000 | 8037.36 | 27.96 | 0 | 0 | 0 | 0 | 33723.48 | 0 | 0 | 0 | 0 | 0 | 33723.48
2022041622 | 7 | 0.56843 | 45474.4 | 0.27007 | 9722.52 | 0 | 0 | 1 | 5000 | 9722.52 | 0 | 0 | 0 | 0 | 0 | 30751.88 | 0 | 0 | 0 | 0 | 0 | 30751.88
2022041623 | 7 | 0.54256 | 43404.8 | 0.28261 | 10173.96 | 0 | 0 | 1 | 5000 | 10173.96 | 0 | 0 | 0 | 0 | 0 | 28230.84 | 0 | 0 | 0 | 0 | 0 | 28230.84
2022041624 | 7 | 0.51298 | 41038.4 | 0.27396 | 9862.56 | 0 | 0 | 1 | 5000 | 9862.56 | 0 | 0 | 0 | 0 | 0 | 26175.84 | 0 | 0 | 0 | 0 | 0 | 26175.84
2022041701 | 1 | 0.48422 | 38737.6 | 0.2532 | 9115.2 | 0 | 0 | 1 | 5000 | 9115.2 | 0 | 0 | 0 | 0 | 0 | 24622.4 | 0 | 0 | 0 | 0 | 0 | 24622.4
2022041702 | 1 | 0.46115 | 36892 | 0.22729 | 8182.44 | 0 | 0 | 1 | 5000 | 8182.44 | 0 | 0 | 0 | 0 | 0 | 23709.56 | 0 | 0 | 0 | 0 | 0 | 23709.56
2022041703 | 1 | 0.44492 | 35593.6 | 0.1987 | 7153.2 | 0 | 0 | 1 | 5000 | 7153.2 | 0 | 0 | 0 | 0 | 0 | 23440.4 | 0 | 0 | 0 | 0 | 0 | 23440.4
2022041704 | 1 | 0.43497 | 34797.6 | 0.13076 | 4707.36 | 0 | 0 | 1 | 5000 | 4707.36 | 0 | 0 | 0 | 0 | 0 | 25090.24 | 0 | 0 | 0 | 0 | 0 | 25090.24
2022041705 | 1 | 0.4298 | 34384 | 0.10342 | 3723.12 | 0 | 0 | 1 | 5000 | 3723.12 | 0 | 0 | 0 | 0 | 0 | 25660.88 | 0 | 0 | 0 | 0 | 0 | 25660.88
2022041706 | 1 | 0.43062 | 34449.6 | 0.10155 | 3655.8 | 0 | 0 | 1 | 5000 | 3655.8 | 0 | 0 | 0 | 0 | 0 | 25793.8 | 0 | 0 | 0 | 0 | 0 | 25793.8
2022041707 | 1 | 0.43683 | 34946.4 | 0.08948 | 3221.28 | 0 | 0 | 1 | 5000 | 3221.28 | 0 | 0 | 0 | 0 | 0 | 26725.12 | 0 | 0 | 0 | 0 | 0 | 26725.12
2022041708 | 1 | 0.44412 | 35529.6 | 0.10064 | 3623.04 | 0.02689 | 322.68 | 1 | 5000 | 3623.04 | 322.68 | 0 | 0 | 0 | 0 | 26583.88 | 0 | 0 | 0 | 0 | 0 | 26583.88
2022041709 | 1 | 0.46462 | 37169.6 | 0.11115 | 4001.4 | 0.31627 | 3795.24 | 1 | 5000 | 4001.4 | 3795.24 | 0 | 0 | 0 | 0 | 24372.96 | 0 | 0 | 0 | 0 | 0 | 24372.96
2022041710 | 1 | 0.49176 | 39340.8 | 0.12061 | 4341.96 | 0.55957 | 6714.84 | 1 | 5000 | 4341.96 | 6714.84 | 0 | 0 | 0 | 0 | 23284 | 0 | 0 | 0 | 0 | 0 | 23284
2022041711 | 1 | 0.51277 | 41021.6 | 0.13076 | 4707.36 | 0.63152 | 7578.24 | 1 | 5000 | 4707.36 | 7578.24 | 0 | 0 | 0 | 0 | 23736 | 0 | 0 | 0 | 0 | 0 | 23736
2022041712 | 1 | 0.53106 | 42484.8 | 0.18005 | 6481.8 | 0.68611 | 8233.32 | 1 | 5000 | 6481.8 | 8233.32 | 0 | 0 | 0 | 0 | 22769.68 | 0 | 0 | 0 | 0 | 0 | 22769.68
2022041713 | 1 | 0.55225 | 44180 | 0.23511 | 8463.96 | 0.72322 | 8678.64 | 1 | 5000 | 8463.96 | 8678.64 | 0 | 0 | 0 | 0 | 22037.4 | 0 | 0 | 0 | 0 | 0 | 22037.4
2022041714 | 1 | 0.56923 | 45538.4 | 0.25892 | 9321.12 | 0.71887 | 8626.44 | 1 | 5000 | 9321.12 | 8626.44 | 0 | 0 | 0 | 0 | 22590.84 | 0 | 0 | 0 | 0 | 0 | 22590.84
2022041715 | 1 | 0.58427 | 46741.6 | 0.2289 | 8240.4 | 0.73629 | 8835.48 | 1 | 5000 | 8240.4 | 8835.48 | 0 | 0 | 0 | 0 | 24665.72 | 0 | 0 | 0 | 0 | 0 | 24665.72
2022041716 | 1 | 0.59958 | 47966.4 | 0.19119 | 6882.84 | 0.76434 | 9172.08 | 1 | 5000 | 6882.84 | 9172.08 | 0 | 0 | 0 | 0 | 26911.48 | 0 | 0 | 0 | 0 | 0 | 26911.48
2022041717 | 1 | 0.61375 | 49100 | 0.1576 | 5673.6 | 0.74344 | 8921.28 | 1 | 5000 | 5673.6 | 8921.28 | 0 | 0 | 0 | 0 | 29505.12 | 0 | 0 | 0 | 0 | 0 | 29505.12
2022041718 | 1 | 0.62063 | 49650.4 | 0.13568 | 4884.48 | 0.72776 | 8733.12 | 1 | 5000 | 4884.48 | 8733.12 | 0 | 0 | 0 | 0 | 31032.8 | 0 | 0 | 0 | 0 | 0 | 31032.8
2022041719 | 1 | 0.61699 | 49359.2 | 0.12838 | 4621.68 | 0.5921 | 7105.2 | 1 | 5000 | 4621.68 | 7105.2 | 0 | 0 | 0 | 0 | 32632.32 | 0 | 0 | 0 | 0 | 0 | 32632.32
2022041720 | 1 | 0.60489 | 48391.2 | 0.15434 | 5556.24 | 0.20073 | 2408.76 | 1 | 5000 | 5556.24 | 2408.76 | 0 | 0 | 0 | 0 | 35426.2 | 0 | 0 | 0 | 0 | 0 | 35426.2
2022041721 | 1 | 0.60145 | 48116 | 0.22739 | 8186.04 | 0.00313 | 37.56 | 1 | 5000 | 8186.04 | 37.56 | 0 | 0 | 0 | 0 | 34892.4 | 0 | 0 | 0 | 0 | 0 | 34892.4
2022041722 | 1 | 0.58607 | 46885.6 | 0.32846 | 11824.56 | 0 | 0 | 1 | 5000 | 11824.56 | 0 | 0 | 0 | 0 | 0 | 30061.04 | 0 | 0 | 0 | 0 | 0 | 30061.04
2022041723 | 1 | 0.55497 | 44397.6 | 0.3833 | 13798.8 | 0 | 0 | 1 | 5000 | 13798.8 | 0 | 0 | 0 | 0 | 0 | 25598.8 | 0 | 0 | 0 | 0 | 0 | 25598.8
2022041724 | 1 | 0.5153 | 41224 | 0.40478 | 14572.08 | 0 | 0 | 1 | 5000 | 14572.08 | 0 | 0 | 0 | 0 | 0 | 21651.92 | 0 | 0 | 0 | 0 | 0 | 21651.92
2022041801 | 2 | 0.48133 | 38506.4 | 0.38788 | 13963.68 | 0 | 0 | 1 | 5000 | 13963.68 | 0 | 0 | 0 | 0 | 0 | 19542.72 | 0 | 0 | 0 | 0 | 0 | 19542.72
2022041802 | 2 | 0.45707 | 36565.6 | 0.35946 | 12940.56 | 0 | 0 | 1 | 5000 | 12940.56 | 0 | 0 | 0 | 0 | 0 | 18625.04 | 0 | 0 | 0 | 0 | 0 | 18625.04
2022041803 | 2 | 0.44205 | 35364 | 0.34013 | 12244.68 | 0 | 0 | 1 | 5000 | 12244.68 | 0 | 0 | 0 | 0 | 0 | 18119.32 | 0 | 0 | 0 | 0 | 0 | 18119.32
2022041804 | 2 | 0.42754 | 34203.2 | 0.31312 | 11272.32 | 0 | 0 | 1 | 5000 | 11272.32 | 0 | 0 | 0 | 0 | 0 | 17930.88 | 0 | 0 | 0 | 0 | 0 | 17930.88
2022041805 | 2 | 0.43102 | 34481.6 | 0.29425 | 10593 | 0 | 0 | 1 | 5000 | 10593 | 0 | 0 | 0 | 0 | 0 | 18888.6 | 0 | 0 | 0 | 0 | 0 | 18888.6
2022041806 | 2 | 0.44711 | 35768.8 | 0.30741 | 11066.76 | 0 | 0 | 1 | 5000 | 11066.76 | 0 | 0 | 0 | 0 | 0 | 19702.04 | 0 | 0 | 0 | 0 | 0 | 19702.04
2022041807 | 2 | 0.47104 | 37683.2 | 0.30846 | 11104.56 | 0 | 0 | 1 | 5000 | 11104.56 | 0 | 0 | 0 | 0 | 0 | 21578.64 | 0 | 0 | 0 | 0 | 0 | 21578.64
2022041808 | 2 | 0.48324 | 38659.2 | 0.34361 | 12369.96 | 0.03922 | 470.64 | 1 | 5000 | 12369.96 | 470.64 | 0 | 0 | 0 | 0 | 20818.6 | 0 | 0 | 0 | 0 | 0 | 20818.6
2022041809 | 2 | 0.49741 | 39792.8 | 0.32423 | 11672.28 | 0.36327 | 4359.24 | 1 | 5000 | 11672.28 | 4359.24 | 0 | 0 | 0 | 0 | 18761.28 | 0 | 0 | 0 | 0 | 0 | 18761.28
2022041810 | 2 | 0.51466 | 41172.8 | 0.37962 | 13666.32 | 0.58018 | 6962.16 | 1 | 5000 | 13666.32 | 6962.16 | 0 | 0 | 0 | 0 | 15544.32 | 0 | 0 | 0 | 0 | 0 | 15544.32
2022041811 | 2 | 0.5293 | 42344 | 0.38619 | 13902.84 | 0.64754 | 7770.48 | 1 | 5000 | 13902.84 | 7770.48 | 0 | 0 | 0 | 0 | 15670.68 | 0 | 0 | 0 | 0 | 0 | 15670.68
2022041812 | 2 | 0.54197 | 43357.6 | 0.36417 | 13110.12 | 0.70656 | 8478.72 | 1 | 5000 | 13110.12 | 8478.72 | 0 | 0 | 0 | 0 | 16768.76 | 0 | 0 | 0 | 0 | 0 | 16768.76
2022041813 | 2 | 0.55567 | 44453.6 | 0.34922 | 12571.92 | 0.76065 | 9127.8 | 1 | 5000 | 12571.92 | 9127.8 | 0 | 0 | 0 | 0 | 17753.88 | 0 | 0 | 0 | 0 | 0 | 17753.88
2022041814 | 2 | 0.56999 | 45599.2 | 0.34147 | 12292.92 | 0.79307 | 9516.84 | 1 | 5000 | 12292.92 | 9516.84 | 0 | 0 | 0 | 0 | 18789.44 | 0 | 0 | 0 | 0 | 0 | 18789.44
2022041815 | 2 | 0.58587 | 46869.6 | 0.34337 | 12361.32 | 0.79278 | 9513.36 | 1 | 5000 | 12361.32 | 9513.36 | 0 | 0 | 0 | 0 | 19994.92 | 0 | 0 | 0 | 0 | 0 | 19994.92
2022041816 | 2 | 0.60241 | 48192.8 | 0.34402 | 12384.72 | 0.79954 | 9594.48 | 1 | 5000 | 12384.72 | 9594.48 | 0 | 0 | 0 | 0 | 21213.6 | 0 | 0 | 0 | 0 | 0 | 21213.6
2022041817 | 2 | 0.6158 | 49264 | 0.36006 | 12962.16 | 0.77071 | 9248.52 | 1 | 5000 | 12962.16 | 9248.52 | 0 | 0 | 0 | 0 | 22053.32 | 0 | 0 | 0 | 0 | 0 | 22053.32
2022041818 | 2 | 0.62032 | 49625.6 | 0.39271 | 14137.56 | 0.70748 | 8489.76 | 1 | 5000 | 14137.56 | 8489.76 | 0 | 0 | 0 | 0 | 21998.28 | 0 | 0 | 0 | 0 | 0 | 21998.28
2022041819 | 2 | 0.61155 | 48924 | 0.44043 | 15855.48 | 0.53146 | 6377.52 | 1 | 5000 | 15855.48 | 6377.52 | 0 | 0 | 0 | 0 | 21691 | 0 | 0 | 0 | 0 | 0 | 21691
2022041820 | 2 | 0.59338 | 47470.4 | 0.45165 | 16259.4 | 0.16814 | 2017.68 | 1 | 5000 | 16259.4 | 2017.68 | 0 | 0 | 0 | 0 | 24193.32 | 0 | 0 | 0 | 0 | 0 | 24193.32
2022041821 | 2 | 0.58854 | 47083.2 | 0.44658 | 16076.88 | 0.02606 | 312.72 | 1 | 5000 | 16076.88 | 312.72 | 0 | 0 | 0 | 0 | 25693.6 | 0 | 0 | 0 | 0 | 0 | 25693.6
2022041822 | 2 | 0.56723 | 45378.4 | 0.49277 | 17739.72 | 0.02406 | 288.72 | 1 | 5000 | 17739.72 | 288.72 | 0 | 0 | 0 | 0 | 22349.96 | 0 | 0 | 0 | 0 | 0 | 22349.96
2022041823 | 2 | 0.52924 | 42339.2 | 0.51566 | 18563.76 | 0.02406 | 288.72 | 1 | 5000 | 18563.76 | 288.72 | 0 | 0 | 0 | 0 | 18486.72 | 0 | 0 | 0 | 0 | 0 | 18486.72
2022041824 | 2 | 0.48706 | 38964.8 | 0.53677 | 19323.72 | 0.01067 | 128.04 | 1 | 5000 | 19323.72 | 128.04 | 0 | 0 | 0 | 0 | 14513.04 | 0 | 0 | 0 | 0 | 0 | 14513.04
2022041901 | 3 | 0.45495 | 36396 | 0.5599 | 20156.4 | 0 | 0 | 1 | 5000 | 20156.4 | 0 | 0 | 0 | 0 | 0 | 11239.6 | 0 | 0 | 0 | 0 | 0 | 11239.6
2022041902 | 3 | 0.43428 | 34742.4 | 0.55957 | 20144.52 | 0 | 0 | 1 | 5000 | 20144.52 | 0 | 0 | 0 | 0 | 0 | 9597.88 | 0 | 0 | 0 | 0 | 0 | 9597.88
2022041903 | 3 | 0.4224 | 33792 | 0.53046 | 19096.56 | 0 | 0 | 1 | 5000 | 19096.56 | 0 | 0 | 0 | 0 | 0 | 9695.44 | 0 | 0 | 0 | 0 | 0 | 9695.44
2022041904 | 3 | 0.4169 | 33352 | 0.51283 | 18461.88 | 0 | 0 | 1 | 5000 | 18461.88 | 0 | 0 | 0 | 0 | 0 | 9890.12 | 0 | 0 | 0 | 0 | 0 | 9890.12
2022041905 | 3 | 0.42034 | 33627.2 | 0.49451 | 17802.36 | 0 | 0 | 1 | 5000 | 17802.36 | 0 | 0 | 0 | 0 | 0 | 10824.84 | 0 | 0 | 0 | 0 | 0 | 10824.84
2022041906 | 3 | 0.43874 | 35099.2 | 0.50022 | 18007.92 | 0 | 0 | 1 | 5000 | 18007.92 | 0 | 0 | 0 | 0 | 0 | 12091.28 | 0 | 0 | 0 | 0 | 0 | 12091.28
2022041907 | 3 | 0.47339 | 37871.2 | 0.51244 | 18447.84 | 5e-05 | 0.6 | 1 | 5000 | 18447.84 | 0.6 | 0 | 0 | 0 | 0 | 14422.76 | 0 | 0 | 0 | 0 | 0 | 14422.76
2022041908 | 3 | 0.48896 | 39116.8 | 0.52865 | 19031.4 | 0.0231 | 277.2 | 1 | 5000 | 19031.4 | 277.2 | 0 | 0 | 0 | 0 | 14808.2 | 0 | 0 | 0 | 0 | 0 | 14808.2
2022041909 | 3 | 0.4944 | 39552 | 0.5332 | 19195.2 | 0.14809 | 1777.08 | 1 | 5000 | 19195.2 | 1777.08 | 0 | 0 | 0 | 0 | 13579.72 | 0 | 0 | 0 | 0 | 0 | 13579.72
2022041910 | 3 | 0.50433 | 40346.4 | 0.56064 | 20183.04 | 0.22504 | 2700.48 | 1 | 5000 | 20183.04 | 2700.48 | 0 | 0 | 0 | 0 | 12462.88 | 0 | 0 | 0 | 0 | 0 | 12462.88
2022041911 | 3 | 0.51414 | 41131.2 | 0.57464 | 20687.04 | 0.21549 | 2585.88 | 1 | 5000 | 20687.04 | 2585.88 | 0 | 0 | 0 | 0 | 12858.28 | 0 | 0 | 0 | 0 | 0 | 12858.28
2022041912 | 3 | 0.52542 | 42033.6 | 0.5841 | 21027.6 | 0.25702 | 3084.24 | 1 | 5000 | 21027.6 | 3084.24 | 0 | 0 | 0 | 0 | 12921.76 | 0 | 0 | 0 | 0 | 0 | 12921.76
2022041913 | 3 | 0.53416 | 42732.8 | 0.60039 | 21614.04 | 0.27055 | 3246.6 | 1 | 5000 | 21614.04 | 3246.6 | 0 | 0 | 0 | 0 | 12872.16 | 0 | 0 | 0 | 0 | 0 | 12872.16
2022041914 | 3 | 0.54396 | 43516.8 | 0.60872 | 21913.92 | 0.26508 | 3180.96 | 1 | 5000 | 21913.92 | 3180.96 | 0 | 0 | 0 | 0 | 13421.92 | 0 | 0 | 0 | 0 | 0 | 13421.92
2022041915 | 3 | 0.5527 | 44216 | 0.62699 | 22571.64 | 0.25486 | 3058.32 | 1 | 5000 | 22571.64 | 3058.32 | 0 | 0 | 0 | 0 | 13586.04 | 0 | 0 | 0 | 0 | 0 | 13586.04
2022041916 | 3 | 0.55541 | 44432.8 | 0.62851 | 22626.36 | 0.22702 | 2724.24 | 1 | 5000 | 22626.36 | 2724.24 | 0 | 0 | 0 | 0 | 14082.2 | 0 | 0 | 0 | 0 | 0 | 14082.2
2022041917 | 3 | 0.55992 | 44793.6 | 0.63212 | 22756.32 | 0.18152 | 2178.24 | 1 | 5000 | 22756.32 | 2178.24 | 0 | 0 | 0 | 0 | 14859.04 | 0 | 0 | 0 | 0 | 0 | 14859.04
2022041918 | 3 | 0.56024 | 44819.2 | 0.63807 | 22970.52 | 0.12282 | 1473.84 | 1 | 5000 | 22970.52 | 1473.84 | 0 | 0 | 0 | 0 | 15374.84 | 0 | 0 | 0 | 0 | 0 | 15374.84
2022041919 | 3 | 0.55759 | 44607.2 | 0.6494 | 23378.4 | 0.0538 | 645.6 | 1 | 5000 | 23378.4 | 645.6 | 0 | 0 | 0 | 0 | 15583.2 | 0 | 0 | 0 | 0 | 0 | 15583.2
2022041920 | 3 | 0.55761 | 44608.8 | 0.65595 | 23614.2 | 0.01687 | 202.44 | 1 | 5000 | 23614.2 | 202.44 | 0 | 0 | 0 | 0 | 15792.16 | 0 | 0 | 0 | 0 | 0 | 15792.16
2022041921 | 3 | 0.56444 | 45155.2 | 0.65959 | 23745.24 | 0.00045 | 5.4 | 1 | 5000 | 23745.24 | 5.4 | 0 | 0 | 0 | 0 | 16404.56 | 0 | 0 | 0 | 0 | 0 | 16404.56
2022041922 | 3 | 0.552 | 44160 | 0.65283 | 23501.88 | 0 | 0 | 1 | 5000 | 23501.88 | 0 | 0 | 0 | 0 | 0 | 15658.12 | 0 | 0 | 0 | 0 | 0 | 15658.12
2022041923 | 3 | 0.52584 | 42067.2 | 0.64631 | 23267.16 | 0 | 0 | 1 | 5000 | 23267.16 | 0 | 0 | 0 | 0 | 0 | 13800.04 | 0 | 0 | 0 | 0 | 0 | 13800.04
2022041924 | 3 | 0.49288 | 39430.4 | 0.63975 | 23031 | 0 | 0 | 1 | 5000 | 23031 | 0 | 0 | 0 | 0 | 0 | 11399.4 | 0 | 0 | 0 | 0 | 0 | 11399.4
2022042001 | 4 | 0.46807 | 37445.6 | 0.63995 | 23038.2 | 0 | 0 | 1 | 5000 | 23038.2 | 0 | 0 | 0 | 0 | 0 | 9407.4 | 0 | 0 | 0 | 0 | 0 | 9407.4
2022042002 | 4 | 0.45414 | 36331.2 | 0.63938 | 23017.68 | 0 | 0 | 1 | 5000 | 23017.68 | 0 | 0 | 0 | 0 | 0 | 8313.52 | 0 | 0 | 0 | 0 | 0 | 8313.52
2022042003 | 4 | 0.44621 | 35696.8 | 0.63884 | 22998.24 | 0 | 0 | 1 | 5000 | 22998.24 | 0 | 0 | 0 | 0 | 0 | 7698.56 | 0 | 0 | 0 | 0 | 0 | 7698.56
2022042004 | 4 | 0.44213 | 35370.4 | 0.6302 | 22687.2 | 0 | 0 | 1 | 5000 | 22687.2 | 0 | 0 | 0 | 0 | 0 | 7683.2 | 0 | 0 | 0 | 0 | 0 | 7683.2
2022042005 | 4 | 0.44761 | 35808.8 | 0.62316 | 22433.76 | 0 | 0 | 1 | 5000 | 22433.76 | 0 | 0 | 0 | 0 | 0 | 8375.04 | 0 | 0 | 0 | 0 | 0 | 8375.04
2022042006 | 4 | 0.46847 | 37477.6 | 0.63008 | 22682.88 | 0 | 0 | 1 | 5000 | 22682.88 | 0 | 0 | 0 | 0 | 0 | 9794.72 | 0 | 0 | 0 | 0 | 0 | 9794.72
2022042007 | 4 | 0.50066 | 40052.8 | 0.61555 | 22159.8 | 0 | 0 | 1 | 5000 | 22159.8 | 0 | 0 | 0 | 0 | 0 | 12893 | 0 | 0 | 0 | 0 | 0 | 12893
2022042008 | 4 | 0.52153 | 41722.4 | 0.61079 | 21988.44 | 0.0147 | 176.4 | 1 | 5000 | 21988.44 | 176.4 | 0 | 0 | 0 | 0 | 14557.56 | 0 | 0 | 0 | 0 | 0 | 14557.56
2022042009 | 4 | 0.52954 | 42363.2 | 0.56788 | 20443.68 | 0.12274 | 1472.88 | 1 | 5000 | 20443.68 | 1472.88 | 0 | 0 | 0 | 0 | 15446.64 | 0 | 0 | 0 | 0 | 0 | 15446.64
2022042010 | 4 | 0.54534 | 43627.2 | 0.57409 | 20667.24 | 0.19102 | 2292.24 | 1 | 5000 | 20667.24 | 2292.24 | 0 | 0 | 0 | 0 | 15667.72 | 0 | 0 | 0 | 0 | 0 | 15667.72
2022042011 | 4 | 0.5633 | 45064 | 0.5731 | 20631.6 | 0.2467 | 2960.4 | 1 | 5000 | 20631.6 | 2960.4 | 0 | 0 | 0 | 0 | 16472 | 0 | 0 | 0 | 0 | 0 | 16472
2022042012 | 4 | 0.58073 | 46458.4 | 0.56756 | 20432.16 | 0.2914 | 3496.8 | 1 | 5000 | 20432.16 | 3496.8 | 0 | 0 | 0 | 0 | 17529.44 | 0 | 0 | 0 | 0 | 0 | 17529.44
2022042013 | 4 | 0.59853 | 47882.4 | 0.51763 | 18634.68 | 0.46578 | 5589.36 | 1 | 5000 | 18634.68 | 5589.36 | 0 | 0 | 0 | 0 | 18658.36 | 0 | 0 | 0 | 0 | 0 | 18658.36
2022042014 | 4 | 0.61931 | 49544.8 | 0.46332 | 16679.52 | 0.64562 | 7747.44 | 1 | 5000 | 16679.52 | 7747.44 | 0 | 0 | 0 | 0 | 20117.84 | 0 | 0 | 0 | 0 | 0 | 20117.84
2022042015 | 4 | 0.64035 | 51228 | 0.41455 | 14923.8 | 0.68314 | 8197.68 | 1 | 5000 | 14923.8 | 8197.68 | 0 | 0 | 0 | 0 | 23106.52 | 0 | 0 | 0 | 0 | 0 | 23106.52
2022042016 | 4 | 0.65694 | 52555.2 | 0.38631 | 13907.16 | 0.66335 | 7960.2 | 1 | 5000 | 13907.16 | 7960.2 | 0 | 0 | 0 | 0 | 25687.84 | 0 | 0 | 0 | 0 | 0 | 25687.84
2022042017 | 4 | 0.67458 | 53966.4 | 0.37462 | 13486.32 | 0.66565 | 7987.8 | 1 | 5000 | 13486.32 | 7987.8 | 0 | 0 | 0 | 0 | 27492.28 | 0 | 0 | 0 | 0 | 0 | 27492.28
2022042018 | 4 | 0.68436 | 54748.8 | 0.36798 | 13247.28 | 0.62806 | 7536.72 | 1 | 5000 | 13247.28 | 7536.72 | 0 | 0 | 0 | 0 | 28964.8 | 0 | 0 | 0 | 0 | 0 | 28964.8
2022042019 | 4 | 0.67693 | 54154.4 | 0.36158 | 13016.88 | 0.51112 | 6133.44 | 1 | 5000 | 13016.88 | 6133.44 | 0 | 0 | 0 | 0 | 30004.08 | 0 | 0 | 0 | 0 | 0 | 30004.08
2022042020 | 4 | 0.65979 | 52783.2 | 0.34181 | 12305.16 | 0.20078 | 2409.36 | 1 | 5000 | 12305.16 | 2409.36 | 0 | 0 | 0 | 0 | 33068.68 | 0 | 0 | 0 | 0 | 0 | 33068.68
2022042021 | 4 | 0.65325 | 52260 | 0.35509 | 12783.24 | 0.00388 | 46.56 | 1 | 5000 | 12783.24 | 46.56 | 0 | 0 | 0 | 0 | 34430.2 | 0 | 0 | 0 | 0 | 0 | 34430.2
2022042022 | 4 | 0.63777 | 51021.6 | 0.4369 | 15728.4 | 0 | 0 | 1 | 5000 | 15728.4 | 0 | 0 | 0 | 0 | 0 | 30293.2 | 0 | 0 | 0 | 0 | 0 | 30293.2
2022042023 | 4 | 0.60165 | 48132 | 0.55141 | 19850.76 | 0 | 0 | 1 | 5000 | 19850.76 | 0 | 0 | 0 | 0 | 0 | 23281.24 | 0 | 0 | 0 | 0 | 0 | 23281.24
2022042024 | 4 | 0.56323 | 45058.4 | 0.61895 | 22282.2 | 0 | 0 | 1 | 5000 | 22282.2 | 0 | 0 | 0 | 0 | 0 | 17776.2 | 0 | 0 | 0 | 0 | 0 | 17776.2
2022042101 | 5 | 0.52705 | 42164 | 0.62633 | 22547.88 | 0 | 0 | 1 | 5000 | 22547.88 | 0 | 0 | 0 | 0 | 0 | 14616.12 | 0 | 0 | 0 | 0 | 0 | 14616.12
2022042102 | 5 | 0.50393 | 40314.4 | 0.62681 | 22565.16 | 0 | 0 | 1 | 5000 | 22565.16 | 0 | 0 | 0 | 0 | 0 | 12749.24 | 0 | 0 | 0 | 0 | 0 | 12749.24
2022042103 | 5 | 0.48812 | 39049.6 | 0.61748 | 22229.28 | 0 | 0 | 1 | 5000 | 22229.28 | 0 | 0 | 0 | 0 | 0 | 11820.32 | 0 | 0 | 0 | 0 | 0 | 11820.32
2022042104 | 5 | 0.48181 | 38544.8 | 0.61068 | 21984.48 | 0 | 0 | 1 | 5000 | 21984.48 | 0 | 0 | 0 | 0 | 0 | 11560.32 | 0 | 0 | 0 | 0 | 0 | 11560.32
2022042105 | 5 | 0.48425 | 38740 | 0.60381 | 21737.16 | 0 | 0 | 1 | 5000 | 21737.16 | 0 | 0 | 0 | 0 | 0 | 12002.84 | 0 | 0 | 0 | 0 | 0 | 12002.84
2022042106 | 5 | 0.50286 | 40228.8 | 0.60649 | 21833.64 | 0 | 0 | 1 | 5000 | 21833.64 | 0 | 0 | 0 | 0 | 0 | 13395.16 | 0 | 0 | 0 | 0 | 0 | 13395.16
2022042107 | 5 | 0.5341 | 42728 | 0.60613 | 21820.68 | 0 | 0 | 1 | 5000 | 21820.68 | 0 | 0 | 0 | 0 | 0 | 15907.32 | 0 | 0 | 0 | 0 | 0 | 15907.32
2022042108 | 5 | 0.55043 | 44034.4 | 0.57901 | 20844.36 | 0.03359 | 403.08 | 1 | 5000 | 20844.36 | 403.08 | 0 | 0 | 0 | 0 | 17786.96 | 0 | 0 | 0 | 0 | 0 | 17786.96
2022042109 | 5 | 0.5611 | 44888 | 0.55709 | 20055.24 | 0.26442 | 3173.04 | 1 | 5000 | 20055.24 | 3173.04 | 0 | 0 | 0 | 0 | 16659.72 | 0 | 0 | 0 | 0 | 0 | 16659.72
2022042110 | 5 | 0.57825 | 46260 | 0.56436 | 20316.96 | 0.29511 | 3541.32 | 1 | 5000 | 20316.96 | 3541.32 | 0 | 0 | 0 | 0 | 17401.72 | 0 | 0 | 0 | 0 | 0 | 17401.72
2022042111 | 5 | 0.59961 | 47968.8 | 0.55066 | 19823.76 | 0.40531 | 4863.72 | 1 | 5000 | 19823.76 | 4863.72 | 0 | 0 | 0 | 0 | 18281.32 | 0 | 0 | 0 | 0 | 0 | 18281.32
2022042112 | 5 | 0.61759 | 49407.2 | 0.5201 | 18723.6 | 0.54682 | 6561.84 | 1 | 5000 | 18723.6 | 6561.84 | 0 | 0 | 0 | 0 | 19121.76 | 0 | 0 | 0 | 0 | 0 | 19121.76
2022042113 | 5 | 0.63524 | 50819.2 | 0.48123 | 17324.28 | 0.69198 | 8303.76 | 1 | 5000 | 17324.28 | 8303.76 | 0 | 0 | 0 | 0 | 20191.16 | 0 | 0 | 0 | 0 | 0 | 20191.16
2022042114 | 5 | 0.65501 | 52400.8 | 0.44329 | 15958.44 | 0.71845 | 8621.4 | 1 | 5000 | 15958.44 | 8621.4 | 0 | 0 | 0 | 0 | 22820.96 | 0 | 0 | 0 | 0 | 0 | 22820.96
2022042115 | 5 | 0.67376 | 53900.8 | 0.45286 | 16302.96 | 0.72608 | 8712.96 | 1 | 5000 | 16302.96 | 8712.96 | 0 | 0 | 0 | 0 | 23884.88 | 0 | 0 | 0 | 0 | 0 | 23884.88
2022042116 | 5 | 0.68818 | 55054.4 | 0.50049 | 18017.64 | 0.68059 | 8167.08 | 1 | 5000 | 18017.64 | 8167.08 | 0 | 0 | 0 | 0 | 23869.68 | 0 | 0 | 0 | 0 | 0 | 23869.68
2022042117 | 5 | 0.69792 | 55833.6 | 0.55099 | 19835.64 | 0.56734 | 6808.08 | 1 | 5000 | 19835.64 | 6808.08 | 0 | 0 | 0 | 0 | 24189.88 | 0 | 0 | 0 | 0 | 0 | 24189.88
2022042118 | 5 | 0.69434 | 55547.2 | 0.60428 | 21754.08 | 0.37943 | 4553.16 | 1 | 5000 | 21754.08 | 4553.16 | 0 | 0 | 0 | 0 | 24239.96 | 0 | 0 | 0 | 0 | 0 | 24239.96
2022042119 | 5 | 0.68008 | 54406.4 | 0.63368 | 22812.48 | 0.25172 | 3020.64 | 1 | 5000 | 22812.48 | 3020.64 | 0 | 0 | 0 | 0 | 23573.28 | 0 | 0 | 0 | 0 | 0 | 23573.28
2022042120 | 5 | 0.66666 | 53332.8 | 0.65365 | 23531.4 | 0.0832 | 998.4 | 1 | 5000 | 23531.4 | 998.4 | 0 | 0 | 0 | 0 | 23803 | 0 | 0 | 0 | 0 | 0 | 23803
2022042121 | 5 | 0.66539 | 53231.2 | 0.67283 | 24221.88 | 0.00309 | 37.08 | 1 | 5000 | 24221.88 | 37.08 | 0 | 0 | 0 | 0 | 23972.24 | 0 | 0 | 0 | 0 | 0 | 23972.24
2022042122 | 5 | 0.64652 | 51721.6 | 0.67739 | 24386.04 | 0 | 0 | 1 | 5000 | 24386.04 | 0 | 0 | 0 | 0 | 0 | 22335.56 | 0 | 0 | 0 | 0 | 0 | 22335.56
2022042123 | 5 | 0.6108 | 48864 | 0.66438 | 23917.68 | 0 | 0 | 1 | 5000 | 23917.68 | 0 | 0 | 0 | 0 | 0 | 19946.32 | 0 | 0 | 0 | 0 | 0 | 19946.32
2022042124 | 5 | 0.56978 | 45582.4 | 0.65282 | 23501.52 | 0 | 0 | 1 | 5000 | 23501.52 | 0 | 0 | 0 | 0 | 0 | 17080.88 | 0 | 0 | 0 | 0 | 0 | 17080.88
2022042201 | 6 | 0.5343 | 42744 | 0.66151 | 23814.36 | 0 | 0 | 1 | 5000 | 23814.36 | 0 | 0 | 0 | 0 | 0 | 13929.64 | 0 | 0 | 0 | 0 | 0 | 13929.64
2022042202 | 6 | 0.51024 | 40819.2 | 0.66079 | 23788.44 | 0 | 0 | 1 | 5000 | 23788.44 | 0 | 0 | 0 | 0 | 0 | 12030.76 | 0 | 0 | 0 | 0 | 0 | 12030.76
2022042203 | 6 | 0.49349 | 39479.2 | 0.65722 | 23659.92 | 0 | 0 | 1 | 5000 | 23659.92 | 0 | 0 | 0 | 0 | 0 | 10819.28 | 0 | 0 | 0 | 0 | 0 | 10819.28
2022042204 | 6 | 0.48467 | 38773.6 | 0.6531 | 23511.6 | 0 | 0 | 1 | 5000 | 23511.6 | 0 | 0 | 0 | 0 | 0 | 10262 | 0 | 0 | 0 | 0 | 0 | 10262
2022042205 | 6 | 0.48796 | 39036.8 | 0.64903 | 23365.08 | 0 | 0 | 1 | 5000 | 23365.08 | 0 | 0 | 0 | 0 | 0 | 10671.72 | 0 | 0 | 0 | 0 | 0 | 10671.72
2022042206 | 6 | 0.50493 | 40394.4 | 0.64857 | 23348.52 | 0 | 0 | 1 | 5000 | 23348.52 | 0 | 0 | 0 | 0 | 0 | 12045.88 | 0 | 0 | 0 | 0 | 0 | 12045.88
2022042207 | 6 | 0.53761 | 43008.8 | 0.65263 | 23494.68 | 0 | 0 | 1 | 5000 | 23494.68 | 0 | 0 | 0 | 0 | 0 | 14514.12 | 0 | 0 | 0 | 0 | 0 | 14514.12
2022042208 | 6 | 0.54586 | 43668.8 | 0.66088 | 23791.68 | 0.0202 | 242.4 | 1 | 5000 | 23791.68 | 242.4 | 0 | 0 | 0 | 0 | 14634.72 | 0 | 0 | 0 | 0 | 0 | 14634.72
2022042209 | 6 | 0.55984 | 44787.2 | 0.66054 | 23779.44 | 0.10855 | 1302.6 | 1 | 5000 | 23779.44 | 1302.6 | 0 | 0 | 0 | 0 | 14705.16 | 0 | 0 | 0 | 0 | 0 | 14705.16
2022042210 | 6 | 0.58207 | 46565.6 | 0.65942 | 23739.12 | 0.14931 | 1791.72 | 1 | 5000 | 23739.12 | 1791.72 | 0 | 0 | 0 | 0 | 16034.76 | 0 | 0 | 0 | 0 | 0 | 16034.76
2022042211 | 6 | 0.60236 | 48188.8 | 0.66108 | 23798.88 | 0.16123 | 1934.76 | 1 | 5000 | 23798.88 | 1934.76 | 0 | 0 | 0 | 0 | 17455.16 | 0 | 0 | 0 | 0 | 0 | 17455.16
2022042212 | 6 | 0.62177 | 49741.6 | 0.67055 | 24139.8 | 0.15268 | 1832.16 | 1 | 5000 | 24139.8 | 1832.16 | 0 | 0 | 0 | 0 | 18769.64 | 0 | 0 | 0 | 0 | 0 | 18769.64
2022042213 | 6 | 0.64236 | 51388.8 | 0.67151 | 24174.36 | 0.18021 | 2162.52 | 1 | 5000 | 24174.36 | 2162.52 | 0 | 0 | 0 | 0 | 20051.92 | 0 | 0 | 0 | 0 | 0 | 20051.92
2022042214 | 6 | 0.66259 | 53007.2 | 0.6716 | 24177.6 | 0.19259 | 2311.08 | 1 | 5000 | 24177.6 | 2311.08 | 0 | 0 | 0 | 0 | 21518.52 | 0 | 0 | 0 | 0 | 0 | 21518.52
2022042215 | 6 | 0.6744 | 53952 | 0.66069 | 23784.84 | 0.2019 | 2422.8 | 1 | 5000 | 23784.84 | 2422.8 | 0 | 0 | 0 | 0 | 22744.36 | 0 | 0 | 0 | 0 | 0 | 22744.36
2022042216 | 6 | 0.68796 | 55036.8 | 0.6509 | 23432.4 | 0.22662 | 2719.44 | 1 | 5000 | 23432.4 | 2719.44 | 0 | 0 | 0 | 0 | 23884.96 | 0 | 0 | 0 | 0 | 0 | 23884.96
2022042217 | 6 | 0.70089 | 56071.2 | 0.64922 | 23371.92 | 0.2437 | 2924.4 | 1 | 5000 | 23371.92 | 2924.4 | 0 | 0 | 0 | 0 | 24774.88 | 0 | 0 | 0 | 0 | 0 | 24774.88
2022042218 | 6 | 0.70278 | 56222.4 | 0.65256 | 23492.16 | 0.24629 | 2955.48 | 1 | 5000 | 23492.16 | 2955.48 | 0 | 0 | 0 | 0 | 24774.76 | 0 | 0 | 0 | 0 | 0 | 24774.76
2022042219 | 6 | 0.67991 | 54392.8 | 0.65496 | 23578.56 | 0.19113 | 2293.56 | 1 | 5000 | 23578.56 | 2293.56 | 0 | 0 | 0 | 0 | 23520.68 | 0 | 0 | 0 | 0 | 0 | 23520.68
2022042220 | 6 | 0.65213 | 52170.4 | 0.65377 | 23535.72 | 0.07744 | 929.28 | 1 | 5000 | 23535.72 | 929.28 | 0 | 0 | 0 | 0 | 22705.4 | 0 | 0 | 0 | 0 | 0 | 22705.4
2022042221 | 6 | 0.64111 | 51288.8 | 0.67458 | 24284.88 | 0.00248 | 29.76 | 1 | 5000 | 24284.88 | 29.76 | 0 | 0 | 0 | 0 | 21974.16 | 0 | 0 | 0 | 0 | 0 | 21974.16
2022042222 | 6 | 0.62012 | 49609.6 | 0.67075 | 24147 | 0 | 0 | 1 | 5000 | 24147 | 0 | 0 | 0 | 0 | 0 | 20462.6 | 0 | 0 | 0 | 0 | 0 | 20462.6
2022042223 | 6 | 0.58937 | 47149.6 | 0.67206 | 24194.16 | 0 | 0 | 1 | 5000 | 24194.16 | 0 | 0 | 0 | 0 | 0 | 17955.44 | 0 | 0 | 0 | 0 | 0 | 17955.44
2022042224 | 6 | 0.55442 | 44353.6 | 0.66775 | 24039 | 0 | 0 | 1 | 5000 | 24039 | 0 | 0 | 0 | 0 | 0 | 15314.6 | 0 | 0 | 0 | 0 | 0 | 15314.6
2022042301 | 7 | 0.52368 | 41894.4 | 0.66743 | 24027.48 | 0 | 0 | 1 | 5000 | 24027.48 | 0 | 0 | 0 | 0 | 0 | 12866.92 | 0 | 0 | 0 | 0 | 0 | 12866.92
2022042302 | 7 | 0.49912 | 39929.6 | 0.66199 | 23831.64 | 0 | 0 | 1 | 5000 | 23831.64 | 0 | 0 | 0 | 0 | 0 | 11097.96 | 0 | 0 | 0 | 0 | 0 | 11097.96
2022042303 | 7 | 0.48001 | 38400.8 | 0.65674 | 23642.64 | 0 | 0 | 1 | 5000 | 23642.64 | 0 | 0 | 0 | 0 | 0 | 9758.16 | 0 | 0 | 0 | 0 | 0 | 9758.16
2022042304 | 7 | 0.47106 | 37684.8 | 0.65598 | 23615.28 | 0 | 0 | 1 | 5000 | 23615.28 | 0 | 0 | 0 | 0 | 0 | 9069.52 | 0 | 0 | 0 | 0 | 0 | 9069.52
2022042305 | 7 | 0.4646 | 37168 | 0.64846 | 23344.56 | 0 | 0 | 1 | 5000 | 23344.56 | 0 | 0 | 0 | 0 | 0 | 8823.44 | 0 | 0 | 0 | 0 | 0 | 8823.44
2022042306 | 7 | 0.46648 | 37318.4 | 0.64634 | 23268.24 | 0 | 0 | 1 | 5000 | 23268.24 | 0 | 0 | 0 | 0 | 0 | 9050.16 | 0 | 0 | 0 | 0 | 0 | 9050.16
2022042307 | 7 | 0.47508 | 38006.4 | 0.64317 | 23154.12 | 5e-05 | 0.6 | 1 | 5000 | 23154.12 | 0.6 | 0 | 0 | 0 | 0 | 9851.68 | 0 | 0 | 0 | 0 | 0 | 9851.68
2022042308 | 7 | 0.48617 | 38893.6 | 0.64795 | 23326.2 | 0.02642 | 317.04 | 1 | 5000 | 23326.2 | 317.04 | 0 | 0 | 0 | 0 | 10250.36 | 0 | 0 | 0 | 0 | 0 | 10250.36
2022042309 | 7 | 0.51057 | 40845.6 | 0.6362 | 22903.2 | 0.13377 | 1605.24 | 1 | 5000 | 22903.2 | 1605.24 | 0 | 0 | 0 | 0 | 11337.16 | 0 | 0 | 0 | 0 | 0 | 11337.16
2022042310 | 7 | 0.53688 | 42950.4 | 0.62986 | 22674.96 | 0.19811 | 2377.32 | 1 | 5000 | 22674.96 | 2377.32 | 0 | 0 | 0 | 0 | 12898.12 | 0 | 0 | 0 | 0 | 0 | 12898.12
2022042311 | 7 | 0.56285 | 45028 | 0.61328 | 22078.08 | 0.31014 | 3721.68 | 1 | 5000 | 22078.08 | 3721.68 | 0 | 0 | 0 | 0 | 14228.24 | 0 | 0 | 0 | 0 | 0 | 14228.24
2022042312 | 7 | 0.5854 | 46832 | 0.58867 | 21192.12 | 0.40415 | 4849.8 | 1 | 5000 | 21192.12 | 4849.8 | 0 | 0 | 0 | 0 | 15790.08 | 0 | 0 | 0 | 0 | 0 | 15790.08
2022042313 | 7 | 0.60171 | 48136.8 | 0.55866 | 20111.76 | 0.51418 | 6170.16 | 1 | 5000 | 20111.76 | 6170.16 | 0 | 0 | 0 | 0 | 16854.88 | 0 | 0 | 0 | 0 | 0 | 16854.88
2022042314 | 7 | 0.61811 | 49448.8 | 0.53433 | 19235.88 | 0.60924 | 7310.88 | 1 | 5000 | 19235.88 | 7310.88 | 0 | 0 | 0 | 0 | 17902.04 | 0 | 0 | 0 | 0 | 0 | 17902.04
2022042315 | 7 | 0.63256 | 50604.8 | 0.53921 | 19411.56 | 0.60786 | 7294.32 | 1 | 5000 | 19411.56 | 7294.32 | 0 | 0 | 0 | 0 | 18898.92 | 0 | 0 | 0 | 0 | 0 | 18898.92
2022042316 | 7 | 0.64585 | 51668 | 0.56636 | 20388.96 | 0.52048 | 6245.76 | 1 | 5000 | 20388.96 | 6245.76 | 0 | 0 | 0 | 0 | 20033.28 | 0 | 0 | 0 | 0 | 0 | 20033.28
2022042317 | 7 | 0.65526 | 52420.8 | 0.58382 | 21017.52 | 0.47345 | 5681.4 | 1 | 5000 | 21017.52 | 5681.4 | 0 | 0 | 0 | 0 | 20721.88 | 0 | 0 | 0 | 0 | 0 | 20721.88
2022042318 | 7 | 0.65325 | 52260 | 0.59101 | 21276.36 | 0.4437 | 5324.4 | 1 | 5000 | 21276.36 | 5324.4 | 0 | 0 | 0 | 0 | 20659.24 | 0 | 0 | 0 | 0 | 0 | 20659.24
2022042319 | 7 | 0.64088 | 51270.4 | 0.60042 | 21615.12 | 0.32077 | 3849.24 | 1 | 5000 | 21615.12 | 3849.24 | 0 | 0 | 0 | 0 | 20806.04 | 0 | 0 | 0 | 0 | 0 | 20806.04
2022042320 | 7 | 0.61994 | 49595.2 | 0.59902 | 21564.72 | 0.1519 | 1822.8 | 1 | 5000 | 21564.72 | 1822.8 | 0 | 0 | 0 | 0 | 21207.68 | 0 | 0 | 0 | 0 | 0 | 21207.68
2022042321 | 7 | 0.61191 | 48952.8 | 0.56956 | 20504.16 | 0.00581 | 69.72 | 1 | 5000 | 20504.16 | 69.72 | 0 | 0 | 0 | 0 | 23378.92 | 0 | 0 | 0 | 0 | 0 | 23378.92
2022042322 | 7 | 0.59714 | 47771.2 | 0.58862 | 21190.32 | 0 | 0 | 1 | 5000 | 21190.32 | 0 | 0 | 0 | 0 | 0 | 21580.88 | 0 | 0 | 0 | 0 | 0 | 21580.88
2022042323 | 7 | 0.57252 | 45801.6 | 0.60473 | 21770.28 | 0 | 0 | 1 | 5000 | 21770.28 | 0 | 0 | 0 | 0 | 0 | 19031.32 | 0 | 0 | 0 | 0 | 0 | 19031.32
2022042324 | 7 | 0.54115 | 43292 | 0.61766 | 22235.76 | 0 | 0 | 1 | 5000 | 22235.76 | 0 | 0 | 0 | 0 | 0 | 16056.24 | 0 | 0 | 0 | 0 | 0 | 16056.24
2022042401 | 1 | 0.51521 | 41216.8 | 0.58871 | 21193.56 | 0 | 0 | 1 | 5000 | 21193.56 | 0 | 0 | 0 | 0 | 0 | 15023.24 | 0 | 0 | 0 | 0 | 0 | 15023.24
2022042402 | 1 | 0.48899 | 39119.2 | 0.57261 | 20613.96 | 0 | 0 | 1 | 5000 | 20613.96 | 0 | 0 | 0 | 0 | 0 | 13505.24 | 0 | 0 | 0 | 0 | 0 | 13505.24
2022042403 | 1 | 0.47192 | 37753.6 | 0.52682 | 18965.52 | 0 | 0 | 1 | 5000 | 18965.52 | 0 | 0 | 0 | 0 | 0 | 13788.08 | 0 | 0 | 0 | 0 | 0 | 13788.08
2022042404 | 1 | 0.45971 | 36776.8 | 0.49416 | 17789.76 | 0 | 0 | 1 | 5000 | 17789.76 | 0 | 0 | 0 | 0 | 0 | 13987.04 | 0 | 0 | 0 | 0 | 0 | 13987.04
2022042405 | 1 | 0.45515 | 36412 | 0.45569 | 16404.84 | 0 | 0 | 1 | 5000 | 16404.84 | 0 | 0 | 0 | 0 | 0 | 15007.16 | 0 | 0 | 0 | 0 | 0 | 15007.16
2022042406 | 1 | 0.45367 | 36293.6 | 0.40988 | 14755.68 | 0 | 0 | 1 | 5000 | 14755.68 | 0 | 0 | 0 | 0 | 0 | 16537.92 | 0 | 0 | 0 | 0 | 0 | 16537.92
2022042407 | 1 | 0.45623 | 36498.4 | 0.40328 | 14518.08 | 5e-05 | 0.6 | 1 | 5000 | 14518.08 | 0.6 | 0 | 0 | 0 | 0 | 16979.72 | 0 | 0 | 0 | 0 | 0 | 16979.72
2022042408 | 1 | 0.46197 | 36957.6 | 0.42744 | 15387.84 | 0.03055 | 366.6 | 1 | 5000 | 15387.84 | 366.6 | 0 | 0 | 0 | 0 | 16203.16 | 0 | 0 | 0 | 0 | 0 | 16203.16
2022042409 | 1 | 0.48564 | 38851.2 | 0.45222 | 16279.92 | 0.23659 | 2839.08 | 1 | 5000 | 16279.92 | 2839.08 | 0 | 0 | 0 | 0 | 14732.2 | 0 | 0 | 0 | 0 | 0 | 14732.2
2022042410 | 1 | 0.51886 | 41508.8 | 0.49722 | 17899.92 | 0.36661 | 4399.32 | 1 | 5000 | 17899.92 | 4399.32 | 0 | 0 | 0 | 0 | 14209.56 | 0 | 0 | 0 | 0 | 0 | 14209.56
2022042411 | 1 | 0.54793 | 43834.4 | 0.50456 | 18164.16 | 0.44583 | 5349.96 | 1 | 5000 | 18164.16 | 5349.96 | 0 | 0 | 0 | 0 | 15320.28 | 0 | 0 | 0 | 0 | 0 | 15320.28
2022042412 | 1 | 0.57537 | 46029.6 | 0.49579 | 17848.44 | 0.53932 | 6471.84 | 1 | 5000 | 17848.44 | 6471.84 | 0 | 0 | 0 | 0 | 16709.32 | 0 | 0 | 0 | 0 | 0 | 16709.32
2022042413 | 1 | 0.59718 | 47774.4 | 0.49213 | 17716.68 | 0.547 | 6564 | 1 | 5000 | 17716.68 | 6564 | 0 | 0 | 0 | 0 | 18493.72 | 0 | 0 | 0 | 0 | 0 | 18493.72
2022042414 | 1 | 0.61206 | 48964.8 | 0.48503 | 17461.08 | 0.53793 | 6455.16 | 1 | 5000 | 17461.08 | 6455.16 | 0 | 0 | 0 | 0 | 20048.56 | 0 | 0 | 0 | 0 | 0 | 20048.56
2022042415 | 1 | 0.63104 | 50483.2 | 0.46977 | 16911.72 | 0.5965 | 7158 | 1 | 5000 | 16911.72 | 7158 | 0 | 0 | 0 | 0 | 21413.48 | 0 | 0 | 0 | 0 | 0 | 21413.48
2022042416 | 1 | 0.64515 | 51612 | 0.45268 | 16296.48 | 0.57822 | 6938.64 | 1 | 5000 | 16296.48 | 6938.64 | 0 | 0 | 0 | 0 | 23376.88 | 0 | 0 | 0 | 0 | 0 | 23376.88
2022042417 | 1 | 0.65445 | 52356 | 0.42925 | 15453 | 0.56874 | 6824.88 | 1 | 5000 | 15453 | 6824.88 | 0 | 0 | 0 | 0 | 25078.12 | 0 | 0 | 0 | 0 | 0 | 25078.12
2022042418 | 1 | 0.65606 | 52484.8 | 0.42328 | 15238.08 | 0.53539 | 6424.68 | 1 | 5000 | 15238.08 | 6424.68 | 0 | 0 | 0 | 0 | 25822.04 | 0 | 0 | 0 | 0 | 0 | 25822.04
2022042419 | 1 | 0.64452 | 51561.6 | 0.42293 | 15225.48 | 0.44446 | 5333.52 | 1 | 5000 | 15225.48 | 5333.52 | 0 | 0 | 0 | 0 | 26002.6 | 0 | 0 | 0 | 0 | 0 | 26002.6
2022042420 | 1 | 0.62336 | 49868.8 | 0.42022 | 15127.92 | 0.16757 | 2010.84 | 1 | 5000 | 15127.92 | 2010.84 | 0 | 0 | 0 | 0 | 27730.04 | 0 | 0 | 0 | 0 | 0 | 27730.04
2022042421 | 1 | 0.61839 | 49471.2 | 0.43733 | 15743.88 | 0.00487 | 58.44 | 1 | 5000 | 15743.88 | 58.44 | 0 | 0 | 0 | 0 | 28668.88 | 0 | 0 | 0 | 0 | 0 | 28668.88
2022042422 | 1 | 0.60178 | 48142.4 | 0.45458 | 16364.88 | 0 | 0 | 1 | 5000 | 16364.88 | 0 | 0 | 0 | 0 | 0 | 26777.52 | 0 | 0 | 0 | 0 | 0 | 26777.52
2022042423 | 1 | 0.57017 | 45613.6 | 0.46829 | 16858.44 | 0 | 0 | 1 | 5000 | 16858.44 | 0 | 0 | 0 | 0 | 0 | 23755.16 | 0 | 0 | 0 | 0 | 0 | 23755.16
2022042424 | 1 | 0.53057 | 42445.6 | 0.49287 | 17743.32 | 0 | 0 | 1 | 5000 | 17743.32 | 0 | 0 | 0 | 0 | 0 | 19702.28 | 0 | 0 | 0 | 0 | 0 | 19702.28
2022042501 | 2 | 0.49946 | 39956.8 | 0.51188 | 18427.68 | 0 | 0 | 1 | 5000 | 18427.68 | 0 | 0 | 0 | 0 | 0 | 16529.12 | 0 | 0 | 0 | 0 | 0 | 16529.12
2022042502 | 2 | 0.47825 | 38260 | 0.48939 | 17618.04 | 0 | 0 | 1 | 5000 | 17618.04 | 0 | 0 | 0 | 0 | 0 | 15641.96 | 0 | 0 | 0 | 0 | 0 | 15641.96
2022042503 | 2 | 0.46219 | 36975.2 | 0.44142 | 15891.12 | 0 | 0 | 1 | 5000 | 15891.12 | 0 | 0 | 0 | 0 | 0 | 16084.08 | 0 | 0 | 0 | 0 | 0 | 16084.08
2022042504 | 2 | 0.45713 | 36570.4 | 0.42237 | 15205.32 | 0 | 0 | 1 | 5000 | 15205.32 | 0 | 0 | 0 | 0 | 0 | 16365.08 | 0 | 0 | 0 | 0 | 0 | 16365.08
2022042505 | 2 | 0.46107 | 36885.6 | 0.43833 | 15779.88 | 0 | 0 | 1 | 5000 | 15779.88 | 0 | 0 | 0 | 0 | 0 | 16105.72 | 0 | 0 | 0 | 0 | 0 | 16105.72
2022042506 | 2 | 0.47842 | 38273.6 | 0.46724 | 16820.64 | 0 | 0 | 1 | 5000 | 16820.64 | 0 | 0 | 0 | 0 | 0 | 16452.96 | 0 | 0 | 0 | 0 | 0 | 16452.96
2022042507 | 2 | 0.50547 | 40437.6 | 0.49724 | 17900.64 | 0 | 0 | 1 | 5000 | 17900.64 | 0 | 0 | 0 | 0 | 0 | 17536.96 | 0 | 0 | 0 | 0 | 0 | 17536.96
2022042508 | 2 | 0.52435 | 41948 | 0.53899 | 19403.64 | 0.01592 | 191.04 | 1 | 5000 | 19403.64 | 191.04 | 0 | 0 | 0 | 0 | 17353.32 | 0 | 0 | 0 | 0 | 0 | 17353.32
2022042509 | 2 | 0.53564 | 42851.2 | 0.56773 | 20438.28 | 0.11787 | 1414.44 | 1 | 5000 | 20438.28 | 1414.44 | 0 | 0 | 0 | 0 | 15998.48 | 0 | 0 | 0 | 0 | 0 | 15998.48
2022042510 | 2 | 0.55369 | 44295.2 | 0.59711 | 21495.96 | 0.18334 | 2200.08 | 1 | 5000 | 21495.96 | 2200.08 | 0 | 0 | 0 | 0 | 15599.16 | 0 | 0 | 0 | 0 | 0 | 15599.16
2022042511 | 2 | 0.56852 | 45481.6 | 0.60217 | 21678.12 | 0.21049 | 2525.88 | 1 | 5000 | 21678.12 | 2525.88 | 0 | 0 | 0 | 0 | 16277.6 | 0 | 0 | 0 | 0 | 0 | 16277.6
2022042512 | 2 | 0.58238 | 46590.4 | 0.58891 | 21200.76 | 0.26129 | 3135.48 | 1 | 5000 | 21200.76 | 3135.48 | 0 | 0 | 0 | 0 | 17254.16 | 0 | 0 | 0 | 0 | 0 | 17254.16
2022042513 | 2 | 0.59197 | 47357.6 | 0.53064 | 19103.04 | 0.42795 | 5135.4 | 1 | 5000 | 19103.04 | 5135.4 | 0 | 0 | 0 | 0 | 18119.16 | 0 | 0 | 0 | 0 | 0 | 18119.16
2022042514 | 2 | 0.59613 | 47690.4 | 0.47602 | 17136.72 | 0.54636 | 6556.32 | 1 | 5000 | 17136.72 | 6556.32 | 0 | 0 | 0 | 0 | 18997.36 | 0 | 0 | 0 | 0 | 0 | 18997.36
2022042515 | 2 | 0.58927 | 47141.6 | 0.46166 | 16619.76 | 0.57589 | 6910.68 | 1 | 5000 | 16619.76 | 6910.68 | 0 | 0 | 0 | 0 | 18611.16 | 0 | 0 | 0 | 0 | 0 | 18611.16
2022042516 | 2 | 0.57094 | 45675.2 | 0.45382 | 16337.52 | 0.58764 | 7051.68 | 1 | 5000 | 16337.52 | 7051.68 | 0 | 0 | 0 | 0 | 17286 | 0 | 0 | 0 | 0 | 0 | 17286
2022042517 | 2 | 0.56222 | 44977.6 | 0.44331 | 15959.16 | 0.56371 | 6764.52 | 1 | 5000 | 15959.16 | 6764.52 | 0 | 0 | 0 | 0 | 17253.92 | 0 | 0 | 0 | 0 | 0 | 17253.92
2022042518 | 2 | 0.55818 | 44654.4 | 0.44972 | 16189.92 | 0.53157 | 6378.84 | 1 | 5000 | 16189.92 | 6378.84 | 0 | 0 | 0 | 0 | 17085.64 | 0 | 0 | 0 | 0 | 0 | 17085.64
2022042519 | 2 | 0.54892 | 43913.6 | 0.46824 | 16856.64 | 0.47478 | 5697.36 | 1 | 5000 | 16856.64 | 5697.36 | 0 | 0 | 0 | 0 | 16359.6 | 0 | 0 | 0 | 0 | 0 | 16359.6
2022042520 | 2 | 0.53941 | 43152.8 | 0.47009 | 16923.24 | 0.19255 | 2310.6 | 1 | 5000 | 16923.24 | 2310.6 | 0 | 0 | 0 | 0 | 18918.96 | 0 | 0 | 0 | 0 | 0 | 18918.96
2022042521 | 2 | 0.53947 | 43157.6 | 0.41991 | 15116.76 | 0.00497 | 59.64 | 1 | 5000 | 15116.76 | 59.64 | 0 | 0 | 0 | 0 | 22981.2 | 0 | 0 | 0 | 0 | 0 | 22981.2
2022042522 | 2 | 0.52504 | 42003.2 | 0.40125 | 14445 | 0 | 0 | 1 | 5000 | 14445 | 0 | 0 | 0 | 0 | 0 | 22558.2 | 0 | 0 | 0 | 0 | 0 | 22558.2
2022042523 | 2 | 0.49483 | 39586.4 | 0.41674 | 15002.64 | 0 | 0 | 1 | 5000 | 15002.64 | 0 | 0 | 0 | 0 | 0 | 19583.76 | 0 | 0 | 0 | 0 | 0 | 19583.76
2022042524 | 2 | 0.46022 | 36817.6 | 0.38239 | 13766.04 | 0 | 0 | 1 | 5000 | 13766.04 | 0 | 0 | 0 | 0 | 0 | 18051.56 | 0 | 0 | 0 | 0 | 0 | 18051.56
2022042601 | 3 | 0.43628 | 34902.4 | 0.35137 | 12649.32 | 0 | 0 | 1 | 5000 | 12649.32 | 0 | 0 | 0 | 0 | 0 | 17253.08 | 0 | 0 | 0 | 0 | 0 | 17253.08
2022042602 | 3 | 0.42118 | 33694.4 | 0.36984 | 13314.24 | 0 | 0 | 1 | 5000 | 13314.24 | 0 | 0 | 0 | 0 | 0 | 15380.16 | 0 | 0 | 0 | 0 | 0 | 15380.16
2022042603 | 3 | 0.41205 | 32964 | 0.35274 | 12698.64 | 0 | 0 | 1 | 5000 | 12698.64 | 0 | 0 | 0 | 0 | 0 | 15265.36 | 0 | 0 | 0 | 0 | 0 | 15265.36
2022042604 | 3 | 0.40795 | 32636 | 0.33085 | 11910.6 | 0 | 0 | 1 | 5000 | 11910.6 | 0 | 0 | 0 | 0 | 0 | 15725.4 | 0 | 0 | 0 | 0 | 0 | 15725.4
2022042605 | 3 | 0.41184 | 32947.2 | 0.30898 | 11123.28 | 0 | 0 | 1 | 5000 | 11123.28 | 0 | 0 | 0 | 0 | 0 | 16823.92 | 0 | 0 | 0 | 0 | 0 | 16823.92
2022042606 | 3 | 0.43068 | 34454.4 | 0.30129 | 10846.44 | 0 | 0 | 1 | 5000 | 10846.44 | 0 | 0 | 0 | 0 | 0 | 18607.96 | 0 | 0 | 0 | 0 | 0 | 18607.96
2022042607 | 3 | 0.46534 | 37227.2 | 0.31185 | 11226.6 | 0.00028 | 3.36 | 1 | 5000 | 11226.6 | 3.36 | 0 | 0 | 0 | 0 | 20997.24 | 0 | 0 | 0 | 0 | 0 | 20997.24
2022042608 | 3 | 0.48171 | 38536.8 | 0.27415 | 9869.4 | 0.07086 | 850.32 | 1 | 5000 | 9869.4 | 850.32 | 0 | 0 | 0 | 0 | 22817.08 | 0 | 0 | 0 | 0 | 0 | 22817.08
2022042609 | 3 | 0.48841 | 39072.8 | 0.22967 | 8268.12 | 0.3895 | 4674 | 1 | 5000 | 8268.12 | 4674 | 0 | 0 | 0 | 0 | 21130.68 | 0 | 0 | 0 | 0 | 0 | 21130.68
2022042610 | 3 | 0.49406 | 39524.8 | 0.26895 | 9682.2 | 0.55628 | 6675.36 | 1 | 5000 | 9682.2 | 6675.36 | 0 | 0 | 0 | 0 | 18167.24 | 0 | 0 | 0 | 0 | 0 | 18167.24
2022042611 | 3 | 0.49926 | 39940.8 | 0.27488 | 9895.68 | 0.60393 | 7247.16 | 1 | 5000 | 9895.68 | 7247.16 | 0 | 0 | 0 | 0 | 17797.96 | 0 | 0 | 0 | 0 | 0 | 17797.96
2022042612 | 3 | 0.50538 | 40430.4 | 0.2311 | 8319.6 | 0.6459 | 7750.8 | 1 | 5000 | 8319.6 | 7750.8 | 0 | 0 | 0 | 0 | 19360 | 0 | 0 | 0 | 0 | 0 | 19360
2022042613 | 3 | 0.51112 | 40889.6 | 0.20819 | 7494.84 | 0.65924 | 7910.88 | 1 | 5000 | 7494.84 | 7910.88 | 0 | 0 | 0 | 0 | 20483.88 | 0 | 0 | 0 | 0 | 0 | 20483.88
2022042614 | 3 | 0.52003 | 41602.4 | 0.20586 | 7410.96 | 0.67607 | 8112.84 | 1 | 5000 | 7410.96 | 8112.84 | 0 | 0 | 0 | 0 | 21078.6 | 0 | 0 | 0 | 0 | 0 | 21078.6
2022042615 | 3 | 0.53235 | 42588 | 0.20917 | 7530.12 | 0.70721 | 8486.52 | 1 | 5000 | 7530.12 | 8486.52 | 0 | 0 | 0 | 0 | 21571.36 | 0 | 0 | 0 | 0 | 0 | 21571.36
2022042616 | 3 | 0.5448 | 43584 | 0.21629 | 7786.44 | 0.72026 | 8643.12 | 1 | 5000 | 7786.44 | 8643.12 | 0 | 0 | 0 | 0 | 22154.44 | 0 | 0 | 0 | 0 | 0 | 22154.44
2022042617 | 3 | 0.55947 | 44757.6 | 0.22368 | 8052.48 | 0.72959 | 8755.08 | 1 | 5000 | 8052.48 | 8755.08 | 0 | 0 | 0 | 0 | 22950.04 | 0 | 0 | 0 | 0 | 0 | 22950.04
2022042618 | 3 | 0.57 | 45600 | 0.24144 | 8691.84 | 0.67753 | 8130.36 | 1 | 5000 | 8691.84 | 8130.36 | 0 | 0 | 0 | 0 | 23777.8 | 0 | 0 | 0 | 0 | 0 | 23777.8
2022042619 | 3 | 0.56715 | 45372 | 0.27675 | 9963 | 0.55413 | 6649.56 | 1 | 5000 | 9963 | 6649.56 | 0 | 0 | 0 | 0 | 23759.44 | 0 | 0 | 0 | 0 | 0 | 23759.44
2022042620 | 3 | 0.55895 | 44716 | 0.30435 | 10956.6 | 0.22075 | 2649 | 1 | 5000 | 10956.6 | 2649 | 0 | 0 | 0 | 0 | 26110.4 | 0 | 0 | 0 | 0 | 0 | 26110.4
2022042621 | 3 | 0.56042 | 44833.6 | 0.30338 | 10921.68 | 0.00522 | 62.64 | 1 | 5000 | 10921.68 | 62.64 | 0 | 0 | 0 | 0 | 28849.28 | 0 | 0 | 0 | 0 | 0 | 28849.28
2022042622 | 3 | 0.54769 | 43815.2 | 0.35108 | 12638.88 | 0 | 0 | 1 | 5000 | 12638.88 | 0 | 0 | 0 | 0 | 0 | 26176.32 | 0 | 0 | 0 | 0 | 0 | 26176.32
2022042623 | 3 | 0.51616 | 41292.8 | 0.41372 | 14893.92 | 0 | 0 | 1 | 5000 | 14893.92 | 0 | 0 | 0 | 0 | 0 | 21398.88 | 0 | 0 | 0 | 0 | 0 | 21398.88
2022042624 | 3 | 0.47969 | 38375.2 | 0.45822 | 16495.92 | 0 | 0 | 1 | 5000 | 16495.92 | 0 | 0 | 0 | 0 | 0 | 16879.28 | 0 | 0 | 0 | 0 | 0 | 16879.28
2022042701 | 4 | 0.45109 | 36087.2 | 0.4619 | 16628.4 | 0 | 0 | 1 | 5000 | 16628.4 | 0 | 0 | 0 | 0 | 0 | 14458.8 | 0 | 0 | 0 | 0 | 0 | 14458.8
2022042702 | 4 | 0.43103 | 34482.4 | 0.45121 | 16243.56 | 0 | 0 | 1 | 5000 | 16243.56 | 0 | 0 | 0 | 0 | 0 | 13238.84 | 0 | 0 | 0 | 0 | 0 | 13238.84
2022042703 | 4 | 0.41902 | 33521.6 | 0.45522 | 16387.92 | 0 | 0 | 1 | 5000 | 16387.92 | 0 | 0 | 0 | 0 | 0 | 12133.68 | 0 | 0 | 0 | 0 | 0 | 12133.68
2022042704 | 4 | 0.41545 | 33236 | 0.45146 | 16252.56 | 0 | 0 | 1 | 5000 | 16252.56 | 0 | 0 | 0 | 0 | 0 | 11983.44 | 0 | 0 | 0 | 0 | 0 | 11983.44
2022042705 | 4 | 0.41895 | 33516 | 0.4271 | 15375.6 | 0 | 0 | 1 | 5000 | 15375.6 | 0 | 0 | 0 | 0 | 0 | 13140.4 | 0 | 0 | 0 | 0 | 0 | 13140.4
2022042706 | 4 | 0.43705 | 34964 | 0.41466 | 14927.76 | 0 | 0 | 1 | 5000 | 14927.76 | 0 | 0 | 0 | 0 | 0 | 15036.24 | 0 | 0 | 0 | 0 | 0 | 15036.24
2022042707 | 4 | 0.47047 | 37637.6 | 0.40649 | 14633.64 | 0.00037 | 4.44 | 1 | 5000 | 14633.64 | 4.44 | 0 | 0 | 0 | 0 | 17999.52 | 0 | 0 | 0 | 0 | 0 | 17999.52
2022042708 | 4 | 0.48373 | 38698.4 | 0.3972 | 14299.2 | 0.05014 | 601.68 | 1 | 5000 | 14299.2 | 601.68 | 0 | 0 | 0 | 0 | 18797.52 | 0 | 0 | 0 | 0 | 0 | 18797.52
2022042709 | 4 | 0.49349 | 39479.2 | 0.35635 | 12828.6 | 0.23024 | 2762.88 | 1 | 5000 | 12828.6 | 2762.88 | 0 | 0 | 0 | 0 | 18887.72 | 0 | 0 | 0 | 0 | 0 | 18887.72
2022042710 | 4 | 0.5064 | 40512 | 0.37485 | 13494.6 | 0.40289 | 4834.68 | 1 | 5000 | 13494.6 | 4834.68 | 0 | 0 | 0 | 0 | 17182.72 | 0 | 0 | 0 | 0 | 0 | 17182.72
2022042711 | 4 | 0.52134 | 41707.2 | 0.40645 | 14632.2 | 0.55995 | 6719.4 | 1 | 5000 | 14632.2 | 6719.4 | 0 | 0 | 0 | 0 | 15355.6 | 0 | 0 | 0 | 0 | 0 | 15355.6
2022042712 | 4 | 0.53722 | 42977.6 | 0.43371 | 15613.56 | 0.59438 | 7132.56 | 1 | 5000 | 15613.56 | 7132.56 | 0 | 0 | 0 | 0 | 15231.48 | 0 | 0 | 0 | 0 | 0 | 15231.48
2022042713 | 4 | 0.55328 | 44262.4 | 0.47162 | 16978.32 | 0.55581 | 6669.72 | 1 | 5000 | 16978.32 | 6669.72 | 0 | 0 | 0 | 0 | 15614.36 | 0 | 0 | 0 | 0 | 0 | 15614.36
2022042714 | 4 | 0.57196 | 45756.8 | 0.49499 | 17819.64 | 0.50303 | 6036.36 | 1 | 5000 | 17819.64 | 6036.36 | 0 | 0 | 0 | 0 | 16900.8 | 0 | 0 | 0 | 0 | 0 | 16900.8
2022042715 | 4 | 0.5901 | 47208 | 0.51817 | 18654.12 | 0.47952 | 5754.24 | 1 | 5000 | 18654.12 | 5754.24 | 0 | 0 | 0 | 0 | 17799.64 | 0 | 0 | 0 | 0 | 0 | 17799.64
2022042716 | 4 | 0.60675 | 48540 | 0.54283 | 19541.88 | 0.42444 | 5093.28 | 1 | 5000 | 19541.88 | 5093.28 | 0 | 0 | 0 | 0 | 18904.84 | 0 | 0 | 0 | 0 | 0 | 18904.84
2022042717 | 4 | 0.62244 | 49795.2 | 0.57961 | 20865.96 | 0.36125 | 4335 | 1 | 5000 | 20865.96 | 4335 | 0 | 0 | 0 | 0 | 19594.24 | 0 | 0 | 0 | 0 | 0 | 19594.24
2022042718 | 4 | 0.62842 | 50273.6 | 0.58939 | 21218.04 | 0.34614 | 4153.68 | 1 | 5000 | 21218.04 | 4153.68 | 0 | 0 | 0 | 0 | 19901.88 | 0 | 0 | 0 | 0 | 0 | 19901.88
2022042719 | 4 | 0.61859 | 49487.2 | 0.59834 | 21540.24 | 0.2623 | 3147.6 | 1 | 5000 | 21540.24 | 3147.6 | 0 | 0 | 0 | 0 | 19799.36 | 0 | 0 | 0 | 0 | 0 | 19799.36
2022042720 | 4 | 0.60383 | 48306.4 | 0.6084 | 21902.4 | 0.08144 | 977.28 | 1 | 5000 | 21902.4 | 977.28 | 0 | 0 | 0 | 0 | 20426.72 | 0 | 0 | 0 | 0 | 0 | 20426.72
2022042721 | 4 | 0.59688 | 47750.4 | 0.57721 | 20779.56 | 0.00235 | 28.2 | 1 | 5000 | 20779.56 | 28.2 | 0 | 0 | 0 | 0 | 21942.64 | 0 | 0 | 0 | 0 | 0 | 21942.64
2022042722 | 4 | 0.58033 | 46426.4 | 0.58841 | 21182.76 | 0 | 0 | 1 | 5000 | 21182.76 | 0 | 0 | 0 | 0 | 0 | 20243.64 | 0 | 0 | 0 | 0 | 0 | 20243.64
2022042723 | 4 | 0.54531 | 43624.8 | 0.61385 | 22098.6 | 0 | 0 | 1 | 5000 | 22098.6 | 0 | 0 | 0 | 0 | 0 | 16526.2 | 0 | 0 | 0 | 0 | 0 | 16526.2
2022042724 | 4 | 0.50627 | 40501.6 | 0.61992 | 22317.12 | 0 | 0 | 1 | 5000 | 22317.12 | 0 | 0 | 0 | 0 | 0 | 13184.48 | 0 | 0 | 0 | 0 | 0 | 13184.48
2022042801 | 5 | 0.47511 | 38008.8 | 0.63529 | 22870.44 | 0 | 0 | 1 | 5000 | 22870.44 | 0 | 0 | 0 | 0 | 0 | 10138.36 | 0 | 0 | 0 | 0 | 0 | 10138.36
2022042802 | 5 | 0.45483 | 36386.4 | 0.63535 | 22872.6 | 0 | 0 | 1 | 5000 | 22872.6 | 0 | 0 | 0 | 0 | 0 | 8513.8 | 0 | 0 | 0 | 0 | 0 | 8513.8
2022042803 | 5 | 0.44214 | 35371.2 | 0.61481 | 22133.16 | 0 | 0 | 1 | 5000 | 22133.16 | 0 | 0 | 0 | 0 | 0 | 8238.04 | 0 | 0 | 0 | 0 | 0 | 8238.04
2022042804 | 5 | 0.43647 | 34917.6 | 0.60209 | 21675.24 | 0 | 0 | 1 | 5000 | 21675.24 | 0 | 0 | 0 | 0 | 0 | 8242.36 | 0 | 0 | 0 | 0 | 0 | 8242.36
2022042805 | 5 | 0.43752 | 35001.6 | 0.58653 | 21115.08 | 0 | 0 | 1 | 5000 | 21115.08 | 0 | 0 | 0 | 0 | 0 | 8886.52 | 0 | 0 | 0 | 0 | 0 | 8886.52
2022042806 | 5 | 0.45464 | 36371.2 | 0.55257 | 19892.52 | 0 | 0 | 1 | 5000 | 19892.52 | 0 | 0 | 0 | 0 | 0 | 11478.68 | 0 | 0 | 0 | 0 | 0 | 11478.68
2022042807 | 5 | 0.48637 | 38909.6 | 0.53144 | 19131.84 | 0.0003 | 3.6 | 1 | 5000 | 19131.84 | 3.6 | 0 | 0 | 0 | 0 | 14774.16 | 0 | 0 | 0 | 0 | 0 | 14774.16
2022042808 | 5 | 0.50275 | 40220 | 0.49634 | 17868.24 | 0.05921 | 710.52 | 1 | 5000 | 17868.24 | 710.52 | 0 | 0 | 0 | 0 | 16641.24 | 0 | 0 | 0 | 0 | 0 | 16641.24
2022042809 | 5 | 0.52121 | 41696.8 | 0.48376 | 17415.36 | 0.3564 | 4276.8 | 1 | 5000 | 17415.36 | 4276.8 | 0 | 0 | 0 | 0 | 15004.64 | 0 | 0 | 0 | 0 | 0 | 15004.64
2022042810 | 5 | 0.54197 | 43357.6 | 0.52875 | 19035 | 0.46878 | 5625.36 | 1 | 5000 | 19035 | 5625.36 | 0 | 0 | 0 | 0 | 13697.24 | 0 | 0 | 0 | 0 | 0 | 13697.24
2022042811 | 5 | 0.5611 | 44888 | 0.54464 | 19607.04 | 0.55176 | 6621.12 | 1 | 5000 | 19607.04 | 6621.12 | 0 | 0 | 0 | 0 | 13659.84 | 0 | 0 | 0 | 0 | 0 | 13659.84
2022042812 | 5 | 0.58097 | 46477.6 | 0.52949 | 19061.64 | 0.6554 | 7864.8 | 1 | 5000 | 19061.64 | 7864.8 | 0 | 0 | 0 | 0 | 14551.16 | 0 | 0 | 0 | 0 | 0 | 14551.16
2022042813 | 5 | 0.6027 | 48216 | 0.52752 | 18990.72 | 0.69105 | 8292.6 | 1 | 5000 | 18990.72 | 8292.6 | 0 | 0 | 0 | 0 | 15932.68 | 0 | 0 | 0 | 0 | 0 | 15932.68
2022042814 | 5 | 0.62551 | 50040.8 | 0.53443 | 19239.48 | 0.72374 | 8684.88 | 1 | 5000 | 19239.48 | 8684.88 | 0 | 0 | 0 | 0 | 17116.44 | 0 | 0 | 0 | 0 | 0 | 17116.44
2022042815 | 5 | 0.6431 | 51448 | 0.56475 | 20331 | 0.65571 | 7868.52 | 1 | 5000 | 20331 | 7868.52 | 0 | 0 | 0 | 0 | 18248.48 | 0 | 0 | 0 | 0 | 0 | 18248.48
2022042816 | 5 | 0.65876 | 52700.8 | 0.59765 | 21515.4 | 0.56566 | 6787.92 | 1 | 5000 | 21515.4 | 6787.92 | 0 | 0 | 0 | 0 | 19397.48 | 0 | 0 | 0 | 0 | 0 | 19397.48
2022042817 | 5 | 0.67233 | 53786.4 | 0.61185 | 22026.6 | 0.51132 | 6135.84 | 1 | 5000 | 22026.6 | 6135.84 | 0 | 0 | 0 | 0 | 20623.96 | 0 | 0 | 0 | 0 | 0 | 20623.96
2022042818 | 5 | 0.67895 | 54316 | 0.63686 | 22926.96 | 0.43878 | 5265.36 | 1 | 5000 | 22926.96 | 5265.36 | 0 | 0 | 0 | 0 | 21123.68 | 0 | 0 | 0 | 0 | 0 | 21123.68
2022042819 | 5 | 0.66714 | 53371.2 | 0.63114 | 22721.04 | 0.39519 | 4742.28 | 1 | 5000 | 22721.04 | 4742.28 | 0 | 0 | 0 | 0 | 20907.88 | 0 | 0 | 0 | 0 | 0 | 20907.88
2022042820 | 5 | 0.65345 | 52276 | 0.6495 | 23382 | 0.19871 | 2384.52 | 1 | 5000 | 23382 | 2384.52 | 0 | 0 | 0 | 0 | 21509.48 | 0 | 0 | 0 | 0 | 0 | 21509.48
2022042821 | 5 | 0.64337 | 51469.6 | 0.65836 | 23700.96 | 0.01516 | 181.92 | 1 | 5000 | 23700.96 | 181.92 | 0 | 0 | 0 | 0 | 22586.72 | 0 | 0 | 0 | 0 | 0 | 22586.72
2022042822 | 5 | 0.62584 | 50067.2 | 0.67184 | 24186.24 | 0.00893 | 107.16 | 1 | 5000 | 24186.24 | 107.16 | 0 | 0 | 0 | 0 | 20773.8 | 0 | 0 | 0 | 0 | 0 | 20773.8
2022042823 | 5 | 0.58872 | 47097.6 | 0.68574 | 24686.64 | 0.00893 | 107.16 | 1 | 5000 | 24686.64 | 107.16 | 0 | 0 | 0 | 0 | 17303.8 | 0 | 0 | 0 | 0 | 0 | 17303.8
2022042824 | 5 | 0.54799 | 43839.2 | 0.68368 | 24612.48 | 0.00892 | 107.04 | 1 | 5000 | 24612.48 | 107.04 | 0 | 0 | 0 | 0 | 14119.68 | 0 | 0 | 0 | 0 | 0 | 14119.68
2022042901 | 6 | 0.51528 | 41222.4 | 0.67345 | 24244.2 | 0.00892 | 107.04 | 1 | 5000 | 24244.2 | 107.04 | 0 | 0 | 0 | 0 | 11871.16 | 0 | 0 | 0 | 0 | 0 | 11871.16
2022042902 | 6 | 0.49317 | 39453.6 | 0.67062 | 24142.32 | 0.00892 | 107.04 | 1 | 5000 | 24142.32 | 107.04 | 0 | 0 | 0 | 0 | 10204.24 | 0 | 0 | 0 | 0 | 0 | 10204.24
2022042903 | 6 | 0.47582 | 38065.6 | 0.65734 | 23664.24 | 0.00892 | 107.04 | 1 | 5000 | 23664.24 | 107.04 | 0 | 0 | 0 | 0 | 9294.32 | 0 | 0 | 0 | 0 | 0 | 9294.32
2022042904 | 6 | 0.47756 | 38204.8 | 0.65125 | 23445 | 0.00892 | 107.04 | 1 | 5000 | 23445 | 107.04 | 0 | 0 | 0 | 0 | 9652.76 | 0 | 0 | 0 | 0 | 0 | 9652.76
2022042905 | 6 | 0.47998 | 38398.4 | 0.65069 | 23424.84 | 0.00892 | 107.04 | 1 | 5000 | 23424.84 | 107.04 | 0 | 0 | 0 | 0 | 9866.52 | 0 | 0 | 0 | 0 | 0 | 9866.52
2022042906 | 6 | 0.49177 | 39341.6 | 0.64992 | 23397.12 | 0.00893 | 107.16 | 1 | 5000 | 23397.12 | 107.16 | 0 | 0 | 0 | 0 | 10837.32 | 0 | 0 | 0 | 0 | 0 | 10837.32
2022042907 | 6 | 0.51589 | 41271.2 | 0.64346 | 23164.56 | 0.00105 | 12.6 | 1 | 5000 | 23164.56 | 12.6 | 0 | 0 | 0 | 0 | 13094.04 | 0 | 0 | 0 | 0 | 0 | 13094.04
2022042908 | 6 | 0.53353 | 42682.4 | 0.61899 | 22283.64 | 0.05891 | 706.92 | 1 | 5000 | 22283.64 | 706.92 | 0 | 0 | 0 | 0 | 14691.84 | 0 | 0 | 0 | 0 | 0 | 14691.84
2022042909 | 6 | 0.55007 | 44005.6 | 0.5871 | 21135.6 | 0.28295 | 3395.4 | 1 | 5000 | 21135.6 | 3395.4 | 0 | 0 | 0 | 0 | 14474.6 | 0 | 0 | 0 | 0 | 0 | 14474.6
2022042910 | 6 | 0.5673 | 45384 | 0.60209 | 21675.24 | 0.30892 | 3707.04 | 1 | 5000 | 21675.24 | 3707.04 | 0 | 0 | 0 | 0 | 15001.72 | 0 | 0 | 0 | 0 | 0 | 15001.72
2022042911 | 6 | 0.59061 | 47248.8 | 0.59435 | 21396.6 | 0.38593 | 4631.16 | 1 | 5000 | 21396.6 | 4631.16 | 0 | 0 | 0 | 0 | 16221.04 | 0 | 0 | 0 | 0 | 0 | 16221.04
2022042912 | 6 | 0.6101 | 48808 | 0.57862 | 20830.32 | 0.47821 | 5738.52 | 1 | 5000 | 20830.32 | 5738.52 | 0 | 0 | 0 | 0 | 17239.16 | 0 | 0 | 0 | 0 | 0 | 17239.16
2022042913 | 6 | 0.62931 | 50344.8 | 0.56163 | 20218.68 | 0.60476 | 7257.12 | 1 | 5000 | 20218.68 | 7257.12 | 0 | 0 | 0 | 0 | 17869 | 0 | 0 | 0 | 0 | 0 | 17869
2022042914 | 6 | 0.65077 | 52061.6 | 0.54849 | 19745.64 | 0.64781 | 7773.72 | 1 | 5000 | 19745.64 | 7773.72 | 0 | 0 | 0 | 0 | 19542.24 | 0 | 0 | 0 | 0 | 0 | 19542.24
2022042915 | 6 | 0.67095 | 53676 | 0.5618 | 20224.8 | 0.64213 | 7705.56 | 1 | 5000 | 20224.8 | 7705.56 | 0 | 0 | 0 | 0 | 20745.64 | 0 | 0 | 0 | 0 | 0 | 20745.64
2022042916 | 6 | 0.68324 | 54659.2 | 0.57557 | 20720.52 | 0.61312 | 7357.44 | 1 | 5000 | 20720.52 | 7357.44 | 0 | 0 | 0 | 0 | 21581.24 | 0 | 0 | 0 | 0 | 0 | 21581.24
2022042917 | 6 | 0.69416 | 55532.8 | 0.59088 | 21271.68 | 0.56943 | 6833.16 | 1 | 5000 | 21271.68 | 6833.16 | 0 | 0 | 0 | 0 | 22427.96 | 0 | 0 | 0 | 0 | 0 | 22427.96
2022042918 | 6 | 0.69282 | 55425.6 | 0.59515 | 21425.4 | 0.5249 | 6298.8 | 1 | 5000 | 21425.4 | 6298.8 | 0 | 0 | 0 | 0 | 22701.4 | 0 | 0 | 0 | 0 | 0 | 22701.4
2022042919 | 6 | 0.67857 | 54285.6 | 0.59182 | 21305.52 | 0.43474 | 5216.88 | 1 | 5000 | 21305.52 | 5216.88 | 0 | 0 | 0 | 0 | 22763.2 | 0 | 0 | 0 | 0 | 0 | 22763.2
2022042920 | 6 | 0.65602 | 52481.6 | 0.57369 | 20652.84 | 0.21823 | 2618.76 | 1 | 5000 | 20652.84 | 2618.76 | 0 | 0 | 0 | 0 | 24210 | 0 | 0 | 0 | 0 | 0 | 24210
2022042921 | 6 | 0.64392 | 51513.6 | 0.54108 | 19478.88 | 0.00766 | 91.92 | 1 | 5000 | 19478.88 | 91.92 | 0 | 0 | 0 | 0 | 26942.8 | 0 | 0 | 0 | 0 | 0 | 26942.8
2022042922 | 6 | 0.62815 | 50252 | 0.57257 | 20612.52 | 0 | 0 | 1 | 5000 | 20612.52 | 0 | 0 | 0 | 0 | 0 | 24639.48 | 0 | 0 | 0 | 0 | 0 | 24639.48
2022042923 | 6 | 0.60139 | 48111.2 | 0.60045 | 21616.2 | 0 | 0 | 1 | 5000 | 21616.2 | 0 | 0 | 0 | 0 | 0 | 21495 | 0 | 0 | 0 | 0 | 0 | 21495
2022042924 | 6 | 0.56756 | 45404.8 | 0.63112 | 22720.32 | 0 | 0 | 1 | 5000 | 22720.32 | 0 | 0 | 0 | 0 | 0 | 17684.48 | 0 | 0 | 0 | 0 | 0 | 17684.48
2022043001 | 7 | 0.53559 | 42847.2 | 0.63857 | 22988.52 | 0 | 0 | 1 | 5000 | 22988.52 | 0 | 0 | 0 | 0 | 0 | 14858.68 | 0 | 0 | 0 | 0 | 0 | 14858.68
2022043002 | 7 | 0.51151 | 40920.8 | 0.61959 | 22305.24 | 0 | 0 | 1 | 5000 | 22305.24 | 0 | 0 | 0 | 0 | 0 | 13615.56 | 0 | 0 | 0 | 0 | 0 | 13615.56
2022043003 | 7 | 0.49315 | 39452 | 0.58156 | 20936.16 | 0 | 0 | 1 | 5000 | 20936.16 | 0 | 0 | 0 | 0 | 0 | 13515.84 | 0 | 0 | 0 | 0 | 0 | 13515.84
2022043004 | 7 | 0.481 | 38480 | 0.55212 | 19876.32 | 0 | 0 | 1 | 5000 | 19876.32 | 0 | 0 | 0 | 0 | 0 | 13603.68 | 0 | 0 | 0 | 0 | 0 | 13603.68
2022043005 | 7 | 0.4759 | 38072 | 0.50896 | 18322.56 | 0 | 0 | 1 | 5000 | 18322.56 | 0 | 0 | 0 | 0 | 0 | 14749.44 | 0 | 0 | 0 | 0 | 0 | 14749.44
2022043006 | 7 | 0.47677 | 38141.6 | 0.48199 | 17351.64 | 0 | 0 | 1 | 5000 | 17351.64 | 0 | 0 | 0 | 0 | 0 | 15789.96 | 0 | 0 | 0 | 0 | 0 | 15789.96
2022043007 | 7 | 0.48171 | 38536.8 | 0.41704 | 15013.44 | 8e-05 | 0.96 | 1 | 5000 | 15013.44 | 0.96 | 0 | 0 | 0 | 0 | 18522.4 | 0 | 0 | 0 | 0 | 0 | 18522.4
2022043008 | 7 | 0.49375 | 39500 | 0.4169 | 15008.4 | 0.06765 | 811.8 | 1 | 5000 | 15008.4 | 811.8 | 0 | 0 | 0 | 0 | 18679.8 | 0 | 0 | 0 | 0 | 0 | 18679.8
2022043009 | 7 | 0.52301 | 41840.8 | 0.41727 | 15021.72 | 0.40079 | 4809.48 | 1 | 5000 | 15021.72 | 4809.48 | 0 | 0 | 0 | 0 | 17009.6 | 0 | 0 | 0 | 0 | 0 | 17009.6
2022043010 | 7 | 0.55364 | 44291.2 | 0.49843 | 17943.48 | 0.39525 | 4743 | 1 | 5000 | 17943.48 | 4743 | 0 | 0 | 0 | 0 | 16604.72 | 0 | 0 | 0 | 0 | 0 | 16604.72
2022043011 | 7 | 0.57825 | 46260 | 0.52629 | 18946.44 | 0.33218 | 3986.16 | 1 | 5000 | 18946.44 | 3986.16 | 0 | 0 | 0 | 0 | 18327.4 | 0 | 0 | 0 | 0 | 0 | 18327.4
2022043012 | 7 | 0.59776 | 47820.8 | 0.4822 | 17359.2 | 0.46645 | 5597.4 | 1 | 5000 | 17359.2 | 5597.4 | 0 | 0 | 0 | 0 | 19864.2 | 0 | 0 | 0 | 0 | 0 | 19864.2
2022043013 | 7 | 0.61703 | 49362.4 | 0.39472 | 14209.92 | 0.66241 | 7948.92 | 1 | 5000 | 14209.92 | 7948.92 | 0 | 0 | 0 | 0 | 22203.56 | 0 | 0 | 0 | 0 | 0 | 22203.56
2022043014 | 7 | 0.64105 | 51284 | 0.29117 | 10482.12 | 0.77789 | 9334.68 | 1 | 5000 | 10482.12 | 9334.68 | 0 | 0 | 0 | 0 | 26467.2 | 0 | 0 | 0 | 0 | 0 | 26467.2
2022043015 | 7 | 0.66435 | 53148 | 0.19766 | 7115.76 | 0.79807 | 9576.84 | 1 | 5000 | 7115.76 | 9576.84 | 0 | 0 | 0 | 0 | 31455.4 | 0 | 0 | 0 | 0 | 0 | 31455.4
2022043016 | 7 | 0.68241 | 54592.8 | 0.16317 | 5874.12 | 0.81057 | 9726.84 | 1 | 5000 | 5874.12 | 9726.84 | 0 | 0 | 0 | 0 | 33991.84 | 0 | 0 | 0 | 0 | 0 | 33991.84
2022043017 | 7 | 0.69468 | 55574.4 | 0.15226 | 5481.36 | 0.81844 | 9821.28 | 1 | 5000 | 5481.36 | 9821.28 | 0 | 0 | 0 | 0 | 35271.76 | 0 | 0 | 0 | 0 | 0 | 35271.76
2022043018 | 7 | 0.69415 | 55532 | 0.14978 | 5392.08 | 0.77604 | 9312.48 | 1 | 5000 | 5392.08 | 9312.48 | 0 | 0 | 0 | 0 | 35827.44 | 0 | 0 | 0 | 0 | 0 | 35827.44
2022043019 | 7 | 0.67789 | 54231.2 | 0.16649 | 5993.64 | 0.6353 | 7623.6 | 1 | 5000 | 5993.64 | 7623.6 | 0 | 0 | 0 | 0 | 35613.96 | 0 | 0 | 0 | 0 | 0 | 35613.96
2022043020 | 7 | 0.64981 | 51984.8 | 0.17503 | 6301.08 | 0.24075 | 2889 | 1 | 5000 | 6301.08 | 2889 | 0 | 0 | 0 | 0 | 37794.72 | 0 | 0 | 0 | 0 | 0 | 37794.72
2022043021 | 7 | 0.63158 | 50526.4 | 0.19868 | 7152.48 | 0.00711 | 85.32 | 1 | 5000 | 7152.48 | 85.32 | 0 | 0 | 0 | 0 | 38288.6 | 0 | 0 | 0 | 0 | 0 | 38288.6
2022043022 | 7 | 0.60688 | 48550.4 | 0.24687 | 8887.32 | 0 | 0 | 1 | 5000 | 8887.32 | 0 | 0 | 0 | 0 | 0 | 34663.08 | 0 | 0 | 0 | 0 | 0 | 34663.08
2022043023 | 7 | 0.57446 | 45956.8 | 0.28975 | 10431 | 0 | 0 | 1 | 5000 | 10431 | 0 | 0 | 0 | 0 | 0 | 30525.8 | 0 | 0 | 0 | 0 | 0 | 30525.8
2022043024 | 7 | 0.54014 | 43211.2 | 0.31619 | 11382.84 | 0 | 0 | 1 | 5000 | 11382.84 | 0 | 0 | 0 | 0 | 0 | 26828.36 | 0 | 0 | 0 | 0 | 0 | 26828.36
2022050101 | 1 | 0.50863 | 40690.4 | 0.33912 | 12208.32 | 0 | 0 | 1 | 5000 | 12208.32 | 0 | 0 | 0 | 0 | 0 | 23482.08 | 0 | 0 | 0 | 0 | 0 | 23482.08
2022050102 | 1 | 0.48263 | 38610.4 | 0.36171 | 13021.56 | 0 | 0 | 1 | 5000 | 13021.56 | 0 | 0 | 0 | 0 | 0 | 20588.84 | 0 | 0 | 0 | 0 | 0 | 20588.84
2022050103 | 1 | 0.46571 | 37256.8 | 0.36032 | 12971.52 | 0 | 0 | 1 | 5000 | 12971.52 | 0 | 0 | 0 | 0 | 0 | 19285.28 | 0 | 0 | 0 | 0 | 0 | 19285.28
2022050104 | 1 | 0.45385 | 36308 | 0.36168 | 13020.48 | 0 | 0 | 1 | 5000 | 13020.48 | 0 | 0 | 0 | 0 | 0 | 18287.52 | 0 | 0 | 0 | 0 | 0 | 18287.52
2022050105 | 1 | 0.44576 | 35660.8 | 0.38296 | 13786.56 | 0 | 0 | 1 | 5000 | 13786.56 | 0 | 0 | 0 | 0 | 0 | 16874.24 | 0 | 0 | 0 | 0 | 0 | 16874.24
2022050106 | 1 | 0.44683 | 35746.4 | 0.41293 | 14865.48 | 0 | 0 | 1 | 5000 | 14865.48 | 0 | 0 | 0 | 0 | 0 | 15880.92 | 0 | 0 | 0 | 0 | 0 | 15880.92
2022050107 | 1 | 0.44839 | 35871.2 | 0.43859 | 15789.24 | 0.00052 | 6.24 | 1 | 5000 | 15789.24 | 6.24 | 0 | 0 | 0 | 0 | 15075.72 | 0 | 0 | 0 | 0 | 0 | 15075.72
2022050108 | 1 | 0.45644 | 36515.2 | 0.45012 | 16204.32 | 0.05215 | 625.8 | 1 | 5000 | 16204.32 | 625.8 | 0 | 0 | 0 | 0 | 14685.08 | 0 | 0 | 0 | 0 | 0 | 14685.08
2022050109 | 1 | 0.48353 | 38682.4 | 0.45195 | 16270.2 | 0.23439 | 2812.68 | 1 | 5000 | 16270.2 | 2812.68 | 0 | 0 | 0 | 0 | 14599.52 | 0 | 0 | 0 | 0 | 0 | 14599.52
2022050110 | 1 | 0.51859 | 41487.2 | 0.51105 | 18397.8 | 0.35857 | 4302.84 | 1 | 5000 | 18397.8 | 4302.84 | 0 | 0 | 0 | 0 | 13786.56 | 0 | 0 | 0 | 0 | 0 | 13786.56
2022050111 | 1 | 0.5525 | 44200 | 0.56426 | 20313.36 | 0.41311 | 4957.32 | 1 | 5000 | 20313.36 | 4957.32 | 0 | 0 | 0 | 0 | 13929.32 | 0 | 0 | 0 | 0 | 0 | 13929.32
2022050112 | 1 | 0.58462 | 46769.6 | 0.58141 | 20930.76 | 0.42839 | 5140.68 | 1 | 5000 | 20930.76 | 5140.68 | 0 | 0 | 0 | 0 | 15698.16 | 0 | 0 | 0 | 0 | 0 | 15698.16
2022050113 | 1 | 0.61311 | 49048.8 | 0.58985 | 21234.6 | 0.4589 | 5506.8 | 1 | 5000 | 21234.6 | 5506.8 | 0 | 0 | 0 | 0 | 17307.4 | 0 | 0 | 0 | 0 | 0 | 17307.4
2022050114 | 1 | 0.63949 | 51159.2 | 0.59592 | 21453.12 | 0.494 | 5928 | 1 | 5000 | 21453.12 | 5928 | 0 | 0 | 0 | 0 | 18778.08 | 0 | 0 | 0 | 0 | 0 | 18778.08
2022050115 | 1 | 0.66247 | 52997.6 | 0.59498 | 21419.28 | 0.50894 | 6107.28 | 1 | 5000 | 21419.28 | 6107.28 | 0 | 0 | 0 | 0 | 20471.04 | 0 | 0 | 0 | 0 | 0 | 20471.04
2022050116 | 1 | 0.68396 | 54716.8 | 0.60573 | 21806.28 | 0.45875 | 5505 | 1 | 5000 | 21806.28 | 5505 | 0 | 0 | 0 | 0 | 22405.52 | 0 | 0 | 0 | 0 | 0 | 22405.52
2022050117 | 1 | 0.69748 | 55798.4 | 0.62229 | 22402.44 | 0.40394 | 4847.28 | 1 | 5000 | 22402.44 | 4847.28 | 0 | 0 | 0 | 0 | 23548.68 | 0 | 0 | 0 | 0 | 0 | 23548.68
2022050118 | 1 | 0.70219 | 56175.2 | 0.636 | 22896 | 0.27683 | 3321.96 | 1 | 5000 | 22896 | 3321.96 | 0 | 0 | 0 | 0 | 24957.24 | 0 | 0 | 0 | 0 | 0 | 24957.24
2022050119 | 1 | 0.69364 | 55491.2 | 0.63415 | 22829.4 | 0.20501 | 2460.12 | 1 | 5000 | 22829.4 | 2460.12 | 0 | 0 | 0 | 0 | 25201.68 | 0 | 0 | 0 | 0 | 0 | 25201.68
2022050120 | 1 | 0.67278 | 53822.4 | 0.62218 | 22398.48 | 0.08256 | 990.72 | 1 | 5000 | 22398.48 | 990.72 | 0 | 0 | 0 | 0 | 25433.2 | 0 | 0 | 0 | 0 | 0 | 25433.2
2022050121 | 1 | 0.66543 | 53234.4 | 0.58456 | 21044.16 | 0.00448 | 53.76 | 1 | 5000 | 21044.16 | 53.76 | 0 | 0 | 0 | 0 | 27136.48 | 0 | 0 | 0 | 0 | 0 | 27136.48
2022050122 | 1 | 0.64592 | 51673.6 | 0.56333 | 20279.88 | 0 | 0 | 1 | 5000 | 20279.88 | 0 | 0 | 0 | 0 | 0 | 26393.72 | 0 | 0 | 0 | 0 | 0 | 26393.72
2022050123 | 1 | 0.61191 | 48952.8 | 0.60337 | 21721.32 | 0 | 0 | 1 | 5000 | 21721.32 | 0 | 0 | 0 | 0 | 0 | 22231.48 | 0 | 0 | 0 | 0 | 0 | 22231.48
2022050124 | 1 | 0.57173 | 45738.4 | 0.63396 | 22822.56 | 0 | 0 | 1 | 5000 | 22822.56 | 0 | 0 | 0 | 0 | 0 | 17915.84 | 0 | 0 | 0 | 0 | 0 | 17915.84
2022050201 | 2 | 0.53584 | 42867.2 | 0.62607 | 22538.52 | 0 | 0 | 1 | 5000 | 22538.52 | 0 | 0 | 0 | 0 | 0 | 15328.68 | 0 | 0 | 0 | 0 | 0 | 15328.68
2022050202 | 2 | 0.51276 | 41020.8 | 0.60738 | 21865.68 | 0 | 0 | 1 | 5000 | 21865.68 | 0 | 0 | 0 | 0 | 0 | 14155.12 | 0 | 0 | 0 | 0 | 0 | 14155.12
2022050203 | 2 | 0.49793 | 39834.4 | 0.61336 | 22080.96 | 0 | 0 | 1 | 5000 | 22080.96 | 0 | 0 | 0 | 0 | 0 | 12753.44 | 0 | 0 | 0 | 0 | 0 | 12753.44
2022050204 | 2 | 0.48752 | 39001.6 | 0.61619 | 22182.84 | 0 | 0 | 1 | 5000 | 22182.84 | 0 | 0 | 0 | 0 | 0 | 11818.76 | 0 | 0 | 0 | 0 | 0 | 11818.76
2022050205 | 2 | 0.49019 | 39215.2 | 0.60091 | 21632.76 | 0 | 0 | 1 | 5000 | 21632.76 | 0 | 0 | 0 | 0 | 0 | 12582.44 | 0 | 0 | 0 | 0 | 0 | 12582.44
2022050206 | 2 | 0.50521 | 40416.8 | 0.62839 | 22622.04 | 0 | 0 | 1 | 5000 | 22622.04 | 0 | 0 | 0 | 0 | 0 | 12794.76 | 0 | 0 | 0 | 0 | 0 | 12794.76
2022050207 | 2 | 0.53843 | 43074.4 | 0.65676 | 23643.36 | 0 | 0 | 1 | 5000 | 23643.36 | 0 | 0 | 0 | 0 | 0 | 14431.04 | 0 | 0 | 0 | 0 | 0 | 14431.04
2022050208 | 2 | 0.55632 | 44505.6 | 0.66559 | 23961.24 | 0.04372 | 524.64 | 1 | 5000 | 23961.24 | 524.64 | 0 | 0 | 0 | 0 | 15019.72 | 0 | 0 | 0 | 0 | 0 | 15019.72
2022050209 | 2 | 0.57218 | 45774.4 | 0.62982 | 22673.52 | 0.25709 | 3085.08 | 1 | 5000 | 22673.52 | 3085.08 | 0 | 0 | 0 | 0 | 15015.8 | 0 | 0 | 0 | 0 | 0 | 15015.8
2022050210 | 2 | 0.59524 | 47619.2 | 0.63355 | 22807.8 | 0.34114 | 4093.68 | 1 | 5000 | 22807.8 | 4093.68 | 0 | 0 | 0 | 0 | 15717.72 | 0 | 0 | 0 | 0 | 0 | 15717.72
2022050211 | 2 | 0.62604 | 50083.2 | 0.63454 | 22843.44 | 0.37791 | 4534.92 | 1 | 5000 | 22843.44 | 4534.92 | 0 | 0 | 0 | 0 | 17704.84 | 0 | 0 | 0 | 0 | 0 | 17704.84
2022050212 | 2 | 0.653 | 52240 | 0.63313 | 22792.68 | 0.39572 | 4748.64 | 1 | 5000 | 22792.68 | 4748.64 | 0 | 0 | 0 | 0 | 19698.68 | 0 | 0 | 0 | 0 | 0 | 19698.68
2022050213 | 2 | 0.67969 | 54375.2 | 0.61688 | 22207.68 | 0.45751 | 5490.12 | 1 | 5000 | 22207.68 | 5490.12 | 0 | 0 | 0 | 0 | 21677.4 | 0 | 0 | 0 | 0 | 0 | 21677.4
2022050214 | 2 | 0.70216 | 56172.8 | 0.57865 | 20831.4 | 0.62923 | 7550.76 | 1 | 5000 | 20831.4 | 7550.76 | 0 | 0 | 0 | 0 | 22790.64 | 0 | 0 | 0 | 0 | 0 | 22790.64
2022050215 | 2 | 0.71305 | 57044 | 0.54844 | 19743.84 | 0.66734 | 8008.08 | 1 | 5000 | 19743.84 | 8008.08 | 0 | 0 | 0 | 0 | 24292.08 | 0 | 0 | 0 | 0 | 0 | 24292.08
2022050216 | 2 | 0.71924 | 57539.2 | 0.53451 | 19242.36 | 0.68964 | 8275.68 | 1 | 5000 | 19242.36 | 8275.68 | 0 | 0 | 0 | 0 | 25021.16 | 0 | 0 | 0 | 0 | 0 | 25021.16
2022050217 | 2 | 0.72743 | 58194.4 | 0.53648 | 19313.28 | 0.68221 | 8186.52 | 1 | 5000 | 19313.28 | 8186.52 | 0 | 0 | 0 | 0 | 25694.6 | 0 | 0 | 0 | 0 | 0 | 25694.6
2022050218 | 2 | 0.73209 | 58567.2 | 0.5317 | 19141.2 | 0.67582 | 8109.84 | 1 | 5000 | 19141.2 | 8109.84 | 0 | 0 | 0 | 0 | 26316.16 | 0 | 0 | 0 | 0 | 0 | 26316.16
2022050219 | 2 | 0.72245 | 57796 | 0.53682 | 19325.52 | 0.5797 | 6956.4 | 1 | 5000 | 19325.52 | 6956.4 | 0 | 0 | 0 | 0 | 26514.08 | 0 | 0 | 0 | 0 | 0 | 26514.08
2022050220 | 2 | 0.69886 | 55908.8 | 0.50965 | 18347.4 | 0.23934 | 2872.08 | 1 | 5000 | 18347.4 | 2872.08 | 0 | 0 | 0 | 0 | 29689.32 | 0 | 0 | 0 | 0 | 0 | 29689.32
2022050221 | 2 | 0.68284 | 54627.2 | 0.47634 | 17148.24 | 0.00888 | 106.56 | 1 | 5000 | 17148.24 | 106.56 | 0 | 0 | 0 | 0 | 32372.4 | 0 | 0 | 0 | 0 | 0 | 32372.4
2022050222 | 2 | 0.6687 | 53496 | 0.49396 | 17782.56 | 0 | 0 | 1 | 5000 | 17782.56 | 0 | 0 | 0 | 0 | 0 | 30713.44 | 0 | 0 | 0 | 0 | 0 | 30713.44
2022050223 | 2 | 0.63067 | 50453.6 | 0.55812 | 20092.32 | 0 | 0 | 1 | 5000 | 20092.32 | 0 | 0 | 0 | 0 | 0 | 25361.28 | 0 | 0 | 0 | 0 | 0 | 25361.28
2022050224 | 2 | 0.59053 | 47242.4 | 0.62222 | 22399.92 | 0 | 0 | 1 | 5000 | 22399.92 | 0 | 0 | 0 | 0 | 0 | 19842.48 | 0 | 0 | 0 | 0 | 0 | 19842.48
2022050301 | 3 | 0.55818 | 44654.4 | 0.6331 | 22791.6 | 0 | 0 | 1 | 5000 | 22791.6 | 0 | 0 | 0 | 0 | 0 | 16862.8 | 0 | 0 | 0 | 0 | 0 | 16862.8
2022050302 | 3 | 0.53052 | 42441.6 | 0.62304 | 22429.44 | 0 | 0 | 1 | 5000 | 22429.44 | 0 | 0 | 0 | 0 | 0 | 15012.16 | 0 | 0 | 0 | 0 | 0 | 15012.16
2022050303 | 3 | 0.50887 | 40709.6 | 0.60882 | 21917.52 | 0 | 0 | 1 | 5000 | 21917.52 | 0 | 0 | 0 | 0 | 0 | 13792.08 | 0 | 0 | 0 | 0 | 0 | 13792.08
2022050304 | 3 | 0.49745 | 39796 | 0.5743 | 20674.8 | 0 | 0 | 1 | 5000 | 20674.8 | 0 | 0 | 0 | 0 | 0 | 14121.2 | 0 | 0 | 0 | 0 | 0 | 14121.2
2022050305 | 3 | 0.4975 | 39800 | 0.51349 | 18485.64 | 0 | 0 | 1 | 5000 | 18485.64 | 0 | 0 | 0 | 0 | 0 | 16314.36 | 0 | 0 | 0 | 0 | 0 | 16314.36
2022050306 | 3 | 0.51069 | 40855.2 | 0.47625 | 17145 | 0 | 0 | 1 | 5000 | 17145 | 0 | 0 | 0 | 0 | 0 | 18710.2 | 0 | 0 | 0 | 0 | 0 | 18710.2
2022050307 | 3 | 0.53921 | 43136.8 | 0.45268 | 16296.48 | 8e-05 | 0.96 | 1 | 5000 | 16296.48 | 0.96 | 0 | 0 | 0 | 0 | 21839.36 | 0 | 0 | 0 | 0 | 0 | 21839.36
2022050308 | 3 | 0.54943 | 43954.4 | 0.43031 | 15491.16 | 0.04889 | 586.68 | 1 | 5000 | 15491.16 | 586.68 | 0 | 0 | 0 | 0 | 22876.56 | 0 | 0 | 0 | 0 | 0 | 22876.56
2022050309 | 3 | 0.55966 | 44772.8 | 0.41438 | 14917.68 | 0.27774 | 3332.88 | 1 | 5000 | 14917.68 | 3332.88 | 0 | 0 | 0 | 0 | 21522.24 | 0 | 0 | 0 | 0 | 0 | 21522.24
2022050310 | 3 | 0.57177 | 45741.6 | 0.34732 | 12503.52 | 0.39924 | 4790.88 | 1 | 5000 | 12503.52 | 4790.88 | 0 | 0 | 0 | 0 | 23447.2 | 0 | 0 | 0 | 0 | 0 | 23447.2
2022050311 | 3 | 0.58435 | 46748 | 0.25855 | 9307.8 | 0.44975 | 5397 | 1 | 5000 | 9307.8 | 5397 | 0 | 0 | 0 | 0 | 27043.2 | 0 | 0 | 0 | 0 | 0 | 27043.2
2022050312 | 3 | 0.59983 | 47986.4 | 0.19987 | 7195.32 | 0.56149 | 6737.88 | 1 | 5000 | 7195.32 | 6737.88 | 0 | 0 | 0 | 0 | 29053.2 | 0 | 0 | 0 | 0 | 0 | 29053.2
2022050313 | 3 | 0.61514 | 49211.2 | 0.16078 | 5788.08 | 0.62879 | 7545.48 | 1 | 5000 | 5788.08 | 7545.48 | 0 | 0 | 0 | 0 | 30877.64 | 0 | 0 | 0 | 0 | 0 | 30877.64
2022050314 | 3 | 0.63099 | 50479.2 | 0.14446 | 5200.56 | 0.66901 | 8028.12 | 1 | 5000 | 5200.56 | 8028.12 | 0 | 0 | 0 | 0 | 32250.52 | 0 | 0 | 0 | 0 | 0 | 32250.52
2022050315 | 3 | 0.64512 | 51609.6 | 0.14452 | 5202.72 | 0.66909 | 8029.08 | 1 | 5000 | 5202.72 | 8029.08 | 0 | 0 | 0 | 0 | 33377.8 | 0 | 0 | 0 | 0 | 0 | 33377.8
2022050316 | 3 | 0.65967 | 52773.6 | 0.15044 | 5415.84 | 0.62661 | 7519.32 | 1 | 5000 | 5415.84 | 7519.32 | 0 | 0 | 0 | 0 | 34838.44 | 0 | 0 | 0 | 0 | 0 | 34838.44
2022050317 | 3 | 0.67415 | 53932 | 0.18519 | 6666.84 | 0.54882 | 6585.84 | 1 | 5000 | 6666.84 | 6585.84 | 0 | 0 | 0 | 0 | 35679.32 | 0 | 0 | 0 | 0 | 0 | 35679.32
2022050318 | 3 | 0.67678 | 54142.4 | 0.23239 | 8366.04 | 0.38972 | 4676.64 | 1 | 5000 | 8366.04 | 4676.64 | 0 | 0 | 0 | 0 | 36099.72 | 0 | 0 | 0 | 0 | 0 | 36099.72
2022050319 | 3 | 0.66436 | 53148.8 | 0.26658 | 9596.88 | 0.21437 | 2572.44 | 1 | 5000 | 9596.88 | 2572.44 | 0 | 0 | 0 | 0 | 35979.48 | 0 | 0 | 0 | 0 | 0 | 35979.48
2022050320 | 3 | 0.64747 | 51797.6 | 0.29656 | 10676.16 | 0.06538 | 784.56 | 1 | 5000 | 10676.16 | 784.56 | 0 | 0 | 0 | 0 | 35336.88 | 0 | 0 | 0 | 0 | 0 | 35336.88
2022050321 | 3 | 0.64221 | 51376.8 | 0.32015 | 11525.4 | 0.00368 | 44.16 | 1 | 5000 | 11525.4 | 44.16 | 0 | 0 | 0 | 0 | 34807.24 | 0 | 0 | 0 | 0 | 0 | 34807.24
2022050322 | 3 | 0.62139 | 49711.2 | 0.33902 | 12204.72 | 0.00241 | 28.92 | 1 | 5000 | 12204.72 | 28.92 | 0 | 0 | 0 | 0 | 32477.56 | 0 | 0 | 0 | 0 | 0 | 32477.56
2022050323 | 3 | 0.58665 | 46932 | 0.36487 | 13135.32 | 0.00241 | 28.92 | 1 | 5000 | 13135.32 | 28.92 | 0 | 0 | 0 | 0 | 28767.76 | 0 | 0 | 0 | 0 | 0 | 28767.76
2022050324 | 3 | 0.5457 | 43656 | 0.37302 | 13428.72 | 0.0002 | 2.4 | 1 | 5000 | 13428.72 | 2.4 | 0 | 0 | 0 | 0 | 25224.88 | 0 | 0 | 0 | 0 | 0 | 25224.88
2022050401 | 4 | 0.51324 | 41059.2 | 0.37707 | 13574.52 | 0 | 0 | 1 | 5000 | 13574.52 | 0 | 0 | 0 | 0 | 0 | 22484.68 | 0 | 0 | 0 | 0 | 0 | 22484.68
2022050402 | 4 | 0.49309 | 39447.2 | 0.39989 | 14396.04 | 0 | 0 | 1 | 5000 | 14396.04 | 0 | 0 | 0 | 0 | 0 | 20051.16 | 0 | 0 | 0 | 0 | 0 | 20051.16
2022050403 | 4 | 0.48072 | 38457.6 | 0.40668 | 14640.48 | 0 | 0 | 1 | 5000 | 14640.48 | 0 | 0 | 0 | 0 | 0 | 18817.12 | 0 | 0 | 0 | 0 | 0 | 18817.12
2022050404 | 4 | 0.47501 | 38000.8 | 0.38766 | 13955.76 | 0 | 0 | 1 | 5000 | 13955.76 | 0 | 0 | 0 | 0 | 0 | 19045.04 | 0 | 0 | 0 | 0 | 0 | 19045.04
2022050405 | 4 | 0.47762 | 38209.6 | 0.37483 | 13493.88 | 0 | 0 | 1 | 5000 | 13493.88 | 0 | 0 | 0 | 0 | 0 | 19715.72 | 0 | 0 | 0 | 0 | 0 | 19715.72
2022050406 | 4 | 0.49692 | 39753.6 | 0.36449 | 13121.64 | 0 | 0 | 1 | 5000 | 13121.64 | 0 | 0 | 0 | 0 | 0 | 21631.96 | 0 | 0 | 0 | 0 | 0 | 21631.96
2022050407 | 4 | 0.5296 | 42368 | 0.35896 | 12922.56 | 0.0001 | 1.2 | 1 | 5000 | 12922.56 | 1.2 | 0 | 0 | 0 | 0 | 24444.24 | 0 | 0 | 0 | 0 | 0 | 24444.24
2022050408 | 4 | 0.54461 | 43568.8 | 0.34029 | 12250.44 | 0.02063 | 247.56 | 1 | 5000 | 12250.44 | 247.56 | 0 | 0 | 0 | 0 | 26070.8 | 0 | 0 | 0 | 0 | 0 | 26070.8
2022050409 | 4 | 0.55838 | 44670.4 | 0.35444 | 12759.84 | 0.13909 | 1669.08 | 1 | 5000 | 12759.84 | 1669.08 | 0 | 0 | 0 | 0 | 25241.48 | 0 | 0 | 0 | 0 | 0 | 25241.48
2022050410 | 4 | 0.57869 | 46295.2 | 0.37063 | 13342.68 | 0.31755 | 3810.6 | 1 | 5000 | 13342.68 | 3810.6 | 0 | 0 | 0 | 0 | 24141.92 | 0 | 0 | 0 | 0 | 0 | 24141.92
2022050411 | 4 | 0.60507 | 48405.6 | 0.40557 | 14600.52 | 0.44845 | 5381.4 | 1 | 5000 | 14600.52 | 5381.4 | 0 | 0 | 0 | 0 | 23423.68 | 0 | 0 | 0 | 0 | 0 | 23423.68
2022050412 | 4 | 0.63347 | 50677.6 | 0.44934 | 16176.24 | 0.47599 | 5711.88 | 1 | 5000 | 16176.24 | 5711.88 | 0 | 0 | 0 | 0 | 23789.48 | 0 | 0 | 0 | 0 | 0 | 23789.48
2022050413 | 4 | 0.66077 | 52861.6 | 0.49012 | 17644.32 | 0.5644 | 6772.8 | 1 | 5000 | 17644.32 | 6772.8 | 0 | 0 | 0 | 0 | 23444.48 | 0 | 0 | 0 | 0 | 0 | 23444.48
2022050414 | 4 | 0.68647 | 54917.6 | 0.50653 | 18235.08 | 0.58858 | 7062.96 | 1 | 5000 | 18235.08 | 7062.96 | 0 | 0 | 0 | 0 | 24619.56 | 0 | 0 | 0 | 0 | 0 | 24619.56
2022050415 | 4 | 0.71163 | 56930.4 | 0.51931 | 18695.16 | 0.58311 | 6997.32 | 1 | 5000 | 18695.16 | 6997.32 | 0 | 0 | 0 | 0 | 26237.92 | 0 | 0 | 0 | 0 | 0 | 26237.92
2022050416 | 4 | 0.7277 | 58216 | 0.54521 | 19627.56 | 0.57268 | 6872.16 | 1 | 5000 | 19627.56 | 6872.16 | 0 | 0 | 0 | 0 | 26716.28 | 0 | 0 | 0 | 0 | 0 | 26716.28
2022050417 | 4 | 0.73733 | 58986.4 | 0.56006 | 20162.16 | 0.44384 | 5326.08 | 1 | 5000 | 20162.16 | 5326.08 | 0 | 0 | 0 | 0 | 28498.16 | 0 | 0 | 0 | 0 | 0 | 28498.16
2022050418 | 4 | 0.73865 | 59092 | 0.58005 | 20881.8 | 0.37571 | 4508.52 | 1 | 5000 | 20881.8 | 4508.52 | 0 | 0 | 0 | 0 | 28701.68 | 0 | 0 | 0 | 0 | 0 | 28701.68
2022050419 | 4 | 0.72452 | 57961.6 | 0.61083 | 21989.88 | 0.2978 | 3573.6 | 1 | 5000 | 21989.88 | 3573.6 | 0 | 0 | 0 | 0 | 27398.12 | 0 | 0 | 0 | 0 | 0 | 27398.12
2022050420 | 4 | 0.70257 | 56205.6 | 0.61396 | 22102.56 | 0.11885 | 1426.2 | 1 | 5000 | 22102.56 | 1426.2 | 0 | 0 | 0 | 0 | 27676.84 | 0 | 0 | 0 | 0 | 0 | 27676.84
2022050421 | 4 | 0.69122 | 55297.6 | 0.58658 | 21116.88 | 0.00755 | 90.6 | 1 | 5000 | 21116.88 | 90.6 | 0 | 0 | 0 | 0 | 29090.12 | 0 | 0 | 0 | 0 | 0 | 29090.12
2022050422 | 4 | 0.67271 | 53816.8 | 0.60751 | 21870.36 | 0 | 0 | 1 | 5000 | 21870.36 | 0 | 0 | 0 | 0 | 0 | 26946.44 | 0 | 0 | 0 | 0 | 0 | 26946.44
2022050423 | 4 | 0.63768 | 51014.4 | 0.5907 | 21265.2 | 0 | 0 | 1 | 5000 | 21265.2 | 0 | 0 | 0 | 0 | 0 | 24749.2 | 0 | 0 | 0 | 0 | 0 | 24749.2
2022050424 | 4 | 0.59452 | 47561.6 | 0.59511 | 21423.96 | 0 | 0 | 1 | 5000 | 21423.96 | 0 | 0 | 0 | 0 | 0 | 21137.64 | 0 | 0 | 0 | 0 | 0 | 21137.64
2022050501 | 5 | 0.55927 | 44741.6 | 0.58186 | 20946.96 | 0 | 0 | 1 | 5000 | 20946.96 | 0 | 0 | 0 | 0 | 0 | 18794.64 | 0 | 0 | 0 | 0 | 0 | 18794.64
2022050502 | 5 | 0.53414 | 42731.2 | 0.59988 | 21595.68 | 0 | 0 | 1 | 5000 | 21595.68 | 0 | 0 | 0 | 0 | 0 | 16135.52 | 0 | 0 | 0 | 0 | 0 | 16135.52
2022050503 | 5 | 0.51665 | 41332 | 0.60291 | 21704.76 | 0 | 0 | 1 | 5000 | 21704.76 | 0 | 0 | 0 | 0 | 0 | 14627.24 | 0 | 0 | 0 | 0 | 0 | 14627.24
2022050504 | 5 | 0.50722 | 40577.6 | 0.59284 | 21342.24 | 0 | 0 | 1 | 5000 | 21342.24 | 0 | 0 | 0 | 0 | 0 | 14235.36 | 0 | 0 | 0 | 0 | 0 | 14235.36
2022050505 | 5 | 0.50797 | 40637.6 | 0.56607 | 20378.52 | 0 | 0 | 1 | 5000 | 20378.52 | 0 | 0 | 0 | 0 | 0 | 15259.08 | 0 | 0 | 0 | 0 | 0 | 15259.08
2022050506 | 5 | 0.52719 | 42175.2 | 0.4919 | 17708.4 | 0 | 0 | 1 | 5000 | 17708.4 | 0 | 0 | 0 | 0 | 0 | 19466.8 | 0 | 0 | 0 | 0 | 0 | 19466.8
2022050507 | 5 | 0.55758 | 44606.4 | 0.45925 | 16533 | 0.00013 | 1.56 | 1 | 5000 | 16533 | 1.56 | 0 | 0 | 0 | 0 | 23071.84 | 0 | 0 | 0 | 0 | 0 | 23071.84
2022050508 | 5 | 0.57157 | 45725.6 | 0.44239 | 15926.04 | 0.04245 | 509.4 | 1 | 5000 | 15926.04 | 509.4 | 0 | 0 | 0 | 0 | 24290.16 | 0 | 0 | 0 | 0 | 0 | 24290.16
2022050509 | 5 | 0.5862 | 46896 | 0.44541 | 16034.76 | 0.25972 | 3116.64 | 1 | 5000 | 16034.76 | 3116.64 | 0 | 0 | 0 | 0 | 22744.6 | 0 | 0 | 0 | 0 | 0 | 22744.6
2022050510 | 5 | 0.60415 | 48332 | 0.47524 | 17108.64 | 0.42443 | 5093.16 | 1 | 5000 | 17108.64 | 5093.16 | 0 | 0 | 0 | 0 | 21130.2 | 0 | 0 | 0 | 0 | 0 | 21130.2
2022050511 | 5 | 0.63221 | 50576.8 | 0.49551 | 17838.36 | 0.5524 | 6628.8 | 1 | 5000 | 17838.36 | 6628.8 | 0 | 0 | 0 | 0 | 21109.64 | 0 | 0 | 0 | 0 | 0 | 21109.64
2022050512 | 5 | 0.65007 | 52005.6 | 0.45704 | 16453.44 | 0.59827 | 7179.24 | 1 | 5000 | 16453.44 | 7179.24 | 0 | 0 | 0 | 0 | 23372.92 | 0 | 0 | 0 | 0 | 0 | 23372.92
2022050513 | 5 | 0.66764 | 53411.2 | 0.43403 | 15625.08 | 0.61887 | 7426.44 | 1 | 5000 | 15625.08 | 7426.44 | 0 | 0 | 0 | 0 | 25359.68 | 0 | 0 | 0 | 0 | 0 | 25359.68
2022050514 | 5 | 0.67788 | 54230.4 | 0.42446 | 15280.56 | 0.61092 | 7331.04 | 1 | 5000 | 15280.56 | 7331.04 | 0 | 0 | 0 | 0 | 26618.8 | 0 | 0 | 0 | 0 | 0 | 26618.8
2022050515 | 5 | 0.67952 | 54361.6 | 0.40656 | 14636.16 | 0.60516 | 7261.92 | 1 | 5000 | 14636.16 | 7261.92 | 0 | 0 | 0 | 0 | 27463.52 | 0 | 0 | 0 | 0 | 0 | 27463.52
2022050516 | 5 | 0.68028 | 54422.4 | 0.39912 | 14368.32 | 0.60485 | 7258.2 | 1 | 5000 | 14368.32 | 7258.2 | 0 | 0 | 0 | 0 | 27795.88 | 0 | 0 | 0 | 0 | 0 | 27795.88
2022050517 | 5 | 0.69149 | 55319.2 | 0.41066 | 14783.76 | 0.56587 | 6790.44 | 1 | 5000 | 14783.76 | 6790.44 | 0 | 0 | 0 | 0 | 28745 | 0 | 0 | 0 | 0 | 0 | 28745
2022050518 | 5 | 0.69113 | 55290.4 | 0.40184 | 14466.24 | 0.54505 | 6540.6 | 1 | 5000 | 14466.24 | 6540.6 | 0 | 0 | 0 | 0 | 29283.56 | 0 | 0 | 0 | 0 | 0 | 29283.56
2022050519 | 5 | 0.67827 | 54261.6 | 0.34116 | 12281.76 | 0.56365 | 6763.8 | 1 | 5000 | 12281.76 | 6763.8 | 0 | 0 | 0 | 0 | 30216.04 | 0 | 0 | 0 | 0 | 0 | 30216.04
2022050520 | 5 | 0.65302 | 52241.6 | 0.23346 | 8404.56 | 0.25728 | 3087.36 | 1 | 5000 | 8404.56 | 3087.36 | 0 | 0 | 0 | 0 | 35749.68 | 0 | 0 | 0 | 0 | 0 | 35749.68
2022050521 | 5 | 0.63112 | 50489.6 | 0.13708 | 4934.88 | 0.01078 | 129.36 | 1 | 5000 | 4934.88 | 129.36 | 0 | 0 | 0 | 0 | 40425.36 | 0 | 0 | 0 | 0 | 0 | 40425.36
2022050522 | 5 | 0.60574 | 48459.2 | 0.11516 | 4145.76 | 0 | 0 | 1 | 5000 | 4145.76 | 0 | 0 | 0 | 0 | 0 | 39313.44 | 0 | 0 | 0 | 0 | 0 | 39313.44
2022050523 | 5 | 0.56587 | 45269.6 | 0.11419 | 4110.84 | 0 | 0 | 1 | 5000 | 4110.84 | 0 | 0 | 0 | 0 | 0 | 36158.76 | 0 | 0 | 0 | 0 | 0 | 36158.76
2022050524 | 5 | 0.52431 | 41944.8 | 0.13614 | 4901.04 | 0 | 0 | 1 | 5000 | 4901.04 | 0 | 0 | 0 | 0 | 0 | 32043.76 | 0 | 0 | 0 | 0 | 0 | 32043.76
2022050601 | 6 | 0.49139 | 39311.2 | 0.18087 | 6511.32 | 0 | 0 | 1 | 5000 | 6511.32 | 0 | 0 | 0 | 0 | 0 | 27799.88 | 0 | 0 | 0 | 0 | 0 | 27799.88
2022050602 | 6 | 0.46902 | 37521.6 | 0.2324 | 8366.4 | 0 | 0 | 1 | 5000 | 8366.4 | 0 | 0 | 0 | 0 | 0 | 24155.2 | 0 | 0 | 0 | 0 | 0 | 24155.2
2022050603 | 6 | 0.45872 | 36697.6 | 0.31305 | 11269.8 | 0 | 0 | 1 | 5000 | 11269.8 | 0 | 0 | 0 | 0 | 0 | 20427.8 | 0 | 0 | 0 | 0 | 0 | 20427.8
2022050604 | 6 | 0.45081 | 36064.8 | 0.3373 | 12142.8 | 0 | 0 | 1 | 5000 | 12142.8 | 0 | 0 | 0 | 0 | 0 | 18922 | 0 | 0 | 0 | 0 | 0 | 18922
2022050605 | 6 | 0.45192 | 36153.6 | 0.33449 | 12041.64 | 0 | 0 | 1 | 5000 | 12041.64 | 0 | 0 | 0 | 0 | 0 | 19111.96 | 0 | 0 | 0 | 0 | 0 | 19111.96
2022050606 | 6 | 0.4664 | 37312 | 0.31893 | 11481.48 | 0 | 0 | 1 | 5000 | 11481.48 | 0 | 0 | 0 | 0 | 0 | 20830.52 | 0 | 0 | 0 | 0 | 0 | 20830.52
2022050607 | 6 | 0.49392 | 39513.6 | 0.28013 | 10084.68 | 0.00134 | 16.08 | 1 | 5000 | 10084.68 | 16.08 | 0 | 0 | 0 | 0 | 24412.84 | 0 | 0 | 0 | 0 | 0 | 24412.84
2022050608 | 6 | 0.51099 | 40879.2 | 0.22143 | 7971.48 | 0.14325 | 1719 | 1 | 5000 | 7971.48 | 1719 | 0 | 0 | 0 | 0 | 26188.72 | 0 | 0 | 0 | 0 | 0 | 26188.72
2022050609 | 6 | 0.53028 | 42422.4 | 0.17113 | 6160.68 | 0.56588 | 6790.56 | 1 | 5000 | 6160.68 | 6790.56 | 0 | 0 | 0 | 0 | 24471.16 | 0 | 0 | 0 | 0 | 0 | 24471.16
2022050610 | 6 | 0.55383 | 44306.4 | 0.17219 | 6198.84 | 0.73426 | 8811.12 | 1 | 5000 | 6198.84 | 8811.12 | 0 | 0 | 0 | 0 | 24296.44 | 0 | 0 | 0 | 0 | 0 | 24296.44
2022050611 | 6 | 0.58538 | 46830.4 | 0.19524 | 7028.64 | 0.76672 | 9200.64 | 1 | 5000 | 7028.64 | 9200.64 | 0 | 0 | 0 | 0 | 25601.12 | 0 | 0 | 0 | 0 | 0 | 25601.12
2022050612 | 6 | 0.62131 | 49704.8 | 0.1946 | 7005.6 | 0.78082 | 9369.84 | 1 | 5000 | 7005.6 | 9369.84 | 0 | 0 | 0 | 0 | 28329.36 | 0 | 0 | 0 | 0 | 0 | 28329.36
2022050613 | 6 | 0.65871 | 52696.8 | 0.17436 | 6276.96 | 0.78099 | 9371.88 | 1 | 5000 | 6276.96 | 9371.88 | 0 | 0 | 0 | 0 | 32047.96 | 0 | 0 | 0 | 0 | 0 | 32047.96
2022050614 | 6 | 0.69664 | 55731.2 | 0.15847 | 5704.92 | 0.77851 | 9342.12 | 1 | 5000 | 5704.92 | 9342.12 | 0 | 0 | 0 | 0 | 35684.16 | 0 | 0 | 0 | 0 | 0 | 35684.16
2022050615 | 6 | 0.73088 | 58470.4 | 0.18195 | 6550.2 | 0.77481 | 9297.72 | 1 | 5000 | 6550.2 | 9297.72 | 0 | 0 | 0 | 0 | 37622.48 | 0 | 0 | 0 | 0 | 0 | 37622.48
2022050616 | 6 | 0.75858 | 60686.4 | 0.19714 | 7097.04 | 0.76571 | 9188.52 | 1 | 5000 | 7097.04 | 9188.52 | 0 | 0 | 0 | 0 | 39400.84 | 0 | 0 | 0 | 0 | 0 | 39400.84
2022050617 | 6 | 0.77959 | 62367.2 | 0.21491 | 7736.76 | 0.74599 | 8951.88 | 1 | 5000 | 7736.76 | 8951.88 | 0 | 0 | 0 | 0 | 40678.56 | 0 | 0 | 0 | 0 | 0 | 40678.56
2022050618 | 6 | 0.78639 | 62911.2 | 0.22473 | 8090.28 | 0.73064 | 8767.68 | 1 | 5000 | 8090.28 | 8767.68 | 0 | 0 | 0 | 0 | 41053.24 | 0 | 0 | 0 | 0 | 0 | 41053.24
2022050619 | 6 | 0.76229 | 60983.2 | 0.24275 | 8739 | 0.55275 | 6633 | 1 | 5000 | 8739 | 6633 | 0 | 0 | 0 | 0 | 40611.2 | 0 | 0 | 0 | 0 | 0 | 40611.2
2022050620 | 6 | 0.72958 | 58366.4 | 0.25844 | 9303.84 | 0.20067 | 2408.04 | 1 | 5000 | 9303.84 | 2408.04 | 0 | 0 | 0 | 0 | 41654.52 | 0 | 0 | 0 | 0 | 0 | 41654.52
2022050621 | 6 | 0.70547 | 56437.6 | 0.27587 | 9931.32 | 0.00873 | 104.76 | 1 | 5000 | 9931.32 | 104.76 | 0 | 0 | 0 | 0 | 41401.52 | 0 | 0 | 0 | 0 | 0 | 41401.52
2022050622 | 6 | 0.68007 | 54405.6 | 0.32484 | 11694.24 | 0 | 0 | 1 | 5000 | 11694.24 | 0 | 0 | 0 | 0 | 0 | 37711.36 | 0 | 0 | 0 | 0 | 0 | 37711.36
2022050623 | 6 | 0.64415 | 51532 | 0.36836 | 13260.96 | 0 | 0 | 1 | 5000 | 13260.96 | 0 | 0 | 0 | 0 | 0 | 33271.04 | 0 | 0 | 0 | 0 | 0 | 33271.04
2022050624 | 6 | 0.60468 | 48374.4 | 0.42392 | 15261.12 | 0 | 0 | 1 | 5000 | 15261.12 | 0 | 0 | 0 | 0 | 0 | 28113.28 | 0 | 0 | 0 | 0 | 0 | 28113.28
2022050701 | 7 | 0.56579 | 45263.2 | 0.43776 | 15759.36 | 0 | 0 | 1 | 5000 | 15759.36 | 0 | 0 | 0 | 0 | 0 | 24503.84 | 0 | 0 | 0 | 0 | 0 | 24503.84
2022050702 | 7 | 0.5373 | 42984 | 0.4633 | 16678.8 | 0 | 0 | 1 | 5000 | 16678.8 | 0 | 0 | 0 | 0 | 0 | 21305.2 | 0 | 0 | 0 | 0 | 0 | 21305.2
2022050703 | 7 | 0.5138 | 41104 | 0.44661 | 16077.96 | 0 | 0 | 1 | 5000 | 16077.96 | 0 | 0 | 0 | 0 | 0 | 20026.04 | 0 | 0 | 0 | 0 | 0 | 20026.04
2022050704 | 7 | 0.5003 | 40024 | 0.42693 | 15369.48 | 0 | 0 | 1 | 5000 | 15369.48 | 0 | 0 | 0 | 0 | 0 | 19654.52 | 0 | 0 | 0 | 0 | 0 | 19654.52
2022050705 | 7 | 0.4924 | 39392 | 0.42408 | 15266.88 | 0 | 0 | 1 | 5000 | 15266.88 | 0 | 0 | 0 | 0 | 0 | 19125.12 | 0 | 0 | 0 | 0 | 0 | 19125.12
2022050706 | 7 | 0.49389 | 39511.2 | 0.42374 | 15254.64 | 0 | 0 | 1 | 5000 | 15254.64 | 0 | 0 | 0 | 0 | 0 | 19256.56 | 0 | 0 | 0 | 0 | 0 | 19256.56
2022050707 | 7 | 0.5018 | 40144 | 0.4101 | 14763.6 | 0.00074 | 8.88 | 1 | 5000 | 14763.6 | 8.88 | 0 | 0 | 0 | 0 | 20371.52 | 0 | 0 | 0 | 0 | 0 | 20371.52
2022050708 | 7 | 0.51073 | 40858.4 | 0.38186 | 13746.96 | 0.10684 | 1282.08 | 1 | 5000 | 13746.96 | 1282.08 | 0 | 0 | 0 | 0 | 20829.36 | 0 | 0 | 0 | 0 | 0 | 20829.36
2022050709 | 7 | 0.53961 | 43168.8 | 0.3158 | 11368.8 | 0.4981 | 5977.2 | 1 | 5000 | 11368.8 | 5977.2 | 0 | 0 | 0 | 0 | 20822.8 | 0 | 0 | 0 | 0 | 0 | 20822.8
2022050710 | 7 | 0.57692 | 46153.6 | 0.25932 | 9335.52 | 0.67624 | 8114.88 | 1 | 5000 | 9335.52 | 8114.88 | 0 | 0 | 0 | 0 | 23703.2 | 0 | 0 | 0 | 0 | 0 | 23703.2
2022050711 | 7 | 0.61909 | 49527.2 | 0.23638 | 8509.68 | 0.71674 | 8600.88 | 1 | 5000 | 8509.68 | 8600.88 | 0 | 0 | 0 | 0 | 27416.64 | 0 | 0 | 0 | 0 | 0 | 27416.64
2022050712 | 7 | 0.66019 | 52815.2 | 0.2226 | 8013.6 | 0.76088 | 9130.56 | 1 | 5000 | 8013.6 | 9130.56 | 0 | 0 | 0 | 0 | 30671.04 | 0 | 0 | 0 | 0 | 0 | 30671.04
2022050713 | 7 | 0.70067 | 56053.6 | 0.24155 | 8695.8 | 0.773 | 9276 | 1 | 5000 | 8695.8 | 9276 | 0 | 0 | 0 | 0 | 33081.8 | 0 | 0 | 0 | 0 | 0 | 33081.8
2022050714 | 7 | 0.7395 | 59160 | 0.29221 | 10519.56 | 0.7758 | 9309.6 | 1 | 5000 | 10519.56 | 9309.6 | 0 | 0 | 0 | 0 | 34330.84 | 0 | 0 | 0 | 0 | 0 | 34330.84
2022050715 | 7 | 0.77375 | 61900 | 0.36747 | 13228.92 | 0.76099 | 9131.88 | 1 | 5000 | 13228.92 | 9131.88 | 0 | 0 | 0 | 0 | 34539.2 | 0 | 0 | 0 | 0 | 0 | 34539.2
2022050716 | 7 | 0.80226 | 64180.8 | 0.44139 | 15890.04 | 0.70096 | 8411.52 | 1 | 5000 | 15890.04 | 8411.52 | 0 | 0 | 0 | 0 | 34879.24 | 0 | 0 | 0 | 0 | 0 | 34879.24
2022050717 | 7 | 0.81939 | 65551.2 | 0.4877 | 17557.2 | 0.65577 | 7869.24 | 1 | 5000 | 17557.2 | 7869.24 | 0 | 0 | 0 | 0 | 35124.76 | 0 | 0 | 0 | 0 | 0 | 35124.76
2022050718 | 7 | 0.82261 | 65808.8 | 0.52848 | 19025.28 | 0.56354 | 6762.48 | 1 | 5000 | 19025.28 | 6762.48 | 0 | 0 | 0 | 0 | 35021.04 | 0 | 0 | 0 | 0 | 0 | 35021.04
2022050719 | 7 | 0.80748 | 64598.4 | 0.54551 | 19638.36 | 0.4716 | 5659.2 | 1 | 5000 | 19638.36 | 5659.2 | 0 | 0 | 0 | 0 | 34300.84 | 0 | 0 | 0 | 0 | 0 | 34300.84
2022050720 | 7 | 0.77693 | 62154.4 | 0.55638 | 20029.68 | 0.23488 | 2818.56 | 1 | 5000 | 20029.68 | 2818.56 | 0 | 0 | 0 | 0 | 34306.16 | 0 | 0 | 0 | 0 | 0 | 34306.16
2022050721 | 7 | 0.75138 | 60110.4 | 0.56377 | 20295.72 | 0.0113 | 135.6 | 1 | 5000 | 20295.72 | 135.6 | 0 | 0 | 0 | 0 | 34679.08 | 0 | 0 | 0 | 0 | 0 | 34679.08
2022050722 | 7 | 0.72598 | 58078.4 | 0.60109 | 21639.24 | 0 | 0 | 1 | 5000 | 21639.24 | 0 | 0 | 0 | 0 | 0 | 31439.16 | 0 | 0 | 0 | 0 | 0 | 31439.16
2022050723 | 7 | 0.69149 | 55319.2 | 0.63726 | 22941.36 | 0 | 0 | 1 | 5000 | 22941.36 | 0 | 0 | 0 | 0 | 0 | 27377.84 | 0 | 0 | 0 | 0 | 0 | 27377.84
2022050724 | 7 | 0.65414 | 52331.2 | 0.67332 | 24239.52 | 0 | 0 | 1 | 5000 | 24239.52 | 0 | 0 | 0 | 0 | 0 | 23091.68 | 0 | 0 | 0 | 0 | 0 | 23091.68
2022050801 | 1 | 0.61849 | 49479.2 | 0.6845 | 24642 | 0 | 0 | 1 | 5000 | 24642 | 0 | 0 | 0 | 0 | 0 | 19837.2 | 0 | 0 | 0 | 0 | 0 | 19837.2
2022050802 | 1 | 0.58801 | 47040.8 | 0.68422 | 24631.92 | 0 | 0 | 1 | 5000 | 24631.92 | 0 | 0 | 0 | 0 | 0 | 17408.88 | 0 | 0 | 0 | 0 | 0 | 17408.88
2022050803 | 1 | 0.56523 | 45218.4 | 0.67312 | 24232.32 | 0 | 0 | 1 | 5000 | 24232.32 | 0 | 0 | 0 | 0 | 0 | 15986.08 | 0 | 0 | 0 | 0 | 0 | 15986.08
2022050804 | 1 | 0.55104 | 44083.2 | 0.65503 | 23581.08 | 0 | 0 | 1 | 5000 | 23581.08 | 0 | 0 | 0 | 0 | 0 | 15502.12 | 0 | 0 | 0 | 0 | 0 | 15502.12
2022050805 | 1 | 0.53571 | 42856.8 | 0.64123 | 23084.28 | 0 | 0 | 1 | 5000 | 23084.28 | 0 | 0 | 0 | 0 | 0 | 14772.52 | 0 | 0 | 0 | 0 | 0 | 14772.52
2022050806 | 1 | 0.52971 | 42376.8 | 0.62582 | 22529.52 | 0 | 0 | 1 | 5000 | 22529.52 | 0 | 0 | 0 | 0 | 0 | 14847.28 | 0 | 0 | 0 | 0 | 0 | 14847.28
2022050807 | 1 | 0.52947 | 42357.6 | 0.61272 | 22057.92 | 0.00044 | 5.28 | 1 | 5000 | 22057.92 | 5.28 | 0 | 0 | 0 | 0 | 15294.4 | 0 | 0 | 0 | 0 | 0 | 15294.4
2022050808 | 1 | 0.53405 | 42724 | 0.59816 | 21533.76 | 0.10928 | 1311.36 | 1 | 5000 | 21533.76 | 1311.36 | 0 | 0 | 0 | 0 | 14878.88 | 0 | 0 | 0 | 0 | 0 | 14878.88
2022050809 | 1 | 0.56568 | 45254.4 | 0.52538 | 18913.68 | 0.48112 | 5773.44 | 1 | 5000 | 18913.68 | 5773.44 | 0 | 0 | 0 | 0 | 15567.28 | 0 | 0 | 0 | 0 | 0 | 15567.28
2022050810 | 1 | 0.61133 | 48906.4 | 0.49307 | 17750.52 | 0.70078 | 8409.36 | 1 | 5000 | 17750.52 | 8409.36 | 0 | 0 | 0 | 0 | 17746.52 | 0 | 0 | 0 | 0 | 0 | 17746.52
2022050811 | 1 | 0.6568 | 52544 | 0.45962 | 16546.32 | 0.76146 | 9137.52 | 1 | 5000 | 16546.32 | 9137.52 | 0 | 0 | 0 | 0 | 21860.16 | 0 | 0 | 0 | 0 | 0 | 21860.16
2022050812 | 1 | 0.69551 | 55640.8 | 0.40271 | 14497.56 | 0.78897 | 9467.64 | 1 | 5000 | 14497.56 | 9467.64 | 0 | 0 | 0 | 0 | 26675.6 | 0 | 0 | 0 | 0 | 0 | 26675.6
2022050813 | 1 | 0.73494 | 58795.2 | 0.36525 | 13149 | 0.79454 | 9534.48 | 1 | 5000 | 13149 | 9534.48 | 0 | 0 | 0 | 0 | 31111.72 | 0 | 0 | 0 | 0 | 0 | 31111.72
2022050814 | 1 | 0.77003 | 61602.4 | 0.38748 | 13949.28 | 0.79379 | 9525.48 | 1 | 5000 | 13949.28 | 9525.48 | 0 | 0 | 0 | 0 | 33127.64 | 0 | 0 | 0 | 0 | 0 | 33127.64
2022050815 | 1 | 0.80229 | 64183.2 | 0.44222 | 15919.92 | 0.78537 | 9424.44 | 1 | 5000 | 15919.92 | 9424.44 | 0 | 0 | 0 | 0 | 33838.84 | 0 | 0 | 0 | 0 | 0 | 33838.84
2022050816 | 1 | 0.82674 | 66139.2 | 0.49903 | 17965.08 | 0.76772 | 9212.64 | 1 | 5000 | 17965.08 | 9212.64 | 0 | 0 | 0 | 0 | 33961.48 | 0 | 0 | 0 | 0 | 0 | 33961.48
2022050817 | 1 | 0.84256 | 67404.8 | 0.53681 | 19325.16 | 0.73152 | 8778.24 | 1 | 5000 | 19325.16 | 8778.24 | 0 | 0 | 0 | 0 | 34301.4 | 0 | 0 | 0 | 0 | 0 | 34301.4
2022050818 | 1 | 0.84517 | 67613.6 | 0.55865 | 20111.4 | 0.66326 | 7959.12 | 1 | 5000 | 20111.4 | 7959.12 | 0 | 0 | 0 | 0 | 34543.08 | 0 | 0 | 0 | 0 | 0 | 34543.08
2022050819 | 1 | 0.82863 | 66290.4 | 0.57522 | 20707.92 | 0.55133 | 6615.96 | 1 | 5000 | 20707.92 | 6615.96 | 0 | 0 | 0 | 0 | 33966.52 | 0 | 0 | 0 | 0 | 0 | 33966.52
2022050820 | 1 | 0.79692 | 63753.6 | 0.58443 | 21039.48 | 0.25834 | 3100.08 | 1 | 5000 | 21039.48 | 3100.08 | 0 | 0 | 0 | 0 | 34614.04 | 0 | 0 | 0 | 0 | 0 | 34614.04
2022050821 | 1 | 0.77442 | 61953.6 | 0.57769 | 20796.84 | 0.0156 | 187.2 | 1 | 5000 | 20796.84 | 187.2 | 0 | 0 | 0 | 0 | 35969.56 | 0 | 0 | 0 | 0 | 0 | 35969.56
2022050822 | 1 | 0.75156 | 60124.8 | 0.61896 | 22282.56 | 0 | 0 | 1 | 5000 | 22282.56 | 0 | 0 | 0 | 0 | 0 | 32842.24 | 0 | 0 | 0 | 0 | 0 | 32842.24
2022050823 | 1 | 0.70732 | 56585.6 | 0.65186 | 23466.96 | 0 | 0 | 1 | 5000 | 23466.96 | 0 | 0 | 0 | 0 | 0 | 28118.64 | 0 | 0 | 0 | 0 | 0 | 28118.64
2022050824 | 1 | 0.65973 | 52778.4 | 0.65464 | 23567.04 | 0 | 0 | 1 | 5000 | 23567.04 | 0 | 0 | 0 | 0 | 0 | 24211.36 | 0 | 0 | 0 | 0 | 0 | 24211.36
2022050901 | 2 | 0.61797 | 49437.6 | 0.65105 | 23437.8 | 0 | 0 | 1 | 5000 | 23437.8 | 0 | 0 | 0 | 0 | 0 | 20999.8 | 0 | 0 | 0 | 0 | 0 | 20999.8
2022050902 | 2 | 0.58835 | 47068 | 0.6515 | 23454 | 0 | 0 | 1 | 5000 | 23454 | 0 | 0 | 0 | 0 | 0 | 18614 | 0 | 0 | 0 | 0 | 0 | 18614
2022050903 | 2 | 0.56913 | 45530.4 | 0.65655 | 23635.8 | 0 | 0 | 1 | 5000 | 23635.8 | 0 | 0 | 0 | 0 | 0 | 16894.6 | 0 | 0 | 0 | 0 | 0 | 16894.6
2022050904 | 2 | 0.56021 | 44816.8 | 0.65041 | 23414.76 | 0 | 0 | 1 | 5000 | 23414.76 | 0 | 0 | 0 | 0 | 0 | 16402.04 | 0 | 0 | 0 | 0 | 0 | 16402.04
2022050905 | 2 | 0.55986 | 44788.8 | 0.63458 | 22844.88 | 0 | 0 | 1 | 5000 | 22844.88 | 0 | 0 | 0 | 0 | 0 | 16943.92 | 0 | 0 | 0 | 0 | 0 | 16943.92
2022050906 | 2 | 0.57602 | 46081.6 | 0.61991 | 22316.76 | 0 | 0 | 1 | 5000 | 22316.76 | 0 | 0 | 0 | 0 | 0 | 18764.84 | 0 | 0 | 0 | 0 | 0 | 18764.84
2022050907 | 2 | 0.60409 | 48327.2 | 0.61436 | 22116.96 | 0.00035 | 4.2 | 1 | 5000 | 22116.96 | 4.2 | 0 | 0 | 0 | 0 | 21206.04 | 0 | 0 | 0 | 0 | 0 | 21206.04
2022050908 | 2 | 0.61902 | 49521.6 | 0.58939 | 21218.04 | 0.10012 | 1201.44 | 1 | 5000 | 21218.04 | 1201.44 | 0 | 0 | 0 | 0 | 22102.12 | 0 | 0 | 0 | 0 | 0 | 22102.12
2022050909 | 2 | 0.63711 | 50968.8 | 0.56768 | 20436.48 | 0.39774 | 4772.88 | 1 | 5000 | 20436.48 | 4772.88 | 0 | 0 | 0 | 0 | 20759.44 | 0 | 0 | 0 | 0 | 0 | 20759.44
2022050910 | 2 | 0.66844 | 53475.2 | 0.57437 | 20677.32 | 0.46712 | 5605.44 | 1 | 5000 | 20677.32 | 5605.44 | 0 | 0 | 0 | 0 | 22192.44 | 0 | 0 | 0 | 0 | 0 | 22192.44
2022050911 | 2 | 0.70638 | 56510.4 | 0.56298 | 20267.28 | 0.59891 | 7186.92 | 1 | 5000 | 20267.28 | 7186.92 | 0 | 0 | 0 | 0 | 24056.2 | 0 | 0 | 0 | 0 | 0 | 24056.2
2022050912 | 2 | 0.75153 | 60122.4 | 0.55099 | 19835.64 | 0.68296 | 8195.52 | 1 | 5000 | 19835.64 | 8195.52 | 0 | 0 | 0 | 0 | 27091.24 | 0 | 0 | 0 | 0 | 0 | 27091.24
2022050913 | 2 | 0.79183 | 63346.4 | 0.543 | 19548 | 0.73086 | 8770.32 | 1 | 5000 | 19548 | 8770.32 | 0 | 0 | 0 | 0 | 30028.08 | 0 | 0 | 0 | 0 | 0 | 30028.08
2022050914 | 2 | 0.82761 | 66208.8 | 0.53535 | 19272.6 | 0.73562 | 8827.44 | 1 | 5000 | 19272.6 | 8827.44 | 0 | 0 | 0 | 0 | 33108.76 | 0 | 0 | 0 | 0 | 0 | 33108.76
2022050915 | 2 | 0.85795 | 68636 | 0.54087 | 19471.32 | 0.71296 | 8555.52 | 1 | 5000 | 19471.32 | 8555.52 | 0 | 0 | 0 | 0 | 35609.16 | 0 | 0 | 0 | 0 | 0 | 35609.16
2022050916 | 2 | 0.87492 | 69993.6 | 0.54467 | 19608.12 | 0.69056 | 8286.72 | 1 | 5000 | 19608.12 | 8286.72 | 0 | 0 | 0 | 0 | 37098.76 | 0 | 0 | 0 | 0 | 0 | 37098.76
2022050917 | 2 | 0.8859 | 70872 | 0.54407 | 19586.52 | 0.66171 | 7940.52 | 1 | 5000 | 19586.52 | 7940.52 | 0 | 0 | 0 | 0 | 38344.96 | 0 | 0 | 0 | 0 | 0 | 38344.96
2022050918 | 2 | 0.88257 | 70605.6 | 0.56103 | 20197.08 | 0.59706 | 7164.72 | 1 | 5000 | 20197.08 | 7164.72 | 0 | 0 | 0 | 0 | 38243.8 | 0 | 0 | 0 | 0 | 0 | 38243.8
2022050919 | 2 | 0.86303 | 69042.4 | 0.57515 | 20705.4 | 0.51113 | 6133.56 | 1 | 5000 | 20705.4 | 6133.56 | 0 | 0 | 0 | 0 | 37203.44 | 0 | 0 | 0 | 0 | 0 | 37203.44
2022050920 | 2 | 0.82992 | 66393.6 | 0.58975 | 21231 | 0.25949 | 3113.88 | 1 | 5000 | 21231 | 3113.88 | 0 | 0 | 0 | 0 | 37048.72 | 0 | 0 | 0 | 0 | 0 | 37048.72
2022050921 | 2 | 0.80894 | 64715.2 | 0.59243 | 21327.48 | 0.02076 | 249.12 | 1 | 5000 | 21327.48 | 249.12 | 0 | 0 | 0 | 0 | 38138.6 | 0 | 0 | 0 | 0 | 0 | 38138.6
2022050922 | 2 | 0.78177 | 62541.6 | 0.62674 | 22562.64 | 0.00042 | 5.04 | 1 | 5000 | 22562.64 | 5.04 | 0 | 0 | 0 | 0 | 34973.92 | 0 | 0 | 0 | 0 | 0 | 34973.92
2022050923 | 2 | 0.7312 | 58496 | 0.63398 | 22823.28 | 0 | 0 | 1 | 5000 | 22823.28 | 0 | 0 | 0 | 0 | 0 | 30672.72 | 0 | 0 | 0 | 0 | 0 | 30672.72
2022050924 | 2 | 0.67924 | 54339.2 | 0.64204 | 23113.44 | 0 | 0 | 1 | 5000 | 23113.44 | 0 | 0 | 0 | 0 | 0 | 26225.76 | 0 | 0 | 0 | 0 | 0 | 26225.76
2022051001 | 3 | 0.63664 | 50931.2 | 0.64573 | 23246.28 | 0 | 0 | 1 | 5000 | 23246.28 | 0 | 0 | 0 | 0 | 0 | 22684.92 | 0 | 0 | 0 | 0 | 0 | 22684.92
2022051002 | 3 | 0.6105 | 48840 | 0.65336 | 23520.96 | 0 | 0 | 1 | 5000 | 23520.96 | 0 | 0 | 0 | 0 | 0 | 20319.04 | 0 | 0 | 0 | 0 | 0 | 20319.04
2022051003 | 3 | 0.58702 | 46961.6 | 0.6509 | 23432.4 | 0 | 0 | 1 | 5000 | 23432.4 | 0 | 0 | 0 | 0 | 0 | 18529.2 | 0 | 0 | 0 | 0 | 0 | 18529.2
2022051004 | 3 | 0.57157 | 45725.6 | 0.62639 | 22550.04 | 0 | 0 | 1 | 5000 | 22550.04 | 0 | 0 | 0 | 0 | 0 | 18175.56 | 0 | 0 | 0 | 0 | 0 | 18175.56
2022051005 | 3 | 0.56861 | 45488.8 | 0.60291 | 21704.76 | 0 | 0 | 1 | 5000 | 21704.76 | 0 | 0 | 0 | 0 | 0 | 18784.04 | 0 | 0 | 0 | 0 | 0 | 18784.04
2022051006 | 3 | 0.58373 | 46698.4 | 0.5765 | 20754 | 0 | 0 | 1 | 5000 | 20754 | 0 | 0 | 0 | 0 | 0 | 20944.4 | 0 | 0 | 0 | 0 | 0 | 20944.4
2022051007 | 3 | 0.60596 | 48476.8 | 0.53064 | 19103.04 | 0.00046 | 5.52 | 1 | 5000 | 19103.04 | 5.52 | 0 | 0 | 0 | 0 | 24368.24 | 0 | 0 | 0 | 0 | 0 | 24368.24
2022051008 | 3 | 0.61903 | 49522.4 | 0.52321 | 18835.56 | 0.07727 | 927.24 | 1 | 5000 | 18835.56 | 927.24 | 0 | 0 | 0 | 0 | 24759.6 | 0 | 0 | 0 | 0 | 0 | 24759.6
2022051009 | 3 | 0.63751 | 51000.8 | 0.54265 | 19535.4 | 0.32011 | 3841.32 | 1 | 5000 | 19535.4 | 3841.32 | 0 | 0 | 0 | 0 | 22624.08 | 0 | 0 | 0 | 0 | 0 | 22624.08
2022051010 | 3 | 0.66461 | 53168.8 | 0.56578 | 20368.08 | 0.44468 | 5336.16 | 1 | 5000 | 20368.08 | 5336.16 | 0 | 0 | 0 | 0 | 22464.56 | 0 | 0 | 0 | 0 | 0 | 22464.56
2022051011 | 3 | 0.69557 | 55645.6 | 0.55084 | 19830.24 | 0.51652 | 6198.24 | 1 | 5000 | 19830.24 | 6198.24 | 0 | 0 | 0 | 0 | 24617.12 | 0 | 0 | 0 | 0 | 0 | 24617.12
2022051012 | 3 | 0.73028 | 58422.4 | 0.51238 | 18445.68 | 0.58713 | 7045.56 | 1 | 5000 | 18445.68 | 7045.56 | 0 | 0 | 0 | 0 | 27931.16 | 0 | 0 | 0 | 0 | 0 | 27931.16
2022051013 | 3 | 0.76178 | 60942.4 | 0.48301 | 17388.36 | 0.60494 | 7259.28 | 1 | 5000 | 17388.36 | 7259.28 | 0 | 0 | 0 | 0 | 31294.76 | 0 | 0 | 0 | 0 | 0 | 31294.76
2022051014 | 3 | 0.79687 | 63749.6 | 0.48582 | 17489.52 | 0.63803 | 7656.36 | 1 | 5000 | 17489.52 | 7656.36 | 0 | 0 | 0 | 0 | 33603.72 | 0 | 0 | 0 | 0 | 0 | 33603.72
2022051015 | 3 | 0.82477 | 65981.6 | 0.54497 | 19618.92 | 0.65824 | 7898.88 | 1 | 5000 | 19618.92 | 7898.88 | 0 | 0 | 0 | 0 | 33463.8 | 0 | 0 | 0 | 0 | 0 | 33463.8
2022051016 | 3 | 0.84769 | 67815.2 | 0.59183 | 21305.88 | 0.63832 | 7659.84 | 1 | 5000 | 21305.88 | 7659.84 | 0 | 0 | 0 | 0 | 33849.48 | 0 | 0 | 0 | 0 | 0 | 33849.48
2022051017 | 3 | 0.86096 | 68876.8 | 0.60396 | 21742.56 | 0.61798 | 7415.76 | 1 | 5000 | 21742.56 | 7415.76 | 0 | 0 | 0 | 0 | 34718.48 | 0 | 0 | 0 | 0 | 0 | 34718.48
2022051018 | 3 | 0.8601 | 68808 | 0.65361 | 23529.96 | 0.45058 | 5406.96 | 1 | 5000 | 23529.96 | 5406.96 | 0 | 0 | 0 | 0 | 34871.08 | 0 | 0 | 0 | 0 | 0 | 34871.08
2022051019 | 3 | 0.83865 | 67092 | 0.67761 | 24393.96 | 0.26417 | 3170.04 | 1 | 5000 | 24393.96 | 3170.04 | 0 | 0 | 0 | 0 | 34528 | 0 | 0 | 0 | 0 | 0 | 34528
2022051020 | 3 | 0.8031 | 64248 | 0.67302 | 24228.72 | 0.07851 | 942.12 | 1 | 5000 | 24228.72 | 942.12 | 0 | 0 | 0 | 0 | 34077.16 | 0 | 0 | 0 | 0 | 0 | 34077.16
2022051021 | 3 | 0.77725 | 62180 | 0.6435 | 23166 | 0.00489 | 58.68 | 1 | 5000 | 23166 | 58.68 | 0 | 0 | 0 | 0 | 33955.32 | 0 | 0 | 0 | 0 | 0 | 33955.32
2022051022 | 3 | 0.74786 | 59828.8 | 0.59837 | 21541.32 | 0 | 0 | 1 | 5000 | 21541.32 | 0 | 0 | 0 | 0 | 0 | 33287.48 | 0 | 0 | 0 | 0 | 0 | 33287.48
2022051023 | 3 | 0.69453 | 55562.4 | 0.57265 | 20615.4 | 0 | 0 | 1 | 5000 | 20615.4 | 0 | 0 | 0 | 0 | 0 | 29947 | 0 | 0 | 0 | 0 | 0 | 29947
2022051024 | 3 | 0.64342 | 51473.6 | 0.5605 | 20178 | 0 | 0 | 1 | 5000 | 20178 | 0 | 0 | 0 | 0 | 0 | 26295.6 | 0 | 0 | 0 | 0 | 0 | 26295.6
2022051101 | 4 | 0.60165 | 48132 | 0.53955 | 19423.8 | 0 | 0 | 1 | 5000 | 19423.8 | 0 | 0 | 0 | 0 | 0 | 23708.2 | 0 | 0 | 0 | 0 | 0 | 23708.2
2022051102 | 4 | 0.56666 | 45332.8 | 0.47052 | 16938.72 | 0 | 0 | 1 | 5000 | 16938.72 | 0 | 0 | 0 | 0 | 0 | 23394.08 | 0 | 0 | 0 | 0 | 0 | 23394.08
2022051103 | 4 | 0.54484 | 43587.2 | 0.39347 | 14164.92 | 0 | 0 | 1 | 5000 | 14164.92 | 0 | 0 | 0 | 0 | 0 | 24422.28 | 0 | 0 | 0 | 0 | 0 | 24422.28
2022051104 | 4 | 0.52986 | 42388.8 | 0.34777 | 12519.72 | 0 | 0 | 1 | 5000 | 12519.72 | 0 | 0 | 0 | 0 | 0 | 24869.08 | 0 | 0 | 0 | 0 | 0 | 24869.08
2022051105 | 4 | 0.52631 | 42104.8 | 0.29146 | 10492.56 | 0 | 0 | 1 | 5000 | 10492.56 | 0 | 0 | 0 | 0 | 0 | 26612.24 | 0 | 0 | 0 | 0 | 0 | 26612.24
2022051106 | 4 | 0.53843 | 43074.4 | 0.29728 | 10702.08 | 0 | 0 | 1 | 5000 | 10702.08 | 0 | 0 | 0 | 0 | 0 | 27372.32 | 0 | 0 | 0 | 0 | 0 | 27372.32
2022051107 | 4 | 0.56201 | 44960.8 | 0.31235 | 11244.6 | 0.00099 | 11.88 | 1 | 5000 | 11244.6 | 11.88 | 0 | 0 | 0 | 0 | 28704.32 | 0 | 0 | 0 | 0 | 0 | 28704.32
2022051108 | 4 | 0.57702 | 46161.6 | 0.32926 | 11853.36 | 0.07288 | 874.56 | 1 | 5000 | 11853.36 | 874.56 | 0 | 0 | 0 | 0 | 28433.68 | 0 | 0 | 0 | 0 | 0 | 28433.68
2022051109 | 4 | 0.60143 | 48114.4 | 0.34332 | 12359.52 | 0.40213 | 4825.56 | 1 | 5000 | 12359.52 | 4825.56 | 0 | 0 | 0 | 0 | 25929.32 | 0 | 0 | 0 | 0 | 0 | 25929.32
2022051110 | 4 | 0.6379 | 51032 | 0.4288 | 15436.8 | 0.63157 | 7578.84 | 1 | 5000 | 15436.8 | 7578.84 | 0 | 0 | 0 | 0 | 23016.36 | 0 | 0 | 0 | 0 | 0 | 23016.36
2022051111 | 4 | 0.67954 | 54363.2 | 0.51128 | 18406.08 | 0.55101 | 6612.12 | 1 | 5000 | 18406.08 | 6612.12 | 0 | 0 | 0 | 0 | 24345 | 0 | 0 | 0 | 0 | 0 | 24345
2022051112 | 4 | 0.71398 | 57118.4 | 0.56569 | 20364.84 | 0.46209 | 5545.08 | 1 | 5000 | 20364.84 | 5545.08 | 0 | 0 | 0 | 0 | 26208.48 | 0 | 0 | 0 | 0 | 0 | 26208.48
2022051113 | 4 | 0.74787 | 59829.6 | 0.57711 | 20775.96 | 0.50181 | 6021.72 | 1 | 5000 | 20775.96 | 6021.72 | 0 | 0 | 0 | 0 | 28031.92 | 0 | 0 | 0 | 0 | 0 | 28031.92
2022051114 | 4 | 0.78695 | 62956 | 0.59226 | 21321.36 | 0.51715 | 6205.8 | 1 | 5000 | 21321.36 | 6205.8 | 0 | 0 | 0 | 0 | 30428.84 | 0 | 0 | 0 | 0 | 0 | 30428.84
2022051115 | 4 | 0.81566 | 65252.8 | 0.596 | 21456 | 0.50243 | 6029.16 | 1 | 5000 | 21456 | 6029.16 | 0 | 0 | 0 | 0 | 32767.64 | 0 | 0 | 0 | 0 | 0 | 32767.64
2022051116 | 4 | 0.83734 | 66987.2 | 0.61291 | 22064.76 | 0.50789 | 6094.68 | 1 | 5000 | 22064.76 | 6094.68 | 0 | 0 | 0 | 0 | 33827.76 | 0 | 0 | 0 | 0 | 0 | 33827.76
2022051117 | 4 | 0.85552 | 68441.6 | 0.63492 | 22857.12 | 0.46791 | 5614.92 | 1 | 5000 | 22857.12 | 5614.92 | 0 | 0 | 0 | 0 | 34969.56 | 0 | 0 | 0 | 0 | 0 | 34969.56
2022051118 | 4 | 0.85753 | 68602.4 | 0.65383 | 23537.88 | 0.40763 | 4891.56 | 1 | 5000 | 23537.88 | 4891.56 | 0 | 0 | 0 | 0 | 35172.96 | 0 | 0 | 0 | 0 | 0 | 35172.96
2022051119 | 4 | 0.83803 | 67042.4 | 0.6656 | 23961.6 | 0.32876 | 3945.12 | 1 | 5000 | 23961.6 | 3945.12 | 0 | 0 | 0 | 0 | 34135.68 | 0 | 0 | 0 | 0 | 0 | 34135.68
2022051120 | 4 | 0.80231 | 64184.8 | 0.66528 | 23950.08 | 0.13609 | 1633.08 | 1 | 5000 | 23950.08 | 1633.08 | 0 | 0 | 0 | 0 | 33601.64 | 0 | 0 | 0 | 0 | 0 | 33601.64
2022051121 | 4 | 0.77191 | 61752.8 | 0.65748 | 23669.28 | 0.00624 | 74.88 | 1 | 5000 | 23669.28 | 74.88 | 0 | 0 | 0 | 0 | 33008.64 | 0 | 0 | 0 | 0 | 0 | 33008.64
2022051122 | 4 | 0.7398 | 59184 | 0.65026 | 23409.36 | 0 | 0 | 1 | 5000 | 23409.36 | 0 | 0 | 0 | 0 | 0 | 30774.64 | 0 | 0 | 0 | 0 | 0 | 30774.64
2022051123 | 4 | 0.68851 | 55080.8 | 0.6539 | 23540.4 | 0 | 0 | 1 | 5000 | 23540.4 | 0 | 0 | 0 | 0 | 0 | 26540.4 | 0 | 0 | 0 | 0 | 0 | 26540.4
2022051124 | 4 | 0.63174 | 50539.2 | 0.64838 | 23341.68 | 0 | 0 | 1 | 5000 | 23341.68 | 0 | 0 | 0 | 0 | 0 | 22197.52 | 0 | 0 | 0 | 0 | 0 | 22197.52
2022051201 | 5 | 0.58622 | 46897.6 | 0.627 | 22572 | 0 | 0 | 1 | 5000 | 22572 | 0 | 0 | 0 | 0 | 0 | 19325.6 | 0 | 0 | 0 | 0 | 0 | 19325.6
2022051202 | 5 | 0.55336 | 44268.8 | 0.59973 | 21590.28 | 0 | 0 | 1 | 5000 | 21590.28 | 0 | 0 | 0 | 0 | 0 | 17678.52 | 0 | 0 | 0 | 0 | 0 | 17678.52
2022051203 | 5 | 0.52954 | 42363.2 | 0.58056 | 20900.16 | 0 | 0 | 1 | 5000 | 20900.16 | 0 | 0 | 0 | 0 | 0 | 16463.04 | 0 | 0 | 0 | 0 | 0 | 16463.04
2022051204 | 5 | 0.51534 | 41227.2 | 0.56975 | 20511 | 0 | 0 | 1 | 5000 | 20511 | 0 | 0 | 0 | 0 | 0 | 15716.2 | 0 | 0 | 0 | 0 | 0 | 15716.2
2022051205 | 5 | 0.511 | 40880 | 0.56278 | 20260.08 | 0 | 0 | 1 | 5000 | 20260.08 | 0 | 0 | 0 | 0 | 0 | 15619.92 | 0 | 0 | 0 | 0 | 0 | 15619.92
2022051206 | 5 | 0.52504 | 42003.2 | 0.54581 | 19649.16 | 0 | 0 | 1 | 5000 | 19649.16 | 0 | 0 | 0 | 0 | 0 | 17354.04 | 0 | 0 | 0 | 0 | 0 | 17354.04
2022051207 | 5 | 0.54656 | 43724.8 | 0.5469 | 19688.4 | 0.00172 | 20.64 | 1 | 5000 | 19688.4 | 20.64 | 0 | 0 | 0 | 0 | 19015.76 | 0 | 0 | 0 | 0 | 0 | 19015.76
2022051208 | 5 | 0.5602 | 44816 | 0.5426 | 19533.6 | 0.11766 | 1411.92 | 1 | 5000 | 19533.6 | 1411.92 | 0 | 0 | 0 | 0 | 18870.48 | 0 | 0 | 0 | 0 | 0 | 18870.48
2022051209 | 5 | 0.58519 | 46815.2 | 0.52934 | 19056.24 | 0.35733 | 4287.96 | 1 | 5000 | 19056.24 | 4287.96 | 0 | 0 | 0 | 0 | 18471 | 0 | 0 | 0 | 0 | 0 | 18471
2022051210 | 5 | 0.61785 | 49428 | 0.55087 | 19831.32 | 0.44026 | 5283.12 | 1 | 5000 | 19831.32 | 5283.12 | 0 | 0 | 0 | 0 | 19313.56 | 0 | 0 | 0 | 0 | 0 | 19313.56
2022051211 | 5 | 0.65739 | 52591.2 | 0.54388 | 19579.68 | 0.52139 | 6256.68 | 1 | 5000 | 19579.68 | 6256.68 | 0 | 0 | 0 | 0 | 21754.84 | 0 | 0 | 0 | 0 | 0 | 21754.84
2022051212 | 5 | 0.69205 | 55364 | 0.51709 | 18615.24 | 0.60727 | 7287.24 | 1 | 5000 | 18615.24 | 7287.24 | 0 | 0 | 0 | 0 | 24461.52 | 0 | 0 | 0 | 0 | 0 | 24461.52
2022051213 | 5 | 0.73157 | 58525.6 | 0.51963 | 18706.68 | 0.66013 | 7921.56 | 1 | 5000 | 18706.68 | 7921.56 | 0 | 0 | 0 | 0 | 26897.36 | 0 | 0 | 0 | 0 | 0 | 26897.36
2022051214 | 5 | 0.77059 | 61647.2 | 0.50261 | 18093.96 | 0.65784 | 7894.08 | 1 | 5000 | 18093.96 | 7894.08 | 0 | 0 | 0 | 0 | 30659.16 | 0 | 0 | 0 | 0 | 0 | 30659.16
2022051215 | 5 | 0.80266 | 64212.8 | 0.46423 | 16712.28 | 0.63128 | 7575.36 | 1 | 5000 | 16712.28 | 7575.36 | 0 | 0 | 0 | 0 | 34925.16 | 0 | 0 | 0 | 0 | 0 | 34925.16
2022051216 | 5 | 0.82881 | 66304.8 | 0.42951 | 15462.36 | 0.65394 | 7847.28 | 1 | 5000 | 15462.36 | 7847.28 | 0 | 0 | 0 | 0 | 37995.16 | 0 | 0 | 0 | 0 | 0 | 37995.16
2022051217 | 5 | 0.84833 | 67866.4 | 0.42887 | 15439.32 | 0.70805 | 8496.6 | 1 | 5000 | 15439.32 | 8496.6 | 0 | 0 | 0 | 0 | 38930.48 | 0 | 0 | 0 | 0 | 0 | 38930.48
2022051218 | 5 | 0.84924 | 67939.2 | 0.4415 | 15894 | 0.6686 | 8023.2 | 1 | 5000 | 15894 | 8023.2 | 0 | 0 | 0 | 0 | 39022 | 0 | 0 | 0 | 0 | 0 | 39022
2022051219 | 5 | 0.82817 | 66253.6 | 0.46374 | 16694.64 | 0.47352 | 5682.24 | 1 | 5000 | 16694.64 | 5682.24 | 0 | 0 | 0 | 0 | 38876.72 | 0 | 0 | 0 | 0 | 0 | 38876.72
2022051220 | 5 | 0.79233 | 63386.4 | 0.49871 | 17953.56 | 0.16647 | 1997.64 | 1 | 5000 | 17953.56 | 1997.64 | 0 | 0 | 0 | 0 | 38435.2 | 0 | 0 | 0 | 0 | 0 | 38435.2
2022051221 | 5 | 0.76204 | 60963.2 | 0.50107 | 18038.52 | 0.0193 | 231.6 | 1 | 5000 | 18038.52 | 231.6 | 0 | 0 | 0 | 0 | 37693.08 | 0 | 0 | 0 | 0 | 0 | 37693.08
2022051222 | 5 | 0.73017 | 58413.6 | 0.56162 | 20218.32 | 0 | 0 | 1 | 5000 | 20218.32 | 0 | 0 | 0 | 0 | 0 | 33195.28 | 0 | 0 | 0 | 0 | 0 | 33195.28
2022051223 | 5 | 0.68301 | 54640.8 | 0.62881 | 22637.16 | 0 | 0 | 1 | 5000 | 22637.16 | 0 | 0 | 0 | 0 | 0 | 27003.64 | 0 | 0 | 0 | 0 | 0 | 27003.64
2022051224 | 5 | 0.62853 | 50282.4 | 0.63756 | 22952.16 | 0 | 0 | 1 | 5000 | 22952.16 | 0 | 0 | 0 | 0 | 0 | 22330.24 | 0 | 0 | 0 | 0 | 0 | 22330.24
2022051301 | 6 | 0.58207 | 46565.6 | 0.61166 | 22019.76 | 0 | 0 | 1 | 5000 | 22019.76 | 0 | 0 | 0 | 0 | 0 | 19545.84 | 0 | 0 | 0 | 0 | 0 | 19545.84
2022051302 | 6 | 0.54902 | 43921.6 | 0.58694 | 21129.84 | 0 | 0 | 1 | 5000 | 21129.84 | 0 | 0 | 0 | 0 | 0 | 17791.76 | 0 | 0 | 0 | 0 | 0 | 17791.76
2022051303 | 6 | 0.52512 | 42009.6 | 0.56598 | 20375.28 | 0 | 0 | 1 | 5000 | 20375.28 | 0 | 0 | 0 | 0 | 0 | 16634.32 | 0 | 0 | 0 | 0 | 0 | 16634.32
2022051304 | 6 | 0.50944 | 40755.2 | 0.5168 | 18604.8 | 0 | 0 | 1 | 5000 | 18604.8 | 0 | 0 | 0 | 0 | 0 | 17150.4 | 0 | 0 | 0 | 0 | 0 | 17150.4
2022051305 | 6 | 0.50541 | 40432.8 | 0.48793 | 17565.48 | 0 | 0 | 1 | 5000 | 17565.48 | 0 | 0 | 0 | 0 | 0 | 17867.32 | 0 | 0 | 0 | 0 | 0 | 17867.32
2022051306 | 6 | 0.51947 | 41557.6 | 0.47928 | 17254.08 | 0 | 0 | 1 | 5000 | 17254.08 | 0 | 0 | 0 | 0 | 0 | 19303.52 | 0 | 0 | 0 | 0 | 0 | 19303.52
2022051307 | 6 | 0.53963 | 43170.4 | 0.46199 | 16631.64 | 0.00228 | 27.36 | 1 | 5000 | 16631.64 | 27.36 | 0 | 0 | 0 | 0 | 21511.4 | 0 | 0 | 0 | 0 | 0 | 21511.4
2022051308 | 6 | 0.55682 | 44545.6 | 0.45637 | 16429.32 | 0.1548 | 1857.6 | 1 | 5000 | 16429.32 | 1857.6 | 0 | 0 | 0 | 0 | 21258.68 | 0 | 0 | 0 | 0 | 0 | 21258.68
2022051309 | 6 | 0.58191 | 46552.8 | 0.3879 | 13964.4 | 0.55405 | 6648.6 | 1 | 5000 | 13964.4 | 6648.6 | 0 | 0 | 0 | 0 | 20939.8 | 0 | 0 | 0 | 0 | 0 | 20939.8
2022051310 | 6 | 0.61433 | 49146.4 | 0.36166 | 13019.76 | 0.70868 | 8504.16 | 1 | 5000 | 13019.76 | 8504.16 | 0 | 0 | 0 | 0 | 22622.48 | 0 | 0 | 0 | 0 | 0 | 22622.48
2022051311 | 6 | 0.65187 | 52149.6 | 0.27964 | 10067.04 | 0.70311 | 8437.32 | 1 | 5000 | 10067.04 | 8437.32 | 0 | 0 | 0 | 0 | 28645.24 | 0 | 0 | 0 | 0 | 0 | 28645.24
2022051312 | 6 | 0.68882 | 55105.6 | 0.21556 | 7760.16 | 0.64867 | 7784.04 | 1 | 5000 | 7760.16 | 7784.04 | 0 | 0 | 0 | 0 | 34561.4 | 0 | 0 | 0 | 0 | 0 | 34561.4
2022051313 | 6 | 0.72504 | 58003.2 | 0.16404 | 5905.44 | 0.72547 | 8705.64 | 1 | 5000 | 5905.44 | 8705.64 | 0 | 0 | 0 | 0 | 38392.12 | 0 | 0 | 0 | 0 | 0 | 38392.12
2022051314 | 6 | 0.76149 | 60919.2 | 0.13811 | 4971.96 | 0.74635 | 8956.2 | 1 | 5000 | 4971.96 | 8956.2 | 0 | 0 | 0 | 0 | 41991.04 | 0 | 0 | 0 | 0 | 0 | 41991.04
2022051315 | 6 | 0.78305 | 62644 | 0.12405 | 4465.8 | 0.7379 | 8854.8 | 1 | 5000 | 4465.8 | 8854.8 | 0 | 0 | 0 | 0 | 44323.4 | 0 | 0 | 0 | 0 | 0 | 44323.4
2022051316 | 6 | 0.80469 | 64375.2 | 0.13573 | 4886.28 | 0.7336 | 8803.2 | 1 | 5000 | 4886.28 | 8803.2 | 0 | 0 | 0 | 0 | 45685.72 | 0 | 0 | 0 | 0 | 0 | 45685.72
2022051317 | 6 | 0.81659 | 65327.2 | 0.15714 | 5657.04 | 0.72784 | 8734.08 | 1 | 5000 | 5657.04 | 8734.08 | 0 | 0 | 0 | 0 | 45936.08 | 0 | 0 | 0 | 0 | 0 | 45936.08
2022051318 | 6 | 0.81413 | 65130.4 | 0.17562 | 6322.32 | 0.65294 | 7835.28 | 1 | 5000 | 6322.32 | 7835.28 | 0 | 0 | 0 | 0 | 45972.8 | 0 | 0 | 0 | 0 | 0 | 45972.8
2022051319 | 6 | 0.7973 | 63784 | 0.22954 | 8263.44 | 0.53419 | 6410.28 | 1 | 5000 | 8263.44 | 6410.28 | 0 | 0 | 0 | 0 | 44110.28 | 0 | 0 | 0 | 0 | 0 | 44110.28
2022051320 | 6 | 0.76568 | 61254.4 | 0.29646 | 10672.56 | 0.25795 | 3095.4 | 1 | 5000 | 10672.56 | 3095.4 | 0 | 0 | 0 | 0 | 42486.44 | 0 | 0 | 0 | 0 | 0 | 42486.44
2022051321 | 6 | 0.73901 | 59120.8 | 0.32137 | 11569.32 | 0.01781 | 213.72 | 1 | 5000 | 11569.32 | 213.72 | 0 | 0 | 0 | 0 | 42337.76 | 0 | 0 | 0 | 0 | 0 | 42337.76
2022051322 | 6 | 0.71028 | 56822.4 | 0.3263 | 11746.8 | 0 | 0 | 1 | 5000 | 11746.8 | 0 | 0 | 0 | 0 | 0 | 40075.6 | 0 | 0 | 0 | 0 | 0 | 40075.6
2022051323 | 6 | 0.67175 | 53740 | 0.40729 | 14662.44 | 0 | 0 | 1 | 5000 | 14662.44 | 0 | 0 | 0 | 0 | 0 | 34077.56 | 0 | 0 | 0 | 0 | 0 | 34077.56
2022051324 | 6 | 0.6282 | 50256 | 0.45446 | 16360.56 | 0 | 0 | 1 | 5000 | 16360.56 | 0 | 0 | 0 | 0 | 0 | 28895.44 | 0 | 0 | 0 | 0 | 0 | 28895.44
2022051401 | 7 | 0.58914 | 47131.2 | 0.44522 | 16027.92 | 0 | 0 | 1 | 5000 | 16027.92 | 0 | 0 | 0 | 0 | 0 | 26103.28 | 0 | 0 | 0 | 0 | 0 | 26103.28
2022051402 | 7 | 0.55596 | 44476.8 | 0.46896 | 16882.56 | 0 | 0 | 1 | 5000 | 16882.56 | 0 | 0 | 0 | 0 | 0 | 22594.24 | 0 | 0 | 0 | 0 | 0 | 22594.24
2022051403 | 7 | 0.5307 | 42456 | 0.4793 | 17254.8 | 0 | 0 | 1 | 5000 | 17254.8 | 0 | 0 | 0 | 0 | 0 | 20201.2 | 0 | 0 | 0 | 0 | 0 | 20201.2
2022051404 | 7 | 0.5088 | 40704 | 0.45334 | 16320.24 | 0 | 0 | 1 | 5000 | 16320.24 | 0 | 0 | 0 | 0 | 0 | 19383.76 | 0 | 0 | 0 | 0 | 0 | 19383.76
2022051405 | 7 | 0.4963 | 39704 | 0.41916 | 15089.76 | 0 | 0 | 1 | 5000 | 15089.76 | 0 | 0 | 0 | 0 | 0 | 19614.24 | 0 | 0 | 0 | 0 | 0 | 19614.24
2022051406 | 7 | 0.49331 | 39464.8 | 0.36225 | 13041 | 0 | 0 | 1 | 5000 | 13041 | 0 | 0 | 0 | 0 | 0 | 21423.8 | 0 | 0 | 0 | 0 | 0 | 21423.8
2022051407 | 7 | 0.4963 | 39704 | 0.30588 | 11011.68 | 0.00183 | 21.96 | 1 | 5000 | 11011.68 | 21.96 | 0 | 0 | 0 | 0 | 23670.36 | 0 | 0 | 0 | 0 | 0 | 23670.36
2022051408 | 7 | 0.51043 | 40834.4 | 0.27489 | 9896.04 | 0.1396 | 1675.2 | 1 | 5000 | 9896.04 | 1675.2 | 0 | 0 | 0 | 0 | 24263.16 | 0 | 0 | 0 | 0 | 0 | 24263.16
2022051409 | 7 | 0.54652 | 43721.6 | 0.24458 | 8804.88 | 0.55521 | 6662.52 | 1 | 5000 | 8804.88 | 6662.52 | 0 | 0 | 0 | 0 | 23254.2 | 0 | 0 | 0 | 0 | 0 | 23254.2
2022051410 | 7 | 0.59412 | 47529.6 | 0.29595 | 10654.2 | 0.72534 | 8704.08 | 1 | 5000 | 10654.2 | 8704.08 | 0 | 0 | 0 | 0 | 23171.32 | 0 | 0 | 0 | 0 | 0 | 23171.32
2022051411 | 7 | 0.63584 | 50867.2 | 0.2666 | 9597.6 | 0.77635 | 9316.2 | 1 | 5000 | 9597.6 | 9316.2 | 0 | 0 | 0 | 0 | 26953.4 | 0 | 0 | 0 | 0 | 0 | 26953.4
2022051412 | 7 | 0.67715 | 54172 | 0.18178 | 6544.08 | 0.80042 | 9605.04 | 1 | 5000 | 6544.08 | 9605.04 | 0 | 0 | 0 | 0 | 33022.88 | 0 | 0 | 0 | 0 | 0 | 33022.88
2022051413 | 7 | 0.71748 | 57398.4 | 0.114 | 4104 | 0.7934 | 9520.8 | 1 | 5000 | 4104 | 9520.8 | 0 | 0 | 0 | 0 | 38773.6 | 0 | 0 | 0 | 0 | 0 | 38773.6
2022051414 | 7 | 0.75186 | 60148.8 | 0.09818 | 3534.48 | 0.78859 | 9463.08 | 1 | 5000 | 3534.48 | 9463.08 | 0 | 0 | 0 | 0 | 42151.24 | 0 | 0 | 0 | 0 | 0 | 42151.24
2022051415 | 7 | 0.78589 | 62871.2 | 0.10856 | 3908.16 | 0.77819 | 9338.28 | 1 | 5000 | 3908.16 | 9338.28 | 0 | 0 | 0 | 0 | 44624.76 | 0 | 0 | 0 | 0 | 0 | 44624.76
2022051416 | 7 | 0.81024 | 64819.2 | 0.13964 | 5027.04 | 0.74397 | 8927.64 | 1 | 5000 | 5027.04 | 8927.64 | 0 | 0 | 0 | 0 | 45864.52 | 0 | 0 | 0 | 0 | 0 | 45864.52
2022051417 | 7 | 0.82576 | 66060.8 | 0.19966 | 7187.76 | 0.70101 | 8412.12 | 1 | 5000 | 7187.76 | 8412.12 | 0 | 0 | 0 | 0 | 45460.92 | 0 | 0 | 0 | 0 | 0 | 45460.92
2022051418 | 7 | 0.82639 | 66111.2 | 0.26496 | 9538.56 | 0.65468 | 7856.16 | 1 | 5000 | 9538.56 | 7856.16 | 0 | 0 | 0 | 0 | 43716.48 | 0 | 0 | 0 | 0 | 0 | 43716.48
2022051419 | 7 | 0.80883 | 64706.4 | 0.30754 | 11071.44 | 0.5719 | 6862.8 | 1 | 5000 | 11071.44 | 6862.8 | 0 | 0 | 0 | 0 | 41772.16 | 0 | 0 | 0 | 0 | 0 | 41772.16
2022051420 | 7 | 0.77408 | 61926.4 | 0.34041 | 12254.76 | 0.26937 | 3232.44 | 1 | 5000 | 12254.76 | 3232.44 | 0 | 0 | 0 | 0 | 41439.2 | 0 | 0 | 0 | 0 | 0 | 41439.2
2022051421 | 7 | 0.74344 | 59475.2 | 0.38464 | 13847.04 | 0.01761 | 211.32 | 1 | 5000 | 13847.04 | 211.32 | 0 | 0 | 0 | 0 | 40416.84 | 0 | 0 | 0 | 0 | 0 | 40416.84
2022051422 | 7 | 0.71442 | 57153.6 | 0.45366 | 16331.76 | 0 | 0 | 1 | 5000 | 16331.76 | 0 | 0 | 0 | 0 | 0 | 35821.84 | 0 | 0 | 0 | 0 | 0 | 35821.84
2022051423 | 7 | 0.67404 | 53923.2 | 0.52619 | 18942.84 | 0 | 0 | 1 | 5000 | 18942.84 | 0 | 0 | 0 | 0 | 0 | 29980.36 | 0 | 0 | 0 | 0 | 0 | 29980.36
2022051424 | 7 | 0.63312 | 50649.6 | 0.57319 | 20634.84 | 0 | 0 | 1 | 5000 | 20634.84 | 0 | 0 | 0 | 0 | 0 | 25014.76 | 0 | 0 | 0 | 0 | 0 | 25014.76
2022051501 | 1 | 0.59489 | 47591.2 | 0.58689 | 21128.04 | 0 | 0 | 1 | 5000 | 21128.04 | 0 | 0 | 0 | 0 | 0 | 21463.16 | 0 | 0 | 0 | 0 | 0 | 21463.16
2022051502 | 1 | 0.56109 | 44887.2 | 0.57651 | 20754.36 | 0 | 0 | 1 | 5000 | 20754.36 | 0 | 0 | 0 | 0 | 0 | 19132.84 | 0 | 0 | 0 | 0 | 0 | 19132.84
2022051503 | 1 | 0.53269 | 42615.2 | 0.52804 | 19009.44 | 0 | 0 | 1 | 5000 | 19009.44 | 0 | 0 | 0 | 0 | 0 | 18605.76 | 0 | 0 | 0 | 0 | 0 | 18605.76
2022051504 | 1 | 0.51246 | 40996.8 | 0.49048 | 17657.28 | 0 | 0 | 1 | 5000 | 17657.28 | 0 | 0 | 0 | 0 | 0 | 18339.52 | 0 | 0 | 0 | 0 | 0 | 18339.52
2022051505 | 1 | 0.49789 | 39831.2 | 0.46581 | 16769.16 | 0 | 0 | 1 | 5000 | 16769.16 | 0 | 0 | 0 | 0 | 0 | 18062.04 | 0 | 0 | 0 | 0 | 0 | 18062.04
2022051506 | 1 | 0.49216 | 39372.8 | 0.46146 | 16612.56 | 0 | 0 | 1 | 5000 | 16612.56 | 0 | 0 | 0 | 0 | 0 | 17760.24 | 0 | 0 | 0 | 0 | 0 | 17760.24
2022051507 | 1 | 0.48578 | 38862.4 | 0.44496 | 16018.56 | 0.00022 | 2.64 | 1 | 5000 | 16018.56 | 2.64 | 0 | 0 | 0 | 0 | 17841.2 | 0 | 0 | 0 | 0 | 0 | 17841.2
2022051508 | 1 | 0.49176 | 39340.8 | 0.44082 | 15869.52 | 0.06384 | 766.08 | 1 | 5000 | 15869.52 | 766.08 | 0 | 0 | 0 | 0 | 17705.2 | 0 | 0 | 0 | 0 | 0 | 17705.2
2022051509 | 1 | 0.53014 | 42411.2 | 0.37638 | 13549.68 | 0.48965 | 5875.8 | 1 | 5000 | 13549.68 | 5875.8 | 0 | 0 | 0 | 0 | 17985.72 | 0 | 0 | 0 | 0 | 0 | 17985.72
2022051510 | 1 | 0.5791 | 46328 | 0.35983 | 12953.88 | 0.71694 | 8603.28 | 1 | 5000 | 12953.88 | 8603.28 | 0 | 0 | 0 | 0 | 19770.84 | 0 | 0 | 0 | 0 | 0 | 19770.84
2022051511 | 1 | 0.6281 | 50248 | 0.35342 | 12723.12 | 0.78042 | 9365.04 | 1 | 5000 | 12723.12 | 9365.04 | 0 | 0 | 0 | 0 | 23159.84 | 0 | 0 | 0 | 0 | 0 | 23159.84
2022051512 | 1 | 0.68121 | 54496.8 | 0.35977 | 12951.72 | 0.7967 | 9560.4 | 1 | 5000 | 12951.72 | 9560.4 | 0 | 0 | 0 | 0 | 26984.68 | 0 | 0 | 0 | 0 | 0 | 26984.68
2022051513 | 1 | 0.73299 | 58639.2 | 0.35119 | 12642.84 | 0.80261 | 9631.32 | 1 | 5000 | 12642.84 | 9631.32 | 0 | 0 | 0 | 0 | 31365.04 | 0 | 0 | 0 | 0 | 0 | 31365.04
2022051514 | 1 | 0.77768 | 62214.4 | 0.33434 | 12036.24 | 0.80628 | 9675.36 | 1 | 5000 | 12036.24 | 9675.36 | 0 | 0 | 0 | 0 | 35502.8 | 0 | 0 | 0 | 0 | 0 | 35502.8
2022051515 | 1 | 0.80888 | 64710.4 | 0.31501 | 11340.36 | 0.79836 | 9580.32 | 1 | 5000 | 11340.36 | 9580.32 | 0 | 0 | 0 | 0 | 38789.72 | 0 | 0 | 0 | 0 | 0 | 38789.72
2022051516 | 1 | 0.83445 | 66756 | 0.30094 | 10833.84 | 0.77935 | 9352.2 | 1 | 5000 | 10833.84 | 9352.2 | 0 | 0 | 0 | 0 | 41569.96 | 0 | 0 | 0 | 0 | 0 | 41569.96
2022051517 | 1 | 0.85305 | 68244 | 0.29635 | 10668.6 | 0.75049 | 9005.88 | 1 | 5000 | 10668.6 | 9005.88 | 0 | 0 | 0 | 0 | 43569.52 | 0 | 0 | 0 | 0 | 0 | 43569.52
2022051518 | 1 | 0.85896 | 68716.8 | 0.32036 | 11532.96 | 0.71331 | 8559.72 | 1 | 5000 | 11532.96 | 8559.72 | 0 | 0 | 0 | 0 | 43624.12 | 0 | 0 | 0 | 0 | 0 | 43624.12
2022051519 | 1 | 0.84699 | 67759.2 | 0.37409 | 13467.24 | 0.6016 | 7219.2 | 1 | 5000 | 13467.24 | 7219.2 | 0 | 0 | 0 | 0 | 42072.76 | 0 | 0 | 0 | 0 | 0 | 42072.76
2022051520 | 1 | 0.8152 | 65216 | 0.44175 | 15903 | 0.27518 | 3302.16 | 1 | 5000 | 15903 | 3302.16 | 0 | 0 | 0 | 0 | 41010.84 | 0 | 0 | 0 | 0 | 0 | 41010.84
2022051521 | 1 | 0.78357 | 62685.6 | 0.51029 | 18370.44 | 0.01819 | 218.28 | 1 | 5000 | 18370.44 | 218.28 | 0 | 0 | 0 | 0 | 39096.88 | 0 | 0 | 0 | 0 | 0 | 39096.88
2022051522 | 1 | 0.75583 | 60466.4 | 0.57972 | 20869.92 | 0 | 0 | 1 | 5000 | 20869.92 | 0 | 0 | 0 | 0 | 0 | 34596.48 | 0 | 0 | 0 | 0 | 0 | 34596.48
2022051523 | 1 | 0.70111 | 56088.8 | 0.58581 | 21089.16 | 0 | 0 | 1 | 5000 | 21089.16 | 0 | 0 | 0 | 0 | 0 | 29999.64 | 0 | 0 | 0 | 0 | 0 | 29999.64
2022051524 | 1 | 0.63956 | 51164.8 | 0.59364 | 21371.04 | 0 | 0 | 1 | 5000 | 21371.04 | 0 | 0 | 0 | 0 | 0 | 24793.76 | 0 | 0 | 0 | 0 | 0 | 24793.76
2022051601 | 2 | 0.58794 | 47035.2 | 0.57072 | 20545.92 | 0 | 0 | 1 | 5000 | 20545.92 | 0 | 0 | 0 | 0 | 0 | 21489.28 | 0 | 0 | 0 | 0 | 0 | 21489.28
2022051602 | 2 | 0.55197 | 44157.6 | 0.494 | 17784 | 0 | 0 | 1 | 5000 | 17784 | 0 | 0 | 0 | 0 | 0 | 21373.6 | 0 | 0 | 0 | 0 | 0 | 21373.6
2022051603 | 2 | 0.52807 | 42245.6 | 0.40929 | 14734.44 | 0 | 0 | 1 | 5000 | 14734.44 | 0 | 0 | 0 | 0 | 0 | 22511.16 | 0 | 0 | 0 | 0 | 0 | 22511.16
2022051604 | 2 | 0.51572 | 41257.6 | 0.36542 | 13155.12 | 0 | 0 | 1 | 5000 | 13155.12 | 0 | 0 | 0 | 0 | 0 | 23102.48 | 0 | 0 | 0 | 0 | 0 | 23102.48
2022051605 | 2 | 0.51334 | 41067.2 | 0.35677 | 12843.72 | 0 | 0 | 1 | 5000 | 12843.72 | 0 | 0 | 0 | 0 | 0 | 23223.48 | 0 | 0 | 0 | 0 | 0 | 23223.48
2022051606 | 2 | 0.52491 | 41992.8 | 0.32249 | 11609.64 | 0 | 0 | 1 | 5000 | 11609.64 | 0 | 0 | 0 | 0 | 0 | 25383.16 | 0 | 0 | 0 | 0 | 0 | 25383.16
2022051607 | 2 | 0.55133 | 44106.4 | 0.29822 | 10735.92 | 0.00116 | 13.92 | 1 | 5000 | 10735.92 | 13.92 | 0 | 0 | 0 | 0 | 28356.56 | 0 | 0 | 0 | 0 | 0 | 28356.56
2022051608 | 2 | 0.56216 | 44972.8 | 0.28144 | 10131.84 | 0.11602 | 1392.24 | 1 | 5000 | 10131.84 | 1392.24 | 0 | 0 | 0 | 0 | 28448.72 | 0 | 0 | 0 | 0 | 0 | 28448.72
2022051609 | 2 | 0.5878 | 47024 | 0.23254 | 8371.44 | 0.49823 | 5978.76 | 1 | 5000 | 8371.44 | 5978.76 | 0 | 0 | 0 | 0 | 27673.8 | 0 | 0 | 0 | 0 | 0 | 27673.8
2022051610 | 2 | 0.62508 | 50006.4 | 0.20148 | 7253.28 | 0.7137 | 8564.4 | 1 | 5000 | 7253.28 | 8564.4 | 0 | 0 | 0 | 0 | 29188.72 | 0 | 0 | 0 | 0 | 0 | 29188.72
2022051611 | 2 | 0.66372 | 53097.6 | 0.16729 | 6022.44 | 0.75289 | 9034.68 | 1 | 5000 | 6022.44 | 9034.68 | 0 | 0 | 0 | 0 | 33040.48 | 0 | 0 | 0 | 0 | 0 | 33040.48
2022051612 | 2 | 0.70692 | 56553.6 | 0.17008 | 6122.88 | 0.78429 | 9411.48 | 1 | 5000 | 6122.88 | 9411.48 | 0 | 0 | 0 | 0 | 36019.24 | 0 | 0 | 0 | 0 | 0 | 36019.24
2022051613 | 2 | 0.7504 | 60032 | 0.18785 | 6762.6 | 0.80143 | 9617.16 | 1 | 5000 | 6762.6 | 9617.16 | 0 | 0 | 0 | 0 | 38652.24 | 0 | 0 | 0 | 0 | 0 | 38652.24
2022051614 | 2 | 0.79285 | 63428 | 0.19773 | 7118.28 | 0.7871 | 9445.2 | 1 | 5000 | 7118.28 | 9445.2 | 0 | 0 | 0 | 0 | 41864.52 | 0 | 0 | 0 | 0 | 0 | 41864.52
2022051615 | 2 | 0.83115 | 66492 | 0.24315 | 8753.4 | 0.77038 | 9244.56 | 1 | 5000 | 8753.4 | 9244.56 | 0 | 0 | 0 | 0 | 43494.04 | 0 | 0 | 0 | 0 | 0 | 43494.04
2022051616 | 2 | 0.85992 | 68793.6 | 0.28672 | 10321.92 | 0.72786 | 8734.32 | 1 | 5000 | 10321.92 | 8734.32 | 0 | 0 | 0 | 0 | 44737.36 | 0 | 0 | 0 | 0 | 0 | 44737.36
2022051617 | 2 | 0.8792 | 70336 | 0.33713 | 12136.68 | 0.67804 | 8136.48 | 1 | 5000 | 12136.68 | 8136.48 | 0 | 0 | 0 | 0 | 45062.84 | 0 | 0 | 0 | 0 | 0 | 45062.84
2022051618 | 2 | 0.88041 | 70432.8 | 0.39193 | 14109.48 | 0.58273 | 6992.76 | 1 | 5000 | 14109.48 | 6992.76 | 0 | 0 | 0 | 0 | 44330.56 | 0 | 0 | 0 | 0 | 0 | 44330.56
2022051619 | 2 | 0.86091 | 68872.8 | 0.44216 | 15917.76 | 0.38484 | 4618.08 | 1 | 5000 | 15917.76 | 4618.08 | 0 | 0 | 0 | 0 | 43336.96 | 0 | 0 | 0 | 0 | 0 | 43336.96
2022051620 | 2 | 0.82593 | 66074.4 | 0.5052 | 18187.2 | 0.17014 | 2041.68 | 1 | 5000 | 18187.2 | 2041.68 | 0 | 0 | 0 | 0 | 40845.52 | 0 | 0 | 0 | 0 | 0 | 40845.52
2022051621 | 2 | 0.79438 | 63550.4 | 0.53918 | 19410.48 | 0.01 | 120 | 1 | 5000 | 19410.48 | 120 | 0 | 0 | 0 | 0 | 39019.92 | 0 | 0 | 0 | 0 | 0 | 39019.92
2022051622 | 2 | 0.76109 | 60887.2 | 0.5763 | 20746.8 | 0 | 0 | 1 | 5000 | 20746.8 | 0 | 0 | 0 | 0 | 0 | 35140.4 | 0 | 0 | 0 | 0 | 0 | 35140.4
2022051623 | 2 | 0.70628 | 56502.4 | 0.55867 | 20112.12 | 0 | 0 | 1 | 5000 | 20112.12 | 0 | 0 | 0 | 0 | 0 | 31390.28 | 0 | 0 | 0 | 0 | 0 | 31390.28
2022051624 | 2 | 0.65179 | 52143.2 | 0.55349 | 19925.64 | 0 | 0 | 1 | 5000 | 19925.64 | 0 | 0 | 0 | 0 | 0 | 27217.56 | 0 | 0 | 0 | 0 | 0 | 27217.56
2022051701 | 3 | 0.60411 | 48328.8 | 0.54472 | 19609.92 | 0 | 0 | 1 | 5000 | 19609.92 | 0 | 0 | 0 | 0 | 0 | 23718.88 | 0 | 0 | 0 | 0 | 0 | 23718.88
2022051702 | 3 | 0.56788 | 45430.4 | 0.47712 | 17176.32 | 0 | 0 | 1 | 5000 | 17176.32 | 0 | 0 | 0 | 0 | 0 | 23254.08 | 0 | 0 | 0 | 0 | 0 | 23254.08
2022051703 | 3 | 0.54224 | 43379.2 | 0.4443 | 15994.8 | 0 | 0 | 1 | 5000 | 15994.8 | 0 | 0 | 0 | 0 | 0 | 22384.4 | 0 | 0 | 0 | 0 | 0 | 22384.4
2022051704 | 3 | 0.53087 | 42469.6 | 0.45512 | 16384.32 | 0 | 0 | 1 | 5000 | 16384.32 | 0 | 0 | 0 | 0 | 0 | 21085.28 | 0 | 0 | 0 | 0 | 0 | 21085.28
2022051705 | 3 | 0.53009 | 42407.2 | 0.50731 | 18263.16 | 0 | 0 | 1 | 5000 | 18263.16 | 0 | 0 | 0 | 0 | 0 | 19144.04 | 0 | 0 | 0 | 0 | 0 | 19144.04
2022051706 | 3 | 0.54697 | 43757.6 | 0.51298 | 18467.28 | 0 | 0 | 1 | 5000 | 18467.28 | 0 | 0 | 0 | 0 | 0 | 20290.32 | 0 | 0 | 0 | 0 | 0 | 20290.32
2022051707 | 3 | 0.5697 | 45576 | 0.50282 | 18101.52 | 0.00109 | 13.08 | 1 | 5000 | 18101.52 | 13.08 | 0 | 0 | 0 | 0 | 22461.4 | 0 | 0 | 0 | 0 | 0 | 22461.4
2022051708 | 3 | 0.58211 | 46568.8 | 0.50627 | 18225.72 | 0.07333 | 879.96 | 1 | 5000 | 18225.72 | 879.96 | 0 | 0 | 0 | 0 | 22463.12 | 0 | 0 | 0 | 0 | 0 | 22463.12
2022051709 | 3 | 0.60636 | 48508.8 | 0.52834 | 19020.24 | 0.31403 | 3768.36 | 1 | 5000 | 19020.24 | 3768.36 | 0 | 0 | 0 | 0 | 20720.2 | 0 | 0 | 0 | 0 | 0 | 20720.2
2022051710 | 3 | 0.64488 | 51590.4 | 0.60472 | 21769.92 | 0.41759 | 5011.08 | 1 | 5000 | 21769.92 | 5011.08 | 0 | 0 | 0 | 0 | 19809.4 | 0 | 0 | 0 | 0 | 0 | 19809.4
2022051711 | 3 | 0.68126 | 54500.8 | 0.61836 | 22260.96 | 0.42842 | 5141.04 | 1 | 5000 | 22260.96 | 5141.04 | 0 | 0 | 0 | 0 | 22098.8 | 0 | 0 | 0 | 0 | 0 | 22098.8
2022051712 | 3 | 0.7272 | 58176 | 0.61716 | 22217.76 | 0.48404 | 5808.48 | 1 | 5000 | 22217.76 | 5808.48 | 0 | 0 | 0 | 0 | 25149.76 | 0 | 0 | 0 | 0 | 0 | 25149.76
2022051713 | 3 | 0.76985 | 61588 | 0.63628 | 22906.08 | 0.44922 | 5390.64 | 1 | 5000 | 22906.08 | 5390.64 | 0 | 0 | 0 | 0 | 28291.28 | 0 | 0 | 0 | 0 | 0 | 28291.28
2022051714 | 3 | 0.80929 | 64743.2 | 0.66329 | 23878.44 | 0.43891 | 5266.92 | 1 | 5000 | 23878.44 | 5266.92 | 0 | 0 | 0 | 0 | 30597.84 | 0 | 0 | 0 | 0 | 0 | 30597.84
2022051715 | 3 | 0.84191 | 67352.8 | 0.67658 | 24356.88 | 0.4554 | 5464.8 | 1 | 5000 | 24356.88 | 5464.8 | 0 | 0 | 0 | 0 | 32531.12 | 0 | 0 | 0 | 0 | 0 | 32531.12
2022051716 | 3 | 0.87061 | 69648.8 | 0.66552 | 23958.72 | 0.49798 | 5975.76 | 1 | 5000 | 23958.72 | 5975.76 | 0 | 0 | 0 | 0 | 34714.32 | 0 | 0 | 0 | 0 | 0 | 34714.32
2022051717 | 3 | 0.88708 | 70966.4 | 0.64638 | 23269.68 | 0.52748 | 6329.76 | 1 | 5000 | 23269.68 | 6329.76 | 0 | 0 | 0 | 0 | 36366.96 | 0 | 0 | 0 | 0 | 0 | 36366.96
2022051718 | 3 | 0.88328 | 70662.4 | 0.65387 | 23539.32 | 0.47795 | 5735.4 | 1 | 5000 | 23539.32 | 5735.4 | 0 | 0 | 0 | 0 | 36387.68 | 0 | 0 | 0 | 0 | 0 | 36387.68
2022051719 | 3 | 0.86032 | 68825.6 | 0.65933 | 23735.88 | 0.40844 | 4901.28 | 1 | 5000 | 23735.88 | 4901.28 | 0 | 0 | 0 | 0 | 35188.44 | 0 | 0 | 0 | 0 | 0 | 35188.44
2022051720 | 3 | 0.82469 | 65975.2 | 0.66018 | 23766.48 | 0.23175 | 2781 | 1 | 5000 | 23766.48 | 2781 | 0 | 0 | 0 | 0 | 34427.72 | 0 | 0 | 0 | 0 | 0 | 34427.72
2022051721 | 3 | 0.79625 | 63700 | 0.67027 | 24129.72 | 0.01883 | 225.96 | 1 | 5000 | 24129.72 | 225.96 | 0 | 0 | 0 | 0 | 34344.32 | 0 | 0 | 0 | 0 | 0 | 34344.32
2022051722 | 3 | 0.76601 | 61280.8 | 0.675 | 24300 | 0 | 0 | 1 | 5000 | 24300 | 0 | 0 | 0 | 0 | 0 | 31980.8 | 0 | 0 | 0 | 0 | 0 | 31980.8
2022051723 | 3 | 0.71475 | 57180 | 0.67581 | 24329.16 | 0 | 0 | 1 | 5000 | 24329.16 | 0 | 0 | 0 | 0 | 0 | 27850.84 | 0 | 0 | 0 | 0 | 0 | 27850.84
2022051724 | 3 | 0.66082 | 52865.6 | 0.68644 | 24711.84 | 0 | 0 | 1 | 5000 | 24711.84 | 0 | 0 | 0 | 0 | 0 | 23153.76 | 0 | 0 | 0 | 0 | 0 | 23153.76
2022051801 | 4 | 0.61711 | 49368.8 | 0.67974 | 24470.64 | 0 | 0 | 1 | 5000 | 24470.64 | 0 | 0 | 0 | 0 | 0 | 19898.16 | 0 | 0 | 0 | 0 | 0 | 19898.16
2022051802 | 4 | 0.58805 | 47044 | 0.68352 | 24606.72 | 0 | 0 | 1 | 5000 | 24606.72 | 0 | 0 | 0 | 0 | 0 | 17437.28 | 0 | 0 | 0 | 0 | 0 | 17437.28
2022051803 | 4 | 0.56488 | 45190.4 | 0.66876 | 24075.36 | 0 | 0 | 1 | 5000 | 24075.36 | 0 | 0 | 0 | 0 | 0 | 16115.04 | 0 | 0 | 0 | 0 | 0 | 16115.04
2022051804 | 4 | 0.55077 | 44061.6 | 0.65131 | 23447.16 | 0 | 0 | 1 | 5000 | 23447.16 | 0 | 0 | 0 | 0 | 0 | 15614.44 | 0 | 0 | 0 | 0 | 0 | 15614.44
2022051805 | 4 | 0.54718 | 43774.4 | 0.61999 | 22319.64 | 0 | 0 | 1 | 5000 | 22319.64 | 0 | 0 | 0 | 0 | 0 | 16454.76 | 0 | 0 | 0 | 0 | 0 | 16454.76
2022051806 | 4 | 0.56097 | 44877.6 | 0.59734 | 21504.24 | 0 | 0 | 1 | 5000 | 21504.24 | 0 | 0 | 0 | 0 | 0 | 18373.36 | 0 | 0 | 0 | 0 | 0 | 18373.36
2022051807 | 4 | 0.58068 | 46454.4 | 0.58136 | 20928.96 | 0.00185 | 22.2 | 1 | 5000 | 20928.96 | 22.2 | 0 | 0 | 0 | 0 | 20503.24 | 0 | 0 | 0 | 0 | 0 | 20503.24
2022051808 | 4 | 0.59215 | 47372 | 0.55873 | 20114.28 | 0.13616 | 1633.92 | 1 | 5000 | 20114.28 | 1633.92 | 0 | 0 | 0 | 0 | 20623.8 | 0 | 0 | 0 | 0 | 0 | 20623.8
2022051809 | 4 | 0.61803 | 49442.4 | 0.50103 | 18037.08 | 0.50539 | 6064.68 | 1 | 5000 | 18037.08 | 6064.68 | 0 | 0 | 0 | 0 | 20340.64 | 0 | 0 | 0 | 0 | 0 | 20340.64
2022051810 | 4 | 0.64856 | 51884.8 | 0.49366 | 17771.76 | 0.6877 | 8252.4 | 1 | 5000 | 17771.76 | 8252.4 | 0 | 0 | 0 | 0 | 20860.64 | 0 | 0 | 0 | 0 | 0 | 20860.64
2022051811 | 4 | 0.68275 | 54620 | 0.4748 | 17092.8 | 0.76081 | 9129.72 | 1 | 5000 | 17092.8 | 9129.72 | 0 | 0 | 0 | 0 | 23397.48 | 0 | 0 | 0 | 0 | 0 | 23397.48
2022051812 | 4 | 0.71984 | 57587.2 | 0.43733 | 15743.88 | 0.77848 | 9341.76 | 1 | 5000 | 15743.88 | 9341.76 | 0 | 0 | 0 | 0 | 27501.56 | 0 | 0 | 0 | 0 | 0 | 27501.56
2022051813 | 4 | 0.76168 | 60934.4 | 0.41349 | 14885.64 | 0.77846 | 9341.52 | 1 | 5000 | 14885.64 | 9341.52 | 0 | 0 | 0 | 0 | 31707.24 | 0 | 0 | 0 | 0 | 0 | 31707.24
2022051814 | 4 | 0.798 | 63840 | 0.40493 | 14577.48 | 0.76327 | 9159.24 | 1 | 5000 | 14577.48 | 9159.24 | 0 | 0 | 0 | 0 | 35103.28 | 0 | 0 | 0 | 0 | 0 | 35103.28
2022051815 | 4 | 0.82768 | 66214.4 | 0.38228 | 13762.08 | 0.7494 | 8992.8 | 1 | 5000 | 13762.08 | 8992.8 | 0 | 0 | 0 | 0 | 38459.52 | 0 | 0 | 0 | 0 | 0 | 38459.52
2022051816 | 4 | 0.85477 | 68381.6 | 0.37358 | 13448.88 | 0.7341 | 8809.2 | 1 | 5000 | 13448.88 | 8809.2 | 0 | 0 | 0 | 0 | 41123.52 | 0 | 0 | 0 | 0 | 0 | 41123.52
2022051817 | 4 | 0.87604 | 70083.2 | 0.37133 | 13367.88 | 0.71918 | 8630.16 | 1 | 5000 | 13367.88 | 8630.16 | 0 | 0 | 0 | 0 | 43085.16 | 0 | 0 | 0 | 0 | 0 | 43085.16
2022051818 | 4 | 0.88015 | 70412 | 0.36399 | 13103.64 | 0.67547 | 8105.64 | 1 | 5000 | 13103.64 | 8105.64 | 0 | 0 | 0 | 0 | 44202.72 | 0 | 0 | 0 | 0 | 0 | 44202.72
2022051819 | 4 | 0.86102 | 68881.6 | 0.36637 | 13189.32 | 0.55411 | 6649.32 | 1 | 5000 | 13189.32 | 6649.32 | 0 | 0 | 0 | 0 | 44042.96 | 0 | 0 | 0 | 0 | 0 | 44042.96
2022051820 | 4 | 0.82673 | 66138.4 | 0.37113 | 13360.68 | 0.24301 | 2916.12 | 1 | 5000 | 13360.68 | 2916.12 | 0 | 0 | 0 | 0 | 44861.6 | 0 | 0 | 0 | 0 | 0 | 44861.6
2022051821 | 4 | 0.79588 | 63670.4 | 0.40406 | 14546.16 | 0.01361 | 163.32 | 1 | 5000 | 14546.16 | 163.32 | 0 | 0 | 0 | 0 | 43960.92 | 0 | 0 | 0 | 0 | 0 | 43960.92
2022051822 | 4 | 0.76703 | 61362.4 | 0.47987 | 17275.32 | 0 | 0 | 1 | 5000 | 17275.32 | 0 | 0 | 0 | 0 | 0 | 39087.08 | 0 | 0 | 0 | 0 | 0 | 39087.08
2022051823 | 4 | 0.71656 | 57324.8 | 0.54965 | 19787.4 | 0 | 0 | 1 | 5000 | 19787.4 | 0 | 0 | 0 | 0 | 0 | 32537.4 | 0 | 0 | 0 | 0 | 0 | 32537.4
2022051824 | 4 | 0.66392 | 53113.6 | 0.5875 | 21150 | 0 | 0 | 1 | 5000 | 21150 | 0 | 0 | 0 | 0 | 0 | 26963.6 | 0 | 0 | 0 | 0 | 0 | 26963.6
2022051901 | 5 | 0.62167 | 49733.6 | 0.58608 | 21098.88 | 0 | 0 | 1 | 5000 | 21098.88 | 0 | 0 | 0 | 0 | 0 | 23634.72 | 0 | 0 | 0 | 0 | 0 | 23634.72
2022051902 | 5 | 0.58777 | 47021.6 | 0.59898 | 21563.28 | 0 | 0 | 1 | 5000 | 21563.28 | 0 | 0 | 0 | 0 | 0 | 20458.32 | 0 | 0 | 0 | 0 | 0 | 20458.32
2022051903 | 5 | 0.56544 | 45235.2 | 0.61618 | 22182.48 | 0 | 0 | 1 | 5000 | 22182.48 | 0 | 0 | 0 | 0 | 0 | 18052.72 | 0 | 0 | 0 | 0 | 0 | 18052.72
2022051904 | 5 | 0.55279 | 44223.2 | 0.61465 | 22127.4 | 0 | 0 | 1 | 5000 | 22127.4 | 0 | 0 | 0 | 0 | 0 | 17095.8 | 0 | 0 | 0 | 0 | 0 | 17095.8
2022051905 | 5 | 0.54782 | 43825.6 | 0.55047 | 19816.92 | 0 | 0 | 1 | 5000 | 19816.92 | 0 | 0 | 0 | 0 | 0 | 19008.68 | 0 | 0 | 0 | 0 | 0 | 19008.68
2022051906 | 5 | 0.56285 | 45028 | 0.46987 | 16915.32 | 0 | 0 | 1 | 5000 | 16915.32 | 0 | 0 | 0 | 0 | 0 | 23112.68 | 0 | 0 | 0 | 0 | 0 | 23112.68
2022051907 | 5 | 0.58394 | 46715.2 | 0.43393 | 15621.48 | 0.00112 | 13.44 | 1 | 5000 | 15621.48 | 13.44 | 0 | 0 | 0 | 0 | 26080.28 | 0 | 0 | 0 | 0 | 0 | 26080.28
2022051908 | 5 | 0.59257 | 47405.6 | 0.34605 | 12457.8 | 0.12481 | 1497.72 | 1 | 5000 | 12457.8 | 1497.72 | 0 | 0 | 0 | 0 | 28450.08 | 0 | 0 | 0 | 0 | 0 | 28450.08
2022051909 | 5 | 0.61712 | 49369.6 | 0.35026 | 12609.36 | 0.4831 | 5797.2 | 1 | 5000 | 12609.36 | 5797.2 | 0 | 0 | 0 | 0 | 25963.04 | 0 | 0 | 0 | 0 | 0 | 25963.04
2022051910 | 5 | 0.65505 | 52404 | 0.38306 | 13790.16 | 0.69055 | 8286.6 | 1 | 5000 | 13790.16 | 8286.6 | 0 | 0 | 0 | 0 | 25327.24 | 0 | 0 | 0 | 0 | 0 | 25327.24
2022051911 | 5 | 0.69465 | 55572 | 0.40526 | 14589.36 | 0.75239 | 9028.68 | 1 | 5000 | 14589.36 | 9028.68 | 0 | 0 | 0 | 0 | 26953.96 | 0 | 0 | 0 | 0 | 0 | 26953.96
2022051912 | 5 | 0.73396 | 58716.8 | 0.40188 | 14467.68 | 0.77905 | 9348.6 | 1 | 5000 | 14467.68 | 9348.6 | 0 | 0 | 0 | 0 | 29900.52 | 0 | 0 | 0 | 0 | 0 | 29900.52
2022051913 | 5 | 0.77286 | 61828.8 | 0.38439 | 13838.04 | 0.80386 | 9646.32 | 1 | 5000 | 13838.04 | 9646.32 | 0 | 0 | 0 | 0 | 33344.44 | 0 | 0 | 0 | 0 | 0 | 33344.44
2022051914 | 5 | 0.81182 | 64945.6 | 0.41316 | 14873.76 | 0.81441 | 9772.92 | 1 | 5000 | 14873.76 | 9772.92 | 0 | 0 | 0 | 0 | 35298.92 | 0 | 0 | 0 | 0 | 0 | 35298.92
2022051915 | 5 | 0.84728 | 67782.4 | 0.47704 | 17173.44 | 0.79853 | 9582.36 | 1 | 5000 | 17173.44 | 9582.36 | 0 | 0 | 0 | 0 | 36026.6 | 0 | 0 | 0 | 0 | 0 | 36026.6
2022051916 | 5 | 0.87427 | 69941.6 | 0.53284 | 19182.24 | 0.76316 | 9157.92 | 1 | 5000 | 19182.24 | 9157.92 | 0 | 0 | 0 | 0 | 36601.44 | 0 | 0 | 0 | 0 | 0 | 36601.44
2022051917 | 5 | 0.89168 | 71334.4 | 0.56379 | 20296.44 | 0.72939 | 8752.68 | 1 | 5000 | 20296.44 | 8752.68 | 0 | 0 | 0 | 0 | 37285.28 | 0 | 0 | 0 | 0 | 0 | 37285.28
2022051918 | 5 | 0.88939 | 71151.2 | 0.57747 | 20788.92 | 0.69475 | 8337 | 1 | 5000 | 20788.92 | 8337 | 0 | 0 | 0 | 0 | 37025.28 | 0 | 0 | 0 | 0 | 0 | 37025.28
2022051919 | 5 | 0.86257 | 69005.6 | 0.57984 | 20874.24 | 0.57801 | 6936.12 | 1 | 5000 | 20874.24 | 6936.12 | 0 | 0 | 0 | 0 | 36195.24 | 0 | 0 | 0 | 0 | 0 | 36195.24
2022051920 | 5 | 0.82616 | 66092.8 | 0.57146 | 20572.56 | 0.27816 | 3337.92 | 1 | 5000 | 20572.56 | 3337.92 | 0 | 0 | 0 | 0 | 37182.32 | 0 | 0 | 0 | 0 | 0 | 37182.32
2022051921 | 5 | 0.79856 | 63884.8 | 0.58718 | 21138.48 | 0.022 | 264 | 1 | 5000 | 21138.48 | 264 | 0 | 0 | 0 | 0 | 37482.32 | 0 | 0 | 0 | 0 | 0 | 37482.32
2022051922 | 5 | 0.77213 | 61770.4 | 0.65573 | 23606.28 | 0 | 0 | 1 | 5000 | 23606.28 | 0 | 0 | 0 | 0 | 0 | 33164.12 | 0 | 0 | 0 | 0 | 0 | 33164.12
2022051923 | 5 | 0.72792 | 58233.6 | 0.7058 | 25408.8 | 0 | 0 | 1 | 5000 | 25408.8 | 0 | 0 | 0 | 0 | 0 | 27824.8 | 0 | 0 | 0 | 0 | 0 | 27824.8
2022051924 | 5 | 0.67897 | 54317.6 | 0.72929 | 26254.44 | 0 | 0 | 1 | 5000 | 26254.44 | 0 | 0 | 0 | 0 | 0 | 23063.16 | 0 | 0 | 0 | 0 | 0 | 23063.16
2022052001 | 6 | 0.63279 | 50623.2 | 0.72668 | 26160.48 | 0 | 0 | 1 | 5000 | 26160.48 | 0 | 0 | 0 | 0 | 0 | 19462.72 | 0 | 0 | 0 | 0 | 0 | 19462.72
2022052002 | 6 | 0.60365 | 48292 | 0.7259 | 26132.4 | 0 | 0 | 1 | 5000 | 26132.4 | 0 | 0 | 0 | 0 | 0 | 17159.6 | 0 | 0 | 0 | 0 | 0 | 17159.6
2022052003 | 6 | 0.58343 | 46674.4 | 0.72664 | 26159.04 | 0 | 0 | 1 | 5000 | 26159.04 | 0 | 0 | 0 | 0 | 0 | 15515.36 | 0 | 0 | 0 | 0 | 0 | 15515.36
2022052004 | 6 | 0.57108 | 45686.4 | 0.7186 | 25869.6 | 0 | 0 | 1 | 5000 | 25869.6 | 0 | 0 | 0 | 0 | 0 | 14816.8 | 0 | 0 | 0 | 0 | 0 | 14816.8
2022052005 | 6 | 0.57004 | 45603.2 | 0.707 | 25452 | 0 | 0 | 1 | 5000 | 25452 | 0 | 0 | 0 | 0 | 0 | 15151.2 | 0 | 0 | 0 | 0 | 0 | 15151.2
2022052006 | 6 | 0.58347 | 46677.6 | 0.67993 | 24477.48 | 0 | 0 | 1 | 5000 | 24477.48 | 0 | 0 | 0 | 0 | 0 | 17200.12 | 0 | 0 | 0 | 0 | 0 | 17200.12
2022052007 | 6 | 0.60776 | 48620.8 | 0.66564 | 23963.04 | 0.00109 | 13.08 | 1 | 5000 | 23963.04 | 13.08 | 0 | 0 | 0 | 0 | 19644.68 | 0 | 0 | 0 | 0 | 0 | 19644.68
2022052008 | 6 | 0.62332 | 49865.6 | 0.64218 | 23118.48 | 0.11949 | 1433.88 | 1 | 5000 | 23118.48 | 1433.88 | 0 | 0 | 0 | 0 | 20313.24 | 0 | 0 | 0 | 0 | 0 | 20313.24
2022052009 | 6 | 0.64623 | 51698.4 | 0.61326 | 22077.36 | 0.43664 | 5239.68 | 1 | 5000 | 22077.36 | 5239.68 | 0 | 0 | 0 | 0 | 19381.36 | 0 | 0 | 0 | 0 | 0 | 19381.36
2022052010 | 6 | 0.68101 | 54480.8 | 0.59546 | 21436.56 | 0.57236 | 6868.32 | 1 | 5000 | 21436.56 | 6868.32 | 0 | 0 | 0 | 0 | 21175.92 | 0 | 0 | 0 | 0 | 0 | 21175.92
2022052011 | 6 | 0.72171 | 57736.8 | 0.55808 | 20090.88 | 0.70859 | 8503.08 | 1 | 5000 | 20090.88 | 8503.08 | 0 | 0 | 0 | 0 | 24142.84 | 0 | 0 | 0 | 0 | 0 | 24142.84
2022052012 | 6 | 0.7608 | 60864 | 0.49494 | 17817.84 | 0.74382 | 8925.84 | 1 | 5000 | 17817.84 | 8925.84 | 0 | 0 | 0 | 0 | 29120.32 | 0 | 0 | 0 | 0 | 0 | 29120.32
2022052013 | 6 | 0.799 | 63920 | 0.42121 | 15163.56 | 0.75797 | 9095.64 | 1 | 5000 | 15163.56 | 9095.64 | 0 | 0 | 0 | 0 | 34660.8 | 0 | 0 | 0 | 0 | 0 | 34660.8
2022052014 | 6 | 0.83448 | 66758.4 | 0.35719 | 12858.84 | 0.75923 | 9110.76 | 1 | 5000 | 12858.84 | 9110.76 | 0 | 0 | 0 | 0 | 39788.8 | 0 | 0 | 0 | 0 | 0 | 39788.8
2022052015 | 6 | 0.8554 | 68432 | 0.30029 | 10810.44 | 0.74562 | 8947.44 | 1 | 5000 | 10810.44 | 8947.44 | 0 | 0 | 0 | 0 | 43674.12 | 0 | 0 | 0 | 0 | 0 | 43674.12
2022052016 | 6 | 0.86869 | 69495.2 | 0.28431 | 10235.16 | 0.7323 | 8787.6 | 1 | 5000 | 10235.16 | 8787.6 | 0 | 0 | 0 | 0 | 45472.44 | 0 | 0 | 0 | 0 | 0 | 45472.44
2022052017 | 6 | 0.8742 | 69936 | 0.30165 | 10859.4 | 0.7027 | 8432.4 | 1 | 5000 | 10859.4 | 8432.4 | 0 | 0 | 0 | 0 | 45644.2 | 0 | 0 | 0 | 0 | 0 | 45644.2
2022052018 | 6 | 0.87141 | 69712.8 | 0.35265 | 12695.4 | 0.62905 | 7548.6 | 1 | 5000 | 12695.4 | 7548.6 | 0 | 0 | 0 | 0 | 44468.8 | 0 | 0 | 0 | 0 | 0 | 44468.8
2022052019 | 6 | 0.84561 | 67648.8 | 0.39796 | 14326.56 | 0.47622 | 5714.64 | 1 | 5000 | 14326.56 | 5714.64 | 0 | 0 | 0 | 0 | 42607.6 | 0 | 0 | 0 | 0 | 0 | 42607.6
2022052020 | 6 | 0.81151 | 64920.8 | 0.43855 | 15787.8 | 0.244 | 2928 | 1 | 5000 | 15787.8 | 2928 | 0 | 0 | 0 | 0 | 41205 | 0 | 0 | 0 | 0 | 0 | 41205
2022052021 | 6 | 0.78426 | 62740.8 | 0.43235 | 15564.6 | 0.02796 | 335.52 | 1 | 5000 | 15564.6 | 335.52 | 0 | 0 | 0 | 0 | 41840.68 | 0 | 0 | 0 | 0 | 0 | 41840.68
2022052022 | 6 | 0.76052 | 60841.6 | 0.46612 | 16780.32 | 0 | 0 | 1 | 5000 | 16780.32 | 0 | 0 | 0 | 0 | 0 | 39061.28 | 0 | 0 | 0 | 0 | 0 | 39061.28
2022052023 | 6 | 0.72545 | 58036 | 0.52802 | 19008.72 | 0 | 0 | 1 | 5000 | 19008.72 | 0 | 0 | 0 | 0 | 0 | 34027.28 | 0 | 0 | 0 | 0 | 0 | 34027.28
2022052024 | 6 | 0.69033 | 55226.4 | 0.59068 | 21264.48 | 0 | 0 | 1 | 5000 | 21264.48 | 0 | 0 | 0 | 0 | 0 | 28961.92 | 0 | 0 | 0 | 0 | 0 | 28961.92
2022052101 | 7 | 0.65035 | 52028 | 0.59402 | 21384.72 | 0 | 0 | 1 | 5000 | 21384.72 | 0 | 0 | 0 | 0 | 0 | 25643.28 | 0 | 0 | 0 | 0 | 0 | 25643.28
2022052102 | 7 | 0.61866 | 49492.8 | 0.58433 | 21035.88 | 0 | 0 | 1 | 5000 | 21035.88 | 0 | 0 | 0 | 0 | 0 | 23456.92 | 0 | 0 | 0 | 0 | 0 | 23456.92
2022052103 | 7 | 0.59405 | 47524 | 0.57809 | 20811.24 | 0 | 0 | 1 | 5000 | 20811.24 | 0 | 0 | 0 | 0 | 0 | 21712.76 | 0 | 0 | 0 | 0 | 0 | 21712.76
2022052104 | 7 | 0.5776 | 46208 | 0.57146 | 20572.56 | 0 | 0 | 1 | 5000 | 20572.56 | 0 | 0 | 0 | 0 | 0 | 20635.44 | 0 | 0 | 0 | 0 | 0 | 20635.44
2022052105 | 7 | 0.56836 | 45468.8 | 0.57564 | 20723.04 | 0 | 0 | 1 | 5000 | 20723.04 | 0 | 0 | 0 | 0 | 0 | 19745.76 | 0 | 0 | 0 | 0 | 0 | 19745.76
2022052106 | 7 | 0.56689 | 45351.2 | 0.57078 | 20548.08 | 0 | 0 | 1 | 5000 | 20548.08 | 0 | 0 | 0 | 0 | 0 | 19803.12 | 0 | 0 | 0 | 0 | 0 | 19803.12
2022052107 | 7 | 0.57017 | 45613.6 | 0.56125 | 20205 | 0.00172 | 20.64 | 1 | 5000 | 20205 | 20.64 | 0 | 0 | 0 | 0 | 20387.96 | 0 | 0 | 0 | 0 | 0 | 20387.96
2022052108 | 7 | 0.58781 | 47024.8 | 0.60764 | 21875.04 | 0.12685 | 1522.2 | 1 | 5000 | 21875.04 | 1522.2 | 0 | 0 | 0 | 0 | 18627.56 | 0 | 0 | 0 | 0 | 0 | 18627.56
2022052109 | 7 | 0.61811 | 49448.8 | 0.62341 | 22442.76 | 0.27523 | 3302.76 | 1 | 5000 | 22442.76 | 3302.76 | 0 | 0 | 0 | 0 | 18703.28 | 0 | 0 | 0 | 0 | 0 | 18703.28
2022052110 | 7 | 0.65453 | 52362.4 | 0.60654 | 21835.44 | 0.37573 | 4508.76 | 1 | 5000 | 21835.44 | 4508.76 | 0 | 0 | 0 | 0 | 21018.2 | 0 | 0 | 0 | 0 | 0 | 21018.2
2022052111 | 7 | 0.69731 | 55784.8 | 0.5833 | 20998.8 | 0.53976 | 6477.12 | 1 | 5000 | 20998.8 | 6477.12 | 0 | 0 | 0 | 0 | 23308.88 | 0 | 0 | 0 | 0 | 0 | 23308.88
2022052112 | 7 | 0.73835 | 59068 | 0.56848 | 20465.28 | 0.57452 | 6894.24 | 1 | 5000 | 20465.28 | 6894.24 | 0 | 0 | 0 | 0 | 26708.48 | 0 | 0 | 0 | 0 | 0 | 26708.48
2022052113 | 7 | 0.77591 | 62072.8 | 0.53201 | 19152.36 | 0.61398 | 7367.76 | 1 | 5000 | 19152.36 | 7367.76 | 0 | 0 | 0 | 0 | 30552.68 | 0 | 0 | 0 | 0 | 0 | 30552.68
2022052114 | 7 | 0.80585 | 64468 | 0.49726 | 17901.36 | 0.64108 | 7692.96 | 1 | 5000 | 17901.36 | 7692.96 | 0 | 0 | 0 | 0 | 33873.68 | 0 | 0 | 0 | 0 | 0 | 33873.68
2022052115 | 7 | 0.82704 | 66163.2 | 0.46906 | 16886.16 | 0.6929 | 8314.8 | 1 | 5000 | 16886.16 | 8314.8 | 0 | 0 | 0 | 0 | 35962.24 | 0 | 0 | 0 | 0 | 0 | 35962.24
2022052116 | 7 | 0.83792 | 67033.6 | 0.45231 | 16283.16 | 0.74577 | 8949.24 | 1 | 5000 | 16283.16 | 8949.24 | 0 | 0 | 0 | 0 | 36801.2 | 0 | 0 | 0 | 0 | 0 | 36801.2
2022052117 | 7 | 0.83696 | 66956.8 | 0.45759 | 16473.24 | 0.71731 | 8607.72 | 1 | 5000 | 16473.24 | 8607.72 | 0 | 0 | 0 | 0 | 36875.84 | 0 | 0 | 0 | 0 | 0 | 36875.84
2022052118 | 7 | 0.81733 | 65386.4 | 0.49874 | 17954.64 | 0.64487 | 7738.44 | 1 | 5000 | 17954.64 | 7738.44 | 0 | 0 | 0 | 0 | 34693.32 | 0 | 0 | 0 | 0 | 0 | 34693.32
2022052119 | 7 | 0.77813 | 62250.4 | 0.54866 | 19751.76 | 0.46136 | 5536.32 | 1 | 5000 | 19751.76 | 5536.32 | 0 | 0 | 0 | 0 | 31962.32 | 0 | 0 | 0 | 0 | 0 | 31962.32
2022052120 | 7 | 0.7396 | 59168 | 0.59364 | 21371.04 | 0.23006 | 2760.72 | 1 | 5000 | 21371.04 | 2760.72 | 0 | 0 | 0 | 0 | 30036.24 | 0 | 0 | 0 | 0 | 0 | 30036.24
2022052121 | 7 | 0.71526 | 57220.8 | 0.63045 | 22696.2 | 0.02212 | 265.44 | 1 | 5000 | 22696.2 | 265.44 | 0 | 0 | 0 | 0 | 29259.16 | 0 | 0 | 0 | 0 | 0 | 29259.16
2022052122 | 7 | 0.69017 | 55213.6 | 0.62492 | 22497.12 | 0 | 0 | 1 | 5000 | 22497.12 | 0 | 0 | 0 | 0 | 0 | 27716.48 | 0 | 0 | 0 | 0 | 0 | 27716.48
2022052123 | 7 | 0.65478 | 52382.4 | 0.66017 | 23766.12 | 0 | 0 | 1 | 5000 | 23766.12 | 0 | 0 | 0 | 0 | 0 | 23616.28 | 0 | 0 | 0 | 0 | 0 | 23616.28
2022052124 | 7 | 0.61304 | 49043.2 | 0.64984 | 23394.24 | 0 | 0 | 1 | 5000 | 23394.24 | 0 | 0 | 0 | 0 | 0 | 20648.96 | 0 | 0 | 0 | 0 | 0 | 20648.96
2022052201 | 1 | 0.57436 | 45948.8 | 0.62847 | 22624.92 | 0 | 0 | 1 | 5000 | 22624.92 | 0 | 0 | 0 | 0 | 0 | 18323.88 | 0 | 0 | 0 | 0 | 0 | 18323.88
2022052202 | 1 | 0.54086 | 43268.8 | 0.61376 | 22095.36 | 0 | 0 | 1 | 5000 | 22095.36 | 0 | 0 | 0 | 0 | 0 | 16173.44 | 0 | 0 | 0 | 0 | 0 | 16173.44
2022052203 | 1 | 0.51391 | 41112.8 | 0.60291 | 21704.76 | 0 | 0 | 1 | 5000 | 21704.76 | 0 | 0 | 0 | 0 | 0 | 14408.04 | 0 | 0 | 0 | 0 | 0 | 14408.04
2022052204 | 1 | 0.49169 | 39335.2 | 0.58383 | 21017.88 | 0 | 0 | 1 | 5000 | 21017.88 | 0 | 0 | 0 | 0 | 0 | 13317.32 | 0 | 0 | 0 | 0 | 0 | 13317.32
2022052205 | 1 | 0.47124 | 37699.2 | 0.5589 | 20120.4 | 0 | 0 | 1 | 5000 | 20120.4 | 0 | 0 | 0 | 0 | 0 | 12578.8 | 0 | 0 | 0 | 0 | 0 | 12578.8
2022052206 | 1 | 0.46457 | 37165.6 | 0.5369 | 19328.4 | 0 | 0 | 1 | 5000 | 19328.4 | 0 | 0 | 0 | 0 | 0 | 12837.2 | 0 | 0 | 0 | 0 | 0 | 12837.2
2022052207 | 1 | 0.46217 | 36973.6 | 0.52835 | 19020.6 | 0.00017 | 2.04 | 1 | 5000 | 19020.6 | 2.04 | 0 | 0 | 0 | 0 | 12950.96 | 0 | 0 | 0 | 0 | 0 | 12950.96
2022052208 | 1 | 0.46845 | 37476 | 0.51829 | 18658.44 | 0.03226 | 387.12 | 1 | 5000 | 18658.44 | 387.12 | 0 | 0 | 0 | 0 | 13430.44 | 0 | 0 | 0 | 0 | 0 | 13430.44
2022052209 | 1 | 0.48483 | 38786.4 | 0.51235 | 18444.6 | 0.11969 | 1436.28 | 1 | 5000 | 18444.6 | 1436.28 | 0 | 0 | 0 | 0 | 13905.52 | 0 | 0 | 0 | 0 | 0 | 13905.52
2022052210 | 1 | 0.50577 | 40461.6 | 0.52415 | 18869.4 | 0.19196 | 2303.52 | 1 | 5000 | 18869.4 | 2303.52 | 0 | 0 | 0 | 0 | 14288.68 | 0 | 0 | 0 | 0 | 0 | 14288.68
2022052211 | 1 | 0.52148 | 41718.4 | 0.4578 | 16480.8 | 0.34577 | 4149.24 | 1 | 5000 | 16480.8 | 4149.24 | 0 | 0 | 0 | 0 | 16088.36 | 0 | 0 | 0 | 0 | 0 | 16088.36
2022052212 | 1 | 0.53699 | 42959.2 | 0.33076 | 11907.36 | 0.48642 | 5837.04 | 1 | 5000 | 11907.36 | 5837.04 | 0 | 0 | 0 | 0 | 20214.8 | 0 | 0 | 0 | 0 | 0 | 20214.8
2022052213 | 1 | 0.55546 | 44436.8 | 0.26128 | 9406.08 | 0.58226 | 6987.12 | 1 | 5000 | 9406.08 | 6987.12 | 0 | 0 | 0 | 0 | 23043.6 | 0 | 0 | 0 | 0 | 0 | 23043.6
2022052214 | 1 | 0.57534 | 46027.2 | 0.20219 | 7278.84 | 0.62457 | 7494.84 | 1 | 5000 | 7278.84 | 7494.84 | 0 | 0 | 0 | 0 | 26253.52 | 0 | 0 | 0 | 0 | 0 | 26253.52
2022052215 | 1 | 0.59615 | 47692 | 0.13657 | 4916.52 | 0.64154 | 7698.48 | 1 | 5000 | 4916.52 | 7698.48 | 0 | 0 | 0 | 0 | 30077 | 0 | 0 | 0 | 0 | 0 | 30077
2022052216 | 1 | 0.61535 | 49228 | 0.09887 | 3559.32 | 0.63435 | 7612.2 | 1 | 5000 | 3559.32 | 7612.2 | 0 | 0 | 0 | 0 | 33056.48 | 0 | 0 | 0 | 0 | 0 | 33056.48
2022052217 | 1 | 0.63296 | 50636.8 | 0.08766 | 3155.76 | 0.58718 | 7046.16 | 1 | 5000 | 3155.76 | 7046.16 | 0 | 0 | 0 | 0 | 35434.88 | 0 | 0 | 0 | 0 | 0 | 35434.88
2022052218 | 1 | 0.6421 | 51368 | 0.08586 | 3090.96 | 0.48138 | 5776.56 | 1 | 5000 | 3090.96 | 5776.56 | 0 | 0 | 0 | 0 | 37500.48 | 0 | 0 | 0 | 0 | 0 | 37500.48
2022052219 | 1 | 0.63959 | 51167.2 | 0.1271 | 4575.6 | 0.32121 | 3854.52 | 1 | 5000 | 4575.6 | 3854.52 | 0 | 0 | 0 | 0 | 37737.08 | 0 | 0 | 0 | 0 | 0 | 37737.08
2022052220 | 1 | 0.62451 | 49960.8 | 0.16289 | 5864.04 | 0.13178 | 1581.36 | 1 | 5000 | 5864.04 | 1581.36 | 0 | 0 | 0 | 0 | 37515.4 | 0 | 0 | 0 | 0 | 0 | 37515.4
2022052221 | 1 | 0.61477 | 49181.6 | 0.18189 | 6548.04 | 0.01186 | 142.32 | 1 | 5000 | 6548.04 | 142.32 | 0 | 0 | 0 | 0 | 37491.24 | 0 | 0 | 0 | 0 | 0 | 37491.24
2022052222 | 1 | 0.60241 | 48192.8 | 0.21661 | 7797.96 | 0.00502 | 60.24 | 1 | 5000 | 7797.96 | 60.24 | 0 | 0 | 0 | 0 | 35334.6 | 0 | 0 | 0 | 0 | 0 | 35334.6
2022052223 | 1 | 0.57054 | 45643.2 | 0.25652 | 9234.72 | 0.00502 | 60.24 | 1 | 5000 | 9234.72 | 60.24 | 0 | 0 | 0 | 0 | 31348.24 | 0 | 0 | 0 | 0 | 0 | 31348.24
2022052224 | 1 | 0.52984 | 42387.2 | 0.28774 | 10358.64 | 0.00502 | 60.24 | 1 | 5000 | 10358.64 | 60.24 | 0 | 0 | 0 | 0 | 26968.32 | 0 | 0 | 0 | 0 | 0 | 26968.32
2022052301 | 2 | 0.49595 | 39676 | 0.29495 | 10618.2 | 0.00502 | 60.24 | 1 | 5000 | 10618.2 | 60.24 | 0 | 0 | 0 | 0 | 23997.56 | 0 | 0 | 0 | 0 | 0 | 23997.56
2022052302 | 2 | 0.47244 | 37795.2 | 0.28687 | 10327.32 | 0.00502 | 60.24 | 1 | 5000 | 10327.32 | 60.24 | 0 | 0 | 0 | 0 | 22407.64 | 0 | 0 | 0 | 0 | 0 | 22407.64
2022052303 | 2 | 0.4579 | 36632 | 0.25742 | 9267.12 | 0.00502 | 60.24 | 1 | 5000 | 9267.12 | 60.24 | 0 | 0 | 0 | 0 | 22304.64 | 0 | 0 | 0 | 0 | 0 | 22304.64
2022052304 | 2 | 0.45461 | 36368.8 | 0.23854 | 8587.44 | 0.00502 | 60.24 | 1 | 5000 | 8587.44 | 60.24 | 0 | 0 | 0 | 0 | 22721.12 | 0 | 0 | 0 | 0 | 0 | 22721.12
2022052305 | 2 | 0.457 | 36560 | 0.22907 | 8246.52 | 0.00355 | 42.6 | 1 | 5000 | 8246.52 | 42.6 | 0 | 0 | 0 | 0 | 23270.88 | 0 | 0 | 0 | 0 | 0 | 23270.88
2022052306 | 2 | 0.47765 | 38212 | 0.22731 | 8183.16 | 0 | 0 | 1 | 5000 | 8183.16 | 0 | 0 | 0 | 0 | 0 | 25028.84 | 0 | 0 | 0 | 0 | 0 | 25028.84
2022052307 | 2 | 0.50368 | 40294.4 | 0.22847 | 8224.92 | 0.00043 | 5.16 | 1 | 5000 | 8224.92 | 5.16 | 0 | 0 | 0 | 0 | 27064.32 | 0 | 0 | 0 | 0 | 0 | 27064.32
2022052308 | 2 | 0.51806 | 41444.8 | 0.22763 | 8194.68 | 0.03736 | 448.32 | 1 | 5000 | 8194.68 | 448.32 | 0 | 0 | 0 | 0 | 27801.8 | 0 | 0 | 0 | 0 | 0 | 27801.8
2022052309 | 2 | 0.53048 | 42438.4 | 0.229 | 8244 | 0.1419 | 1702.8 | 1 | 5000 | 8244 | 1702.8 | 0 | 0 | 0 | 0 | 27491.6 | 0 | 0 | 0 | 0 | 0 | 27491.6
2022052310 | 2 | 0.54595 | 43676 | 0.23477 | 8451.72 | 0.28127 | 3375.24 | 1 | 5000 | 8451.72 | 3375.24 | 0 | 0 | 0 | 0 | 26849.04 | 0 | 0 | 0 | 0 | 0 | 26849.04
2022052311 | 2 | 0.56583 | 45266.4 | 0.23407 | 8426.52 | 0.37663 | 4519.56 | 1 | 5000 | 8426.52 | 4519.56 | 0 | 0 | 0 | 0 | 27320.32 | 0 | 0 | 0 | 0 | 0 | 27320.32
2022052312 | 2 | 0.59228 | 47382.4 | 0.26439 | 9518.04 | 0.44429 | 5331.48 | 1 | 5000 | 9518.04 | 5331.48 | 0 | 0 | 0 | 0 | 27532.88 | 0 | 0 | 0 | 0 | 0 | 27532.88
2022052313 | 2 | 0.61926 | 49540.8 | 0.31051 | 11178.36 | 0.50993 | 6119.16 | 1 | 5000 | 11178.36 | 6119.16 | 0 | 0 | 0 | 0 | 27243.28 | 0 | 0 | 0 | 0 | 0 | 27243.28
2022052314 | 2 | 0.64873 | 51898.4 | 0.34309 | 12351.24 | 0.51896 | 6227.52 | 1 | 5000 | 12351.24 | 6227.52 | 0 | 0 | 0 | 0 | 28319.64 | 0 | 0 | 0 | 0 | 0 | 28319.64
2022052315 | 2 | 0.67343 | 53874.4 | 0.36852 | 13266.72 | 0.47688 | 5722.56 | 1 | 5000 | 13266.72 | 5722.56 | 0 | 0 | 0 | 0 | 29885.12 | 0 | 0 | 0 | 0 | 0 | 29885.12
2022052316 | 2 | 0.69606 | 55684.8 | 0.40385 | 14538.6 | 0.47946 | 5753.52 | 1 | 5000 | 14538.6 | 5753.52 | 0 | 0 | 0 | 0 | 30392.68 | 0 | 0 | 0 | 0 | 0 | 30392.68
2022052317 | 2 | 0.70533 | 56426.4 | 0.41157 | 14816.52 | 0.52335 | 6280.2 | 1 | 5000 | 14816.52 | 6280.2 | 0 | 0 | 0 | 0 | 30329.68 | 0 | 0 | 0 | 0 | 0 | 30329.68
2022052318 | 2 | 0.70245 | 56196 | 0.44866 | 16151.76 | 0.53808 | 6456.96 | 1 | 5000 | 16151.76 | 6456.96 | 0 | 0 | 0 | 0 | 28587.28 | 0 | 0 | 0 | 0 | 0 | 28587.28
2022052319 | 2 | 0.68585 | 54868 | 0.49966 | 17987.76 | 0.4096 | 4915.2 | 1 | 5000 | 17987.76 | 4915.2 | 0 | 0 | 0 | 0 | 26965.04 | 0 | 0 | 0 | 0 | 0 | 26965.04
2022052320 | 2 | 0.66299 | 53039.2 | 0.53255 | 19171.8 | 0.14009 | 1681.08 | 1 | 5000 | 19171.8 | 1681.08 | 0 | 0 | 0 | 0 | 27186.32 | 0 | 0 | 0 | 0 | 0 | 27186.32
2022052321 | 2 | 0.65302 | 52241.6 | 0.55802 | 20088.72 | 0.01255 | 150.6 | 1 | 5000 | 20088.72 | 150.6 | 0 | 0 | 0 | 0 | 27002.28 | 0 | 0 | 0 | 0 | 0 | 27002.28
2022052322 | 2 | 0.63472 | 50777.6 | 0.54249 | 19529.64 | 0 | 0 | 1 | 5000 | 19529.64 | 0 | 0 | 0 | 0 | 0 | 26247.96 | 0 | 0 | 0 | 0 | 0 | 26247.96
2022052323 | 2 | 0.59694 | 47755.2 | 0.5312 | 19123.2 | 0 | 0 | 1 | 5000 | 19123.2 | 0 | 0 | 0 | 0 | 0 | 23632 | 0 | 0 | 0 | 0 | 0 | 23632
2022052324 | 2 | 0.55275 | 44220 | 0.49932 | 17975.52 | 0 | 0 | 1 | 5000 | 17975.52 | 0 | 0 | 0 | 0 | 0 | 21244.48 | 0 | 0 | 0 | 0 | 0 | 21244.48
2022052401 | 3 | 0.52001 | 41600.8 | 0.49852 | 17946.72 | 0 | 0 | 1 | 5000 | 17946.72 | 0 | 0 | 0 | 0 | 0 | 18654.08 | 0 | 0 | 0 | 0 | 0 | 18654.08
2022052402 | 3 | 0.49781 | 39824.8 | 0.50277 | 18099.72 | 0 | 0 | 1 | 5000 | 18099.72 | 0 | 0 | 0 | 0 | 0 | 16725.08 | 0 | 0 | 0 | 0 | 0 | 16725.08
2022052403 | 3 | 0.48214 | 38571.2 | 0.44783 | 16121.88 | 0 | 0 | 1 | 5000 | 16121.88 | 0 | 0 | 0 | 0 | 0 | 17449.32 | 0 | 0 | 0 | 0 | 0 | 17449.32
2022052404 | 3 | 0.47844 | 38275.2 | 0.47874 | 17234.64 | 0 | 0 | 1 | 5000 | 17234.64 | 0 | 0 | 0 | 0 | 0 | 16040.56 | 0 | 0 | 0 | 0 | 0 | 16040.56
2022052405 | 3 | 0.47819 | 38255.2 | 0.47331 | 17039.16 | 0 | 0 | 1 | 5000 | 17039.16 | 0 | 0 | 0 | 0 | 0 | 16216.04 | 0 | 0 | 0 | 0 | 0 | 16216.04
2022052406 | 3 | 0.49677 | 39741.6 | 0.44903 | 16165.08 | 0.00025 | 3 | 1 | 5000 | 16165.08 | 3 | 0 | 0 | 0 | 0 | 18573.52 | 0 | 0 | 0 | 0 | 0 | 18573.52
2022052407 | 3 | 0.52113 | 41690.4 | 0.36709 | 13215.24 | 0.00089 | 10.68 | 1 | 5000 | 13215.24 | 10.68 | 0 | 0 | 0 | 0 | 23464.48 | 0 | 0 | 0 | 0 | 0 | 23464.48
2022052408 | 3 | 0.5328 | 42624 | 0.27297 | 9826.92 | 0.04029 | 483.48 | 1 | 5000 | 9826.92 | 483.48 | 0 | 0 | 0 | 0 | 27313.6 | 0 | 0 | 0 | 0 | 0 | 27313.6
2022052409 | 3 | 0.54567 | 43653.6 | 0.23753 | 8551.08 | 0.15262 | 1831.44 | 1 | 5000 | 8551.08 | 1831.44 | 0 | 0 | 0 | 0 | 28271.08 | 0 | 0 | 0 | 0 | 0 | 28271.08
2022052410 | 3 | 0.56082 | 44865.6 | 0.20767 | 7476.12 | 0.24849 | 2981.88 | 1 | 5000 | 7476.12 | 2981.88 | 0 | 0 | 0 | 0 | 29407.6 | 0 | 0 | 0 | 0 | 0 | 29407.6
2022052411 | 3 | 0.58001 | 46400.8 | 0.2017 | 7261.2 | 0.33226 | 3987.12 | 1 | 5000 | 7261.2 | 3987.12 | 0 | 0 | 0 | 0 | 30152.48 | 0 | 0 | 0 | 0 | 0 | 30152.48
2022052412 | 3 | 0.58683 | 46946.4 | 0.17511 | 6303.96 | 0.46062 | 5527.44 | 1 | 5000 | 6303.96 | 5527.44 | 0 | 0 | 0 | 0 | 30115 | 0 | 0 | 0 | 0 | 0 | 30115
2022052413 | 3 | 0.5953 | 47624 | 0.14559 | 5241.24 | 0.5317 | 6380.4 | 1 | 5000 | 5241.24 | 6380.4 | 0 | 0 | 0 | 0 | 31002.36 | 0 | 0 | 0 | 0 | 0 | 31002.36
2022052414 | 3 | 0.61319 | 49055.2 | 0.16915 | 6089.4 | 0.53955 | 6474.6 | 1 | 5000 | 6089.4 | 6474.6 | 0 | 0 | 0 | 0 | 31491.2 | 0 | 0 | 0 | 0 | 0 | 31491.2
2022052415 | 3 | 0.62814 | 50251.2 | 0.23214 | 8357.04 | 0.52108 | 6252.96 | 1 | 5000 | 8357.04 | 6252.96 | 0 | 0 | 0 | 0 | 30641.2 | 0 | 0 | 0 | 0 | 0 | 30641.2
2022052416 | 3 | 0.6426 | 51408 | 0.29811 | 10731.96 | 0.46 | 5520 | 1 | 5000 | 10731.96 | 5520 | 0 | 0 | 0 | 0 | 30156.04 | 0 | 0 | 0 | 0 | 0 | 30156.04
2022052417 | 3 | 0.66363 | 53090.4 | 0.36811 | 13251.96 | 0.36124 | 4334.88 | 1 | 5000 | 13251.96 | 4334.88 | 0 | 0 | 0 | 0 | 30503.56 | 0 | 0 | 0 | 0 | 0 | 30503.56
2022052418 | 3 | 0.66908 | 53526.4 | 0.41506 | 14942.16 | 0.29207 | 3504.84 | 1 | 5000 | 14942.16 | 3504.84 | 0 | 0 | 0 | 0 | 30079.4 | 0 | 0 | 0 | 0 | 0 | 30079.4
2022052419 | 3 | 0.65526 | 52420.8 | 0.46176 | 16623.36 | 0.14216 | 1705.92 | 1 | 5000 | 16623.36 | 1705.92 | 0 | 0 | 0 | 0 | 29091.52 | 0 | 0 | 0 | 0 | 0 | 29091.52
2022052420 | 3 | 0.63625 | 50900 | 0.49113 | 17680.68 | 0.04909 | 589.08 | 1 | 5000 | 17680.68 | 589.08 | 0 | 0 | 0 | 0 | 27630.24 | 0 | 0 | 0 | 0 | 0 | 27630.24
2022052421 | 3 | 0.62867 | 50293.6 | 0.56826 | 20457.36 | 0.00797 | 95.64 | 1 | 5000 | 20457.36 | 95.64 | 0 | 0 | 0 | 0 | 24740.6 | 0 | 0 | 0 | 0 | 0 | 24740.6
2022052422 | 3 | 0.61442 | 49153.6 | 0.59581 | 21449.16 | 0 | 0 | 1 | 5000 | 21449.16 | 0 | 0 | 0 | 0 | 0 | 22704.44 | 0 | 0 | 0 | 0 | 0 | 22704.44
2022052423 | 3 | 0.57437 | 45949.6 | 0.53869 | 19392.84 | 0 | 0 | 1 | 5000 | 19392.84 | 0 | 0 | 0 | 0 | 0 | 21556.76 | 0 | 0 | 0 | 0 | 0 | 21556.76
2022052424 | 3 | 0.53191 | 42552.8 | 0.48731 | 17543.16 | 0 | 0 | 1 | 5000 | 17543.16 | 0 | 0 | 0 | 0 | 0 | 20009.64 | 0 | 0 | 0 | 0 | 0 | 20009.64
2022052501 | 4 | 0.49313 | 39450.4 | 0.52386 | 18858.96 | 0 | 0 | 1 | 5000 | 18858.96 | 0 | 0 | 0 | 0 | 0 | 15591.44 | 0 | 0 | 0 | 0 | 0 | 15591.44
2022052502 | 4 | 0.46929 | 37543.2 | 0.53986 | 19434.96 | 0 | 0 | 1 | 5000 | 19434.96 | 0 | 0 | 0 | 0 | 0 | 13108.24 | 0 | 0 | 0 | 0 | 0 | 13108.24
2022052503 | 4 | 0.45282 | 36225.6 | 0.48234 | 17364.24 | 0 | 0 | 1 | 5000 | 17364.24 | 0 | 0 | 0 | 0 | 0 | 13861.36 | 0 | 0 | 0 | 0 | 0 | 13861.36
2022052504 | 4 | 0.43785 | 35028 | 0.45278 | 16300.08 | 0 | 0 | 1 | 5000 | 16300.08 | 0 | 0 | 0 | 0 | 0 | 13727.92 | 0 | 0 | 0 | 0 | 0 | 13727.92
2022052505 | 4 | 0.43432 | 34745.6 | 0.44565 | 16043.4 | 0 | 0 | 1 | 5000 | 16043.4 | 0 | 0 | 0 | 0 | 0 | 13702.2 | 0 | 0 | 0 | 0 | 0 | 13702.2
2022052506 | 4 | 0.45102 | 36081.6 | 0.45944 | 16539.84 | 0 | 0 | 1 | 5000 | 16539.84 | 0 | 0 | 0 | 0 | 0 | 14541.76 | 0 | 0 | 0 | 0 | 0 | 14541.76
2022052507 | 4 | 0.47807 | 38245.6 | 0.45748 | 16469.28 | 0.00075 | 9 | 1 | 5000 | 16469.28 | 9 | 0 | 0 | 0 | 0 | 16767.32 | 0 | 0 | 0 | 0 | 0 | 16767.32
2022052508 | 4 | 0.49115 | 39292 | 0.44756 | 16112.16 | 0.08426 | 1011.12 | 1 | 5000 | 16112.16 | 1011.12 | 0 | 0 | 0 | 0 | 17168.72 | 0 | 0 | 0 | 0 | 0 | 17168.72
2022052509 | 4 | 0.50436 | 40348.8 | 0.43489 | 15656.04 | 0.26212 | 3145.44 | 1 | 5000 | 15656.04 | 3145.44 | 0 | 0 | 0 | 0 | 16547.32 | 0 | 0 | 0 | 0 | 0 | 16547.32
2022052510 | 4 | 0.5186 | 41488 | 0.47278 | 17020.08 | 0.29467 | 3536.04 | 1 | 5000 | 17020.08 | 3536.04 | 0 | 0 | 0 | 0 | 15931.88 | 0 | 0 | 0 | 0 | 0 | 15931.88
2022052511 | 4 | 0.53378 | 42702.4 | 0.47557 | 17120.52 | 0.36357 | 4362.84 | 1 | 5000 | 17120.52 | 4362.84 | 0 | 0 | 0 | 0 | 16219.04 | 0 | 0 | 0 | 0 | 0 | 16219.04
2022052512 | 4 | 0.54912 | 43929.6 | 0.44471 | 16009.56 | 0.47705 | 5724.6 | 1 | 5000 | 16009.56 | 5724.6 | 0 | 0 | 0 | 0 | 17195.44 | 0 | 0 | 0 | 0 | 0 | 17195.44
2022052513 | 4 | 0.56655 | 45324 | 0.44895 | 16162.2 | 0.48193 | 5783.16 | 1 | 5000 | 16162.2 | 5783.16 | 0 | 0 | 0 | 0 | 18378.64 | 0 | 0 | 0 | 0 | 0 | 18378.64
2022052514 | 4 | 0.58717 | 46973.6 | 0.43185 | 15546.6 | 0.52519 | 6302.28 | 1 | 5000 | 15546.6 | 6302.28 | 0 | 0 | 0 | 0 | 20124.72 | 0 | 0 | 0 | 0 | 0 | 20124.72
2022052515 | 4 | 0.60658 | 48526.4 | 0.42456 | 15284.16 | 0.53298 | 6395.76 | 1 | 5000 | 15284.16 | 6395.76 | 0 | 0 | 0 | 0 | 21846.48 | 0 | 0 | 0 | 0 | 0 | 21846.48
2022052516 | 4 | 0.62482 | 49985.6 | 0.4346 | 15645.6 | 0.4814 | 5776.8 | 1 | 5000 | 15645.6 | 5776.8 | 0 | 0 | 0 | 0 | 23563.2 | 0 | 0 | 0 | 0 | 0 | 23563.2
2022052517 | 4 | 0.64009 | 51207.2 | 0.42381 | 15257.16 | 0.44852 | 5382.24 | 1 | 5000 | 15257.16 | 5382.24 | 0 | 0 | 0 | 0 | 25567.8 | 0 | 0 | 0 | 0 | 0 | 25567.8
2022052518 | 4 | 0.64714 | 51771.2 | 0.38151 | 13734.36 | 0.45334 | 5440.08 | 1 | 5000 | 13734.36 | 5440.08 | 0 | 0 | 0 | 0 | 27596.76 | 0 | 0 | 0 | 0 | 0 | 27596.76
2022052519 | 4 | 0.6407 | 51256 | 0.34085 | 12270.6 | 0.43913 | 5269.56 | 1 | 5000 | 12270.6 | 5269.56 | 0 | 0 | 0 | 0 | 28715.84 | 0 | 0 | 0 | 0 | 0 | 28715.84
2022052520 | 4 | 0.62098 | 49678.4 | 0.25563 | 9202.68 | 0.29501 | 3540.12 | 1 | 5000 | 9202.68 | 3540.12 | 0 | 0 | 0 | 0 | 31935.6 | 0 | 0 | 0 | 0 | 0 | 31935.6
2022052521 | 4 | 0.60158 | 48126.4 | 0.12388 | 4459.68 | 0.02914 | 349.68 | 1 | 5000 | 4459.68 | 349.68 | 0 | 0 | 0 | 0 | 38317.04 | 0 | 0 | 0 | 0 | 0 | 38317.04
2022052522 | 4 | 0.58332 | 46665.6 | 0.06178 | 2224.08 | 0 | 0 | 1 | 5000 | 2224.08 | 0 | 0 | 0 | 0 | 0 | 39441.52 | 0 | 0 | 0 | 0 | 0 | 39441.52
2022052523 | 4 | 0.54568 | 43654.4 | 0.04572 | 1645.92 | 0 | 0 | 1 | 5000 | 1645.92 | 0 | 0 | 0 | 0 | 0 | 37008.48 | 0 | 0 | 0 | 0 | 0 | 37008.48
2022052524 | 4 | 0.50365 | 40292 | 0.05275 | 1899 | 0 | 0 | 1 | 5000 | 1899 | 0 | 0 | 0 | 0 | 0 | 33393 | 0 | 0 | 0 | 0 | 0 | 33393
2022052601 | 5 | 0.46921 | 37536.8 | 0.07323 | 2636.28 | 0 | 0 | 1 | 5000 | 2636.28 | 0 | 0 | 0 | 0 | 0 | 29900.52 | 0 | 0 | 0 | 0 | 0 | 29900.52
2022052602 | 5 | 0.44725 | 35780 | 0.11586 | 4170.96 | 0 | 0 | 1 | 5000 | 4170.96 | 0 | 0 | 0 | 0 | 0 | 26609.04 | 0 | 0 | 0 | 0 | 0 | 26609.04
2022052603 | 5 | 0.43204 | 34563.2 | 0.19509 | 7023.24 | 0 | 0 | 1 | 5000 | 7023.24 | 0 | 0 | 0 | 0 | 0 | 22539.96 | 0 | 0 | 0 | 0 | 0 | 22539.96
2022052604 | 5 | 0.42602 | 34081.6 | 0.25738 | 9265.68 | 0 | 0 | 1 | 5000 | 9265.68 | 0 | 0 | 0 | 0 | 0 | 19815.92 | 0 | 0 | 0 | 0 | 0 | 19815.92
2022052605 | 5 | 0.43177 | 34541.6 | 0.28766 | 10355.76 | 0 | 0 | 1 | 5000 | 10355.76 | 0 | 0 | 0 | 0 | 0 | 19185.84 | 0 | 0 | 0 | 0 | 0 | 19185.84
2022052606 | 5 | 0.44713 | 35770.4 | 0.32169 | 11580.84 | 0 | 0 | 1 | 5000 | 11580.84 | 0 | 0 | 0 | 0 | 0 | 19189.56 | 0 | 0 | 0 | 0 | 0 | 19189.56
2022052607 | 5 | 0.47198 | 37758.4 | 0.35744 | 12867.84 | 0.00391 | 46.92 | 1 | 5000 | 12867.84 | 46.92 | 0 | 0 | 0 | 0 | 19843.64 | 0 | 0 | 0 | 0 | 0 | 19843.64
2022052608 | 5 | 0.4903 | 39224 | 0.34453 | 12403.08 | 0.20444 | 2453.28 | 1 | 5000 | 12403.08 | 2453.28 | 0 | 0 | 0 | 0 | 19367.64 | 0 | 0 | 0 | 0 | 0 | 19367.64
2022052609 | 5 | 0.51501 | 41200.8 | 0.2523 | 9082.8 | 0.6145 | 7374 | 1 | 5000 | 9082.8 | 7374 | 0 | 0 | 0 | 0 | 19744 | 0 | 0 | 0 | 0 | 0 | 19744
2022052610 | 5 | 0.5414 | 43312 | 0.19978 | 7192.08 | 0.7593 | 9111.6 | 1 | 5000 | 7192.08 | 9111.6 | 0 | 0 | 0 | 0 | 22008.32 | 0 | 0 | 0 | 0 | 0 | 22008.32
2022052611 | 5 | 0.57245 | 45796 | 0.21931 | 7895.16 | 0.79268 | 9512.16 | 1 | 5000 | 7895.16 | 9512.16 | 0 | 0 | 0 | 0 | 23388.68 | 0 | 0 | 0 | 0 | 0 | 23388.68
2022052612 | 5 | 0.6048 | 48384 | 0.16345 | 5884.2 | 0.8133 | 9759.6 | 1 | 5000 | 5884.2 | 9759.6 | 0 | 0 | 0 | 0 | 27740.2 | 0 | 0 | 0 | 0 | 0 | 27740.2
2022052613 | 5 | 0.63746 | 50996.8 | 0.11982 | 4313.52 | 0.81505 | 9780.6 | 1 | 5000 | 4313.52 | 9780.6 | 0 | 0 | 0 | 0 | 31902.68 | 0 | 0 | 0 | 0 | 0 | 31902.68
2022052614 | 5 | 0.67342 | 53873.6 | 0.11124 | 4004.64 | 0.81582 | 9789.84 | 1 | 5000 | 4004.64 | 9789.84 | 0 | 0 | 0 | 0 | 35079.12 | 0 | 0 | 0 | 0 | 0 | 35079.12
2022052615 | 5 | 0.70859 | 56687.2 | 0.10627 | 3825.72 | 0.83254 | 9990.48 | 1 | 5000 | 3825.72 | 9990.48 | 0 | 0 | 0 | 0 | 37871 | 0 | 0 | 0 | 0 | 0 | 37871
2022052616 | 5 | 0.73683 | 58946.4 | 0.10156 | 3656.16 | 0.83396 | 10007.52 | 1 | 5000 | 3656.16 | 10007.52 | 0 | 0 | 0 | 0 | 40282.72 | 0 | 0 | 0 | 0 | 0 | 40282.72
2022052617 | 5 | 0.75756 | 60604.8 | 0.10578 | 3808.08 | 0.81927 | 9831.24 | 1 | 5000 | 3808.08 | 9831.24 | 0 | 0 | 0 | 0 | 41965.48 | 0 | 0 | 0 | 0 | 0 | 41965.48
2022052618 | 5 | 0.76964 | 61571.2 | 0.10881 | 3917.16 | 0.7941 | 9529.2 | 1 | 5000 | 3917.16 | 9529.2 | 0 | 0 | 0 | 0 | 43124.84 | 0 | 0 | 0 | 0 | 0 | 43124.84
2022052619 | 5 | 0.76141 | 60912.8 | 0.11166 | 4019.76 | 0.69114 | 8293.68 | 1 | 5000 | 4019.76 | 8293.68 | 0 | 0 | 0 | 0 | 43599.36 | 0 | 0 | 0 | 0 | 0 | 43599.36
2022052620 | 5 | 0.73512 | 58809.6 | 0.12495 | 4498.2 | 0.36025 | 4323 | 1 | 5000 | 4498.2 | 4323 | 0 | 0 | 0 | 0 | 44988.4 | 0 | 0 | 0 | 0 | 0 | 44988.4
2022052621 | 5 | 0.69969 | 55975.2 | 0.16502 | 5940.72 | 0.03554 | 426.48 | 1 | 5000 | 5940.72 | 426.48 | 0 | 0 | 0 | 0 | 44608 | 0 | 0 | 0 | 0 | 0 | 44608
2022052622 | 5 | 0.67161 | 53728.8 | 0.22178 | 7984.08 | 0 | 0 | 1 | 5000 | 7984.08 | 0 | 0 | 0 | 0 | 0 | 40744.72 | 0 | 0 | 0 | 0 | 0 | 40744.72
2022052623 | 5 | 0.62388 | 49910.4 | 0.26232 | 9443.52 | 0 | 0 | 1 | 5000 | 9443.52 | 0 | 0 | 0 | 0 | 0 | 35466.88 | 0 | 0 | 0 | 0 | 0 | 35466.88
2022052624 | 5 | 0.57644 | 46115.2 | 0.28955 | 10423.8 | 0 | 0 | 1 | 5000 | 10423.8 | 0 | 0 | 0 | 0 | 0 | 30691.4 | 0 | 0 | 0 | 0 | 0 | 30691.4
2022052701 | 6 | 0.53616 | 42892.8 | 0.35122 | 12643.92 | 0 | 0 | 1 | 5000 | 12643.92 | 0 | 0 | 0 | 0 | 0 | 25248.88 | 0 | 0 | 0 | 0 | 0 | 25248.88
2022052702 | 6 | 0.50525 | 40420 | 0.38097 | 13714.92 | 0 | 0 | 1 | 5000 | 13714.92 | 0 | 0 | 0 | 0 | 0 | 21705.08 | 0 | 0 | 0 | 0 | 0 | 21705.08
2022052703 | 6 | 0.48866 | 39092.8 | 0.38246 | 13768.56 | 0 | 0 | 1 | 5000 | 13768.56 | 0 | 0 | 0 | 0 | 0 | 20324.24 | 0 | 0 | 0 | 0 | 0 | 20324.24
2022052704 | 6 | 0.47487 | 37989.6 | 0.36481 | 13133.16 | 0 | 0 | 1 | 5000 | 13133.16 | 0 | 0 | 0 | 0 | 0 | 19856.44 | 0 | 0 | 0 | 0 | 0 | 19856.44
2022052705 | 6 | 0.47174 | 37739.2 | 0.3644 | 13118.4 | 0 | 0 | 1 | 5000 | 13118.4 | 0 | 0 | 0 | 0 | 0 | 19620.8 | 0 | 0 | 0 | 0 | 0 | 19620.8
2022052706 | 6 | 0.4837 | 38696 | 0.35035 | 12612.6 | 0 | 0 | 1 | 5000 | 12612.6 | 0 | 0 | 0 | 0 | 0 | 21083.4 | 0 | 0 | 0 | 0 | 0 | 21083.4
2022052707 | 6 | 0.50313 | 40250.4 | 0.34257 | 12332.52 | 0.00627 | 75.24 | 1 | 5000 | 12332.52 | 75.24 | 0 | 0 | 0 | 0 | 22842.64 | 0 | 0 | 0 | 0 | 0 | 22842.64
2022052708 | 6 | 0.52212 | 41769.6 | 0.31256 | 11252.16 | 0.20328 | 2439.36 | 1 | 5000 | 11252.16 | 2439.36 | 0 | 0 | 0 | 0 | 23078.08 | 0 | 0 | 0 | 0 | 0 | 23078.08
2022052709 | 6 | 0.55333 | 44266.4 | 0.23451 | 8442.36 | 0.59642 | 7157.04 | 1 | 5000 | 8442.36 | 7157.04 | 0 | 0 | 0 | 0 | 23667 | 0 | 0 | 0 | 0 | 0 | 23667
2022052710 | 6 | 0.59089 | 47271.2 | 0.25214 | 9077.04 | 0.74541 | 8944.92 | 1 | 5000 | 9077.04 | 8944.92 | 0 | 0 | 0 | 0 | 24249.24 | 0 | 0 | 0 | 0 | 0 | 24249.24
2022052711 | 6 | 0.63026 | 50420.8 | 0.27304 | 9829.44 | 0.76952 | 9234.24 | 1 | 5000 | 9829.44 | 9234.24 | 0 | 0 | 0 | 0 | 26357.12 | 0 | 0 | 0 | 0 | 0 | 26357.12
2022052712 | 6 | 0.67542 | 54033.6 | 0.26513 | 9544.68 | 0.78331 | 9399.72 | 1 | 5000 | 9544.68 | 9399.72 | 0 | 0 | 0 | 0 | 30089.2 | 0 | 0 | 0 | 0 | 0 | 30089.2
2022052713 | 6 | 0.71797 | 57437.6 | 0.26538 | 9553.68 | 0.78871 | 9464.52 | 1 | 5000 | 9553.68 | 9464.52 | 0 | 0 | 0 | 0 | 33419.4 | 0 | 0 | 0 | 0 | 0 | 33419.4
2022052714 | 6 | 0.75834 | 60667.2 | 0.26525 | 9549 | 0.78982 | 9477.84 | 1 | 5000 | 9549 | 9477.84 | 0 | 0 | 0 | 0 | 36640.36 | 0 | 0 | 0 | 0 | 0 | 36640.36
2022052715 | 6 | 0.79178 | 63342.4 | 0.26706 | 9614.16 | 0.77306 | 9276.72 | 1 | 5000 | 9614.16 | 9276.72 | 0 | 0 | 0 | 0 | 39451.52 | 0 | 0 | 0 | 0 | 0 | 39451.52
2022052716 | 6 | 0.81829 | 65463.2 | 0.28145 | 10132.2 | 0.73992 | 8879.04 | 1 | 5000 | 10132.2 | 8879.04 | 0 | 0 | 0 | 0 | 41451.96 | 0 | 0 | 0 | 0 | 0 | 41451.96
2022052717 | 6 | 0.83517 | 66813.6 | 0.29826 | 10737.36 | 0.71525 | 8583 | 1 | 5000 | 10737.36 | 8583 | 0 | 0 | 0 | 0 | 42493.24 | 0 | 0 | 0 | 0 | 0 | 42493.24
2022052718 | 6 | 0.83741 | 66992.8 | 0.32159 | 11577.24 | 0.68862 | 8263.44 | 1 | 5000 | 11577.24 | 8263.44 | 0 | 0 | 0 | 0 | 42152.12 | 0 | 0 | 0 | 0 | 0 | 42152.12
2022052719 | 6 | 0.82351 | 65880.8 | 0.36866 | 13271.76 | 0.60756 | 7290.72 | 1 | 5000 | 13271.76 | 7290.72 | 0 | 0 | 0 | 0 | 40318.32 | 0 | 0 | 0 | 0 | 0 | 40318.32
2022052720 | 6 | 0.79123 | 63298.4 | 0.4236 | 15249.6 | 0.31164 | 3739.68 | 1 | 5000 | 15249.6 | 3739.68 | 0 | 0 | 0 | 0 | 39309.12 | 0 | 0 | 0 | 0 | 0 | 39309.12
2022052721 | 6 | 0.75009 | 60007.2 | 0.48754 | 17551.44 | 0.02937 | 352.44 | 1 | 5000 | 17551.44 | 352.44 | 0 | 0 | 0 | 0 | 37103.32 | 0 | 0 | 0 | 0 | 0 | 37103.32
2022052722 | 6 | 0.71655 | 57324 | 0.5835 | 21006 | 0 | 0 | 1 | 5000 | 21006 | 0 | 0 | 0 | 0 | 0 | 31318 | 0 | 0 | 0 | 0 | 0 | 31318
2022052723 | 6 | 0.67197 | 53757.6 | 0.64264 | 23135.04 | 0 | 0 | 1 | 5000 | 23135.04 | 0 | 0 | 0 | 0 | 0 | 25622.56 | 0 | 0 | 0 | 0 | 0 | 25622.56
2022052724 | 6 | 0.6274 | 50192 | 0.64702 | 23292.72 | 0 | 0 | 1 | 5000 | 23292.72 | 0 | 0 | 0 | 0 | 0 | 21899.28 | 0 | 0 | 0 | 0 | 0 | 21899.28
2022052801 | 7 | 0.58084 | 46467.2 | 0.6337 | 22813.2 | 0 | 0 | 1 | 5000 | 22813.2 | 0 | 0 | 0 | 0 | 0 | 18654 | 0 | 0 | 0 | 0 | 0 | 18654
2022052802 | 7 | 0.54812 | 43849.6 | 0.63428 | 22834.08 | 0 | 0 | 1 | 5000 | 22834.08 | 0 | 0 | 0 | 0 | 0 | 16015.52 | 0 | 0 | 0 | 0 | 0 | 16015.52
2022052803 | 7 | 0.52145 | 41716 | 0.62744 | 22587.84 | 0 | 0 | 1 | 5000 | 22587.84 | 0 | 0 | 0 | 0 | 0 | 14128.16 | 0 | 0 | 0 | 0 | 0 | 14128.16
2022052804 | 7 | 0.50393 | 40314.4 | 0.60756 | 21872.16 | 0 | 0 | 1 | 5000 | 21872.16 | 0 | 0 | 0 | 0 | 0 | 13442.24 | 0 | 0 | 0 | 0 | 0 | 13442.24
2022052805 | 7 | 0.49169 | 39335.2 | 0.59074 | 21266.64 | 0 | 0 | 1 | 5000 | 21266.64 | 0 | 0 | 0 | 0 | 0 | 13068.56 | 0 | 0 | 0 | 0 | 0 | 13068.56
2022052806 | 7 | 0.49278 | 39422.4 | 0.58371 | 21013.56 | 0 | 0 | 1 | 5000 | 21013.56 | 0 | 0 | 0 | 0 | 0 | 13408.84 | 0 | 0 | 0 | 0 | 0 | 13408.84
2022052807 | 7 | 0.49126 | 39300.8 | 0.57769 | 20796.84 | 0.00231 | 27.72 | 1 | 5000 | 20796.84 | 27.72 | 0 | 0 | 0 | 0 | 13476.24 | 0 | 0 | 0 | 0 | 0 | 13476.24
2022052808 | 7 | 0.50427 | 40341.6 | 0.57439 | 20678.04 | 0.0928 | 1113.6 | 1 | 5000 | 20678.04 | 1113.6 | 0 | 0 | 0 | 0 | 13549.96 | 0 | 0 | 0 | 0 | 0 | 13549.96
2022052809 | 7 | 0.54168 | 43334.4 | 0.56222 | 20239.92 | 0.29589 | 3550.68 | 1 | 5000 | 20239.92 | 3550.68 | 0 | 0 | 0 | 0 | 14543.8 | 0 | 0 | 0 | 0 | 0 | 14543.8
2022052810 | 7 | 0.58486 | 46788.8 | 0.57591 | 20732.76 | 0.3895 | 4674 | 1 | 5000 | 20732.76 | 4674 | 0 | 0 | 0 | 0 | 16382.04 | 0 | 0 | 0 | 0 | 0 | 16382.04
2022052811 | 7 | 0.63187 | 50549.6 | 0.58666 | 21119.76 | 0.4243 | 5091.6 | 1 | 5000 | 21119.76 | 5091.6 | 0 | 0 | 0 | 0 | 19338.24 | 0 | 0 | 0 | 0 | 0 | 19338.24
2022052812 | 7 | 0.68163 | 54530.4 | 0.57617 | 20742.12 | 0.45902 | 5508.24 | 1 | 5000 | 20742.12 | 5508.24 | 0 | 0 | 0 | 0 | 23280.04 | 0 | 0 | 0 | 0 | 0 | 23280.04
2022052813 | 7 | 0.72477 | 57981.6 | 0.56942 | 20499.12 | 0.49504 | 5940.48 | 1 | 5000 | 20499.12 | 5940.48 | 0 | 0 | 0 | 0 | 26542 | 0 | 0 | 0 | 0 | 0 | 26542
2022052814 | 7 | 0.76302 | 61041.6 | 0.55453 | 19963.08 | 0.55099 | 6611.88 | 1 | 5000 | 19963.08 | 6611.88 | 0 | 0 | 0 | 0 | 29466.64 | 0 | 0 | 0 | 0 | 0 | 29466.64
2022052815 | 7 | 0.79568 | 63654.4 | 0.57281 | 20621.16 | 0.57198 | 6863.76 | 1 | 5000 | 20621.16 | 6863.76 | 0 | 0 | 0 | 0 | 31169.48 | 0 | 0 | 0 | 0 | 0 | 31169.48
2022052816 | 7 | 0.82142 | 65713.6 | 0.58248 | 20969.28 | 0.60274 | 7232.88 | 1 | 5000 | 20969.28 | 7232.88 | 0 | 0 | 0 | 0 | 32511.44 | 0 | 0 | 0 | 0 | 0 | 32511.44
2022052817 | 7 | 0.83793 | 67034.4 | 0.60067 | 21624.12 | 0.6173 | 7407.6 | 1 | 5000 | 21624.12 | 7407.6 | 0 | 0 | 0 | 0 | 33002.68 | 0 | 0 | 0 | 0 | 0 | 33002.68
2022052818 | 7 | 0.84166 | 67332.8 | 0.62111 | 22359.96 | 0.56179 | 6741.48 | 1 | 5000 | 22359.96 | 6741.48 | 0 | 0 | 0 | 0 | 33231.36 | 0 | 0 | 0 | 0 | 0 | 33231.36
2022052819 | 7 | 0.82686 | 66148.8 | 0.64949 | 23381.64 | 0.42808 | 5136.96 | 1 | 5000 | 23381.64 | 5136.96 | 0 | 0 | 0 | 0 | 32630.2 | 0 | 0 | 0 | 0 | 0 | 32630.2
2022052820 | 7 | 0.79713 | 63770.4 | 0.66475 | 23931 | 0.21269 | 2552.28 | 1 | 5000 | 23931 | 2552.28 | 0 | 0 | 0 | 0 | 32287.12 | 0 | 0 | 0 | 0 | 0 | 32287.12
2022052821 | 7 | 0.76243 | 60994.4 | 0.67881 | 24437.16 | 0.01775 | 213 | 1 | 5000 | 24437.16 | 213 | 0 | 0 | 0 | 0 | 31344.24 | 0 | 0 | 0 | 0 | 0 | 31344.24
2022052822 | 7 | 0.73601 | 58880.8 | 0.69454 | 25003.44 | 0 | 0 | 1 | 5000 | 25003.44 | 0 | 0 | 0 | 0 | 0 | 28877.36 | 0 | 0 | 0 | 0 | 0 | 28877.36
2022052823 | 7 | 0.69675 | 55740 | 0.69301 | 24948.36 | 0 | 0 | 1 | 5000 | 24948.36 | 0 | 0 | 0 | 0 | 0 | 25791.64 | 0 | 0 | 0 | 0 | 0 | 25791.64
2022052824 | 7 | 0.65475 | 52380 | 0.70708 | 25454.88 | 0 | 0 | 1 | 5000 | 25454.88 | 0 | 0 | 0 | 0 | 0 | 21925.12 | 0 | 0 | 0 | 0 | 0 | 21925.12
2022052901 | 1 | 0.61689 | 49351.2 | 0.71722 | 25819.92 | 0 | 0 | 1 | 5000 | 25819.92 | 0 | 0 | 0 | 0 | 0 | 18531.28 | 0 | 0 | 0 | 0 | 0 | 18531.28
2022052902 | 1 | 0.58486 | 46788.8 | 0.72454 | 26083.44 | 0 | 0 | 1 | 5000 | 26083.44 | 0 | 0 | 0 | 0 | 0 | 15705.36 | 0 | 0 | 0 | 0 | 0 | 15705.36
2022052903 | 1 | 0.56104 | 44883.2 | 0.72139 | 25970.04 | 0 | 0 | 1 | 5000 | 25970.04 | 0 | 0 | 0 | 0 | 0 | 13913.16 | 0 | 0 | 0 | 0 | 0 | 13913.16
2022052904 | 1 | 0.5463 | 43704 | 0.71127 | 25605.72 | 0 | 0 | 1 | 5000 | 25605.72 | 0 | 0 | 0 | 0 | 0 | 13098.28 | 0 | 0 | 0 | 0 | 0 | 13098.28
2022052905 | 1 | 0.5286 | 42288 | 0.68206 | 24554.16 | 0 | 0 | 1 | 5000 | 24554.16 | 0 | 0 | 0 | 0 | 0 | 12733.84 | 0 | 0 | 0 | 0 | 0 | 12733.84
2022052906 | 1 | 0.52201 | 41760.8 | 0.67602 | 24336.72 | 0 | 0 | 1 | 5000 | 24336.72 | 0 | 0 | 0 | 0 | 0 | 12424.08 | 0 | 0 | 0 | 0 | 0 | 12424.08
2022052907 | 1 | 0.51834 | 41467.2 | 0.66873 | 24074.28 | 0.00202 | 24.24 | 1 | 5000 | 24074.28 | 24.24 | 0 | 0 | 0 | 0 | 12368.68 | 0 | 0 | 0 | 0 | 0 | 12368.68
2022052908 | 1 | 0.52615 | 42092 | 0.65655 | 23635.8 | 0.07386 | 886.32 | 1 | 5000 | 23635.8 | 886.32 | 0 | 0 | 0 | 0 | 12569.88 | 0 | 0 | 0 | 0 | 0 | 12569.88
2022052909 | 1 | 0.5617 | 44936 | 0.66607 | 23978.52 | 0.25815 | 3097.8 | 1 | 5000 | 23978.52 | 3097.8 | 0 | 0 | 0 | 0 | 12859.68 | 0 | 0 | 0 | 0 | 0 | 12859.68
2022052910 | 1 | 0.60703 | 48562.4 | 0.68324 | 24596.64 | 0.37556 | 4506.72 | 1 | 5000 | 24596.64 | 4506.72 | 0 | 0 | 0 | 0 | 14459.04 | 0 | 0 | 0 | 0 | 0 | 14459.04
2022052911 | 1 | 0.64985 | 51988 | 0.67334 | 24240.24 | 0.46198 | 5543.76 | 1 | 5000 | 24240.24 | 5543.76 | 0 | 0 | 0 | 0 | 17204 | 0 | 0 | 0 | 0 | 0 | 17204
2022052912 | 1 | 0.69367 | 55493.6 | 0.68 | 24480 | 0.45992 | 5519.04 | 1 | 5000 | 24480 | 5519.04 | 0 | 0 | 0 | 0 | 20494.56 | 0 | 0 | 0 | 0 | 0 | 20494.56
2022052913 | 1 | 0.73605 | 58884 | 0.68718 | 24738.48 | 0.45943 | 5513.16 | 1 | 5000 | 24738.48 | 5513.16 | 0 | 0 | 0 | 0 | 23632.36 | 0 | 0 | 0 | 0 | 0 | 23632.36
2022052914 | 1 | 0.76945 | 61556 | 0.66194 | 23829.84 | 0.54616 | 6553.92 | 1 | 5000 | 23829.84 | 6553.92 | 0 | 0 | 0 | 0 | 26172.24 | 0 | 0 | 0 | 0 | 0 | 26172.24
2022052915 | 1 | 0.79583 | 63666.4 | 0.67726 | 24381.36 | 0.51275 | 6153 | 1 | 5000 | 24381.36 | 6153 | 0 | 0 | 0 | 0 | 28132.04 | 0 | 0 | 0 | 0 | 0 | 28132.04
2022052916 | 1 | 0.8171 | 65368 | 0.67606 | 24338.16 | 0.51803 | 6216.36 | 1 | 5000 | 24338.16 | 6216.36 | 0 | 0 | 0 | 0 | 29813.48 | 0 | 0 | 0 | 0 | 0 | 29813.48
2022052917 | 1 | 0.83171 | 66536.8 | 0.67259 | 24213.24 | 0.52146 | 6257.52 | 1 | 5000 | 24213.24 | 6257.52 | 0 | 0 | 0 | 0 | 31066.04 | 0 | 0 | 0 | 0 | 0 | 31066.04
2022052918 | 1 | 0.83211 | 66568.8 | 0.67369 | 24252.84 | 0.49076 | 5889.12 | 1 | 5000 | 24252.84 | 5889.12 | 0 | 0 | 0 | 0 | 31426.84 | 0 | 0 | 0 | 0 | 0 | 31426.84
2022052919 | 1 | 0.81463 | 65170.4 | 0.67311 | 24231.96 | 0.42477 | 5097.24 | 1 | 5000 | 24231.96 | 5097.24 | 0 | 0 | 0 | 0 | 30841.2 | 0 | 0 | 0 | 0 | 0 | 30841.2
2022052920 | 1 | 0.78473 | 62778.4 | 0.6904 | 24854.4 | 0.23918 | 2870.16 | 1 | 5000 | 24854.4 | 2870.16 | 0 | 0 | 0 | 0 | 30053.84 | 0 | 0 | 0 | 0 | 0 | 30053.84
2022052921 | 1 | 0.7553 | 60424 | 0.72784 | 26202.24 | 0.03453 | 414.36 | 1 | 5000 | 26202.24 | 414.36 | 0 | 0 | 0 | 0 | 28807.4 | 0 | 0 | 0 | 0 | 0 | 28807.4
2022052922 | 1 | 0.73305 | 58644 | 0.74368 | 26772.48 | 0 | 0 | 1 | 5000 | 26772.48 | 0 | 0 | 0 | 0 | 0 | 26871.52 | 0 | 0 | 0 | 0 | 0 | 26871.52
2022052923 | 1 | 0.69515 | 55612 | 0.75385 | 27138.6 | 0 | 0 | 1 | 5000 | 27138.6 | 0 | 0 | 0 | 0 | 0 | 23473.4 | 0 | 0 | 0 | 0 | 0 | 23473.4
2022052924 | 1 | 0.65563 | 52450.4 | 0.7533 | 27118.8 | 0 | 0 | 1 | 5000 | 27118.8 | 0 | 0 | 0 | 0 | 0 | 20331.6 | 0 | 0 | 0 | 0 | 0 | 20331.6
2022053001 | 2 | 0.62008 | 49606.4 | 0.74691 | 26888.76 | 0 | 0 | 1 | 5000 | 26888.76 | 0 | 0 | 0 | 0 | 0 | 17717.64 | 0 | 0 | 0 | 0 | 0 | 17717.64
2022053002 | 2 | 0.58906 | 47124.8 | 0.74366 | 26771.76 | 0 | 0 | 1 | 5000 | 26771.76 | 0 | 0 | 0 | 0 | 0 | 15353.04 | 0 | 0 | 0 | 0 | 0 | 15353.04
2022053003 | 2 | 0.56815 | 45452 | 0.73736 | 26544.96 | 0 | 0 | 1 | 5000 | 26544.96 | 0 | 0 | 0 | 0 | 0 | 13907.04 | 0 | 0 | 0 | 0 | 0 | 13907.04
2022053004 | 2 | 0.55548 | 44438.4 | 0.73137 | 26329.32 | 0 | 0 | 1 | 5000 | 26329.32 | 0 | 0 | 0 | 0 | 0 | 13109.08 | 0 | 0 | 0 | 0 | 0 | 13109.08
2022053005 | 2 | 0.55266 | 44212.8 | 0.7257 | 26125.2 | 0 | 0 | 1 | 5000 | 26125.2 | 0 | 0 | 0 | 0 | 0 | 13087.6 | 0 | 0 | 0 | 0 | 0 | 13087.6
2022053006 | 2 | 0.5575 | 44600 | 0.72589 | 26132.04 | 0 | 0 | 1 | 5000 | 26132.04 | 0 | 0 | 0 | 0 | 0 | 13467.96 | 0 | 0 | 0 | 0 | 0 | 13467.96
2022053007 | 2 | 0.55635 | 44508 | 0.71094 | 25593.84 | 0.00402 | 48.24 | 1 | 5000 | 25593.84 | 48.24 | 0 | 0 | 0 | 0 | 13865.92 | 0 | 0 | 0 | 0 | 0 | 13865.92
2022053008 | 2 | 0.56142 | 44913.6 | 0.67168 | 24180.48 | 0.14865 | 1783.8 | 1 | 5000 | 24180.48 | 1783.8 | 0 | 0 | 0 | 0 | 13949.32 | 0 | 0 | 0 | 0 | 0 | 13949.32
2022053009 | 2 | 0.5921 | 47368 | 0.65424 | 23552.64 | 0.36584 | 4390.08 | 1 | 5000 | 23552.64 | 4390.08 | 0 | 0 | 0 | 0 | 14425.28 | 0 | 0 | 0 | 0 | 0 | 14425.28
2022053010 | 2 | 0.63406 | 50724.8 | 0.64567 | 23244.12 | 0.43558 | 5226.96 | 1 | 5000 | 23244.12 | 5226.96 | 0 | 0 | 0 | 0 | 17253.72 | 0 | 0 | 0 | 0 | 0 | 17253.72
2022053011 | 2 | 0.67951 | 54360.8 | 0.60801 | 21888.36 | 0.58761 | 7051.32 | 1 | 5000 | 21888.36 | 7051.32 | 0 | 0 | 0 | 0 | 20421.12 | 0 | 0 | 0 | 0 | 0 | 20421.12
2022053012 | 2 | 0.71774 | 57419.2 | 0.54815 | 19733.4 | 0.74261 | 8911.32 | 1 | 5000 | 19733.4 | 8911.32 | 0 | 0 | 0 | 0 | 23774.48 | 0 | 0 | 0 | 0 | 0 | 23774.48
2022053013 | 2 | 0.74881 | 59904.8 | 0.4713 | 16966.8 | 0.75438 | 9052.56 | 1 | 5000 | 16966.8 | 9052.56 | 0 | 0 | 0 | 0 | 28885.44 | 0 | 0 | 0 | 0 | 0 | 28885.44
2022053014 | 2 | 0.77871 | 62296.8 | 0.44175 | 15903 | 0.76247 | 9149.64 | 1 | 5000 | 15903 | 9149.64 | 0 | 0 | 0 | 0 | 32244.16 | 0 | 0 | 0 | 0 | 0 | 32244.16
2022053015 | 2 | 0.80315 | 64252 | 0.47035 | 16932.6 | 0.76234 | 9148.08 | 1 | 5000 | 16932.6 | 9148.08 | 0 | 0 | 0 | 0 | 33171.32 | 0 | 0 | 0 | 0 | 0 | 33171.32
2022053016 | 2 | 0.82332 | 65865.6 | 0.51709 | 18615.24 | 0.76015 | 9121.8 | 1 | 5000 | 18615.24 | 9121.8 | 0 | 0 | 0 | 0 | 33128.56 | 0 | 0 | 0 | 0 | 0 | 33128.56
2022053017 | 2 | 0.83592 | 66873.6 | 0.56034 | 20172.24 | 0.72979 | 8757.48 | 1 | 5000 | 20172.24 | 8757.48 | 0 | 0 | 0 | 0 | 32943.88 | 0 | 0 | 0 | 0 | 0 | 32943.88
2022053018 | 2 | 0.83896 | 67116.8 | 0.60362 | 21730.32 | 0.63436 | 7612.32 | 1 | 5000 | 21730.32 | 7612.32 | 0 | 0 | 0 | 0 | 32774.16 | 0 | 0 | 0 | 0 | 0 | 32774.16
2022053019 | 2 | 0.82415 | 65932 | 0.64196 | 23110.56 | 0.48313 | 5797.56 | 1 | 5000 | 23110.56 | 5797.56 | 0 | 0 | 0 | 0 | 32023.88 | 0 | 0 | 0 | 0 | 0 | 32023.88
2022053020 | 2 | 0.79821 | 63856.8 | 0.67604 | 24337.44 | 0.25637 | 3076.44 | 1 | 5000 | 24337.44 | 3076.44 | 0 | 0 | 0 | 0 | 31442.92 | 0 | 0 | 0 | 0 | 0 | 31442.92
2022053021 | 2 | 0.77164 | 61731.2 | 0.6682 | 24055.2 | 0.03687 | 442.44 | 1 | 5000 | 24055.2 | 442.44 | 0 | 0 | 0 | 0 | 32233.56 | 0 | 0 | 0 | 0 | 0 | 32233.56
2022053022 | 2 | 0.75245 | 60196 | 0.66587 | 23971.32 | 0 | 0 | 1 | 5000 | 23971.32 | 0 | 0 | 0 | 0 | 0 | 31224.68 | 0 | 0 | 0 | 0 | 0 | 31224.68
2022053023 | 2 | 0.71352 | 57081.6 | 0.70109 | 25239.24 | 0 | 0 | 1 | 5000 | 25239.24 | 0 | 0 | 0 | 0 | 0 | 26842.36 | 0 | 0 | 0 | 0 | 0 | 26842.36
2022053024 | 2 | 0.67026 | 53620.8 | 0.72657 | 26156.52 | 0 | 0 | 1 | 5000 | 26156.52 | 0 | 0 | 0 | 0 | 0 | 22464.28 | 0 | 0 | 0 | 0 | 0 | 22464.28
2022053101 | 3 | 0.63226 | 50580.8 | 0.73092 | 26313.12 | 0 | 0 | 1 | 5000 | 26313.12 | 0 | 0 | 0 | 0 | 0 | 19267.68 | 0 | 0 | 0 | 0 | 0 | 19267.68
2022053102 | 3 | 0.60404 | 48323.2 | 0.72094 | 25953.84 | 0 | 0 | 1 | 5000 | 25953.84 | 0 | 0 | 0 | 0 | 0 | 17369.36 | 0 | 0 | 0 | 0 | 0 | 17369.36
2022053103 | 3 | 0.58506 | 46804.8 | 0.71009 | 25563.24 | 0 | 0 | 1 | 5000 | 25563.24 | 0 | 0 | 0 | 0 | 0 | 16241.56 | 0 | 0 | 0 | 0 | 0 | 16241.56
2022053104 | 3 | 0.57436 | 45948.8 | 0.6978 | 25120.8 | 0 | 0 | 1 | 5000 | 25120.8 | 0 | 0 | 0 | 0 | 0 | 15828 | 0 | 0 | 0 | 0 | 0 | 15828
2022053105 | 3 | 0.5719 | 45752 | 0.6745 | 24282 | 0 | 0 | 1 | 5000 | 24282 | 0 | 0 | 0 | 0 | 0 | 16470 | 0 | 0 | 0 | 0 | 0 | 16470
2022053106 | 3 | 0.583 | 46640 | 0.64904 | 23365.44 | 0 | 0 | 1 | 5000 | 23365.44 | 0 | 0 | 0 | 0 | 0 | 18274.56 | 0 | 0 | 0 | 0 | 0 | 18274.56
2022053107 | 3 | 0.59771 | 47816.8 | 0.61489 | 22136.04 | 0.0045 | 54 | 1 | 5000 | 22136.04 | 54 | 0 | 0 | 0 | 0 | 20626.76 | 0 | 0 | 0 | 0 | 0 | 20626.76
2022053108 | 3 | 0.61469 | 49175.2 | 0.58081 | 20909.16 | 0.13609 | 1633.08 | 1 | 5000 | 20909.16 | 1633.08 | 0 | 0 | 0 | 0 | 21632.96 | 0 | 0 | 0 | 0 | 0 | 21632.96
2022053109 | 3 | 0.64848 | 51878.4 | 0.59911 | 21567.96 | 0.33467 | 4016.04 | 1 | 5000 | 21567.96 | 4016.04 | 0 | 0 | 0 | 0 | 21294.4 | 0 | 0 | 0 | 0 | 0 | 21294.4
2022053110 | 3 | 0.68444 | 54755.2 | 0.61841 | 22262.76 | 0.36063 | 4327.56 | 1 | 5000 | 22262.76 | 4327.56 | 0 | 0 | 0 | 0 | 23164.88 | 0 | 0 | 0 | 0 | 0 | 23164.88
2022053111 | 3 | 0.72675 | 58140 | 0.59906 | 21566.16 | 0.45143 | 5417.16 | 1 | 5000 | 21566.16 | 5417.16 | 0 | 0 | 0 | 0 | 26156.68 | 0 | 0 | 0 | 0 | 0 | 26156.68
2022053112 | 3 | 0.77088 | 61670.4 | 0.55007 | 19802.52 | 0.60486 | 7258.32 | 1 | 5000 | 19802.52 | 7258.32 | 0 | 0 | 0 | 0 | 29609.56 | 0 | 0 | 0 | 0 | 0 | 29609.56
2022053113 | 3 | 0.8087 | 64696 | 0.4918 | 17704.8 | 0.75374 | 9044.88 | 1 | 5000 | 17704.8 | 9044.88 | 0 | 0 | 0 | 0 | 32946.32 | 0 | 0 | 0 | 0 | 0 | 32946.32
2022053114 | 3 | 0.84176 | 67340.8 | 0.4562 | 16423.2 | 0.76821 | 9218.52 | 1 | 5000 | 16423.2 | 9218.52 | 0 | 0 | 0 | 0 | 36699.08 | 0 | 0 | 0 | 0 | 0 | 36699.08
2022053115 | 3 | 0.8682 | 69456 | 0.4514 | 16250.4 | 0.76463 | 9175.56 | 1 | 5000 | 16250.4 | 9175.56 | 0 | 0 | 0 | 0 | 39030.04 | 0 | 0 | 0 | 0 | 0 | 39030.04
2022053116 | 3 | 0.88957 | 71165.6 | 0.46501 | 16740.36 | 0.72803 | 8736.36 | 1 | 5000 | 16740.36 | 8736.36 | 0 | 0 | 0 | 0 | 40688.88 | 0 | 0 | 0 | 0 | 0 | 40688.88
2022053117 | 3 | 0.89813 | 71850.4 | 0.49448 | 17801.28 | 0.62236 | 7468.32 | 1 | 5000 | 17801.28 | 7468.32 | 0 | 0 | 0 | 0 | 41580.8 | 0 | 0 | 0 | 0 | 0 | 41580.8
2022053118 | 3 | 0.89575 | 71660 | 0.55572 | 20005.92 | 0.54938 | 6592.56 | 1 | 5000 | 20005.92 | 6592.56 | 0 | 0 | 0 | 0 | 40061.52 | 0 | 0 | 0 | 0 | 0 | 40061.52
2022053119 | 3 | 0.87773 | 70218.4 | 0.6219 | 22388.4 | 0.4441 | 5329.2 | 1 | 5000 | 22388.4 | 5329.2 | 0 | 0 | 0 | 0 | 37500.8 | 0 | 0 | 0 | 0 | 0 | 37500.8
2022053120 | 3 | 0.84546 | 67636.8 | 0.65873 | 23714.28 | 0.21313 | 2557.56 | 1 | 5000 | 23714.28 | 2557.56 | 0 | 0 | 0 | 0 | 36364.96 | 0 | 0 | 0 | 0 | 0 | 36364.96
2022053121 | 3 | 0.81143 | 64914.4 | 0.66304 | 23869.44 | 0.02701 | 324.12 | 1 | 5000 | 23869.44 | 324.12 | 0 | 0 | 0 | 0 | 35720.84 | 0 | 0 | 0 | 0 | 0 | 35720.84
2022053122 | 3 | 0.78516 | 62812.8 | 0.6428 | 23140.8 | 0 | 0 | 1 | 5000 | 23140.8 | 0 | 0 | 0 | 0 | 0 | 34672 | 0 | 0 | 0 | 0 | 0 | 34672
2022053123 | 3 | 0.73902 | 59121.6 | 0.62915 | 22649.4 | 0 | 0 | 1 | 5000 | 22649.4 | 0 | 0 | 0 | 0 | 0 | 31472.2 | 0 | 0 | 0 | 0 | 0 | 31472.2
2022053124 | 3 | 0.68822 | 55057.6 | 0.60837 | 21901.32 | 0 | 0 | 1 | 5000 | 21901.32 | 0 | 0 | 0 | 0 | 0 | 28156.28 | 0 | 0 | 0 | 0 | 0 | 28156.28
2022060101 | 4 | 0.64347 | 51477.6 | 0.55833 | 20099.88 | 0 | 0 | 1 | 5000 | 20099.88 | 0 | 0 | 0 | 0 | 0 | 26377.72 | 0 | 0 | 0 | 0 | 0 | 26377.72
2022060102 | 4 | 0.60933 | 48746.4 | 0.48148 | 17333.28 | 0 | 0 | 1 | 5000 | 17333.28 | 0 | 0 | 0 | 0 | 0 | 26413.12 | 0 | 0 | 0 | 0 | 0 | 26413.12
2022060103 | 4 | 0.58539 | 46831.2 | 0.45995 | 16558.2 | 0 | 0 | 1 | 5000 | 16558.2 | 0 | 0 | 0 | 0 | 0 | 25273 | 0 | 0 | 0 | 0 | 0 | 25273
2022060104 | 4 | 0.56838 | 45470.4 | 0.42927 | 15453.72 | 0 | 0 | 1 | 5000 | 15453.72 | 0 | 0 | 0 | 0 | 0 | 25016.68 | 0 | 0 | 0 | 0 | 0 | 25016.68
2022060105 | 4 | 0.56468 | 45174.4 | 0.42684 | 15366.24 | 0 | 0 | 1 | 5000 | 15366.24 | 0 | 0 | 0 | 0 | 0 | 24808.16 | 0 | 0 | 0 | 0 | 0 | 24808.16
2022060106 | 4 | 0.57378 | 45902.4 | 0.41347 | 14884.92 | 0 | 0 | 1 | 5000 | 14884.92 | 0 | 0 | 0 | 0 | 0 | 26017.48 | 0 | 0 | 0 | 0 | 0 | 26017.48
2022060107 | 4 | 0.59333 | 47466.4 | 0.37956 | 13664.16 | 0.00236 | 28.32 | 1 | 5000 | 13664.16 | 28.32 | 0 | 0 | 0 | 0 | 28773.92 | 0 | 0 | 0 | 0 | 0 | 28773.92
2022060108 | 4 | 0.60242 | 48193.6 | 0.35756 | 12872.16 | 0.08977 | 1077.24 | 1 | 5000 | 12872.16 | 1077.24 | 0 | 0 | 0 | 0 | 29244.2 | 0 | 0 | 0 | 0 | 0 | 29244.2
2022060109 | 4 | 0.62946 | 50356.8 | 0.36702 | 13212.72 | 0.31978 | 3837.36 | 1 | 5000 | 13212.72 | 3837.36 | 0 | 0 | 0 | 0 | 28306.72 | 0 | 0 | 0 | 0 | 0 | 28306.72
2022060110 | 4 | 0.66817 | 53453.6 | 0.43888 | 15799.68 | 0.48453 | 5814.36 | 1 | 5000 | 15799.68 | 5814.36 | 0 | 0 | 0 | 0 | 26839.56 | 0 | 0 | 0 | 0 | 0 | 26839.56
2022060111 | 4 | 0.71194 | 56955.2 | 0.43339 | 15602.04 | 0.63931 | 7671.72 | 1 | 5000 | 15602.04 | 7671.72 | 0 | 0 | 0 | 0 | 28681.44 | 0 | 0 | 0 | 0 | 0 | 28681.44
2022060112 | 4 | 0.75608 | 60486.4 | 0.38625 | 13905 | 0.67087 | 8050.44 | 1 | 5000 | 13905 | 8050.44 | 0 | 0 | 0 | 0 | 33530.96 | 0 | 0 | 0 | 0 | 0 | 33530.96
2022060113 | 4 | 0.79783 | 63826.4 | 0.33689 | 12128.04 | 0.68189 | 8182.68 | 1 | 5000 | 12128.04 | 8182.68 | 0 | 0 | 0 | 0 | 38515.68 | 0 | 0 | 0 | 0 | 0 | 38515.68
2022060114 | 4 | 0.83473 | 66778.4 | 0.31936 | 11496.96 | 0.67393 | 8087.16 | 1 | 5000 | 11496.96 | 8087.16 | 0 | 0 | 0 | 0 | 42194.28 | 0 | 0 | 0 | 0 | 0 | 42194.28
2022060115 | 4 | 0.85454 | 68363.2 | 0.33192 | 11949.12 | 0.65688 | 7882.56 | 1 | 5000 | 11949.12 | 7882.56 | 0 | 0 | 0 | 0 | 43531.52 | 0 | 0 | 0 | 0 | 0 | 43531.52
2022060116 | 4 | 0.85597 | 68477.6 | 0.3517 | 12661.2 | 0.59255 | 7110.6 | 1 | 5000 | 12661.2 | 7110.6 | 0 | 0 | 0 | 0 | 43705.8 | 0 | 0 | 0 | 0 | 0 | 43705.8
2022060117 | 4 | 0.84538 | 67630.4 | 0.39317 | 14154.12 | 0.40589 | 4870.68 | 1 | 5000 | 14154.12 | 4870.68 | 0 | 0 | 0 | 0 | 43605.6 | 0 | 0 | 0 | 0 | 0 | 43605.6
2022060118 | 4 | 0.8343 | 66744 | 0.45498 | 16379.28 | 0.24665 | 2959.8 | 1 | 5000 | 16379.28 | 2959.8 | 0 | 0 | 0 | 0 | 42404.92 | 0 | 0 | 0 | 0 | 0 | 42404.92
2022060119 | 4 | 0.81847 | 65477.6 | 0.48517 | 17466.12 | 0.18073 | 2168.76 | 1 | 5000 | 17466.12 | 2168.76 | 0 | 0 | 0 | 0 | 40842.72 | 0 | 0 | 0 | 0 | 0 | 40842.72
2022060120 | 4 | 0.78907 | 63125.6 | 0.43812 | 15772.32 | 0.05342 | 641.04 | 1 | 5000 | 15772.32 | 641.04 | 0 | 0 | 0 | 0 | 41712.24 | 0 | 0 | 0 | 0 | 0 | 41712.24
2022060121 | 4 | 0.75943 | 60754.4 | 0.45132 | 16247.52 | 0.00284 | 34.08 | 1 | 5000 | 16247.52 | 34.08 | 0 | 0 | 0 | 0 | 39472.8 | 0 | 0 | 0 | 0 | 0 | 39472.8
2022060122 | 4 | 0.73025 | 58420 | 0.46145 | 16612.2 | 0 | 0 | 1 | 5000 | 16612.2 | 0 | 0 | 0 | 0 | 0 | 36807.8 | 0 | 0 | 0 | 0 | 0 | 36807.8
2022060123 | 4 | 0.68703 | 54962.4 | 0.46102 | 16596.72 | 0 | 0 | 1 | 5000 | 16596.72 | 0 | 0 | 0 | 0 | 0 | 33365.68 | 0 | 0 | 0 | 0 | 0 | 33365.68
2022060124 | 4 | 0.63834 | 51067.2 | 0.47911 | 17247.96 | 0 | 0 | 1 | 5000 | 17247.96 | 0 | 0 | 0 | 0 | 0 | 28819.24 | 0 | 0 | 0 | 0 | 0 | 28819.24
2022060201 | 5 | 0.59745 | 47796 | 0.42105 | 15157.8 | 0 | 0 | 1 | 5000 | 15157.8 | 0 | 0 | 0 | 0 | 0 | 27638.2 | 0 | 0 | 0 | 0 | 0 | 27638.2
2022060202 | 5 | 0.56868 | 45494.4 | 0.37722 | 13579.92 | 0 | 0 | 1 | 5000 | 13579.92 | 0 | 0 | 0 | 0 | 0 | 26914.48 | 0 | 0 | 0 | 0 | 0 | 26914.48
2022060203 | 5 | 0.54781 | 43824.8 | 0.38931 | 14015.16 | 0 | 0 | 1 | 5000 | 14015.16 | 0 | 0 | 0 | 0 | 0 | 24809.64 | 0 | 0 | 0 | 0 | 0 | 24809.64
2022060204 | 5 | 0.53087 | 42469.6 | 0.30433 | 10955.88 | 0 | 0 | 1 | 5000 | 10955.88 | 0 | 0 | 0 | 0 | 0 | 26513.72 | 0 | 0 | 0 | 0 | 0 | 26513.72
2022060205 | 5 | 0.5279 | 42232 | 0.23108 | 8318.88 | 0 | 0 | 1 | 5000 | 8318.88 | 0 | 0 | 0 | 0 | 0 | 28913.12 | 0 | 0 | 0 | 0 | 0 | 28913.12
2022060206 | 5 | 0.52699 | 42159.2 | 0.16011 | 5763.96 | 0 | 0 | 1 | 5000 | 5763.96 | 0 | 0 | 0 | 0 | 0 | 31395.24 | 0 | 0 | 0 | 0 | 0 | 31395.24
2022060207 | 5 | 0.54282 | 43425.6 | 0.15521 | 5587.56 | 0.00072 | 8.64 | 1 | 5000 | 5587.56 | 8.64 | 0 | 0 | 0 | 0 | 32829.4 | 0 | 0 | 0 | 0 | 0 | 32829.4
2022060208 | 5 | 0.5553 | 44424 | 0.14717 | 5298.12 | 0.04526 | 543.12 | 1 | 5000 | 5298.12 | 543.12 | 0 | 0 | 0 | 0 | 33582.76 | 0 | 0 | 0 | 0 | 0 | 33582.76
2022060209 | 5 | 0.57555 | 46044 | 0.13557 | 4880.52 | 0.13915 | 1669.8 | 1 | 5000 | 4880.52 | 1669.8 | 0 | 0 | 0 | 0 | 34493.68 | 0 | 0 | 0 | 0 | 0 | 34493.68
2022060210 | 5 | 0.60044 | 48035.2 | 0.12638 | 4549.68 | 0.19817 | 2378.04 | 1 | 5000 | 4549.68 | 2378.04 | 0 | 0 | 0 | 0 | 36107.48 | 0 | 0 | 0 | 0 | 0 | 36107.48
2022060211 | 5 | 0.6298 | 50384 | 0.10248 | 3689.28 | 0.31228 | 3747.36 | 1 | 5000 | 3689.28 | 3747.36 | 0 | 0 | 0 | 0 | 37947.36 | 0 | 0 | 0 | 0 | 0 | 37947.36
2022060212 | 5 | 0.66143 | 52914.4 | 0.08494 | 3057.84 | 0.40412 | 4849.44 | 1 | 5000 | 3057.84 | 4849.44 | 0 | 0 | 0 | 0 | 40007.12 | 0 | 0 | 0 | 0 | 0 | 40007.12
2022060213 | 5 | 0.69382 | 55505.6 | 0.07412 | 2668.32 | 0.45424 | 5450.88 | 1 | 5000 | 2668.32 | 5450.88 | 0 | 0 | 0 | 0 | 42386.4 | 0 | 0 | 0 | 0 | 0 | 42386.4
2022060214 | 5 | 0.72616 | 58092.8 | 0.07712 | 2776.32 | 0.48784 | 5854.08 | 1 | 5000 | 2776.32 | 5854.08 | 0 | 0 | 0 | 0 | 44462.4 | 0 | 0 | 0 | 0 | 0 | 44462.4
2022060215 | 5 | 0.75884 | 60707.2 | 0.09355 | 3367.8 | 0.54026 | 6483.12 | 1 | 5000 | 3367.8 | 6483.12 | 0 | 0 | 0 | 0 | 45856.28 | 0 | 0 | 0 | 0 | 0 | 45856.28
2022060216 | 5 | 0.78729 | 62983.2 | 0.10084 | 3630.24 | 0.56426 | 6771.12 | 1 | 5000 | 3630.24 | 6771.12 | 0 | 0 | 0 | 0 | 47581.84 | 0 | 0 | 0 | 0 | 0 | 47581.84
2022060217 | 5 | 0.8051 | 64408 | 0.11099 | 3995.64 | 0.57786 | 6934.32 | 1 | 5000 | 3995.64 | 6934.32 | 0 | 0 | 0 | 0 | 48478.04 | 0 | 0 | 0 | 0 | 0 | 48478.04
2022060218 | 5 | 0.80958 | 64766.4 | 0.12707 | 4574.52 | 0.56042 | 6725.04 | 1 | 5000 | 4574.52 | 6725.04 | 0 | 0 | 0 | 0 | 48466.84 | 0 | 0 | 0 | 0 | 0 | 48466.84
2022060219 | 5 | 0.79296 | 63436.8 | 0.15306 | 5510.16 | 0.41307 | 4956.84 | 1 | 5000 | 5510.16 | 4956.84 | 0 | 0 | 0 | 0 | 47969.8 | 0 | 0 | 0 | 0 | 0 | 47969.8
2022060220 | 5 | 0.76231 | 60984.8 | 0.16888 | 6079.68 | 0.16923 | 2030.76 | 1 | 5000 | 6079.68 | 2030.76 | 0 | 0 | 0 | 0 | 47874.36 | 0 | 0 | 0 | 0 | 0 | 47874.36
2022060221 | 5 | 0.73216 | 58572.8 | 0.17802 | 6408.72 | 0.01619 | 194.28 | 1 | 5000 | 6408.72 | 194.28 | 0 | 0 | 0 | 0 | 46969.8 | 0 | 0 | 0 | 0 | 0 | 46969.8
2022060222 | 5 | 0.70492 | 56393.6 | 0.20618 | 7422.48 | 0 | 0 | 1 | 5000 | 7422.48 | 0 | 0 | 0 | 0 | 0 | 43971.12 | 0 | 0 | 0 | 0 | 0 | 43971.12
2022060223 | 5 | 0.66001 | 52800.8 | 0.21891 | 7880.76 | 0 | 0 | 1 | 5000 | 7880.76 | 0 | 0 | 0 | 0 | 0 | 39920.04 | 0 | 0 | 0 | 0 | 0 | 39920.04
2022060224 | 5 | 0.61217 | 48973.6 | 0.22493 | 8097.48 | 0 | 0 | 1 | 5000 | 8097.48 | 0 | 0 | 0 | 0 | 0 | 35876.12 | 0 | 0 | 0 | 0 | 0 | 35876.12
2022060301 | 6 | 0.57027 | 45621.6 | 0.25124 | 9044.64 | 0 | 0 | 1 | 5000 | 9044.64 | 0 | 0 | 0 | 0 | 0 | 31576.96 | 0 | 0 | 0 | 0 | 0 | 31576.96
2022060302 | 6 | 0.53932 | 43145.6 | 0.26132 | 9407.52 | 0 | 0 | 1 | 5000 | 9407.52 | 0 | 0 | 0 | 0 | 0 | 28738.08 | 0 | 0 | 0 | 0 | 0 | 28738.08
2022060303 | 6 | 0.51677 | 41341.6 | 0.24826 | 8937.36 | 0 | 0 | 1 | 5000 | 8937.36 | 0 | 0 | 0 | 0 | 0 | 27404.24 | 0 | 0 | 0 | 0 | 0 | 27404.24
2022060304 | 6 | 0.50456 | 40364.8 | 0.24231 | 8723.16 | 0 | 0 | 1 | 5000 | 8723.16 | 0 | 0 | 0 | 0 | 0 | 26641.64 | 0 | 0 | 0 | 0 | 0 | 26641.64
2022060305 | 6 | 0.49787 | 39829.6 | 0.25844 | 9303.84 | 0 | 0 | 1 | 5000 | 9303.84 | 0 | 0 | 0 | 0 | 0 | 25525.76 | 0 | 0 | 0 | 0 | 0 | 25525.76
2022060306 | 6 | 0.51039 | 40831.2 | 0.28612 | 10300.32 | 0 | 0 | 1 | 5000 | 10300.32 | 0 | 0 | 0 | 0 | 0 | 25530.88 | 0 | 0 | 0 | 0 | 0 | 25530.88
2022060307 | 6 | 0.52593 | 42074.4 | 0.20992 | 7557.12 | 0.00426 | 51.12 | 1 | 5000 | 7557.12 | 51.12 | 0 | 0 | 0 | 0 | 29466.16 | 0 | 0 | 0 | 0 | 0 | 29466.16
2022060308 | 6 | 0.54303 | 43442.4 | 0.1584 | 5702.4 | 0.107 | 1284 | 1 | 5000 | 5702.4 | 1284 | 0 | 0 | 0 | 0 | 31456 | 0 | 0 | 0 | 0 | 0 | 31456
2022060309 | 6 | 0.57011 | 45608.8 | 0.13033 | 4691.88 | 0.38344 | 4601.28 | 1 | 5000 | 4691.88 | 4601.28 | 0 | 0 | 0 | 0 | 31315.64 | 0 | 0 | 0 | 0 | 0 | 31315.64
2022060310 | 6 | 0.6045 | 48360 | 0.11458 | 4124.88 | 0.56071 | 6728.52 | 1 | 5000 | 4124.88 | 6728.52 | 0 | 0 | 0 | 0 | 32506.6 | 0 | 0 | 0 | 0 | 0 | 32506.6
2022060311 | 6 | 0.64203 | 51362.4 | 0.0961 | 3459.6 | 0.63466 | 7615.92 | 1 | 5000 | 3459.6 | 7615.92 | 0 | 0 | 0 | 0 | 35286.88 | 0 | 0 | 0 | 0 | 0 | 35286.88
2022060312 | 6 | 0.67633 | 54106.4 | 0.11842 | 4263.12 | 0.65044 | 7805.28 | 1 | 5000 | 4263.12 | 7805.28 | 0 | 0 | 0 | 0 | 37038 | 0 | 0 | 0 | 0 | 0 | 37038
2022060313 | 6 | 0.70454 | 56363.2 | 0.13982 | 5033.52 | 0.64673 | 7760.76 | 1 | 5000 | 5033.52 | 7760.76 | 0 | 0 | 0 | 0 | 38568.92 | 0 | 0 | 0 | 0 | 0 | 38568.92
2022060314 | 6 | 0.73532 | 58825.6 | 0.13264 | 4775.04 | 0.66051 | 7926.12 | 1 | 5000 | 4775.04 | 7926.12 | 0 | 0 | 0 | 0 | 41124.44 | 0 | 0 | 0 | 0 | 0 | 41124.44
2022060315 | 6 | 0.75904 | 60723.2 | 0.13907 | 5006.52 | 0.69629 | 8355.48 | 1 | 5000 | 5006.52 | 8355.48 | 0 | 0 | 0 | 0 | 42361.2 | 0 | 0 | 0 | 0 | 0 | 42361.2
2022060316 | 6 | 0.77496 | 61996.8 | 0.14309 | 5151.24 | 0.70043 | 8405.16 | 1 | 5000 | 5151.24 | 8405.16 | 0 | 0 | 0 | 0 | 43440.4 | 0 | 0 | 0 | 0 | 0 | 43440.4
2022060317 | 6 | 0.77956 | 62364.8 | 0.16488 | 5935.68 | 0.7082 | 8498.4 | 1 | 5000 | 5935.68 | 8498.4 | 0 | 0 | 0 | 0 | 42930.72 | 0 | 0 | 0 | 0 | 0 | 42930.72
2022060318 | 6 | 0.77109 | 61687.2 | 0.19021 | 6847.56 | 0.63544 | 7625.28 | 1 | 5000 | 6847.56 | 7625.28 | 0 | 0 | 0 | 0 | 42214.36 | 0 | 0 | 0 | 0 | 0 | 42214.36
2022060319 | 6 | 0.74659 | 59727.2 | 0.21302 | 7668.72 | 0.48008 | 5760.96 | 1 | 5000 | 7668.72 | 5760.96 | 0 | 0 | 0 | 0 | 41297.52 | 0 | 0 | 0 | 0 | 0 | 41297.52
2022060320 | 6 | 0.71812 | 57449.6 | 0.24174 | 8702.64 | 0.15813 | 1897.56 | 1 | 5000 | 8702.64 | 1897.56 | 0 | 0 | 0 | 0 | 41849.4 | 0 | 0 | 0 | 0 | 0 | 41849.4
2022060321 | 6 | 0.69121 | 55296.8 | 0.25202 | 9072.72 | 0.00596 | 71.52 | 1 | 5000 | 9072.72 | 71.52 | 0 | 0 | 0 | 0 | 41152.56 | 0 | 0 | 0 | 0 | 0 | 41152.56
2022060322 | 6 | 0.66711 | 53368.8 | 0.26162 | 9418.32 | 0 | 0 | 1 | 5000 | 9418.32 | 0 | 0 | 0 | 0 | 0 | 38950.48 | 0 | 0 | 0 | 0 | 0 | 38950.48
2022060323 | 6 | 0.62932 | 50345.6 | 0.26092 | 9393.12 | 0 | 0 | 1 | 5000 | 9393.12 | 0 | 0 | 0 | 0 | 0 | 35952.48 | 0 | 0 | 0 | 0 | 0 | 35952.48
2022060324 | 6 | 0.58813 | 47050.4 | 0.27167 | 9780.12 | 0 | 0 | 1 | 5000 | 9780.12 | 0 | 0 | 0 | 0 | 0 | 32270.28 | 0 | 0 | 0 | 0 | 0 | 32270.28
2022060401 | 7 | 0.55417 | 44333.6 | 0.29563 | 10642.68 | 0 | 0 | 1 | 5000 | 10642.68 | 0 | 0 | 0 | 0 | 0 | 28690.92 | 0 | 0 | 0 | 0 | 0 | 28690.92
2022060402 | 7 | 0.52599 | 42079.2 | 0.31449 | 11321.64 | 0 | 0 | 1 | 5000 | 11321.64 | 0 | 0 | 0 | 0 | 0 | 25757.56 | 0 | 0 | 0 | 0 | 0 | 25757.56
2022060403 | 7 | 0.50351 | 40280.8 | 0.29366 | 10571.76 | 0 | 0 | 1 | 5000 | 10571.76 | 0 | 0 | 0 | 0 | 0 | 24709.04 | 0 | 0 | 0 | 0 | 0 | 24709.04
2022060404 | 7 | 0.49036 | 39228.8 | 0.26021 | 9367.56 | 0 | 0 | 1 | 5000 | 9367.56 | 0 | 0 | 0 | 0 | 0 | 24861.24 | 0 | 0 | 0 | 0 | 0 | 24861.24
2022060405 | 7 | 0.48335 | 38668 | 0.24303 | 8749.08 | 0 | 0 | 1 | 5000 | 8749.08 | 0 | 0 | 0 | 0 | 0 | 24918.92 | 0 | 0 | 0 | 0 | 0 | 24918.92
2022060406 | 7 | 0.48173 | 38538.4 | 0.23291 | 8384.76 | 0 | 0 | 1 | 5000 | 8384.76 | 0 | 0 | 0 | 0 | 0 | 25153.64 | 0 | 0 | 0 | 0 | 0 | 25153.64
2022060407 | 7 | 0.48244 | 38595.2 | 0.1717 | 6181.2 | 0.00376 | 45.12 | 1 | 5000 | 6181.2 | 45.12 | 0 | 0 | 0 | 0 | 27368.88 | 0 | 0 | 0 | 0 | 0 | 27368.88
2022060408 | 7 | 0.49354 | 39483.2 | 0.16564 | 5963.04 | 0.11648 | 1397.76 | 1 | 5000 | 5963.04 | 1397.76 | 0 | 0 | 0 | 0 | 27122.4 | 0 | 0 | 0 | 0 | 0 | 27122.4
2022060409 | 7 | 0.52227 | 41781.6 | 0.14022 | 5047.92 | 0.37482 | 4497.84 | 1 | 5000 | 5047.92 | 4497.84 | 0 | 0 | 0 | 0 | 27235.84 | 0 | 0 | 0 | 0 | 0 | 27235.84
2022060410 | 7 | 0.5606 | 44848 | 0.11982 | 4313.52 | 0.59724 | 7166.88 | 1 | 5000 | 4313.52 | 7166.88 | 0 | 0 | 0 | 0 | 28367.6 | 0 | 0 | 0 | 0 | 0 | 28367.6
2022060411 | 7 | 0.60139 | 48111.2 | 0.11676 | 4203.36 | 0.71217 | 8546.04 | 1 | 5000 | 4203.36 | 8546.04 | 0 | 0 | 0 | 0 | 30361.8 | 0 | 0 | 0 | 0 | 0 | 30361.8
2022060412 | 7 | 0.64222 | 51377.6 | 0.14927 | 5373.72 | 0.73423 | 8810.76 | 1 | 5000 | 5373.72 | 8810.76 | 0 | 0 | 0 | 0 | 32193.12 | 0 | 0 | 0 | 0 | 0 | 32193.12
2022060413 | 7 | 0.67759 | 54207.2 | 0.15887 | 5719.32 | 0.74812 | 8977.44 | 1 | 5000 | 5719.32 | 8977.44 | 0 | 0 | 0 | 0 | 34510.44 | 0 | 0 | 0 | 0 | 0 | 34510.44
2022060414 | 7 | 0.6966 | 55728 | 0.16906 | 6086.16 | 0.72629 | 8715.48 | 1 | 5000 | 6086.16 | 8715.48 | 0 | 0 | 0 | 0 | 35926.36 | 0 | 0 | 0 | 0 | 0 | 35926.36
2022060415 | 7 | 0.73513 | 58810.4 | 0.1648 | 5932.8 | 0.72239 | 8668.68 | 1 | 5000 | 5932.8 | 8668.68 | 0 | 0 | 0 | 0 | 39208.92 | 0 | 0 | 0 | 0 | 0 | 39208.92
2022060416 | 7 | 0.76678 | 61342.4 | 0.16746 | 6028.56 | 0.67826 | 8139.12 | 1 | 5000 | 6028.56 | 8139.12 | 0 | 0 | 0 | 0 | 42174.72 | 0 | 0 | 0 | 0 | 0 | 42174.72
2022060417 | 7 | 0.7855 | 62840 | 0.17531 | 6311.16 | 0.64943 | 7793.16 | 1 | 5000 | 6311.16 | 7793.16 | 0 | 0 | 0 | 0 | 43735.68 | 0 | 0 | 0 | 0 | 0 | 43735.68
2022060418 | 7 | 0.78296 | 62636.8 | 0.18725 | 6741 | 0.62197 | 7463.64 | 1 | 5000 | 6741 | 7463.64 | 0 | 0 | 0 | 0 | 43432.16 | 0 | 0 | 0 | 0 | 0 | 43432.16
2022060419 | 7 | 0.77338 | 61870.4 | 0.22239 | 8006.04 | 0.4953 | 5943.6 | 1 | 5000 | 8006.04 | 5943.6 | 0 | 0 | 0 | 0 | 42920.76 | 0 | 0 | 0 | 0 | 0 | 42920.76
2022060420 | 7 | 0.7509 | 60072 | 0.28528 | 10270.08 | 0.27468 | 3296.16 | 1 | 5000 | 10270.08 | 3296.16 | 0 | 0 | 0 | 0 | 41505.76 | 0 | 0 | 0 | 0 | 0 | 41505.76
2022060421 | 7 | 0.72413 | 57930.4 | 0.35246 | 12688.56 | 0.02677 | 321.24 | 1 | 5000 | 12688.56 | 321.24 | 0 | 0 | 0 | 0 | 39920.6 | 0 | 0 | 0 | 0 | 0 | 39920.6
2022060422 | 7 | 0.70469 | 56375.2 | 0.47227 | 17001.72 | 0 | 0 | 1 | 5000 | 17001.72 | 0 | 0 | 0 | 0 | 0 | 34373.48 | 0 | 0 | 0 | 0 | 0 | 34373.48
2022060423 | 7 | 0.66966 | 53572.8 | 0.57202 | 20592.72 | 0 | 0 | 1 | 5000 | 20592.72 | 0 | 0 | 0 | 0 | 0 | 27980.08 | 0 | 0 | 0 | 0 | 0 | 27980.08
2022060424 | 7 | 0.63218 | 50574.4 | 0.61476 | 22131.36 | 0 | 0 | 1 | 5000 | 22131.36 | 0 | 0 | 0 | 0 | 0 | 23443.04 | 0 | 0 | 0 | 0 | 0 | 23443.04
2022060501 | 1 | 0.5949 | 47592 | 0.62778 | 22600.08 | 0 | 0 | 1 | 5000 | 22600.08 | 0 | 0 | 0 | 0 | 0 | 19991.92 | 0 | 0 | 0 | 0 | 0 | 19991.92
2022060502 | 1 | 0.56346 | 45076.8 | 0.61688 | 22207.68 | 0 | 0 | 1 | 5000 | 22207.68 | 0 | 0 | 0 | 0 | 0 | 17869.12 | 0 | 0 | 0 | 0 | 0 | 17869.12
2022060503 | 1 | 0.53722 | 42977.6 | 0.59293 | 21345.48 | 0 | 0 | 1 | 5000 | 21345.48 | 0 | 0 | 0 | 0 | 0 | 16632.12 | 0 | 0 | 0 | 0 | 0 | 16632.12
2022060504 | 1 | 0.51829 | 41463.2 | 0.56851 | 20466.36 | 0 | 0 | 1 | 5000 | 20466.36 | 0 | 0 | 0 | 0 | 0 | 15996.84 | 0 | 0 | 0 | 0 | 0 | 15996.84
2022060505 | 1 | 0.50934 | 40747.2 | 0.56297 | 20266.92 | 0 | 0 | 1 | 5000 | 20266.92 | 0 | 0 | 0 | 0 | 0 | 15480.28 | 0 | 0 | 0 | 0 | 0 | 15480.28
2022060506 | 1 | 0.50281 | 40224.8 | 0.54997 | 19798.92 | 0 | 0 | 1 | 5000 | 19798.92 | 0 | 0 | 0 | 0 | 0 | 15425.88 | 0 | 0 | 0 | 0 | 0 | 15425.88
2022060507 | 1 | 0.49537 | 39629.6 | 0.52719 | 18978.84 | 0.00093 | 11.16 | 1 | 5000 | 18978.84 | 11.16 | 0 | 0 | 0 | 0 | 15639.6 | 0 | 0 | 0 | 0 | 0 | 15639.6
2022060508 | 1 | 0.50615 | 40492 | 0.52262 | 18814.32 | 0.06498 | 779.76 | 1 | 5000 | 18814.32 | 779.76 | 0 | 0 | 0 | 0 | 15897.92 | 0 | 0 | 0 | 0 | 0 | 15897.92
2022060509 | 1 | 0.54847 | 43877.6 | 0.5135 | 18486 | 0.39294 | 4715.28 | 1 | 5000 | 18486 | 4715.28 | 0 | 0 | 0 | 0 | 15676.32 | 0 | 0 | 0 | 0 | 0 | 15676.32
2022060510 | 1 | 0.59981 | 47984.8 | 0.49917 | 17970.12 | 0.62844 | 7541.28 | 1 | 5000 | 17970.12 | 7541.28 | 0 | 0 | 0 | 0 | 17473.4 | 0 | 0 | 0 | 0 | 0 | 17473.4
2022060511 | 1 | 0.64672 | 51737.6 | 0.44834 | 16140.24 | 0.73569 | 8828.28 | 1 | 5000 | 16140.24 | 8828.28 | 0 | 0 | 0 | 0 | 21769.08 | 0 | 0 | 0 | 0 | 0 | 21769.08
2022060512 | 1 | 0.69167 | 55333.6 | 0.38896 | 14002.56 | 0.78409 | 9409.08 | 1 | 5000 | 14002.56 | 9409.08 | 0 | 0 | 0 | 0 | 26921.96 | 0 | 0 | 0 | 0 | 0 | 26921.96
2022060513 | 1 | 0.73519 | 58815.2 | 0.34643 | 12471.48 | 0.78741 | 9448.92 | 1 | 5000 | 12471.48 | 9448.92 | 0 | 0 | 0 | 0 | 31894.8 | 0 | 0 | 0 | 0 | 0 | 31894.8
2022060514 | 1 | 0.77695 | 62156 | 0.35404 | 12745.44 | 0.77367 | 9284.04 | 1 | 5000 | 12745.44 | 9284.04 | 0 | 0 | 0 | 0 | 35126.52 | 0 | 0 | 0 | 0 | 0 | 35126.52
2022060515 | 1 | 0.81258 | 65006.4 | 0.38516 | 13865.76 | 0.72712 | 8725.44 | 1 | 5000 | 13865.76 | 8725.44 | 0 | 0 | 0 | 0 | 37415.2 | 0 | 0 | 0 | 0 | 0 | 37415.2
2022060516 | 1 | 0.83768 | 67014.4 | 0.41882 | 15077.52 | 0.71971 | 8636.52 | 1 | 5000 | 15077.52 | 8636.52 | 0 | 0 | 0 | 0 | 38300.36 | 0 | 0 | 0 | 0 | 0 | 38300.36
2022060517 | 1 | 0.85232 | 68185.6 | 0.44031 | 15851.16 | 0.70042 | 8405.04 | 1 | 5000 | 15851.16 | 8405.04 | 0 | 0 | 0 | 0 | 38929.4 | 0 | 0 | 0 | 0 | 0 | 38929.4
2022060518 | 1 | 0.85173 | 68138.4 | 0.46023 | 16568.28 | 0.64774 | 7772.88 | 1 | 5000 | 16568.28 | 7772.88 | 0 | 0 | 0 | 0 | 38797.24 | 0 | 0 | 0 | 0 | 0 | 38797.24
2022060519 | 1 | 0.83719 | 66975.2 | 0.46523 | 16748.28 | 0.52299 | 6275.88 | 1 | 5000 | 16748.28 | 6275.88 | 0 | 0 | 0 | 0 | 38951.04 | 0 | 0 | 0 | 0 | 0 | 38951.04
2022060520 | 1 | 0.80598 | 64478.4 | 0.44954 | 16183.44 | 0.25302 | 3036.24 | 1 | 5000 | 16183.44 | 3036.24 | 0 | 0 | 0 | 0 | 40258.72 | 0 | 0 | 0 | 0 | 0 | 40258.72
2022060521 | 1 | 0.7746 | 61968 | 0.43603 | 15697.08 | 0.0197 | 236.4 | 1 | 5000 | 15697.08 | 236.4 | 0 | 0 | 0 | 0 | 41034.52 | 0 | 0 | 0 | 0 | 0 | 41034.52
2022060522 | 1 | 0.74879 | 59903.2 | 0.46155 | 16615.8 | 0 | 0 | 1 | 5000 | 16615.8 | 0 | 0 | 0 | 0 | 0 | 38287.4 | 0 | 0 | 0 | 0 | 0 | 38287.4
2022060523 | 1 | 0.70566 | 56452.8 | 0.49676 | 17883.36 | 0 | 0 | 1 | 5000 | 17883.36 | 0 | 0 | 0 | 0 | 0 | 33569.44 | 0 | 0 | 0 | 0 | 0 | 33569.44
2022060524 | 1 | 0.65812 | 52649.6 | 0.53686 | 19326.96 | 0 | 0 | 1 | 5000 | 19326.96 | 0 | 0 | 0 | 0 | 0 | 28322.64 | 0 | 0 | 0 | 0 | 0 | 28322.64
2022060601 | 2 | 0.61746 | 49396.8 | 0.5806 | 20901.6 | 0 | 0 | 1 | 5000 | 20901.6 | 0 | 0 | 0 | 0 | 0 | 23495.2 | 0 | 0 | 0 | 0 | 0 | 23495.2
2022060602 | 2 | 0.58951 | 47160.8 | 0.61596 | 22174.56 | 0 | 0 | 1 | 5000 | 22174.56 | 0 | 0 | 0 | 0 | 0 | 19986.24 | 0 | 0 | 0 | 0 | 0 | 19986.24
2022060603 | 2 | 0.57095 | 45676 | 0.63695 | 22930.2 | 0 | 0 | 1 | 5000 | 22930.2 | 0 | 0 | 0 | 0 | 0 | 17745.8 | 0 | 0 | 0 | 0 | 0 | 17745.8
2022060604 | 2 | 0.56446 | 45156.8 | 0.63145 | 22732.2 | 0 | 0 | 1 | 5000 | 22732.2 | 0 | 0 | 0 | 0 | 0 | 17424.6 | 0 | 0 | 0 | 0 | 0 | 17424.6
2022060605 | 2 | 0.56002 | 44801.6 | 0.62061 | 22341.96 | 0 | 0 | 1 | 5000 | 22341.96 | 0 | 0 | 0 | 0 | 0 | 17459.64 | 0 | 0 | 0 | 0 | 0 | 17459.64
2022060606 | 2 | 0.57095 | 45676 | 0.61776 | 22239.36 | 0 | 0 | 1 | 5000 | 22239.36 | 0 | 0 | 0 | 0 | 0 | 18436.64 | 0 | 0 | 0 | 0 | 0 | 18436.64
2022060607 | 2 | 0.58624 | 46899.2 | 0.59611 | 21459.96 | 0.00195 | 23.4 | 1 | 5000 | 21459.96 | 23.4 | 0 | 0 | 0 | 0 | 20415.84 | 0 | 0 | 0 | 0 | 0 | 20415.84
2022060608 | 2 | 0.60309 | 48247.2 | 0.56083 | 20189.88 | 0.17585 | 2110.2 | 1 | 5000 | 20189.88 | 2110.2 | 0 | 0 | 0 | 0 | 20947.12 | 0 | 0 | 0 | 0 | 0 | 20947.12
2022060609 | 2 | 0.63569 | 50855.2 | 0.51462 | 18526.32 | 0.53396 | 6407.52 | 1 | 5000 | 18526.32 | 6407.52 | 0 | 0 | 0 | 0 | 20921.36 | 0 | 0 | 0 | 0 | 0 | 20921.36
2022060610 | 2 | 0.67758 | 54206.4 | 0.49355 | 17767.8 | 0.71275 | 8553 | 1 | 5000 | 17767.8 | 8553 | 0 | 0 | 0 | 0 | 22885.6 | 0 | 0 | 0 | 0 | 0 | 22885.6
2022060611 | 2 | 0.72135 | 57708 | 0.45361 | 16329.96 | 0.76691 | 9202.92 | 1 | 5000 | 16329.96 | 9202.92 | 0 | 0 | 0 | 0 | 27175.12 | 0 | 0 | 0 | 0 | 0 | 27175.12
2022060612 | 2 | 0.76528 | 61222.4 | 0.381 | 13716 | 0.80492 | 9659.04 | 1 | 5000 | 13716 | 9659.04 | 0 | 0 | 0 | 0 | 32847.36 | 0 | 0 | 0 | 0 | 0 | 32847.36
2022060613 | 2 | 0.807 | 64560 | 0.30809 | 11091.24 | 0.80929 | 9711.48 | 1 | 5000 | 11091.24 | 9711.48 | 0 | 0 | 0 | 0 | 38757.28 | 0 | 0 | 0 | 0 | 0 | 38757.28
2022060614 | 2 | 0.84832 | 67865.6 | 0.26085 | 9390.6 | 0.81138 | 9736.56 | 1 | 5000 | 9390.6 | 9736.56 | 0 | 0 | 0 | 0 | 43738.44 | 0 | 0 | 0 | 0 | 0 | 43738.44
2022060615 | 2 | 0.87852 | 70281.6 | 0.23921 | 8611.56 | 0.80463 | 9655.56 | 1 | 5000 | 8611.56 | 9655.56 | 0 | 0 | 0 | 0 | 47014.48 | 0 | 0 | 0 | 0 | 0 | 47014.48
2022060616 | 2 | 0.89577 | 71661.6 | 0.23587 | 8491.32 | 0.78272 | 9392.64 | 1 | 5000 | 8491.32 | 9392.64 | 0 | 0 | 0 | 0 | 48777.64 | 0 | 0 | 0 | 0 | 0 | 48777.64
2022060617 | 2 | 0.90663 | 72530.4 | 0.24786 | 8922.96 | 0.75316 | 9037.92 | 1 | 5000 | 8922.96 | 9037.92 | 0 | 0 | 0 | 0 | 49569.52 | 0 | 0 | 0 | 0 | 0 | 49569.52
2022060618 | 2 | 0.90661 | 72528.8 | 0.26455 | 9523.8 | 0.7134 | 8560.8 | 1 | 5000 | 9523.8 | 8560.8 | 0 | 0 | 0 | 0 | 49444.2 | 0 | 0 | 0 | 0 | 0 | 49444.2
2022060619 | 2 | 0.89585 | 71668 | 0.27181 | 9785.16 | 0.60713 | 7285.56 | 1 | 5000 | 9785.16 | 7285.56 | 0 | 0 | 0 | 0 | 49597.28 | 0 | 0 | 0 | 0 | 0 | 49597.28
2022060620 | 2 | 0.87133 | 69706.4 | 0.29069 | 10464.84 | 0.34082 | 4089.84 | 1 | 5000 | 10464.84 | 4089.84 | 0 | 0 | 0 | 0 | 50151.72 | 0 | 0 | 0 | 0 | 0 | 50151.72
2022060621 | 2 | 0.83863 | 67090.4 | 0.33601 | 12096.36 | 0.04127 | 495.24 | 1 | 5000 | 12096.36 | 495.24 | 0 | 0 | 0 | 0 | 49498.8 | 0 | 0 | 0 | 0 | 0 | 49498.8
2022060622 | 2 | 0.80825 | 64660 | 0.40474 | 14570.64 | 0 | 0 | 1 | 5000 | 14570.64 | 0 | 0 | 0 | 0 | 0 | 45089.36 | 0 | 0 | 0 | 0 | 0 | 45089.36
2022060623 | 2 | 0.75744 | 60595.2 | 0.46691 | 16808.76 | 0.00011 | 1.32 | 1 | 5000 | 16808.76 | 1.32 | 0 | 0 | 0 | 0 | 38785.12 | 0 | 0 | 0 | 0 | 0 | 38785.12
2022060624 | 2 | 0.70062 | 56049.6 | 0.48221 | 17359.56 | 0 | 0 | 1 | 5000 | 17359.56 | 0 | 0 | 0 | 0 | 0 | 33690.04 | 0 | 0 | 0 | 0 | 0 | 33690.04
2022060701 | 3 | 0.65452 | 52361.6 | 0.50118 | 18042.48 | 0 | 0 | 1 | 5000 | 18042.48 | 0 | 0 | 0 | 0 | 0 | 29319.12 | 0 | 0 | 0 | 0 | 0 | 29319.12
2022060702 | 3 | 0.62044 | 49635.2 | 0.50315 | 18113.4 | 0 | 0 | 1 | 5000 | 18113.4 | 0 | 0 | 0 | 0 | 0 | 26521.8 | 0 | 0 | 0 | 0 | 0 | 26521.8
2022060703 | 3 | 0.59515 | 47612 | 0.50087 | 18031.32 | 0 | 0 | 1 | 5000 | 18031.32 | 0 | 0 | 0 | 0 | 0 | 24580.68 | 0 | 0 | 0 | 0 | 0 | 24580.68
2022060704 | 3 | 0.58004 | 46403.2 | 0.50163 | 18058.68 | 0 | 0 | 1 | 5000 | 18058.68 | 0 | 0 | 0 | 0 | 0 | 23344.52 | 0 | 0 | 0 | 0 | 0 | 23344.52
2022060705 | 3 | 0.57602 | 46081.6 | 0.50438 | 18157.68 | 0 | 0 | 1 | 5000 | 18157.68 | 0 | 0 | 0 | 0 | 0 | 22923.92 | 0 | 0 | 0 | 0 | 0 | 22923.92
2022060706 | 3 | 0.58289 | 46631.2 | 0.48821 | 17575.56 | 0 | 0 | 1 | 5000 | 17575.56 | 0 | 0 | 0 | 0 | 0 | 24055.64 | 0 | 0 | 0 | 0 | 0 | 24055.64
2022060707 | 3 | 0.59649 | 47719.2 | 0.47646 | 17152.56 | 0.00301 | 36.12 | 1 | 5000 | 17152.56 | 36.12 | 0 | 0 | 0 | 0 | 25530.52 | 0 | 0 | 0 | 0 | 0 | 25530.52
2022060708 | 3 | 0.6146 | 49168 | 0.47669 | 17160.84 | 0.1876 | 2251.2 | 1 | 5000 | 17160.84 | 2251.2 | 0 | 0 | 0 | 0 | 24755.96 | 0 | 0 | 0 | 0 | 0 | 24755.96
2022060709 | 3 | 0.64974 | 51979.2 | 0.46788 | 16843.68 | 0.54289 | 6514.68 | 1 | 5000 | 16843.68 | 6514.68 | 0 | 0 | 0 | 0 | 23620.84 | 0 | 0 | 0 | 0 | 0 | 23620.84
2022060710 | 3 | 0.68699 | 54959.2 | 0.44866 | 16151.76 | 0.66505 | 7980.6 | 1 | 5000 | 16151.76 | 7980.6 | 0 | 0 | 0 | 0 | 25826.84 | 0 | 0 | 0 | 0 | 0 | 25826.84
2022060711 | 3 | 0.72619 | 58095.2 | 0.37164 | 13379.04 | 0.69176 | 8301.12 | 1 | 5000 | 13379.04 | 8301.12 | 0 | 0 | 0 | 0 | 31415.04 | 0 | 0 | 0 | 0 | 0 | 31415.04
2022060712 | 3 | 0.76589 | 61271.2 | 0.293 | 10548 | 0.7309 | 8770.8 | 1 | 5000 | 10548 | 8770.8 | 0 | 0 | 0 | 0 | 36952.4 | 0 | 0 | 0 | 0 | 0 | 36952.4
2022060713 | 3 | 0.80935 | 64748 | 0.23357 | 8408.52 | 0.75956 | 9114.72 | 1 | 5000 | 8408.52 | 9114.72 | 0 | 0 | 0 | 0 | 42224.76 | 0 | 0 | 0 | 0 | 0 | 42224.76
2022060714 | 3 | 0.85126 | 68100.8 | 0.20031 | 7211.16 | 0.78494 | 9419.28 | 1 | 5000 | 7211.16 | 9419.28 | 0 | 0 | 0 | 0 | 46470.36 | 0 | 0 | 0 | 0 | 0 | 46470.36
2022060715 | 3 | 0.88552 | 70841.6 | 0.19335 | 6960.6 | 0.78023 | 9362.76 | 1 | 5000 | 6960.6 | 9362.76 | 0 | 0 | 0 | 0 | 49518.24 | 0 | 0 | 0 | 0 | 0 | 49518.24
2022060716 | 3 | 0.90267 | 72213.6 | 0.20132 | 7247.52 | 0.77332 | 9279.84 | 1 | 5000 | 7247.52 | 9279.84 | 0 | 0 | 0 | 0 | 50686.24 | 0 | 0 | 0 | 0 | 0 | 50686.24
2022060717 | 3 | 0.91147 | 72917.6 | 0.22355 | 8047.8 | 0.71537 | 8584.44 | 1 | 5000 | 8047.8 | 8584.44 | 0 | 0 | 0 | 0 | 51285.36 | 0 | 0 | 0 | 0 | 0 | 51285.36
2022060718 | 3 | 0.91159 | 72927.2 | 0.25816 | 9293.76 | 0.64592 | 7751.04 | 1 | 5000 | 9293.76 | 7751.04 | 0 | 0 | 0 | 0 | 50882.4 | 0 | 0 | 0 | 0 | 0 | 50882.4
2022060719 | 3 | 0.90145 | 72116 | 0.29922 | 10771.92 | 0.53473 | 6416.76 | 1 | 5000 | 10771.92 | 6416.76 | 0 | 0 | 0 | 0 | 49927.32 | 0 | 0 | 0 | 0 | 0 | 49927.32
2022060720 | 3 | 0.87227 | 69781.6 | 0.35277 | 12699.72 | 0.27295 | 3275.4 | 1 | 5000 | 12699.72 | 3275.4 | 0 | 0 | 0 | 0 | 48806.48 | 0 | 0 | 0 | 0 | 0 | 48806.48
2022060721 | 3 | 0.83969 | 67175.2 | 0.38857 | 13988.52 | 0.03123 | 374.76 | 1 | 5000 | 13988.52 | 374.76 | 0 | 0 | 0 | 0 | 47811.92 | 0 | 0 | 0 | 0 | 0 | 47811.92
2022060722 | 3 | 0.80911 | 64728.8 | 0.40607 | 14618.52 | 0 | 0 | 1 | 5000 | 14618.52 | 0 | 0 | 0 | 0 | 0 | 45110.28 | 0 | 0 | 0 | 0 | 0 | 45110.28
2022060723 | 3 | 0.75822 | 60657.6 | 0.4254 | 15314.4 | 0 | 0 | 1 | 5000 | 15314.4 | 0 | 0 | 0 | 0 | 0 | 40343.2 | 0 | 0 | 0 | 0 | 0 | 40343.2
2022060724 | 3 | 0.70557 | 56445.6 | 0.44434 | 15996.24 | 0 | 0 | 1 | 5000 | 15996.24 | 0 | 0 | 0 | 0 | 0 | 35449.36 | 0 | 0 | 0 | 0 | 0 | 35449.36
2022060801 | 4 | 0.65794 | 52635.2 | 0.44111 | 15879.96 | 0 | 0 | 1 | 5000 | 15879.96 | 0 | 0 | 0 | 0 | 0 | 31755.24 | 0 | 0 | 0 | 0 | 0 | 31755.24
2022060802 | 4 | 0.62512 | 50009.6 | 0.45886 | 16518.96 | 0 | 0 | 1 | 5000 | 16518.96 | 0 | 0 | 0 | 0 | 0 | 28490.64 | 0 | 0 | 0 | 0 | 0 | 28490.64
2022060803 | 4 | 0.60176 | 48140.8 | 0.45709 | 16455.24 | 0 | 0 | 1 | 5000 | 16455.24 | 0 | 0 | 0 | 0 | 0 | 26685.56 | 0 | 0 | 0 | 0 | 0 | 26685.56
2022060804 | 4 | 0.5857 | 46856 | 0.42942 | 15459.12 | 0 | 0 | 1 | 5000 | 15459.12 | 0 | 0 | 0 | 0 | 0 | 26396.88 | 0 | 0 | 0 | 0 | 0 | 26396.88
2022060805 | 4 | 0.58047 | 46437.6 | 0.42218 | 15198.48 | 0 | 0 | 1 | 5000 | 15198.48 | 0 | 0 | 0 | 0 | 0 | 26239.12 | 0 | 0 | 0 | 0 | 0 | 26239.12
2022060806 | 4 | 0.58823 | 47058.4 | 0.42336 | 15240.96 | 0 | 0 | 1 | 5000 | 15240.96 | 0 | 0 | 0 | 0 | 0 | 26817.44 | 0 | 0 | 0 | 0 | 0 | 26817.44
2022060807 | 4 | 0.59962 | 47969.6 | 0.44158 | 15896.88 | 0.00406 | 48.72 | 1 | 5000 | 15896.88 | 48.72 | 0 | 0 | 0 | 0 | 27024 | 0 | 0 | 0 | 0 | 0 | 27024
2022060808 | 4 | 0.61821 | 49456.8 | 0.47786 | 17202.96 | 0.14116 | 1693.92 | 1 | 5000 | 17202.96 | 1693.92 | 0 | 0 | 0 | 0 | 25559.92 | 0 | 0 | 0 | 0 | 0 | 25559.92
2022060809 | 4 | 0.65505 | 52404 | 0.49726 | 17901.36 | 0.42924 | 5150.88 | 1 | 5000 | 17901.36 | 5150.88 | 0 | 0 | 0 | 0 | 24351.76 | 0 | 0 | 0 | 0 | 0 | 24351.76
2022060810 | 4 | 0.69173 | 55338.4 | 0.51645 | 18592.2 | 0.50762 | 6091.44 | 1 | 5000 | 18592.2 | 6091.44 | 0 | 0 | 0 | 0 | 25654.76 | 0 | 0 | 0 | 0 | 0 | 25654.76
2022060811 | 4 | 0.73291 | 58632.8 | 0.49837 | 17941.32 | 0.58914 | 7069.68 | 1 | 5000 | 17941.32 | 7069.68 | 0 | 0 | 0 | 0 | 28621.8 | 0 | 0 | 0 | 0 | 0 | 28621.8
2022060812 | 4 | 0.77029 | 61623.2 | 0.50744 | 18267.84 | 0.5721 | 6865.2 | 1 | 5000 | 18267.84 | 6865.2 | 0 | 0 | 0 | 0 | 31490.16 | 0 | 0 | 0 | 0 | 0 | 31490.16
2022060813 | 4 | 0.79615 | 63692 | 0.5112 | 18403.2 | 0.48538 | 5824.56 | 1 | 5000 | 18403.2 | 5824.56 | 0 | 0 | 0 | 0 | 34464.24 | 0 | 0 | 0 | 0 | 0 | 34464.24
2022060814 | 4 | 0.82187 | 65749.6 | 0.48756 | 17552.16 | 0.51362 | 6163.44 | 1 | 5000 | 17552.16 | 6163.44 | 0 | 0 | 0 | 0 | 37034 | 0 | 0 | 0 | 0 | 0 | 37034
2022060815 | 4 | 0.84402 | 67521.6 | 0.46462 | 16726.32 | 0.56455 | 6774.6 | 1 | 5000 | 16726.32 | 6774.6 | 0 | 0 | 0 | 0 | 39020.68 | 0 | 0 | 0 | 0 | 0 | 39020.68
2022060816 | 4 | 0.8603 | 68824 | 0.41622 | 14983.92 | 0.5608 | 6729.6 | 1 | 5000 | 14983.92 | 6729.6 | 0 | 0 | 0 | 0 | 42110.48 | 0 | 0 | 0 | 0 | 0 | 42110.48
2022060817 | 4 | 0.87284 | 69827.2 | 0.36693 | 13209.48 | 0.44745 | 5369.4 | 1 | 5000 | 13209.48 | 5369.4 | 0 | 0 | 0 | 0 | 46248.32 | 0 | 0 | 0 | 0 | 0 | 46248.32
2022060818 | 4 | 0.87324 | 69859.2 | 0.372 | 13392 | 0.39635 | 4756.2 | 1 | 5000 | 13392 | 4756.2 | 0 | 0 | 0 | 0 | 46711 | 0 | 0 | 0 | 0 | 0 | 46711
2022060819 | 4 | 0.85568 | 68454.4 | 0.36965 | 13307.4 | 0.27503 | 3300.36 | 1 | 5000 | 13307.4 | 3300.36 | 0 | 0 | 0 | 0 | 46846.64 | 0 | 0 | 0 | 0 | 0 | 46846.64
2022060820 | 4 | 0.8272 | 66176 | 0.36292 | 13065.12 | 0.09847 | 1181.64 | 1 | 5000 | 13065.12 | 1181.64 | 0 | 0 | 0 | 0 | 46929.24 | 0 | 0 | 0 | 0 | 0 | 46929.24
2022060821 | 4 | 0.7959 | 63672 | 0.33113 | 11920.68 | 0.00696 | 83.52 | 1 | 5000 | 11920.68 | 83.52 | 0 | 0 | 0 | 0 | 46667.8 | 0 | 0 | 0 | 0 | 0 | 46667.8
2022060822 | 4 | 0.76815 | 61452 | 0.3342 | 12031.2 | 0 | 0 | 1 | 5000 | 12031.2 | 0 | 0 | 0 | 0 | 0 | 44420.8 | 0 | 0 | 0 | 0 | 0 | 44420.8
2022060823 | 4 | 0.72107 | 57685.6 | 0.34719 | 12498.84 | 0 | 0 | 1 | 5000 | 12498.84 | 0 | 0 | 0 | 0 | 0 | 40186.76 | 0 | 0 | 0 | 0 | 0 | 40186.76
2022060824 | 4 | 0.66825 | 53460 | 0.31852 | 11466.72 | 0 | 0 | 1 | 5000 | 11466.72 | 0 | 0 | 0 | 0 | 0 | 36993.28 | 0 | 0 | 0 | 0 | 0 | 36993.28
2022060901 | 5 | 0.62242 | 49793.6 | 0.28064 | 10103.04 | 0.00115 | 13.8 | 1 | 5000 | 10103.04 | 13.8 | 0 | 0 | 0 | 0 | 34676.76 | 0 | 0 | 0 | 0 | 0 | 34676.76
2022060902 | 5 | 0.58873 | 47098.4 | 0.2437 | 8773.2 | 0.00091 | 10.92 | 1 | 5000 | 8773.2 | 10.92 | 0 | 0 | 0 | 0 | 33314.28 | 0 | 0 | 0 | 0 | 0 | 33314.28
2022060903 | 5 | 0.56627 | 45301.6 | 0.24038 | 8653.68 | 0.00019 | 2.28 | 1 | 5000 | 8653.68 | 2.28 | 0 | 0 | 0 | 0 | 31645.64 | 0 | 0 | 0 | 0 | 0 | 31645.64
2022060904 | 5 | 0.55159 | 44127.2 | 0.22527 | 8109.72 | 0.0003 | 3.6 | 1 | 5000 | 8109.72 | 3.6 | 0 | 0 | 0 | 0 | 31013.88 | 0 | 0 | 0 | 0 | 0 | 31013.88
2022060905 | 5 | 0.54594 | 43675.2 | 0.19563 | 7042.68 | 0 | 0 | 1 | 5000 | 7042.68 | 0 | 0 | 0 | 0 | 0 | 31632.52 | 0 | 0 | 0 | 0 | 0 | 31632.52
2022060906 | 5 | 0.55488 | 44390.4 | 0.18985 | 6834.6 | 0 | 0 | 1 | 5000 | 6834.6 | 0 | 0 | 0 | 0 | 0 | 32555.8 | 0 | 0 | 0 | 0 | 0 | 32555.8
2022060907 | 5 | 0.57053 | 45642.4 | 0.17027 | 6129.72 | 0.00215 | 25.8 | 1 | 5000 | 6129.72 | 25.8 | 0 | 0 | 0 | 0 | 34486.88 | 0 | 0 | 0 | 0 | 0 | 34486.88
2022060908 | 5 | 0.59026 | 47220.8 | 0.15101 | 5436.36 | 0.12692 | 1523.04 | 1 | 5000 | 5436.36 | 1523.04 | 0 | 0 | 0 | 0 | 35261.4 | 0 | 0 | 0 | 0 | 0 | 35261.4
2022060909 | 5 | 0.6182 | 49456 | 0.13029 | 4690.44 | 0.47361 | 5683.32 | 1 | 5000 | 4690.44 | 5683.32 | 0 | 0 | 0 | 0 | 34082.24 | 0 | 0 | 0 | 0 | 0 | 34082.24
2022060910 | 5 | 0.65645 | 52516 | 0.15197 | 5470.92 | 0.62695 | 7523.4 | 1 | 5000 | 5470.92 | 7523.4 | 0 | 0 | 0 | 0 | 34521.68 | 0 | 0 | 0 | 0 | 0 | 34521.68
2022060911 | 5 | 0.7037 | 56296 | 0.1474 | 5306.4 | 0.70328 | 8439.36 | 1 | 5000 | 5306.4 | 8439.36 | 0 | 0 | 0 | 0 | 37550.24 | 0 | 0 | 0 | 0 | 0 | 37550.24
2022060912 | 5 | 0.7543 | 60344 | 0.15557 | 5600.52 | 0.78836 | 9460.32 | 1 | 5000 | 5600.52 | 9460.32 | 0 | 0 | 0 | 0 | 40283.16 | 0 | 0 | 0 | 0 | 0 | 40283.16
2022060913 | 5 | 0.80228 | 64182.4 | 0.18013 | 6484.68 | 0.80122 | 9614.64 | 1 | 5000 | 6484.68 | 9614.64 | 0 | 0 | 0 | 0 | 43083.08 | 0 | 0 | 0 | 0 | 0 | 43083.08
2022060914 | 5 | 0.8471 | 67768 | 0.21189 | 7628.04 | 0.79326 | 9519.12 | 1 | 5000 | 7628.04 | 9519.12 | 0 | 0 | 0 | 0 | 45620.84 | 0 | 0 | 0 | 0 | 0 | 45620.84
2022060915 | 5 | 0.88259 | 70607.2 | 0.23553 | 8479.08 | 0.78326 | 9399.12 | 1 | 5000 | 8479.08 | 9399.12 | 0 | 0 | 0 | 0 | 47729 | 0 | 0 | 0 | 0 | 0 | 47729
2022060916 | 5 | 0.90085 | 72068 | 0.26439 | 9518.04 | 0.75298 | 9035.76 | 1 | 5000 | 9518.04 | 9035.76 | 0 | 0 | 0 | 0 | 48514.2 | 0 | 0 | 0 | 0 | 0 | 48514.2
2022060917 | 5 | 0.90942 | 72753.6 | 0.31358 | 11288.88 | 0.70626 | 8475.12 | 1 | 5000 | 11288.88 | 8475.12 | 0 | 0 | 0 | 0 | 47989.6 | 0 | 0 | 0 | 0 | 0 | 47989.6
2022060918 | 5 | 0.90908 | 72726.4 | 0.3468 | 12484.8 | 0.65486 | 7858.32 | 1 | 5000 | 12484.8 | 7858.32 | 0 | 0 | 0 | 0 | 47383.28 | 0 | 0 | 0 | 0 | 0 | 47383.28
2022060919 | 5 | 0.89975 | 71980 | 0.36025 | 12969 | 0.55371 | 6644.52 | 1 | 5000 | 12969 | 6644.52 | 0 | 0 | 0 | 0 | 47366.48 | 0 | 0 | 0 | 0 | 0 | 47366.48
2022060920 | 5 | 0.87132 | 69705.6 | 0.38862 | 13990.32 | 0.27274 | 3272.88 | 1 | 5000 | 13990.32 | 3272.88 | 0 | 0 | 0 | 0 | 47442.4 | 0 | 0 | 0 | 0 | 0 | 47442.4
2022060921 | 5 | 0.83727 | 66981.6 | 0.38026 | 13689.36 | 0.0285 | 342 | 1 | 5000 | 13689.36 | 342 | 0 | 0 | 0 | 0 | 47950.24 | 0 | 0 | 0 | 0 | 0 | 47950.24
2022060922 | 5 | 0.80728 | 64582.4 | 0.39568 | 14244.48 | 0 | 0 | 1 | 5000 | 14244.48 | 0 | 0 | 0 | 0 | 0 | 45337.92 | 0 | 0 | 0 | 0 | 0 | 45337.92
2022060923 | 5 | 0.7603 | 60824 | 0.44413 | 15988.68 | 0 | 0 | 1 | 5000 | 15988.68 | 0 | 0 | 0 | 0 | 0 | 39835.32 | 0 | 0 | 0 | 0 | 0 | 39835.32
2022060924 | 5 | 0.70778 | 56622.4 | 0.44698 | 16091.28 | 0 | 0 | 1 | 5000 | 16091.28 | 0 | 0 | 0 | 0 | 0 | 35531.12 | 0 | 0 | 0 | 0 | 0 | 35531.12
2022061001 | 6 | 0.65914 | 52731.2 | 0.43313 | 15592.68 | 0 | 0 | 1 | 5000 | 15592.68 | 0 | 0 | 0 | 0 | 0 | 32138.52 | 0 | 0 | 0 | 0 | 0 | 32138.52
2022061002 | 6 | 0.62163 | 49730.4 | 0.43641 | 15710.76 | 0 | 0 | 1 | 5000 | 15710.76 | 0 | 0 | 0 | 0 | 0 | 29019.64 | 0 | 0 | 0 | 0 | 0 | 29019.64
2022061003 | 6 | 0.59427 | 47541.6 | 0.43248 | 15569.28 | 0 | 0 | 1 | 5000 | 15569.28 | 0 | 0 | 0 | 0 | 0 | 26972.32 | 0 | 0 | 0 | 0 | 0 | 26972.32
2022061004 | 6 | 0.57692 | 46153.6 | 0.35398 | 12743.28 | 0 | 0 | 1 | 5000 | 12743.28 | 0 | 0 | 0 | 0 | 0 | 28410.32 | 0 | 0 | 0 | 0 | 0 | 28410.32
2022061005 | 6 | 0.57096 | 45676.8 | 0.29246 | 10528.56 | 0 | 0 | 1 | 5000 | 10528.56 | 0 | 0 | 0 | 0 | 0 | 30148.24 | 0 | 0 | 0 | 0 | 0 | 30148.24
2022061006 | 6 | 0.57646 | 46116.8 | 0.30243 | 10887.48 | 0 | 0 | 1 | 5000 | 10887.48 | 0 | 0 | 0 | 0 | 0 | 30229.32 | 0 | 0 | 0 | 0 | 0 | 30229.32
2022061007 | 6 | 0.58931 | 47144.8 | 0.30881 | 11117.16 | 0.002 | 24 | 1 | 5000 | 11117.16 | 24 | 0 | 0 | 0 | 0 | 31003.64 | 0 | 0 | 0 | 0 | 0 | 31003.64
2022061008 | 6 | 0.60477 | 48381.6 | 0.34023 | 12248.28 | 0.14803 | 1776.36 | 1 | 5000 | 12248.28 | 1776.36 | 0 | 0 | 0 | 0 | 29356.96 | 0 | 0 | 0 | 0 | 0 | 29356.96
2022061009 | 6 | 0.63386 | 50708.8 | 0.3403 | 12250.8 | 0.46683 | 5601.96 | 1 | 5000 | 12250.8 | 5601.96 | 0 | 0 | 0 | 0 | 27856.04 | 0 | 0 | 0 | 0 | 0 | 27856.04
2022061010 | 6 | 0.67043 | 53634.4 | 0.367 | 13212 | 0.6213 | 7455.6 | 1 | 5000 | 13212 | 7455.6 | 0 | 0 | 0 | 0 | 27966.8 | 0 | 0 | 0 | 0 | 0 | 27966.8
2022061011 | 6 | 0.71174 | 56939.2 | 0.35581 | 12809.16 | 0.70575 | 8469 | 1 | 5000 | 12809.16 | 8469 | 0 | 0 | 0 | 0 | 30661.04 | 0 | 0 | 0 | 0 | 0 | 30661.04
2022061012 | 6 | 0.76018 | 60814.4 | 0.31007 | 11162.52 | 0.76892 | 9227.04 | 1 | 5000 | 11162.52 | 9227.04 | 0 | 0 | 0 | 0 | 35424.84 | 0 | 0 | 0 | 0 | 0 | 35424.84
2022061013 | 6 | 0.80616 | 64492.8 | 0.2242 | 8071.2 | 0.78972 | 9476.64 | 1 | 5000 | 8071.2 | 9476.64 | 0 | 0 | 0 | 0 | 41944.96 | 0 | 0 | 0 | 0 | 0 | 41944.96
2022061014 | 6 | 0.85383 | 68306.4 | 0.18795 | 6766.2 | 0.79826 | 9579.12 | 1 | 5000 | 6766.2 | 9579.12 | 0 | 0 | 0 | 0 | 46961.08 | 0 | 0 | 0 | 0 | 0 | 46961.08
2022061015 | 6 | 0.89329 | 71463.2 | 0.19197 | 6910.92 | 0.79352 | 9522.24 | 1 | 5000 | 6910.92 | 9522.24 | 0 | 0 | 0 | 0 | 50030.04 | 0 | 0 | 0 | 0 | 0 | 50030.04
2022061016 | 6 | 0.91184 | 72947.2 | 0.196 | 7056 | 0.80301 | 9636.12 | 1 | 5000 | 7056 | 9636.12 | 0 | 0 | 0 | 0 | 51255.08 | 0 | 0 | 0 | 0 | 0 | 51255.08
2022061017 | 6 | 0.9209 | 73672 | 0.20612 | 7420.32 | 0.76352 | 9162.24 | 1 | 5000 | 7420.32 | 9162.24 | 0 | 0 | 0 | 0 | 52089.44 | 0 | 0 | 0 | 0 | 0 | 52089.44
2022061018 | 6 | 0.92548 | 74038.4 | 0.22445 | 8080.2 | 0.71097 | 8531.64 | 1 | 5000 | 8080.2 | 8531.64 | 0 | 0 | 0 | 0 | 52426.56 | 0 | 0 | 0 | 0 | 0 | 52426.56
2022061019 | 6 | 0.92021 | 73616.8 | 0.23872 | 8593.92 | 0.6097 | 7316.4 | 1 | 5000 | 8593.92 | 7316.4 | 0 | 0 | 0 | 0 | 52706.48 | 0 | 0 | 0 | 0 | 0 | 52706.48
2022061020 | 6 | 0.89505 | 71604 | 0.25275 | 9099 | 0.33356 | 4002.72 | 1 | 5000 | 9099 | 4002.72 | 0 | 0 | 0 | 0 | 53502.28 | 0 | 0 | 0 | 0 | 0 | 53502.28
2022061021 | 6 | 0.85693 | 68554.4 | 0.29583 | 10649.88 | 0.03616 | 433.92 | 1 | 5000 | 10649.88 | 433.92 | 0 | 0 | 0 | 0 | 52470.6 | 0 | 0 | 0 | 0 | 0 | 52470.6
2022061022 | 6 | 0.82564 | 66051.2 | 0.37965 | 13667.4 | 0 | 0 | 1 | 5000 | 13667.4 | 0 | 0 | 0 | 0 | 0 | 47383.8 | 0 | 0 | 0 | 0 | 0 | 47383.8
2022061023 | 6 | 0.77912 | 62329.6 | 0.46433 | 16715.88 | 0 | 0 | 1 | 5000 | 16715.88 | 0 | 0 | 0 | 0 | 0 | 40613.72 | 0 | 0 | 0 | 0 | 0 | 40613.72
2022061024 | 6 | 0.73422 | 58737.6 | 0.51287 | 18463.32 | 0 | 0 | 1 | 5000 | 18463.32 | 0 | 0 | 0 | 0 | 0 | 35274.28 | 0 | 0 | 0 | 0 | 0 | 35274.28
2022061101 | 7 | 0.68738 | 54990.4 | 0.54168 | 19500.48 | 0 | 0 | 1 | 5000 | 19500.48 | 0 | 0 | 0 | 0 | 0 | 30489.92 | 0 | 0 | 0 | 0 | 0 | 30489.92
2022061102 | 7 | 0.64963 | 51970.4 | 0.55242 | 19887.12 | 0 | 0 | 1 | 5000 | 19887.12 | 0 | 0 | 0 | 0 | 0 | 27083.28 | 0 | 0 | 0 | 0 | 0 | 27083.28
2022061103 | 7 | 0.6188 | 49504 | 0.56225 | 20241 | 0 | 0 | 1 | 5000 | 20241 | 0 | 0 | 0 | 0 | 0 | 24263 | 0 | 0 | 0 | 0 | 0 | 24263
2022061104 | 7 | 0.59805 | 47844 | 0.5524 | 19886.4 | 0 | 0 | 1 | 5000 | 19886.4 | 0 | 0 | 0 | 0 | 0 | 22957.6 | 0 | 0 | 0 | 0 | 0 | 22957.6
2022061105 | 7 | 0.581 | 46480 | 0.53668 | 19320.48 | 0 | 0 | 1 | 5000 | 19320.48 | 0 | 0 | 0 | 0 | 0 | 22159.52 | 0 | 0 | 0 | 0 | 0 | 22159.52
2022061106 | 7 | 0.57656 | 46124.8 | 0.53691 | 19328.76 | 0 | 0 | 1 | 5000 | 19328.76 | 0 | 0 | 0 | 0 | 0 | 21796.04 | 0 | 0 | 0 | 0 | 0 | 21796.04
2022061107 | 7 | 0.57638 | 46110.4 | 0.51859 | 18669.24 | 0.00386 | 46.32 | 1 | 5000 | 18669.24 | 46.32 | 0 | 0 | 0 | 0 | 22394.84 | 0 | 0 | 0 | 0 | 0 | 22394.84
2022061108 | 7 | 0.58525 | 46820 | 0.45974 | 16550.64 | 0.19762 | 2371.44 | 1 | 5000 | 16550.64 | 2371.44 | 0 | 0 | 0 | 0 | 22897.92 | 0 | 0 | 0 | 0 | 0 | 22897.92
2022061109 | 7 | 0.62752 | 50201.6 | 0.40991 | 14756.76 | 0.56039 | 6724.68 | 1 | 5000 | 14756.76 | 6724.68 | 0 | 0 | 0 | 0 | 23720.16 | 0 | 0 | 0 | 0 | 0 | 23720.16
2022061110 | 7 | 0.68311 | 54648.8 | 0.44441 | 15998.76 | 0.7302 | 8762.4 | 1 | 5000 | 15998.76 | 8762.4 | 0 | 0 | 0 | 0 | 24887.64 | 0 | 0 | 0 | 0 | 0 | 24887.64
2022061111 | 7 | 0.73915 | 59132 | 0.43838 | 15781.68 | 0.79451 | 9534.12 | 1 | 5000 | 15781.68 | 9534.12 | 0 | 0 | 0 | 0 | 28816.2 | 0 | 0 | 0 | 0 | 0 | 28816.2
2022061112 | 7 | 0.79457 | 63565.6 | 0.37836 | 13620.96 | 0.8088 | 9705.6 | 1 | 5000 | 13620.96 | 9705.6 | 0 | 0 | 0 | 0 | 35239.04 | 0 | 0 | 0 | 0 | 0 | 35239.04
2022061113 | 7 | 0.8413 | 67304 | 0.34743 | 12507.48 | 0.81265 | 9751.8 | 1 | 5000 | 12507.48 | 9751.8 | 0 | 0 | 0 | 0 | 40044.72 | 0 | 0 | 0 | 0 | 0 | 40044.72
2022061114 | 7 | 0.88328 | 70662.4 | 0.33059 | 11901.24 | 0.7922 | 9506.4 | 1 | 5000 | 11901.24 | 9506.4 | 0 | 0 | 0 | 0 | 44254.76 | 0 | 0 | 0 | 0 | 0 | 44254.76
2022061115 | 7 | 0.913 | 73040 | 0.30217 | 10878.12 | 0.78341 | 9400.92 | 1 | 5000 | 10878.12 | 9400.92 | 0 | 0 | 0 | 0 | 47760.96 | 0 | 0 | 0 | 0 | 0 | 47760.96
2022061116 | 7 | 0.92554 | 74043.2 | 0.30594 | 11013.84 | 0.75867 | 9104.04 | 1 | 5000 | 11013.84 | 9104.04 | 0 | 0 | 0 | 0 | 48925.32 | 0 | 0 | 0 | 0 | 0 | 48925.32
2022061117 | 7 | 0.93167 | 74533.6 | 0.31393 | 11301.48 | 0.73039 | 8764.68 | 1 | 5000 | 11301.48 | 8764.68 | 0 | 0 | 0 | 0 | 49467.44 | 0 | 0 | 0 | 0 | 0 | 49467.44
2022061118 | 7 | 0.93112 | 74489.6 | 0.34439 | 12398.04 | 0.68559 | 8227.08 | 1 | 5000 | 12398.04 | 8227.08 | 0 | 0 | 0 | 0 | 48864.48 | 0 | 0 | 0 | 0 | 0 | 48864.48
2022061119 | 7 | 0.92496 | 73996.8 | 0.38139 | 13730.04 | 0.58712 | 7045.44 | 1 | 5000 | 13730.04 | 7045.44 | 0 | 0 | 0 | 0 | 48221.32 | 0 | 0 | 0 | 0 | 0 | 48221.32
2022061120 | 7 | 0.90285 | 72228 | 0.41895 | 15082.2 | 0.35604 | 4272.48 | 1 | 5000 | 15082.2 | 4272.48 | 0 | 0 | 0 | 0 | 47873.32 | 0 | 0 | 0 | 0 | 0 | 47873.32
2022061121 | 7 | 0.86717 | 69373.6 | 0.47389 | 17060.04 | 0.04513 | 541.56 | 1 | 5000 | 17060.04 | 541.56 | 0 | 0 | 0 | 0 | 46772 | 0 | 0 | 0 | 0 | 0 | 46772
2022061122 | 7 | 0.83535 | 66828 | 0.57853 | 20827.08 | 0 | 0 | 1 | 5000 | 20827.08 | 0 | 0 | 0 | 0 | 0 | 41000.92 | 0 | 0 | 0 | 0 | 0 | 41000.92
2022061123 | 7 | 0.79314 | 63451.2 | 0.64741 | 23306.76 | 0 | 0 | 1 | 5000 | 23306.76 | 0 | 0 | 0 | 0 | 0 | 35144.44 | 0 | 0 | 0 | 0 | 0 | 35144.44
2022061124 | 7 | 0.74635 | 59708 | 0.65795 | 23686.2 | 0 | 0 | 1 | 5000 | 23686.2 | 0 | 0 | 0 | 0 | 0 | 31021.8 | 0 | 0 | 0 | 0 | 0 | 31021.8
2022061201 | 1 | 0.69997 | 55997.6 | 0.66467 | 23928.12 | 0 | 0 | 1 | 5000 | 23928.12 | 0 | 0 | 0 | 0 | 0 | 27069.48 | 0 | 0 | 0 | 0 | 0 | 27069.48
2022061202 | 1 | 0.6633 | 53064 | 0.67214 | 24197.04 | 0 | 0 | 1 | 5000 | 24197.04 | 0 | 0 | 0 | 0 | 0 | 23866.96 | 0 | 0 | 0 | 0 | 0 | 23866.96
2022061203 | 1 | 0.63699 | 50959.2 | 0.67212 | 24196.32 | 0 | 0 | 1 | 5000 | 24196.32 | 0 | 0 | 0 | 0 | 0 | 21762.88 | 0 | 0 | 0 | 0 | 0 | 21762.88
2022061204 | 1 | 0.61334 | 49067.2 | 0.66427 | 23913.72 | 0 | 0 | 1 | 5000 | 23913.72 | 0 | 0 | 0 | 0 | 0 | 20153.48 | 0 | 0 | 0 | 0 | 0 | 20153.48
2022061205 | 1 | 0.59741 | 47792.8 | 0.66021 | 23767.56 | 0 | 0 | 1 | 5000 | 23767.56 | 0 | 0 | 0 | 0 | 0 | 19025.24 | 0 | 0 | 0 | 0 | 0 | 19025.24
2022061206 | 1 | 0.59121 | 47296.8 | 0.65604 | 23617.44 | 0 | 0 | 1 | 5000 | 23617.44 | 0 | 0 | 0 | 0 | 0 | 18679.36 | 0 | 0 | 0 | 0 | 0 | 18679.36
2022061207 | 1 | 0.57816 | 46252.8 | 0.63548 | 22877.28 | 0.00427 | 51.24 | 1 | 5000 | 22877.28 | 51.24 | 0 | 0 | 0 | 0 | 18324.28 | 0 | 0 | 0 | 0 | 0 | 18324.28
2022061208 | 1 | 0.58308 | 46646.4 | 0.59548 | 21437.28 | 0.19269 | 2312.28 | 1 | 5000 | 21437.28 | 2312.28 | 0 | 0 | 0 | 0 | 17896.84 | 0 | 0 | 0 | 0 | 0 | 17896.84
2022061209 | 1 | 0.6253 | 50024 | 0.57475 | 20691 | 0.51836 | 6220.32 | 1 | 5000 | 20691 | 6220.32 | 0 | 0 | 0 | 0 | 18112.68 | 0 | 0 | 0 | 0 | 0 | 18112.68
2022061210 | 1 | 0.67872 | 54297.6 | 0.60541 | 21794.76 | 0.56238 | 6748.56 | 1 | 5000 | 21794.76 | 6748.56 | 0 | 0 | 0 | 0 | 20754.28 | 0 | 0 | 0 | 0 | 0 | 20754.28
2022061211 | 1 | 0.7339 | 58712 | 0.60546 | 21796.56 | 0.58717 | 7046.04 | 1 | 5000 | 21796.56 | 7046.04 | 0 | 0 | 0 | 0 | 24869.4 | 0 | 0 | 0 | 0 | 0 | 24869.4
2022061212 | 1 | 0.78953 | 63162.4 | 0.5826 | 20973.6 | 0.68363 | 8203.56 | 1 | 5000 | 20973.6 | 8203.56 | 0 | 0 | 0 | 0 | 28985.24 | 0 | 0 | 0 | 0 | 0 | 28985.24
2022061213 | 1 | 0.84121 | 67296.8 | 0.55729 | 20062.44 | 0.75893 | 9107.16 | 1 | 5000 | 20062.44 | 9107.16 | 0 | 0 | 0 | 0 | 33127.2 | 0 | 0 | 0 | 0 | 0 | 33127.2
2022061214 | 1 | 0.88168 | 70534.4 | 0.55407 | 19946.52 | 0.76895 | 9227.4 | 1 | 5000 | 19946.52 | 9227.4 | 0 | 0 | 0 | 0 | 36360.48 | 0 | 0 | 0 | 0 | 0 | 36360.48
2022061215 | 1 | 0.91355 | 73084 | 0.55073 | 19826.28 | 0.74147 | 8897.64 | 1 | 5000 | 19826.28 | 8897.64 | 0 | 0 | 0 | 0 | 39360.08 | 0 | 0 | 0 | 0 | 0 | 39360.08
2022061216 | 1 | 0.9274 | 74192 | 0.55173 | 19862.28 | 0.74571 | 8948.52 | 1 | 5000 | 19862.28 | 8948.52 | 0 | 0 | 0 | 0 | 40381.2 | 0 | 0 | 0 | 0 | 0 | 40381.2
2022061217 | 1 | 0.93516 | 74812.8 | 0.54131 | 19487.16 | 0.74577 | 8949.24 | 1 | 5000 | 19487.16 | 8949.24 | 0 | 0 | 0 | 0 | 41376.4 | 0 | 0 | 0 | 0 | 0 | 41376.4
2022061218 | 1 | 0.9384 | 75072 | 0.54494 | 19617.84 | 0.70936 | 8512.32 | 1 | 5000 | 19617.84 | 8512.32 | 0 | 0 | 0 | 0 | 41941.84 | 0 | 0 | 0 | 0 | 0 | 41941.84
2022061219 | 1 | 0.93206 | 74564.8 | 0.54369 | 19572.84 | 0.61714 | 7405.68 | 1 | 5000 | 19572.84 | 7405.68 | 0 | 0 | 0 | 0 | 42586.28 | 0 | 0 | 0 | 0 | 0 | 42586.28
2022061220 | 1 | 0.91044 | 72835.2 | 0.5449 | 19616.4 | 0.36081 | 4329.72 | 1 | 5000 | 19616.4 | 4329.72 | 0 | 0 | 0 | 0 | 43889.08 | 0 | 0 | 0 | 0 | 0 | 43889.08
2022061221 | 1 | 0.87081 | 69664.8 | 0.55587 | 20011.32 | 0.04272 | 512.64 | 1 | 5000 | 20011.32 | 512.64 | 0 | 0 | 0 | 0 | 44140.84 | 0 | 0 | 0 | 0 | 0 | 44140.84
2022061222 | 1 | 0.8434 | 67472 | 0.60703 | 21853.08 | 0 | 0 | 1 | 5000 | 21853.08 | 0 | 0 | 0 | 0 | 0 | 40618.92 | 0 | 0 | 0 | 0 | 0 | 40618.92
2022061223 | 1 | 0.79732 | 63785.6 | 0.65565 | 23603.4 | 0 | 0 | 1 | 5000 | 23603.4 | 0 | 0 | 0 | 0 | 0 | 35182.2 | 0 | 0 | 0 | 0 | 0 | 35182.2
2022061224 | 1 | 0.74541 | 59632.8 | 0.6805 | 24498 | 0 | 0 | 1 | 5000 | 24498 | 0 | 0 | 0 | 0 | 0 | 30134.8 | 0 | 0 | 0 | 0 | 0 | 30134.8
2022061301 | 2 | 0.698 | 55840 | 0.69144 | 24891.84 | 0 | 0 | 1 | 5000 | 24891.84 | 0 | 0 | 0 | 0 | 0 | 25948.16 | 0 | 0 | 0 | 0 | 0 | 25948.16
2022061302 | 2 | 0.66406 | 53124.8 | 0.69441 | 24998.76 | 0 | 0 | 1 | 5000 | 24998.76 | 0 | 0 | 0 | 0 | 0 | 23126.04 | 0 | 0 | 0 | 0 | 0 | 23126.04
2022061303 | 2 | 0.63891 | 51112.8 | 0.6997 | 25189.2 | 0 | 0 | 1 | 5000 | 25189.2 | 0 | 0 | 0 | 0 | 0 | 20923.6 | 0 | 0 | 0 | 0 | 0 | 20923.6
2022061304 | 2 | 0.62298 | 49838.4 | 0.69383 | 24977.88 | 0 | 0 | 1 | 5000 | 24977.88 | 0 | 0 | 0 | 0 | 0 | 19860.52 | 0 | 0 | 0 | 0 | 0 | 19860.52
2022061305 | 2 | 0.61564 | 49251.2 | 0.6783 | 24418.8 | 0 | 0 | 1 | 5000 | 24418.8 | 0 | 0 | 0 | 0 | 0 | 19832.4 | 0 | 0 | 0 | 0 | 0 | 19832.4
2022061306 | 2 | 0.62125 | 49700 | 0.65972 | 23749.92 | 0 | 0 | 1 | 5000 | 23749.92 | 0 | 0 | 0 | 0 | 0 | 20950.08 | 0 | 0 | 0 | 0 | 0 | 20950.08
2022061307 | 2 | 0.63061 | 50448.8 | 0.64197 | 23110.92 | 0.00516 | 61.92 | 1 | 5000 | 23110.92 | 61.92 | 0 | 0 | 0 | 0 | 22275.96 | 0 | 0 | 0 | 0 | 0 | 22275.96
2022061308 | 2 | 0.64748 | 51798.4 | 0.62501 | 22500.36 | 0.16896 | 2027.52 | 1 | 5000 | 22500.36 | 2027.52 | 0 | 0 | 0 | 0 | 22270.52 | 0 | 0 | 0 | 0 | 0 | 22270.52
2022061309 | 2 | 0.68129 | 54503.2 | 0.62615 | 22541.4 | 0.33477 | 4017.24 | 1 | 5000 | 22541.4 | 4017.24 | 0 | 0 | 0 | 0 | 22944.56 | 0 | 0 | 0 | 0 | 0 | 22944.56
2022061310 | 2 | 0.72761 | 58208.8 | 0.66495 | 23938.2 | 0.40203 | 4824.36 | 1 | 5000 | 23938.2 | 4824.36 | 0 | 0 | 0 | 0 | 24446.24 | 0 | 0 | 0 | 0 | 0 | 24446.24
2022061311 | 2 | 0.77683 | 62146.4 | 0.68064 | 24503.04 | 0.43255 | 5190.6 | 1 | 5000 | 24503.04 | 5190.6 | 0 | 0 | 0 | 0 | 27452.76 | 0 | 0 | 0 | 0 | 0 | 27452.76
2022061312 | 2 | 0.8262 | 66096 | 0.69552 | 25038.72 | 0.43638 | 5236.56 | 1 | 5000 | 25038.72 | 5236.56 | 0 | 0 | 0 | 0 | 30820.72 | 0 | 0 | 0 | 0 | 0 | 30820.72
2022061313 | 2 | 0.86721 | 69376.8 | 0.69485 | 25014.6 | 0.46342 | 5561.04 | 1 | 5000 | 25014.6 | 5561.04 | 0 | 0 | 0 | 0 | 33801.16 | 0 | 0 | 0 | 0 | 0 | 33801.16
2022061314 | 2 | 0.90192 | 72153.6 | 0.69084 | 24870.24 | 0.49065 | 5887.8 | 1 | 5000 | 24870.24 | 5887.8 | 0 | 0 | 0 | 0 | 36395.56 | 0 | 0 | 0 | 0 | 0 | 36395.56
2022061315 | 2 | 0.92793 | 74234.4 | 0.69281 | 24941.16 | 0.49649 | 5957.88 | 1 | 5000 | 24941.16 | 5957.88 | 0 | 0 | 0 | 0 | 38335.36 | 0 | 0 | 0 | 0 | 0 | 38335.36
2022061316 | 2 | 0.93047 | 74437.6 | 0.6893 | 24814.8 | 0.49217 | 5906.04 | 1 | 5000 | 24814.8 | 5906.04 | 0 | 0 | 0 | 0 | 38716.76 | 0 | 0 | 0 | 0 | 0 | 38716.76
2022061317 | 2 | 0.93355 | 74684 | 0.67742 | 24387.12 | 0.50965 | 6115.8 | 1 | 5000 | 24387.12 | 6115.8 | 0 | 0 | 0 | 0 | 39181.08 | 0 | 0 | 0 | 0 | 0 | 39181.08
2022061318 | 2 | 0.93235 | 74588 | 0.67268 | 24216.48 | 0.49077 | 5889.24 | 1 | 5000 | 24216.48 | 5889.24 | 0 | 0 | 0 | 0 | 39482.28 | 0 | 0 | 0 | 0 | 0 | 39482.28
2022061319 | 2 | 0.91882 | 73505.6 | 0.67221 | 24199.56 | 0.41171 | 4940.52 | 1 | 5000 | 24199.56 | 4940.52 | 0 | 0 | 0 | 0 | 39365.52 | 0 | 0 | 0 | 0 | 0 | 39365.52
2022061320 | 2 | 0.89424 | 71539.2 | 0.67784 | 24402.24 | 0.26231 | 3147.72 | 1 | 5000 | 24402.24 | 3147.72 | 0 | 0 | 0 | 0 | 38989.24 | 0 | 0 | 0 | 0 | 0 | 38989.24
2022061321 | 2 | 0.8559 | 68472 | 0.68762 | 24754.32 | 0.04541 | 544.92 | 1 | 5000 | 24754.32 | 544.92 | 0 | 0 | 0 | 0 | 38172.76 | 0 | 0 | 0 | 0 | 0 | 38172.76
2022061322 | 2 | 0.83278 | 66622.4 | 0.70163 | 25258.68 | 0.007 | 84 | 1 | 5000 | 25258.68 | 84 | 0 | 0 | 0 | 0 | 36279.72 | 0 | 0 | 0 | 0 | 0 | 36279.72
2022061323 | 2 | 0.78427 | 62741.6 | 0.71906 | 25886.16 | 0 | 0 | 1 | 5000 | 25886.16 | 0 | 0 | 0 | 0 | 0 | 31855.44 | 0 | 0 | 0 | 0 | 0 | 31855.44
2022061324 | 2 | 0.73346 | 58676.8 | 0.72338 | 26041.68 | 7e-05 | 0.84 | 1 | 5000 | 26041.68 | 0.84 | 0 | 0 | 0 | 0 | 27634.28 | 0 | 0 | 0 | 0 | 0 | 27634.28
2022061401 | 3 | 0.68976 | 55180.8 | 0.72995 | 26278.2 | 8e-05 | 0.96 | 1 | 5000 | 26278.2 | 0.96 | 0 | 0 | 0 | 0 | 23901.64 | 0 | 0 | 0 | 0 | 0 | 23901.64
2022061402 | 3 | 0.658 | 52640 | 0.72375 | 26055 | 8e-05 | 0.96 | 1 | 5000 | 26055 | 0.96 | 0 | 0 | 0 | 0 | 21584.04 | 0 | 0 | 0 | 0 | 0 | 21584.04
2022061403 | 3 | 0.63456 | 50764.8 | 0.71508 | 25742.88 | 8e-05 | 0.96 | 1 | 5000 | 25742.88 | 0.96 | 0 | 0 | 0 | 0 | 20020.96 | 0 | 0 | 0 | 0 | 0 | 20020.96
2022061404 | 3 | 0.61866 | 49492.8 | 0.70448 | 25361.28 | 8e-05 | 0.96 | 1 | 5000 | 25361.28 | 0.96 | 0 | 0 | 0 | 0 | 19130.56 | 0 | 0 | 0 | 0 | 0 | 19130.56
2022061405 | 3 | 0.61629 | 49303.2 | 0.7039 | 25340.4 | 9e-05 | 1.08 | 1 | 5000 | 25340.4 | 1.08 | 0 | 0 | 0 | 0 | 18961.72 | 0 | 0 | 0 | 0 | 0 | 18961.72
2022061406 | 3 | 0.62094 | 49675.2 | 0.69592 | 25053.12 | 9e-05 | 1.08 | 1 | 5000 | 25053.12 | 1.08 | 0 | 0 | 0 | 0 | 19621 | 0 | 0 | 0 | 0 | 0 | 19621
2022061407 | 3 | 0.62873 | 50298.4 | 0.68749 | 24749.64 | 0.00526 | 63.12 | 1 | 5000 | 24749.64 | 63.12 | 0 | 0 | 0 | 0 | 20485.64 | 0 | 0 | 0 | 0 | 0 | 20485.64
2022061408 | 3 | 0.64441 | 51552.8 | 0.67534 | 24312.24 | 0.10581 | 1269.72 | 1 | 5000 | 24312.24 | 1269.72 | 0 | 0 | 0 | 0 | 20970.84 | 0 | 0 | 0 | 0 | 0 | 20970.84
2022061409 | 3 | 0.67493 | 53994.4 | 0.67053 | 24139.08 | 0.26095 | 3131.4 | 1 | 5000 | 24139.08 | 3131.4 | 0 | 0 | 0 | 0 | 21723.92 | 0 | 0 | 0 | 0 | 0 | 21723.92
2022061410 | 3 | 0.71574 | 57259.2 | 0.68203 | 24553.08 | 0.37241 | 4468.92 | 1 | 5000 | 24553.08 | 4468.92 | 0 | 0 | 0 | 0 | 23237.2 | 0 | 0 | 0 | 0 | 0 | 23237.2
2022061411 | 3 | 0.75761 | 60608.8 | 0.6779 | 24404.4 | 0.44543 | 5345.16 | 1 | 5000 | 24404.4 | 5345.16 | 0 | 0 | 0 | 0 | 25859.24 | 0 | 0 | 0 | 0 | 0 | 25859.24
2022061412 | 3 | 0.79983 | 63986.4 | 0.66864 | 24071.04 | 0.50619 | 6074.28 | 1 | 5000 | 24071.04 | 6074.28 | 0 | 0 | 0 | 0 | 28841.08 | 0 | 0 | 0 | 0 | 0 | 28841.08
2022061413 | 3 | 0.83955 | 67164 | 0.64623 | 23264.28 | 0.58259 | 6991.08 | 1 | 5000 | 23264.28 | 6991.08 | 0 | 0 | 0 | 0 | 31908.64 | 0 | 0 | 0 | 0 | 0 | 31908.64
2022061414 | 3 | 0.87226 | 69780.8 | 0.59823 | 21536.28 | 0.72279 | 8673.48 | 1 | 5000 | 21536.28 | 8673.48 | 0 | 0 | 0 | 0 | 34571.04 | 0 | 0 | 0 | 0 | 0 | 34571.04
2022061415 | 3 | 0.89705 | 71764 | 0.57365 | 20651.4 | 0.77779 | 9333.48 | 1 | 5000 | 20651.4 | 9333.48 | 0 | 0 | 0 | 0 | 36779.12 | 0 | 0 | 0 | 0 | 0 | 36779.12
2022061416 | 3 | 0.91219 | 72975.2 | 0.57753 | 20791.08 | 0.76518 | 9182.16 | 1 | 5000 | 20791.08 | 9182.16 | 0 | 0 | 0 | 0 | 38001.96 | 0 | 0 | 0 | 0 | 0 | 38001.96
2022061417 | 3 | 0.92137 | 73709.6 | 0.59997 | 21598.92 | 0.69827 | 8379.24 | 1 | 5000 | 21598.92 | 8379.24 | 0 | 0 | 0 | 0 | 38731.44 | 0 | 0 | 0 | 0 | 0 | 38731.44
2022061418 | 3 | 0.91689 | 73351.2 | 0.63494 | 22857.84 | 0.55529 | 6663.48 | 1 | 5000 | 22857.84 | 6663.48 | 0 | 0 | 0 | 0 | 38829.88 | 0 | 0 | 0 | 0 | 0 | 38829.88
2022061419 | 3 | 0.89447 | 71557.6 | 0.67191 | 24188.76 | 0.346 | 4152 | 1 | 5000 | 24188.76 | 4152 | 0 | 0 | 0 | 0 | 38216.84 | 0 | 0 | 0 | 0 | 0 | 38216.84
2022061420 | 3 | 0.86091 | 68872.8 | 0.70948 | 25541.28 | 0.13582 | 1629.84 | 1 | 5000 | 25541.28 | 1629.84 | 0 | 0 | 0 | 0 | 36701.68 | 0 | 0 | 0 | 0 | 0 | 36701.68
2022061421 | 3 | 0.83179 | 66543.2 | 0.7142 | 25711.2 | 0.0153 | 183.6 | 1 | 5000 | 25711.2 | 183.6 | 0 | 0 | 0 | 0 | 35648.4 | 0 | 0 | 0 | 0 | 0 | 35648.4
2022061422 | 3 | 0.80652 | 64521.6 | 0.68093 | 24513.48 | 0 | 0 | 1 | 5000 | 24513.48 | 0 | 0 | 0 | 0 | 0 | 35008.12 | 0 | 0 | 0 | 0 | 0 | 35008.12
2022061423 | 3 | 0.76232 | 60985.6 | 0.67695 | 24370.2 | 0 | 0 | 1 | 5000 | 24370.2 | 0 | 0 | 0 | 0 | 0 | 31615.4 | 0 | 0 | 0 | 0 | 0 | 31615.4
2022061424 | 3 | 0.71574 | 57259.2 | 0.70144 | 25251.84 | 7e-05 | 0.84 | 1 | 5000 | 25251.84 | 0.84 | 0 | 0 | 0 | 0 | 27006.52 | 0 | 0 | 0 | 0 | 0 | 27006.52
2022061501 | 4 | 0.67544 | 54035.2 | 0.71874 | 25874.64 | 8e-05 | 0.96 | 1 | 5000 | 25874.64 | 0.96 | 0 | 0 | 0 | 0 | 23159.6 | 0 | 0 | 0 | 0 | 0 | 23159.6
2022061502 | 4 | 0.64579 | 51663.2 | 0.71608 | 25778.88 | 9e-05 | 1.08 | 1 | 5000 | 25778.88 | 1.08 | 0 | 0 | 0 | 0 | 20883.24 | 0 | 0 | 0 | 0 | 0 | 20883.24
2022061503 | 4 | 0.62697 | 50157.6 | 0.70698 | 25451.28 | 9e-05 | 1.08 | 1 | 5000 | 25451.28 | 1.08 | 0 | 0 | 0 | 0 | 19705.24 | 0 | 0 | 0 | 0 | 0 | 19705.24
2022061504 | 4 | 0.61458 | 49166.4 | 0.70357 | 25328.52 | 0.0001 | 1.2 | 1 | 5000 | 25328.52 | 1.2 | 0 | 0 | 0 | 0 | 18836.68 | 0 | 0 | 0 | 0 | 0 | 18836.68
2022061505 | 4 | 0.60903 | 48722.4 | 0.69293 | 24945.48 | 0.0001 | 1.2 | 1 | 5000 | 24945.48 | 1.2 | 0 | 0 | 0 | 0 | 18775.72 | 0 | 0 | 0 | 0 | 0 | 18775.72
2022061506 | 4 | 0.6164 | 49312 | 0.67388 | 24259.68 | 0.0001 | 1.2 | 1 | 5000 | 24259.68 | 1.2 | 0 | 0 | 0 | 0 | 20051.12 | 0 | 0 | 0 | 0 | 0 | 20051.12
2022061507 | 4 | 0.63098 | 50478.4 | 0.66627 | 23985.72 | 0.00648 | 77.76 | 1 | 5000 | 23985.72 | 77.76 | 0 | 0 | 0 | 0 | 21414.92 | 0 | 0 | 0 | 0 | 0 | 21414.92
2022061508 | 4 | 0.64729 | 51783.2 | 0.65986 | 23754.96 | 0.10196 | 1223.52 | 1 | 5000 | 23754.96 | 1223.52 | 0 | 0 | 0 | 0 | 21804.72 | 0 | 0 | 0 | 0 | 0 | 21804.72
2022061509 | 4 | 0.67376 | 53900.8 | 0.64918 | 23370.48 | 0.24789 | 2974.68 | 1 | 5000 | 23370.48 | 2974.68 | 0 | 0 | 0 | 0 | 22555.64 | 0 | 0 | 0 | 0 | 0 | 22555.64
2022061510 | 4 | 0.71101 | 56880.8 | 0.66879 | 24076.44 | 0.31832 | 3819.84 | 1 | 5000 | 24076.44 | 3819.84 | 0 | 0 | 0 | 0 | 23984.52 | 0 | 0 | 0 | 0 | 0 | 23984.52
2022061511 | 4 | 0.75178 | 60142.4 | 0.652 | 23472 | 0.41215 | 4945.8 | 1 | 5000 | 23472 | 4945.8 | 0 | 0 | 0 | 0 | 26724.6 | 0 | 0 | 0 | 0 | 0 | 26724.6
2022061512 | 4 | 0.78879 | 63103.2 | 0.64431 | 23195.16 | 0.47136 | 5656.32 | 1 | 5000 | 23195.16 | 5656.32 | 0 | 0 | 0 | 0 | 29251.72 | 0 | 0 | 0 | 0 | 0 | 29251.72
2022061513 | 4 | 0.82477 | 65981.6 | 0.62319 | 22434.84 | 0.53055 | 6366.6 | 1 | 5000 | 22434.84 | 6366.6 | 0 | 0 | 0 | 0 | 32180.16 | 0 | 0 | 0 | 0 | 0 | 32180.16
2022061514 | 4 | 0.8583 | 68664 | 0.59429 | 21394.44 | 0.60295 | 7235.4 | 1 | 5000 | 21394.44 | 7235.4 | 0 | 0 | 0 | 0 | 35034.16 | 0 | 0 | 0 | 0 | 0 | 35034.16
2022061515 | 4 | 0.88437 | 70749.6 | 0.57816 | 20813.76 | 0.66782 | 8013.84 | 1 | 5000 | 20813.76 | 8013.84 | 0 | 0 | 0 | 0 | 36922 | 0 | 0 | 0 | 0 | 0 | 36922
2022061516 | 4 | 0.89887 | 71909.6 | 0.57044 | 20535.84 | 0.69777 | 8373.24 | 1 | 5000 | 20535.84 | 8373.24 | 0 | 0 | 0 | 0 | 38000.52 | 0 | 0 | 0 | 0 | 0 | 38000.52
2022061517 | 4 | 0.9096 | 72768 | 0.55631 | 20027.16 | 0.68206 | 8184.72 | 1 | 5000 | 20027.16 | 8184.72 | 0 | 0 | 0 | 0 | 39556.12 | 0 | 0 | 0 | 0 | 0 | 39556.12
2022061518 | 4 | 0.91023 | 72818.4 | 0.56591 | 20372.76 | 0.67445 | 8093.4 | 1 | 5000 | 20372.76 | 8093.4 | 0 | 0 | 0 | 0 | 39352.24 | 0 | 0 | 0 | 0 | 0 | 39352.24
2022061519 | 4 | 0.89797 | 71837.6 | 0.58786 | 21162.96 | 0.58491 | 7018.92 | 1 | 5000 | 21162.96 | 7018.92 | 0 | 0 | 0 | 0 | 38655.72 | 0 | 0 | 0 | 0 | 0 | 38655.72
2022061520 | 4 | 0.87021 | 69616.8 | 0.60434 | 21756.24 | 0.33002 | 3960.24 | 1 | 5000 | 21756.24 | 3960.24 | 0 | 0 | 0 | 0 | 38900.32 | 0 | 0 | 0 | 0 | 0 | 38900.32
2022061521 | 4 | 0.83715 | 66972 | 0.61804 | 22249.44 | 0.04842 | 581.04 | 1 | 5000 | 22249.44 | 581.04 | 0 | 0 | 0 | 0 | 39141.52 | 0 | 0 | 0 | 0 | 0 | 39141.52
2022061522 | 4 | 0.81248 | 64998.4 | 0.62914 | 22649.04 | 0 | 0 | 1 | 5000 | 22649.04 | 0 | 0 | 0 | 0 | 0 | 37349.36 | 0 | 0 | 0 | 0 | 0 | 37349.36
2022061523 | 4 | 0.76896 | 61516.8 | 0.6574 | 23666.4 | 5e-05 | 0.6 | 1 | 5000 | 23666.4 | 0.6 | 0 | 0 | 0 | 0 | 32849.8 | 0 | 0 | 0 | 0 | 0 | 32849.8
2022061524 | 4 | 0.71976 | 57580.8 | 0.66766 | 24035.76 | 6e-05 | 0.72 | 1 | 5000 | 24035.76 | 0.72 | 0 | 0 | 0 | 0 | 28544.32 | 0 | 0 | 0 | 0 | 0 | 28544.32
2022061601 | 5 | 0.67557 | 54045.6 | 0.65927 | 23733.72 | 6e-05 | 0.72 | 1 | 5000 | 23733.72 | 0.72 | 0 | 0 | 0 | 0 | 25311.16 | 0 | 0 | 0 | 0 | 0 | 25311.16
2022061602 | 5 | 0.64291 | 51432.8 | 0.63681 | 22925.16 | 6e-05 | 0.72 | 1 | 5000 | 22925.16 | 0.72 | 0 | 0 | 0 | 0 | 23506.92 | 0 | 0 | 0 | 0 | 0 | 23506.92
2022061603 | 5 | 0.61808 | 49446.4 | 0.60886 | 21918.96 | 6e-05 | 0.72 | 1 | 5000 | 21918.96 | 0.72 | 0 | 0 | 0 | 0 | 22526.72 | 0 | 0 | 0 | 0 | 0 | 22526.72
2022061604 | 5 | 0.60212 | 48169.6 | 0.58671 | 21121.56 | 0.00027 | 3.24 | 1 | 5000 | 21121.56 | 3.24 | 0 | 0 | 0 | 0 | 22044.8 | 0 | 0 | 0 | 0 | 0 | 22044.8
2022061605 | 5 | 0.59578 | 47662.4 | 0.55279 | 19900.44 | 6e-05 | 0.72 | 1 | 5000 | 19900.44 | 0.72 | 0 | 0 | 0 | 0 | 22761.24 | 0 | 0 | 0 | 0 | 0 | 22761.24
2022061606 | 5 | 0.59924 | 47939.2 | 0.50539 | 18194.04 | 6e-05 | 0.72 | 1 | 5000 | 18194.04 | 0.72 | 0 | 0 | 0 | 0 | 24744.44 | 0 | 0 | 0 | 0 | 0 | 24744.44
2022061607 | 5 | 0.61098 | 48878.4 | 0.47057 | 16940.52 | 0.00821 | 98.52 | 1 | 5000 | 16940.52 | 98.52 | 0 | 0 | 0 | 0 | 26839.36 | 0 | 0 | 0 | 0 | 0 | 26839.36
2022061608 | 5 | 0.62357 | 49885.6 | 0.41775 | 15039 | 0.17749 | 2129.88 | 1 | 5000 | 15039 | 2129.88 | 0 | 0 | 0 | 0 | 27716.72 | 0 | 0 | 0 | 0 | 0 | 27716.72
2022061609 | 5 | 0.65858 | 52686.4 | 0.42224 | 15200.64 | 0.5442 | 6530.4 | 1 | 5000 | 15200.64 | 6530.4 | 0 | 0 | 0 | 0 | 25955.36 | 0 | 0 | 0 | 0 | 0 | 25955.36
2022061610 | 5 | 0.70231 | 56184.8 | 0.46762 | 16834.32 | 0.61696 | 7403.52 | 1 | 5000 | 16834.32 | 7403.52 | 0 | 0 | 0 | 0 | 26946.96 | 0 | 0 | 0 | 0 | 0 | 26946.96
2022061611 | 5 | 0.75183 | 60146.4 | 0.43166 | 15539.76 | 0.72032 | 8643.84 | 1 | 5000 | 15539.76 | 8643.84 | 0 | 0 | 0 | 0 | 30962.8 | 0 | 0 | 0 | 0 | 0 | 30962.8
2022061612 | 5 | 0.80105 | 64084 | 0.4015 | 14454 | 0.79695 | 9563.4 | 1 | 5000 | 14454 | 9563.4 | 0 | 0 | 0 | 0 | 35066.6 | 0 | 0 | 0 | 0 | 0 | 35066.6
2022061613 | 5 | 0.84706 | 67764.8 | 0.40675 | 14643 | 0.79396 | 9527.52 | 1 | 5000 | 14643 | 9527.52 | 0 | 0 | 0 | 0 | 38594.28 | 0 | 0 | 0 | 0 | 0 | 38594.28
2022061614 | 5 | 0.89179 | 71343.2 | 0.42297 | 15226.92 | 0.79278 | 9513.36 | 1 | 5000 | 15226.92 | 9513.36 | 0 | 0 | 0 | 0 | 41602.92 | 0 | 0 | 0 | 0 | 0 | 41602.92
2022061615 | 5 | 0.92365 | 73892 | 0.44293 | 15945.48 | 0.79943 | 9593.16 | 1 | 5000 | 15945.48 | 9593.16 | 0 | 0 | 0 | 0 | 43353.36 | 0 | 0 | 0 | 0 | 0 | 43353.36
2022061616 | 5 | 0.93717 | 74973.6 | 0.47932 | 17255.52 | 0.75698 | 9083.76 | 1 | 5000 | 17255.52 | 9083.76 | 0 | 0 | 0 | 0 | 43634.32 | 0 | 0 | 0 | 0 | 0 | 43634.32
2022061617 | 5 | 0.94107 | 75285.6 | 0.49811 | 17931.96 | 0.72826 | 8739.12 | 1 | 5000 | 17931.96 | 8739.12 | 0 | 0 | 0 | 0 | 43614.52 | 0 | 0 | 0 | 0 | 0 | 43614.52
2022061618 | 5 | 0.93802 | 75041.6 | 0.50032 | 18011.52 | 0.70002 | 8400.24 | 1 | 5000 | 18011.52 | 8400.24 | 0 | 0 | 0 | 0 | 43629.84 | 0 | 0 | 0 | 0 | 0 | 43629.84
2022061619 | 5 | 0.92927 | 74341.6 | 0.49751 | 17910.36 | 0.62001 | 7440.12 | 1 | 5000 | 17910.36 | 7440.12 | 0 | 0 | 0 | 0 | 43991.12 | 0 | 0 | 0 | 0 | 0 | 43991.12
2022061620 | 5 | 0.89984 | 71987.2 | 0.49352 | 17766.72 | 0.32552 | 3906.24 | 1 | 5000 | 17766.72 | 3906.24 | 0 | 0 | 0 | 0 | 45314.24 | 0 | 0 | 0 | 0 | 0 | 45314.24
2022061621 | 5 | 0.8612 | 68896 | 0.47394 | 17061.84 | 0.03837 | 460.44 | 1 | 5000 | 17061.84 | 460.44 | 0 | 0 | 0 | 0 | 46373.72 | 0 | 0 | 0 | 0 | 0 | 46373.72
2022061622 | 5 | 0.82733 | 66186.4 | 0.49895 | 17962.2 | 0 | 0 | 1 | 5000 | 17962.2 | 0 | 0 | 0 | 0 | 0 | 43224.2 | 0 | 0 | 0 | 0 | 0 | 43224.2
2022061623 | 5 | 0.77718 | 62174.4 | 0.56565 | 20363.4 | 6e-05 | 0.72 | 1 | 5000 | 20363.4 | 0.72 | 0 | 0 | 0 | 0 | 36810.28 | 0 | 0 | 0 | 0 | 0 | 36810.28
2022061624 | 5 | 0.72295 | 57836 | 0.59138 | 21289.68 | 5e-05 | 0.6 | 1 | 5000 | 21289.68 | 0.6 | 0 | 0 | 0 | 0 | 31545.72 | 0 | 0 | 0 | 0 | 0 | 31545.72
2022061701 | 6 | 0.67457 | 53965.6 | 0.57964 | 20867.04 | 8e-05 | 0.96 | 1 | 5000 | 20867.04 | 0.96 | 0 | 0 | 0 | 0 | 28097.6 | 0 | 0 | 0 | 0 | 0 | 28097.6
2022061702 | 6 | 0.63442 | 50753.6 | 0.55962 | 20146.32 | 8e-05 | 0.96 | 1 | 5000 | 20146.32 | 0.96 | 0 | 0 | 0 | 0 | 25606.32 | 0 | 0 | 0 | 0 | 0 | 25606.32
2022061703 | 6 | 0.60666 | 48532.8 | 0.53768 | 19356.48 | 8e-05 | 0.96 | 1 | 5000 | 19356.48 | 0.96 | 0 | 0 | 0 | 0 | 24175.36 | 0 | 0 | 0 | 0 | 0 | 24175.36
2022061704 | 6 | 0.58559 | 46847.2 | 0.49762 | 17914.32 | 8e-05 | 0.96 | 1 | 5000 | 17914.32 | 0.96 | 0 | 0 | 0 | 0 | 23931.92 | 0 | 0 | 0 | 0 | 0 | 23931.92
2022061705 | 6 | 0.57502 | 46001.6 | 0.43863 | 15790.68 | 7e-05 | 0.84 | 1 | 5000 | 15790.68 | 0.84 | 0 | 0 | 0 | 0 | 25210.08 | 0 | 0 | 0 | 0 | 0 | 25210.08
2022061706 | 6 | 0.57764 | 46211.2 | 0.39999 | 14399.64 | 0.00011 | 1.32 | 1 | 5000 | 14399.64 | 1.32 | 0 | 0 | 0 | 0 | 26810.24 | 0 | 0 | 0 | 0 | 0 | 26810.24
2022061707 | 6 | 0.5839 | 46712 | 0.35864 | 12911.04 | 0.00458 | 54.96 | 1 | 5000 | 12911.04 | 54.96 | 0 | 0 | 0 | 0 | 28746 | 0 | 0 | 0 | 0 | 0 | 28746
2022061708 | 6 | 0.59854 | 47883.2 | 0.28973 | 10430.28 | 0.189 | 2268 | 1 | 5000 | 10430.28 | 2268 | 0 | 0 | 0 | 0 | 30184.92 | 0 | 0 | 0 | 0 | 0 | 30184.92
2022061709 | 6 | 0.63609 | 50887.2 | 0.20013 | 7204.68 | 0.57417 | 6890.04 | 1 | 5000 | 7204.68 | 6890.04 | 0 | 0 | 0 | 0 | 31792.48 | 0 | 0 | 0 | 0 | 0 | 31792.48
2022061710 | 6 | 0.68637 | 54909.6 | 0.22198 | 7991.28 | 0.73817 | 8858.04 | 1 | 5000 | 7991.28 | 8858.04 | 0 | 0 | 0 | 0 | 33060.28 | 0 | 0 | 0 | 0 | 0 | 33060.28
2022061711 | 6 | 0.74222 | 59377.6 | 0.24129 | 8686.44 | 0.79463 | 9535.56 | 1 | 5000 | 8686.44 | 9535.56 | 0 | 0 | 0 | 0 | 36155.6 | 0 | 0 | 0 | 0 | 0 | 36155.6
2022061712 | 6 | 0.79725 | 63780 | 0.21314 | 7673.04 | 0.81143 | 9737.16 | 1 | 5000 | 7673.04 | 9737.16 | 0 | 0 | 0 | 0 | 41369.8 | 0 | 0 | 0 | 0 | 0 | 41369.8
2022061713 | 6 | 0.84539 | 67631.2 | 0.18952 | 6822.72 | 0.8083 | 9699.6 | 1 | 5000 | 6822.72 | 9699.6 | 0 | 0 | 0 | 0 | 46108.88 | 0 | 0 | 0 | 0 | 0 | 46108.88
2022061714 | 6 | 0.88894 | 71115.2 | 0.21914 | 7889.04 | 0.78759 | 9451.08 | 1 | 5000 | 7889.04 | 9451.08 | 0 | 0 | 0 | 0 | 48775.08 | 0 | 0 | 0 | 0 | 0 | 48775.08
2022061715 | 6 | 0.91981 | 73584.8 | 0.26858 | 9668.88 | 0.78628 | 9435.36 | 1 | 5000 | 9668.88 | 9435.36 | 0 | 0 | 0 | 0 | 49480.56 | 0 | 0 | 0 | 0 | 0 | 49480.56
2022061716 | 6 | 0.93457 | 74765.6 | 0.31668 | 11400.48 | 0.74129 | 8895.48 | 1 | 5000 | 11400.48 | 8895.48 | 0 | 0 | 0 | 0 | 49469.64 | 0 | 0 | 0 | 0 | 0 | 49469.64
2022061717 | 6 | 0.93705 | 74964 | 0.35726 | 12861.36 | 0.72221 | 8666.52 | 1 | 5000 | 12861.36 | 8666.52 | 0 | 0 | 0 | 0 | 48436.12 | 0 | 0 | 0 | 0 | 0 | 48436.12
2022061718 | 6 | 0.93406 | 74724.8 | 0.38758 | 13952.88 | 0.7077 | 8492.4 | 1 | 5000 | 13952.88 | 8492.4 | 0 | 0 | 0 | 0 | 47279.52 | 0 | 0 | 0 | 0 | 0 | 47279.52
2022061719 | 6 | 0.91584 | 73267.2 | 0.4068 | 14644.8 | 0.61964 | 7435.68 | 1 | 5000 | 14644.8 | 7435.68 | 0 | 0 | 0 | 0 | 46186.72 | 0 | 0 | 0 | 0 | 0 | 46186.72
2022061720 | 6 | 0.88371 | 70696.8 | 0.41858 | 15068.88 | 0.34733 | 4167.96 | 1 | 5000 | 15068.88 | 4167.96 | 0 | 0 | 0 | 0 | 46459.96 | 0 | 0 | 0 | 0 | 0 | 46459.96
2022061721 | 6 | 0.84584 | 67667.2 | 0.409 | 14724 | 0.04352 | 522.24 | 1 | 5000 | 14724 | 522.24 | 0 | 0 | 0 | 0 | 47420.96 | 0 | 0 | 0 | 0 | 0 | 47420.96
2022061722 | 6 | 0.81199 | 64959.2 | 0.43551 | 15678.36 | 5e-05 | 0.6 | 1 | 5000 | 15678.36 | 0.6 | 0 | 0 | 0 | 0 | 44280.24 | 0 | 0 | 0 | 0 | 0 | 44280.24
2022061723 | 6 | 0.76636 | 61308.8 | 0.49109 | 17679.24 | 8e-05 | 0.96 | 1 | 5000 | 17679.24 | 0.96 | 0 | 0 | 0 | 0 | 38628.6 | 0 | 0 | 0 | 0 | 0 | 38628.6
2022061724 | 6 | 0.71726 | 57380.8 | 0.49428 | 17794.08 | 0.00011 | 1.32 | 1 | 5000 | 17794.08 | 1.32 | 0 | 0 | 0 | 0 | 34585.4 | 0 | 0 | 0 | 0 | 0 | 34585.4
2022061801 | 7 | 0.66993 | 53594.4 | 0.46747 | 16828.92 | 0.00011 | 1.32 | 1 | 5000 | 16828.92 | 1.32 | 0 | 0 | 0 | 0 | 31764.16 | 0 | 0 | 0 | 0 | 0 | 31764.16
2022061802 | 7 | 0.63086 | 50468.8 | 0.43402 | 15624.72 | 0.00011 | 1.32 | 1 | 5000 | 15624.72 | 1.32 | 0 | 0 | 0 | 0 | 29842.76 | 0 | 0 | 0 | 0 | 0 | 29842.76
2022061803 | 7 | 0.59901 | 47920.8 | 0.40609 | 14619.24 | 0.00011 | 1.32 | 1 | 5000 | 14619.24 | 1.32 | 0 | 0 | 0 | 0 | 28300.24 | 0 | 0 | 0 | 0 | 0 | 28300.24
2022061804 | 7 | 0.57512 | 46009.6 | 0.36305 | 13069.8 | 0.0001 | 1.2 | 1 | 5000 | 13069.8 | 1.2 | 0 | 0 | 0 | 0 | 27938.6 | 0 | 0 | 0 | 0 | 0 | 27938.6
2022061805 | 7 | 0.55935 | 44748 | 0.32302 | 11628.72 | 0.0001 | 1.2 | 1 | 5000 | 11628.72 | 1.2 | 0 | 0 | 0 | 0 | 28118.08 | 0 | 0 | 0 | 0 | 0 | 28118.08
2022061806 | 7 | 0.55329 | 44263.2 | 0.2958 | 10648.8 | 0.0001 | 1.2 | 1 | 5000 | 10648.8 | 1.2 | 0 | 0 | 0 | 0 | 28613.2 | 0 | 0 | 0 | 0 | 0 | 28613.2
2022061807 | 7 | 0.54853 | 43882.4 | 0.25711 | 9255.96 | 0.00459 | 55.08 | 1 | 5000 | 9255.96 | 55.08 | 0 | 0 | 0 | 0 | 29571.36 | 0 | 0 | 0 | 0 | 0 | 29571.36
2022061808 | 7 | 0.56306 | 45044.8 | 0.20758 | 7472.88 | 0.19029 | 2283.48 | 1 | 5000 | 7472.88 | 2283.48 | 0 | 0 | 0 | 0 | 30288.44 | 0 | 0 | 0 | 0 | 0 | 30288.44
2022061809 | 7 | 0.60331 | 48264.8 | 0.14226 | 5121.36 | 0.58522 | 7022.64 | 1 | 5000 | 5121.36 | 7022.64 | 0 | 0 | 0 | 0 | 31120.8 | 0 | 0 | 0 | 0 | 0 | 31120.8
2022061810 | 7 | 0.65074 | 52059.2 | 0.15889 | 5720.04 | 0.74445 | 8933.4 | 1 | 5000 | 5720.04 | 8933.4 | 0 | 0 | 0 | 0 | 32405.76 | 0 | 0 | 0 | 0 | 0 | 32405.76
2022061811 | 7 | 0.70698 | 56558.4 | 0.15368 | 5532.48 | 0.79455 | 9534.6 | 1 | 5000 | 5532.48 | 9534.6 | 0 | 0 | 0 | 0 | 36491.32 | 0 | 0 | 0 | 0 | 0 | 36491.32
2022061812 | 7 | 0.76159 | 60927.2 | 0.15549 | 5597.64 | 0.80643 | 9677.16 | 1 | 5000 | 5597.64 | 9677.16 | 0 | 0 | 0 | 0 | 40652.4 | 0 | 0 | 0 | 0 | 0 | 40652.4
2022061813 | 7 | 0.80992 | 64793.6 | 0.20241 | 7286.76 | 0.79271 | 9512.52 | 1 | 5000 | 7286.76 | 9512.52 | 0 | 0 | 0 | 0 | 42994.32 | 0 | 0 | 0 | 0 | 0 | 42994.32
2022061814 | 7 | 0.84767 | 67813.6 | 0.24786 | 8922.96 | 0.79057 | 9486.84 | 1 | 5000 | 8922.96 | 9486.84 | 0 | 0 | 0 | 0 | 44403.8 | 0 | 0 | 0 | 0 | 0 | 44403.8
2022061815 | 7 | 0.87713 | 70170.4 | 0.29406 | 10586.16 | 0.77296 | 9275.52 | 1 | 5000 | 10586.16 | 9275.52 | 0 | 0 | 0 | 0 | 45308.72 | 0 | 0 | 0 | 0 | 0 | 45308.72
2022061816 | 7 | 0.89724 | 71779.2 | 0.32575 | 11727 | 0.76053 | 9126.36 | 1 | 5000 | 11727 | 9126.36 | 0 | 0 | 0 | 0 | 45925.84 | 0 | 0 | 0 | 0 | 0 | 45925.84
2022061817 | 7 | 0.90777 | 72621.6 | 0.36528 | 13150.08 | 0.72952 | 8754.24 | 1 | 5000 | 13150.08 | 8754.24 | 0 | 0 | 0 | 0 | 45717.28 | 0 | 0 | 0 | 0 | 0 | 45717.28
2022061818 | 7 | 0.90689 | 72551.2 | 0.39985 | 14394.6 | 0.69322 | 8318.64 | 1 | 5000 | 14394.6 | 8318.64 | 0 | 0 | 0 | 0 | 44837.96 | 0 | 0 | 0 | 0 | 0 | 44837.96
2022061819 | 7 | 0.89095 | 71276 | 0.43224 | 15560.64 | 0.62816 | 7537.92 | 1 | 5000 | 15560.64 | 7537.92 | 0 | 0 | 0 | 0 | 43177.44 | 0 | 0 | 0 | 0 | 0 | 43177.44
2022061820 | 7 | 0.86098 | 68878.4 | 0.44362 | 15970.32 | 0.36902 | 4428.24 | 1 | 5000 | 15970.32 | 4428.24 | 0 | 0 | 0 | 0 | 43479.84 | 0 | 0 | 0 | 0 | 0 | 43479.84
2022061821 | 7 | 0.82316 | 65852.8 | 0.43272 | 15577.92 | 0.05988 | 718.56 | 1 | 5000 | 15577.92 | 718.56 | 0 | 0 | 0 | 0 | 44556.32 | 0 | 0 | 0 | 0 | 0 | 44556.32
2022061822 | 7 | 0.79669 | 63735.2 | 0.44121 | 15883.56 | 0.00892 | 107.04 | 1 | 5000 | 15883.56 | 107.04 | 0 | 0 | 0 | 0 | 42744.6 | 0 | 0 | 0 | 0 | 0 | 42744.6
2022061823 | 7 | 0.75567 | 60453.6 | 0.49183 | 17705.88 | 0.00113 | 13.56 | 1 | 5000 | 17705.88 | 13.56 | 0 | 0 | 0 | 0 | 37734.16 | 0 | 0 | 0 | 0 | 0 | 37734.16
2022061824 | 7 | 0.71222 | 56977.6 | 0.52183 | 18785.88 | 0 | 0 | 1 | 5000 | 18785.88 | 0 | 0 | 0 | 0 | 0 | 33191.72 | 0 | 0 | 0 | 0 | 0 | 33191.72
2022061901 | 1 | 0.668 | 53440 | 0.51264 | 18455.04 | 0 | 0 | 1 | 5000 | 18455.04 | 0 | 0 | 0 | 0 | 0 | 29984.96 | 0 | 0 | 0 | 0 | 0 | 29984.96
2022061902 | 1 | 0.63116 | 50492.8 | 0.48828 | 17578.08 | 0 | 0 | 1 | 5000 | 17578.08 | 0 | 0 | 0 | 0 | 0 | 27914.72 | 0 | 0 | 0 | 0 | 0 | 27914.72
2022061903 | 1 | 0.60021 | 48016.8 | 0.44735 | 16104.6 | 0 | 0 | 1 | 5000 | 16104.6 | 0 | 0 | 0 | 0 | 0 | 26912.2 | 0 | 0 | 0 | 0 | 0 | 26912.2
2022061904 | 1 | 0.57962 | 46369.6 | 0.42373 | 15254.28 | 0 | 0 | 1 | 5000 | 15254.28 | 0 | 0 | 0 | 0 | 0 | 26115.32 | 0 | 0 | 0 | 0 | 0 | 26115.32
2022061905 | 1 | 0.56292 | 45033.6 | 0.39356 | 14168.16 | 0 | 0 | 1 | 5000 | 14168.16 | 0 | 0 | 0 | 0 | 0 | 25865.44 | 0 | 0 | 0 | 0 | 0 | 25865.44
2022061906 | 1 | 0.55403 | 44322.4 | 0.3674 | 13226.4 | 0 | 0 | 1 | 5000 | 13226.4 | 0 | 0 | 0 | 0 | 0 | 26096 | 0 | 0 | 0 | 0 | 0 | 26096
2022061907 | 1 | 0.54507 | 43605.6 | 0.3341 | 12027.6 | 0.00539 | 64.68 | 1 | 5000 | 12027.6 | 64.68 | 0 | 0 | 0 | 0 | 26513.32 | 0 | 0 | 0 | 0 | 0 | 26513.32
2022061908 | 1 | 0.55675 | 44540 | 0.25563 | 9202.68 | 0.22201 | 2664.12 | 1 | 5000 | 9202.68 | 2664.12 | 0 | 0 | 0 | 0 | 27673.2 | 0 | 0 | 0 | 0 | 0 | 27673.2
2022061909 | 1 | 0.59932 | 47945.6 | 0.20097 | 7234.92 | 0.62323 | 7478.76 | 1 | 5000 | 7234.92 | 7478.76 | 0 | 0 | 0 | 0 | 28231.92 | 0 | 0 | 0 | 0 | 0 | 28231.92
2022061910 | 1 | 0.65763 | 52610.4 | 0.24159 | 8697.24 | 0.76815 | 9217.8 | 1 | 5000 | 8697.24 | 9217.8 | 0 | 0 | 0 | 0 | 29695.36 | 0 | 0 | 0 | 0 | 0 | 29695.36
2022061911 | 1 | 0.7165 | 57320 | 0.28343 | 10203.48 | 0.81248 | 9749.76 | 1 | 5000 | 10203.48 | 9749.76 | 0 | 0 | 0 | 0 | 32366.76 | 0 | 0 | 0 | 0 | 0 | 32366.76
2022061912 | 1 | 0.77425 | 61940 | 0.29554 | 10639.44 | 0.81531 | 9783.72 | 1 | 5000 | 10639.44 | 9783.72 | 0 | 0 | 0 | 0 | 36516.84 | 0 | 0 | 0 | 0 | 0 | 36516.84
2022061913 | 1 | 0.82218 | 65774.4 | 0.32162 | 11578.32 | 0.80655 | 9678.6 | 1 | 5000 | 11578.32 | 9678.6 | 0 | 0 | 0 | 0 | 39517.48 | 0 | 0 | 0 | 0 | 0 | 39517.48
2022061914 | 1 | 0.86072 | 68857.6 | 0.3572 | 12859.2 | 0.79495 | 9539.4 | 1 | 5000 | 12859.2 | 9539.4 | 0 | 0 | 0 | 0 | 41459 | 0 | 0 | 0 | 0 | 0 | 41459
2022061915 | 1 | 0.88819 | 71055.2 | 0.39544 | 14235.84 | 0.78809 | 9457.08 | 1 | 5000 | 14235.84 | 9457.08 | 0 | 0 | 0 | 0 | 42362.28 | 0 | 0 | 0 | 0 | 0 | 42362.28
2022061916 | 1 | 0.90707 | 72565.6 | 0.43454 | 15643.44 | 0.75207 | 9024.84 | 1 | 5000 | 15643.44 | 9024.84 | 0 | 0 | 0 | 0 | 42897.32 | 0 | 0 | 0 | 0 | 0 | 42897.32
2022061917 | 1 | 0.9203 | 73624 | 0.46768 | 16836.48 | 0.71829 | 8619.48 | 1 | 5000 | 16836.48 | 8619.48 | 0 | 0 | 0 | 0 | 43168.04 | 0 | 0 | 0 | 0 | 0 | 43168.04
2022061918 | 1 | 0.92448 | 73958.4 | 0.49298 | 17747.28 | 0.63619 | 7634.28 | 1 | 5000 | 17747.28 | 7634.28 | 0 | 0 | 0 | 0 | 43576.84 | 0 | 0 | 0 | 0 | 0 | 43576.84
2022061919 | 1 | 0.91113 | 72890.4 | 0.52543 | 18915.48 | 0.53903 | 6468.36 | 1 | 5000 | 18915.48 | 6468.36 | 0 | 0 | 0 | 0 | 42506.56 | 0 | 0 | 0 | 0 | 0 | 42506.56
2022061920 | 1 | 0.87733 | 70186.4 | 0.55004 | 19801.44 | 0.33603 | 4032.36 | 1 | 5000 | 19801.44 | 4032.36 | 0 | 0 | 0 | 0 | 41352.6 | 0 | 0 | 0 | 0 | 0 | 41352.6
2022061921 | 1 | 0.83477 | 66781.6 | 0.51086 | 18390.96 | 0.04619 | 554.28 | 1 | 5000 | 18390.96 | 554.28 | 0 | 0 | 0 | 0 | 42836.36 | 0 | 0 | 0 | 0 | 0 | 42836.36
2022061922 | 1 | 0.80484 | 64387.2 | 0.45241 | 16286.76 | 0 | 0 | 1 | 5000 | 16286.76 | 0 | 0 | 0 | 0 | 0 | 43100.44 | 0 | 0 | 0 | 0 | 0 | 43100.44
2022061923 | 1 | 0.75804 | 60643.2 | 0.45525 | 16389 | 7e-05 | 0.84 | 1 | 5000 | 16389 | 0.84 | 0 | 0 | 0 | 0 | 39253.36 | 0 | 0 | 0 | 0 | 0 | 39253.36
2022061924 | 1 | 0.70565 | 56452 | 0.47546 | 17116.56 | 0.0001 | 1.2 | 1 | 5000 | 17116.56 | 1.2 | 0 | 0 | 0 | 0 | 34334.24 | 0 | 0 | 0 | 0 | 0 | 34334.24
2022062001 | 2 | 0.65968 | 52774.4 | 0.49373 | 17774.28 | 0.0001 | 1.2 | 1 | 5000 | 17774.28 | 1.2 | 0 | 0 | 0 | 0 | 29998.92 | 0 | 0 | 0 | 0 | 0 | 29998.92
2022062002 | 2 | 0.62409 | 49927.2 | 0.50354 | 18127.44 | 0.0001 | 1.2 | 1 | 5000 | 18127.44 | 1.2 | 0 | 0 | 0 | 0 | 26798.56 | 0 | 0 | 0 | 0 | 0 | 26798.56
2022062003 | 2 | 0.59719 | 47775.2 | 0.49297 | 17746.92 | 0.0001 | 1.2 | 1 | 5000 | 17746.92 | 1.2 | 0 | 0 | 0 | 0 | 25027.08 | 0 | 0 | 0 | 0 | 0 | 25027.08
2022062004 | 2 | 0.58226 | 46580.8 | 0.47586 | 17130.96 | 0.0001 | 1.2 | 1 | 5000 | 17130.96 | 1.2 | 0 | 0 | 0 | 0 | 24448.64 | 0 | 0 | 0 | 0 | 0 | 24448.64
2022062005 | 2 | 0.57298 | 45838.4 | 0.42959 | 15465.24 | 0.0001 | 1.2 | 1 | 5000 | 15465.24 | 1.2 | 0 | 0 | 0 | 0 | 25371.96 | 0 | 0 | 0 | 0 | 0 | 25371.96
2022062006 | 2 | 0.5747 | 45976 | 0.36148 | 13013.28 | 0.0001 | 1.2 | 1 | 5000 | 13013.28 | 1.2 | 0 | 0 | 0 | 0 | 27961.52 | 0 | 0 | 0 | 0 | 0 | 27961.52
2022062007 | 2 | 0.58276 | 46620.8 | 0.30575 | 11007 | 0.00583 | 69.96 | 1 | 5000 | 11007 | 69.96 | 0 | 0 | 0 | 0 | 30543.84 | 0 | 0 | 0 | 0 | 0 | 30543.84
2022062008 | 2 | 0.60244 | 48195.2 | 0.25078 | 9028.08 | 0.21976 | 2637.12 | 1 | 5000 | 9028.08 | 2637.12 | 0 | 0 | 0 | 0 | 31530 | 0 | 0 | 0 | 0 | 0 | 31530
2022062009 | 2 | 0.64451 | 51560.8 | 0.21967 | 7908.12 | 0.61794 | 7415.28 | 1 | 5000 | 7908.12 | 7415.28 | 0 | 0 | 0 | 0 | 31237.4 | 0 | 0 | 0 | 0 | 0 | 31237.4
2022062010 | 2 | 0.69968 | 55974.4 | 0.28223 | 10160.28 | 0.76595 | 9191.4 | 1 | 5000 | 10160.28 | 9191.4 | 0 | 0 | 0 | 0 | 31622.72 | 0 | 0 | 0 | 0 | 0 | 31622.72
2022062011 | 2 | 0.76108 | 60886.4 | 0.36516 | 13145.76 | 0.79395 | 9527.4 | 1 | 5000 | 13145.76 | 9527.4 | 0 | 0 | 0 | 0 | 33213.24 | 0 | 0 | 0 | 0 | 0 | 33213.24
2022062012 | 2 | 0.82184 | 65747.2 | 0.42521 | 15307.56 | 0.72768 | 8732.16 | 1 | 5000 | 15307.56 | 8732.16 | 0 | 0 | 0 | 0 | 36707.48 | 0 | 0 | 0 | 0 | 0 | 36707.48
2022062013 | 2 | 0.8728 | 69824 | 0.45809 | 16491.24 | 0.69394 | 8327.28 | 1 | 5000 | 16491.24 | 8327.28 | 0 | 0 | 0 | 0 | 40005.48 | 0 | 0 | 0 | 0 | 0 | 40005.48
2022062014 | 2 | 0.91765 | 73412 | 0.4827 | 17377.2 | 0.70016 | 8401.92 | 1 | 5000 | 17377.2 | 8401.92 | 0 | 0 | 0 | 0 | 42632.88 | 0 | 0 | 0 | 0 | 0 | 42632.88
2022062015 | 2 | 0.94447 | 75557.6 | 0.48875 | 17595 | 0.73073 | 8768.76 | 1 | 5000 | 17595 | 8768.76 | 0 | 0 | 0 | 0 | 44193.84 | 0 | 0 | 0 | 0 | 0 | 44193.84
2022062016 | 2 | 0.95373 | 76298.4 | 0.46766 | 16835.76 | 0.73142 | 8777.04 | 1 | 5000 | 16835.76 | 8777.04 | 0 | 0 | 0 | 0 | 45685.6 | 0 | 0 | 0 | 0 | 0 | 45685.6
2022062017 | 2 | 0.95924 | 76739.2 | 0.4673 | 16822.8 | 0.6805 | 8166 | 1 | 5000 | 16822.8 | 8166 | 0 | 0 | 0 | 0 | 46750.4 | 0 | 0 | 0 | 0 | 0 | 46750.4
2022062018 | 2 | 0.95809 | 76647.2 | 0.49063 | 17662.68 | 0.6321 | 7585.2 | 1 | 5000 | 17662.68 | 7585.2 | 0 | 0 | 0 | 0 | 46399.32 | 0 | 0 | 0 | 0 | 0 | 46399.32
2022062019 | 2 | 0.94821 | 75856.8 | 0.50463 | 18166.68 | 0.50145 | 6017.4 | 1 | 5000 | 18166.68 | 6017.4 | 0 | 0 | 0 | 0 | 46672.72 | 0 | 0 | 0 | 0 | 0 | 46672.72
2022062020 | 2 | 0.92089 | 73671.2 | 0.49219 | 17718.84 | 0.23399 | 2807.88 | 1 | 5000 | 17718.84 | 2807.88 | 0 | 0 | 0 | 0 | 48144.48 | 0 | 0 | 0 | 0 | 0 | 48144.48
2022062021 | 2 | 0.88235 | 70588 | 0.4372 | 15739.2 | 0.01974 | 236.88 | 1 | 5000 | 15739.2 | 236.88 | 0 | 0 | 0 | 0 | 49611.92 | 0 | 0 | 0 | 0 | 0 | 49611.92
2022062022 | 2 | 0.85291 | 68232.8 | 0.40702 | 14652.72 | 0 | 0 | 1 | 5000 | 14652.72 | 0 | 0 | 0 | 0 | 0 | 48580.08 | 0 | 0 | 0 | 0 | 0 | 48580.08
2022062023 | 2 | 0.80181 | 64144.8 | 0.446 | 16056 | 0 | 0 | 1 | 5000 | 16056 | 0 | 0 | 0 | 0 | 0 | 43088.8 | 0 | 0 | 0 | 0 | 0 | 43088.8
2022062024 | 2 | 0.7486 | 59888 | 0.49212 | 17716.32 | 0 | 0 | 1 | 5000 | 17716.32 | 0 | 0 | 0 | 0 | 0 | 37171.68 | 0 | 0 | 0 | 0 | 0 | 37171.68
2022062101 | 3 | 0.69986 | 55988.8 | 0.499 | 17964 | 0 | 0 | 1 | 5000 | 17964 | 0 | 0 | 0 | 0 | 0 | 33024.8 | 0 | 0 | 0 | 0 | 0 | 33024.8
2022062102 | 3 | 0.66214 | 52971.2 | 0.48114 | 17321.04 | 0 | 0 | 1 | 5000 | 17321.04 | 0 | 0 | 0 | 0 | 0 | 30650.16 | 0 | 0 | 0 | 0 | 0 | 30650.16
2022062103 | 3 | 0.63127 | 50501.6 | 0.44222 | 15919.92 | 0 | 0 | 1 | 5000 | 15919.92 | 0 | 0 | 0 | 0 | 0 | 29581.68 | 0 | 0 | 0 | 0 | 0 | 29581.68
2022062104 | 3 | 0.61284 | 49027.2 | 0.40766 | 14675.76 | 0 | 0 | 1 | 5000 | 14675.76 | 0 | 0 | 0 | 0 | 0 | 29351.44 | 0 | 0 | 0 | 0 | 0 | 29351.44
2022062105 | 3 | 0.6037 | 48296 | 0.39094 | 14073.84 | 0 | 0 | 1 | 5000 | 14073.84 | 0 | 0 | 0 | 0 | 0 | 29222.16 | 0 | 0 | 0 | 0 | 0 | 29222.16
2022062106 | 3 | 0.60776 | 48620.8 | 0.36266 | 13055.76 | 0 | 0 | 1 | 5000 | 13055.76 | 0 | 0 | 0 | 0 | 0 | 30565.04 | 0 | 0 | 0 | 0 | 0 | 30565.04
2022062107 | 3 | 0.61805 | 49444 | 0.33696 | 12130.56 | 0.00533 | 63.96 | 1 | 5000 | 12130.56 | 63.96 | 0 | 0 | 0 | 0 | 32249.48 | 0 | 0 | 0 | 0 | 0 | 32249.48
2022062108 | 3 | 0.63623 | 50898.4 | 0.28626 | 10305.36 | 0.19631 | 2355.72 | 1 | 5000 | 10305.36 | 2355.72 | 0 | 0 | 0 | 0 | 33237.32 | 0 | 0 | 0 | 0 | 0 | 33237.32
2022062109 | 3 | 0.67577 | 54061.6 | 0.24876 | 8955.36 | 0.56253 | 6750.36 | 1 | 5000 | 8955.36 | 6750.36 | 0 | 0 | 0 | 0 | 33355.88 | 0 | 0 | 0 | 0 | 0 | 33355.88
2022062110 | 3 | 0.72327 | 57861.6 | 0.32435 | 11676.6 | 0.70239 | 8428.68 | 1 | 5000 | 11676.6 | 8428.68 | 0 | 0 | 0 | 0 | 32756.32 | 0 | 0 | 0 | 0 | 0 | 32756.32
2022062111 | 3 | 0.77212 | 61769.6 | 0.34374 | 12374.64 | 0.74878 | 8985.36 | 1 | 5000 | 12374.64 | 8985.36 | 0 | 0 | 0 | 0 | 35409.6 | 0 | 0 | 0 | 0 | 0 | 35409.6
2022062112 | 3 | 0.82319 | 65855.2 | 0.30603 | 11017.08 | 0.77513 | 9301.56 | 1 | 5000 | 11017.08 | 9301.56 | 0 | 0 | 0 | 0 | 40536.56 | 0 | 0 | 0 | 0 | 0 | 40536.56
2022062113 | 3 | 0.86869 | 69495.2 | 0.24697 | 8890.92 | 0.75596 | 9071.52 | 1 | 5000 | 8890.92 | 9071.52 | 0 | 0 | 0 | 0 | 46532.76 | 0 | 0 | 0 | 0 | 0 | 46532.76
2022062114 | 3 | 0.90666 | 72532.8 | 0.22328 | 8038.08 | 0.76238 | 9148.56 | 1 | 5000 | 8038.08 | 9148.56 | 0 | 0 | 0 | 0 | 50346.16 | 0 | 0 | 0 | 0 | 0 | 50346.16
2022062115 | 3 | 0.93414 | 74731.2 | 0.23238 | 8365.68 | 0.74859 | 8983.08 | 1 | 5000 | 8365.68 | 8983.08 | 0 | 0 | 0 | 0 | 52382.44 | 0 | 0 | 0 | 0 | 0 | 52382.44
2022062116 | 3 | 0.94961 | 75968.8 | 0.26943 | 9699.48 | 0.75624 | 9074.88 | 1 | 5000 | 9699.48 | 9074.88 | 0 | 0 | 0 | 0 | 52194.44 | 0 | 0 | 0 | 0 | 0 | 52194.44
2022062117 | 3 | 0.95273 | 76218.4 | 0.31581 | 11369.16 | 0.73976 | 8877.12 | 1 | 5000 | 11369.16 | 8877.12 | 0 | 0 | 0 | 0 | 50972.12 | 0 | 0 | 0 | 0 | 0 | 50972.12
2022062118 | 3 | 0.94979 | 75983.2 | 0.34324 | 12356.64 | 0.68796 | 8255.52 | 1 | 5000 | 12356.64 | 8255.52 | 0 | 0 | 0 | 0 | 50371.04 | 0 | 0 | 0 | 0 | 0 | 50371.04
2022062119 | 3 | 0.93536 | 74828.8 | 0.36859 | 13269.24 | 0.5756 | 6907.2 | 1 | 5000 | 13269.24 | 6907.2 | 0 | 0 | 0 | 0 | 49652.36 | 0 | 0 | 0 | 0 | 0 | 49652.36
2022062120 | 3 | 0.90484 | 72387.2 | 0.3838 | 13816.8 | 0.29853 | 3582.36 | 1 | 5000 | 13816.8 | 3582.36 | 0 | 0 | 0 | 0 | 49988.04 | 0 | 0 | 0 | 0 | 0 | 49988.04
2022062121 | 3 | 0.86339 | 69071.2 | 0.38004 | 13681.44 | 0.02376 | 285.12 | 1 | 5000 | 13681.44 | 285.12 | 0 | 0 | 0 | 0 | 50104.64 | 0 | 0 | 0 | 0 | 0 | 50104.64
2022062122 | 3 | 0.83125 | 66500 | 0.39072 | 14065.92 | 0 | 0 | 1 | 5000 | 14065.92 | 0 | 0 | 0 | 0 | 0 | 47434.08 | 0 | 0 | 0 | 0 | 0 | 47434.08
2022062123 | 3 | 0.78205 | 62564 | 0.44059 | 15861.24 | 0 | 0 | 1 | 5000 | 15861.24 | 0 | 0 | 0 | 0 | 0 | 41702.76 | 0 | 0 | 0 | 0 | 0 | 41702.76
2022062124 | 3 | 0.72667 | 58133.6 | 0.45844 | 16503.84 | 0 | 0 | 1 | 5000 | 16503.84 | 0 | 0 | 0 | 0 | 0 | 36629.76 | 0 | 0 | 0 | 0 | 0 | 36629.76
2022062201 | 4 | 0.67756 | 54204.8 | 0.43427 | 15633.72 | 0 | 0 | 1 | 5000 | 15633.72 | 0 | 0 | 0 | 0 | 0 | 33571.08 | 0 | 0 | 0 | 0 | 0 | 33571.08
2022062202 | 4 | 0.63986 | 51188.8 | 0.42719 | 15378.84 | 0 | 0 | 1 | 5000 | 15378.84 | 0 | 0 | 0 | 0 | 0 | 30809.96 | 0 | 0 | 0 | 0 | 0 | 30809.96
2022062203 | 4 | 0.61195 | 48956 | 0.40233 | 14483.88 | 0 | 0 | 1 | 5000 | 14483.88 | 0 | 0 | 0 | 0 | 0 | 29472.12 | 0 | 0 | 0 | 0 | 0 | 29472.12
2022062204 | 4 | 0.59279 | 47423.2 | 0.35089 | 12632.04 | 0 | 0 | 1 | 5000 | 12632.04 | 0 | 0 | 0 | 0 | 0 | 29791.16 | 0 | 0 | 0 | 0 | 0 | 29791.16
2022062205 | 4 | 0.58406 | 46724.8 | 0.29327 | 10557.72 | 0 | 0 | 1 | 5000 | 10557.72 | 0 | 0 | 0 | 0 | 0 | 31167.08 | 0 | 0 | 0 | 0 | 0 | 31167.08
2022062206 | 4 | 0.58894 | 47115.2 | 0.24524 | 8828.64 | 0 | 0 | 1 | 5000 | 8828.64 | 0 | 0 | 0 | 0 | 0 | 33286.56 | 0 | 0 | 0 | 0 | 0 | 33286.56
2022062207 | 4 | 0.59918 | 47934.4 | 0.22006 | 7922.16 | 0.00533 | 63.96 | 1 | 5000 | 7922.16 | 63.96 | 0 | 0 | 0 | 0 | 34948.28 | 0 | 0 | 0 | 0 | 0 | 34948.28
2022062208 | 4 | 0.61843 | 49474.4 | 0.16691 | 6008.76 | 0.2081 | 2497.2 | 1 | 5000 | 6008.76 | 2497.2 | 0 | 0 | 0 | 0 | 35968.44 | 0 | 0 | 0 | 0 | 0 | 35968.44
2022062209 | 4 | 0.6577 | 52616 | 0.1085 | 3906 | 0.58499 | 7019.88 | 1 | 5000 | 3906 | 7019.88 | 0 | 0 | 0 | 0 | 36690.12 | 0 | 0 | 0 | 0 | 0 | 36690.12
2022062210 | 4 | 0.70408 | 56326.4 | 0.11122 | 4003.92 | 0.70489 | 8458.68 | 1 | 5000 | 4003.92 | 8458.68 | 0 | 0 | 0 | 0 | 38863.8 | 0 | 0 | 0 | 0 | 0 | 38863.8
2022062211 | 4 | 0.75728 | 60582.4 | 0.08852 | 3186.72 | 0.74161 | 8899.32 | 1 | 5000 | 3186.72 | 8899.32 | 0 | 0 | 0 | 0 | 43496.36 | 0 | 0 | 0 | 0 | 0 | 43496.36
2022062212 | 4 | 0.81185 | 64948 | 0.08658 | 3116.88 | 0.78844 | 9461.28 | 1 | 5000 | 3116.88 | 9461.28 | 0 | 0 | 0 | 0 | 47369.84 | 0 | 0 | 0 | 0 | 0 | 47369.84
2022062213 | 4 | 0.85911 | 68728.8 | 0.10601 | 3816.36 | 0.79125 | 9495 | 1 | 5000 | 3816.36 | 9495 | 0 | 0 | 0 | 0 | 50417.44 | 0 | 0 | 0 | 0 | 0 | 50417.44
2022062214 | 4 | 0.90021 | 72016.8 | 0.12589 | 4532.04 | 0.75608 | 9072.96 | 1 | 5000 | 4532.04 | 9072.96 | 0 | 0 | 0 | 0 | 53411.8 | 0 | 0 | 0 | 0 | 0 | 53411.8
2022062215 | 4 | 0.92661 | 74128.8 | 0.15073 | 5426.28 | 0.70761 | 8491.32 | 1 | 5000 | 5426.28 | 8491.32 | 0 | 0 | 0 | 0 | 55211.2 | 0 | 0 | 0 | 0 | 0 | 55211.2
2022062216 | 4 | 0.94304 | 75443.2 | 0.17179 | 6184.44 | 0.70546 | 8465.52 | 1 | 5000 | 6184.44 | 8465.52 | 0 | 0 | 0 | 0 | 55793.24 | 0 | 0 | 0 | 0 | 0 | 55793.24
2022062217 | 4 | 0.95132 | 76105.6 | 0.19442 | 6999.12 | 0.68864 | 8263.68 | 1 | 5000 | 6999.12 | 8263.68 | 0 | 0 | 0 | 0 | 55842.8 | 0 | 0 | 0 | 0 | 0 | 55842.8
2022062218 | 4 | 0.94629 | 75703.2 | 0.21203 | 7633.08 | 0.64595 | 7751.4 | 1 | 5000 | 7633.08 | 7751.4 | 0 | 0 | 0 | 0 | 55318.72 | 0 | 0 | 0 | 0 | 0 | 55318.72
2022062219 | 4 | 0.92852 | 74281.6 | 0.23168 | 8340.48 | 0.55119 | 6614.28 | 1 | 5000 | 8340.48 | 6614.28 | 0 | 0 | 0 | 0 | 54326.84 | 0 | 0 | 0 | 0 | 0 | 54326.84
2022062220 | 4 | 0.89869 | 71895.2 | 0.25309 | 9111.24 | 0.35147 | 4217.64 | 1 | 5000 | 9111.24 | 4217.64 | 0 | 0 | 0 | 0 | 53566.32 | 0 | 0 | 0 | 0 | 0 | 53566.32
2022062221 | 4 | 0.86386 | 69108.8 | 0.27166 | 9779.76 | 0.05122 | 614.64 | 1 | 5000 | 9779.76 | 614.64 | 0 | 0 | 0 | 0 | 53714.4 | 0 | 0 | 0 | 0 | 0 | 53714.4
2022062222 | 4 | 0.83348 | 66678.4 | 0.31742 | 11427.12 | 0 | 0 | 1 | 5000 | 11427.12 | 0 | 0 | 0 | 0 | 0 | 50251.28 | 0 | 0 | 0 | 0 | 0 | 50251.28
2022062223 | 4 | 0.78394 | 62715.2 | 0.36768 | 13236.48 | 0 | 0 | 1 | 5000 | 13236.48 | 0 | 0 | 0 | 0 | 0 | 44478.72 | 0 | 0 | 0 | 0 | 0 | 44478.72
2022062224 | 4 | 0.73006 | 58404.8 | 0.39378 | 14176.08 | 0 | 0 | 1 | 5000 | 14176.08 | 0 | 0 | 0 | 0 | 0 | 39228.72 | 0 | 0 | 0 | 0 | 0 | 39228.72
2022062301 | 5 | 0.68116 | 54492.8 | 0.41525 | 14949 | 0 | 0 | 1 | 5000 | 14949 | 0 | 0 | 0 | 0 | 0 | 34543.8 | 0 | 0 | 0 | 0 | 0 | 34543.8
2022062302 | 5 | 0.64215 | 51372 | 0.41144 | 14811.84 | 0 | 0 | 1 | 5000 | 14811.84 | 0 | 0 | 0 | 0 | 0 | 31560.16 | 0 | 0 | 0 | 0 | 0 | 31560.16
2022062303 | 5 | 0.61262 | 49009.6 | 0.39787 | 14323.32 | 0 | 0 | 1 | 5000 | 14323.32 | 0 | 0 | 0 | 0 | 0 | 29686.28 | 0 | 0 | 0 | 0 | 0 | 29686.28
2022062304 | 5 | 0.59229 | 47383.2 | 0.37419 | 13470.84 | 0 | 0 | 1 | 5000 | 13470.84 | 0 | 0 | 0 | 0 | 0 | 28912.36 | 0 | 0 | 0 | 0 | 0 | 28912.36
2022062305 | 5 | 0.58554 | 46843.2 | 0.35384 | 12738.24 | 0 | 0 | 1 | 5000 | 12738.24 | 0 | 0 | 0 | 0 | 0 | 29104.96 | 0 | 0 | 0 | 0 | 0 | 29104.96
2022062306 | 5 | 0.58877 | 47101.6 | 0.33817 | 12174.12 | 0 | 0 | 1 | 5000 | 12174.12 | 0 | 0 | 0 | 0 | 0 | 29927.48 | 0 | 0 | 0 | 0 | 0 | 29927.48
2022062307 | 5 | 0.59764 | 47811.2 | 0.32868 | 11832.48 | 0.00513 | 61.56 | 1 | 5000 | 11832.48 | 61.56 | 0 | 0 | 0 | 0 | 30917.16 | 0 | 0 | 0 | 0 | 0 | 30917.16
2022062308 | 5 | 0.61702 | 49361.6 | 0.27991 | 10076.76 | 0.1937 | 2324.4 | 1 | 5000 | 10076.76 | 2324.4 | 0 | 0 | 0 | 0 | 31960.44 | 0 | 0 | 0 | 0 | 0 | 31960.44
2022062309 | 5 | 0.65804 | 52643.2 | 0.20486 | 7374.96 | 0.57998 | 6959.76 | 1 | 5000 | 7374.96 | 6959.76 | 0 | 0 | 0 | 0 | 33308.48 | 0 | 0 | 0 | 0 | 0 | 33308.48
2022062310 | 5 | 0.71349 | 57079.2 | 0.21547 | 7756.92 | 0.76745 | 9209.4 | 1 | 5000 | 7756.92 | 9209.4 | 0 | 0 | 0 | 0 | 35112.88 | 0 | 0 | 0 | 0 | 0 | 35112.88
2022062311 | 5 | 0.77457 | 61965.6 | 0.18393 | 6621.48 | 0.80766 | 9691.92 | 1 | 5000 | 6621.48 | 9691.92 | 0 | 0 | 0 | 0 | 40652.2 | 0 | 0 | 0 | 0 | 0 | 40652.2
2022062312 | 5 | 0.83168 | 66534.4 | 0.15963 | 5746.68 | 0.81208 | 9744.96 | 1 | 5000 | 5746.68 | 9744.96 | 0 | 0 | 0 | 0 | 46042.76 | 0 | 0 | 0 | 0 | 0 | 46042.76
2022062313 | 5 | 0.87968 | 70374.4 | 0.15972 | 5749.92 | 0.78933 | 9471.96 | 1 | 5000 | 5749.92 | 9471.96 | 0 | 0 | 0 | 0 | 50152.52 | 0 | 0 | 0 | 0 | 0 | 50152.52
2022062314 | 5 | 0.92227 | 73781.6 | 0.17499 | 6299.64 | 0.75025 | 9003 | 1 | 5000 | 6299.64 | 9003 | 0 | 0 | 0 | 0 | 53478.96 | 0 | 0 | 0 | 0 | 0 | 53478.96
2022062315 | 5 | 0.95018 | 76014.4 | 0.19549 | 7037.64 | 0.7461 | 8953.2 | 1 | 5000 | 7037.64 | 8953.2 | 0 | 0 | 0 | 0 | 55023.56 | 0 | 0 | 0 | 0 | 0 | 55023.56
2022062316 | 5 | 0.95693 | 76554.4 | 0.2033 | 7318.8 | 0.71954 | 8634.48 | 1 | 5000 | 7318.8 | 8634.48 | 0 | 0 | 0 | 0 | 55601.12 | 0 | 0 | 0 | 0 | 0 | 55601.12
2022062317 | 5 | 0.9595 | 76760 | 0.20717 | 7458.12 | 0.68839 | 8260.68 | 1 | 5000 | 7458.12 | 8260.68 | 0 | 0 | 0 | 0 | 56041.2 | 0 | 0 | 0 | 0 | 0 | 56041.2
2022062318 | 5 | 0.95751 | 76600.8 | 0.21242 | 7647.12 | 0.70698 | 8483.76 | 1 | 5000 | 7647.12 | 8483.76 | 0 | 0 | 0 | 0 | 55469.92 | 0 | 0 | 0 | 0 | 0 | 55469.92
2022062319 | 5 | 0.9521 | 76168 | 0.2302 | 8287.2 | 0.61696 | 7403.52 | 1 | 5000 | 8287.2 | 7403.52 | 0 | 0 | 0 | 0 | 55477.28 | 0 | 0 | 0 | 0 | 0 | 55477.28
2022062320 | 5 | 0.92983 | 74386.4 | 0.26642 | 9591.12 | 0.35777 | 4293.24 | 1 | 5000 | 9591.12 | 4293.24 | 0 | 0 | 0 | 0 | 55502.04 | 0 | 0 | 0 | 0 | 0 | 55502.04
2022062321 | 5 | 0.89247 | 71397.6 | 0.30203 | 10873.08 | 0.04867 | 584.04 | 1 | 5000 | 10873.08 | 584.04 | 0 | 0 | 0 | 0 | 54940.48 | 0 | 0 | 0 | 0 | 0 | 54940.48
2022062322 | 5 | 0.85863 | 68690.4 | 0.36353 | 13087.08 | 0 | 0 | 1 | 5000 | 13087.08 | 0 | 0 | 0 | 0 | 0 | 50603.32 | 0 | 0 | 0 | 0 | 0 | 50603.32
2022062323 | 5 | 0.80833 | 64666.4 | 0.44118 | 15882.48 | 0 | 0 | 1 | 5000 | 15882.48 | 0 | 0 | 0 | 0 | 0 | 43783.92 | 0 | 0 | 0 | 0 | 0 | 43783.92
2022062324 | 5 | 0.75401 | 60320.8 | 0.49808 | 17930.88 | 0 | 0 | 1 | 5000 | 17930.88 | 0 | 0 | 0 | 0 | 0 | 37389.92 | 0 | 0 | 0 | 0 | 0 | 37389.92
2022062401 | 6 | 0.70452 | 56361.6 | 0.53385 | 19218.6 | 0 | 0 | 1 | 5000 | 19218.6 | 0 | 0 | 0 | 0 | 0 | 32143 | 0 | 0 | 0 | 0 | 0 | 32143
2022062402 | 6 | 0.66827 | 53461.6 | 0.55622 | 20023.92 | 0 | 0 | 1 | 5000 | 20023.92 | 0 | 0 | 0 | 0 | 0 | 28437.68 | 0 | 0 | 0 | 0 | 0 | 28437.68
2022062403 | 6 | 0.63477 | 50781.6 | 0.55103 | 19837.08 | 0 | 0 | 1 | 5000 | 19837.08 | 0 | 0 | 0 | 0 | 0 | 25944.52 | 0 | 0 | 0 | 0 | 0 | 25944.52
2022062404 | 6 | 0.61242 | 48993.6 | 0.53266 | 19175.76 | 0 | 0 | 1 | 5000 | 19175.76 | 0 | 0 | 0 | 0 | 0 | 24817.84 | 0 | 0 | 0 | 0 | 0 | 24817.84
2022062405 | 6 | 0.60145 | 48116 | 0.52148 | 18773.28 | 0 | 0 | 1 | 5000 | 18773.28 | 0 | 0 | 0 | 0 | 0 | 24342.72 | 0 | 0 | 0 | 0 | 0 | 24342.72
2022062406 | 6 | 0.60426 | 48340.8 | 0.5148 | 18532.8 | 0 | 0 | 1 | 5000 | 18532.8 | 0 | 0 | 0 | 0 | 0 | 24808 | 0 | 0 | 0 | 0 | 0 | 24808
2022062407 | 6 | 0.60742 | 48593.6 | 0.48482 | 17453.52 | 0.00484 | 58.08 | 1 | 5000 | 17453.52 | 58.08 | 0 | 0 | 0 | 0 | 26082 | 0 | 0 | 0 | 0 | 0 | 26082
2022062408 | 6 | 0.62336 | 49868.8 | 0.431 | 15516 | 0.20199 | 2423.88 | 1 | 5000 | 15516 | 2423.88 | 0 | 0 | 0 | 0 | 26928.92 | 0 | 0 | 0 | 0 | 0 | 26928.92
2022062409 | 6 | 0.6653 | 53224 | 0.356 | 12816 | 0.61318 | 7358.16 | 1 | 5000 | 12816 | 7358.16 | 0 | 0 | 0 | 0 | 28049.84 | 0 | 0 | 0 | 0 | 0 | 28049.84
2022062410 | 6 | 0.72063 | 57650.4 | 0.39609 | 14259.24 | 0.7597 | 9116.4 | 1 | 5000 | 14259.24 | 9116.4 | 0 | 0 | 0 | 0 | 29274.76 | 0 | 0 | 0 | 0 | 0 | 29274.76
2022062411 | 6 | 0.78053 | 62442.4 | 0.39142 | 14091.12 | 0.79583 | 9549.96 | 1 | 5000 | 14091.12 | 9549.96 | 0 | 0 | 0 | 0 | 33801.32 | 0 | 0 | 0 | 0 | 0 | 33801.32
2022062412 | 6 | 0.8344 | 66752 | 0.36299 | 13067.64 | 0.79567 | 9548.04 | 1 | 5000 | 13067.64 | 9548.04 | 0 | 0 | 0 | 0 | 39136.32 | 0 | 0 | 0 | 0 | 0 | 39136.32
2022062413 | 6 | 0.88226 | 70580.8 | 0.34874 | 12554.64 | 0.80085 | 9610.2 | 1 | 5000 | 12554.64 | 9610.2 | 0 | 0 | 0 | 0 | 43415.96 | 0 | 0 | 0 | 0 | 0 | 43415.96
2022062414 | 6 | 0.92039 | 73631.2 | 0.30834 | 11100.24 | 0.81681 | 9801.72 | 1 | 5000 | 11100.24 | 9801.72 | 0 | 0 | 0 | 0 | 47729.24 | 0 | 0 | 0 | 0 | 0 | 47729.24
2022062415 | 6 | 0.94649 | 75719.2 | 0.28783 | 10361.88 | 0.80863 | 9703.56 | 1 | 5000 | 10361.88 | 9703.56 | 0 | 0 | 0 | 0 | 50653.76 | 0 | 0 | 0 | 0 | 0 | 50653.76
2022062416 | 6 | 0.95324 | 76259.2 | 0.28128 | 10126.08 | 0.78622 | 9434.64 | 1 | 5000 | 10126.08 | 9434.64 | 0 | 0 | 0 | 0 | 51698.48 | 0 | 0 | 0 | 0 | 0 | 51698.48
2022062417 | 6 | 0.95648 | 76518.4 | 0.27735 | 9984.6 | 0.77162 | 9259.44 | 1 | 5000 | 9984.6 | 9259.44 | 0 | 0 | 0 | 0 | 52274.36 | 0 | 0 | 0 | 0 | 0 | 52274.36
2022062418 | 6 | 0.9557 | 76456 | 0.29106 | 10478.16 | 0.73083 | 8769.96 | 1 | 5000 | 10478.16 | 8769.96 | 0 | 0 | 0 | 0 | 52207.88 | 0 | 0 | 0 | 0 | 0 | 52207.88
2022062419 | 6 | 0.94869 | 75895.2 | 0.32159 | 11577.24 | 0.64173 | 7700.76 | 1 | 5000 | 11577.24 | 7700.76 | 0 | 0 | 0 | 0 | 51617.2 | 0 | 0 | 0 | 0 | 0 | 51617.2
2022062420 | 6 | 0.92356 | 73884.8 | 0.35083 | 12629.88 | 0.3675 | 4410 | 1 | 5000 | 12629.88 | 4410 | 0 | 0 | 0 | 0 | 51844.92 | 0 | 0 | 0 | 0 | 0 | 51844.92
2022062421 | 6 | 0.88433 | 70746.4 | 0.37372 | 13453.92 | 0.04818 | 578.16 | 1 | 5000 | 13453.92 | 578.16 | 0 | 0 | 0 | 0 | 51714.32 | 0 | 0 | 0 | 0 | 0 | 51714.32
2022062422 | 6 | 0.85167 | 68133.6 | 0.44493 | 16017.48 | 0 | 0 | 1 | 5000 | 16017.48 | 0 | 0 | 0 | 0 | 0 | 47116.12 | 0 | 0 | 0 | 0 | 0 | 47116.12
2022062423 | 6 | 0.80304 | 64243.2 | 0.53719 | 19338.84 | 0 | 0 | 1 | 5000 | 19338.84 | 0 | 0 | 0 | 0 | 0 | 39904.36 | 0 | 0 | 0 | 0 | 0 | 39904.36
2022062424 | 6 | 0.75308 | 60246.4 | 0.59724 | 21500.64 | 0 | 0 | 1 | 5000 | 21500.64 | 0 | 0 | 0 | 0 | 0 | 33745.76 | 0 | 0 | 0 | 0 | 0 | 33745.76
2022062501 | 7 | 0.70418 | 56334.4 | 0.63081 | 22709.16 | 6e-05 | 0.72 | 1 | 5000 | 22709.16 | 0.72 | 0 | 0 | 0 | 0 | 28624.52 | 0 | 0 | 0 | 0 | 0 | 28624.52
2022062502 | 7 | 0.66449 | 53159.2 | 0.61776 | 22239.36 | 5e-05 | 0.6 | 1 | 5000 | 22239.36 | 0.6 | 0 | 0 | 0 | 0 | 25919.24 | 0 | 0 | 0 | 0 | 0 | 25919.24
2022062503 | 7 | 0.63183 | 50546.4 | 0.59452 | 21402.72 | 0 | 0 | 1 | 5000 | 21402.72 | 0 | 0 | 0 | 0 | 0 | 24143.68 | 0 | 0 | 0 | 0 | 0 | 24143.68
2022062504 | 7 | 0.60838 | 48670.4 | 0.56691 | 20408.76 | 0 | 0 | 1 | 5000 | 20408.76 | 0 | 0 | 0 | 0 | 0 | 23261.64 | 0 | 0 | 0 | 0 | 0 | 23261.64
2022062505 | 7 | 0.59214 | 47371.2 | 0.55599 | 20015.64 | 0 | 0 | 1 | 5000 | 20015.64 | 0 | 0 | 0 | 0 | 0 | 22355.56 | 0 | 0 | 0 | 0 | 0 | 22355.56
2022062506 | 7 | 0.58432 | 46745.6 | 0.54935 | 19776.6 | 0 | 0 | 1 | 5000 | 19776.6 | 0 | 0 | 0 | 0 | 0 | 21969 | 0 | 0 | 0 | 0 | 0 | 21969
2022062507 | 7 | 0.57416 | 45932.8 | 0.50735 | 18264.6 | 0.00523 | 62.76 | 1 | 5000 | 18264.6 | 62.76 | 0 | 0 | 0 | 0 | 22605.44 | 0 | 0 | 0 | 0 | 0 | 22605.44
2022062508 | 7 | 0.58428 | 46742.4 | 0.42944 | 15459.84 | 0.21675 | 2601 | 1 | 5000 | 15459.84 | 2601 | 0 | 0 | 0 | 0 | 23681.56 | 0 | 0 | 0 | 0 | 0 | 23681.56
2022062509 | 7 | 0.62667 | 50133.6 | 0.36072 | 12985.92 | 0.6315 | 7578 | 1 | 5000 | 12985.92 | 7578 | 0 | 0 | 0 | 0 | 24569.68 | 0 | 0 | 0 | 0 | 0 | 24569.68
2022062510 | 7 | 0.68205 | 54564 | 0.40255 | 14491.8 | 0.77262 | 9271.44 | 1 | 5000 | 14491.8 | 9271.44 | 0 | 0 | 0 | 0 | 25800.76 | 0 | 0 | 0 | 0 | 0 | 25800.76
2022062511 | 7 | 0.7369 | 58952 | 0.34621 | 12463.56 | 0.82499 | 9899.88 | 1 | 5000 | 12463.56 | 9899.88 | 0 | 0 | 0 | 0 | 31588.56 | 0 | 0 | 0 | 0 | 0 | 31588.56
2022062512 | 7 | 0.78795 | 63036 | 0.24672 | 8881.92 | 0.83716 | 10045.92 | 1 | 5000 | 8881.92 | 10045.92 | 0 | 0 | 0 | 0 | 39108.16 | 0 | 0 | 0 | 0 | 0 | 39108.16
2022062513 | 7 | 0.83162 | 66529.6 | 0.18867 | 6792.12 | 0.82965 | 9955.8 | 1 | 5000 | 6792.12 | 9955.8 | 0 | 0 | 0 | 0 | 44781.68 | 0 | 0 | 0 | 0 | 0 | 44781.68
2022062514 | 7 | 0.86781 | 69424.8 | 0.18335 | 6600.6 | 0.82047 | 9845.64 | 1 | 5000 | 6600.6 | 9845.64 | 0 | 0 | 0 | 0 | 47978.56 | 0 | 0 | 0 | 0 | 0 | 47978.56
2022062515 | 7 | 0.89793 | 71834.4 | 0.19242 | 6927.12 | 0.7956 | 9547.2 | 1 | 5000 | 6927.12 | 9547.2 | 0 | 0 | 0 | 0 | 50360.08 | 0 | 0 | 0 | 0 | 0 | 50360.08
2022062516 | 7 | 0.91988 | 73590.4 | 0.20358 | 7328.88 | 0.79607 | 9552.84 | 1 | 5000 | 7328.88 | 9552.84 | 0 | 0 | 0 | 0 | 51708.68 | 0 | 0 | 0 | 0 | 0 | 51708.68
2022062517 | 7 | 0.93447 | 74757.6 | 0.2299 | 8276.4 | 0.77837 | 9340.44 | 1 | 5000 | 8276.4 | 9340.44 | 0 | 0 | 0 | 0 | 52140.76 | 0 | 0 | 0 | 0 | 0 | 52140.76
2022062518 | 7 | 0.93907 | 75125.6 | 0.26757 | 9632.52 | 0.76002 | 9120.24 | 1 | 5000 | 9632.52 | 9120.24 | 0 | 0 | 0 | 0 | 51372.84 | 0 | 0 | 0 | 0 | 0 | 51372.84
2022062519 | 7 | 0.92472 | 73977.6 | 0.29724 | 10700.64 | 0.67184 | 8062.08 | 1 | 5000 | 10700.64 | 8062.08 | 0 | 0 | 0 | 0 | 50214.88 | 0 | 0 | 0 | 0 | 0 | 50214.88
2022062520 | 7 | 0.89531 | 71624.8 | 0.32481 | 11693.16 | 0.39464 | 4735.68 | 1 | 5000 | 11693.16 | 4735.68 | 0 | 0 | 0 | 0 | 50195.96 | 0 | 0 | 0 | 0 | 0 | 50195.96
2022062521 | 7 | 0.85396 | 68316.8 | 0.35163 | 12658.68 | 0.04634 | 556.08 | 1 | 5000 | 12658.68 | 556.08 | 0 | 0 | 0 | 0 | 50102.04 | 0 | 0 | 0 | 0 | 0 | 50102.04
2022062522 | 7 | 0.81753 | 65402.4 | 0.39797 | 14326.92 | 0 | 0 | 1 | 5000 | 14326.92 | 0 | 0 | 0 | 0 | 0 | 46075.48 | 0 | 0 | 0 | 0 | 0 | 46075.48
2022062523 | 7 | 0.77271 | 61816.8 | 0.48529 | 17470.44 | 0 | 0 | 1 | 5000 | 17470.44 | 0 | 0 | 0 | 0 | 0 | 39346.36 | 0 | 0 | 0 | 0 | 0 | 39346.36
2022062524 | 7 | 0.725 | 58000 | 0.53877 | 19395.72 | 0 | 0 | 1 | 5000 | 19395.72 | 0 | 0 | 0 | 0 | 0 | 33604.28 | 0 | 0 | 0 | 0 | 0 | 33604.28
2022062601 | 1 | 0.67798 | 54238.4 | 0.5394 | 19418.4 | 0 | 0 | 1 | 5000 | 19418.4 | 0 | 0 | 0 | 0 | 0 | 29820 | 0 | 0 | 0 | 0 | 0 | 29820
2022062602 | 1 | 0.63814 | 51051.2 | 0.52114 | 18761.04 | 0 | 0 | 1 | 5000 | 18761.04 | 0 | 0 | 0 | 0 | 0 | 27290.16 | 0 | 0 | 0 | 0 | 0 | 27290.16
2022062603 | 1 | 0.60753 | 48602.4 | 0.48561 | 17481.96 | 0 | 0 | 1 | 5000 | 17481.96 | 0 | 0 | 0 | 0 | 0 | 26120.44 | 0 | 0 | 0 | 0 | 0 | 26120.44
2022062604 | 1 | 0.58413 | 46730.4 | 0.44955 | 16183.8 | 0 | 0 | 1 | 5000 | 16183.8 | 0 | 0 | 0 | 0 | 0 | 25546.6 | 0 | 0 | 0 | 0 | 0 | 25546.6
2022062605 | 1 | 0.56922 | 45537.6 | 0.41512 | 14944.32 | 0 | 0 | 1 | 5000 | 14944.32 | 0 | 0 | 0 | 0 | 0 | 25593.28 | 0 | 0 | 0 | 0 | 0 | 25593.28
2022062606 | 1 | 0.55518 | 44414.4 | 0.34601 | 12456.36 | 0 | 0 | 1 | 5000 | 12456.36 | 0 | 0 | 0 | 0 | 0 | 26958.04 | 0 | 0 | 0 | 0 | 0 | 26958.04
2022062607 | 1 | 0.54338 | 43470.4 | 0.28412 | 10228.32 | 0.0054 | 64.8 | 1 | 5000 | 10228.32 | 64.8 | 0 | 0 | 0 | 0 | 28177.28 | 0 | 0 | 0 | 0 | 0 | 28177.28
2022062608 | 1 | 0.55489 | 44391.2 | 0.23892 | 8601.12 | 0.19029 | 2283.48 | 1 | 5000 | 8601.12 | 2283.48 | 0 | 0 | 0 | 0 | 28506.6 | 0 | 0 | 0 | 0 | 0 | 28506.6
2022062609 | 1 | 0.59902 | 47921.6 | 0.25344 | 9123.84 | 0.57444 | 6893.28 | 1 | 5000 | 9123.84 | 6893.28 | 0 | 0 | 0 | 0 | 26904.48 | 0 | 0 | 0 | 0 | 0 | 26904.48
2022062610 | 1 | 0.6553 | 52424 | 0.26976 | 9711.36 | 0.75752 | 9090.24 | 1 | 5000 | 9711.36 | 9090.24 | 0 | 0 | 0 | 0 | 28622.4 | 0 | 0 | 0 | 0 | 0 | 28622.4
2022062611 | 1 | 0.71216 | 56972.8 | 0.24592 | 8853.12 | 0.81224 | 9746.88 | 1 | 5000 | 8853.12 | 9746.88 | 0 | 0 | 0 | 0 | 33372.8 | 0 | 0 | 0 | 0 | 0 | 33372.8
2022062612 | 1 | 0.77064 | 61651.2 | 0.22515 | 8105.4 | 0.81578 | 9789.36 | 1 | 5000 | 8105.4 | 9789.36 | 0 | 0 | 0 | 0 | 38756.44 | 0 | 0 | 0 | 0 | 0 | 38756.44
2022062613 | 1 | 0.82229 | 65783.2 | 0.23213 | 8356.68 | 0.80104 | 9612.48 | 1 | 5000 | 8356.68 | 9612.48 | 0 | 0 | 0 | 0 | 42814.04 | 0 | 0 | 0 | 0 | 0 | 42814.04
2022062614 | 1 | 0.86701 | 69360.8 | 0.25944 | 9339.84 | 0.76711 | 9205.32 | 1 | 5000 | 9339.84 | 9205.32 | 0 | 0 | 0 | 0 | 45815.64 | 0 | 0 | 0 | 0 | 0 | 45815.64
2022062615 | 1 | 0.89981 | 71984.8 | 0.28323 | 10196.28 | 0.73994 | 8879.28 | 1 | 5000 | 10196.28 | 8879.28 | 0 | 0 | 0 | 0 | 47909.24 | 0 | 0 | 0 | 0 | 0 | 47909.24
2022062616 | 1 | 0.92451 | 73960.8 | 0.31994 | 11517.84 | 0.69601 | 8352.12 | 1 | 5000 | 11517.84 | 8352.12 | 0 | 0 | 0 | 0 | 49090.84 | 0 | 0 | 0 | 0 | 0 | 49090.84
2022062617 | 1 | 0.94036 | 75228.8 | 0.35573 | 12806.28 | 0.68556 | 8226.72 | 1 | 5000 | 12806.28 | 8226.72 | 0 | 0 | 0 | 0 | 49195.8 | 0 | 0 | 0 | 0 | 0 | 49195.8
2022062618 | 1 | 0.94429 | 75543.2 | 0.39627 | 14265.72 | 0.66336 | 7960.32 | 1 | 5000 | 14265.72 | 7960.32 | 0 | 0 | 0 | 0 | 48317.16 | 0 | 0 | 0 | 0 | 0 | 48317.16
2022062619 | 1 | 0.93267 | 74613.6 | 0.43778 | 15760.08 | 0.583 | 6996 | 1 | 5000 | 15760.08 | 6996 | 0 | 0 | 0 | 0 | 46857.52 | 0 | 0 | 0 | 0 | 0 | 46857.52
2022062620 | 1 | 0.90383 | 72306.4 | 0.48489 | 17456.04 | 0.32856 | 3942.72 | 1 | 5000 | 17456.04 | 3942.72 | 0 | 0 | 0 | 0 | 45907.64 | 0 | 0 | 0 | 0 | 0 | 45907.64
2022062621 | 1 | 0.86469 | 69175.2 | 0.48415 | 17429.4 | 0.03395 | 407.4 | 1 | 5000 | 17429.4 | 407.4 | 0 | 0 | 0 | 0 | 46338.4 | 0 | 0 | 0 | 0 | 0 | 46338.4
2022062622 | 1 | 0.83513 | 66810.4 | 0.45866 | 16511.76 | 0 | 0 | 1 | 5000 | 16511.76 | 0 | 0 | 0 | 0 | 0 | 45298.64 | 0 | 0 | 0 | 0 | 0 | 45298.64
2022062623 | 1 | 0.78505 | 62804 | 0.45849 | 16505.64 | 0 | 0 | 1 | 5000 | 16505.64 | 0 | 0 | 0 | 0 | 0 | 41298.36 | 0 | 0 | 0 | 0 | 0 | 41298.36
2022062624 | 1 | 0.73007 | 58405.6 | 0.45644 | 16431.84 | 0 | 0 | 1 | 5000 | 16431.84 | 0 | 0 | 0 | 0 | 0 | 36973.76 | 0 | 0 | 0 | 0 | 0 | 36973.76
2022062701 | 2 | 0.67919 | 54335.2 | 0.45487 | 16375.32 | 0 | 0 | 1 | 5000 | 16375.32 | 0 | 0 | 0 | 0 | 0 | 32959.88 | 0 | 0 | 0 | 0 | 0 | 32959.88
2022062702 | 2 | 0.63941 | 51152.8 | 0.40944 | 14739.84 | 0 | 0 | 1 | 5000 | 14739.84 | 0 | 0 | 0 | 0 | 0 | 31412.96 | 0 | 0 | 0 | 0 | 0 | 31412.96
2022062703 | 2 | 0.60822 | 48657.6 | 0.35465 | 12767.4 | 0 | 0 | 1 | 5000 | 12767.4 | 0 | 0 | 0 | 0 | 0 | 30890.2 | 0 | 0 | 0 | 0 | 0 | 30890.2
2022062704 | 2 | 0.5854 | 46832 | 0.30836 | 11100.96 | 0 | 0 | 1 | 5000 | 11100.96 | 0 | 0 | 0 | 0 | 0 | 30731.04 | 0 | 0 | 0 | 0 | 0 | 30731.04
2022062705 | 2 | 0.57768 | 46214.4 | 0.28794 | 10365.84 | 0 | 0 | 1 | 5000 | 10365.84 | 0 | 0 | 0 | 0 | 0 | 30848.56 | 0 | 0 | 0 | 0 | 0 | 30848.56
2022062706 | 2 | 0.58179 | 46543.2 | 0.29249 | 10529.64 | 0 | 0 | 1 | 5000 | 10529.64 | 0 | 0 | 0 | 0 | 0 | 31013.56 | 0 | 0 | 0 | 0 | 0 | 31013.56
2022062707 | 2 | 0.59178 | 47342.4 | 0.27592 | 9933.12 | 0.00391 | 46.92 | 1 | 5000 | 9933.12 | 46.92 | 0 | 0 | 0 | 0 | 32362.36 | 0 | 0 | 0 | 0 | 0 | 32362.36
2022062708 | 2 | 0.60036 | 48028.8 | 0.21802 | 7848.72 | 0.12966 | 1555.92 | 1 | 5000 | 7848.72 | 1555.92 | 0 | 0 | 0 | 0 | 33624.16 | 0 | 0 | 0 | 0 | 0 | 33624.16
2022062709 | 2 | 0.62922 | 50337.6 | 0.17285 | 6222.6 | 0.40943 | 4913.16 | 1 | 5000 | 6222.6 | 4913.16 | 0 | 0 | 0 | 0 | 34201.84 | 0 | 0 | 0 | 0 | 0 | 34201.84
2022062710 | 2 | 0.67357 | 53885.6 | 0.1434 | 5162.4 | 0.61821 | 7418.52 | 1 | 5000 | 5162.4 | 7418.52 | 0 | 0 | 0 | 0 | 36304.68 | 0 | 0 | 0 | 0 | 0 | 36304.68
2022062711 | 2 | 0.72778 | 58222.4 | 0.11828 | 4258.08 | 0.73153 | 8778.36 | 1 | 5000 | 4258.08 | 8778.36 | 0 | 0 | 0 | 0 | 40185.96 | 0 | 0 | 0 | 0 | 0 | 40185.96
2022062712 | 2 | 0.78051 | 62440.8 | 0.08448 | 3041.28 | 0.7979 | 9574.8 | 1 | 5000 | 3041.28 | 9574.8 | 0 | 0 | 0 | 0 | 44824.72 | 0 | 0 | 0 | 0 | 0 | 44824.72
2022062713 | 2 | 0.83192 | 66553.6 | 0.07989 | 2876.04 | 0.82069 | 9848.28 | 1 | 5000 | 2876.04 | 9848.28 | 0 | 0 | 0 | 0 | 48829.28 | 0 | 0 | 0 | 0 | 0 | 48829.28
2022062714 | 2 | 0.87722 | 70177.6 | 0.08639 | 3110.04 | 0.80756 | 9690.72 | 1 | 5000 | 3110.04 | 9690.72 | 0 | 0 | 0 | 0 | 52376.84 | 0 | 0 | 0 | 0 | 0 | 52376.84
2022062715 | 2 | 0.90202 | 72161.6 | 0.10592 | 3813.12 | 0.74013 | 8881.56 | 1 | 5000 | 3813.12 | 8881.56 | 0 | 0 | 0 | 0 | 54466.92 | 0 | 0 | 0 | 0 | 0 | 54466.92
2022062716 | 2 | 0.89582 | 71665.6 | 0.14093 | 5073.48 | 0.67654 | 8118.48 | 1 | 5000 | 5073.48 | 8118.48 | 0 | 0 | 0 | 0 | 53473.64 | 0 | 0 | 0 | 0 | 0 | 53473.64
2022062717 | 2 | 0.87923 | 70338.4 | 0.17553 | 6319.08 | 0.63329 | 7599.48 | 1 | 5000 | 6319.08 | 7599.48 | 0 | 0 | 0 | 0 | 51419.84 | 0 | 0 | 0 | 0 | 0 | 51419.84
2022062718 | 2 | 0.8579 | 68632 | 0.23164 | 8339.04 | 0.57657 | 6918.84 | 1 | 5000 | 8339.04 | 6918.84 | 0 | 0 | 0 | 0 | 48374.12 | 0 | 0 | 0 | 0 | 0 | 48374.12
2022062719 | 2 | 0.82928 | 66342.4 | 0.28158 | 10136.88 | 0.45996 | 5519.52 | 1 | 5000 | 10136.88 | 5519.52 | 0 | 0 | 0 | 0 | 45686 | 0 | 0 | 0 | 0 | 0 | 45686
2022062720 | 2 | 0.79552 | 63641.6 | 0.30993 | 11157.48 | 0.23605 | 2832.6 | 1 | 5000 | 11157.48 | 2832.6 | 0 | 0 | 0 | 0 | 44651.52 | 0 | 0 | 0 | 0 | 0 | 44651.52
2022062721 | 2 | 0.76807 | 61445.6 | 0.30999 | 11159.64 | 0.03165 | 379.8 | 1 | 5000 | 11159.64 | 379.8 | 0 | 0 | 0 | 0 | 44906.16 | 0 | 0 | 0 | 0 | 0 | 44906.16
2022062722 | 2 | 0.74171 | 59336.8 | 0.29253 | 10531.08 | 0 | 0 | 1 | 5000 | 10531.08 | 0 | 0 | 0 | 0 | 0 | 43805.72 | 0 | 0 | 0 | 0 | 0 | 43805.72
2022062723 | 2 | 0.69659 | 55727.2 | 0.29966 | 10787.76 | 0 | 0 | 1 | 5000 | 10787.76 | 0 | 0 | 0 | 0 | 0 | 39939.44 | 0 | 0 | 0 | 0 | 0 | 39939.44
2022062724 | 2 | 0.64892 | 51913.6 | 0.25828 | 9298.08 | 0 | 0 | 1 | 5000 | 9298.08 | 0 | 0 | 0 | 0 | 0 | 37615.52 | 0 | 0 | 0 | 0 | 0 | 37615.52
2022062801 | 3 | 0.60889 | 48711.2 | 0.21778 | 7840.08 | 0 | 0 | 1 | 5000 | 7840.08 | 0 | 0 | 0 | 0 | 0 | 35871.12 | 0 | 0 | 0 | 0 | 0 | 35871.12
2022062802 | 3 | 0.57728 | 46182.4 | 0.18502 | 6660.72 | 0 | 0 | 1 | 5000 | 6660.72 | 0 | 0 | 0 | 0 | 0 | 34521.68 | 0 | 0 | 0 | 0 | 0 | 34521.68
2022062803 | 3 | 0.55947 | 44757.6 | 0.16333 | 5879.88 | 0 | 0 | 1 | 5000 | 5879.88 | 0 | 0 | 0 | 0 | 0 | 33877.72 | 0 | 0 | 0 | 0 | 0 | 33877.72
2022062804 | 3 | 0.54436 | 43548.8 | 0.1287 | 4633.2 | 0 | 0 | 1 | 5000 | 4633.2 | 0 | 0 | 0 | 0 | 0 | 33915.6 | 0 | 0 | 0 | 0 | 0 | 33915.6
2022062805 | 3 | 0.54095 | 43276 | 0.1022 | 3679.2 | 0 | 0 | 1 | 5000 | 3679.2 | 0 | 0 | 0 | 0 | 0 | 34596.8 | 0 | 0 | 0 | 0 | 0 | 34596.8
2022062806 | 3 | 0.55083 | 44066.4 | 0.08772 | 3157.92 | 0 | 0 | 1 | 5000 | 3157.92 | 0 | 0 | 0 | 0 | 0 | 35908.48 | 0 | 0 | 0 | 0 | 0 | 35908.48
2022062807 | 3 | 0.56532 | 45225.6 | 0.09 | 3240 | 0.00407 | 48.84 | 1 | 5000 | 3240 | 48.84 | 0 | 0 | 0 | 0 | 36936.76 | 0 | 0 | 0 | 0 | 0 | 36936.76
2022062808 | 3 | 0.58038 | 46430.4 | 0.09155 | 3295.8 | 0.13977 | 1677.24 | 1 | 5000 | 3295.8 | 1677.24 | 0 | 0 | 0 | 0 | 36457.36 | 0 | 0 | 0 | 0 | 0 | 36457.36
2022062809 | 3 | 0.60578 | 48462.4 | 0.0782 | 2815.2 | 0.46617 | 5594.04 | 1 | 5000 | 2815.2 | 5594.04 | 0 | 0 | 0 | 0 | 35053.16 | 0 | 0 | 0 | 0 | 0 | 35053.16
2022062810 | 3 | 0.63992 | 51193.6 | 0.07048 | 2537.28 | 0.66456 | 7974.72 | 1 | 5000 | 2537.28 | 7974.72 | 0 | 0 | 0 | 0 | 35681.6 | 0 | 0 | 0 | 0 | 0 | 35681.6
2022062811 | 3 | 0.6807 | 54456 | 0.05625 | 2025 | 0.75683 | 9081.96 | 1 | 5000 | 2025 | 9081.96 | 0 | 0 | 0 | 0 | 38349.04 | 0 | 0 | 0 | 0 | 0 | 38349.04
2022062812 | 3 | 0.7224 | 57792 | 0.05195 | 1870.2 | 0.76237 | 9148.44 | 1 | 5000 | 1870.2 | 9148.44 | 0 | 0 | 0 | 0 | 41773.36 | 0 | 0 | 0 | 0 | 0 | 41773.36
2022062813 | 3 | 0.76371 | 61096.8 | 0.05806 | 2090.16 | 0.74336 | 8920.32 | 1 | 5000 | 2090.16 | 8920.32 | 0 | 0 | 0 | 0 | 45086.32 | 0 | 0 | 0 | 0 | 0 | 45086.32
2022062814 | 3 | 0.79633 | 63706.4 | 0.0802 | 2887.2 | 0.72071 | 8648.52 | 1 | 5000 | 2887.2 | 8648.52 | 0 | 0 | 0 | 0 | 47170.68 | 0 | 0 | 0 | 0 | 0 | 47170.68
2022062815 | 3 | 0.82061 | 65648.8 | 0.11907 | 4286.52 | 0.68949 | 8273.88 | 1 | 5000 | 4286.52 | 8273.88 | 0 | 0 | 0 | 0 | 48088.4 | 0 | 0 | 0 | 0 | 0 | 48088.4
2022062816 | 3 | 0.83115 | 66492 | 0.15904 | 5725.44 | 0.66399 | 7967.88 | 1 | 5000 | 5725.44 | 7967.88 | 0 | 0 | 0 | 0 | 47798.68 | 0 | 0 | 0 | 0 | 0 | 47798.68
2022062817 | 3 | 0.8343 | 66744 | 0.18352 | 6606.72 | 0.66065 | 7927.8 | 1 | 5000 | 6606.72 | 7927.8 | 0 | 0 | 0 | 0 | 47209.48 | 0 | 0 | 0 | 0 | 0 | 47209.48
2022062818 | 3 | 0.82515 | 66012 | 0.23499 | 8459.64 | 0.53388 | 6406.56 | 1 | 5000 | 8459.64 | 6406.56 | 0 | 0 | 0 | 0 | 46145.8 | 0 | 0 | 0 | 0 | 0 | 46145.8
2022062819 | 3 | 0.80866 | 64692.8 | 0.2667 | 9601.2 | 0.42578 | 5109.36 | 1 | 5000 | 9601.2 | 5109.36 | 0 | 0 | 0 | 0 | 44982.24 | 0 | 0 | 0 | 0 | 0 | 44982.24
2022062820 | 3 | 0.78102 | 62481.6 | 0.2792 | 10051.2 | 0.21693 | 2603.16 | 1 | 5000 | 10051.2 | 2603.16 | 0 | 0 | 0 | 0 | 44827.24 | 0 | 0 | 0 | 0 | 0 | 44827.24
2022062821 | 3 | 0.74696 | 59756.8 | 0.26213 | 9436.68 | 0.01978 | 237.36 | 1 | 5000 | 9436.68 | 237.36 | 0 | 0 | 0 | 0 | 45082.76 | 0 | 0 | 0 | 0 | 0 | 45082.76
2022062822 | 3 | 0.72103 | 57682.4 | 0.25873 | 9314.28 | 0 | 0 | 1 | 5000 | 9314.28 | 0 | 0 | 0 | 0 | 0 | 43368.12 | 0 | 0 | 0 | 0 | 0 | 43368.12
2022062823 | 3 | 0.67554 | 54043.2 | 0.23867 | 8592.12 | 0 | 0 | 1 | 5000 | 8592.12 | 0 | 0 | 0 | 0 | 0 | 40451.08 | 0 | 0 | 0 | 0 | 0 | 40451.08
2022062824 | 3 | 0.62648 | 50118.4 | 0.20628 | 7426.08 | 0 | 0 | 1 | 5000 | 7426.08 | 0 | 0 | 0 | 0 | 0 | 37692.32 | 0 | 0 | 0 | 0 | 0 | 37692.32
2022062901 | 4 | 0.58553 | 46842.4 | 0.16331 | 5879.16 | 0 | 0 | 1 | 5000 | 5879.16 | 0 | 0 | 0 | 0 | 0 | 35963.24 | 0 | 0 | 0 | 0 | 0 | 35963.24
2022062902 | 4 | 0.55572 | 44457.6 | 0.12577 | 4527.72 | 0 | 0 | 1 | 5000 | 4527.72 | 0 | 0 | 0 | 0 | 0 | 34929.88 | 0 | 0 | 0 | 0 | 0 | 34929.88
2022062903 | 4 | 0.53355 | 42684 | 0.10552 | 3798.72 | 0 | 0 | 1 | 5000 | 3798.72 | 0 | 0 | 0 | 0 | 0 | 33885.28 | 0 | 0 | 0 | 0 | 0 | 33885.28
2022062904 | 4 | 0.52008 | 41606.4 | 0.09865 | 3551.4 | 0 | 0 | 1 | 5000 | 3551.4 | 0 | 0 | 0 | 0 | 0 | 33055 | 0 | 0 | 0 | 0 | 0 | 33055
2022062905 | 4 | 0.5175 | 41400 | 0.09118 | 3282.48 | 0 | 0 | 1 | 5000 | 3282.48 | 0 | 0 | 0 | 0 | 0 | 33117.52 | 0 | 0 | 0 | 0 | 0 | 33117.52
2022062906 | 4 | 0.52703 | 42162.4 | 0.08448 | 3041.28 | 0 | 0 | 1 | 5000 | 3041.28 | 0 | 0 | 0 | 0 | 0 | 34121.12 | 0 | 0 | 0 | 0 | 0 | 34121.12
2022062907 | 4 | 0.54248 | 43398.4 | 0.08124 | 2924.64 | 0.00411 | 49.32 | 1 | 5000 | 2924.64 | 49.32 | 0 | 0 | 0 | 0 | 35424.44 | 0 | 0 | 0 | 0 | 0 | 35424.44
2022062908 | 4 | 0.5558 | 44464 | 0.07772 | 2797.92 | 0.12791 | 1534.92 | 1 | 5000 | 2797.92 | 1534.92 | 0 | 0 | 0 | 0 | 35131.16 | 0 | 0 | 0 | 0 | 0 | 35131.16
2022062909 | 4 | 0.58452 | 46761.6 | 0.05031 | 1811.16 | 0.47068 | 5648.16 | 1 | 5000 | 1811.16 | 5648.16 | 0 | 0 | 0 | 0 | 34302.28 | 0 | 0 | 0 | 0 | 0 | 34302.28
2022062910 | 4 | 0.62924 | 50339.2 | 0.05201 | 1872.36 | 0.65005 | 7800.6 | 1 | 5000 | 1872.36 | 7800.6 | 0 | 0 | 0 | 0 | 35666.24 | 0 | 0 | 0 | 0 | 0 | 35666.24
2022062911 | 4 | 0.6775 | 54200 | 0.06218 | 2238.48 | 0.72216 | 8665.92 | 1 | 5000 | 2238.48 | 8665.92 | 0 | 0 | 0 | 0 | 38295.6 | 0 | 0 | 0 | 0 | 0 | 38295.6
2022062912 | 4 | 0.72716 | 58172.8 | 0.05401 | 1944.36 | 0.77458 | 9294.96 | 1 | 5000 | 1944.36 | 9294.96 | 0 | 0 | 0 | 0 | 41933.48 | 0 | 0 | 0 | 0 | 0 | 41933.48
2022062913 | 4 | 0.77326 | 61860.8 | 0.05685 | 2046.6 | 0.78411 | 9409.32 | 1 | 5000 | 2046.6 | 9409.32 | 0 | 0 | 0 | 0 | 45404.88 | 0 | 0 | 0 | 0 | 0 | 45404.88
2022062914 | 4 | 0.81492 | 65193.6 | 0.07577 | 2727.72 | 0.76985 | 9238.2 | 1 | 5000 | 2727.72 | 9238.2 | 0 | 0 | 0 | 0 | 48227.68 | 0 | 0 | 0 | 0 | 0 | 48227.68
2022062915 | 4 | 0.84525 | 67620 | 0.0989 | 3560.4 | 0.75568 | 9068.16 | 1 | 5000 | 3560.4 | 9068.16 | 0 | 0 | 0 | 0 | 49991.44 | 0 | 0 | 0 | 0 | 0 | 49991.44
2022062916 | 4 | 0.86621 | 69296.8 | 0.12782 | 4601.52 | 0.72282 | 8673.84 | 1 | 5000 | 4601.52 | 8673.84 | 0 | 0 | 0 | 0 | 51021.44 | 0 | 0 | 0 | 0 | 0 | 51021.44
2022062917 | 4 | 0.87756 | 70204.8 | 0.14665 | 5279.4 | 0.71786 | 8614.32 | 1 | 5000 | 5279.4 | 8614.32 | 0 | 0 | 0 | 0 | 51311.08 | 0 | 0 | 0 | 0 | 0 | 51311.08
2022062918 | 4 | 0.87605 | 70084 | 0.14615 | 5261.4 | 0.70058 | 8406.96 | 1 | 5000 | 5261.4 | 8406.96 | 0 | 0 | 0 | 0 | 51415.64 | 0 | 0 | 0 | 0 | 0 | 51415.64
2022062919 | 4 | 0.85928 | 68742.4 | 0.14638 | 5269.68 | 0.57742 | 6929.04 | 1 | 5000 | 5269.68 | 6929.04 | 0 | 0 | 0 | 0 | 51543.68 | 0 | 0 | 0 | 0 | 0 | 51543.68
2022062920 | 4 | 0.83069 | 66455.2 | 0.16819 | 6054.84 | 0.32133 | 3855.96 | 1 | 5000 | 6054.84 | 3855.96 | 0 | 0 | 0 | 0 | 51544.4 | 0 | 0 | 0 | 0 | 0 | 51544.4
2022062921 | 4 | 0.79465 | 63572 | 0.18622 | 6703.92 | 0.04596 | 551.52 | 1 | 5000 | 6703.92 | 551.52 | 0 | 0 | 0 | 0 | 51316.56 | 0 | 0 | 0 | 0 | 0 | 51316.56
2022062922 | 4 | 0.76542 | 61233.6 | 0.25627 | 9225.72 | 0 | 0 | 1 | 5000 | 9225.72 | 0 | 0 | 0 | 0 | 0 | 47007.88 | 0 | 0 | 0 | 0 | 0 | 47007.88
2022062923 | 4 | 0.71744 | 57395.2 | 0.33199 | 11951.64 | 0 | 0 | 1 | 5000 | 11951.64 | 0 | 0 | 0 | 0 | 0 | 40443.56 | 0 | 0 | 0 | 0 | 0 | 40443.56
2022062924 | 4 | 0.66681 | 53344.8 | 0.37553 | 13519.08 | 0 | 0 | 1 | 5000 | 13519.08 | 0 | 0 | 0 | 0 | 0 | 34825.72 | 0 | 0 | 0 | 0 | 0 | 34825.72
2022063001 | 5 | 0.62141 | 49712.8 | 0.38326 | 13797.36 | 0 | 0 | 1 | 5000 | 13797.36 | 0 | 0 | 0 | 0 | 0 | 30915.44 | 0 | 0 | 0 | 0 | 0 | 30915.44
2022063002 | 5 | 0.58678 | 46942.4 | 0.39414 | 14189.04 | 0 | 0 | 1 | 5000 | 14189.04 | 0 | 0 | 0 | 0 | 0 | 27753.36 | 0 | 0 | 0 | 0 | 0 | 27753.36
2022063003 | 5 | 0.56481 | 45184.8 | 0.4011 | 14439.6 | 0 | 0 | 1 | 5000 | 14439.6 | 0 | 0 | 0 | 0 | 0 | 25745.2 | 0 | 0 | 0 | 0 | 0 | 25745.2
2022063004 | 5 | 0.54607 | 43685.6 | 0.3847 | 13849.2 | 0 | 0 | 1 | 5000 | 13849.2 | 0 | 0 | 0 | 0 | 0 | 24836.4 | 0 | 0 | 0 | 0 | 0 | 24836.4
2022063005 | 5 | 0.53996 | 43196.8 | 0.37143 | 13371.48 | 0 | 0 | 1 | 5000 | 13371.48 | 0 | 0 | 0 | 0 | 0 | 24825.32 | 0 | 0 | 0 | 0 | 0 | 24825.32
2022063006 | 5 | 0.54633 | 43706.4 | 0.37552 | 13518.72 | 0 | 0 | 1 | 5000 | 13518.72 | 0 | 0 | 0 | 0 | 0 | 25187.68 | 0 | 0 | 0 | 0 | 0 | 25187.68
2022063007 | 5 | 0.55722 | 44577.6 | 0.36842 | 13263.12 | 0.00391 | 46.92 | 1 | 5000 | 13263.12 | 46.92 | 0 | 0 | 0 | 0 | 26267.56 | 0 | 0 | 0 | 0 | 0 | 26267.56
2022063008 | 5 | 0.5756 | 46048 | 0.3221 | 11595.6 | 0.17365 | 2083.8 | 1 | 5000 | 11595.6 | 2083.8 | 0 | 0 | 0 | 0 | 27368.6 | 0 | 0 | 0 | 0 | 0 | 27368.6
2022063009 | 5 | 0.6114 | 48912 | 0.21787 | 7843.32 | 0.56603 | 6792.36 | 1 | 5000 | 7843.32 | 6792.36 | 0 | 0 | 0 | 0 | 29276.32 | 0 | 0 | 0 | 0 | 0 | 29276.32
2022063010 | 5 | 0.6574 | 52592 | 0.22743 | 8187.48 | 0.70272 | 8432.64 | 1 | 5000 | 8187.48 | 8432.64 | 0 | 0 | 0 | 0 | 30971.88 | 0 | 0 | 0 | 0 | 0 | 30971.88
2022063011 | 5 | 0.7045 | 56360 | 0.21974 | 7910.64 | 0.74304 | 8916.48 | 1 | 5000 | 7910.64 | 8916.48 | 0 | 0 | 0 | 0 | 34532.88 | 0 | 0 | 0 | 0 | 0 | 34532.88
2022063012 | 5 | 0.74573 | 59658.4 | 0.14957 | 5384.52 | 0.74266 | 8911.92 | 1 | 5000 | 5384.52 | 8911.92 | 0 | 0 | 0 | 0 | 40361.96 | 0 | 0 | 0 | 0 | 0 | 40361.96
2022063013 | 5 | 0.78594 | 62875.2 | 0.06874 | 2474.64 | 0.71589 | 8590.68 | 1 | 5000 | 2474.64 | 8590.68 | 0 | 0 | 0 | 0 | 46809.88 | 0 | 0 | 0 | 0 | 0 | 46809.88
2022063014 | 5 | 0.81678 | 65342.4 | 0.05388 | 1939.68 | 0.72739 | 8728.68 | 1 | 5000 | 1939.68 | 8728.68 | 0 | 0 | 0 | 0 | 49674.04 | 0 | 0 | 0 | 0 | 0 | 49674.04
2022063015 | 5 | 0.84233 | 67386.4 | 0.07254 | 2611.44 | 0.70929 | 8511.48 | 1 | 5000 | 2611.44 | 8511.48 | 0 | 0 | 0 | 0 | 51263.48 | 0 | 0 | 0 | 0 | 0 | 51263.48
2022063016 | 5 | 0.8609 | 68872 | 0.09851 | 3546.36 | 0.68609 | 8233.08 | 1 | 5000 | 3546.36 | 8233.08 | 0 | 0 | 0 | 0 | 52092.56 | 0 | 0 | 0 | 0 | 0 | 52092.56
2022063017 | 5 | 0.8734 | 69872 | 0.12128 | 4366.08 | 0.69857 | 8382.84 | 1 | 5000 | 4366.08 | 8382.84 | 0 | 0 | 0 | 0 | 52123.08 | 0 | 0 | 0 | 0 | 0 | 52123.08
2022063018 | 5 | 0.87179 | 69743.2 | 0.15296 | 5506.56 | 0.6416 | 7699.2 | 1 | 5000 | 5506.56 | 7699.2 | 0 | 0 | 0 | 0 | 51537.44 | 0 | 0 | 0 | 0 | 0 | 51537.44
2022063019 | 5 | 0.85663 | 68530.4 | 0.17746 | 6388.56 | 0.5738 | 6885.6 | 1 | 5000 | 6388.56 | 6885.6 | 0 | 0 | 0 | 0 | 50256.24 | 0 | 0 | 0 | 0 | 0 | 50256.24
2022063020 | 5 | 0.83351 | 66680.8 | 0.23738 | 8545.68 | 0.31473 | 3776.76 | 1 | 5000 | 8545.68 | 3776.76 | 0 | 0 | 0 | 0 | 49358.36 | 0 | 0 | 0 | 0 | 0 | 49358.36
2022063021 | 5 | 0.80754 | 64603.2 | 0.28777 | 10359.72 | 0.0473 | 567.6 | 1 | 5000 | 10359.72 | 567.6 | 0 | 0 | 0 | 0 | 48675.88 | 0 | 0 | 0 | 0 | 0 | 48675.88
2022063022 | 5 | 0.78596 | 62876.8 | 0.36674 | 13202.64 | 0.00249 | 29.88 | 1 | 5000 | 13202.64 | 29.88 | 0 | 0 | 0 | 0 | 44644.28 | 0 | 0 | 0 | 0 | 0 | 44644.28
2022063023 | 5 | 0.74577 | 59661.6 | 0.44702 | 16092.72 | 0.00115 | 13.8 | 1 | 5000 | 16092.72 | 13.8 | 0 | 0 | 0 | 0 | 38555.08 | 0 | 0 | 0 | 0 | 0 | 38555.08
2022063024 | 5 | 0.69869 | 55895.2 | 0.49255 | 17731.8 | 0 | 0 | 1 | 5000 | 17731.8 | 0 | 0 | 0 | 0 | 0 | 33163.4 | 0 | 0 | 0 | 0 | 0 | 33163.4
2022070101 | 6 | 0.65476 | 52380.8 | 0.50415 | 18149.4 | 0 | 0 | 1 | 5000 | 18149.4 | 0 | 0 | 0 | 0 | 0 | 29231.4 | 0 | 0 | 0 | 0 | 0 | 29231.4
2022070102 | 6 | 0.62047 | 49637.6 | 0.51688 | 18607.68 | 0 | 0 | 1 | 5000 | 18607.68 | 0 | 0 | 0 | 0 | 0 | 26029.92 | 0 | 0 | 0 | 0 | 0 | 26029.92
2022070103 | 6 | 0.5949 | 47592 | 0.50269 | 18096.84 | 0 | 0 | 1 | 5000 | 18096.84 | 0 | 0 | 0 | 0 | 0 | 24495.16 | 0 | 0 | 0 | 0 | 0 | 24495.16
2022070104 | 6 | 0.57765 | 46212 | 0.48146 | 17332.56 | 0 | 0 | 1 | 5000 | 17332.56 | 0 | 0 | 0 | 0 | 0 | 23879.44 | 0 | 0 | 0 | 0 | 0 | 23879.44
2022070105 | 6 | 0.56904 | 45523.2 | 0.44951 | 16182.36 | 0 | 0 | 1 | 5000 | 16182.36 | 0 | 0 | 0 | 0 | 0 | 24340.84 | 0 | 0 | 0 | 0 | 0 | 24340.84
2022070106 | 6 | 0.57409 | 45927.2 | 0.41023 | 14768.28 | 0 | 0 | 1 | 5000 | 14768.28 | 0 | 0 | 0 | 0 | 0 | 26158.92 | 0 | 0 | 0 | 0 | 0 | 26158.92
2022070107 | 6 | 0.57594 | 46075.2 | 0.36903 | 13285.08 | 0.00395 | 47.4 | 1 | 5000 | 13285.08 | 47.4 | 0 | 0 | 0 | 0 | 27742.72 | 0 | 0 | 0 | 0 | 0 | 27742.72
2022070108 | 6 | 0.58696 | 46956.8 | 0.31233 | 11243.88 | 0.17791 | 2134.92 | 1 | 5000 | 11243.88 | 2134.92 | 0 | 0 | 0 | 0 | 28578 | 0 | 0 | 0 | 0 | 0 | 28578
2022070109 | 6 | 0.61743 | 49394.4 | 0.26019 | 9366.84 | 0.51416 | 6169.92 | 1 | 5000 | 9366.84 | 6169.92 | 0 | 0 | 0 | 0 | 28857.64 | 0 | 0 | 0 | 0 | 0 | 28857.64
2022070110 | 6 | 0.65645 | 52516 | 0.27632 | 9947.52 | 0.64751 | 7770.12 | 1 | 5000 | 9947.52 | 7770.12 | 0 | 0 | 0 | 0 | 29798.36 | 0 | 0 | 0 | 0 | 0 | 29798.36
2022070111 | 6 | 0.70092 | 56073.6 | 0.2 | 7200 | 0.69743 | 8369.16 | 1 | 5000 | 7200 | 8369.16 | 0 | 0 | 0 | 0 | 35504.44 | 0 | 0 | 0 | 0 | 0 | 35504.44
2022070112 | 6 | 0.74507 | 59605.6 | 0.11278 | 4060.08 | 0.7154 | 8584.8 | 1 | 5000 | 4060.08 | 8584.8 | 0 | 0 | 0 | 0 | 41960.72 | 0 | 0 | 0 | 0 | 0 | 41960.72
2022070113 | 6 | 0.78553 | 62842.4 | 0.06541 | 2354.76 | 0.69835 | 8380.2 | 1 | 5000 | 2354.76 | 8380.2 | 0 | 0 | 0 | 0 | 47107.44 | 0 | 0 | 0 | 0 | 0 | 47107.44
2022070114 | 6 | 0.82041 | 65632.8 | 0.06976 | 2511.36 | 0.68539 | 8224.68 | 1 | 5000 | 2511.36 | 8224.68 | 0 | 0 | 0 | 0 | 49896.76 | 0 | 0 | 0 | 0 | 0 | 49896.76
2022070115 | 6 | 0.84612 | 67689.6 | 0.10181 | 3665.16 | 0.69423 | 8330.76 | 1 | 5000 | 3665.16 | 8330.76 | 0 | 0 | 0 | 0 | 50693.68 | 0 | 0 | 0 | 0 | 0 | 50693.68
2022070116 | 6 | 0.86349 | 69079.2 | 0.15585 | 5610.6 | 0.69314 | 8317.68 | 1 | 5000 | 5610.6 | 8317.68 | 0 | 0 | 0 | 0 | 50150.92 | 0 | 0 | 0 | 0 | 0 | 50150.92
2022070117 | 6 | 0.87807 | 70245.6 | 0.21169 | 7620.84 | 0.67155 | 8058.6 | 1 | 5000 | 7620.84 | 8058.6 | 0 | 0 | 0 | 0 | 49566.16 | 0 | 0 | 0 | 0 | 0 | 49566.16
2022070118 | 6 | 0.88291 | 70632.8 | 0.22724 | 8180.64 | 0.62427 | 7491.24 | 1 | 5000 | 8180.64 | 7491.24 | 0 | 0 | 0 | 0 | 49960.92 | 0 | 0 | 0 | 0 | 0 | 49960.92
2022070119 | 6 | 0.87101 | 69680.8 | 0.27997 | 10078.92 | 0.57688 | 6922.56 | 1 | 5000 | 10078.92 | 6922.56 | 0 | 0 | 0 | 0 | 47679.32 | 0 | 0 | 0 | 0 | 0 | 47679.32
2022070120 | 6 | 0.84695 | 67756 | 0.35975 | 12951 | 0.34503 | 4140.36 | 1 | 5000 | 12951 | 4140.36 | 0 | 0 | 0 | 0 | 45664.64 | 0 | 0 | 0 | 0 | 0 | 45664.64
2022070121 | 6 | 0.81584 | 65267.2 | 0.40775 | 14679 | 0.04942 | 593.04 | 1 | 5000 | 14679 | 593.04 | 0 | 0 | 0 | 0 | 44995.16 | 0 | 0 | 0 | 0 | 0 | 44995.16
2022070122 | 6 | 0.79021 | 63216.8 | 0.45173 | 16262.28 | 0 | 0 | 1 | 5000 | 16262.28 | 0 | 0 | 0 | 0 | 0 | 41954.52 | 0 | 0 | 0 | 0 | 0 | 41954.52
2022070123 | 6 | 0.74942 | 59953.6 | 0.50164 | 18059.04 | 0 | 0 | 1 | 5000 | 18059.04 | 0 | 0 | 0 | 0 | 0 | 36894.56 | 0 | 0 | 0 | 0 | 0 | 36894.56
2022070124 | 6 | 0.70637 | 56509.6 | 0.51551 | 18558.36 | 0 | 0 | 1 | 5000 | 18558.36 | 0 | 0 | 0 | 0 | 0 | 32951.24 | 0 | 0 | 0 | 0 | 0 | 32951.24
2022070201 | 7 | 0.66491 | 53192.8 | 0.51987 | 18715.32 | 0 | 0 | 1 | 5000 | 18715.32 | 0 | 0 | 0 | 0 | 0 | 29477.48 | 0 | 0 | 0 | 0 | 0 | 29477.48
2022070202 | 7 | 0.63286 | 50628.8 | 0.47943 | 17259.48 | 0 | 0 | 1 | 5000 | 17259.48 | 0 | 0 | 0 | 0 | 0 | 28369.32 | 0 | 0 | 0 | 0 | 0 | 28369.32
2022070203 | 7 | 0.60386 | 48308.8 | 0.44396 | 15982.56 | 0 | 0 | 1 | 5000 | 15982.56 | 0 | 0 | 0 | 0 | 0 | 27326.24 | 0 | 0 | 0 | 0 | 0 | 27326.24
2022070204 | 7 | 0.58237 | 46589.6 | 0.42659 | 15357.24 | 0 | 0 | 1 | 5000 | 15357.24 | 0 | 0 | 0 | 0 | 0 | 26232.36 | 0 | 0 | 0 | 0 | 0 | 26232.36
2022070205 | 7 | 0.56921 | 45536.8 | 0.38449 | 13841.64 | 0 | 0 | 1 | 5000 | 13841.64 | 0 | 0 | 0 | 0 | 0 | 26695.16 | 0 | 0 | 0 | 0 | 0 | 26695.16
2022070206 | 7 | 0.56299 | 45039.2 | 0.35066 | 12623.76 | 0 | 0 | 1 | 5000 | 12623.76 | 0 | 0 | 0 | 0 | 0 | 27415.44 | 0 | 0 | 0 | 0 | 0 | 27415.44
2022070207 | 7 | 0.55883 | 44706.4 | 0.31509 | 11343.24 | 0.00418 | 50.16 | 1 | 5000 | 11343.24 | 50.16 | 0 | 0 | 0 | 0 | 28313 | 0 | 0 | 0 | 0 | 0 | 28313
2022070208 | 7 | 0.56868 | 45494.4 | 0.25513 | 9184.68 | 0.18295 | 2195.4 | 1 | 5000 | 9184.68 | 2195.4 | 0 | 0 | 0 | 0 | 29114.32 | 0 | 0 | 0 | 0 | 0 | 29114.32
2022070209 | 7 | 0.61017 | 48813.6 | 0.2125 | 7650 | 0.5795 | 6954 | 1 | 5000 | 7650 | 6954 | 0 | 0 | 0 | 0 | 29209.6 | 0 | 0 | 0 | 0 | 0 | 29209.6
2022070210 | 7 | 0.66423 | 53138.4 | 0.23039 | 8294.04 | 0.72292 | 8675.04 | 1 | 5000 | 8294.04 | 8675.04 | 0 | 0 | 0 | 0 | 31169.32 | 0 | 0 | 0 | 0 | 0 | 31169.32
2022070211 | 7 | 0.72004 | 57603.2 | 0.20035 | 7212.6 | 0.77985 | 9358.2 | 1 | 5000 | 7212.6 | 9358.2 | 0 | 0 | 0 | 0 | 36032.4 | 0 | 0 | 0 | 0 | 0 | 36032.4
2022070212 | 7 | 0.77062 | 61649.6 | 0.16172 | 5821.92 | 0.74773 | 8972.76 | 1 | 5000 | 5821.92 | 8972.76 | 0 | 0 | 0 | 0 | 41854.92 | 0 | 0 | 0 | 0 | 0 | 41854.92
2022070213 | 7 | 0.81154 | 64923.2 | 0.14155 | 5095.8 | 0.7233 | 8679.6 | 1 | 5000 | 5095.8 | 8679.6 | 0 | 0 | 0 | 0 | 46147.8 | 0 | 0 | 0 | 0 | 0 | 46147.8
2022070214 | 7 | 0.83944 | 67155.2 | 0.14412 | 5188.32 | 0.70918 | 8510.16 | 1 | 5000 | 5188.32 | 8510.16 | 0 | 0 | 0 | 0 | 48456.72 | 0 | 0 | 0 | 0 | 0 | 48456.72
2022070215 | 7 | 0.86059 | 68847.2 | 0.1744 | 6278.4 | 0.65983 | 7917.96 | 1 | 5000 | 6278.4 | 7917.96 | 0 | 0 | 0 | 0 | 49650.84 | 0 | 0 | 0 | 0 | 0 | 49650.84
2022070216 | 7 | 0.87927 | 70341.6 | 0.2376 | 8553.6 | 0.66104 | 7932.48 | 1 | 5000 | 8553.6 | 7932.48 | 0 | 0 | 0 | 0 | 48855.52 | 0 | 0 | 0 | 0 | 0 | 48855.52
2022070217 | 7 | 0.89218 | 71374.4 | 0.29942 | 10779.12 | 0.62115 | 7453.8 | 1 | 5000 | 10779.12 | 7453.8 | 0 | 0 | 0 | 0 | 48141.48 | 0 | 0 | 0 | 0 | 0 | 48141.48
2022070218 | 7 | 0.89476 | 71580.8 | 0.35644 | 12831.84 | 0.62428 | 7491.36 | 1 | 5000 | 12831.84 | 7491.36 | 0 | 0 | 0 | 0 | 46257.6 | 0 | 0 | 0 | 0 | 0 | 46257.6
2022070219 | 7 | 0.88144 | 70515.2 | 0.38347 | 13804.92 | 0.56295 | 6755.4 | 1 | 5000 | 13804.92 | 6755.4 | 0 | 0 | 0 | 0 | 44954.88 | 0 | 0 | 0 | 0 | 0 | 44954.88
2022070220 | 7 | 0.85382 | 68305.6 | 0.41607 | 14978.52 | 0.33207 | 3984.84 | 1 | 5000 | 14978.52 | 3984.84 | 0 | 0 | 0 | 0 | 44342.24 | 0 | 0 | 0 | 0 | 0 | 44342.24
2022070221 | 7 | 0.81996 | 65596.8 | 0.44569 | 16044.84 | 0.05044 | 605.28 | 1 | 5000 | 16044.84 | 605.28 | 0 | 0 | 0 | 0 | 43946.68 | 0 | 0 | 0 | 0 | 0 | 43946.68
2022070222 | 7 | 0.79405 | 63524 | 0.43638 | 15709.68 | 0 | 0 | 1 | 5000 | 15709.68 | 0 | 0 | 0 | 0 | 0 | 42814.32 | 0 | 0 | 0 | 0 | 0 | 42814.32
2022070223 | 7 | 0.75657 | 60525.6 | 0.41284 | 14862.24 | 0 | 0 | 1 | 5000 | 14862.24 | 0 | 0 | 0 | 0 | 0 | 40663.36 | 0 | 0 | 0 | 0 | 0 | 40663.36
2022070224 | 7 | 0.7137 | 57096 | 0.4024 | 14486.4 | 0 | 0 | 1 | 5000 | 14486.4 | 0 | 0 | 0 | 0 | 0 | 37609.6 | 0 | 0 | 0 | 0 | 0 | 37609.6
2022070301 | 1 | 0.6725 | 53800 | 0.39104 | 14077.44 | 0 | 0 | 1 | 5000 | 14077.44 | 0 | 0 | 0 | 0 | 0 | 34722.56 | 0 | 0 | 0 | 0 | 0 | 34722.56
2022070302 | 1 | 0.63894 | 51115.2 | 0.37113 | 13360.68 | 0 | 0 | 1 | 5000 | 13360.68 | 0 | 0 | 0 | 0 | 0 | 32754.52 | 0 | 0 | 0 | 0 | 0 | 32754.52
2022070303 | 1 | 0.61034 | 48827.2 | 0.36489 | 13136.04 | 0 | 0 | 1 | 5000 | 13136.04 | 0 | 0 | 0 | 0 | 0 | 30691.16 | 0 | 0 | 0 | 0 | 0 | 30691.16
2022070304 | 1 | 0.58947 | 47157.6 | 0.33838 | 12181.68 | 0 | 0 | 1 | 5000 | 12181.68 | 0 | 0 | 0 | 0 | 0 | 29975.92 | 0 | 0 | 0 | 0 | 0 | 29975.92
2022070305 | 1 | 0.5742 | 45936 | 0.31241 | 11246.76 | 0 | 0 | 1 | 5000 | 11246.76 | 0 | 0 | 0 | 0 | 0 | 29689.24 | 0 | 0 | 0 | 0 | 0 | 29689.24
2022070306 | 1 | 0.56723 | 45378.4 | 0.32146 | 11572.56 | 0 | 0 | 1 | 5000 | 11572.56 | 0 | 0 | 0 | 0 | 0 | 28805.84 | 0 | 0 | 0 | 0 | 0 | 28805.84
2022070307 | 1 | 0.5604 | 44832 | 0.30659 | 11037.24 | 0.00369 | 44.28 | 1 | 5000 | 11037.24 | 44.28 | 0 | 0 | 0 | 0 | 28750.48 | 0 | 0 | 0 | 0 | 0 | 28750.48
2022070308 | 1 | 0.5703 | 45624 | 0.28799 | 10367.64 | 0.16555 | 1986.6 | 1 | 5000 | 10367.64 | 1986.6 | 0 | 0 | 0 | 0 | 28269.76 | 0 | 0 | 0 | 0 | 0 | 28269.76
2022070309 | 1 | 0.61066 | 48852.8 | 0.27735 | 9984.6 | 0.54025 | 6483 | 1 | 5000 | 9984.6 | 6483 | 0 | 0 | 0 | 0 | 27385.2 | 0 | 0 | 0 | 0 | 0 | 27385.2
2022070310 | 1 | 0.66477 | 53181.6 | 0.31375 | 11295 | 0.69238 | 8308.56 | 1 | 5000 | 11295 | 8308.56 | 0 | 0 | 0 | 0 | 28578.04 | 0 | 0 | 0 | 0 | 0 | 28578.04
2022070311 | 1 | 0.71684 | 57347.2 | 0.28317 | 10194.12 | 0.74938 | 8992.56 | 1 | 5000 | 10194.12 | 8992.56 | 0 | 0 | 0 | 0 | 33160.52 | 0 | 0 | 0 | 0 | 0 | 33160.52
2022070312 | 1 | 0.76958 | 61566.4 | 0.26982 | 9713.52 | 0.77014 | 9241.68 | 1 | 5000 | 9713.52 | 9241.68 | 0 | 0 | 0 | 0 | 37611.2 | 0 | 0 | 0 | 0 | 0 | 37611.2
2022070313 | 1 | 0.81554 | 65243.2 | 0.29894 | 10761.84 | 0.77511 | 9301.32 | 1 | 5000 | 10761.84 | 9301.32 | 0 | 0 | 0 | 0 | 40180.04 | 0 | 0 | 0 | 0 | 0 | 40180.04
2022070314 | 1 | 0.85243 | 68194.4 | 0.33551 | 12078.36 | 0.73067 | 8768.04 | 1 | 5000 | 12078.36 | 8768.04 | 0 | 0 | 0 | 0 | 42348 | 0 | 0 | 0 | 0 | 0 | 42348
2022070315 | 1 | 0.88014 | 70411.2 | 0.38457 | 13844.52 | 0.72347 | 8681.64 | 1 | 5000 | 13844.52 | 8681.64 | 0 | 0 | 0 | 0 | 42885.04 | 0 | 0 | 0 | 0 | 0 | 42885.04
2022070316 | 1 | 0.89993 | 71994.4 | 0.43088 | 15511.68 | 0.67512 | 8101.44 | 1 | 5000 | 15511.68 | 8101.44 | 0 | 0 | 0 | 0 | 43381.28 | 0 | 0 | 0 | 0 | 0 | 43381.28
2022070317 | 1 | 0.90634 | 72507.2 | 0.46265 | 16655.4 | 0.63889 | 7666.68 | 1 | 5000 | 16655.4 | 7666.68 | 0 | 0 | 0 | 0 | 43185.12 | 0 | 0 | 0 | 0 | 0 | 43185.12
2022070318 | 1 | 0.9062 | 72496 | 0.51728 | 18622.08 | 0.58205 | 6984.6 | 1 | 5000 | 18622.08 | 6984.6 | 0 | 0 | 0 | 0 | 41889.32 | 0 | 0 | 0 | 0 | 0 | 41889.32
2022070319 | 1 | 0.89155 | 71324 | 0.54765 | 19715.4 | 0.47771 | 5732.52 | 1 | 5000 | 19715.4 | 5732.52 | 0 | 0 | 0 | 0 | 40876.08 | 0 | 0 | 0 | 0 | 0 | 40876.08
2022070320 | 1 | 0.86134 | 68907.2 | 0.54148 | 19493.28 | 0.27697 | 3323.64 | 1 | 5000 | 19493.28 | 3323.64 | 0 | 0 | 0 | 0 | 41090.28 | 0 | 0 | 0 | 0 | 0 | 41090.28
2022070321 | 1 | 0.82025 | 65620 | 0.52573 | 18926.28 | 0.04579 | 549.48 | 1 | 5000 | 18926.28 | 549.48 | 0 | 0 | 0 | 0 | 41144.24 | 0 | 0 | 0 | 0 | 0 | 41144.24
2022070322 | 1 | 0.78783 | 63026.4 | 0.4574 | 16466.4 | 0 | 0 | 1 | 5000 | 16466.4 | 0 | 0 | 0 | 0 | 0 | 41560 | 0 | 0 | 0 | 0 | 0 | 41560
2022070323 | 1 | 0.7474 | 59792 | 0.42099 | 15155.64 | 0 | 0 | 1 | 5000 | 15155.64 | 0 | 0 | 0 | 0 | 0 | 39636.36 | 0 | 0 | 0 | 0 | 0 | 39636.36
2022070324 | 1 | 0.70644 | 56515.2 | 0.39814 | 14333.04 | 0 | 0 | 1 | 5000 | 14333.04 | 0 | 0 | 0 | 0 | 0 | 37182.16 | 0 | 0 | 0 | 0 | 0 | 37182.16
2022070401 | 2 | 0.66602 | 53281.6 | 0.41031 | 14771.16 | 0 | 0 | 1 | 5000 | 14771.16 | 0 | 0 | 0 | 0 | 0 | 33510.44 | 0 | 0 | 0 | 0 | 0 | 33510.44
2022070402 | 2 | 0.63242 | 50593.6 | 0.4259 | 15332.4 | 0 | 0 | 1 | 5000 | 15332.4 | 0 | 0 | 0 | 0 | 0 | 30261.2 | 0 | 0 | 0 | 0 | 0 | 30261.2
2022070403 | 2 | 0.60905 | 48724 | 0.44508 | 16022.88 | 0 | 0 | 1 | 5000 | 16022.88 | 0 | 0 | 0 | 0 | 0 | 27701.12 | 0 | 0 | 0 | 0 | 0 | 27701.12
2022070404 | 2 | 0.59214 | 47371.2 | 0.4601 | 16563.6 | 0 | 0 | 1 | 5000 | 16563.6 | 0 | 0 | 0 | 0 | 0 | 25807.6 | 0 | 0 | 0 | 0 | 0 | 25807.6
2022070405 | 2 | 0.58278 | 46622.4 | 0.4715 | 16974 | 0 | 0 | 1 | 5000 | 16974 | 0 | 0 | 0 | 0 | 0 | 24648.4 | 0 | 0 | 0 | 0 | 0 | 24648.4
2022070406 | 2 | 0.57777 | 46221.6 | 0.46717 | 16818.12 | 0 | 0 | 1 | 5000 | 16818.12 | 0 | 0 | 0 | 0 | 0 | 24403.48 | 0 | 0 | 0 | 0 | 0 | 24403.48
2022070407 | 2 | 0.56933 | 45546.4 | 0.44718 | 16098.48 | 0.00392 | 47.04 | 1 | 5000 | 16098.48 | 47.04 | 0 | 0 | 0 | 0 | 24400.88 | 0 | 0 | 0 | 0 | 0 | 24400.88
2022070408 | 2 | 0.57522 | 46017.6 | 0.40271 | 14497.56 | 0.17231 | 2067.72 | 1 | 5000 | 14497.56 | 2067.72 | 0 | 0 | 0 | 0 | 24452.32 | 0 | 0 | 0 | 0 | 0 | 24452.32
2022070409 | 2 | 0.61514 | 49211.2 | 0.4116 | 14817.6 | 0.54636 | 6556.32 | 1 | 5000 | 14817.6 | 6556.32 | 0 | 0 | 0 | 0 | 22837.28 | 0 | 0 | 0 | 0 | 0 | 22837.28
2022070410 | 2 | 0.66982 | 53585.6 | 0.4852 | 17467.2 | 0.71714 | 8605.68 | 1 | 5000 | 17467.2 | 8605.68 | 0 | 0 | 0 | 0 | 22512.72 | 0 | 0 | 0 | 0 | 0 | 22512.72
2022070411 | 2 | 0.72472 | 57977.6 | 0.46773 | 16838.28 | 0.77393 | 9287.16 | 1 | 5000 | 16838.28 | 9287.16 | 0 | 0 | 0 | 0 | 26852.16 | 0 | 0 | 0 | 0 | 0 | 26852.16
2022070412 | 2 | 0.77777 | 62221.6 | 0.42975 | 15471 | 0.7795 | 9354 | 1 | 5000 | 15471 | 9354 | 0 | 0 | 0 | 0 | 32396.6 | 0 | 0 | 0 | 0 | 0 | 32396.6
2022070413 | 2 | 0.8233 | 65864 | 0.40917 | 14730.12 | 0.7783 | 9339.6 | 1 | 5000 | 14730.12 | 9339.6 | 0 | 0 | 0 | 0 | 36794.28 | 0 | 0 | 0 | 0 | 0 | 36794.28
2022070414 | 2 | 0.86155 | 68924 | 0.41251 | 14850.36 | 0.75314 | 9037.68 | 1 | 5000 | 14850.36 | 9037.68 | 0 | 0 | 0 | 0 | 40035.96 | 0 | 0 | 0 | 0 | 0 | 40035.96
2022070415 | 2 | 0.88939 | 71151.2 | 0.41527 | 14949.72 | 0.70756 | 8490.72 | 1 | 5000 | 14949.72 | 8490.72 | 0 | 0 | 0 | 0 | 42710.76 | 0 | 0 | 0 | 0 | 0 | 42710.76
2022070416 | 2 | 0.91036 | 72828.8 | 0.42682 | 15365.52 | 0.69263 | 8311.56 | 1 | 5000 | 15365.52 | 8311.56 | 0 | 0 | 0 | 0 | 44151.72 | 0 | 0 | 0 | 0 | 0 | 44151.72
2022070417 | 2 | 0.9247 | 73976 | 0.45855 | 16507.8 | 0.69429 | 8331.48 | 1 | 5000 | 16507.8 | 8331.48 | 0 | 0 | 0 | 0 | 44136.72 | 0 | 0 | 0 | 0 | 0 | 44136.72
2022070418 | 2 | 0.92904 | 74323.2 | 0.50176 | 18063.36 | 0.65271 | 7832.52 | 1 | 5000 | 18063.36 | 7832.52 | 0 | 0 | 0 | 0 | 43427.32 | 0 | 0 | 0 | 0 | 0 | 43427.32
2022070419 | 2 | 0.91511 | 73208.8 | 0.54474 | 19610.64 | 0.48793 | 5855.16 | 1 | 5000 | 19610.64 | 5855.16 | 0 | 0 | 0 | 0 | 42743 | 0 | 0 | 0 | 0 | 0 | 42743
2022070420 | 2 | 0.88514 | 70811.2 | 0.59739 | 21506.04 | 0.19321 | 2318.52 | 1 | 5000 | 21506.04 | 2318.52 | 0 | 0 | 0 | 0 | 41986.64 | 0 | 0 | 0 | 0 | 0 | 41986.64
2022070421 | 2 | 0.84449 | 67559.2 | 0.60237 | 21685.32 | 0.03194 | 383.28 | 1 | 5000 | 21685.32 | 383.28 | 0 | 0 | 0 | 0 | 40490.6 | 0 | 0 | 0 | 0 | 0 | 40490.6
2022070422 | 2 | 0.80639 | 64511.2 | 0.57747 | 20788.92 | 0.0002 | 2.4 | 1 | 5000 | 20788.92 | 2.4 | 0 | 0 | 0 | 0 | 38719.88 | 0 | 0 | 0 | 0 | 0 | 38719.88
2022070423 | 2 | 0.76832 | 61465.6 | 0.58179 | 20944.44 | 0 | 0 | 1 | 5000 | 20944.44 | 0 | 0 | 0 | 0 | 0 | 35521.16 | 0 | 0 | 0 | 0 | 0 | 35521.16
2022070424 | 2 | 0.7269 | 58152 | 0.60397 | 21742.92 | 0 | 0 | 1 | 5000 | 21742.92 | 0 | 0 | 0 | 0 | 0 | 31409.08 | 0 | 0 | 0 | 0 | 0 | 31409.08
2022070501 | 3 | 0.68335 | 54668 | 0.61303 | 22069.08 | 0 | 0 | 1 | 5000 | 22069.08 | 0 | 0 | 0 | 0 | 0 | 27598.92 | 0 | 0 | 0 | 0 | 0 | 27598.92
2022070502 | 3 | 0.64645 | 51716 | 0.57126 | 20565.36 | 0 | 0 | 1 | 5000 | 20565.36 | 0 | 0 | 0 | 0 | 0 | 26150.64 | 0 | 0 | 0 | 0 | 0 | 26150.64
2022070503 | 3 | 0.61716 | 49372.8 | 0.53638 | 19309.68 | 0 | 0 | 1 | 5000 | 19309.68 | 0 | 0 | 0 | 0 | 0 | 25063.12 | 0 | 0 | 0 | 0 | 0 | 25063.12
2022070504 | 3 | 0.60325 | 48260 | 0.5285 | 19026 | 0 | 0 | 1 | 5000 | 19026 | 0 | 0 | 0 | 0 | 0 | 24234 | 0 | 0 | 0 | 0 | 0 | 24234
2022070505 | 3 | 0.59483 | 47586.4 | 0.53087 | 19111.32 | 0 | 0 | 1 | 5000 | 19111.32 | 0 | 0 | 0 | 0 | 0 | 23475.08 | 0 | 0 | 0 | 0 | 0 | 23475.08
2022070506 | 3 | 0.60256 | 48204.8 | 0.5197 | 18709.2 | 0 | 0 | 1 | 5000 | 18709.2 | 0 | 0 | 0 | 0 | 0 | 24495.6 | 0 | 0 | 0 | 0 | 0 | 24495.6
2022070507 | 3 | 0.61171 | 48936.8 | 0.52152 | 18774.72 | 0.00384 | 46.08 | 1 | 5000 | 18774.72 | 46.08 | 0 | 0 | 0 | 0 | 25116 | 0 | 0 | 0 | 0 | 0 | 25116
2022070508 | 3 | 0.62922 | 50337.6 | 0.48407 | 17426.52 | 0.16011 | 1921.32 | 1 | 5000 | 17426.52 | 1921.32 | 0 | 0 | 0 | 0 | 25989.76 | 0 | 0 | 0 | 0 | 0 | 25989.76
2022070509 | 3 | 0.66951 | 53560.8 | 0.50557 | 18200.52 | 0.46078 | 5529.36 | 1 | 5000 | 18200.52 | 5529.36 | 0 | 0 | 0 | 0 | 24830.92 | 0 | 0 | 0 | 0 | 0 | 24830.92
2022070510 | 3 | 0.71808 | 57446.4 | 0.55598 | 20015.28 | 0.58569 | 7028.28 | 1 | 5000 | 20015.28 | 7028.28 | 0 | 0 | 0 | 0 | 25402.84 | 0 | 0 | 0 | 0 | 0 | 25402.84
2022070511 | 3 | 0.76903 | 61522.4 | 0.50663 | 18238.68 | 0.67767 | 8132.04 | 1 | 5000 | 18238.68 | 8132.04 | 0 | 0 | 0 | 0 | 30151.68 | 0 | 0 | 0 | 0 | 0 | 30151.68
2022070512 | 3 | 0.81994 | 65595.2 | 0.4233 | 15238.8 | 0.7578 | 9093.6 | 1 | 5000 | 15238.8 | 9093.6 | 0 | 0 | 0 | 0 | 36262.8 | 0 | 0 | 0 | 0 | 0 | 36262.8
2022070513 | 3 | 0.86382 | 69105.6 | 0.35037 | 12613.32 | 0.75506 | 9060.72 | 1 | 5000 | 12613.32 | 9060.72 | 0 | 0 | 0 | 0 | 42431.56 | 0 | 0 | 0 | 0 | 0 | 42431.56
2022070514 | 3 | 0.90618 | 72494.4 | 0.31601 | 11376.36 | 0.76369 | 9164.28 | 1 | 5000 | 11376.36 | 9164.28 | 0 | 0 | 0 | 0 | 46953.76 | 0 | 0 | 0 | 0 | 0 | 46953.76
2022070515 | 3 | 0.93618 | 74894.4 | 0.32092 | 11553.12 | 0.77218 | 9266.16 | 1 | 5000 | 11553.12 | 9266.16 | 0 | 0 | 0 | 0 | 49075.12 | 0 | 0 | 0 | 0 | 0 | 49075.12
2022070516 | 3 | 0.9572 | 76576 | 0.35538 | 12793.68 | 0.72058 | 8646.96 | 1 | 5000 | 12793.68 | 8646.96 | 0 | 0 | 0 | 0 | 50135.36 | 0 | 0 | 0 | 0 | 0 | 50135.36
2022070517 | 3 | 0.97053 | 77642.4 | 0.38648 | 13913.28 | 0.67321 | 8078.52 | 1 | 5000 | 13913.28 | 8078.52 | 0 | 0 | 0 | 0 | 50650.6 | 0 | 0 | 0 | 0 | 0 | 50650.6
2022070518 | 3 | 0.96737 | 77389.6 | 0.4083 | 14698.8 | 0.53431 | 6411.72 | 1 | 5000 | 14698.8 | 6411.72 | 0 | 0 | 0 | 0 | 51279.08 | 0 | 0 | 0 | 0 | 0 | 51279.08
2022070519 | 3 | 0.95251 | 76200.8 | 0.44433 | 15995.88 | 0.37185 | 4462.2 | 1 | 5000 | 15995.88 | 4462.2 | 0 | 0 | 0 | 0 | 50742.72 | 0 | 0 | 0 | 0 | 0 | 50742.72
2022070520 | 3 | 0.92724 | 74179.2 | 0.49213 | 17716.68 | 0.20668 | 2480.16 | 1 | 5000 | 17716.68 | 2480.16 | 0 | 0 | 0 | 0 | 48982.36 | 0 | 0 | 0 | 0 | 0 | 48982.36
2022070521 | 3 | 0.88702 | 70961.6 | 0.47915 | 17249.4 | 0.0212 | 254.4 | 1 | 5000 | 17249.4 | 254.4 | 0 | 0 | 0 | 0 | 48457.8 | 0 | 0 | 0 | 0 | 0 | 48457.8
2022070522 | 3 | 0.85444 | 68355.2 | 0.47365 | 17051.4 | 0 | 0 | 1 | 5000 | 17051.4 | 0 | 0 | 0 | 0 | 0 | 46303.8 | 0 | 0 | 0 | 0 | 0 | 46303.8
2022070523 | 3 | 0.80104 | 64083.2 | 0.45066 | 16223.76 | 0 | 0 | 1 | 5000 | 16223.76 | 0 | 0 | 0 | 0 | 0 | 42859.44 | 0 | 0 | 0 | 0 | 0 | 42859.44
2022070524 | 3 | 0.74587 | 59669.6 | 0.44359 | 15969.24 | 0 | 0 | 1 | 5000 | 15969.24 | 0 | 0 | 0 | 0 | 0 | 38700.36 | 0 | 0 | 0 | 0 | 0 | 38700.36
2022070601 | 4 | 0.69676 | 55740.8 | 0.4649 | 16736.4 | 0 | 0 | 1 | 5000 | 16736.4 | 0 | 0 | 0 | 0 | 0 | 34004.4 | 0 | 0 | 0 | 0 | 0 | 34004.4
2022070602 | 4 | 0.65897 | 52717.6 | 0.50324 | 18116.64 | 0 | 0 | 1 | 5000 | 18116.64 | 0 | 0 | 0 | 0 | 0 | 29600.96 | 0 | 0 | 0 | 0 | 0 | 29600.96
2022070603 | 4 | 0.62933 | 50346.4 | 0.49791 | 17924.76 | 0 | 0 | 1 | 5000 | 17924.76 | 0 | 0 | 0 | 0 | 0 | 27421.64 | 0 | 0 | 0 | 0 | 0 | 27421.64
2022070604 | 4 | 0.61124 | 48899.2 | 0.50134 | 18048.24 | 0 | 0 | 1 | 5000 | 18048.24 | 0 | 0 | 0 | 0 | 0 | 25850.96 | 0 | 0 | 0 | 0 | 0 | 25850.96
2022070605 | 4 | 0.60467 | 48373.6 | 0.50536 | 18192.96 | 0 | 0 | 1 | 5000 | 18192.96 | 0 | 0 | 0 | 0 | 0 | 25180.64 | 0 | 0 | 0 | 0 | 0 | 25180.64
2022070606 | 4 | 0.61008 | 48806.4 | 0.50579 | 18208.44 | 0 | 0 | 1 | 5000 | 18208.44 | 0 | 0 | 0 | 0 | 0 | 25597.96 | 0 | 0 | 0 | 0 | 0 | 25597.96
2022070607 | 4 | 0.6221 | 49768 | 0.46902 | 16884.72 | 0.00303 | 36.36 | 1 | 5000 | 16884.72 | 36.36 | 0 | 0 | 0 | 0 | 27846.92 | 0 | 0 | 0 | 0 | 0 | 27846.92
2022070608 | 4 | 0.63221 | 50576.8 | 0.42237 | 15205.32 | 0.15871 | 1904.52 | 1 | 5000 | 15205.32 | 1904.52 | 0 | 0 | 0 | 0 | 28466.96 | 0 | 0 | 0 | 0 | 0 | 28466.96
2022070609 | 4 | 0.66919 | 53535.2 | 0.41782 | 15041.52 | 0.44188 | 5302.56 | 1 | 5000 | 15041.52 | 5302.56 | 0 | 0 | 0 | 0 | 28191.12 | 0 | 0 | 0 | 0 | 0 | 28191.12
2022070610 | 4 | 0.72153 | 57722.4 | 0.47718 | 17178.48 | 0.61049 | 7325.88 | 1 | 5000 | 17178.48 | 7325.88 | 0 | 0 | 0 | 0 | 28218.04 | 0 | 0 | 0 | 0 | 0 | 28218.04
2022070611 | 4 | 0.77514 | 62011.2 | 0.41138 | 14809.68 | 0.73125 | 8775 | 1 | 5000 | 14809.68 | 8775 | 0 | 0 | 0 | 0 | 33426.52 | 0 | 0 | 0 | 0 | 0 | 33426.52
2022070612 | 4 | 0.82394 | 65915.2 | 0.31651 | 11394.36 | 0.74435 | 8932.2 | 1 | 5000 | 11394.36 | 8932.2 | 0 | 0 | 0 | 0 | 40588.64 | 0 | 0 | 0 | 0 | 0 | 40588.64
2022070613 | 4 | 0.87202 | 69761.6 | 0.25186 | 9066.96 | 0.73279 | 8793.48 | 1 | 5000 | 9066.96 | 8793.48 | 0 | 0 | 0 | 0 | 46901.16 | 0 | 0 | 0 | 0 | 0 | 46901.16
2022070614 | 4 | 0.91515 | 73212 | 0.2383 | 8578.8 | 0.77014 | 9241.68 | 1 | 5000 | 8578.8 | 9241.68 | 0 | 0 | 0 | 0 | 50391.52 | 0 | 0 | 0 | 0 | 0 | 50391.52
2022070615 | 4 | 0.94538 | 75630.4 | 0.26801 | 9648.36 | 0.76885 | 9226.2 | 1 | 5000 | 9648.36 | 9226.2 | 0 | 0 | 0 | 0 | 51755.84 | 0 | 0 | 0 | 0 | 0 | 51755.84
2022070616 | 4 | 0.96066 | 76852.8 | 0.30124 | 10844.64 | 0.75216 | 9025.92 | 1 | 5000 | 10844.64 | 9025.92 | 0 | 0 | 0 | 0 | 51982.24 | 0 | 0 | 0 | 0 | 0 | 51982.24
2022070617 | 4 | 0.96538 | 77230.4 | 0.32892 | 11841.12 | 0.70794 | 8495.28 | 1 | 5000 | 11841.12 | 8495.28 | 0 | 0 | 0 | 0 | 51894 | 0 | 0 | 0 | 0 | 0 | 51894
2022070618 | 4 | 0.96191 | 76952.8 | 0.35223 | 12680.28 | 0.67745 | 8129.4 | 1 | 5000 | 12680.28 | 8129.4 | 0 | 0 | 0 | 0 | 51143.12 | 0 | 0 | 0 | 0 | 0 | 51143.12
2022070619 | 4 | 0.94751 | 75800.8 | 0.3646 | 13125.6 | 0.5782 | 6938.4 | 1 | 5000 | 13125.6 | 6938.4 | 0 | 0 | 0 | 0 | 50736.8 | 0 | 0 | 0 | 0 | 0 | 50736.8
2022070620 | 4 | 0.92105 | 73684 | 0.36949 | 13301.64 | 0.33405 | 4008.6 | 1 | 5000 | 13301.64 | 4008.6 | 0 | 0 | 0 | 0 | 51373.76 | 0 | 0 | 0 | 0 | 0 | 51373.76
2022070621 | 4 | 0.88553 | 70842.4 | 0.37787 | 13603.32 | 0.04011 | 481.32 | 1 | 5000 | 13603.32 | 481.32 | 0 | 0 | 0 | 0 | 51757.76 | 0 | 0 | 0 | 0 | 0 | 51757.76
2022070622 | 4 | 0.85246 | 68196.8 | 0.41923 | 15092.28 | 0 | 0 | 1 | 5000 | 15092.28 | 0 | 0 | 0 | 0 | 0 | 48104.52 | 0 | 0 | 0 | 0 | 0 | 48104.52
2022070623 | 4 | 0.80392 | 64313.6 | 0.49047 | 17656.92 | 0 | 0 | 1 | 5000 | 17656.92 | 0 | 0 | 0 | 0 | 0 | 41656.68 | 0 | 0 | 0 | 0 | 0 | 41656.68
2022070624 | 4 | 0.75072 | 60057.6 | 0.53156 | 19136.16 | 0 | 0 | 1 | 5000 | 19136.16 | 0 | 0 | 0 | 0 | 0 | 35921.44 | 0 | 0 | 0 | 0 | 0 | 35921.44
2022070701 | 5 | 0.7038 | 56304 | 0.5194 | 18698.4 | 0 | 0 | 1 | 5000 | 18698.4 | 0 | 0 | 0 | 0 | 0 | 32605.6 | 0 | 0 | 0 | 0 | 0 | 32605.6
2022070702 | 5 | 0.66677 | 53341.6 | 0.51486 | 18534.96 | 0 | 0 | 1 | 5000 | 18534.96 | 0 | 0 | 0 | 0 | 0 | 29806.64 | 0 | 0 | 0 | 0 | 0 | 29806.64
2022070703 | 5 | 0.64212 | 51369.6 | 0.52139 | 18770.04 | 0 | 0 | 1 | 5000 | 18770.04 | 0 | 0 | 0 | 0 | 0 | 27599.56 | 0 | 0 | 0 | 0 | 0 | 27599.56
2022070704 | 5 | 0.62531 | 50024.8 | 0.50642 | 18231.12 | 0 | 0 | 1 | 5000 | 18231.12 | 0 | 0 | 0 | 0 | 0 | 26793.68 | 0 | 0 | 0 | 0 | 0 | 26793.68
2022070705 | 5 | 0.61578 | 49262.4 | 0.49937 | 17977.32 | 0 | 0 | 1 | 5000 | 17977.32 | 0 | 0 | 0 | 0 | 0 | 26285.08 | 0 | 0 | 0 | 0 | 0 | 26285.08
2022070706 | 5 | 0.61729 | 49383.2 | 0.47599 | 17135.64 | 0 | 0 | 1 | 5000 | 17135.64 | 0 | 0 | 0 | 0 | 0 | 27247.56 | 0 | 0 | 0 | 0 | 0 | 27247.56
2022070707 | 5 | 0.62342 | 49873.6 | 0.44554 | 16039.44 | 0.00332 | 39.84 | 1 | 5000 | 16039.44 | 39.84 | 0 | 0 | 0 | 0 | 28794.32 | 0 | 0 | 0 | 0 | 0 | 28794.32
2022070708 | 5 | 0.63821 | 51056.8 | 0.40126 | 14445.36 | 0.17925 | 2151 | 1 | 5000 | 14445.36 | 2151 | 0 | 0 | 0 | 0 | 29460.44 | 0 | 0 | 0 | 0 | 0 | 29460.44
2022070709 | 5 | 0.67767 | 54213.6 | 0.3502 | 12607.2 | 0.56677 | 6801.24 | 1 | 5000 | 12607.2 | 6801.24 | 0 | 0 | 0 | 0 | 29805.16 | 0 | 0 | 0 | 0 | 0 | 29805.16
2022070710 | 5 | 0.72584 | 58067.2 | 0.37102 | 13356.72 | 0.74891 | 8986.92 | 1 | 5000 | 13356.72 | 8986.92 | 0 | 0 | 0 | 0 | 30723.56 | 0 | 0 | 0 | 0 | 0 | 30723.56
2022070711 | 5 | 0.77751 | 62200.8 | 0.30743 | 11067.48 | 0.78752 | 9450.24 | 1 | 5000 | 11067.48 | 9450.24 | 0 | 0 | 0 | 0 | 36683.08 | 0 | 0 | 0 | 0 | 0 | 36683.08
2022070712 | 5 | 0.8295 | 66360 | 0.225 | 8100 | 0.78921 | 9470.52 | 1 | 5000 | 8100 | 9470.52 | 0 | 0 | 0 | 0 | 43789.48 | 0 | 0 | 0 | 0 | 0 | 43789.48
2022070713 | 5 | 0.87826 | 70260.8 | 0.18832 | 6779.52 | 0.78813 | 9457.56 | 1 | 5000 | 6779.52 | 9457.56 | 0 | 0 | 0 | 0 | 49023.72 | 0 | 0 | 0 | 0 | 0 | 49023.72
2022070714 | 5 | 0.91842 | 73473.6 | 0.18222 | 6559.92 | 0.77497 | 9299.64 | 1 | 5000 | 6559.92 | 9299.64 | 0 | 0 | 0 | 0 | 52614.04 | 0 | 0 | 0 | 0 | 0 | 52614.04
2022070715 | 5 | 0.94791 | 75832.8 | 0.17392 | 6261.12 | 0.76365 | 9163.8 | 1 | 5000 | 6261.12 | 9163.8 | 0 | 0 | 0 | 0 | 55407.88 | 0 | 0 | 0 | 0 | 0 | 55407.88
2022070716 | 5 | 0.96245 | 76996 | 0.18917 | 6810.12 | 0.74197 | 8903.64 | 1 | 5000 | 6810.12 | 8903.64 | 0 | 0 | 0 | 0 | 56282.24 | 0 | 0 | 0 | 0 | 0 | 56282.24
2022070717 | 5 | 0.96663 | 77330.4 | 0.2144 | 7718.4 | 0.7319 | 8782.8 | 1 | 5000 | 7718.4 | 8782.8 | 0 | 0 | 0 | 0 | 55829.2 | 0 | 0 | 0 | 0 | 0 | 55829.2
2022070718 | 5 | 0.96091 | 76872.8 | 0.25655 | 9235.8 | 0.69819 | 8378.28 | 1 | 5000 | 9235.8 | 8378.28 | 0 | 0 | 0 | 0 | 54258.72 | 0 | 0 | 0 | 0 | 0 | 54258.72
2022070719 | 5 | 0.94772 | 75817.6 | 0.29378 | 10576.08 | 0.59639 | 7156.68 | 1 | 5000 | 10576.08 | 7156.68 | 0 | 0 | 0 | 0 | 53084.84 | 0 | 0 | 0 | 0 | 0 | 53084.84
2022070720 | 5 | 0.92127 | 73701.6 | 0.31118 | 11202.48 | 0.34052 | 4086.24 | 1 | 5000 | 11202.48 | 4086.24 | 0 | 0 | 0 | 0 | 53412.88 | 0 | 0 | 0 | 0 | 0 | 53412.88
2022070721 | 5 | 0.88715 | 70972 | 0.31 | 11160 | 0.03385 | 406.2 | 1 | 5000 | 11160 | 406.2 | 0 | 0 | 0 | 0 | 54405.8 | 0 | 0 | 0 | 0 | 0 | 54405.8
2022070722 | 5 | 0.85438 | 68350.4 | 0.36572 | 13165.92 | 0 | 0 | 1 | 5000 | 13165.92 | 0 | 0 | 0 | 0 | 0 | 50184.48 | 0 | 0 | 0 | 0 | 0 | 50184.48
2022070723 | 5 | 0.80444 | 64355.2 | 0.43936 | 15816.96 | 0 | 0 | 1 | 5000 | 15816.96 | 0 | 0 | 0 | 0 | 0 | 43538.24 | 0 | 0 | 0 | 0 | 0 | 43538.24
2022070724 | 5 | 0.75104 | 60083.2 | 0.46688 | 16807.68 | 0 | 0 | 1 | 5000 | 16807.68 | 0 | 0 | 0 | 0 | 0 | 38275.52 | 0 | 0 | 0 | 0 | 0 | 38275.52
2022070801 | 6 | 0.70287 | 56229.6 | 0.48337 | 17401.32 | 0 | 0 | 1 | 5000 | 17401.32 | 0 | 0 | 0 | 0 | 0 | 33828.28 | 0 | 0 | 0 | 0 | 0 | 33828.28
2022070802 | 6 | 0.66428 | 53142.4 | 0.47252 | 17010.72 | 0 | 0 | 1 | 5000 | 17010.72 | 0 | 0 | 0 | 0 | 0 | 31131.68 | 0 | 0 | 0 | 0 | 0 | 31131.68
2022070803 | 6 | 0.63647 | 50917.6 | 0.42474 | 15290.64 | 0 | 0 | 1 | 5000 | 15290.64 | 0 | 0 | 0 | 0 | 0 | 30626.96 | 0 | 0 | 0 | 0 | 0 | 30626.96
2022070804 | 6 | 0.62035 | 49628 | 0.3838 | 13816.8 | 0 | 0 | 1 | 5000 | 13816.8 | 0 | 0 | 0 | 0 | 0 | 30811.2 | 0 | 0 | 0 | 0 | 0 | 30811.2
2022070805 | 6 | 0.61237 | 48989.6 | 0.36618 | 13182.48 | 0 | 0 | 1 | 5000 | 13182.48 | 0 | 0 | 0 | 0 | 0 | 30807.12 | 0 | 0 | 0 | 0 | 0 | 30807.12
2022070806 | 6 | 0.61812 | 49449.6 | 0.38169 | 13740.84 | 0 | 0 | 1 | 5000 | 13740.84 | 0 | 0 | 0 | 0 | 0 | 30708.76 | 0 | 0 | 0 | 0 | 0 | 30708.76
2022070807 | 6 | 0.61994 | 49595.2 | 0.37557 | 13520.52 | 0.00334 | 40.08 | 1 | 5000 | 13520.52 | 40.08 | 0 | 0 | 0 | 0 | 31034.6 | 0 | 0 | 0 | 0 | 0 | 31034.6
2022070808 | 6 | 0.63559 | 50847.2 | 0.32751 | 11790.36 | 0.16474 | 1976.88 | 1 | 5000 | 11790.36 | 1976.88 | 0 | 0 | 0 | 0 | 32079.96 | 0 | 0 | 0 | 0 | 0 | 32079.96
2022070809 | 6 | 0.67677 | 54141.6 | 0.27585 | 9930.6 | 0.54854 | 6582.48 | 1 | 5000 | 9930.6 | 6582.48 | 0 | 0 | 0 | 0 | 32628.52 | 0 | 0 | 0 | 0 | 0 | 32628.52
2022070810 | 6 | 0.72895 | 58316 | 0.27214 | 9797.04 | 0.7503 | 9003.6 | 1 | 5000 | 9797.04 | 9003.6 | 0 | 0 | 0 | 0 | 34515.36 | 0 | 0 | 0 | 0 | 0 | 34515.36
2022070811 | 6 | 0.78441 | 62752.8 | 0.18843 | 6783.48 | 0.77418 | 9290.16 | 1 | 5000 | 6783.48 | 9290.16 | 0 | 0 | 0 | 0 | 41679.16 | 0 | 0 | 0 | 0 | 0 | 41679.16
2022070812 | 6 | 0.84059 | 67247.2 | 0.1047 | 3769.2 | 0.7739 | 9286.8 | 1 | 5000 | 3769.2 | 9286.8 | 0 | 0 | 0 | 0 | 49191.2 | 0 | 0 | 0 | 0 | 0 | 49191.2
2022070813 | 6 | 0.8896 | 71168 | 0.06747 | 2428.92 | 0.76019 | 9122.28 | 1 | 5000 | 2428.92 | 9122.28 | 0 | 0 | 0 | 0 | 54616.8 | 0 | 0 | 0 | 0 | 0 | 54616.8
2022070814 | 6 | 0.92929 | 74343.2 | 0.07267 | 2616.12 | 0.76418 | 9170.16 | 1 | 5000 | 2616.12 | 9170.16 | 0 | 0 | 0 | 0 | 57556.92 | 0 | 0 | 0 | 0 | 0 | 57556.92
2022070815 | 6 | 0.95826 | 76660.8 | 0.09388 | 3379.68 | 0.74286 | 8914.32 | 1 | 5000 | 3379.68 | 8914.32 | 0 | 0 | 0 | 0 | 59366.8 | 0 | 0 | 0 | 0 | 0 | 59366.8
2022070816 | 6 | 0.97319 | 77855.2 | 0.11815 | 4253.4 | 0.71107 | 8532.84 | 1 | 5000 | 4253.4 | 8532.84 | 0 | 0 | 0 | 0 | 60068.96 | 0 | 0 | 0 | 0 | 0 | 60068.96
2022070817 | 6 | 0.97975 | 78380 | 0.13813 | 4972.68 | 0.70758 | 8490.96 | 1 | 5000 | 4972.68 | 8490.96 | 0 | 0 | 0 | 0 | 59916.36 | 0 | 0 | 0 | 0 | 0 | 59916.36
2022070818 | 6 | 0.97942 | 78353.6 | 0.14373 | 5174.28 | 0.7052 | 8462.4 | 1 | 5000 | 5174.28 | 8462.4 | 0 | 0 | 0 | 0 | 59716.92 | 0 | 0 | 0 | 0 | 0 | 59716.92
2022070819 | 6 | 0.97392 | 77913.6 | 0.18754 | 6751.44 | 0.63542 | 7625.04 | 1 | 5000 | 6751.44 | 7625.04 | 0 | 0 | 0 | 0 | 58537.12 | 0 | 0 | 0 | 0 | 0 | 58537.12
2022070820 | 6 | 0.95248 | 76198.4 | 0.24242 | 8727.12 | 0.35706 | 4284.72 | 1 | 5000 | 8727.12 | 4284.72 | 0 | 0 | 0 | 0 | 58186.56 | 0 | 0 | 0 | 0 | 0 | 58186.56
2022070821 | 6 | 0.91421 | 73136.8 | 0.26836 | 9660.96 | 0.04447 | 533.64 | 1 | 5000 | 9660.96 | 533.64 | 0 | 0 | 0 | 0 | 57942.2 | 0 | 0 | 0 | 0 | 0 | 57942.2
2022070822 | 6 | 0.88028 | 70422.4 | 0.322 | 11592 | 0 | 0 | 1 | 5000 | 11592 | 0 | 0 | 0 | 0 | 0 | 53830.4 | 0 | 0 | 0 | 0 | 0 | 53830.4
2022070823 | 6 | 0.82847 | 66277.6 | 0.38258 | 13772.88 | 0 | 0 | 1 | 5000 | 13772.88 | 0 | 0 | 0 | 0 | 0 | 47504.72 | 0 | 0 | 0 | 0 | 0 | 47504.72
2022070824 | 6 | 0.7779 | 62232 | 0.4245 | 15282 | 0 | 0 | 1 | 5000 | 15282 | 0 | 0 | 0 | 0 | 0 | 41950 | 0 | 0 | 0 | 0 | 0 | 41950
2022070901 | 7 | 0.73019 | 58415.2 | 0.4294 | 15458.4 | 0 | 0 | 1 | 5000 | 15458.4 | 0 | 0 | 0 | 0 | 0 | 37956.8 | 0 | 0 | 0 | 0 | 0 | 37956.8
2022070902 | 7 | 0.68753 | 55002.4 | 0.38161 | 13737.96 | 0 | 0 | 1 | 5000 | 13737.96 | 0 | 0 | 0 | 0 | 0 | 36264.44 | 0 | 0 | 0 | 0 | 0 | 36264.44
2022070903 | 7 | 0.65193 | 52154.4 | 0.28883 | 10397.88 | 0 | 0 | 1 | 5000 | 10397.88 | 0 | 0 | 0 | 0 | 0 | 36756.52 | 0 | 0 | 0 | 0 | 0 | 36756.52
2022070904 | 7 | 0.62702 | 50161.6 | 0.21564 | 7763.04 | 0 | 0 | 1 | 5000 | 7763.04 | 0 | 0 | 0 | 0 | 0 | 37398.56 | 0 | 0 | 0 | 0 | 0 | 37398.56
2022070905 | 7 | 0.61204 | 48963.2 | 0.15574 | 5606.64 | 0 | 0 | 1 | 5000 | 5606.64 | 0 | 0 | 0 | 0 | 0 | 38356.56 | 0 | 0 | 0 | 0 | 0 | 38356.56
2022070906 | 7 | 0.60342 | 48273.6 | 0.1411 | 5079.6 | 0 | 0 | 1 | 5000 | 5079.6 | 0 | 0 | 0 | 0 | 0 | 38194 | 0 | 0 | 0 | 0 | 0 | 38194
2022070907 | 7 | 0.59627 | 47701.6 | 0.146 | 5256 | 0.00263 | 31.56 | 1 | 5000 | 5256 | 31.56 | 0 | 0 | 0 | 0 | 37414.04 | 0 | 0 | 0 | 0 | 0 | 37414.04
2022070908 | 7 | 0.60554 | 48443.2 | 0.14429 | 5194.44 | 0.14955 | 1794.6 | 1 | 5000 | 5194.44 | 1794.6 | 0 | 0 | 0 | 0 | 36454.16 | 0 | 0 | 0 | 0 | 0 | 36454.16
2022070909 | 7 | 0.64493 | 51594.4 | 0.10552 | 3798.72 | 0.52178 | 6261.36 | 1 | 5000 | 3798.72 | 6261.36 | 0 | 0 | 0 | 0 | 36534.32 | 0 | 0 | 0 | 0 | 0 | 36534.32
2022070910 | 7 | 0.7022 | 56176 | 0.09694 | 3489.84 | 0.67181 | 8061.72 | 1 | 5000 | 3489.84 | 8061.72 | 0 | 0 | 0 | 0 | 39624.44 | 0 | 0 | 0 | 0 | 0 | 39624.44
2022070911 | 7 | 0.76284 | 61027.2 | 0.06297 | 2266.92 | 0.72843 | 8741.16 | 1 | 5000 | 2266.92 | 8741.16 | 0 | 0 | 0 | 0 | 45019.12 | 0 | 0 | 0 | 0 | 0 | 45019.12
2022070912 | 7 | 0.82207 | 65765.6 | 0.04581 | 1649.16 | 0.72115 | 8653.8 | 1 | 5000 | 1649.16 | 8653.8 | 0 | 0 | 0 | 0 | 50462.64 | 0 | 0 | 0 | 0 | 0 | 50462.64
2022070913 | 7 | 0.87246 | 69796.8 | 0.04737 | 1705.32 | 0.71286 | 8554.32 | 1 | 5000 | 1705.32 | 8554.32 | 0 | 0 | 0 | 0 | 54537.16 | 0 | 0 | 0 | 0 | 0 | 54537.16
2022070914 | 7 | 0.91594 | 73275.2 | 0.07529 | 2710.44 | 0.73646 | 8837.52 | 1 | 5000 | 2710.44 | 8837.52 | 0 | 0 | 0 | 0 | 56727.24 | 0 | 0 | 0 | 0 | 0 | 56727.24
2022070915 | 7 | 0.94621 | 75696.8 | 0.11807 | 4250.52 | 0.67194 | 8063.28 | 1 | 5000 | 4250.52 | 8063.28 | 0 | 0 | 0 | 0 | 58383 | 0 | 0 | 0 | 0 | 0 | 58383
2022070916 | 7 | 0.95858 | 76686.4 | 0.13749 | 4949.64 | 0.58432 | 7011.84 | 1 | 5000 | 4949.64 | 7011.84 | 0 | 0 | 0 | 0 | 59724.92 | 0 | 0 | 0 | 0 | 0 | 59724.92
2022070917 | 7 | 0.96773 | 77418.4 | 0.15548 | 5597.28 | 0.52693 | 6323.16 | 1 | 5000 | 5597.28 | 6323.16 | 0 | 0 | 0 | 0 | 60497.96 | 0 | 0 | 0 | 0 | 0 | 60497.96
2022070918 | 7 | 0.96894 | 77515.2 | 0.18738 | 6745.68 | 0.50111 | 6013.32 | 1 | 5000 | 6745.68 | 6013.32 | 0 | 0 | 0 | 0 | 59756.2 | 0 | 0 | 0 | 0 | 0 | 59756.2
2022070919 | 7 | 0.95664 | 76531.2 | 0.19065 | 6863.4 | 0.44086 | 5290.32 | 1 | 5000 | 6863.4 | 5290.32 | 0 | 0 | 0 | 0 | 59377.48 | 0 | 0 | 0 | 0 | 0 | 59377.48
2022070920 | 7 | 0.93566 | 74852.8 | 0.21484 | 7734.24 | 0.27865 | 3343.8 | 1 | 5000 | 7734.24 | 3343.8 | 0 | 0 | 0 | 0 | 58774.76 | 0 | 0 | 0 | 0 | 0 | 58774.76
2022070921 | 7 | 0.89541 | 71632.8 | 0.19503 | 7021.08 | 0.02889 | 346.68 | 1 | 5000 | 7021.08 | 346.68 | 0 | 0 | 0 | 0 | 59265.04 | 0 | 0 | 0 | 0 | 0 | 59265.04
2022070922 | 7 | 0.86395 | 69116 | 0.20218 | 7278.48 | 0 | 0 | 1 | 5000 | 7278.48 | 0 | 0 | 0 | 0 | 0 | 56837.52 | 0 | 0 | 0 | 0 | 0 | 56837.52
2022070923 | 7 | 0.81966 | 65572.8 | 0.20294 | 7305.84 | 0 | 0 | 1 | 5000 | 7305.84 | 0 | 0 | 0 | 0 | 0 | 53266.96 | 0 | 0 | 0 | 0 | 0 | 53266.96
2022070924 | 7 | 0.77168 | 61734.4 | 0.1816 | 6537.6 | 0 | 0 | 1 | 5000 | 6537.6 | 0 | 0 | 0 | 0 | 0 | 50196.8 | 0 | 0 | 0 | 0 | 0 | 50196.8
2022071001 | 1 | 0.72462 | 57969.6 | 0.17553 | 6319.08 | 0 | 0 | 1 | 5000 | 6319.08 | 0 | 0 | 0 | 0 | 0 | 46650.52 | 0 | 0 | 0 | 0 | 0 | 46650.52
2022071002 | 1 | 0.68334 | 54667.2 | 0.16876 | 6075.36 | 0 | 0 | 1 | 5000 | 6075.36 | 0 | 0 | 0 | 0 | 0 | 43591.84 | 0 | 0 | 0 | 0 | 0 | 43591.84
2022071003 | 1 | 0.65134 | 52107.2 | 0.15 | 5400 | 0 | 0 | 1 | 5000 | 5400 | 0 | 0 | 0 | 0 | 0 | 41707.2 | 0 | 0 | 0 | 0 | 0 | 41707.2
2022071004 | 1 | 0.62828 | 50262.4 | 0.14161 | 5097.96 | 0 | 0 | 1 | 5000 | 5097.96 | 0 | 0 | 0 | 0 | 0 | 40164.44 | 0 | 0 | 0 | 0 | 0 | 40164.44
2022071005 | 1 | 0.61077 | 48861.6 | 0.13225 | 4761 | 0 | 0 | 1 | 5000 | 4761 | 0 | 0 | 0 | 0 | 0 | 39100.6 | 0 | 0 | 0 | 0 | 0 | 39100.6
2022071006 | 1 | 0.5973 | 47784 | 0.11121 | 4003.56 | 0 | 0 | 1 | 5000 | 4003.56 | 0 | 0 | 0 | 0 | 0 | 38780.44 | 0 | 0 | 0 | 0 | 0 | 38780.44
2022071007 | 1 | 0.58795 | 47036 | 0.10228 | 3682.08 | 0.00297 | 35.64 | 1 | 5000 | 3682.08 | 35.64 | 0 | 0 | 0 | 0 | 38318.28 | 0 | 0 | 0 | 0 | 0 | 38318.28
2022071008 | 1 | 0.59058 | 47246.4 | 0.07837 | 2821.32 | 0.15365 | 1843.8 | 1 | 5000 | 2821.32 | 1843.8 | 0 | 0 | 0 | 0 | 37581.28 | 0 | 0 | 0 | 0 | 0 | 37581.28
2022071009 | 1 | 0.63027 | 50421.6 | 0.04956 | 1784.16 | 0.51121 | 6134.52 | 1 | 5000 | 1784.16 | 6134.52 | 0 | 0 | 0 | 0 | 37502.92 | 0 | 0 | 0 | 0 | 0 | 37502.92
2022071010 | 1 | 0.68868 | 55094.4 | 0.04711 | 1695.96 | 0.74565 | 8947.8 | 1 | 5000 | 1695.96 | 8947.8 | 0 | 0 | 0 | 0 | 39450.64 | 0 | 0 | 0 | 0 | 0 | 39450.64
2022071011 | 1 | 0.74924 | 59939.2 | 0.03091 | 1112.76 | 0.80382 | 9645.84 | 1 | 5000 | 1112.76 | 9645.84 | 0 | 0 | 0 | 0 | 44180.6 | 0 | 0 | 0 | 0 | 0 | 44180.6
2022071012 | 1 | 0.80945 | 64756 | 0.02256 | 812.16 | 0.80728 | 9687.36 | 1 | 5000 | 812.16 | 9687.36 | 0 | 0 | 0 | 0 | 49256.48 | 0 | 0 | 0 | 0 | 0 | 49256.48
2022071013 | 1 | 0.86553 | 69242.4 | 0.02686 | 966.96 | 0.78532 | 9423.84 | 1 | 5000 | 966.96 | 9423.84 | 0 | 0 | 0 | 0 | 53851.6 | 0 | 0 | 0 | 0 | 0 | 53851.6
2022071014 | 1 | 0.91012 | 72809.6 | 0.04021 | 1447.56 | 0.76176 | 9141.12 | 1 | 5000 | 1447.56 | 9141.12 | 0 | 0 | 0 | 0 | 57220.92 | 0 | 0 | 0 | 0 | 0 | 57220.92
2022071015 | 1 | 0.93707 | 74965.6 | 0.06071 | 2185.56 | 0.72954 | 8754.48 | 1 | 5000 | 2185.56 | 8754.48 | 0 | 0 | 0 | 0 | 59025.56 | 0 | 0 | 0 | 0 | 0 | 59025.56
2022071016 | 1 | 0.95456 | 76364.8 | 0.09042 | 3255.12 | 0.73217 | 8786.04 | 1 | 5000 | 3255.12 | 8786.04 | 0 | 0 | 0 | 0 | 59323.64 | 0 | 0 | 0 | 0 | 0 | 59323.64
2022071017 | 1 | 0.96695 | 77356 | 0.11124 | 4004.64 | 0.70548 | 8465.76 | 1 | 5000 | 4004.64 | 8465.76 | 0 | 0 | 0 | 0 | 59885.6 | 0 | 0 | 0 | 0 | 0 | 59885.6
2022071018 | 1 | 0.96811 | 77448.8 | 0.13401 | 4824.36 | 0.65883 | 7905.96 | 1 | 5000 | 4824.36 | 7905.96 | 0 | 0 | 0 | 0 | 59718.48 | 0 | 0 | 0 | 0 | 0 | 59718.48
2022071019 | 1 | 0.96014 | 76811.2 | 0.15982 | 5753.52 | 0.50718 | 6086.16 | 1 | 5000 | 5753.52 | 6086.16 | 0 | 0 | 0 | 0 | 59971.52 | 0 | 0 | 0 | 0 | 0 | 59971.52
2022071020 | 1 | 0.93783 | 75026.4 | 0.18203 | 6553.08 | 0.26338 | 3160.56 | 1 | 5000 | 6553.08 | 3160.56 | 0 | 0 | 0 | 0 | 60312.76 | 0 | 0 | 0 | 0 | 0 | 60312.76
2022071021 | 1 | 0.9025 | 72200 | 0.21483 | 7733.88 | 0.033 | 396 | 1 | 5000 | 7733.88 | 396 | 0 | 0 | 0 | 0 | 59070.12 | 0 | 0 | 0 | 0 | 0 | 59070.12
2022071022 | 1 | 0.87127 | 69701.6 | 0.25899 | 9323.64 | 0 | 0 | 1 | 5000 | 9323.64 | 0 | 0 | 0 | 0 | 0 | 55377.96 | 0 | 0 | 0 | 0 | 0 | 55377.96
2022071023 | 1 | 0.82373 | 65898.4 | 0.31695 | 11410.2 | 0 | 0 | 1 | 5000 | 11410.2 | 0 | 0 | 0 | 0 | 0 | 49488.2 | 0 | 0 | 0 | 0 | 0 | 49488.2
2022071024 | 1 | 0.77023 | 61618.4 | 0.3363 | 12106.8 | 0 | 0 | 1 | 5000 | 12106.8 | 0 | 0 | 0 | 0 | 0 | 44511.6 | 0 | 0 | 0 | 0 | 0 | 44511.6
2022071101 | 2 | 0.72377 | 57901.6 | 0.33218 | 11958.48 | 0 | 0 | 1 | 5000 | 11958.48 | 0 | 0 | 0 | 0 | 0 | 40943.12 | 0 | 0 | 0 | 0 | 0 | 40943.12
2022071102 | 2 | 0.68808 | 55046.4 | 0.31257 | 11252.52 | 0 | 0 | 1 | 5000 | 11252.52 | 0 | 0 | 0 | 0 | 0 | 38793.88 | 0 | 0 | 0 | 0 | 0 | 38793.88
2022071103 | 2 | 0.65932 | 52745.6 | 0.27409 | 9867.24 | 0 | 0 | 1 | 5000 | 9867.24 | 0 | 0 | 0 | 0 | 0 | 37878.36 | 0 | 0 | 0 | 0 | 0 | 37878.36
2022071104 | 2 | 0.64396 | 51516.8 | 0.21917 | 7890.12 | 0 | 0 | 1 | 5000 | 7890.12 | 0 | 0 | 0 | 0 | 0 | 38626.68 | 0 | 0 | 0 | 0 | 0 | 38626.68
2022071105 | 2 | 0.63528 | 50822.4 | 0.19097 | 6874.92 | 0 | 0 | 1 | 5000 | 6874.92 | 0 | 0 | 0 | 0 | 0 | 38947.48 | 0 | 0 | 0 | 0 | 0 | 38947.48
2022071106 | 2 | 0.63772 | 51017.6 | 0.16866 | 6071.76 | 0 | 0 | 1 | 5000 | 6071.76 | 0 | 0 | 0 | 0 | 0 | 39945.84 | 0 | 0 | 0 | 0 | 0 | 39945.84
2022071107 | 2 | 0.64199 | 51359.2 | 0.13827 | 4977.72 | 0.00202 | 24.24 | 1 | 5000 | 4977.72 | 24.24 | 0 | 0 | 0 | 0 | 41357.24 | 0 | 0 | 0 | 0 | 0 | 41357.24
2022071108 | 2 | 0.65304 | 52243.2 | 0.10387 | 3739.32 | 0.13877 | 1665.24 | 1 | 5000 | 3739.32 | 1665.24 | 0 | 0 | 0 | 0 | 41838.64 | 0 | 0 | 0 | 0 | 0 | 41838.64
2022071109 | 2 | 0.68532 | 54825.6 | 0.07091 | 2552.76 | 0.49658 | 5958.96 | 1 | 5000 | 2552.76 | 5958.96 | 0 | 0 | 0 | 0 | 41313.88 | 0 | 0 | 0 | 0 | 0 | 41313.88
2022071110 | 2 | 0.73465 | 58772 | 0.07458 | 2684.88 | 0.70121 | 8414.52 | 1 | 5000 | 2684.88 | 8414.52 | 0 | 0 | 0 | 0 | 42672.6 | 0 | 0 | 0 | 0 | 0 | 42672.6
2022071111 | 2 | 0.79548 | 63638.4 | 0.05393 | 1941.48 | 0.77295 | 9275.4 | 1 | 5000 | 1941.48 | 9275.4 | 0 | 0 | 0 | 0 | 47421.52 | 0 | 0 | 0 | 0 | 0 | 47421.52
2022071112 | 2 | 0.8569 | 68552 | 0.02984 | 1074.24 | 0.79148 | 9497.76 | 1 | 5000 | 1074.24 | 9497.76 | 0 | 0 | 0 | 0 | 52980 | 0 | 0 | 0 | 0 | 0 | 52980
2022071113 | 2 | 0.90616 | 72492.8 | 0.02095 | 754.2 | 0.78803 | 9456.36 | 1 | 5000 | 754.2 | 9456.36 | 0 | 0 | 0 | 0 | 57282.24 | 0 | 0 | 0 | 0 | 0 | 57282.24
2022071114 | 2 | 0.94187 | 75349.6 | 0.04292 | 1545.12 | 0.76712 | 9205.44 | 1 | 5000 | 1545.12 | 9205.44 | 0 | 0 | 0 | 0 | 59599.04 | 0 | 0 | 0 | 0 | 0 | 59599.04
2022071115 | 2 | 0.96724 | 77379.2 | 0.08581 | 3089.16 | 0.77612 | 9313.44 | 1 | 5000 | 3089.16 | 9313.44 | 0 | 0 | 0 | 0 | 59976.6 | 0 | 0 | 0 | 0 | 0 | 59976.6
2022071116 | 2 | 0.97704 | 78163.2 | 0.13466 | 4847.76 | 0.75392 | 9047.04 | 1 | 5000 | 4847.76 | 9047.04 | 0 | 0 | 0 | 0 | 59268.4 | 0 | 0 | 0 | 0 | 0 | 59268.4
2022071117 | 2 | 0.9804 | 78432 | 0.17614 | 6341.04 | 0.7237 | 8684.4 | 1 | 5000 | 6341.04 | 8684.4 | 0 | 0 | 0 | 0 | 58406.56 | 0 | 0 | 0 | 0 | 0 | 58406.56
2022071118 | 2 | 0.97731 | 78184.8 | 0.20447 | 7360.92 | 0.68586 | 8230.32 | 1 | 5000 | 7360.92 | 8230.32 | 0 | 0 | 0 | 0 | 57593.56 | 0 | 0 | 0 | 0 | 0 | 57593.56
2022071119 | 2 | 0.97124 | 77699.2 | 0.23879 | 8596.44 | 0.61291 | 7354.92 | 1 | 5000 | 8596.44 | 7354.92 | 0 | 0 | 0 | 0 | 56747.84 | 0 | 0 | 0 | 0 | 0 | 56747.84
2022071120 | 2 | 0.94954 | 75963.2 | 0.28286 | 10182.96 | 0.36462 | 4375.44 | 1 | 5000 | 10182.96 | 4375.44 | 0 | 0 | 0 | 0 | 56404.8 | 0 | 0 | 0 | 0 | 0 | 56404.8
2022071121 | 2 | 0.91257 | 73005.6 | 0.28847 | 10384.92 | 0.05129 | 615.48 | 1 | 5000 | 10384.92 | 615.48 | 0 | 0 | 0 | 0 | 57005.2 | 0 | 0 | 0 | 0 | 0 | 57005.2
2022071122 | 2 | 0.87918 | 70334.4 | 0.33509 | 12063.24 | 0 | 0 | 1 | 5000 | 12063.24 | 0 | 0 | 0 | 0 | 0 | 53271.16 | 0 | 0 | 0 | 0 | 0 | 53271.16
2022071123 | 2 | 0.82939 | 66351.2 | 0.39258 | 14132.88 | 0 | 0 | 1 | 5000 | 14132.88 | 0 | 0 | 0 | 0 | 0 | 47218.32 | 0 | 0 | 0 | 0 | 0 | 47218.32
2022071124 | 2 | 0.77389 | 61911.2 | 0.40698 | 14651.28 | 0 | 0 | 1 | 5000 | 14651.28 | 0 | 0 | 0 | 0 | 0 | 42259.92 | 0 | 0 | 0 | 0 | 0 | 42259.92
2022071201 | 3 | 0.72646 | 58116.8 | 0.40404 | 14545.44 | 0 | 0 | 1 | 5000 | 14545.44 | 0 | 0 | 0 | 0 | 0 | 38571.36 | 0 | 0 | 0 | 0 | 0 | 38571.36
2022071202 | 3 | 0.68586 | 54868.8 | 0.37837 | 13621.32 | 0 | 0 | 1 | 5000 | 13621.32 | 0 | 0 | 0 | 0 | 0 | 36247.48 | 0 | 0 | 0 | 0 | 0 | 36247.48
2022071203 | 3 | 0.65539 | 52431.2 | 0.34369 | 12372.84 | 0 | 0 | 1 | 5000 | 12372.84 | 0 | 0 | 0 | 0 | 0 | 35058.36 | 0 | 0 | 0 | 0 | 0 | 35058.36
2022071204 | 3 | 0.63564 | 50851.2 | 0.30103 | 10837.08 | 0 | 0 | 1 | 5000 | 10837.08 | 0 | 0 | 0 | 0 | 0 | 35014.12 | 0 | 0 | 0 | 0 | 0 | 35014.12
2022071205 | 3 | 0.62567 | 50053.6 | 0.26332 | 9479.52 | 0 | 0 | 1 | 5000 | 9479.52 | 0 | 0 | 0 | 0 | 0 | 35574.08 | 0 | 0 | 0 | 0 | 0 | 35574.08
2022071206 | 3 | 0.62714 | 50171.2 | 0.25155 | 9055.8 | 0 | 0 | 1 | 5000 | 9055.8 | 0 | 0 | 0 | 0 | 0 | 36115.4 | 0 | 0 | 0 | 0 | 0 | 36115.4
2022071207 | 3 | 0.63311 | 50648.8 | 0.22488 | 8095.68 | 0.00246 | 29.52 | 1 | 5000 | 8095.68 | 29.52 | 0 | 0 | 0 | 0 | 37523.6 | 0 | 0 | 0 | 0 | 0 | 37523.6
2022071208 | 3 | 0.64536 | 51628.8 | 0.20768 | 7476.48 | 0.12432 | 1491.84 | 1 | 5000 | 7476.48 | 1491.84 | 0 | 0 | 0 | 0 | 37660.48 | 0 | 0 | 0 | 0 | 0 | 37660.48
2022071209 | 3 | 0.67991 | 54392.8 | 0.19833 | 7139.88 | 0.45294 | 5435.28 | 1 | 5000 | 7139.88 | 5435.28 | 0 | 0 | 0 | 0 | 36817.64 | 0 | 0 | 0 | 0 | 0 | 36817.64
2022071210 | 3 | 0.73195 | 58556 | 0.19232 | 6923.52 | 0.68346 | 8201.52 | 1 | 5000 | 6923.52 | 8201.52 | 0 | 0 | 0 | 0 | 38430.96 | 0 | 0 | 0 | 0 | 0 | 38430.96
2022071211 | 3 | 0.79326 | 63460.8 | 0.17351 | 6246.36 | 0.73555 | 8826.6 | 1 | 5000 | 6246.36 | 8826.6 | 0 | 0 | 0 | 0 | 43387.84 | 0 | 0 | 0 | 0 | 0 | 43387.84
2022071212 | 3 | 0.85197 | 68157.6 | 0.20826 | 7497.36 | 0.77608 | 9312.96 | 1 | 5000 | 7497.36 | 9312.96 | 0 | 0 | 0 | 0 | 46347.28 | 0 | 0 | 0 | 0 | 0 | 46347.28
2022071213 | 3 | 0.90358 | 72286.4 | 0.24574 | 8846.64 | 0.75216 | 9025.92 | 1 | 5000 | 8846.64 | 9025.92 | 0 | 0 | 0 | 0 | 49413.84 | 0 | 0 | 0 | 0 | 0 | 49413.84
2022071214 | 3 | 0.94866 | 75892.8 | 0.24724 | 8900.64 | 0.72748 | 8729.76 | 1 | 5000 | 8900.64 | 8729.76 | 0 | 0 | 0 | 0 | 53262.4 | 0 | 0 | 0 | 0 | 0 | 53262.4
2022071215 | 3 | 0.97171 | 77736.8 | 0.22807 | 8210.52 | 0.71397 | 8567.64 | 1 | 5000 | 8210.52 | 8567.64 | 0 | 0 | 0 | 0 | 55958.64 | 0 | 0 | 0 | 0 | 0 | 55958.64
2022071216 | 3 | 0.9799 | 78392 | 0.23734 | 8544.24 | 0.66096 | 7931.52 | 1 | 5000 | 8544.24 | 7931.52 | 0 | 0 | 0 | 0 | 56916.24 | 0 | 0 | 0 | 0 | 0 | 56916.24
2022071217 | 3 | 0.98212 | 78569.6 | 0.26055 | 9379.8 | 0.63181 | 7581.72 | 1 | 5000 | 9379.8 | 7581.72 | 0 | 0 | 0 | 0 | 56608.08 | 0 | 0 | 0 | 0 | 0 | 56608.08
2022071218 | 3 | 0.97269 | 77815.2 | 0.28776 | 10359.36 | 0.55667 | 6680.04 | 1 | 5000 | 10359.36 | 6680.04 | 0 | 0 | 0 | 0 | 55775.8 | 0 | 0 | 0 | 0 | 0 | 55775.8
2022071219 | 3 | 0.95595 | 76476 | 0.32427 | 11673.72 | 0.45069 | 5408.28 | 1 | 5000 | 11673.72 | 5408.28 | 0 | 0 | 0 | 0 | 54394 | 0 | 0 | 0 | 0 | 0 | 54394
2022071220 | 3 | 0.92855 | 74284 | 0.32516 | 11705.76 | 0.27929 | 3351.48 | 1 | 5000 | 11705.76 | 3351.48 | 0 | 0 | 0 | 0 | 54226.76 | 0 | 0 | 0 | 0 | 0 | 54226.76
2022071221 | 3 | 0.89328 | 71462.4 | 0.29194 | 10509.84 | 0.04931 | 591.72 | 1 | 5000 | 10509.84 | 591.72 | 0 | 0 | 0 | 0 | 55360.84 | 0 | 0 | 0 | 0 | 0 | 55360.84
2022071222 | 3 | 0.86245 | 68996 | 0.26681 | 9605.16 | 0.00428 | 51.36 | 1 | 5000 | 9605.16 | 51.36 | 0 | 0 | 0 | 0 | 54339.48 | 0 | 0 | 0 | 0 | 0 | 54339.48
2022071223 | 3 | 0.81059 | 64847.2 | 0.27147 | 9772.92 | 0 | 0 | 1 | 5000 | 9772.92 | 0 | 0 | 0 | 0 | 0 | 50074.28 | 0 | 0 | 0 | 0 | 0 | 50074.28
2022071224 | 3 | 0.75644 | 60515.2 | 0.25147 | 9052.92 | 0 | 0 | 1 | 5000 | 9052.92 | 0 | 0 | 0 | 0 | 0 | 46462.28 | 0 | 0 | 0 | 0 | 0 | 46462.28
2022071301 | 4 | 0.70591 | 56472.8 | 0.23276 | 8379.36 | 0 | 0 | 1 | 5000 | 8379.36 | 0 | 0 | 0 | 0 | 0 | 43093.44 | 0 | 0 | 0 | 0 | 0 | 43093.44
2022071302 | 4 | 0.66603 | 53282.4 | 0.19553 | 7039.08 | 0 | 0 | 1 | 5000 | 7039.08 | 0 | 0 | 0 | 0 | 0 | 41243.32 | 0 | 0 | 0 | 0 | 0 | 41243.32
2022071303 | 4 | 0.63529 | 50823.2 | 0.17294 | 6225.84 | 0 | 0 | 1 | 5000 | 6225.84 | 0 | 0 | 0 | 0 | 0 | 39597.36 | 0 | 0 | 0 | 0 | 0 | 39597.36
2022071304 | 4 | 0.61588 | 49270.4 | 0.1436 | 5169.6 | 0 | 0 | 1 | 5000 | 5169.6 | 0 | 0 | 0 | 0 | 0 | 39100.8 | 0 | 0 | 0 | 0 | 0 | 39100.8
2022071305 | 4 | 0.60781 | 48624.8 | 0.11862 | 4270.32 | 0 | 0 | 1 | 5000 | 4270.32 | 0 | 0 | 0 | 0 | 0 | 39354.48 | 0 | 0 | 0 | 0 | 0 | 39354.48
2022071306 | 4 | 0.61028 | 48822.4 | 0.10882 | 3917.52 | 0 | 0 | 1 | 5000 | 3917.52 | 0 | 0 | 0 | 0 | 0 | 39904.88 | 0 | 0 | 0 | 0 | 0 | 39904.88
2022071307 | 4 | 0.62341 | 49872.8 | 0.09618 | 3462.48 | 0.00207 | 24.84 | 1 | 5000 | 3462.48 | 24.84 | 0 | 0 | 0 | 0 | 41385.48 | 0 | 0 | 0 | 0 | 0 | 41385.48
2022071308 | 4 | 0.63327 | 50661.6 | 0.07341 | 2642.76 | 0.1214 | 1456.8 | 1 | 5000 | 2642.76 | 1456.8 | 0 | 0 | 0 | 0 | 41562.04 | 0 | 0 | 0 | 0 | 0 | 41562.04
2022071309 | 4 | 0.67024 | 53619.2 | 0.0449 | 1616.4 | 0.4647 | 5576.4 | 1 | 5000 | 1616.4 | 5576.4 | 0 | 0 | 0 | 0 | 41426.4 | 0 | 0 | 0 | 0 | 0 | 41426.4
2022071310 | 4 | 0.72112 | 57689.6 | 0.03761 | 1353.96 | 0.66964 | 8035.68 | 1 | 5000 | 1353.96 | 8035.68 | 0 | 0 | 0 | 0 | 43299.96 | 0 | 0 | 0 | 0 | 0 | 43299.96
2022071311 | 4 | 0.78458 | 62766.4 | 0.02866 | 1031.76 | 0.75817 | 9098.04 | 1 | 5000 | 1031.76 | 9098.04 | 0 | 0 | 0 | 0 | 47636.6 | 0 | 0 | 0 | 0 | 0 | 47636.6
2022071312 | 4 | 0.84643 | 67714.4 | 0.01957 | 704.52 | 0.77103 | 9252.36 | 1 | 5000 | 704.52 | 9252.36 | 0 | 0 | 0 | 0 | 52757.52 | 0 | 0 | 0 | 0 | 0 | 52757.52
2022071313 | 4 | 0.89715 | 71772 | 0.01978 | 712.08 | 0.76037 | 9124.44 | 1 | 5000 | 712.08 | 9124.44 | 0 | 0 | 0 | 0 | 56935.48 | 0 | 0 | 0 | 0 | 0 | 56935.48
2022071314 | 4 | 0.93759 | 75007.2 | 0.05657 | 2036.52 | 0.74919 | 8990.28 | 1 | 5000 | 2036.52 | 8990.28 | 0 | 0 | 0 | 0 | 58980.4 | 0 | 0 | 0 | 0 | 0 | 58980.4
2022071315 | 4 | 0.96656 | 77324.8 | 0.11114 | 4001.04 | 0.68035 | 8164.2 | 1 | 5000 | 4001.04 | 8164.2 | 0 | 0 | 0 | 0 | 60159.56 | 0 | 0 | 0 | 0 | 0 | 60159.56
2022071316 | 4 | 0.97714 | 78171.2 | 0.15085 | 5430.6 | 0.57508 | 6900.96 | 1 | 5000 | 5430.6 | 6900.96 | 0 | 0 | 0 | 0 | 60839.64 | 0 | 0 | 0 | 0 | 0 | 60839.64
2022071317 | 4 | 0.98074 | 78459.2 | 0.18962 | 6826.32 | 0.51932 | 6231.84 | 1 | 5000 | 6826.32 | 6231.84 | 0 | 0 | 0 | 0 | 60401.04 | 0 | 0 | 0 | 0 | 0 | 60401.04
2022071318 | 4 | 0.97347 | 77877.6 | 0.21638 | 7789.68 | 0.40999 | 4919.88 | 1 | 5000 | 7789.68 | 4919.88 | 0 | 0 | 0 | 0 | 60168.04 | 0 | 0 | 0 | 0 | 0 | 60168.04
2022071319 | 4 | 0.95556 | 76444.8 | 0.2241 | 8067.6 | 0.30974 | 3716.88 | 1 | 5000 | 8067.6 | 3716.88 | 0 | 0 | 0 | 0 | 59660.32 | 0 | 0 | 0 | 0 | 0 | 59660.32
2022071320 | 4 | 0.93276 | 74620.8 | 0.25436 | 9156.96 | 0.16207 | 1944.84 | 1 | 5000 | 9156.96 | 1944.84 | 0 | 0 | 0 | 0 | 58519 | 0 | 0 | 0 | 0 | 0 | 58519
2022071321 | 4 | 0.90176 | 72140.8 | 0.23959 | 8625.24 | 0.01996 | 239.52 | 1 | 5000 | 8625.24 | 239.52 | 0 | 0 | 0 | 0 | 58276.04 | 0 | 0 | 0 | 0 | 0 | 58276.04
2022071322 | 4 | 0.87426 | 69940.8 | 0.26226 | 9441.36 | 0 | 0 | 1 | 5000 | 9441.36 | 0 | 0 | 0 | 0 | 0 | 55499.44 | 0 | 0 | 0 | 0 | 0 | 55499.44
2022071323 | 4 | 0.82621 | 66096.8 | 0.31602 | 11376.72 | 0 | 0 | 1 | 5000 | 11376.72 | 0 | 0 | 0 | 0 | 0 | 49720.08 | 0 | 0 | 0 | 0 | 0 | 49720.08
2022071324 | 4 | 0.77279 | 61823.2 | 0.30399 | 10943.64 | 0 | 0 | 1 | 5000 | 10943.64 | 0 | 0 | 0 | 0 | 0 | 45879.56 | 0 | 0 | 0 | 0 | 0 | 45879.56
2022071401 | 5 | 0.72478 | 57982.4 | 0.28766 | 10355.76 | 0 | 0 | 1 | 5000 | 10355.76 | 0 | 0 | 0 | 0 | 0 | 42626.64 | 0 | 0 | 0 | 0 | 0 | 42626.64
2022071402 | 5 | 0.6857 | 54856 | 0.23207 | 8354.52 | 0 | 0 | 1 | 5000 | 8354.52 | 0 | 0 | 0 | 0 | 0 | 41501.48 | 0 | 0 | 0 | 0 | 0 | 41501.48
2022071403 | 5 | 0.65491 | 52392.8 | 0.20879 | 7516.44 | 0 | 0 | 1 | 5000 | 7516.44 | 0 | 0 | 0 | 0 | 0 | 39876.36 | 0 | 0 | 0 | 0 | 0 | 39876.36
2022071404 | 5 | 0.63614 | 50891.2 | 0.20884 | 7518.24 | 0 | 0 | 1 | 5000 | 7518.24 | 0 | 0 | 0 | 0 | 0 | 38372.96 | 0 | 0 | 0 | 0 | 0 | 38372.96
2022071405 | 5 | 0.62413 | 49930.4 | 0.21144 | 7611.84 | 0 | 0 | 1 | 5000 | 7611.84 | 0 | 0 | 0 | 0 | 0 | 37318.56 | 0 | 0 | 0 | 0 | 0 | 37318.56
2022071406 | 5 | 0.62562 | 50049.6 | 0.19378 | 6976.08 | 0 | 0 | 1 | 5000 | 6976.08 | 0 | 0 | 0 | 0 | 0 | 38073.52 | 0 | 0 | 0 | 0 | 0 | 38073.52
2022071407 | 5 | 0.63324 | 50659.2 | 0.20284 | 7302.24 | 0.00095 | 11.4 | 1 | 5000 | 7302.24 | 11.4 | 0 | 0 | 0 | 0 | 38345.56 | 0 | 0 | 0 | 0 | 0 | 38345.56
2022071408 | 5 | 0.64274 | 51419.2 | 0.19356 | 6968.16 | 0.09902 | 1188.24 | 1 | 5000 | 6968.16 | 1188.24 | 0 | 0 | 0 | 0 | 38262.8 | 0 | 0 | 0 | 0 | 0 | 38262.8
2022071409 | 5 | 0.67299 | 53839.2 | 0.12827 | 4617.72 | 0.48381 | 5805.72 | 1 | 5000 | 4617.72 | 5805.72 | 0 | 0 | 0 | 0 | 38415.76 | 0 | 0 | 0 | 0 | 0 | 38415.76
2022071410 | 5 | 0.7186 | 57488 | 0.10833 | 3899.88 | 0.69757 | 8370.84 | 1 | 5000 | 3899.88 | 8370.84 | 0 | 0 | 0 | 0 | 40217.28 | 0 | 0 | 0 | 0 | 0 | 40217.28
2022071411 | 5 | 0.76865 | 61492 | 0.09088 | 3271.68 | 0.75234 | 9028.08 | 1 | 5000 | 3271.68 | 9028.08 | 0 | 0 | 0 | 0 | 44192.24 | 0 | 0 | 0 | 0 | 0 | 44192.24
2022071412 | 5 | 0.81106 | 64884.8 | 0.06885 | 2478.6 | 0.74071 | 8888.52 | 1 | 5000 | 2478.6 | 8888.52 | 0 | 0 | 0 | 0 | 48517.68 | 0 | 0 | 0 | 0 | 0 | 48517.68
2022071413 | 5 | 0.84283 | 67426.4 | 0.08286 | 2982.96 | 0.73038 | 8764.56 | 1 | 5000 | 2982.96 | 8764.56 | 0 | 0 | 0 | 0 | 50678.88 | 0 | 0 | 0 | 0 | 0 | 50678.88
2022071414 | 5 | 0.86022 | 68817.6 | 0.1098 | 3952.8 | 0.70842 | 8501.04 | 1 | 5000 | 3952.8 | 8501.04 | 0 | 0 | 0 | 0 | 51363.76 | 0 | 0 | 0 | 0 | 0 | 51363.76
2022071415 | 5 | 0.86837 | 69469.6 | 0.17533 | 6311.88 | 0.64849 | 7781.88 | 1 | 5000 | 6311.88 | 7781.88 | 0 | 0 | 0 | 0 | 50375.84 | 0 | 0 | 0 | 0 | 0 | 50375.84
2022071416 | 5 | 0.87392 | 69913.6 | 0.24914 | 8969.04 | 0.61463 | 7375.56 | 1 | 5000 | 8969.04 | 7375.56 | 0 | 0 | 0 | 0 | 48569 | 0 | 0 | 0 | 0 | 0 | 48569
2022071417 | 5 | 0.87971 | 70376.8 | 0.33551 | 12078.36 | 0.57725 | 6927 | 1 | 5000 | 12078.36 | 6927 | 0 | 0 | 0 | 0 | 46371.44 | 0 | 0 | 0 | 0 | 0 | 46371.44
2022071418 | 5 | 0.8684 | 69472 | 0.40263 | 14494.68 | 0.57424 | 6890.88 | 1 | 5000 | 14494.68 | 6890.88 | 0 | 0 | 0 | 0 | 43086.44 | 0 | 0 | 0 | 0 | 0 | 43086.44
2022071419 | 5 | 0.84254 | 67403.2 | 0.4256 | 15321.6 | 0.43748 | 5249.76 | 1 | 5000 | 15321.6 | 5249.76 | 0 | 0 | 0 | 0 | 41831.84 | 0 | 0 | 0 | 0 | 0 | 41831.84
2022071420 | 5 | 0.80672 | 64537.6 | 0.41142 | 14811.12 | 0.18752 | 2250.24 | 1 | 5000 | 14811.12 | 2250.24 | 0 | 0 | 0 | 0 | 42476.24 | 0 | 0 | 0 | 0 | 0 | 42476.24
2022071421 | 5 | 0.77647 | 62117.6 | 0.41149 | 14813.64 | 0.03248 | 389.76 | 1 | 5000 | 14813.64 | 389.76 | 0 | 0 | 0 | 0 | 41914.2 | 0 | 0 | 0 | 0 | 0 | 41914.2
2022071422 | 5 | 0.75307 | 60245.6 | 0.42933 | 15455.88 | 0 | 0 | 1 | 5000 | 15455.88 | 0 | 0 | 0 | 0 | 0 | 39789.72 | 0 | 0 | 0 | 0 | 0 | 39789.72
2022071423 | 5 | 0.70986 | 56788.8 | 0.4109 | 14792.4 | 0 | 0 | 1 | 5000 | 14792.4 | 0 | 0 | 0 | 0 | 0 | 36996.4 | 0 | 0 | 0 | 0 | 0 | 36996.4
2022071424 | 5 | 0.66233 | 52986.4 | 0.34464 | 12407.04 | 0 | 0 | 1 | 5000 | 12407.04 | 0 | 0 | 0 | 0 | 0 | 35579.36 | 0 | 0 | 0 | 0 | 0 | 35579.36
2022071501 | 6 | 0.61949 | 49559.2 | 0.26629 | 9586.44 | 0 | 0 | 1 | 5000 | 9586.44 | 0 | 0 | 0 | 0 | 0 | 34972.76 | 0 | 0 | 0 | 0 | 0 | 34972.76
2022071502 | 6 | 0.58742 | 46993.6 | 0.203 | 7308 | 0 | 0 | 1 | 5000 | 7308 | 0 | 0 | 0 | 0 | 0 | 34685.6 | 0 | 0 | 0 | 0 | 0 | 34685.6
2022071503 | 6 | 0.56427 | 45141.6 | 0.16754 | 6031.44 | 0 | 0 | 1 | 5000 | 6031.44 | 0 | 0 | 0 | 0 | 0 | 34110.16 | 0 | 0 | 0 | 0 | 0 | 34110.16
2022071504 | 6 | 0.54885 | 43908 | 0.17341 | 6242.76 | 0 | 0 | 1 | 5000 | 6242.76 | 0 | 0 | 0 | 0 | 0 | 32665.24 | 0 | 0 | 0 | 0 | 0 | 32665.24
2022071505 | 6 | 0.54436 | 43548.8 | 0.15846 | 5704.56 | 0 | 0 | 1 | 5000 | 5704.56 | 0 | 0 | 0 | 0 | 0 | 32844.24 | 0 | 0 | 0 | 0 | 0 | 32844.24
2022071506 | 6 | 0.55117 | 44093.6 | 0.16131 | 5807.16 | 0 | 0 | 1 | 5000 | 5807.16 | 0 | 0 | 0 | 0 | 0 | 33286.44 | 0 | 0 | 0 | 0 | 0 | 33286.44
2022071507 | 6 | 0.56232 | 44985.6 | 0.13648 | 4913.28 | 0.00221 | 26.52 | 1 | 5000 | 4913.28 | 26.52 | 0 | 0 | 0 | 0 | 35045.8 | 0 | 0 | 0 | 0 | 0 | 35045.8
2022071508 | 6 | 0.57909 | 46327.2 | 0.10672 | 3841.92 | 0.15624 | 1874.88 | 1 | 5000 | 3841.92 | 1874.88 | 0 | 0 | 0 | 0 | 35610.4 | 0 | 0 | 0 | 0 | 0 | 35610.4
2022071509 | 6 | 0.61738 | 49390.4 | 0.05883 | 2117.88 | 0.57058 | 6846.96 | 1 | 5000 | 2117.88 | 6846.96 | 0 | 0 | 0 | 0 | 35425.56 | 0 | 0 | 0 | 0 | 0 | 35425.56
2022071510 | 6 | 0.66493 | 53194.4 | 0.05839 | 2102.04 | 0.74331 | 8919.72 | 1 | 5000 | 2102.04 | 8919.72 | 0 | 0 | 0 | 0 | 37172.64 | 0 | 0 | 0 | 0 | 0 | 37172.64
2022071511 | 6 | 0.71835 | 57468 | 0.0738 | 2656.8 | 0.76437 | 9172.44 | 1 | 5000 | 2656.8 | 9172.44 | 0 | 0 | 0 | 0 | 40638.76 | 0 | 0 | 0 | 0 | 0 | 40638.76
2022071512 | 6 | 0.77216 | 61772.8 | 0.08055 | 2899.8 | 0.76179 | 9141.48 | 1 | 5000 | 2899.8 | 9141.48 | 0 | 0 | 0 | 0 | 44731.52 | 0 | 0 | 0 | 0 | 0 | 44731.52
2022071513 | 6 | 0.81736 | 65388.8 | 0.08659 | 3117.24 | 0.76881 | 9225.72 | 1 | 5000 | 3117.24 | 9225.72 | 0 | 0 | 0 | 0 | 48045.84 | 0 | 0 | 0 | 0 | 0 | 48045.84
2022071514 | 6 | 0.84968 | 67974.4 | 0.08919 | 3210.84 | 0.76585 | 9190.2 | 1 | 5000 | 3210.84 | 9190.2 | 0 | 0 | 0 | 0 | 50573.36 | 0 | 0 | 0 | 0 | 0 | 50573.36
2022071515 | 6 | 0.86873 | 69498.4 | 0.1008 | 3628.8 | 0.77388 | 9286.56 | 1 | 5000 | 3628.8 | 9286.56 | 0 | 0 | 0 | 0 | 51583.04 | 0 | 0 | 0 | 0 | 0 | 51583.04
2022071516 | 6 | 0.87262 | 69809.6 | 0.11365 | 4091.4 | 0.73744 | 8849.28 | 1 | 5000 | 4091.4 | 8849.28 | 0 | 0 | 0 | 0 | 51868.92 | 0 | 0 | 0 | 0 | 0 | 51868.92
2022071517 | 6 | 0.87695 | 70156 | 0.1287 | 4633.2 | 0.69926 | 8391.12 | 1 | 5000 | 4633.2 | 8391.12 | 0 | 0 | 0 | 0 | 52131.68 | 0 | 0 | 0 | 0 | 0 | 52131.68
2022071518 | 6 | 0.87482 | 69985.6 | 0.13846 | 4984.56 | 0.70057 | 8406.84 | 1 | 5000 | 4984.56 | 8406.84 | 0 | 0 | 0 | 0 | 51594.2 | 0 | 0 | 0 | 0 | 0 | 51594.2
2022071519 | 6 | 0.85655 | 68524 | 0.17182 | 6185.52 | 0.65328 | 7839.36 | 1 | 5000 | 6185.52 | 7839.36 | 0 | 0 | 0 | 0 | 49499.12 | 0 | 0 | 0 | 0 | 0 | 49499.12
2022071520 | 6 | 0.83177 | 66541.6 | 0.22836 | 8220.96 | 0.38122 | 4574.64 | 1 | 5000 | 8220.96 | 4574.64 | 0 | 0 | 0 | 0 | 48746 | 0 | 0 | 0 | 0 | 0 | 48746
2022071521 | 6 | 0.80147 | 64117.6 | 0.27026 | 9729.36 | 0.05197 | 623.64 | 1 | 5000 | 9729.36 | 623.64 | 0 | 0 | 0 | 0 | 48764.6 | 0 | 0 | 0 | 0 | 0 | 48764.6
2022071522 | 6 | 0.77548 | 62038.4 | 0.33748 | 12149.28 | 0 | 0 | 1 | 5000 | 12149.28 | 0 | 0 | 0 | 0 | 0 | 44889.12 | 0 | 0 | 0 | 0 | 0 | 44889.12
2022071523 | 6 | 0.73298 | 58638.4 | 0.42876 | 15435.36 | 0 | 0 | 1 | 5000 | 15435.36 | 0 | 0 | 0 | 0 | 0 | 38203.04 | 0 | 0 | 0 | 0 | 0 | 38203.04
2022071524 | 6 | 0.68923 | 55138.4 | 0.47262 | 17014.32 | 0 | 0 | 1 | 5000 | 17014.32 | 0 | 0 | 0 | 0 | 0 | 33124.08 | 0 | 0 | 0 | 0 | 0 | 33124.08
2022071601 | 7 | 0.64898 | 51918.4 | 0.48275 | 17379 | 0 | 0 | 1 | 5000 | 17379 | 0 | 0 | 0 | 0 | 0 | 29539.4 | 0 | 0 | 0 | 0 | 0 | 29539.4
2022071602 | 7 | 0.61596 | 49276.8 | 0.46894 | 16881.84 | 0 | 0 | 1 | 5000 | 16881.84 | 0 | 0 | 0 | 0 | 0 | 27394.96 | 0 | 0 | 0 | 0 | 0 | 27394.96
2022071603 | 7 | 0.59022 | 47217.6 | 0.45099 | 16235.64 | 0 | 0 | 1 | 5000 | 16235.64 | 0 | 0 | 0 | 0 | 0 | 25981.96 | 0 | 0 | 0 | 0 | 0 | 25981.96
2022071604 | 7 | 0.57556 | 46044.8 | 0.42173 | 15182.28 | 0 | 0 | 1 | 5000 | 15182.28 | 0 | 0 | 0 | 0 | 0 | 25862.52 | 0 | 0 | 0 | 0 | 0 | 25862.52
2022071605 | 7 | 0.56095 | 44876 | 0.37336 | 13440.96 | 0 | 0 | 1 | 5000 | 13440.96 | 0 | 0 | 0 | 0 | 0 | 26435.04 | 0 | 0 | 0 | 0 | 0 | 26435.04
2022071606 | 7 | 0.55645 | 44516 | 0.33194 | 11949.84 | 0 | 0 | 1 | 5000 | 11949.84 | 0 | 0 | 0 | 0 | 0 | 27566.16 | 0 | 0 | 0 | 0 | 0 | 27566.16
2022071607 | 7 | 0.55462 | 44369.6 | 0.2961 | 10659.6 | 0.00219 | 26.28 | 1 | 5000 | 10659.6 | 26.28 | 0 | 0 | 0 | 0 | 28683.72 | 0 | 0 | 0 | 0 | 0 | 28683.72
2022071608 | 7 | 0.56422 | 45137.6 | 0.25039 | 9014.04 | 0.15309 | 1837.08 | 1 | 5000 | 9014.04 | 1837.08 | 0 | 0 | 0 | 0 | 29286.48 | 0 | 0 | 0 | 0 | 0 | 29286.48
2022071609 | 7 | 0.60463 | 48370.4 | 0.16186 | 5826.96 | 0.5772 | 6926.4 | 1 | 5000 | 5826.96 | 6926.4 | 0 | 0 | 0 | 0 | 30617.04 | 0 | 0 | 0 | 0 | 0 | 30617.04
2022071610 | 7 | 0.65659 | 52527.2 | 0.16061 | 5781.96 | 0.75947 | 9113.64 | 1 | 5000 | 5781.96 | 9113.64 | 0 | 0 | 0 | 0 | 32631.6 | 0 | 0 | 0 | 0 | 0 | 32631.6
2022071611 | 7 | 0.71234 | 56987.2 | 0.14035 | 5052.6 | 0.79972 | 9596.64 | 1 | 5000 | 5052.6 | 9596.64 | 0 | 0 | 0 | 0 | 37337.96 | 0 | 0 | 0 | 0 | 0 | 37337.96
2022071612 | 7 | 0.76775 | 61420 | 0.10242 | 3687.12 | 0.80127 | 9615.24 | 1 | 5000 | 3687.12 | 9615.24 | 0 | 0 | 0 | 0 | 43117.64 | 0 | 0 | 0 | 0 | 0 | 43117.64
2022071613 | 7 | 0.81273 | 65018.4 | 0.09757 | 3512.52 | 0.79408 | 9528.96 | 1 | 5000 | 3512.52 | 9528.96 | 0 | 0 | 0 | 0 | 46976.92 | 0 | 0 | 0 | 0 | 0 | 46976.92
2022071614 | 7 | 0.85135 | 68108 | 0.13413 | 4828.68 | 0.8002 | 9602.4 | 1 | 5000 | 4828.68 | 9602.4 | 0 | 0 | 0 | 0 | 48676.92 | 0 | 0 | 0 | 0 | 0 | 48676.92
2022071615 | 7 | 0.88302 | 70641.6 | 0.16932 | 6095.52 | 0.78568 | 9428.16 | 1 | 5000 | 6095.52 | 9428.16 | 0 | 0 | 0 | 0 | 50117.92 | 0 | 0 | 0 | 0 | 0 | 50117.92
2022071616 | 7 | 0.90527 | 72421.6 | 0.20269 | 7296.84 | 0.76934 | 9232.08 | 1 | 5000 | 7296.84 | 9232.08 | 0 | 0 | 0 | 0 | 50892.68 | 0 | 0 | 0 | 0 | 0 | 50892.68
2022071617 | 7 | 0.92074 | 73659.2 | 0.23112 | 8320.32 | 0.74196 | 8903.52 | 1 | 5000 | 8320.32 | 8903.52 | 0 | 0 | 0 | 0 | 51435.36 | 0 | 0 | 0 | 0 | 0 | 51435.36
2022071618 | 7 | 0.92214 | 73771.2 | 0.24684 | 8886.24 | 0.70647 | 8477.64 | 1 | 5000 | 8886.24 | 8477.64 | 0 | 0 | 0 | 0 | 51407.32 | 0 | 0 | 0 | 0 | 0 | 51407.32
2022071619 | 7 | 0.90938 | 72750.4 | 0.2564 | 9230.4 | 0.60932 | 7311.84 | 1 | 5000 | 9230.4 | 7311.84 | 0 | 0 | 0 | 0 | 51208.16 | 0 | 0 | 0 | 0 | 0 | 51208.16
2022071620 | 7 | 0.88093 | 70474.4 | 0.26654 | 9595.44 | 0.3715 | 4458 | 1 | 5000 | 9595.44 | 4458 | 0 | 0 | 0 | 0 | 51420.96 | 0 | 0 | 0 | 0 | 0 | 51420.96
2022071621 | 7 | 0.84587 | 67669.6 | 0.27032 | 9731.52 | 0.05117 | 614.04 | 1 | 5000 | 9731.52 | 614.04 | 0 | 0 | 0 | 0 | 52324.04 | 0 | 0 | 0 | 0 | 0 | 52324.04
2022071622 | 7 | 0.81798 | 65438.4 | 0.32827 | 11817.72 | 0 | 0 | 1 | 5000 | 11817.72 | 0 | 0 | 0 | 0 | 0 | 48620.68 | 0 | 0 | 0 | 0 | 0 | 48620.68
2022071623 | 7 | 0.77568 | 62054.4 | 0.39593 | 14253.48 | 0 | 0 | 1 | 5000 | 14253.48 | 0 | 0 | 0 | 0 | 0 | 42800.92 | 0 | 0 | 0 | 0 | 0 | 42800.92
2022071624 | 7 | 0.72925 | 58340 | 0.43851 | 15786.36 | 0 | 0 | 1 | 5000 | 15786.36 | 0 | 0 | 0 | 0 | 0 | 37553.64 | 0 | 0 | 0 | 0 | 0 | 37553.64
2022071701 | 1 | 0.68653 | 54922.4 | 0.46063 | 16582.68 | 0 | 0 | 1 | 5000 | 16582.68 | 0 | 0 | 0 | 0 | 0 | 33339.72 | 0 | 0 | 0 | 0 | 0 | 33339.72
2022071702 | 1 | 0.65011 | 52008.8 | 0.47328 | 17038.08 | 0 | 0 | 1 | 5000 | 17038.08 | 0 | 0 | 0 | 0 | 0 | 29970.72 | 0 | 0 | 0 | 0 | 0 | 29970.72
2022071703 | 1 | 0.62174 | 49739.2 | 0.45048 | 16217.28 | 0 | 0 | 1 | 5000 | 16217.28 | 0 | 0 | 0 | 0 | 0 | 28521.92 | 0 | 0 | 0 | 0 | 0 | 28521.92
2022071704 | 1 | 0.59999 | 47999.2 | 0.43727 | 15741.72 | 0 | 0 | 1 | 5000 | 15741.72 | 0 | 0 | 0 | 0 | 0 | 27257.48 | 0 | 0 | 0 | 0 | 0 | 27257.48
2022071705 | 1 | 0.58319 | 46655.2 | 0.44434 | 15996.24 | 0 | 0 | 1 | 5000 | 15996.24 | 0 | 0 | 0 | 0 | 0 | 25658.96 | 0 | 0 | 0 | 0 | 0 | 25658.96
2022071706 | 1 | 0.57286 | 45828.8 | 0.42217 | 15198.12 | 0 | 0 | 1 | 5000 | 15198.12 | 0 | 0 | 0 | 0 | 0 | 25630.68 | 0 | 0 | 0 | 0 | 0 | 25630.68
2022071707 | 1 | 0.56301 | 45040.8 | 0.39662 | 14278.32 | 0.00088 | 10.56 | 1 | 5000 | 14278.32 | 10.56 | 0 | 0 | 0 | 0 | 25751.92 | 0 | 0 | 0 | 0 | 0 | 25751.92
2022071708 | 1 | 0.56408 | 45126.4 | 0.34333 | 12359.88 | 0.10018 | 1202.16 | 1 | 5000 | 12359.88 | 1202.16 | 0 | 0 | 0 | 0 | 26564.36 | 0 | 0 | 0 | 0 | 0 | 26564.36
2022071709 | 1 | 0.59921 | 47936.8 | 0.27539 | 9914.04 | 0.47384 | 5686.08 | 1 | 5000 | 9914.04 | 5686.08 | 0 | 0 | 0 | 0 | 27336.68 | 0 | 0 | 0 | 0 | 0 | 27336.68
2022071710 | 1 | 0.65059 | 52047.2 | 0.2852 | 10267.2 | 0.69495 | 8339.4 | 1 | 5000 | 10267.2 | 8339.4 | 0 | 0 | 0 | 0 | 28440.6 | 0 | 0 | 0 | 0 | 0 | 28440.6
2022071711 | 1 | 0.7079 | 56632 | 0.25762 | 9274.32 | 0.77005 | 9240.6 | 1 | 5000 | 9274.32 | 9240.6 | 0 | 0 | 0 | 0 | 33117.08 | 0 | 0 | 0 | 0 | 0 | 33117.08
2022071712 | 1 | 0.7656 | 61248 | 0.20848 | 7505.28 | 0.78484 | 9418.08 | 1 | 5000 | 7505.28 | 9418.08 | 0 | 0 | 0 | 0 | 39324.64 | 0 | 0 | 0 | 0 | 0 | 39324.64
2022071713 | 1 | 0.81978 | 65582.4 | 0.15491 | 5576.76 | 0.79356 | 9522.72 | 1 | 5000 | 5576.76 | 9522.72 | 0 | 0 | 0 | 0 | 45482.92 | 0 | 0 | 0 | 0 | 0 | 45482.92
2022071714 | 1 | 0.86771 | 69416.8 | 0.13786 | 4962.96 | 0.75738 | 9088.56 | 1 | 5000 | 4962.96 | 9088.56 | 0 | 0 | 0 | 0 | 50365.28 | 0 | 0 | 0 | 0 | 0 | 50365.28
2022071715 | 1 | 0.90349 | 72279.2 | 0.14832 | 5339.52 | 0.7315 | 8778 | 1 | 5000 | 5339.52 | 8778 | 0 | 0 | 0 | 0 | 53161.68 | 0 | 0 | 0 | 0 | 0 | 53161.68
2022071716 | 1 | 0.92693 | 74154.4 | 0.15706 | 5654.16 | 0.73219 | 8786.28 | 1 | 5000 | 5654.16 | 8786.28 | 0 | 0 | 0 | 0 | 54713.96 | 0 | 0 | 0 | 0 | 0 | 54713.96
2022071717 | 1 | 0.9435 | 75480 | 0.16571 | 5965.56 | 0.70597 | 8471.64 | 1 | 5000 | 5965.56 | 8471.64 | 0 | 0 | 0 | 0 | 56042.8 | 0 | 0 | 0 | 0 | 0 | 56042.8
2022071718 | 1 | 0.94282 | 75425.6 | 0.16708 | 6014.88 | 0.61625 | 7395 | 1 | 5000 | 6014.88 | 7395 | 0 | 0 | 0 | 0 | 57015.72 | 0 | 0 | 0 | 0 | 0 | 57015.72
2022071719 | 1 | 0.92718 | 74174.4 | 0.17826 | 6417.36 | 0.44409 | 5329.08 | 1 | 5000 | 6417.36 | 5329.08 | 0 | 0 | 0 | 0 | 57427.96 | 0 | 0 | 0 | 0 | 0 | 57427.96
2022071720 | 1 | 0.8985 | 71880 | 0.20043 | 7215.48 | 0.22179 | 2661.48 | 1 | 5000 | 7215.48 | 2661.48 | 0 | 0 | 0 | 0 | 57003.04 | 0 | 0 | 0 | 0 | 0 | 57003.04
2022071721 | 1 | 0.87022 | 69617.6 | 0.2562 | 9223.2 | 0.02832 | 339.84 | 1 | 5000 | 9223.2 | 339.84 | 0 | 0 | 0 | 0 | 55054.56 | 0 | 0 | 0 | 0 | 0 | 55054.56
2022071722 | 1 | 0.84678 | 67742.4 | 0.33628 | 12106.08 | 0 | 0 | 1 | 5000 | 12106.08 | 0 | 0 | 0 | 0 | 0 | 50636.32 | 0 | 0 | 0 | 0 | 0 | 50636.32
2022071723 | 1 | 0.80154 | 64123.2 | 0.43122 | 15523.92 | 0 | 0 | 1 | 5000 | 15523.92 | 0 | 0 | 0 | 0 | 0 | 43599.28 | 0 | 0 | 0 | 0 | 0 | 43599.28
2022071724 | 1 | 0.75105 | 60084 | 0.4857 | 17485.2 | 0 | 0 | 1 | 5000 | 17485.2 | 0 | 0 | 0 | 0 | 0 | 37598.8 | 0 | 0 | 0 | 0 | 0 | 37598.8
2022071801 | 2 | 0.70442 | 56353.6 | 0.50475 | 18171 | 0 | 0 | 1 | 5000 | 18171 | 0 | 0 | 0 | 0 | 0 | 33182.6 | 0 | 0 | 0 | 0 | 0 | 33182.6
2022071802 | 2 | 0.66696 | 53356.8 | 0.50445 | 18160.2 | 0 | 0 | 1 | 5000 | 18160.2 | 0 | 0 | 0 | 0 | 0 | 30196.6 | 0 | 0 | 0 | 0 | 0 | 30196.6
2022071803 | 2 | 0.63886 | 51108.8 | 0.48159 | 17337.24 | 0 | 0 | 1 | 5000 | 17337.24 | 0 | 0 | 0 | 0 | 0 | 28771.56 | 0 | 0 | 0 | 0 | 0 | 28771.56
2022071804 | 2 | 0.61933 | 49546.4 | 0.44299 | 15947.64 | 0 | 0 | 1 | 5000 | 15947.64 | 0 | 0 | 0 | 0 | 0 | 28598.76 | 0 | 0 | 0 | 0 | 0 | 28598.76
2022071805 | 2 | 0.60896 | 48716.8 | 0.40253 | 14491.08 | 0 | 0 | 1 | 5000 | 14491.08 | 0 | 0 | 0 | 0 | 0 | 29225.72 | 0 | 0 | 0 | 0 | 0 | 29225.72
2022071806 | 2 | 0.61326 | 49060.8 | 0.38044 | 13695.84 | 0 | 0 | 1 | 5000 | 13695.84 | 0 | 0 | 0 | 0 | 0 | 30364.96 | 0 | 0 | 0 | 0 | 0 | 30364.96
2022071807 | 2 | 0.61995 | 49596 | 0.34794 | 12525.84 | 0.00052 | 6.24 | 1 | 5000 | 12525.84 | 6.24 | 0 | 0 | 0 | 0 | 32063.92 | 0 | 0 | 0 | 0 | 0 | 32063.92
2022071808 | 2 | 0.63005 | 50404 | 0.31073 | 11186.28 | 0.10112 | 1213.44 | 1 | 5000 | 11186.28 | 1213.44 | 0 | 0 | 0 | 0 | 33004.28 | 0 | 0 | 0 | 0 | 0 | 33004.28
2022071809 | 2 | 0.66497 | 53197.6 | 0.23453 | 8443.08 | 0.47567 | 5708.04 | 1 | 5000 | 8443.08 | 5708.04 | 0 | 0 | 0 | 0 | 34046.48 | 0 | 0 | 0 | 0 | 0 | 34046.48
2022071810 | 2 | 0.7145 | 57160 | 0.21967 | 7908.12 | 0.6809 | 8170.8 | 1 | 5000 | 7908.12 | 8170.8 | 0 | 0 | 0 | 0 | 36081.08 | 0 | 0 | 0 | 0 | 0 | 36081.08
2022071811 | 2 | 0.77062 | 61649.6 | 0.19376 | 6975.36 | 0.765 | 9180 | 1 | 5000 | 6975.36 | 9180 | 0 | 0 | 0 | 0 | 40494.24 | 0 | 0 | 0 | 0 | 0 | 40494.24
2022071812 | 2 | 0.82709 | 66167.2 | 0.14862 | 5350.32 | 0.79075 | 9489 | 1 | 5000 | 5350.32 | 9489 | 0 | 0 | 0 | 0 | 46327.88 | 0 | 0 | 0 | 0 | 0 | 46327.88
2022071813 | 2 | 0.88169 | 70535.2 | 0.10886 | 3918.96 | 0.79508 | 9540.96 | 1 | 5000 | 3918.96 | 9540.96 | 0 | 0 | 0 | 0 | 52075.28 | 0 | 0 | 0 | 0 | 0 | 52075.28
2022071814 | 2 | 0.9268 | 74144 | 0.10713 | 3856.68 | 0.7975 | 9570 | 1 | 5000 | 3856.68 | 9570 | 0 | 0 | 0 | 0 | 55717.32 | 0 | 0 | 0 | 0 | 0 | 55717.32
2022071815 | 2 | 0.96303 | 77042.4 | 0.12348 | 4445.28 | 0.79318 | 9518.16 | 1 | 5000 | 4445.28 | 9518.16 | 0 | 0 | 0 | 0 | 58078.96 | 0 | 0 | 0 | 0 | 0 | 58078.96
2022071816 | 2 | 0.98251 | 78600.8 | 0.13521 | 4867.56 | 0.78082 | 9369.84 | 1 | 5000 | 4867.56 | 9369.84 | 0 | 0 | 0 | 0 | 59363.4 | 0 | 0 | 0 | 0 | 0 | 59363.4
2022071817 | 2 | 0.98974 | 79179.2 | 0.14686 | 5286.96 | 0.76291 | 9154.92 | 1 | 5000 | 5286.96 | 9154.92 | 0 | 0 | 0 | 0 | 59737.32 | 0 | 0 | 0 | 0 | 0 | 59737.32
2022071818 | 2 | 0.98995 | 79196 | 0.15885 | 5718.6 | 0.72864 | 8743.68 | 1 | 5000 | 5718.6 | 8743.68 | 0 | 0 | 0 | 0 | 59733.72 | 0 | 0 | 0 | 0 | 0 | 59733.72
2022071819 | 2 | 0.97631 | 78104.8 | 0.17173 | 6182.28 | 0.61089 | 7330.68 | 1 | 5000 | 6182.28 | 7330.68 | 0 | 0 | 0 | 0 | 59591.84 | 0 | 0 | 0 | 0 | 0 | 59591.84
2022071820 | 2 | 0.94439 | 75551.2 | 0.20383 | 7337.88 | 0.3068 | 3681.6 | 1 | 5000 | 7337.88 | 3681.6 | 0 | 0 | 0 | 0 | 59531.72 | 0 | 0 | 0 | 0 | 0 | 59531.72
2022071821 | 2 | 0.91135 | 72908 | 0.26679 | 9604.44 | 0.03487 | 418.44 | 1 | 5000 | 9604.44 | 418.44 | 0 | 0 | 0 | 0 | 57885.12 | 0 | 0 | 0 | 0 | 0 | 57885.12
2022071822 | 2 | 0.88478 | 70782.4 | 0.36957 | 13304.52 | 0 | 0 | 1 | 5000 | 13304.52 | 0 | 0 | 0 | 0 | 0 | 52477.88 | 0 | 0 | 0 | 0 | 0 | 52477.88
2022071823 | 2 | 0.83508 | 66806.4 | 0.45841 | 16502.76 | 0 | 0 | 1 | 5000 | 16502.76 | 0 | 0 | 0 | 0 | 0 | 45303.64 | 0 | 0 | 0 | 0 | 0 | 45303.64
2022071824 | 2 | 0.77923 | 62338.4 | 0.51266 | 18455.76 | 4e-05 | 0.48 | 1 | 5000 | 18455.76 | 0.48 | 0 | 0 | 0 | 0 | 38882.16 | 0 | 0 | 0 | 0 | 0 | 38882.16
2022071901 | 3 | 0.73301 | 58640.8 | 0.54572 | 19645.92 | 5e-05 | 0.6 | 1 | 5000 | 19645.92 | 0.6 | 0 | 0 | 0 | 0 | 33994.28 | 0 | 0 | 0 | 0 | 0 | 33994.28
2022071902 | 3 | 0.696 | 55680 | 0.56349 | 20285.64 | 5e-05 | 0.6 | 1 | 5000 | 20285.64 | 0.6 | 0 | 0 | 0 | 0 | 30393.76 | 0 | 0 | 0 | 0 | 0 | 30393.76
2022071903 | 3 | 0.66688 | 53350.4 | 0.5573 | 20062.8 | 5e-05 | 0.6 | 1 | 5000 | 20062.8 | 0.6 | 0 | 0 | 0 | 0 | 28287 | 0 | 0 | 0 | 0 | 0 | 28287
2022071904 | 3 | 0.64777 | 51821.6 | 0.53823 | 19376.28 | 4e-05 | 0.48 | 1 | 5000 | 19376.28 | 0.48 | 0 | 0 | 0 | 0 | 27444.84 | 0 | 0 | 0 | 0 | 0 | 27444.84
2022071905 | 3 | 0.63964 | 51171.2 | 0.54626 | 19665.36 | 0 | 0 | 1 | 5000 | 19665.36 | 0 | 0 | 0 | 0 | 0 | 26505.84 | 0 | 0 | 0 | 0 | 0 | 26505.84
2022071906 | 3 | 0.64114 | 51291.2 | 0.54641 | 19670.76 | 4e-05 | 0.48 | 1 | 5000 | 19670.76 | 0.48 | 0 | 0 | 0 | 0 | 26619.96 | 0 | 0 | 0 | 0 | 0 | 26619.96
2022071907 | 3 | 0.64802 | 51841.6 | 0.54199 | 19511.64 | 0.00126 | 15.12 | 1 | 5000 | 19511.64 | 15.12 | 0 | 0 | 0 | 0 | 27314.84 | 0 | 0 | 0 | 0 | 0 | 27314.84
2022071908 | 3 | 0.65782 | 52625.6 | 0.51659 | 18597.24 | 0.12871 | 1544.52 | 1 | 5000 | 18597.24 | 1544.52 | 0 | 0 | 0 | 0 | 27483.84 | 0 | 0 | 0 | 0 | 0 | 27483.84
2022071909 | 3 | 0.69198 | 55358.4 | 0.45476 | 16371.36 | 0.51153 | 6138.36 | 1 | 5000 | 16371.36 | 6138.36 | 0 | 0 | 0 | 0 | 27848.68 | 0 | 0 | 0 | 0 | 0 | 27848.68
2022071910 | 3 | 0.7426 | 59408 | 0.4871 | 17535.6 | 0.69661 | 8359.32 | 1 | 5000 | 17535.6 | 8359.32 | 0 | 0 | 0 | 0 | 28513.08 | 0 | 0 | 0 | 0 | 0 | 28513.08
2022071911 | 3 | 0.79665 | 63732 | 0.44295 | 15946.2 | 0.77246 | 9269.52 | 1 | 5000 | 15946.2 | 9269.52 | 0 | 0 | 0 | 0 | 33516.28 | 0 | 0 | 0 | 0 | 0 | 33516.28
2022071912 | 3 | 0.85105 | 68084 | 0.39299 | 14147.64 | 0.7666 | 9199.2 | 1 | 5000 | 14147.64 | 9199.2 | 0 | 0 | 0 | 0 | 39737.16 | 0 | 0 | 0 | 0 | 0 | 39737.16
2022071913 | 3 | 0.90469 | 72375.2 | 0.39038 | 14053.68 | 0.77518 | 9302.16 | 1 | 5000 | 14053.68 | 9302.16 | 0 | 0 | 0 | 0 | 44019.36 | 0 | 0 | 0 | 0 | 0 | 44019.36
2022071914 | 3 | 0.95252 | 76201.6 | 0.38046 | 13696.56 | 0.75708 | 9084.96 | 1 | 5000 | 13696.56 | 9084.96 | 0 | 0 | 0 | 0 | 48420.08 | 0 | 0 | 0 | 0 | 0 | 48420.08
2022071915 | 3 | 0.98603 | 78882.4 | 0.35695 | 12850.2 | 0.76198 | 9143.76 | 1 | 5000 | 12850.2 | 9143.76 | 0 | 0 | 0 | 0 | 51888.44 | 0 | 0 | 0 | 0 | 0 | 51888.44
2022071916 | 3 | 0.99287 | 79429.6 | 0.33151 | 11934.36 | 0.77138 | 9256.56 | 1 | 5000 | 11934.36 | 9256.56 | 0 | 0 | 0 | 0 | 53238.68 | 0 | 0 | 0 | 0 | 0 | 53238.68
2022071917 | 3 | 0.99743 | 79794.4 | 0.31132 | 11207.52 | 0.75859 | 9103.08 | 1 | 5000 | 11207.52 | 9103.08 | 0 | 0 | 0 | 0 | 54483.8 | 0 | 0 | 0 | 0 | 0 | 54483.8
2022071918 | 3 | 0.99468 | 79574.4 | 0.30376 | 10935.36 | 0.71807 | 8616.84 | 1 | 5000 | 10935.36 | 8616.84 | 0 | 0 | 0 | 0 | 55022.2 | 0 | 0 | 0 | 0 | 0 | 55022.2
2022071919 | 3 | 0.98411 | 78728.8 | 0.30959 | 11145.24 | 0.55989 | 6718.68 | 1 | 5000 | 11145.24 | 6718.68 | 0 | 0 | 0 | 0 | 55864.88 | 0 | 0 | 0 | 0 | 0 | 55864.88
2022071920 | 3 | 0.95944 | 76755.2 | 0.34933 | 12575.88 | 0.25556 | 3066.72 | 1 | 5000 | 12575.88 | 3066.72 | 0 | 0 | 0 | 0 | 56112.6 | 0 | 0 | 0 | 0 | 0 | 56112.6
2022071921 | 3 | 0.92617 | 74093.6 | 0.40988 | 14755.68 | 0.03286 | 394.32 | 1 | 5000 | 14755.68 | 394.32 | 0 | 0 | 0 | 0 | 53943.6 | 0 | 0 | 0 | 0 | 0 | 53943.6
2022071922 | 3 | 0.89557 | 71645.6 | 0.53007 | 19082.52 | 0 | 0 | 1 | 5000 | 19082.52 | 0 | 0 | 0 | 0 | 0 | 47563.08 | 0 | 0 | 0 | 0 | 0 | 47563.08
2022071923 | 3 | 0.84725 | 67780 | 0.60559 | 21801.24 | 0 | 0 | 1 | 5000 | 21801.24 | 0 | 0 | 0 | 0 | 0 | 40978.76 | 0 | 0 | 0 | 0 | 0 | 40978.76
2022071924 | 3 | 0.79392 | 63513.6 | 0.63059 | 22701.24 | 0 | 0 | 1 | 5000 | 22701.24 | 0 | 0 | 0 | 0 | 0 | 35812.36 | 0 | 0 | 0 | 0 | 0 | 35812.36
2022072001 | 4 | 0.74817 | 59853.6 | 0.6478 | 23320.8 | 0 | 0 | 1 | 5000 | 23320.8 | 0 | 0 | 0 | 0 | 0 | 31532.8 | 0 | 0 | 0 | 0 | 0 | 31532.8
2022072002 | 4 | 0.71181 | 56944.8 | 0.6509 | 23432.4 | 0 | 0 | 1 | 5000 | 23432.4 | 0 | 0 | 0 | 0 | 0 | 28512.4 | 0 | 0 | 0 | 0 | 0 | 28512.4
2022072003 | 4 | 0.68455 | 54764 | 0.65184 | 23466.24 | 0 | 0 | 1 | 5000 | 23466.24 | 0 | 0 | 0 | 0 | 0 | 26297.76 | 0 | 0 | 0 | 0 | 0 | 26297.76
2022072004 | 4 | 0.66413 | 53130.4 | 0.62827 | 22617.72 | 0 | 0 | 1 | 5000 | 22617.72 | 0 | 0 | 0 | 0 | 0 | 25512.68 | 0 | 0 | 0 | 0 | 0 | 25512.68
2022072005 | 4 | 0.65103 | 52082.4 | 0.57785 | 20802.6 | 0 | 0 | 1 | 5000 | 20802.6 | 0 | 0 | 0 | 0 | 0 | 26279.8 | 0 | 0 | 0 | 0 | 0 | 26279.8
2022072006 | 4 | 0.64996 | 51996.8 | 0.50586 | 18210.96 | 0 | 0 | 1 | 5000 | 18210.96 | 0 | 0 | 0 | 0 | 0 | 28785.84 | 0 | 0 | 0 | 0 | 0 | 28785.84
2022072007 | 4 | 0.65548 | 52438.4 | 0.44394 | 15981.84 | 0.00106 | 12.72 | 1 | 5000 | 15981.84 | 12.72 | 0 | 0 | 0 | 0 | 31443.84 | 0 | 0 | 0 | 0 | 0 | 31443.84
2022072008 | 4 | 0.66527 | 53221.6 | 0.3804 | 13694.4 | 0.09378 | 1125.36 | 1 | 5000 | 13694.4 | 1125.36 | 0 | 0 | 0 | 0 | 33401.84 | 0 | 0 | 0 | 0 | 0 | 33401.84
2022072009 | 4 | 0.69661 | 55728.8 | 0.34088 | 12271.68 | 0.34552 | 4146.24 | 1 | 5000 | 12271.68 | 4146.24 | 0 | 0 | 0 | 0 | 34310.88 | 0 | 0 | 0 | 0 | 0 | 34310.88
2022072010 | 4 | 0.74234 | 59387.2 | 0.30772 | 11077.92 | 0.45596 | 5471.52 | 1 | 5000 | 11077.92 | 5471.52 | 0 | 0 | 0 | 0 | 37837.76 | 0 | 0 | 0 | 0 | 0 | 37837.76
2022072011 | 4 | 0.79884 | 63907.2 | 0.26792 | 9645.12 | 0.56843 | 6821.16 | 1 | 5000 | 9645.12 | 6821.16 | 0 | 0 | 0 | 0 | 42440.92 | 0 | 0 | 0 | 0 | 0 | 42440.92
2022072012 | 4 | 0.85805 | 68644 | 0.24716 | 8897.76 | 0.65739 | 7888.68 | 1 | 5000 | 8897.76 | 7888.68 | 0 | 0 | 0 | 0 | 46857.56 | 0 | 0 | 0 | 0 | 0 | 46857.56
2022072013 | 4 | 0.90972 | 72777.6 | 0.23287 | 8383.32 | 0.71016 | 8521.92 | 1 | 5000 | 8383.32 | 8521.92 | 0 | 0 | 0 | 0 | 50872.36 | 0 | 0 | 0 | 0 | 0 | 50872.36
2022072014 | 4 | 0.95366 | 76292.8 | 0.22169 | 7980.84 | 0.68182 | 8181.84 | 1 | 5000 | 7980.84 | 8181.84 | 0 | 0 | 0 | 0 | 55130.12 | 0 | 0 | 0 | 0 | 0 | 55130.12
2022072015 | 4 | 0.98242 | 78593.6 | 0.2036 | 7329.6 | 0.69322 | 8318.64 | 1 | 5000 | 7329.6 | 8318.64 | 0 | 0 | 0 | 0 | 57945.36 | 0 | 0 | 0 | 0 | 0 | 57945.36
2022072016 | 4 | 0.9946 | 79568 | 0.18729 | 6742.44 | 0.68421 | 8210.52 | 1 | 5000 | 6742.44 | 8210.52 | 0 | 0 | 0 | 0 | 59615.04 | 0 | 0 | 0 | 0 | 0 | 59615.04
2022072017 | 4 | 1 | 80000 | 0.20721 | 7459.56 | 0.66851 | 8022.12 | 1 | 5000 | 7459.56 | 8022.12 | 0 | 0 | 0 | 0 | 59518.32 | 0 | 0 | 0 | 0 | 0 | 59518.32
2022072018 | 4 | 0.99809 | 79847.2 | 0.24004 | 8641.44 | 0.60091 | 7210.92 | 1 | 5000 | 8641.44 | 7210.92 | 0 | 0 | 0 | 0 | 58994.84 | 0 | 0 | 0 | 0 | 0 | 58994.84
2022072019 | 4 | 0.98344 | 78675.2 | 0.28165 | 10139.4 | 0.55071 | 6608.52 | 1 | 5000 | 10139.4 | 6608.52 | 0 | 0 | 0 | 0 | 56927.28 | 0 | 0 | 0 | 0 | 0 | 56927.28
2022072020 | 4 | 0.95124 | 76099.2 | 0.30909 | 11127.24 | 0.29556 | 3546.72 | 1 | 5000 | 11127.24 | 3546.72 | 0 | 0 | 0 | 0 | 56425.24 | 0 | 0 | 0 | 0 | 0 | 56425.24
2022072021 | 4 | 0.91899 | 73519.2 | 0.31692 | 11409.12 | 0.0338 | 405.6 | 1 | 5000 | 11409.12 | 405.6 | 0 | 0 | 0 | 0 | 56704.48 | 0 | 0 | 0 | 0 | 0 | 56704.48
2022072022 | 4 | 0.88759 | 71007.2 | 0.33336 | 12000.96 | 0 | 0 | 1 | 5000 | 12000.96 | 0 | 0 | 0 | 0 | 0 | 54006.24 | 0 | 0 | 0 | 0 | 0 | 54006.24
2022072023 | 4 | 0.8417 | 67336 | 0.37362 | 13450.32 | 0 | 0 | 1 | 5000 | 13450.32 | 0 | 0 | 0 | 0 | 0 | 48885.68 | 0 | 0 | 0 | 0 | 0 | 48885.68
2022072024 | 4 | 0.79092 | 63273.6 | 0.45163 | 16258.68 | 0 | 0 | 1 | 5000 | 16258.68 | 0 | 0 | 0 | 0 | 0 | 42014.92 | 0 | 0 | 0 | 0 | 0 | 42014.92
2022072101 | 5 | 0.74167 | 59333.6 | 0.46803 | 16849.08 | 0 | 0 | 1 | 5000 | 16849.08 | 0 | 0 | 0 | 0 | 0 | 37484.52 | 0 | 0 | 0 | 0 | 0 | 37484.52
2022072102 | 5 | 0.70578 | 56462.4 | 0.47417 | 17070.12 | 0 | 0 | 1 | 5000 | 17070.12 | 0 | 0 | 0 | 0 | 0 | 34392.28 | 0 | 0 | 0 | 0 | 0 | 34392.28
2022072103 | 5 | 0.67788 | 54230.4 | 0.42224 | 15200.64 | 0 | 0 | 1 | 5000 | 15200.64 | 0 | 0 | 0 | 0 | 0 | 34029.76 | 0 | 0 | 0 | 0 | 0 | 34029.76
2022072104 | 5 | 0.66129 | 52903.2 | 0.34872 | 12553.92 | 0 | 0 | 1 | 5000 | 12553.92 | 0 | 0 | 0 | 0 | 0 | 35349.28 | 0 | 0 | 0 | 0 | 0 | 35349.28
2022072105 | 5 | 0.65043 | 52034.4 | 0.31125 | 11205 | 0 | 0 | 1 | 5000 | 11205 | 0 | 0 | 0 | 0 | 0 | 35829.4 | 0 | 0 | 0 | 0 | 0 | 35829.4
2022072106 | 5 | 0.65346 | 52276.8 | 0.26198 | 9431.28 | 0 | 0 | 1 | 5000 | 9431.28 | 0 | 0 | 0 | 0 | 0 | 37845.52 | 0 | 0 | 0 | 0 | 0 | 37845.52
2022072107 | 5 | 0.66135 | 52908 | 0.25727 | 9261.72 | 0.00062 | 7.44 | 1 | 5000 | 9261.72 | 7.44 | 0 | 0 | 0 | 0 | 38638.84 | 0 | 0 | 0 | 0 | 0 | 38638.84
2022072108 | 5 | 0.66566 | 53252.8 | 0.2381 | 8571.6 | 0.07076 | 849.12 | 1 | 5000 | 8571.6 | 849.12 | 0 | 0 | 0 | 0 | 38832.08 | 0 | 0 | 0 | 0 | 0 | 38832.08
2022072109 | 5 | 0.69346 | 55476.8 | 0.2249 | 8096.4 | 0.26515 | 3181.8 | 1 | 5000 | 8096.4 | 3181.8 | 0 | 0 | 0 | 0 | 39198.6 | 0 | 0 | 0 | 0 | 0 | 39198.6
2022072110 | 5 | 0.72992 | 58393.6 | 0.22244 | 8007.84 | 0.34653 | 4158.36 | 1 | 5000 | 8007.84 | 4158.36 | 0 | 0 | 0 | 0 | 41227.4 | 0 | 0 | 0 | 0 | 0 | 41227.4
2022072111 | 5 | 0.7729 | 61832 | 0.18566 | 6683.76 | 0.42363 | 5083.56 | 1 | 5000 | 6683.76 | 5083.56 | 0 | 0 | 0 | 0 | 45064.68 | 0 | 0 | 0 | 0 | 0 | 45064.68
2022072112 | 5 | 0.82113 | 65690.4 | 0.18851 | 6786.36 | 0.46981 | 5637.72 | 1 | 5000 | 6786.36 | 5637.72 | 0 | 0 | 0 | 0 | 48266.32 | 0 | 0 | 0 | 0 | 0 | 48266.32
2022072113 | 5 | 0.86437 | 69149.6 | 0.19452 | 7002.72 | 0.5206 | 6247.2 | 1 | 5000 | 7002.72 | 6247.2 | 0 | 0 | 0 | 0 | 50899.68 | 0 | 0 | 0 | 0 | 0 | 50899.68
2022072114 | 5 | 0.90428 | 72342.4 | 0.20571 | 7405.56 | 0.57256 | 6870.72 | 1 | 5000 | 7405.56 | 6870.72 | 0 | 0 | 0 | 0 | 53066.12 | 0 | 0 | 0 | 0 | 0 | 53066.12
2022072115 | 5 | 0.93635 | 74908 | 0.23843 | 8583.48 | 0.56261 | 6751.32 | 1 | 5000 | 8583.48 | 6751.32 | 0 | 0 | 0 | 0 | 54573.2 | 0 | 0 | 0 | 0 | 0 | 54573.2
2022072116 | 5 | 0.96065 | 76852 | 0.29025 | 10449 | 0.56347 | 6761.64 | 1 | 5000 | 10449 | 6761.64 | 0 | 0 | 0 | 0 | 54641.36 | 0 | 0 | 0 | 0 | 0 | 54641.36
2022072117 | 5 | 0.97453 | 77962.4 | 0.34821 | 12535.56 | 0.61123 | 7334.76 | 1 | 5000 | 12535.56 | 7334.76 | 0 | 0 | 0 | 0 | 53092.08 | 0 | 0 | 0 | 0 | 0 | 53092.08
2022072118 | 5 | 0.97192 | 77753.6 | 0.38655 | 13915.8 | 0.58502 | 7020.24 | 1 | 5000 | 13915.8 | 7020.24 | 0 | 0 | 0 | 0 | 51817.56 | 0 | 0 | 0 | 0 | 0 | 51817.56
2022072119 | 5 | 0.954 | 76320 | 0.41899 | 15083.64 | 0.45672 | 5480.64 | 1 | 5000 | 15083.64 | 5480.64 | 0 | 0 | 0 | 0 | 50755.72 | 0 | 0 | 0 | 0 | 0 | 50755.72
2022072120 | 5 | 0.91924 | 73539.2 | 0.4484 | 16142.4 | 0.27051 | 3246.12 | 1 | 5000 | 16142.4 | 3246.12 | 0 | 0 | 0 | 0 | 49150.68 | 0 | 0 | 0 | 0 | 0 | 49150.68
2022072121 | 5 | 0.88262 | 70609.6 | 0.39533 | 14231.88 | 0.0212 | 254.4 | 1 | 5000 | 14231.88 | 254.4 | 0 | 0 | 0 | 0 | 51123.32 | 0 | 0 | 0 | 0 | 0 | 51123.32
2022072122 | 5 | 0.85312 | 68249.6 | 0.35057 | 12620.52 | 0 | 0 | 1 | 5000 | 12620.52 | 0 | 0 | 0 | 0 | 0 | 50629.08 | 0 | 0 | 0 | 0 | 0 | 50629.08
2022072123 | 5 | 0.80492 | 64393.6 | 0.36414 | 13109.04 | 0 | 0 | 1 | 5000 | 13109.04 | 0 | 0 | 0 | 0 | 0 | 46284.56 | 0 | 0 | 0 | 0 | 0 | 46284.56
2022072124 | 5 | 0.75322 | 60257.6 | 0.38778 | 13960.08 | 0 | 0 | 1 | 5000 | 13960.08 | 0 | 0 | 0 | 0 | 0 | 41297.52 | 0 | 0 | 0 | 0 | 0 | 41297.52
2022072201 | 6 | 0.7054 | 56432 | 0.39205 | 14113.8 | 0 | 0 | 1 | 5000 | 14113.8 | 0 | 0 | 0 | 0 | 0 | 37318.2 | 0 | 0 | 0 | 0 | 0 | 37318.2
2022072202 | 6 | 0.66637 | 53309.6 | 0.3909 | 14072.4 | 0 | 0 | 1 | 5000 | 14072.4 | 0 | 0 | 0 | 0 | 0 | 34237.2 | 0 | 0 | 0 | 0 | 0 | 34237.2
2022072203 | 6 | 0.63914 | 51131.2 | 0.38759 | 13953.24 | 0 | 0 | 1 | 5000 | 13953.24 | 0 | 0 | 0 | 0 | 0 | 32177.96 | 0 | 0 | 0 | 0 | 0 | 32177.96
2022072204 | 6 | 0.62404 | 49923.2 | 0.3873 | 13942.8 | 0 | 0 | 1 | 5000 | 13942.8 | 0 | 0 | 0 | 0 | 0 | 30980.4 | 0 | 0 | 0 | 0 | 0 | 30980.4
2022072205 | 6 | 0.61587 | 49269.6 | 0.35575 | 12807 | 0 | 0 | 1 | 5000 | 12807 | 0 | 0 | 0 | 0 | 0 | 31462.6 | 0 | 0 | 0 | 0 | 0 | 31462.6
2022072206 | 6 | 0.61893 | 49514.4 | 0.32755 | 11791.8 | 0 | 0 | 1 | 5000 | 11791.8 | 0 | 0 | 0 | 0 | 0 | 32722.6 | 0 | 0 | 0 | 0 | 0 | 32722.6
2022072207 | 6 | 0.62885 | 50308 | 0.33715 | 12137.4 | 0.00034 | 4.08 | 1 | 5000 | 12137.4 | 4.08 | 0 | 0 | 0 | 0 | 33166.52 | 0 | 0 | 0 | 0 | 0 | 33166.52
2022072208 | 6 | 0.6373 | 50984 | 0.33791 | 12164.76 | 0.06045 | 725.4 | 1 | 5000 | 12164.76 | 725.4 | 0 | 0 | 0 | 0 | 33093.84 | 0 | 0 | 0 | 0 | 0 | 33093.84
2022072209 | 6 | 0.66598 | 53278.4 | 0.29751 | 10710.36 | 0.26425 | 3171 | 1 | 5000 | 10710.36 | 3171 | 0 | 0 | 0 | 0 | 34397.04 | 0 | 0 | 0 | 0 | 0 | 34397.04
2022072210 | 6 | 0.71141 | 56912.8 | 0.31648 | 11393.28 | 0.46658 | 5598.96 | 1 | 5000 | 11393.28 | 5598.96 | 0 | 0 | 0 | 0 | 34920.56 | 0 | 0 | 0 | 0 | 0 | 34920.56
2022072211 | 6 | 0.76215 | 60972 | 0.29889 | 10760.04 | 0.64904 | 7788.48 | 1 | 5000 | 10760.04 | 7788.48 | 0 | 0 | 0 | 0 | 37423.48 | 0 | 0 | 0 | 0 | 0 | 37423.48
2022072212 | 6 | 0.81356 | 65084.8 | 0.27006 | 9722.16 | 0.69853 | 8382.36 | 1 | 5000 | 9722.16 | 8382.36 | 0 | 0 | 0 | 0 | 41980.28 | 0 | 0 | 0 | 0 | 0 | 41980.28
2022072213 | 6 | 0.85876 | 68700.8 | 0.25393 | 9141.48 | 0.70837 | 8500.44 | 1 | 5000 | 9141.48 | 8500.44 | 0 | 0 | 0 | 0 | 46058.88 | 0 | 0 | 0 | 0 | 0 | 46058.88
2022072214 | 6 | 0.89392 | 71513.6 | 0.25519 | 9186.84 | 0.71201 | 8544.12 | 1 | 5000 | 9186.84 | 8544.12 | 0 | 0 | 0 | 0 | 48782.64 | 0 | 0 | 0 | 0 | 0 | 48782.64
2022072215 | 6 | 0.90762 | 72609.6 | 0.27682 | 9965.52 | 0.70863 | 8503.56 | 1 | 5000 | 9965.52 | 8503.56 | 0 | 0 | 0 | 0 | 49140.52 | 0 | 0 | 0 | 0 | 0 | 49140.52
2022072216 | 6 | 0.9066 | 72528 | 0.31733 | 11423.88 | 0.69463 | 8335.56 | 1 | 5000 | 11423.88 | 8335.56 | 0 | 0 | 0 | 0 | 47768.56 | 0 | 0 | 0 | 0 | 0 | 47768.56
2022072217 | 6 | 0.90654 | 72523.2 | 0.35476 | 12771.36 | 0.65018 | 7802.16 | 1 | 5000 | 12771.36 | 7802.16 | 0 | 0 | 0 | 0 | 46949.68 | 0 | 0 | 0 | 0 | 0 | 46949.68
2022072218 | 6 | 0.90399 | 72319.2 | 0.38534 | 13872.24 | 0.59628 | 7155.36 | 1 | 5000 | 13872.24 | 7155.36 | 0 | 0 | 0 | 0 | 46291.6 | 0 | 0 | 0 | 0 | 0 | 46291.6
2022072219 | 6 | 0.88768 | 71014.4 | 0.42216 | 15197.76 | 0.48029 | 5763.48 | 1 | 5000 | 15197.76 | 5763.48 | 0 | 0 | 0 | 0 | 45053.16 | 0 | 0 | 0 | 0 | 0 | 45053.16
2022072220 | 6 | 0.86154 | 68923.2 | 0.44438 | 15997.68 | 0.24492 | 2939.04 | 1 | 5000 | 15997.68 | 2939.04 | 0 | 0 | 0 | 0 | 44986.48 | 0 | 0 | 0 | 0 | 0 | 44986.48
2022072221 | 6 | 0.83035 | 66428 | 0.43186 | 15546.96 | 0.01846 | 221.52 | 1 | 5000 | 15546.96 | 221.52 | 0 | 0 | 0 | 0 | 45659.52 | 0 | 0 | 0 | 0 | 0 | 45659.52
2022072222 | 6 | 0.80511 | 64408.8 | 0.43625 | 15705 | 0 | 0 | 1 | 5000 | 15705 | 0 | 0 | 0 | 0 | 0 | 43703.8 | 0 | 0 | 0 | 0 | 0 | 43703.8
2022072223 | 6 | 0.76162 | 60929.6 | 0.48377 | 17415.72 | 0 | 0 | 1 | 5000 | 17415.72 | 0 | 0 | 0 | 0 | 0 | 38513.88 | 0 | 0 | 0 | 0 | 0 | 38513.88
2022072224 | 6 | 0.71893 | 57514.4 | 0.50745 | 18268.2 | 0 | 0 | 1 | 5000 | 18268.2 | 0 | 0 | 0 | 0 | 0 | 34246.2 | 0 | 0 | 0 | 0 | 0 | 34246.2
2022072301 | 7 | 0.67651 | 54120.8 | 0.52193 | 18789.48 | 0 | 0 | 1 | 5000 | 18789.48 | 0 | 0 | 0 | 0 | 0 | 30331.32 | 0 | 0 | 0 | 0 | 0 | 30331.32
2022072302 | 7 | 0.64144 | 51315.2 | 0.51691 | 18608.76 | 0 | 0 | 1 | 5000 | 18608.76 | 0 | 0 | 0 | 0 | 0 | 27706.44 | 0 | 0 | 0 | 0 | 0 | 27706.44
2022072303 | 7 | 0.61561 | 49248.8 | 0.52273 | 18818.28 | 0 | 0 | 1 | 5000 | 18818.28 | 0 | 0 | 0 | 0 | 0 | 25430.52 | 0 | 0 | 0 | 0 | 0 | 25430.52
2022072304 | 7 | 0.59769 | 47815.2 | 0.52526 | 18909.36 | 0 | 0 | 1 | 5000 | 18909.36 | 0 | 0 | 0 | 0 | 0 | 23905.84 | 0 | 0 | 0 | 0 | 0 | 23905.84
2022072305 | 7 | 0.58541 | 46832.8 | 0.50131 | 18047.16 | 0 | 0 | 1 | 5000 | 18047.16 | 0 | 0 | 0 | 0 | 0 | 23785.64 | 0 | 0 | 0 | 0 | 0 | 23785.64
2022072306 | 7 | 0.58008 | 46406.4 | 0.48061 | 17301.96 | 0 | 0 | 1 | 5000 | 17301.96 | 0 | 0 | 0 | 0 | 0 | 24104.44 | 0 | 0 | 0 | 0 | 0 | 24104.44
2022072307 | 7 | 0.5793 | 46344 | 0.46303 | 16669.08 | 0.00113 | 13.56 | 1 | 5000 | 16669.08 | 13.56 | 0 | 0 | 0 | 0 | 24661.36 | 0 | 0 | 0 | 0 | 0 | 24661.36
2022072308 | 7 | 0.58653 | 46922.4 | 0.4232 | 15235.2 | 0.09551 | 1146.12 | 1 | 5000 | 15235.2 | 1146.12 | 0 | 0 | 0 | 0 | 25541.08 | 0 | 0 | 0 | 0 | 0 | 25541.08
2022072309 | 7 | 0.62775 | 50220 | 0.39621 | 14263.56 | 0.43398 | 5207.76 | 1 | 5000 | 14263.56 | 5207.76 | 0 | 0 | 0 | 0 | 25748.68 | 0 | 0 | 0 | 0 | 0 | 25748.68
2022072310 | 7 | 0.68529 | 54823.2 | 0.46843 | 16863.48 | 0.68303 | 8196.36 | 1 | 5000 | 16863.48 | 8196.36 | 0 | 0 | 0 | 0 | 24763.36 | 0 | 0 | 0 | 0 | 0 | 24763.36
2022072311 | 7 | 0.74014 | 59211.2 | 0.45336 | 16320.96 | 0.75558 | 9066.96 | 1 | 5000 | 16320.96 | 9066.96 | 0 | 0 | 0 | 0 | 28823.28 | 0 | 0 | 0 | 0 | 0 | 28823.28
2022072312 | 7 | 0.78931 | 63144.8 | 0.41171 | 14821.56 | 0.75521 | 9062.52 | 1 | 5000 | 14821.56 | 9062.52 | 0 | 0 | 0 | 0 | 34260.72 | 0 | 0 | 0 | 0 | 0 | 34260.72
2022072313 | 7 | 0.8286 | 66288 | 0.36865 | 13271.4 | 0.73684 | 8842.08 | 1 | 5000 | 13271.4 | 8842.08 | 0 | 0 | 0 | 0 | 39174.52 | 0 | 0 | 0 | 0 | 0 | 39174.52
2022072314 | 7 | 0.85839 | 68671.2 | 0.33956 | 12224.16 | 0.75936 | 9112.32 | 1 | 5000 | 12224.16 | 9112.32 | 0 | 0 | 0 | 0 | 42334.72 | 0 | 0 | 0 | 0 | 0 | 42334.72
2022072315 | 7 | 0.8867 | 70936 | 0.3499 | 12596.4 | 0.76401 | 9168.12 | 1 | 5000 | 12596.4 | 9168.12 | 0 | 0 | 0 | 0 | 44171.48 | 0 | 0 | 0 | 0 | 0 | 44171.48
2022072316 | 7 | 0.91056 | 72844.8 | 0.37806 | 13610.16 | 0.73141 | 8776.92 | 1 | 5000 | 13610.16 | 8776.92 | 0 | 0 | 0 | 0 | 45457.72 | 0 | 0 | 0 | 0 | 0 | 45457.72
2022072317 | 7 | 0.92678 | 74142.4 | 0.39603 | 14257.08 | 0.71507 | 8580.84 | 1 | 5000 | 14257.08 | 8580.84 | 0 | 0 | 0 | 0 | 46304.48 | 0 | 0 | 0 | 0 | 0 | 46304.48
2022072318 | 7 | 0.9265 | 74120 | 0.41116 | 14801.76 | 0.69676 | 8361.12 | 1 | 5000 | 14801.76 | 8361.12 | 0 | 0 | 0 | 0 | 45957.12 | 0 | 0 | 0 | 0 | 0 | 45957.12
2022072319 | 7 | 0.91139 | 72911.2 | 0.44417 | 15990.12 | 0.5902 | 7082.4 | 1 | 5000 | 15990.12 | 7082.4 | 0 | 0 | 0 | 0 | 44838.68 | 0 | 0 | 0 | 0 | 0 | 44838.68
2022072320 | 7 | 0.88439 | 70751.2 | 0.48232 | 17363.52 | 0.33912 | 4069.44 | 1 | 5000 | 17363.52 | 4069.44 | 0 | 0 | 0 | 0 | 44318.24 | 0 | 0 | 0 | 0 | 0 | 44318.24
2022072321 | 7 | 0.84874 | 67899.2 | 0.48791 | 17564.76 | 0.03869 | 464.28 | 1 | 5000 | 17564.76 | 464.28 | 0 | 0 | 0 | 0 | 44870.16 | 0 | 0 | 0 | 0 | 0 | 44870.16
2022072322 | 7 | 0.82196 | 65756.8 | 0.50343 | 18123.48 | 0 | 0 | 1 | 5000 | 18123.48 | 0 | 0 | 0 | 0 | 0 | 42633.32 | 0 | 0 | 0 | 0 | 0 | 42633.32
2022072323 | 7 | 0.78133 | 62506.4 | 0.56214 | 20237.04 | 0 | 0 | 1 | 5000 | 20237.04 | 0 | 0 | 0 | 0 | 0 | 37269.36 | 0 | 0 | 0 | 0 | 0 | 37269.36
2022072324 | 7 | 0.73876 | 59100.8 | 0.62152 | 22374.72 | 5e-05 | 0.6 | 1 | 5000 | 22374.72 | 0.6 | 0 | 0 | 0 | 0 | 31725.48 | 0 | 0 | 0 | 0 | 0 | 31725.48
2022072401 | 1 | 0.69903 | 55922.4 | 0.63485 | 22854.6 | 5e-05 | 0.6 | 1 | 5000 | 22854.6 | 0.6 | 0 | 0 | 0 | 0 | 28067.2 | 0 | 0 | 0 | 0 | 0 | 28067.2
2022072402 | 1 | 0.66803 | 53442.4 | 0.61545 | 22156.2 | 5e-05 | 0.6 | 1 | 5000 | 22156.2 | 0.6 | 0 | 0 | 0 | 0 | 26285.6 | 0 | 0 | 0 | 0 | 0 | 26285.6
2022072403 | 1 | 0.64221 | 51376.8 | 0.59841 | 21542.76 | 5e-05 | 0.6 | 1 | 5000 | 21542.76 | 0.6 | 0 | 0 | 0 | 0 | 24833.44 | 0 | 0 | 0 | 0 | 0 | 24833.44
2022072404 | 1 | 0.62033 | 49626.4 | 0.57389 | 20660.04 | 0 | 0 | 1 | 5000 | 20660.04 | 0 | 0 | 0 | 0 | 0 | 23966.36 | 0 | 0 | 0 | 0 | 0 | 23966.36
2022072405 | 1 | 0.60521 | 48416.8 | 0.54167 | 19500.12 | 0 | 0 | 1 | 5000 | 19500.12 | 0 | 0 | 0 | 0 | 0 | 23916.68 | 0 | 0 | 0 | 0 | 0 | 23916.68
2022072406 | 1 | 0.59621 | 47696.8 | 0.50682 | 18245.52 | 0 | 0 | 1 | 5000 | 18245.52 | 0 | 0 | 0 | 0 | 0 | 24451.28 | 0 | 0 | 0 | 0 | 0 | 24451.28
2022072407 | 1 | 0.58618 | 46894.4 | 0.46713 | 16816.68 | 0.00107 | 12.84 | 1 | 5000 | 16816.68 | 12.84 | 0 | 0 | 0 | 0 | 25064.88 | 0 | 0 | 0 | 0 | 0 | 25064.88
2022072408 | 1 | 0.58854 | 47083.2 | 0.43018 | 15486.48 | 0.12284 | 1474.08 | 1 | 5000 | 15486.48 | 1474.08 | 0 | 0 | 0 | 0 | 25122.64 | 0 | 0 | 0 | 0 | 0 | 25122.64
2022072409 | 1 | 0.63009 | 50407.2 | 0.4205 | 15138 | 0.50555 | 6066.6 | 1 | 5000 | 15138 | 6066.6 | 0 | 0 | 0 | 0 | 24202.6 | 0 | 0 | 0 | 0 | 0 | 24202.6
2022072410 | 1 | 0.68467 | 54773.6 | 0.46335 | 16680.6 | 0.70126 | 8415.12 | 1 | 5000 | 16680.6 | 8415.12 | 0 | 0 | 0 | 0 | 24677.88 | 0 | 0 | 0 | 0 | 0 | 24677.88
2022072411 | 1 | 0.73814 | 59051.2 | 0.3863 | 13906.8 | 0.7567 | 9080.4 | 1 | 5000 | 13906.8 | 9080.4 | 0 | 0 | 0 | 0 | 31064 | 0 | 0 | 0 | 0 | 0 | 31064
2022072412 | 1 | 0.7866 | 62928 | 0.3208 | 11548.8 | 0.77484 | 9298.08 | 1 | 5000 | 11548.8 | 9298.08 | 0 | 0 | 0 | 0 | 37081.12 | 0 | 0 | 0 | 0 | 0 | 37081.12
2022072413 | 1 | 0.83414 | 66731.2 | 0.27208 | 9794.88 | 0.76813 | 9217.56 | 1 | 5000 | 9794.88 | 9217.56 | 0 | 0 | 0 | 0 | 42718.76 | 0 | 0 | 0 | 0 | 0 | 42718.76
2022072414 | 1 | 0.87282 | 69825.6 | 0.24498 | 8819.28 | 0.71736 | 8608.32 | 1 | 5000 | 8819.28 | 8608.32 | 0 | 0 | 0 | 0 | 47398 | 0 | 0 | 0 | 0 | 0 | 47398
2022072415 | 1 | 0.90325 | 72260 | 0.25741 | 9266.76 | 0.70302 | 8436.24 | 1 | 5000 | 9266.76 | 8436.24 | 0 | 0 | 0 | 0 | 49557 | 0 | 0 | 0 | 0 | 0 | 49557
2022072416 | 1 | 0.92542 | 74033.6 | 0.2681 | 9651.6 | 0.68045 | 8165.4 | 1 | 5000 | 9651.6 | 8165.4 | 0 | 0 | 0 | 0 | 51216.6 | 0 | 0 | 0 | 0 | 0 | 51216.6
2022072417 | 1 | 0.93865 | 75092 | 0.29217 | 10518.12 | 0.6713 | 8055.6 | 1 | 5000 | 10518.12 | 8055.6 | 0 | 0 | 0 | 0 | 51518.28 | 0 | 0 | 0 | 0 | 0 | 51518.28
2022072418 | 1 | 0.94364 | 75491.2 | 0.32155 | 11575.8 | 0.63783 | 7653.96 | 1 | 5000 | 11575.8 | 7653.96 | 0 | 0 | 0 | 0 | 51261.44 | 0 | 0 | 0 | 0 | 0 | 51261.44
2022072419 | 1 | 0.93258 | 74606.4 | 0.34706 | 12494.16 | 0.57331 | 6879.72 | 1 | 5000 | 12494.16 | 6879.72 | 0 | 0 | 0 | 0 | 50232.52 | 0 | 0 | 0 | 0 | 0 | 50232.52
2022072420 | 1 | 0.90886 | 72708.8 | 0.39537 | 14233.32 | 0.32063 | 3847.56 | 1 | 5000 | 14233.32 | 3847.56 | 0 | 0 | 0 | 0 | 49627.92 | 0 | 0 | 0 | 0 | 0 | 49627.92
2022072421 | 1 | 0.87565 | 70052 | 0.42841 | 15422.76 | 0.03317 | 398.04 | 1 | 5000 | 15422.76 | 398.04 | 0 | 0 | 0 | 0 | 49231.2 | 0 | 0 | 0 | 0 | 0 | 49231.2
2022072422 | 1 | 0.8469 | 67752 | 0.46511 | 16743.96 | 0 | 0 | 1 | 5000 | 16743.96 | 0 | 0 | 0 | 0 | 0 | 46008.04 | 0 | 0 | 0 | 0 | 0 | 46008.04
2022072423 | 1 | 0.79908 | 63926.4 | 0.53312 | 19192.32 | 0 | 0 | 1 | 5000 | 19192.32 | 0 | 0 | 0 | 0 | 0 | 39734.08 | 0 | 0 | 0 | 0 | 0 | 39734.08
2022072424 | 1 | 0.74898 | 59918.4 | 0.56512 | 20344.32 | 0 | 0 | 1 | 5000 | 20344.32 | 0 | 0 | 0 | 0 | 0 | 34574.08 | 0 | 0 | 0 | 0 | 0 | 34574.08
2022072501 | 2 | 0.70252 | 56201.6 | 0.57453 | 20683.08 | 0 | 0 | 1 | 5000 | 20683.08 | 0 | 0 | 0 | 0 | 0 | 30518.52 | 0 | 0 | 0 | 0 | 0 | 30518.52
2022072502 | 2 | 0.67115 | 53692 | 0.56765 | 20435.4 | 0 | 0 | 1 | 5000 | 20435.4 | 0 | 0 | 0 | 0 | 0 | 28256.6 | 0 | 0 | 0 | 0 | 0 | 28256.6
2022072503 | 2 | 0.6458 | 51664 | 0.5466 | 19677.6 | 0 | 0 | 1 | 5000 | 19677.6 | 0 | 0 | 0 | 0 | 0 | 26986.4 | 0 | 0 | 0 | 0 | 0 | 26986.4
2022072504 | 2 | 0.63042 | 50433.6 | 0.52355 | 18847.8 | 0 | 0 | 1 | 5000 | 18847.8 | 0 | 0 | 0 | 0 | 0 | 26585.8 | 0 | 0 | 0 | 0 | 0 | 26585.8
2022072505 | 2 | 0.62549 | 50039.2 | 0.51023 | 18368.28 | 0 | 0 | 1 | 5000 | 18368.28 | 0 | 0 | 0 | 0 | 0 | 26670.92 | 0 | 0 | 0 | 0 | 0 | 26670.92
2022072506 | 2 | 0.6271 | 50168 | 0.49399 | 17783.64 | 0 | 0 | 1 | 5000 | 17783.64 | 0 | 0 | 0 | 0 | 0 | 27384.36 | 0 | 0 | 0 | 0 | 0 | 27384.36
2022072507 | 2 | 0.63282 | 50625.6 | 0.45983 | 16553.88 | 0.00096 | 11.52 | 1 | 5000 | 16553.88 | 11.52 | 0 | 0 | 0 | 0 | 29060.2 | 0 | 0 | 0 | 0 | 0 | 29060.2
2022072508 | 2 | 0.64173 | 51338.4 | 0.39732 | 14303.52 | 0.12267 | 1472.04 | 1 | 5000 | 14303.52 | 1472.04 | 0 | 0 | 0 | 0 | 30562.84 | 0 | 0 | 0 | 0 | 0 | 30562.84
2022072509 | 2 | 0.67884 | 54307.2 | 0.36825 | 13257 | 0.50165 | 6019.8 | 1 | 5000 | 13257 | 6019.8 | 0 | 0 | 0 | 0 | 30030.4 | 0 | 0 | 0 | 0 | 0 | 30030.4
2022072510 | 2 | 0.73104 | 58483.2 | 0.43727 | 15741.72 | 0.71858 | 8622.96 | 1 | 5000 | 15741.72 | 8622.96 | 0 | 0 | 0 | 0 | 29118.52 | 0 | 0 | 0 | 0 | 0 | 29118.52
2022072511 | 2 | 0.78441 | 62752.8 | 0.40601 | 14616.36 | 0.78212 | 9385.44 | 1 | 5000 | 14616.36 | 9385.44 | 0 | 0 | 0 | 0 | 33751 | 0 | 0 | 0 | 0 | 0 | 33751
2022072512 | 2 | 0.8379 | 67032 | 0.34438 | 12397.68 | 0.78997 | 9479.64 | 1 | 5000 | 12397.68 | 9479.64 | 0 | 0 | 0 | 0 | 40154.68 | 0 | 0 | 0 | 0 | 0 | 40154.68
2022072513 | 2 | 0.89023 | 71218.4 | 0.29705 | 10693.8 | 0.78919 | 9470.28 | 1 | 5000 | 10693.8 | 9470.28 | 0 | 0 | 0 | 0 | 46054.32 | 0 | 0 | 0 | 0 | 0 | 46054.32
2022072514 | 2 | 0.93294 | 74635.2 | 0.31482 | 11333.52 | 0.76776 | 9213.12 | 1 | 5000 | 11333.52 | 9213.12 | 0 | 0 | 0 | 0 | 49088.56 | 0 | 0 | 0 | 0 | 0 | 49088.56
2022072515 | 2 | 0.96432 | 77145.6 | 0.34599 | 12455.64 | 0.7427 | 8912.4 | 1 | 5000 | 12455.64 | 8912.4 | 0 | 0 | 0 | 0 | 50777.56 | 0 | 0 | 0 | 0 | 0 | 50777.56
2022072516 | 2 | 0.97906 | 78324.8 | 0.36533 | 13151.88 | 0.70725 | 8487 | 1 | 5000 | 13151.88 | 8487 | 0 | 0 | 0 | 0 | 51685.92 | 0 | 0 | 0 | 0 | 0 | 51685.92
2022072517 | 2 | 0.9866 | 78928 | 0.37143 | 13371.48 | 0.69248 | 8309.76 | 1 | 5000 | 13371.48 | 8309.76 | 0 | 0 | 0 | 0 | 52246.76 | 0 | 0 | 0 | 0 | 0 | 52246.76
2022072518 | 2 | 0.9846 | 78768 | 0.3795 | 13662 | 0.6776 | 8131.2 | 1 | 5000 | 13662 | 8131.2 | 0 | 0 | 0 | 0 | 51974.8 | 0 | 0 | 0 | 0 | 0 | 51974.8
2022072519 | 2 | 0.96855 | 77484 | 0.40615 | 14621.4 | 0.58543 | 7025.16 | 1 | 5000 | 14621.4 | 7025.16 | 0 | 0 | 0 | 0 | 50837.44 | 0 | 0 | 0 | 0 | 0 | 50837.44
2022072520 | 2 | 0.93647 | 74917.6 | 0.43974 | 15830.64 | 0.30062 | 3607.44 | 1 | 5000 | 15830.64 | 3607.44 | 0 | 0 | 0 | 0 | 50479.52 | 0 | 0 | 0 | 0 | 0 | 50479.52
2022072521 | 2 | 0.89681 | 71744.8 | 0.45425 | 16353 | 0.02569 | 308.28 | 1 | 5000 | 16353 | 308.28 | 0 | 0 | 0 | 0 | 50083.52 | 0 | 0 | 0 | 0 | 0 | 50083.52
2022072522 | 2 | 0.86404 | 69123.2 | 0.48222 | 17359.92 | 0 | 0 | 1 | 5000 | 17359.92 | 0 | 0 | 0 | 0 | 0 | 46763.28 | 0 | 0 | 0 | 0 | 0 | 46763.28
2022072523 | 2 | 0.81358 | 65086.4 | 0.55181 | 19865.16 | 0 | 0 | 1 | 5000 | 19865.16 | 0 | 0 | 0 | 0 | 0 | 40221.24 | 0 | 0 | 0 | 0 | 0 | 40221.24
2022072524 | 2 | 0.75937 | 60749.6 | 0.59377 | 21375.72 | 0 | 0 | 1 | 5000 | 21375.72 | 0 | 0 | 0 | 0 | 0 | 34373.88 | 0 | 0 | 0 | 0 | 0 | 34373.88
2022072601 | 3 | 0.71125 | 56900 | 0.59875 | 21555 | 0 | 0 | 1 | 5000 | 21555 | 0 | 0 | 0 | 0 | 0 | 30345 | 0 | 0 | 0 | 0 | 0 | 30345
2022072602 | 3 | 0.67479 | 53983.2 | 0.58309 | 20991.24 | 0 | 0 | 1 | 5000 | 20991.24 | 0 | 0 | 0 | 0 | 0 | 27991.96 | 0 | 0 | 0 | 0 | 0 | 27991.96
2022072603 | 3 | 0.64765 | 51812 | 0.56945 | 20500.2 | 0 | 0 | 1 | 5000 | 20500.2 | 0 | 0 | 0 | 0 | 0 | 26311.8 | 0 | 0 | 0 | 0 | 0 | 26311.8
2022072604 | 3 | 0.62944 | 50355.2 | 0.55869 | 20112.84 | 0 | 0 | 1 | 5000 | 20112.84 | 0 | 0 | 0 | 0 | 0 | 25242.36 | 0 | 0 | 0 | 0 | 0 | 25242.36
2022072605 | 3 | 0.62071 | 49656.8 | 0.53594 | 19293.84 | 0 | 0 | 1 | 5000 | 19293.84 | 0 | 0 | 0 | 0 | 0 | 25362.96 | 0 | 0 | 0 | 0 | 0 | 25362.96
2022072606 | 3 | 0.623 | 49840 | 0.49827 | 17937.72 | 0 | 0 | 1 | 5000 | 17937.72 | 0 | 0 | 0 | 0 | 0 | 26902.28 | 0 | 0 | 0 | 0 | 0 | 26902.28
2022072607 | 3 | 0.63105 | 50484 | 0.46218 | 16638.48 | 0.00085 | 10.2 | 1 | 5000 | 16638.48 | 10.2 | 0 | 0 | 0 | 0 | 28835.32 | 0 | 0 | 0 | 0 | 0 | 28835.32
2022072608 | 3 | 0.6368 | 50944 | 0.41932 | 15095.52 | 0.12449 | 1493.88 | 1 | 5000 | 15095.52 | 1493.88 | 0 | 0 | 0 | 0 | 29354.6 | 0 | 0 | 0 | 0 | 0 | 29354.6
2022072609 | 3 | 0.67349 | 53879.2 | 0.38883 | 13997.88 | 0.51521 | 6182.52 | 1 | 5000 | 13997.88 | 6182.52 | 0 | 0 | 0 | 0 | 28698.8 | 0 | 0 | 0 | 0 | 0 | 28698.8
2022072610 | 3 | 0.7202 | 57616 | 0.44411 | 15987.96 | 0.63984 | 7678.08 | 1 | 5000 | 15987.96 | 7678.08 | 0 | 0 | 0 | 0 | 28949.96 | 0 | 0 | 0 | 0 | 0 | 28949.96
2022072611 | 3 | 0.77182 | 61745.6 | 0.41128 | 14806.08 | 0.75929 | 9111.48 | 1 | 5000 | 14806.08 | 9111.48 | 0 | 0 | 0 | 0 | 32828.04 | 0 | 0 | 0 | 0 | 0 | 32828.04
2022072612 | 3 | 0.82905 | 66324 | 0.36091 | 12992.76 | 0.78919 | 9470.28 | 1 | 5000 | 12992.76 | 9470.28 | 0 | 0 | 0 | 0 | 38860.96 | 0 | 0 | 0 | 0 | 0 | 38860.96
2022072613 | 3 | 0.87766 | 70212.8 | 0.30967 | 11148.12 | 0.77365 | 9283.8 | 1 | 5000 | 11148.12 | 9283.8 | 0 | 0 | 0 | 0 | 44780.88 | 0 | 0 | 0 | 0 | 0 | 44780.88
2022072614 | 3 | 0.91833 | 73466.4 | 0.29784 | 10722.24 | 0.75245 | 9029.4 | 1 | 5000 | 10722.24 | 9029.4 | 0 | 0 | 0 | 0 | 48714.76 | 0 | 0 | 0 | 0 | 0 | 48714.76
2022072615 | 3 | 0.94977 | 75981.6 | 0.29816 | 10733.76 | 0.7269 | 8722.8 | 1 | 5000 | 10733.76 | 8722.8 | 0 | 0 | 0 | 0 | 51525.04 | 0 | 0 | 0 | 0 | 0 | 51525.04
2022072616 | 3 | 0.9704 | 77632 | 0.31081 | 11189.16 | 0.71016 | 8521.92 | 1 | 5000 | 11189.16 | 8521.92 | 0 | 0 | 0 | 0 | 52920.92 | 0 | 0 | 0 | 0 | 0 | 52920.92
2022072617 | 3 | 0.98376 | 78700.8 | 0.32479 | 11692.44 | 0.70467 | 8456.04 | 1 | 5000 | 11692.44 | 8456.04 | 0 | 0 | 0 | 0 | 53552.32 | 0 | 0 | 0 | 0 | 0 | 53552.32
2022072618 | 3 | 0.9843 | 78744 | 0.33786 | 12162.96 | 0.7065 | 8478 | 1 | 5000 | 12162.96 | 8478 | 0 | 0 | 0 | 0 | 53103.04 | 0 | 0 | 0 | 0 | 0 | 53103.04
2022072619 | 3 | 0.96769 | 77415.2 | 0.36182 | 13025.52 | 0.6074 | 7288.8 | 1 | 5000 | 13025.52 | 7288.8 | 0 | 0 | 0 | 0 | 52100.88 | 0 | 0 | 0 | 0 | 0 | 52100.88
2022072620 | 3 | 0.93527 | 74821.6 | 0.39054 | 14059.44 | 0.30672 | 3680.64 | 1 | 5000 | 14059.44 | 3680.64 | 0 | 0 | 0 | 0 | 52081.52 | 0 | 0 | 0 | 0 | 0 | 52081.52
2022072621 | 3 | 0.89787 | 71829.6 | 0.4037 | 14533.2 | 0.02731 | 327.72 | 1 | 5000 | 14533.2 | 327.72 | 0 | 0 | 0 | 0 | 51968.68 | 0 | 0 | 0 | 0 | 0 | 51968.68
2022072622 | 3 | 0.86833 | 69466.4 | 0.43167 | 15540.12 | 0 | 0 | 1 | 5000 | 15540.12 | 0 | 0 | 0 | 0 | 0 | 48926.28 | 0 | 0 | 0 | 0 | 0 | 48926.28
2022072623 | 3 | 0.82106 | 65684.8 | 0.50578 | 18208.08 | 0 | 0 | 1 | 5000 | 18208.08 | 0 | 0 | 0 | 0 | 0 | 42476.72 | 0 | 0 | 0 | 0 | 0 | 42476.72
2022072624 | 3 | 0.77003 | 61602.4 | 0.55295 | 19906.2 | 0 | 0 | 1 | 5000 | 19906.2 | 0 | 0 | 0 | 0 | 0 | 36696.2 | 0 | 0 | 0 | 0 | 0 | 36696.2
2022072701 | 4 | 0.72315 | 57852 | 0.57182 | 20585.52 | 0 | 0 | 1 | 5000 | 20585.52 | 0 | 0 | 0 | 0 | 0 | 32266.48 | 0 | 0 | 0 | 0 | 0 | 32266.48
2022072702 | 4 | 0.68739 | 54991.2 | 0.55759 | 20073.24 | 0 | 0 | 1 | 5000 | 20073.24 | 0 | 0 | 0 | 0 | 0 | 29917.96 | 0 | 0 | 0 | 0 | 0 | 29917.96
2022072703 | 4 | 0.66254 | 53003.2 | 0.53987 | 19435.32 | 0 | 0 | 1 | 5000 | 19435.32 | 0 | 0 | 0 | 0 | 0 | 28567.88 | 0 | 0 | 0 | 0 | 0 | 28567.88
2022072704 | 4 | 0.64537 | 51629.6 | 0.51545 | 18556.2 | 0 | 0 | 1 | 5000 | 18556.2 | 0 | 0 | 0 | 0 | 0 | 28073.4 | 0 | 0 | 0 | 0 | 0 | 28073.4
2022072705 | 4 | 0.63369 | 50695.2 | 0.50437 | 18157.32 | 0 | 0 | 1 | 5000 | 18157.32 | 0 | 0 | 0 | 0 | 0 | 27537.88 | 0 | 0 | 0 | 0 | 0 | 27537.88
2022072706 | 4 | 0.63566 | 50852.8 | 0.48166 | 17339.76 | 0 | 0 | 1 | 5000 | 17339.76 | 0 | 0 | 0 | 0 | 0 | 28513.04 | 0 | 0 | 0 | 0 | 0 | 28513.04
2022072707 | 4 | 0.64558 | 51646.4 | 0.44781 | 16121.16 | 0.00062 | 7.44 | 1 | 5000 | 16121.16 | 7.44 | 0 | 0 | 0 | 0 | 30517.8 | 0 | 0 | 0 | 0 | 0 | 30517.8
2022072708 | 4 | 0.65109 | 52087.2 | 0.39066 | 14063.76 | 0.11483 | 1377.96 | 1 | 5000 | 14063.76 | 1377.96 | 0 | 0 | 0 | 0 | 31645.48 | 0 | 0 | 0 | 0 | 0 | 31645.48
2022072709 | 4 | 0.68424 | 54739.2 | 0.33228 | 11962.08 | 0.5005 | 6006 | 1 | 5000 | 11962.08 | 6006 | 0 | 0 | 0 | 0 | 31771.12 | 0 | 0 | 0 | 0 | 0 | 31771.12
2022072710 | 4 | 0.73103 | 58482.4 | 0.347 | 12492 | 0.70362 | 8443.44 | 1 | 5000 | 12492 | 8443.44 | 0 | 0 | 0 | 0 | 32546.96 | 0 | 0 | 0 | 0 | 0 | 32546.96
2022072711 | 4 | 0.7825 | 62600 | 0.29407 | 10586.52 | 0.7526 | 9031.2 | 1 | 5000 | 10586.52 | 9031.2 | 0 | 0 | 0 | 0 | 37982.28 | 0 | 0 | 0 | 0 | 0 | 37982.28
2022072712 | 4 | 0.83304 | 66643.2 | 0.21104 | 7597.44 | 0.75105 | 9012.6 | 1 | 5000 | 7597.44 | 9012.6 | 0 | 0 | 0 | 0 | 45033.16 | 0 | 0 | 0 | 0 | 0 | 45033.16
2022072713 | 4 | 0.87631 | 70104.8 | 0.19068 | 6864.48 | 0.7688 | 9225.6 | 1 | 5000 | 6864.48 | 9225.6 | 0 | 0 | 0 | 0 | 49014.72 | 0 | 0 | 0 | 0 | 0 | 49014.72
2022072714 | 4 | 0.91462 | 73169.6 | 0.19808 | 7130.88 | 0.72979 | 8757.48 | 1 | 5000 | 7130.88 | 8757.48 | 0 | 0 | 0 | 0 | 52281.24 | 0 | 0 | 0 | 0 | 0 | 52281.24
2022072715 | 4 | 0.93616 | 74892.8 | 0.23249 | 8369.64 | 0.72422 | 8690.64 | 1 | 5000 | 8369.64 | 8690.64 | 0 | 0 | 0 | 0 | 52832.52 | 0 | 0 | 0 | 0 | 0 | 52832.52
2022072716 | 4 | 0.94887 | 75909.6 | 0.23664 | 8519.04 | 0.69636 | 8356.32 | 1 | 5000 | 8519.04 | 8356.32 | 0 | 0 | 0 | 0 | 54034.24 | 0 | 0 | 0 | 0 | 0 | 54034.24
2022072717 | 4 | 0.95417 | 76333.6 | 0.26994 | 9717.84 | 0.65497 | 7859.64 | 1 | 5000 | 9717.84 | 7859.64 | 0 | 0 | 0 | 0 | 53756.12 | 0 | 0 | 0 | 0 | 0 | 53756.12
2022072718 | 4 | 0.94851 | 75880.8 | 0.30755 | 11071.8 | 0.63141 | 7576.92 | 1 | 5000 | 11071.8 | 7576.92 | 0 | 0 | 0 | 0 | 52232.08 | 0 | 0 | 0 | 0 | 0 | 52232.08
2022072719 | 4 | 0.93045 | 74436 | 0.34632 | 12467.52 | 0.56342 | 6761.04 | 1 | 5000 | 12467.52 | 6761.04 | 0 | 0 | 0 | 0 | 50207.44 | 0 | 0 | 0 | 0 | 0 | 50207.44
2022072720 | 4 | 0.90533 | 72426.4 | 0.37704 | 13573.44 | 0.2806 | 3367.2 | 1 | 5000 | 13573.44 | 3367.2 | 0 | 0 | 0 | 0 | 50485.76 | 0 | 0 | 0 | 0 | 0 | 50485.76
2022072721 | 4 | 0.87221 | 69776.8 | 0.39645 | 14272.2 | 0.01539 | 184.68 | 1 | 5000 | 14272.2 | 184.68 | 0 | 0 | 0 | 0 | 50319.92 | 0 | 0 | 0 | 0 | 0 | 50319.92
2022072722 | 4 | 0.84022 | 67217.6 | 0.43363 | 15610.68 | 0 | 0 | 1 | 5000 | 15610.68 | 0 | 0 | 0 | 0 | 0 | 46606.92 | 0 | 0 | 0 | 0 | 0 | 46606.92
2022072723 | 4 | 0.79339 | 63471.2 | 0.48376 | 17415.36 | 0 | 0 | 1 | 5000 | 17415.36 | 0 | 0 | 0 | 0 | 0 | 41055.84 | 0 | 0 | 0 | 0 | 0 | 41055.84
2022072724 | 4 | 0.74334 | 59467.2 | 0.52198 | 18791.28 | 0 | 0 | 1 | 5000 | 18791.28 | 0 | 0 | 0 | 0 | 0 | 35675.92 | 0 | 0 | 0 | 0 | 0 | 35675.92
2022072801 | 5 | 0.70185 | 56148 | 0.52869 | 19032.84 | 0 | 0 | 1 | 5000 | 19032.84 | 0 | 0 | 0 | 0 | 0 | 32115.16 | 0 | 0 | 0 | 0 | 0 | 32115.16
2022072802 | 5 | 0.66536 | 53228.8 | 0.50668 | 18240.48 | 0 | 0 | 1 | 5000 | 18240.48 | 0 | 0 | 0 | 0 | 0 | 29988.32 | 0 | 0 | 0 | 0 | 0 | 29988.32
2022072803 | 5 | 0.64248 | 51398.4 | 0.4924 | 17726.4 | 0 | 0 | 1 | 5000 | 17726.4 | 0 | 0 | 0 | 0 | 0 | 28672 | 0 | 0 | 0 | 0 | 0 | 28672
2022072804 | 5 | 0.62268 | 49814.4 | 0.47066 | 16943.76 | 0 | 0 | 1 | 5000 | 16943.76 | 0 | 0 | 0 | 0 | 0 | 27870.64 | 0 | 0 | 0 | 0 | 0 | 27870.64
2022072805 | 5 | 0.61395 | 49116 | 0.44048 | 15857.28 | 0 | 0 | 1 | 5000 | 15857.28 | 0 | 0 | 0 | 0 | 0 | 28258.72 | 0 | 0 | 0 | 0 | 0 | 28258.72
2022072806 | 5 | 0.61925 | 49540 | 0.38611 | 13899.96 | 0 | 0 | 1 | 5000 | 13899.96 | 0 | 0 | 0 | 0 | 0 | 30640.04 | 0 | 0 | 0 | 0 | 0 | 30640.04
2022072807 | 5 | 0.62984 | 50387.2 | 0.34972 | 12589.92 | 0.00058 | 6.96 | 1 | 5000 | 12589.92 | 6.96 | 0 | 0 | 0 | 0 | 32790.32 | 0 | 0 | 0 | 0 | 0 | 32790.32
2022072808 | 5 | 0.64017 | 51213.6 | 0.31956 | 11504.16 | 0.1178 | 1413.6 | 1 | 5000 | 11504.16 | 1413.6 | 0 | 0 | 0 | 0 | 33295.84 | 0 | 0 | 0 | 0 | 0 | 33295.84
2022072809 | 5 | 0.67648 | 54118.4 | 0.28839 | 10382.04 | 0.49875 | 5985 | 1 | 5000 | 10382.04 | 5985 | 0 | 0 | 0 | 0 | 32751.36 | 0 | 0 | 0 | 0 | 0 | 32751.36
2022072810 | 5 | 0.72759 | 58207.2 | 0.32563 | 11722.68 | 0.73584 | 8830.08 | 1 | 5000 | 11722.68 | 8830.08 | 0 | 0 | 0 | 0 | 32654.44 | 0 | 0 | 0 | 0 | 0 | 32654.44
2022072811 | 5 | 0.78222 | 62577.6 | 0.28192 | 10149.12 | 0.77736 | 9328.32 | 1 | 5000 | 10149.12 | 9328.32 | 0 | 0 | 0 | 0 | 38100.16 | 0 | 0 | 0 | 0 | 0 | 38100.16
2022072812 | 5 | 0.83289 | 66631.2 | 0.22242 | 8007.12 | 0.77838 | 9340.56 | 1 | 5000 | 8007.12 | 9340.56 | 0 | 0 | 0 | 0 | 44283.52 | 0 | 0 | 0 | 0 | 0 | 44283.52
2022072813 | 5 | 0.88066 | 70452.8 | 0.17288 | 6223.68 | 0.76904 | 9228.48 | 1 | 5000 | 6223.68 | 9228.48 | 0 | 0 | 0 | 0 | 50000.64 | 0 | 0 | 0 | 0 | 0 | 50000.64
2022072814 | 5 | 0.9193 | 73544 | 0.1697 | 6109.2 | 0.75563 | 9067.56 | 1 | 5000 | 6109.2 | 9067.56 | 0 | 0 | 0 | 0 | 53367.24 | 0 | 0 | 0 | 0 | 0 | 53367.24
2022072815 | 5 | 0.94287 | 75429.6 | 0.19677 | 7083.72 | 0.73231 | 8787.72 | 1 | 5000 | 7083.72 | 8787.72 | 0 | 0 | 0 | 0 | 54558.16 | 0 | 0 | 0 | 0 | 0 | 54558.16
2022072816 | 5 | 0.9549 | 76392 | 0.22171 | 7981.56 | 0.71767 | 8612.04 | 1 | 5000 | 7981.56 | 8612.04 | 0 | 0 | 0 | 0 | 54798.4 | 0 | 0 | 0 | 0 | 0 | 54798.4
2022072817 | 5 | 0.95276 | 76220.8 | 0.25987 | 9355.32 | 0.69756 | 8370.72 | 1 | 5000 | 9355.32 | 8370.72 | 0 | 0 | 0 | 0 | 53494.76 | 0 | 0 | 0 | 0 | 0 | 53494.76
2022072818 | 5 | 0.94449 | 75559.2 | 0.30458 | 10964.88 | 0.68088 | 8170.56 | 1 | 5000 | 10964.88 | 8170.56 | 0 | 0 | 0 | 0 | 51423.76 | 0 | 0 | 0 | 0 | 0 | 51423.76
2022072819 | 5 | 0.93002 | 74401.6 | 0.35067 | 12624.12 | 0.59425 | 7131 | 1 | 5000 | 12624.12 | 7131 | 0 | 0 | 0 | 0 | 49646.48 | 0 | 0 | 0 | 0 | 0 | 49646.48
2022072820 | 5 | 0.9016 | 72128 | 0.40381 | 14537.16 | 0.32251 | 3870.12 | 1 | 5000 | 14537.16 | 3870.12 | 0 | 0 | 0 | 0 | 48720.72 | 0 | 0 | 0 | 0 | 0 | 48720.72
2022072821 | 5 | 0.87107 | 69685.6 | 0.41615 | 14981.4 | 0.03151 | 378.12 | 1 | 5000 | 14981.4 | 378.12 | 0 | 0 | 0 | 0 | 49326.08 | 0 | 0 | 0 | 0 | 0 | 49326.08
2022072822 | 5 | 0.84288 | 67430.4 | 0.39705 | 14293.8 | 0 | 0 | 1 | 5000 | 14293.8 | 0 | 0 | 0 | 0 | 0 | 48136.6 | 0 | 0 | 0 | 0 | 0 | 48136.6
2022072823 | 5 | 0.79647 | 63717.6 | 0.43426 | 15633.36 | 0 | 0 | 1 | 5000 | 15633.36 | 0 | 0 | 0 | 0 | 0 | 43084.24 | 0 | 0 | 0 | 0 | 0 | 43084.24
2022072824 | 5 | 0.74625 | 59700 | 0.48775 | 17559 | 0 | 0 | 1 | 5000 | 17559 | 0 | 0 | 0 | 0 | 0 | 37141 | 0 | 0 | 0 | 0 | 0 | 37141
2022072901 | 6 | 0.70222 | 56177.6 | 0.50495 | 18178.2 | 0 | 0 | 1 | 5000 | 18178.2 | 0 | 0 | 0 | 0 | 0 | 32999.4 | 0 | 0 | 0 | 0 | 0 | 32999.4
2022072902 | 6 | 0.66612 | 53289.6 | 0.4775 | 17190 | 0 | 0 | 1 | 5000 | 17190 | 0 | 0 | 0 | 0 | 0 | 31099.6 | 0 | 0 | 0 | 0 | 0 | 31099.6
2022072903 | 6 | 0.63986 | 51188.8 | 0.43143 | 15531.48 | 0 | 0 | 1 | 5000 | 15531.48 | 0 | 0 | 0 | 0 | 0 | 30657.32 | 0 | 0 | 0 | 0 | 0 | 30657.32
2022072904 | 6 | 0.62499 | 49999.2 | 0.39011 | 14043.96 | 0 | 0 | 1 | 5000 | 14043.96 | 0 | 0 | 0 | 0 | 0 | 30955.24 | 0 | 0 | 0 | 0 | 0 | 30955.24
2022072905 | 6 | 0.61439 | 49151.2 | 0.37208 | 13394.88 | 0 | 0 | 1 | 5000 | 13394.88 | 0 | 0 | 0 | 0 | 0 | 30756.32 | 0 | 0 | 0 | 0 | 0 | 30756.32
2022072906 | 6 | 0.61876 | 49500.8 | 0.33756 | 12152.16 | 0 | 0 | 1 | 5000 | 12152.16 | 0 | 0 | 0 | 0 | 0 | 32348.64 | 0 | 0 | 0 | 0 | 0 | 32348.64
2022072907 | 6 | 0.62703 | 50162.4 | 0.28339 | 10202.04 | 0.00038 | 4.56 | 1 | 5000 | 10202.04 | 4.56 | 0 | 0 | 0 | 0 | 34955.8 | 0 | 0 | 0 | 0 | 0 | 34955.8
2022072908 | 6 | 0.63595 | 50876 | 0.24489 | 8816.04 | 0.11226 | 1347.12 | 1 | 5000 | 8816.04 | 1347.12 | 0 | 0 | 0 | 0 | 35712.84 | 0 | 0 | 0 | 0 | 0 | 35712.84
2022072909 | 6 | 0.67435 | 53948 | 0.21829 | 7858.44 | 0.5091 | 6109.2 | 1 | 5000 | 7858.44 | 6109.2 | 0 | 0 | 0 | 0 | 34980.36 | 0 | 0 | 0 | 0 | 0 | 34980.36
2022072910 | 6 | 0.72644 | 58115.2 | 0.23379 | 8416.44 | 0.69722 | 8366.64 | 1 | 5000 | 8416.44 | 8366.64 | 0 | 0 | 0 | 0 | 36332.12 | 0 | 0 | 0 | 0 | 0 | 36332.12
2022072911 | 6 | 0.78068 | 62454.4 | 0.20275 | 7299 | 0.7437 | 8924.4 | 1 | 5000 | 7299 | 8924.4 | 0 | 0 | 0 | 0 | 41231 | 0 | 0 | 0 | 0 | 0 | 41231
2022072912 | 6 | 0.83872 | 67097.6 | 0.17206 | 6194.16 | 0.74687 | 8962.44 | 1 | 5000 | 6194.16 | 8962.44 | 0 | 0 | 0 | 0 | 46941 | 0 | 0 | 0 | 0 | 0 | 46941
2022072913 | 6 | 0.88474 | 70779.2 | 0.17263 | 6214.68 | 0.73352 | 8802.24 | 1 | 5000 | 6214.68 | 8802.24 | 0 | 0 | 0 | 0 | 50762.28 | 0 | 0 | 0 | 0 | 0 | 50762.28
2022072914 | 6 | 0.91964 | 73571.2 | 0.20667 | 7440.12 | 0.70721 | 8486.52 | 1 | 5000 | 7440.12 | 8486.52 | 0 | 0 | 0 | 0 | 52644.56 | 0 | 0 | 0 | 0 | 0 | 52644.56
2022072915 | 6 | 0.93822 | 75057.6 | 0.24643 | 8871.48 | 0.68262 | 8191.44 | 1 | 5000 | 8871.48 | 8191.44 | 0 | 0 | 0 | 0 | 52994.68 | 0 | 0 | 0 | 0 | 0 | 52994.68
2022072916 | 6 | 0.95017 | 76013.6 | 0.29627 | 10665.72 | 0.63662 | 7639.44 | 1 | 5000 | 10665.72 | 7639.44 | 0 | 0 | 0 | 0 | 52708.44 | 0 | 0 | 0 | 0 | 0 | 52708.44
2022072917 | 6 | 0.95931 | 76744.8 | 0.33995 | 12238.2 | 0.61213 | 7345.56 | 1 | 5000 | 12238.2 | 7345.56 | 0 | 0 | 0 | 0 | 52161.04 | 0 | 0 | 0 | 0 | 0 | 52161.04
2022072918 | 6 | 0.95097 | 76077.6 | 0.3813 | 13726.8 | 0.56416 | 6769.92 | 1 | 5000 | 13726.8 | 6769.92 | 0 | 0 | 0 | 0 | 50580.88 | 0 | 0 | 0 | 0 | 0 | 50580.88
2022072919 | 6 | 0.91982 | 73585.6 | 0.4363 | 15706.8 | 0.53531 | 6423.72 | 1 | 5000 | 15706.8 | 6423.72 | 0 | 0 | 0 | 0 | 46455.08 | 0 | 0 | 0 | 0 | 0 | 46455.08
2022072920 | 6 | 0.88259 | 70607.2 | 0.42733 | 15383.88 | 0.30073 | 3608.76 | 1 | 5000 | 15383.88 | 3608.76 | 0 | 0 | 0 | 0 | 46614.56 | 0 | 0 | 0 | 0 | 0 | 46614.56
2022072921 | 6 | 0.85085 | 68068 | 0.37515 | 13505.4 | 0.02625 | 315 | 1 | 5000 | 13505.4 | 315 | 0 | 0 | 0 | 0 | 49247.6 | 0 | 0 | 0 | 0 | 0 | 49247.6
2022072922 | 6 | 0.82344 | 65875.2 | 0.38568 | 13884.48 | 0 | 0 | 1 | 5000 | 13884.48 | 0 | 0 | 0 | 0 | 0 | 46990.72 | 0 | 0 | 0 | 0 | 0 | 46990.72
2022072923 | 6 | 0.78222 | 62577.6 | 0.3693 | 13294.8 | 0 | 0 | 1 | 5000 | 13294.8 | 0 | 0 | 0 | 0 | 0 | 44282.8 | 0 | 0 | 0 | 0 | 0 | 44282.8
2022072924 | 6 | 0.73706 | 58964.8 | 0.37272 | 13417.92 | 0 | 0 | 1 | 5000 | 13417.92 | 0 | 0 | 0 | 0 | 0 | 40546.88 | 0 | 0 | 0 | 0 | 0 | 40546.88
2022073001 | 7 | 0.69487 | 55589.6 | 0.37373 | 13454.28 | 0 | 0 | 1 | 5000 | 13454.28 | 0 | 0 | 0 | 0 | 0 | 37135.32 | 0 | 0 | 0 | 0 | 0 | 37135.32
2022073002 | 7 | 0.66224 | 52979.2 | 0.36814 | 13253.04 | 0 | 0 | 1 | 5000 | 13253.04 | 0 | 0 | 0 | 0 | 0 | 34726.16 | 0 | 0 | 0 | 0 | 0 | 34726.16
2022073003 | 7 | 0.63699 | 50959.2 | 0.37021 | 13327.56 | 0 | 0 | 1 | 5000 | 13327.56 | 0 | 0 | 0 | 0 | 0 | 32631.64 | 0 | 0 | 0 | 0 | 0 | 32631.64
2022073004 | 7 | 0.61482 | 49185.6 | 0.35363 | 12730.68 | 0 | 0 | 1 | 5000 | 12730.68 | 0 | 0 | 0 | 0 | 0 | 31454.92 | 0 | 0 | 0 | 0 | 0 | 31454.92
2022073005 | 7 | 0.60324 | 48259.2 | 0.35913 | 12928.68 | 0 | 0 | 1 | 5000 | 12928.68 | 0 | 0 | 0 | 0 | 0 | 30330.52 | 0 | 0 | 0 | 0 | 0 | 30330.52
2022073006 | 7 | 0.59699 | 47759.2 | 0.32938 | 11857.68 | 0 | 0 | 1 | 5000 | 11857.68 | 0 | 0 | 0 | 0 | 0 | 30901.52 | 0 | 0 | 0 | 0 | 0 | 30901.52
2022073007 | 7 | 0.59412 | 47529.6 | 0.2833 | 10198.8 | 0.00037 | 4.44 | 1 | 5000 | 10198.8 | 4.44 | 0 | 0 | 0 | 0 | 32326.36 | 0 | 0 | 0 | 0 | 0 | 32326.36
2022073008 | 7 | 0.5968 | 47744 | 0.23731 | 8543.16 | 0.08195 | 983.4 | 1 | 5000 | 8543.16 | 983.4 | 0 | 0 | 0 | 0 | 33217.44 | 0 | 0 | 0 | 0 | 0 | 33217.44
2022073009 | 7 | 0.63655 | 50924 | 0.20658 | 7436.88 | 0.43373 | 5204.76 | 1 | 5000 | 7436.88 | 5204.76 | 0 | 0 | 0 | 0 | 33282.36 | 0 | 0 | 0 | 0 | 0 | 33282.36
2022073010 | 7 | 0.68907 | 55125.6 | 0.21859 | 7869.24 | 0.65239 | 7828.68 | 1 | 5000 | 7869.24 | 7828.68 | 0 | 0 | 0 | 0 | 34427.68 | 0 | 0 | 0 | 0 | 0 | 34427.68
2022073011 | 7 | 0.74051 | 59240.8 | 0.20009 | 7203.24 | 0.74931 | 8991.72 | 1 | 5000 | 7203.24 | 8991.72 | 0 | 0 | 0 | 0 | 38045.84 | 0 | 0 | 0 | 0 | 0 | 38045.84
2022073012 | 7 | 0.79348 | 63478.4 | 0.19506 | 7022.16 | 0.75685 | 9082.2 | 1 | 5000 | 7022.16 | 9082.2 | 0 | 0 | 0 | 0 | 42374.04 | 0 | 0 | 0 | 0 | 0 | 42374.04
2022073013 | 7 | 0.84355 | 67484 | 0.18933 | 6815.88 | 0.71496 | 8579.52 | 1 | 5000 | 6815.88 | 8579.52 | 0 | 0 | 0 | 0 | 47088.6 | 0 | 0 | 0 | 0 | 0 | 47088.6
2022073014 | 7 | 0.88018 | 70414.4 | 0.20221 | 7279.56 | 0.71998 | 8639.76 | 1 | 5000 | 7279.56 | 8639.76 | 0 | 0 | 0 | 0 | 49495.08 | 0 | 0 | 0 | 0 | 0 | 49495.08
2022073015 | 7 | 0.90603 | 72482.4 | 0.22442 | 8079.12 | 0.69878 | 8385.36 | 1 | 5000 | 8079.12 | 8385.36 | 0 | 0 | 0 | 0 | 51017.92 | 0 | 0 | 0 | 0 | 0 | 51017.92
2022073016 | 7 | 0.9195 | 73560 | 0.24184 | 8706.24 | 0.71104 | 8532.48 | 1 | 5000 | 8706.24 | 8532.48 | 0 | 0 | 0 | 0 | 51321.28 | 0 | 0 | 0 | 0 | 0 | 51321.28
2022073017 | 7 | 0.92848 | 74278.4 | 0.26208 | 9434.88 | 0.68216 | 8185.92 | 1 | 5000 | 9434.88 | 8185.92 | 0 | 0 | 0 | 0 | 51657.6 | 0 | 0 | 0 | 0 | 0 | 51657.6
2022073018 | 7 | 0.92364 | 73891.2 | 0.28554 | 10279.44 | 0.65172 | 7820.64 | 1 | 5000 | 10279.44 | 7820.64 | 0 | 0 | 0 | 0 | 50791.12 | 0 | 0 | 0 | 0 | 0 | 50791.12
2022073019 | 7 | 0.90179 | 72143.2 | 0.29367 | 10572.12 | 0.55671 | 6680.52 | 1 | 5000 | 10572.12 | 6680.52 | 0 | 0 | 0 | 0 | 49890.56 | 0 | 0 | 0 | 0 | 0 | 49890.56
2022073020 | 7 | 0.86886 | 69508.8 | 0.29477 | 10611.72 | 0.29471 | 3536.52 | 1 | 5000 | 10611.72 | 3536.52 | 0 | 0 | 0 | 0 | 50360.56 | 0 | 0 | 0 | 0 | 0 | 50360.56
2022073021 | 7 | 0.83835 | 67068 | 0.31716 | 11417.76 | 0.03069 | 368.28 | 1 | 5000 | 11417.76 | 368.28 | 0 | 0 | 0 | 0 | 50281.96 | 0 | 0 | 0 | 0 | 0 | 50281.96
2022073022 | 7 | 0.81196 | 64956.8 | 0.36187 | 13027.32 | 0 | 0 | 1 | 5000 | 13027.32 | 0 | 0 | 0 | 0 | 0 | 46929.48 | 0 | 0 | 0 | 0 | 0 | 46929.48
2022073023 | 7 | 0.77547 | 62037.6 | 0.4337 | 15613.2 | 0 | 0 | 1 | 5000 | 15613.2 | 0 | 0 | 0 | 0 | 0 | 41424.4 | 0 | 0 | 0 | 0 | 0 | 41424.4
2022073024 | 7 | 0.73415 | 58732 | 0.47309 | 17031.24 | 0 | 0 | 1 | 5000 | 17031.24 | 0 | 0 | 0 | 0 | 0 | 36700.76 | 0 | 0 | 0 | 0 | 0 | 36700.76
2022073101 | 1 | 0.69492 | 55593.6 | 0.50105 | 18037.8 | 0 | 0 | 1 | 5000 | 18037.8 | 0 | 0 | 0 | 0 | 0 | 32555.8 | 0 | 0 | 0 | 0 | 0 | 32555.8
2022073102 | 1 | 0.6623 | 52984 | 0.51555 | 18559.8 | 0 | 0 | 1 | 5000 | 18559.8 | 0 | 0 | 0 | 0 | 0 | 29424.2 | 0 | 0 | 0 | 0 | 0 | 29424.2
2022073103 | 1 | 0.6358 | 50864 | 0.52433 | 18875.88 | 0 | 0 | 1 | 5000 | 18875.88 | 0 | 0 | 0 | 0 | 0 | 26988.12 | 0 | 0 | 0 | 0 | 0 | 26988.12
2022073104 | 1 | 0.6168 | 49344 | 0.52679 | 18964.44 | 0 | 0 | 1 | 5000 | 18964.44 | 0 | 0 | 0 | 0 | 0 | 25379.56 | 0 | 0 | 0 | 0 | 0 | 25379.56
2022073105 | 1 | 0.60109 | 48087.2 | 0.52283 | 18821.88 | 0 | 0 | 1 | 5000 | 18821.88 | 0 | 0 | 0 | 0 | 0 | 24265.32 | 0 | 0 | 0 | 0 | 0 | 24265.32
2022073106 | 1 | 0.59094 | 47275.2 | 0.50512 | 18184.32 | 0 | 0 | 1 | 5000 | 18184.32 | 0 | 0 | 0 | 0 | 0 | 24090.88 | 0 | 0 | 0 | 0 | 0 | 24090.88
2022073107 | 1 | 0.58259 | 46607.2 | 0.49001 | 17640.36 | 0.00024 | 2.88 | 1 | 5000 | 17640.36 | 2.88 | 0 | 0 | 0 | 0 | 23963.96 | 0 | 0 | 0 | 0 | 0 | 23963.96
2022073108 | 1 | 0.58149 | 46519.2 | 0.46795 | 16846.2 | 0.06787 | 814.44 | 1 | 5000 | 16846.2 | 814.44 | 0 | 0 | 0 | 0 | 23858.56 | 0 | 0 | 0 | 0 | 0 | 23858.56
2022073109 | 1 | 0.61651 | 49320.8 | 0.42124 | 15164.64 | 0.38584 | 4630.08 | 1 | 5000 | 15164.64 | 4630.08 | 0 | 0 | 0 | 0 | 24526.08 | 0 | 0 | 0 | 0 | 0 | 24526.08
2022073110 | 1 | 0.66791 | 53432.8 | 0.40599 | 14615.64 | 0.61342 | 7361.04 | 1 | 5000 | 14615.64 | 7361.04 | 0 | 0 | 0 | 0 | 26456.12 | 0 | 0 | 0 | 0 | 0 | 26456.12
2022073111 | 1 | 0.7201 | 57608 | 0.37202 | 13392.72 | 0.7251 | 8701.2 | 1 | 5000 | 13392.72 | 8701.2 | 0 | 0 | 0 | 0 | 30514.08 | 0 | 0 | 0 | 0 | 0 | 30514.08
2022073112 | 1 | 0.77333 | 61866.4 | 0.33344 | 12003.84 | 0.72892 | 8747.04 | 1 | 5000 | 12003.84 | 8747.04 | 0 | 0 | 0 | 0 | 36115.52 | 0 | 0 | 0 | 0 | 0 | 36115.52
2022073113 | 1 | 0.8215 | 65720 | 0.30687 | 11047.32 | 0.72489 | 8698.68 | 1 | 5000 | 11047.32 | 8698.68 | 0 | 0 | 0 | 0 | 40974 | 0 | 0 | 0 | 0 | 0 | 40974
2022073114 | 1 | 0.86337 | 69069.6 | 0.28951 | 10422.36 | 0.74492 | 8939.04 | 1 | 5000 | 10422.36 | 8939.04 | 0 | 0 | 0 | 0 | 44708.2 | 0 | 0 | 0 | 0 | 0 | 44708.2
2022073115 | 1 | 0.89916 | 71932.8 | 0.27736 | 9984.96 | 0.75987 | 9118.44 | 1 | 5000 | 9984.96 | 9118.44 | 0 | 0 | 0 | 0 | 47829.4 | 0 | 0 | 0 | 0 | 0 | 47829.4
2022073116 | 1 | 0.92225 | 73780 | 0.25681 | 9245.16 | 0.75004 | 9000.48 | 1 | 5000 | 9245.16 | 9000.48 | 0 | 0 | 0 | 0 | 50534.36 | 0 | 0 | 0 | 0 | 0 | 50534.36
2022073117 | 1 | 0.9377 | 75016 | 0.25935 | 9336.6 | 0.71438 | 8572.56 | 1 | 5000 | 9336.6 | 8572.56 | 0 | 0 | 0 | 0 | 52106.84 | 0 | 0 | 0 | 0 | 0 | 52106.84
2022073118 | 1 | 0.9441 | 75528 | 0.26701 | 9612.36 | 0.66653 | 7998.36 | 1 | 5000 | 9612.36 | 7998.36 | 0 | 0 | 0 | 0 | 52917.28 | 0 | 0 | 0 | 0 | 0 | 52917.28
2022073119 | 1 | 0.93167 | 74533.6 | 0.28991 | 10436.76 | 0.55864 | 6703.68 | 1 | 5000 | 10436.76 | 6703.68 | 0 | 0 | 0 | 0 | 52393.16 | 0 | 0 | 0 | 0 | 0 | 52393.16
2022073120 | 1 | 0.90197 | 72157.6 | 0.32284 | 11622.24 | 0.27035 | 3244.2 | 1 | 5000 | 11622.24 | 3244.2 | 0 | 0 | 0 | 0 | 52291.16 | 0 | 0 | 0 | 0 | 0 | 52291.16
2022073121 | 1 | 0.86785 | 69428 | 0.35446 | 12760.56 | 0.02129 | 255.48 | 1 | 5000 | 12760.56 | 255.48 | 0 | 0 | 0 | 0 | 51411.96 | 0 | 0 | 0 | 0 | 0 | 51411.96
2022073122 | 1 | 0.83806 | 67044.8 | 0.41478 | 14932.08 | 0 | 0 | 1 | 5000 | 14932.08 | 0 | 0 | 0 | 0 | 0 | 47112.72 | 0 | 0 | 0 | 0 | 0 | 47112.72
2022073123 | 1 | 0.79076 | 63260.8 | 0.48769 | 17556.84 | 0 | 0 | 1 | 5000 | 17556.84 | 0 | 0 | 0 | 0 | 0 | 40703.96 | 0 | 0 | 0 | 0 | 0 | 40703.96
2022073124 | 1 | 0.74041 | 59232.8 | 0.52614 | 18941.04 | 0 | 0 | 1 | 5000 | 18941.04 | 0 | 0 | 0 | 0 | 0 | 35291.76 | 0 | 0 | 0 | 0 | 0 | 35291.76
2022080101 | 2 | 0.69492 | 55593.6 | 0.53508 | 19262.88 | 0 | 0 | 1 | 5000 | 19262.88 | 0 | 0 | 0 | 0 | 0 | 31330.72 | 0 | 0 | 0 | 0 | 0 | 31330.72
2022080102 | 2 | 0.65983 | 52786.4 | 0.5365 | 19314 | 0 | 0 | 1 | 5000 | 19314 | 0 | 0 | 0 | 0 | 0 | 28472.4 | 0 | 0 | 0 | 0 | 0 | 28472.4
2022080103 | 2 | 0.63715 | 50972 | 0.53597 | 19294.92 | 0 | 0 | 1 | 5000 | 19294.92 | 0 | 0 | 0 | 0 | 0 | 26677.08 | 0 | 0 | 0 | 0 | 0 | 26677.08
2022080104 | 2 | 0.62334 | 49867.2 | 0.5379 | 19364.4 | 0 | 0 | 1 | 5000 | 19364.4 | 0 | 0 | 0 | 0 | 0 | 25502.8 | 0 | 0 | 0 | 0 | 0 | 25502.8
2022080105 | 2 | 0.61563 | 49250.4 | 0.52235 | 18804.6 | 0 | 0 | 1 | 5000 | 18804.6 | 0 | 0 | 0 | 0 | 0 | 25445.8 | 0 | 0 | 0 | 0 | 0 | 25445.8
2022080106 | 2 | 0.62236 | 49788.8 | 0.51402 | 18504.72 | 0 | 0 | 1 | 5000 | 18504.72 | 0 | 0 | 0 | 0 | 0 | 26284.08 | 0 | 0 | 0 | 0 | 0 | 26284.08
2022080107 | 2 | 0.63265 | 50612 | 0.48672 | 17521.92 | 0.0002 | 2.4 | 1 | 5000 | 17521.92 | 2.4 | 0 | 0 | 0 | 0 | 28087.68 | 0 | 0 | 0 | 0 | 0 | 28087.68
2022080108 | 2 | 0.63827 | 51061.6 | 0.42334 | 15240.24 | 0.08201 | 984.12 | 1 | 5000 | 15240.24 | 984.12 | 0 | 0 | 0 | 0 | 29837.24 | 0 | 0 | 0 | 0 | 0 | 29837.24
2022080109 | 2 | 0.67199 | 53759.2 | 0.3656 | 13161.6 | 0.45238 | 5428.56 | 1 | 5000 | 13161.6 | 5428.56 | 0 | 0 | 0 | 0 | 30169.04 | 0 | 0 | 0 | 0 | 0 | 30169.04
2022080110 | 2 | 0.71677 | 57341.6 | 0.38378 | 13816.08 | 0.63184 | 7582.08 | 1 | 5000 | 13816.08 | 7582.08 | 0 | 0 | 0 | 0 | 30943.44 | 0 | 0 | 0 | 0 | 0 | 30943.44
2022080111 | 2 | 0.76322 | 61057.6 | 0.34624 | 12464.64 | 0.69601 | 8352.12 | 1 | 5000 | 12464.64 | 8352.12 | 0 | 0 | 0 | 0 | 35240.84 | 0 | 0 | 0 | 0 | 0 | 35240.84
2022080112 | 2 | 0.80993 | 64794.4 | 0.25115 | 9041.4 | 0.68811 | 8257.32 | 1 | 5000 | 9041.4 | 8257.32 | 0 | 0 | 0 | 0 | 42495.68 | 0 | 0 | 0 | 0 | 0 | 42495.68
2022080113 | 2 | 0.85201 | 68160.8 | 0.20576 | 7407.36 | 0.71394 | 8567.28 | 1 | 5000 | 7407.36 | 8567.28 | 0 | 0 | 0 | 0 | 47186.16 | 0 | 0 | 0 | 0 | 0 | 47186.16
2022080114 | 2 | 0.89183 | 71346.4 | 0.19931 | 7175.16 | 0.73012 | 8761.44 | 1 | 5000 | 7175.16 | 8761.44 | 0 | 0 | 0 | 0 | 50409.8 | 0 | 0 | 0 | 0 | 0 | 50409.8
2022080115 | 2 | 0.92183 | 73746.4 | 0.21441 | 7718.76 | 0.73411 | 8809.32 | 1 | 5000 | 7718.76 | 8809.32 | 0 | 0 | 0 | 0 | 52218.32 | 0 | 0 | 0 | 0 | 0 | 52218.32
2022080116 | 2 | 0.94656 | 75724.8 | 0.26835 | 9660.6 | 0.72411 | 8689.32 | 1 | 5000 | 9660.6 | 8689.32 | 0 | 0 | 0 | 0 | 52374.88 | 0 | 0 | 0 | 0 | 0 | 52374.88
2022080117 | 2 | 0.95315 | 76252 | 0.31209 | 11235.24 | 0.69461 | 8335.32 | 1 | 5000 | 11235.24 | 8335.32 | 0 | 0 | 0 | 0 | 51681.44 | 0 | 0 | 0 | 0 | 0 | 51681.44
2022080118 | 2 | 0.94956 | 75964.8 | 0.33971 | 12229.56 | 0.6594 | 7912.8 | 1 | 5000 | 12229.56 | 7912.8 | 0 | 0 | 0 | 0 | 50822.44 | 0 | 0 | 0 | 0 | 0 | 50822.44
2022080119 | 2 | 0.93927 | 75141.6 | 0.37966 | 13667.76 | 0.55902 | 6708.24 | 1 | 5000 | 13667.76 | 6708.24 | 0 | 0 | 0 | 0 | 49765.6 | 0 | 0 | 0 | 0 | 0 | 49765.6
2022080120 | 2 | 0.91105 | 72884 | 0.42116 | 15161.76 | 0.27091 | 3250.92 | 1 | 5000 | 15161.76 | 3250.92 | 0 | 0 | 0 | 0 | 49471.32 | 0 | 0 | 0 | 0 | 0 | 49471.32
2022080121 | 2 | 0.87951 | 70360.8 | 0.43721 | 15739.56 | 0.02645 | 317.4 | 1 | 5000 | 15739.56 | 317.4 | 0 | 0 | 0 | 0 | 49303.84 | 0 | 0 | 0 | 0 | 0 | 49303.84
2022080122 | 2 | 0.84869 | 67895.2 | 0.48116 | 17321.76 | 0 | 0 | 1 | 5000 | 17321.76 | 0 | 0 | 0 | 0 | 0 | 45573.44 | 0 | 0 | 0 | 0 | 0 | 45573.44
2022080123 | 2 | 0.79868 | 63894.4 | 0.52243 | 18807.48 | 0 | 0 | 1 | 5000 | 18807.48 | 0 | 0 | 0 | 0 | 0 | 40086.92 | 0 | 0 | 0 | 0 | 0 | 40086.92
2022080124 | 2 | 0.74537 | 59629.6 | 0.5329 | 19184.4 | 0 | 0 | 1 | 5000 | 19184.4 | 0 | 0 | 0 | 0 | 0 | 35445.2 | 0 | 0 | 0 | 0 | 0 | 35445.2
2022080201 | 3 | 0.69925 | 55940 | 0.55195 | 19870.2 | 0 | 0 | 1 | 5000 | 19870.2 | 0 | 0 | 0 | 0 | 0 | 31069.8 | 0 | 0 | 0 | 0 | 0 | 31069.8
2022080202 | 3 | 0.66568 | 53254.4 | 0.55998 | 20159.28 | 0 | 0 | 1 | 5000 | 20159.28 | 0 | 0 | 0 | 0 | 0 | 28095.12 | 0 | 0 | 0 | 0 | 0 | 28095.12
2022080203 | 3 | 0.64351 | 51480.8 | 0.56335 | 20280.6 | 0 | 0 | 1 | 5000 | 20280.6 | 0 | 0 | 0 | 0 | 0 | 26200.2 | 0 | 0 | 0 | 0 | 0 | 26200.2
2022080204 | 3 | 0.63011 | 50408.8 | 0.56257 | 20252.52 | 0 | 0 | 1 | 5000 | 20252.52 | 0 | 0 | 0 | 0 | 0 | 25156.28 | 0 | 0 | 0 | 0 | 0 | 25156.28
2022080205 | 3 | 0.62359 | 49887.2 | 0.55065 | 19823.4 | 0 | 0 | 1 | 5000 | 19823.4 | 0 | 0 | 0 | 0 | 0 | 25063.8 | 0 | 0 | 0 | 0 | 0 | 25063.8
2022080206 | 3 | 0.63041 | 50432.8 | 0.51815 | 18653.4 | 0 | 0 | 1 | 5000 | 18653.4 | 0 | 0 | 0 | 0 | 0 | 26779.4 | 0 | 0 | 0 | 0 | 0 | 26779.4
2022080207 | 3 | 0.64383 | 51506.4 | 0.51236 | 18444.96 | 0.00016 | 1.92 | 1 | 5000 | 18444.96 | 1.92 | 0 | 0 | 0 | 0 | 28059.52 | 0 | 0 | 0 | 0 | 0 | 28059.52
2022080208 | 3 | 0.65053 | 52042.4 | 0.48279 | 17380.44 | 0.08425 | 1011 | 1 | 5000 | 17380.44 | 1011 | 0 | 0 | 0 | 0 | 28650.96 | 0 | 0 | 0 | 0 | 0 | 28650.96
2022080209 | 3 | 0.68561 | 54848.8 | 0.47384 | 17058.24 | 0.42856 | 5142.72 | 1 | 5000 | 17058.24 | 5142.72 | 0 | 0 | 0 | 0 | 27647.84 | 0 | 0 | 0 | 0 | 0 | 27647.84
2022080210 | 3 | 0.73708 | 58966.4 | 0.55746 | 20068.56 | 0.55843 | 6701.16 | 1 | 5000 | 20068.56 | 6701.16 | 0 | 0 | 0 | 0 | 27196.68 | 0 | 0 | 0 | 0 | 0 | 27196.68
2022080211 | 3 | 0.7893 | 63144 | 0.55426 | 19953.36 | 0.63541 | 7624.92 | 1 | 5000 | 19953.36 | 7624.92 | 0 | 0 | 0 | 0 | 30565.72 | 0 | 0 | 0 | 0 | 0 | 30565.72
2022080212 | 3 | 0.8421 | 67368 | 0.51534 | 18552.24 | 0.75445 | 9053.4 | 1 | 5000 | 18552.24 | 9053.4 | 0 | 0 | 0 | 0 | 34762.36 | 0 | 0 | 0 | 0 | 0 | 34762.36
2022080213 | 3 | 0.88953 | 71162.4 | 0.47796 | 17206.56 | 0.78159 | 9379.08 | 1 | 5000 | 17206.56 | 9379.08 | 0 | 0 | 0 | 0 | 39576.76 | 0 | 0 | 0 | 0 | 0 | 39576.76
2022080214 | 3 | 0.93413 | 74730.4 | 0.45109 | 16239.24 | 0.77554 | 9306.48 | 1 | 5000 | 16239.24 | 9306.48 | 0 | 0 | 0 | 0 | 44184.68 | 0 | 0 | 0 | 0 | 0 | 44184.68
2022080215 | 3 | 0.96304 | 77043.2 | 0.44793 | 16125.48 | 0.77883 | 9345.96 | 1 | 5000 | 16125.48 | 9345.96 | 0 | 0 | 0 | 0 | 46571.76 | 0 | 0 | 0 | 0 | 0 | 46571.76
2022080216 | 3 | 0.97477 | 77981.6 | 0.43933 | 15815.88 | 0.76051 | 9126.12 | 1 | 5000 | 15815.88 | 9126.12 | 0 | 0 | 0 | 0 | 48039.6 | 0 | 0 | 0 | 0 | 0 | 48039.6
2022080217 | 3 | 0.98173 | 78538.4 | 0.43361 | 15609.96 | 0.75719 | 9086.28 | 1 | 5000 | 15609.96 | 9086.28 | 0 | 0 | 0 | 0 | 48842.16 | 0 | 0 | 0 | 0 | 0 | 48842.16
2022080218 | 3 | 0.9815 | 78520 | 0.42808 | 15410.88 | 0.73547 | 8825.64 | 1 | 5000 | 15410.88 | 8825.64 | 0 | 0 | 0 | 0 | 49283.48 | 0 | 0 | 0 | 0 | 0 | 49283.48
2022080219 | 3 | 0.9739 | 77912 | 0.43236 | 15564.96 | 0.63368 | 7604.16 | 1 | 5000 | 15564.96 | 7604.16 | 0 | 0 | 0 | 0 | 49742.88 | 0 | 0 | 0 | 0 | 0 | 49742.88
2022080220 | 3 | 0.94562 | 75649.6 | 0.4653 | 16750.8 | 0.30985 | 3718.2 | 1 | 5000 | 16750.8 | 3718.2 | 0 | 0 | 0 | 0 | 50180.6 | 0 | 0 | 0 | 0 | 0 | 50180.6
2022080221 | 3 | 0.90945 | 72756 | 0.4784 | 17222.4 | 0.02838 | 340.56 | 1 | 5000 | 17222.4 | 340.56 | 0 | 0 | 0 | 0 | 50193.04 | 0 | 0 | 0 | 0 | 0 | 50193.04
2022080222 | 3 | 0.8789 | 70312 | 0.53091 | 19112.76 | 0 | 0 | 1 | 5000 | 19112.76 | 0 | 0 | 0 | 0 | 0 | 46199.24 | 0 | 0 | 0 | 0 | 0 | 46199.24
2022080223 | 3 | 0.8305 | 66440 | 0.60249 | 21689.64 | 0 | 0 | 1 | 5000 | 21689.64 | 0 | 0 | 0 | 0 | 0 | 39750.36 | 0 | 0 | 0 | 0 | 0 | 39750.36
2022080224 | 3 | 0.77697 | 62157.6 | 0.64955 | 23383.8 | 0 | 0 | 1 | 5000 | 23383.8 | 0 | 0 | 0 | 0 | 0 | 33773.8 | 0 | 0 | 0 | 0 | 0 | 33773.8
2022080301 | 4 | 0.73032 | 58425.6 | 0.68286 | 24582.96 | 0 | 0 | 1 | 5000 | 24582.96 | 0 | 0 | 0 | 0 | 0 | 28842.64 | 0 | 0 | 0 | 0 | 0 | 28842.64
2022080302 | 4 | 0.69382 | 55505.6 | 0.69021 | 24847.56 | 0 | 0 | 1 | 5000 | 24847.56 | 0 | 0 | 0 | 0 | 0 | 25658.04 | 0 | 0 | 0 | 0 | 0 | 25658.04
2022080303 | 4 | 0.66843 | 53474.4 | 0.69687 | 25087.32 | 0 | 0 | 1 | 5000 | 25087.32 | 0 | 0 | 0 | 0 | 0 | 23387.08 | 0 | 0 | 0 | 0 | 0 | 23387.08
2022080304 | 4 | 0.65294 | 52235.2 | 0.68675 | 24723 | 0 | 0 | 1 | 5000 | 24723 | 0 | 0 | 0 | 0 | 0 | 22512.2 | 0 | 0 | 0 | 0 | 0 | 22512.2
2022080305 | 4 | 0.64781 | 51824.8 | 0.67884 | 24438.24 | 0 | 0 | 1 | 5000 | 24438.24 | 0 | 0 | 0 | 0 | 0 | 22386.56 | 0 | 0 | 0 | 0 | 0 | 22386.56
2022080306 | 4 | 0.64986 | 51988.8 | 0.66322 | 23875.92 | 0 | 0 | 1 | 5000 | 23875.92 | 0 | 0 | 0 | 0 | 0 | 23112.88 | 0 | 0 | 0 | 0 | 0 | 23112.88
2022080307 | 4 | 0.65914 | 52731.2 | 0.64216 | 23117.76 | 0.00029 | 3.48 | 1 | 5000 | 23117.76 | 3.48 | 0 | 0 | 0 | 0 | 24609.96 | 0 | 0 | 0 | 0 | 0 | 24609.96
2022080308 | 4 | 0.66402 | 53121.6 | 0.61344 | 22083.84 | 0.09281 | 1113.72 | 1 | 5000 | 22083.84 | 1113.72 | 0 | 0 | 0 | 0 | 24924.04 | 0 | 0 | 0 | 0 | 0 | 24924.04
2022080309 | 4 | 0.69488 | 55590.4 | 0.59803 | 21529.08 | 0.40965 | 4915.8 | 1 | 5000 | 21529.08 | 4915.8 | 0 | 0 | 0 | 0 | 24145.52 | 0 | 0 | 0 | 0 | 0 | 24145.52
2022080310 | 4 | 0.74298 | 59438.4 | 0.64248 | 23129.28 | 0.44386 | 5326.32 | 1 | 5000 | 23129.28 | 5326.32 | 0 | 0 | 0 | 0 | 25982.8 | 0 | 0 | 0 | 0 | 0 | 25982.8
2022080311 | 4 | 0.79667 | 63733.6 | 0.59576 | 21447.36 | 0.61615 | 7393.8 | 1 | 5000 | 21447.36 | 7393.8 | 0 | 0 | 0 | 0 | 29892.44 | 0 | 0 | 0 | 0 | 0 | 29892.44
2022080312 | 4 | 0.85035 | 68028 | 0.52533 | 18911.88 | 0.74684 | 8962.08 | 1 | 5000 | 18911.88 | 8962.08 | 0 | 0 | 0 | 0 | 35154.04 | 0 | 0 | 0 | 0 | 0 | 35154.04
2022080313 | 4 | 0.89603 | 71682.4 | 0.45841 | 16502.76 | 0.76856 | 9222.72 | 1 | 5000 | 16502.76 | 9222.72 | 0 | 0 | 0 | 0 | 40956.92 | 0 | 0 | 0 | 0 | 0 | 40956.92
2022080314 | 4 | 0.9378 | 75024 | 0.38581 | 13889.16 | 0.75029 | 9003.48 | 1 | 5000 | 13889.16 | 9003.48 | 0 | 0 | 0 | 0 | 47131.36 | 0 | 0 | 0 | 0 | 0 | 47131.36
2022080315 | 4 | 0.96763 | 77410.4 | 0.35456 | 12764.16 | 0.74978 | 8997.36 | 1 | 5000 | 12764.16 | 8997.36 | 0 | 0 | 0 | 0 | 50648.88 | 0 | 0 | 0 | 0 | 0 | 50648.88
2022080316 | 4 | 0.97796 | 78236.8 | 0.33 | 11880 | 0.71798 | 8615.76 | 1 | 5000 | 11880 | 8615.76 | 0 | 0 | 0 | 0 | 52741.04 | 0 | 0 | 0 | 0 | 0 | 52741.04
2022080317 | 4 | 0.97945 | 78356 | 0.30876 | 11115.36 | 0.71799 | 8615.88 | 1 | 5000 | 11115.36 | 8615.88 | 0 | 0 | 0 | 0 | 53624.76 | 0 | 0 | 0 | 0 | 0 | 53624.76
2022080318 | 4 | 0.97588 | 78070.4 | 0.29369 | 10572.84 | 0.67937 | 8152.44 | 1 | 5000 | 10572.84 | 8152.44 | 0 | 0 | 0 | 0 | 54345.12 | 0 | 0 | 0 | 0 | 0 | 54345.12
2022080319 | 4 | 0.96154 | 76923.2 | 0.29927 | 10773.72 | 0.55367 | 6644.04 | 1 | 5000 | 10773.72 | 6644.04 | 0 | 0 | 0 | 0 | 54505.44 | 0 | 0 | 0 | 0 | 0 | 54505.44
2022080320 | 4 | 0.93218 | 74574.4 | 0.32194 | 11589.84 | 0.27135 | 3256.2 | 1 | 5000 | 11589.84 | 3256.2 | 0 | 0 | 0 | 0 | 54728.36 | 0 | 0 | 0 | 0 | 0 | 54728.36
2022080321 | 4 | 0.90146 | 72116.8 | 0.36477 | 13131.72 | 0.01691 | 202.92 | 1 | 5000 | 13131.72 | 202.92 | 0 | 0 | 0 | 0 | 53782.16 | 0 | 0 | 0 | 0 | 0 | 53782.16
2022080322 | 4 | 0.87369 | 69895.2 | 0.44511 | 16023.96 | 0 | 0 | 1 | 5000 | 16023.96 | 0 | 0 | 0 | 0 | 0 | 48871.24 | 0 | 0 | 0 | 0 | 0 | 48871.24
2022080323 | 4 | 0.82467 | 65973.6 | 0.53479 | 19252.44 | 0 | 0 | 1 | 5000 | 19252.44 | 0 | 0 | 0 | 0 | 0 | 41721.16 | 0 | 0 | 0 | 0 | 0 | 41721.16
2022080324 | 4 | 0.77234 | 61787.2 | 0.58315 | 20993.4 | 0 | 0 | 1 | 5000 | 20993.4 | 0 | 0 | 0 | 0 | 0 | 35793.8 | 0 | 0 | 0 | 0 | 0 | 35793.8
2022080401 | 5 | 0.72765 | 58212 | 0.5951 | 21423.6 | 0 | 0 | 1 | 5000 | 21423.6 | 0 | 0 | 0 | 0 | 0 | 31788.4 | 0 | 0 | 0 | 0 | 0 | 31788.4
2022080402 | 5 | 0.69257 | 55405.6 | 0.58622 | 21103.92 | 0 | 0 | 1 | 5000 | 21103.92 | 0 | 0 | 0 | 0 | 0 | 29301.68 | 0 | 0 | 0 | 0 | 0 | 29301.68
2022080403 | 5 | 0.66558 | 53246.4 | 0.56468 | 20328.48 | 0 | 0 | 1 | 5000 | 20328.48 | 0 | 0 | 0 | 0 | 0 | 27917.92 | 0 | 0 | 0 | 0 | 0 | 27917.92
2022080404 | 5 | 0.64744 | 51795.2 | 0.54042 | 19455.12 | 0 | 0 | 1 | 5000 | 19455.12 | 0 | 0 | 0 | 0 | 0 | 27340.08 | 0 | 0 | 0 | 0 | 0 | 27340.08
2022080405 | 5 | 0.63767 | 51013.6 | 0.53913 | 19408.68 | 0 | 0 | 1 | 5000 | 19408.68 | 0 | 0 | 0 | 0 | 0 | 26604.92 | 0 | 0 | 0 | 0 | 0 | 26604.92
2022080406 | 5 | 0.64318 | 51454.4 | 0.5104 | 18374.4 | 0 | 0 | 1 | 5000 | 18374.4 | 0 | 0 | 0 | 0 | 0 | 28080 | 0 | 0 | 0 | 0 | 0 | 28080
2022080407 | 5 | 0.65196 | 52156.8 | 0.45849 | 16505.64 | 0.00013 | 1.56 | 1 | 5000 | 16505.64 | 1.56 | 0 | 0 | 0 | 0 | 30649.6 | 0 | 0 | 0 | 0 | 0 | 30649.6
2022080408 | 5 | 0.65545 | 52436 | 0.40021 | 14407.56 | 0.07071 | 848.52 | 1 | 5000 | 14407.56 | 848.52 | 0 | 0 | 0 | 0 | 32179.92 | 0 | 0 | 0 | 0 | 0 | 32179.92
2022080409 | 5 | 0.69085 | 55268 | 0.36733 | 13223.88 | 0.41718 | 5006.16 | 1 | 5000 | 13223.88 | 5006.16 | 0 | 0 | 0 | 0 | 32037.96 | 0 | 0 | 0 | 0 | 0 | 32037.96
2022080410 | 5 | 0.7348 | 58784 | 0.3676 | 13233.6 | 0.65888 | 7906.56 | 1 | 5000 | 13233.6 | 7906.56 | 0 | 0 | 0 | 0 | 32643.84 | 0 | 0 | 0 | 0 | 0 | 32643.84
2022080411 | 5 | 0.78736 | 62988.8 | 0.31268 | 11256.48 | 0.72311 | 8677.32 | 1 | 5000 | 11256.48 | 8677.32 | 0 | 0 | 0 | 0 | 38055 | 0 | 0 | 0 | 0 | 0 | 38055
2022080412 | 5 | 0.84108 | 67286.4 | 0.26095 | 9394.2 | 0.75392 | 9047.04 | 1 | 5000 | 9394.2 | 9047.04 | 0 | 0 | 0 | 0 | 43845.16 | 0 | 0 | 0 | 0 | 0 | 43845.16
2022080413 | 5 | 0.89311 | 71448.8 | 0.21911 | 7887.96 | 0.76185 | 9142.2 | 1 | 5000 | 7887.96 | 9142.2 | 0 | 0 | 0 | 0 | 49418.64 | 0 | 0 | 0 | 0 | 0 | 49418.64
2022080414 | 5 | 0.93768 | 75014.4 | 0.21002 | 7560.72 | 0.751 | 9012 | 1 | 5000 | 7560.72 | 9012 | 0 | 0 | 0 | 0 | 53441.68 | 0 | 0 | 0 | 0 | 0 | 53441.68
2022080415 | 5 | 0.96905 | 77524 | 0.21241 | 7646.76 | 0.73114 | 8773.68 | 1 | 5000 | 7646.76 | 8773.68 | 0 | 0 | 0 | 0 | 56103.56 | 0 | 0 | 0 | 0 | 0 | 56103.56
2022080416 | 5 | 0.97743 | 78194.4 | 0.21405 | 7705.8 | 0.70991 | 8518.92 | 1 | 5000 | 7705.8 | 8518.92 | 0 | 0 | 0 | 0 | 56969.68 | 0 | 0 | 0 | 0 | 0 | 56969.68
2022080417 | 5 | 0.97596 | 78076.8 | 0.23796 | 8566.56 | 0.68307 | 8196.84 | 1 | 5000 | 8566.56 | 8196.84 | 0 | 0 | 0 | 0 | 56313.4 | 0 | 0 | 0 | 0 | 0 | 56313.4
2022080418 | 5 | 0.96886 | 77508.8 | 0.30062 | 10822.32 | 0.65572 | 7868.64 | 1 | 5000 | 10822.32 | 7868.64 | 0 | 0 | 0 | 0 | 53817.84 | 0 | 0 | 0 | 0 | 0 | 53817.84
2022080419 | 5 | 0.9503 | 76024 | 0.3544 | 12758.4 | 0.49753 | 5970.36 | 1 | 5000 | 12758.4 | 5970.36 | 0 | 0 | 0 | 0 | 52295.24 | 0 | 0 | 0 | 0 | 0 | 52295.24
2022080420 | 5 | 0.92168 | 73734.4 | 0.372 | 13392 | 0.22295 | 2675.4 | 1 | 5000 | 13392 | 2675.4 | 0 | 0 | 0 | 0 | 52667 | 0 | 0 | 0 | 0 | 0 | 52667
2022080421 | 5 | 0.88933 | 71146.4 | 0.36171 | 13021.56 | 0.01448 | 173.76 | 1 | 5000 | 13021.56 | 173.76 | 0 | 0 | 0 | 0 | 52951.08 | 0 | 0 | 0 | 0 | 0 | 52951.08
2022080422 | 5 | 0.85429 | 68343.2 | 0.39414 | 14189.04 | 0 | 0 | 1 | 5000 | 14189.04 | 0 | 0 | 0 | 0 | 0 | 49154.16 | 0 | 0 | 0 | 0 | 0 | 49154.16
2022080423 | 5 | 0.804 | 64320 | 0.41874 | 15074.64 | 0 | 0 | 1 | 5000 | 15074.64 | 0 | 0 | 0 | 0 | 0 | 44245.36 | 0 | 0 | 0 | 0 | 0 | 44245.36
2022080424 | 5 | 0.75162 | 60129.6 | 0.4475 | 16110 | 0 | 0 | 1 | 5000 | 16110 | 0 | 0 | 0 | 0 | 0 | 39019.6 | 0 | 0 | 0 | 0 | 0 | 39019.6
2022080501 | 6 | 0.70681 | 56544.8 | 0.42151 | 15174.36 | 0 | 0 | 1 | 5000 | 15174.36 | 0 | 0 | 0 | 0 | 0 | 36370.44 | 0 | 0 | 0 | 0 | 0 | 36370.44
2022080502 | 6 | 0.67288 | 53830.4 | 0.37827 | 13617.72 | 0 | 0 | 1 | 5000 | 13617.72 | 0 | 0 | 0 | 0 | 0 | 35212.68 | 0 | 0 | 0 | 0 | 0 | 35212.68
2022080503 | 6 | 0.648 | 51840 | 0.35726 | 12861.36 | 0 | 0 | 1 | 5000 | 12861.36 | 0 | 0 | 0 | 0 | 0 | 33978.64 | 0 | 0 | 0 | 0 | 0 | 33978.64
2022080504 | 6 | 0.63033 | 50426.4 | 0.35721 | 12859.56 | 0 | 0 | 1 | 5000 | 12859.56 | 0 | 0 | 0 | 0 | 0 | 32566.84 | 0 | 0 | 0 | 0 | 0 | 32566.84
2022080505 | 6 | 0.6229 | 49832 | 0.35983 | 12953.88 | 0 | 0 | 1 | 5000 | 12953.88 | 0 | 0 | 0 | 0 | 0 | 31878.12 | 0 | 0 | 0 | 0 | 0 | 31878.12
2022080506 | 6 | 0.6267 | 50136 | 0.34408 | 12386.88 | 0 | 0 | 1 | 5000 | 12386.88 | 0 | 0 | 0 | 0 | 0 | 32749.12 | 0 | 0 | 0 | 0 | 0 | 32749.12
2022080507 | 6 | 0.63803 | 51042.4 | 0.32512 | 11704.32 | 0.00016 | 1.92 | 1 | 5000 | 11704.32 | 1.92 | 0 | 0 | 0 | 0 | 34336.16 | 0 | 0 | 0 | 0 | 0 | 34336.16
2022080508 | 6 | 0.64352 | 51481.6 | 0.29504 | 10621.44 | 0.06684 | 802.08 | 1 | 5000 | 10621.44 | 802.08 | 0 | 0 | 0 | 0 | 35058.08 | 0 | 0 | 0 | 0 | 0 | 35058.08
2022080509 | 6 | 0.67602 | 54081.6 | 0.24631 | 8867.16 | 0.36676 | 4401.12 | 1 | 5000 | 8867.16 | 4401.12 | 0 | 0 | 0 | 0 | 35813.32 | 0 | 0 | 0 | 0 | 0 | 35813.32
2022080510 | 6 | 0.72307 | 57845.6 | 0.27533 | 9911.88 | 0.61355 | 7362.6 | 1 | 5000 | 9911.88 | 7362.6 | 0 | 0 | 0 | 0 | 35571.12 | 0 | 0 | 0 | 0 | 0 | 35571.12
2022080511 | 6 | 0.77617 | 62093.6 | 0.23715 | 8537.4 | 0.73496 | 8819.52 | 1 | 5000 | 8537.4 | 8819.52 | 0 | 0 | 0 | 0 | 39736.68 | 0 | 0 | 0 | 0 | 0 | 39736.68
2022080512 | 6 | 0.82742 | 66193.6 | 0.15614 | 5621.04 | 0.75432 | 9051.84 | 1 | 5000 | 5621.04 | 9051.84 | 0 | 0 | 0 | 0 | 46520.72 | 0 | 0 | 0 | 0 | 0 | 46520.72
2022080513 | 6 | 0.86531 | 69224.8 | 0.09647 | 3472.92 | 0.73592 | 8831.04 | 1 | 5000 | 3472.92 | 8831.04 | 0 | 0 | 0 | 0 | 51920.84 | 0 | 0 | 0 | 0 | 0 | 51920.84
2022080514 | 6 | 0.8941 | 71528 | 0.10065 | 3623.4 | 0.73461 | 8815.32 | 1 | 5000 | 3623.4 | 8815.32 | 0 | 0 | 0 | 0 | 54089.28 | 0 | 0 | 0 | 0 | 0 | 54089.28
2022080515 | 6 | 0.91236 | 72988.8 | 0.14704 | 5293.44 | 0.71214 | 8545.68 | 1 | 5000 | 5293.44 | 8545.68 | 0 | 0 | 0 | 0 | 54149.68 | 0 | 0 | 0 | 0 | 0 | 54149.68
2022080516 | 6 | 0.92731 | 74184.8 | 0.19745 | 7108.2 | 0.66926 | 8031.12 | 1 | 5000 | 7108.2 | 8031.12 | 0 | 0 | 0 | 0 | 54045.48 | 0 | 0 | 0 | 0 | 0 | 54045.48
2022080517 | 6 | 0.92982 | 74385.6 | 0.23471 | 8449.56 | 0.65498 | 7859.76 | 1 | 5000 | 8449.56 | 7859.76 | 0 | 0 | 0 | 0 | 53076.28 | 0 | 0 | 0 | 0 | 0 | 53076.28
2022080518 | 6 | 0.92097 | 73677.6 | 0.27537 | 9913.32 | 0.59264 | 7111.68 | 1 | 5000 | 9913.32 | 7111.68 | 0 | 0 | 0 | 0 | 51652.6 | 0 | 0 | 0 | 0 | 0 | 51652.6
2022080519 | 6 | 0.89898 | 71918.4 | 0.33545 | 12076.2 | 0.50058 | 6006.96 | 1 | 5000 | 12076.2 | 6006.96 | 0 | 0 | 0 | 0 | 48835.24 | 0 | 0 | 0 | 0 | 0 | 48835.24
2022080520 | 6 | 0.87017 | 69613.6 | 0.38839 | 13982.04 | 0.24281 | 2913.72 | 1 | 5000 | 13982.04 | 2913.72 | 0 | 0 | 0 | 0 | 47717.84 | 0 | 0 | 0 | 0 | 0 | 47717.84
2022080521 | 6 | 0.84214 | 67371.2 | 0.41432 | 14915.52 | 0.02139 | 256.68 | 1 | 5000 | 14915.52 | 256.68 | 0 | 0 | 0 | 0 | 47199 | 0 | 0 | 0 | 0 | 0 | 47199
2022080522 | 6 | 0.81365 | 65092 | 0.43883 | 15797.88 | 0.00468 | 56.16 | 1 | 5000 | 15797.88 | 56.16 | 0 | 0 | 0 | 0 | 44237.96 | 0 | 0 | 0 | 0 | 0 | 44237.96
2022080523 | 6 | 0.77164 | 61731.2 | 0.48823 | 17576.28 | 0.00468 | 56.16 | 1 | 5000 | 17576.28 | 56.16 | 0 | 0 | 0 | 0 | 39098.76 | 0 | 0 | 0 | 0 | 0 | 39098.76
2022080524 | 6 | 0.72467 | 57973.6 | 0.551 | 19836 | 0.00468 | 56.16 | 1 | 5000 | 19836 | 56.16 | 0 | 0 | 0 | 0 | 33081.44 | 0 | 0 | 0 | 0 | 0 | 33081.44
2022080601 | 7 | 0.68506 | 54804.8 | 0.55304 | 19909.44 | 0.00468 | 56.16 | 1 | 5000 | 19909.44 | 56.16 | 0 | 0 | 0 | 0 | 29839.2 | 0 | 0 | 0 | 0 | 0 | 29839.2
2022080602 | 7 | 0.64863 | 51890.4 | 0.52734 | 18984.24 | 0.00361 | 43.32 | 1 | 5000 | 18984.24 | 43.32 | 0 | 0 | 0 | 0 | 27862.84 | 0 | 0 | 0 | 0 | 0 | 27862.84
2022080603 | 7 | 0.62475 | 49980 | 0.49727 | 17901.72 | 0 | 0 | 1 | 5000 | 17901.72 | 0 | 0 | 0 | 0 | 0 | 27078.28 | 0 | 0 | 0 | 0 | 0 | 27078.28
2022080604 | 7 | 0.60354 | 48283.2 | 0.48692 | 17529.12 | 0 | 0 | 1 | 5000 | 17529.12 | 0 | 0 | 0 | 0 | 0 | 25754.08 | 0 | 0 | 0 | 0 | 0 | 25754.08
2022080605 | 7 | 0.58963 | 47170.4 | 0.47169 | 16980.84 | 0 | 0 | 1 | 5000 | 16980.84 | 0 | 0 | 0 | 0 | 0 | 25189.56 | 0 | 0 | 0 | 0 | 0 | 25189.56
2022080606 | 7 | 0.58559 | 46847.2 | 0.44278 | 15940.08 | 0 | 0 | 1 | 5000 | 15940.08 | 0 | 0 | 0 | 0 | 0 | 25907.12 | 0 | 0 | 0 | 0 | 0 | 25907.12
2022080607 | 7 | 0.58491 | 46792.8 | 0.4126 | 14853.6 | 0.00016 | 1.92 | 1 | 5000 | 14853.6 | 1.92 | 0 | 0 | 0 | 0 | 26937.28 | 0 | 0 | 0 | 0 | 0 | 26937.28
2022080608 | 7 | 0.58811 | 47048.8 | 0.37011 | 13323.96 | 0.07666 | 919.92 | 1 | 5000 | 13323.96 | 919.92 | 0 | 0 | 0 | 0 | 27804.92 | 0 | 0 | 0 | 0 | 0 | 27804.92
2022080609 | 7 | 0.61646 | 49316.8 | 0.27564 | 9923.04 | 0.41497 | 4979.64 | 1 | 5000 | 9923.04 | 4979.64 | 0 | 0 | 0 | 0 | 29414.12 | 0 | 0 | 0 | 0 | 0 | 29414.12
2022080610 | 7 | 0.6555 | 52440 | 0.28088 | 10111.68 | 0.63246 | 7589.52 | 1 | 5000 | 10111.68 | 7589.52 | 0 | 0 | 0 | 0 | 29738.8 | 0 | 0 | 0 | 0 | 0 | 29738.8
2022080611 | 7 | 0.69836 | 55868.8 | 0.26408 | 9506.88 | 0.72177 | 8661.24 | 1 | 5000 | 9506.88 | 8661.24 | 0 | 0 | 0 | 0 | 32700.68 | 0 | 0 | 0 | 0 | 0 | 32700.68
2022080612 | 7 | 0.74377 | 59501.6 | 0.20912 | 7528.32 | 0.72519 | 8702.28 | 1 | 5000 | 7528.32 | 8702.28 | 0 | 0 | 0 | 0 | 38271 | 0 | 0 | 0 | 0 | 0 | 38271
2022080613 | 7 | 0.78605 | 62884 | 0.2028 | 7300.8 | 0.73039 | 8764.68 | 1 | 5000 | 7300.8 | 8764.68 | 0 | 0 | 0 | 0 | 41818.52 | 0 | 0 | 0 | 0 | 0 | 41818.52
2022080614 | 7 | 0.82689 | 66151.2 | 0.23223 | 8360.28 | 0.73684 | 8842.08 | 1 | 5000 | 8360.28 | 8842.08 | 0 | 0 | 0 | 0 | 43948.84 | 0 | 0 | 0 | 0 | 0 | 43948.84
2022080615 | 7 | 0.85633 | 68506.4 | 0.23177 | 8343.72 | 0.71074 | 8528.88 | 1 | 5000 | 8343.72 | 8528.88 | 0 | 0 | 0 | 0 | 46633.8 | 0 | 0 | 0 | 0 | 0 | 46633.8
2022080616 | 7 | 0.86869 | 69495.2 | 0.23416 | 8429.76 | 0.65913 | 7909.56 | 1 | 5000 | 8429.76 | 7909.56 | 0 | 0 | 0 | 0 | 48155.88 | 0 | 0 | 0 | 0 | 0 | 48155.88
2022080617 | 7 | 0.87396 | 69916.8 | 0.26425 | 9513 | 0.60698 | 7283.76 | 1 | 5000 | 9513 | 7283.76 | 0 | 0 | 0 | 0 | 48120.04 | 0 | 0 | 0 | 0 | 0 | 48120.04
2022080618 | 7 | 0.87253 | 69802.4 | 0.30908 | 11126.88 | 0.57201 | 6864.12 | 1 | 5000 | 11126.88 | 6864.12 | 0 | 0 | 0 | 0 | 46811.4 | 0 | 0 | 0 | 0 | 0 | 46811.4
2022080619 | 7 | 0.85684 | 68547.2 | 0.37175 | 13383 | 0.47652 | 5718.24 | 1 | 5000 | 13383 | 5718.24 | 0 | 0 | 0 | 0 | 44445.96 | 0 | 0 | 0 | 0 | 0 | 44445.96
2022080620 | 7 | 0.82839 | 66271.2 | 0.44219 | 15918.84 | 0.19863 | 2383.56 | 1 | 5000 | 15918.84 | 2383.56 | 0 | 0 | 0 | 0 | 42968.8 | 0 | 0 | 0 | 0 | 0 | 42968.8
2022080621 | 7 | 0.803 | 64240 | 0.48126 | 17325.36 | 0.01472 | 176.64 | 1 | 5000 | 17325.36 | 176.64 | 0 | 0 | 0 | 0 | 41738 | 0 | 0 | 0 | 0 | 0 | 41738
2022080622 | 7 | 0.77931 | 62344.8 | 0.49843 | 17943.48 | 0 | 0 | 1 | 5000 | 17943.48 | 0 | 0 | 0 | 0 | 0 | 39401.32 | 0 | 0 | 0 | 0 | 0 | 39401.32
2022080623 | 7 | 0.74212 | 59369.6 | 0.5068 | 18244.8 | 0 | 0 | 1 | 5000 | 18244.8 | 0 | 0 | 0 | 0 | 0 | 36124.8 | 0 | 0 | 0 | 0 | 0 | 36124.8
2022080624 | 7 | 0.70336 | 56268.8 | 0.4944 | 17798.4 | 0 | 0 | 1 | 5000 | 17798.4 | 0 | 0 | 0 | 0 | 0 | 33470.4 | 0 | 0 | 0 | 0 | 0 | 33470.4
2022080701 | 1 | 0.66439 | 53151.2 | 0.46626 | 16785.36 | 0 | 0 | 1 | 5000 | 16785.36 | 0 | 0 | 0 | 0 | 0 | 31365.84 | 0 | 0 | 0 | 0 | 0 | 31365.84
2022080702 | 1 | 0.63318 | 50654.4 | 0.45767 | 16476.12 | 0 | 0 | 1 | 5000 | 16476.12 | 0 | 0 | 0 | 0 | 0 | 29178.28 | 0 | 0 | 0 | 0 | 0 | 29178.28
2022080703 | 1 | 0.61121 | 48896.8 | 0.46181 | 16625.16 | 0 | 0 | 1 | 5000 | 16625.16 | 0 | 0 | 0 | 0 | 0 | 27271.64 | 0 | 0 | 0 | 0 | 0 | 27271.64
2022080704 | 1 | 0.59111 | 47288.8 | 0.44195 | 15910.2 | 0 | 0 | 1 | 5000 | 15910.2 | 0 | 0 | 0 | 0 | 0 | 26378.6 | 0 | 0 | 0 | 0 | 0 | 26378.6
2022080705 | 1 | 0.57684 | 46147.2 | 0.40924 | 14732.64 | 0 | 0 | 1 | 5000 | 14732.64 | 0 | 0 | 0 | 0 | 0 | 26414.56 | 0 | 0 | 0 | 0 | 0 | 26414.56
2022080706 | 1 | 0.56951 | 45560.8 | 0.38046 | 13696.56 | 0 | 0 | 1 | 5000 | 13696.56 | 0 | 0 | 0 | 0 | 0 | 26864.24 | 0 | 0 | 0 | 0 | 0 | 26864.24
2022080707 | 1 | 0.56503 | 45202.4 | 0.35551 | 12798.36 | 0.00013 | 1.56 | 1 | 5000 | 12798.36 | 1.56 | 0 | 0 | 0 | 0 | 27402.48 | 0 | 0 | 0 | 0 | 0 | 27402.48
2022080708 | 1 | 0.5665 | 45320 | 0.31967 | 11508.12 | 0.08698 | 1043.76 | 1 | 5000 | 11508.12 | 1043.76 | 0 | 0 | 0 | 0 | 27768.12 | 0 | 0 | 0 | 0 | 0 | 27768.12
2022080709 | 1 | 0.60579 | 48463.2 | 0.2803 | 10090.8 | 0.46871 | 5624.52 | 1 | 5000 | 10090.8 | 5624.52 | 0 | 0 | 0 | 0 | 27747.88 | 0 | 0 | 0 | 0 | 0 | 27747.88
2022080710 | 1 | 0.66117 | 52893.6 | 0.34291 | 12344.76 | 0.72714 | 8725.68 | 1 | 5000 | 12344.76 | 8725.68 | 0 | 0 | 0 | 0 | 26823.16 | 0 | 0 | 0 | 0 | 0 | 26823.16
2022080711 | 1 | 0.71554 | 57243.2 | 0.32494 | 11697.84 | 0.78282 | 9393.84 | 1 | 5000 | 11697.84 | 9393.84 | 0 | 0 | 0 | 0 | 31151.52 | 0 | 0 | 0 | 0 | 0 | 31151.52
2022080712 | 1 | 0.76835 | 61468 | 0.28438 | 10237.68 | 0.77642 | 9317.04 | 1 | 5000 | 10237.68 | 9317.04 | 0 | 0 | 0 | 0 | 36913.28 | 0 | 0 | 0 | 0 | 0 | 36913.28
2022080713 | 1 | 0.81305 | 65044 | 0.24483 | 8813.88 | 0.76843 | 9221.16 | 1 | 5000 | 8813.88 | 9221.16 | 0 | 0 | 0 | 0 | 42008.96 | 0 | 0 | 0 | 0 | 0 | 42008.96
2022080714 | 1 | 0.85227 | 68181.6 | 0.24603 | 8857.08 | 0.72103 | 8652.36 | 1 | 5000 | 8857.08 | 8652.36 | 0 | 0 | 0 | 0 | 45672.16 | 0 | 0 | 0 | 0 | 0 | 45672.16
2022080715 | 1 | 0.88177 | 70541.6 | 0.26201 | 9432.36 | 0.69471 | 8336.52 | 1 | 5000 | 9432.36 | 8336.52 | 0 | 0 | 0 | 0 | 47772.72 | 0 | 0 | 0 | 0 | 0 | 47772.72
2022080716 | 1 | 0.90283 | 72226.4 | 0.28717 | 10338.12 | 0.66101 | 7932.12 | 1 | 5000 | 10338.12 | 7932.12 | 0 | 0 | 0 | 0 | 48956.16 | 0 | 0 | 0 | 0 | 0 | 48956.16
2022080717 | 1 | 0.91747 | 73397.6 | 0.31348 | 11285.28 | 0.65844 | 7901.28 | 1 | 5000 | 11285.28 | 7901.28 | 0 | 0 | 0 | 0 | 49211.04 | 0 | 0 | 0 | 0 | 0 | 49211.04
2022080718 | 1 | 0.9199 | 73592 | 0.33835 | 12180.6 | 0.622 | 7464 | 1 | 5000 | 12180.6 | 7464 | 0 | 0 | 0 | 0 | 48947.4 | 0 | 0 | 0 | 0 | 0 | 48947.4
2022080719 | 1 | 0.9047 | 72376 | 0.35621 | 12823.56 | 0.53122 | 6374.64 | 1 | 5000 | 12823.56 | 6374.64 | 0 | 0 | 0 | 0 | 48177.8 | 0 | 0 | 0 | 0 | 0 | 48177.8
2022080720 | 1 | 0.87351 | 69880.8 | 0.371 | 13356 | 0.25666 | 3079.92 | 1 | 5000 | 13356 | 3079.92 | 0 | 0 | 0 | 0 | 48444.88 | 0 | 0 | 0 | 0 | 0 | 48444.88
2022080721 | 1 | 0.84327 | 67461.6 | 0.35259 | 12693.24 | 0.01632 | 195.84 | 1 | 5000 | 12693.24 | 195.84 | 0 | 0 | 0 | 0 | 49572.52 | 0 | 0 | 0 | 0 | 0 | 49572.52
2022080722 | 1 | 0.81616 | 65292.8 | 0.34668 | 12480.48 | 0 | 0 | 1 | 5000 | 12480.48 | 0 | 0 | 0 | 0 | 0 | 47812.32 | 0 | 0 | 0 | 0 | 0 | 47812.32
2022080723 | 1 | 0.77005 | 61604 | 0.37587 | 13531.32 | 0 | 0 | 1 | 5000 | 13531.32 | 0 | 0 | 0 | 0 | 0 | 43072.68 | 0 | 0 | 0 | 0 | 0 | 43072.68
2022080724 | 1 | 0.71867 | 57493.6 | 0.4009 | 14432.4 | 0 | 0 | 1 | 5000 | 14432.4 | 0 | 0 | 0 | 0 | 0 | 38061.2 | 0 | 0 | 0 | 0 | 0 | 38061.2
2022080801 | 2 | 0.67658 | 54126.4 | 0.42369 | 15252.84 | 0 | 0 | 1 | 5000 | 15252.84 | 0 | 0 | 0 | 0 | 0 | 33873.56 | 0 | 0 | 0 | 0 | 0 | 33873.56
2022080802 | 2 | 0.64911 | 51928.8 | 0.43158 | 15536.88 | 0 | 0 | 1 | 5000 | 15536.88 | 0 | 0 | 0 | 0 | 0 | 31391.92 | 0 | 0 | 0 | 0 | 0 | 31391.92
2022080803 | 2 | 0.62438 | 49950.4 | 0.43074 | 15506.64 | 0 | 0 | 1 | 5000 | 15506.64 | 0 | 0 | 0 | 0 | 0 | 29443.76 | 0 | 0 | 0 | 0 | 0 | 29443.76
2022080804 | 2 | 0.60811 | 48648.8 | 0.4048 | 14572.8 | 0 | 0 | 1 | 5000 | 14572.8 | 0 | 0 | 0 | 0 | 0 | 29076 | 0 | 0 | 0 | 0 | 0 | 29076
2022080805 | 2 | 0.60259 | 48207.2 | 0.36285 | 13062.6 | 0 | 0 | 1 | 5000 | 13062.6 | 0 | 0 | 0 | 0 | 0 | 30144.6 | 0 | 0 | 0 | 0 | 0 | 30144.6
2022080806 | 2 | 0.60961 | 48768.8 | 0.32748 | 11789.28 | 0 | 0 | 1 | 5000 | 11789.28 | 0 | 0 | 0 | 0 | 0 | 31979.52 | 0 | 0 | 0 | 0 | 0 | 31979.52
2022080807 | 2 | 0.62599 | 50079.2 | 0.29926 | 10773.36 | 0.0001 | 1.2 | 1 | 5000 | 10773.36 | 1.2 | 0 | 0 | 0 | 0 | 34304.64 | 0 | 0 | 0 | 0 | 0 | 34304.64
2022080808 | 2 | 0.63362 | 50689.6 | 0.27049 | 9737.64 | 0.07829 | 939.48 | 1 | 5000 | 9737.64 | 939.48 | 0 | 0 | 0 | 0 | 35012.48 | 0 | 0 | 0 | 0 | 0 | 35012.48
2022080809 | 2 | 0.66681 | 53344.8 | 0.2347 | 8449.2 | 0.43701 | 5244.12 | 1 | 5000 | 8449.2 | 5244.12 | 0 | 0 | 0 | 0 | 34651.48 | 0 | 0 | 0 | 0 | 0 | 34651.48
2022080810 | 2 | 0.71417 | 57133.6 | 0.24856 | 8948.16 | 0.7212 | 8654.4 | 1 | 5000 | 8948.16 | 8654.4 | 0 | 0 | 0 | 0 | 34531.04 | 0 | 0 | 0 | 0 | 0 | 34531.04
2022080811 | 2 | 0.76573 | 61258.4 | 0.18117 | 6522.12 | 0.78668 | 9440.16 | 1 | 5000 | 6522.12 | 9440.16 | 0 | 0 | 0 | 0 | 40296.12 | 0 | 0 | 0 | 0 | 0 | 40296.12
2022080812 | 2 | 0.81818 | 65454.4 | 0.12027 | 4329.72 | 0.78861 | 9463.32 | 1 | 5000 | 4329.72 | 9463.32 | 0 | 0 | 0 | 0 | 46661.36 | 0 | 0 | 0 | 0 | 0 | 46661.36
2022080813 | 2 | 0.86921 | 69536.8 | 0.10082 | 3629.52 | 0.76745 | 9209.4 | 1 | 5000 | 3629.52 | 9209.4 | 0 | 0 | 0 | 0 | 51697.88 | 0 | 0 | 0 | 0 | 0 | 51697.88
2022080814 | 2 | 0.91109 | 72887.2 | 0.11165 | 4019.4 | 0.73265 | 8791.8 | 1 | 5000 | 4019.4 | 8791.8 | 0 | 0 | 0 | 0 | 55076 | 0 | 0 | 0 | 0 | 0 | 55076
2022080815 | 2 | 0.93645 | 74916 | 0.12594 | 4533.84 | 0.69811 | 8377.32 | 1 | 5000 | 4533.84 | 8377.32 | 0 | 0 | 0 | 0 | 57004.84 | 0 | 0 | 0 | 0 | 0 | 57004.84
2022080816 | 2 | 0.95401 | 76320.8 | 0.15728 | 5662.08 | 0.68162 | 8179.44 | 1 | 5000 | 5662.08 | 8179.44 | 0 | 0 | 0 | 0 | 57479.28 | 0 | 0 | 0 | 0 | 0 | 57479.28
2022080817 | 2 | 0.96068 | 76854.4 | 0.19887 | 7159.32 | 0.65717 | 7886.04 | 1 | 5000 | 7159.32 | 7886.04 | 0 | 0 | 0 | 0 | 56809.04 | 0 | 0 | 0 | 0 | 0 | 56809.04
2022080818 | 2 | 0.9543 | 76344 | 0.20093 | 7233.48 | 0.60739 | 7288.68 | 1 | 5000 | 7233.48 | 7288.68 | 0 | 0 | 0 | 0 | 56821.84 | 0 | 0 | 0 | 0 | 0 | 56821.84
2022080819 | 2 | 0.9325 | 74600 | 0.19587 | 7051.32 | 0.49966 | 5995.92 | 1 | 5000 | 7051.32 | 5995.92 | 0 | 0 | 0 | 0 | 56552.76 | 0 | 0 | 0 | 0 | 0 | 56552.76
2022080820 | 2 | 0.8954 | 71632 | 0.18282 | 6581.52 | 0.22751 | 2730.12 | 1 | 5000 | 6581.52 | 2730.12 | 0 | 0 | 0 | 0 | 57320.36 | 0 | 0 | 0 | 0 | 0 | 57320.36
2022080821 | 2 | 0.86355 | 69084 | 0.19571 | 7045.56 | 0.01198 | 143.76 | 1 | 5000 | 7045.56 | 143.76 | 0 | 0 | 0 | 0 | 56894.68 | 0 | 0 | 0 | 0 | 0 | 56894.68
2022080822 | 2 | 0.83579 | 66863.2 | 0.22675 | 8163 | 0 | 0 | 1 | 5000 | 8163 | 0 | 0 | 0 | 0 | 0 | 53700.2 | 0 | 0 | 0 | 0 | 0 | 53700.2
2022080823 | 2 | 0.78762 | 63009.6 | 0.25525 | 9189 | 0 | 0 | 1 | 5000 | 9189 | 0 | 0 | 0 | 0 | 0 | 48820.6 | 0 | 0 | 0 | 0 | 0 | 48820.6
2022080824 | 2 | 0.73442 | 58753.6 | 0.2822 | 10159.2 | 0 | 0 | 1 | 5000 | 10159.2 | 0 | 0 | 0 | 0 | 0 | 43594.4 | 0 | 0 | 0 | 0 | 0 | 43594.4
2022080901 | 3 | 0.68792 | 55033.6 | 0.30917 | 11130.12 | 0 | 0 | 1 | 5000 | 11130.12 | 0 | 0 | 0 | 0 | 0 | 38903.48 | 0 | 0 | 0 | 0 | 0 | 38903.48
2022080902 | 3 | 0.65293 | 52234.4 | 0.32102 | 11556.72 | 0 | 0 | 1 | 5000 | 11556.72 | 0 | 0 | 0 | 0 | 0 | 35677.68 | 0 | 0 | 0 | 0 | 0 | 35677.68
2022080903 | 3 | 0.62908 | 50326.4 | 0.30989 | 11156.04 | 0 | 0 | 1 | 5000 | 11156.04 | 0 | 0 | 0 | 0 | 0 | 34170.36 | 0 | 0 | 0 | 0 | 0 | 34170.36
2022080904 | 3 | 0.61608 | 49286.4 | 0.30029 | 10810.44 | 0 | 0 | 1 | 5000 | 10810.44 | 0 | 0 | 0 | 0 | 0 | 33475.96 | 0 | 0 | 0 | 0 | 0 | 33475.96
2022080905 | 3 | 0.60982 | 48785.6 | 0.28906 | 10406.16 | 0 | 0 | 1 | 5000 | 10406.16 | 0 | 0 | 0 | 0 | 0 | 33379.44 | 0 | 0 | 0 | 0 | 0 | 33379.44
2022080906 | 3 | 0.61481 | 49184.8 | 0.24026 | 8649.36 | 0 | 0 | 1 | 5000 | 8649.36 | 0 | 0 | 0 | 0 | 0 | 35535.44 | 0 | 0 | 0 | 0 | 0 | 35535.44
2022080907 | 3 | 0.62839 | 50271.2 | 0.213 | 7668 | 9e-05 | 1.08 | 1 | 5000 | 7668 | 1.08 | 0 | 0 | 0 | 0 | 37602.12 | 0 | 0 | 0 | 0 | 0 | 37602.12
2022080908 | 3 | 0.63618 | 50894.4 | 0.1526 | 5493.6 | 0.06453 | 774.36 | 1 | 5000 | 5493.6 | 774.36 | 0 | 0 | 0 | 0 | 39626.44 | 0 | 0 | 0 | 0 | 0 | 39626.44
2022080909 | 3 | 0.66716 | 53372.8 | 0.09542 | 3435.12 | 0.41902 | 5028.24 | 1 | 5000 | 3435.12 | 5028.24 | 0 | 0 | 0 | 0 | 39909.44 | 0 | 0 | 0 | 0 | 0 | 39909.44
2022080910 | 3 | 0.71483 | 57186.4 | 0.07635 | 2748.6 | 0.63911 | 7669.32 | 1 | 5000 | 2748.6 | 7669.32 | 0 | 0 | 0 | 0 | 41768.48 | 0 | 0 | 0 | 0 | 0 | 41768.48
2022080911 | 3 | 0.76944 | 61555.2 | 0.0608 | 2188.8 | 0.66808 | 8016.96 | 1 | 5000 | 2188.8 | 8016.96 | 0 | 0 | 0 | 0 | 46349.44 | 0 | 0 | 0 | 0 | 0 | 46349.44
2022080912 | 3 | 0.8239 | 65912 | 0.04013 | 1444.68 | 0.69776 | 8373.12 | 1 | 5000 | 1444.68 | 8373.12 | 0 | 0 | 0 | 0 | 51094.2 | 0 | 0 | 0 | 0 | 0 | 51094.2
2022080913 | 3 | 0.87038 | 69630.4 | 0.03851 | 1386.36 | 0.68157 | 8178.84 | 1 | 5000 | 1386.36 | 8178.84 | 0 | 0 | 0 | 0 | 55065.2 | 0 | 0 | 0 | 0 | 0 | 55065.2
2022080914 | 3 | 0.9068 | 72544 | 0.05654 | 2035.44 | 0.6718 | 8061.6 | 1 | 5000 | 2035.44 | 8061.6 | 0 | 0 | 0 | 0 | 57446.96 | 0 | 0 | 0 | 0 | 0 | 57446.96
2022080915 | 3 | 0.92359 | 73887.2 | 0.08118 | 2922.48 | 0.62011 | 7441.32 | 1 | 5000 | 2922.48 | 7441.32 | 0 | 0 | 0 | 0 | 58523.4 | 0 | 0 | 0 | 0 | 0 | 58523.4
2022080916 | 3 | 0.92458 | 73966.4 | 0.13134 | 4728.24 | 0.55004 | 6600.48 | 1 | 5000 | 4728.24 | 6600.48 | 0 | 0 | 0 | 0 | 57637.68 | 0 | 0 | 0 | 0 | 0 | 57637.68
2022080917 | 3 | 0.91614 | 73291.2 | 0.17422 | 6271.92 | 0.51032 | 6123.84 | 1 | 5000 | 6271.92 | 6123.84 | 0 | 0 | 0 | 0 | 55895.44 | 0 | 0 | 0 | 0 | 0 | 55895.44
2022080918 | 3 | 0.8942 | 71536 | 0.19918 | 7170.48 | 0.48953 | 5874.36 | 1 | 5000 | 7170.48 | 5874.36 | 0 | 0 | 0 | 0 | 53491.16 | 0 | 0 | 0 | 0 | 0 | 53491.16
2022080919 | 3 | 0.86967 | 69573.6 | 0.24444 | 8799.84 | 0.3844 | 4612.8 | 1 | 5000 | 8799.84 | 4612.8 | 0 | 0 | 0 | 0 | 51160.96 | 0 | 0 | 0 | 0 | 0 | 51160.96
2022080920 | 3 | 0.84124 | 67299.2 | 0.27623 | 9944.28 | 0.1816 | 2179.2 | 1 | 5000 | 9944.28 | 2179.2 | 0 | 0 | 0 | 0 | 50175.72 | 0 | 0 | 0 | 0 | 0 | 50175.72
2022080921 | 3 | 0.82073 | 65658.4 | 0.24037 | 8653.32 | 0.0087 | 104.4 | 1 | 5000 | 8653.32 | 104.4 | 0 | 0 | 0 | 0 | 51900.68 | 0 | 0 | 0 | 0 | 0 | 51900.68
2022080922 | 3 | 0.795 | 63600 | 0.2283 | 8218.8 | 0 | 0 | 1 | 5000 | 8218.8 | 0 | 0 | 0 | 0 | 0 | 50381.2 | 0 | 0 | 0 | 0 | 0 | 50381.2
2022080923 | 3 | 0.75061 | 60048.8 | 0.21498 | 7739.28 | 0 | 0 | 1 | 5000 | 7739.28 | 0 | 0 | 0 | 0 | 0 | 47309.52 | 0 | 0 | 0 | 0 | 0 | 47309.52
2022080924 | 3 | 0.70147 | 56117.6 | 0.19022 | 6847.92 | 0 | 0 | 1 | 5000 | 6847.92 | 0 | 0 | 0 | 0 | 0 | 44269.68 | 0 | 0 | 0 | 0 | 0 | 44269.68
2022081001 | 4 | 0.65783 | 52626.4 | 0.18162 | 6538.32 | 0 | 0 | 1 | 5000 | 6538.32 | 0 | 0 | 0 | 0 | 0 | 41088.08 | 0 | 0 | 0 | 0 | 0 | 41088.08
2022081002 | 4 | 0.62528 | 50022.4 | 0.17226 | 6201.36 | 0 | 0 | 1 | 5000 | 6201.36 | 0 | 0 | 0 | 0 | 0 | 38821.04 | 0 | 0 | 0 | 0 | 0 | 38821.04
2022081003 | 4 | 0.60317 | 48253.6 | 0.16965 | 6107.4 | 0 | 0 | 1 | 5000 | 6107.4 | 0 | 0 | 0 | 0 | 0 | 37146.2 | 0 | 0 | 0 | 0 | 0 | 37146.2
2022081004 | 4 | 0.58905 | 47124 | 0.17215 | 6197.4 | 0 | 0 | 1 | 5000 | 6197.4 | 0 | 0 | 0 | 0 | 0 | 35926.6 | 0 | 0 | 0 | 0 | 0 | 35926.6
2022081005 | 4 | 0.58552 | 46841.6 | 0.16455 | 5923.8 | 0 | 0 | 1 | 5000 | 5923.8 | 0 | 0 | 0 | 0 | 0 | 35917.8 | 0 | 0 | 0 | 0 | 0 | 35917.8
2022081006 | 4 | 0.5954 | 47632 | 0.1476 | 5313.6 | 0 | 0 | 1 | 5000 | 5313.6 | 0 | 0 | 0 | 0 | 0 | 37318.4 | 0 | 0 | 0 | 0 | 0 | 37318.4
2022081007 | 4 | 0.61317 | 49053.6 | 0.13789 | 4964.04 | 7e-05 | 0.84 | 1 | 5000 | 4964.04 | 0.84 | 0 | 0 | 0 | 0 | 39088.72 | 0 | 0 | 0 | 0 | 0 | 39088.72
2022081008 | 4 | 0.62138 | 49710.4 | 0.12258 | 4412.88 | 0.05285 | 634.2 | 1 | 5000 | 4412.88 | 634.2 | 0 | 0 | 0 | 0 | 39663.32 | 0 | 0 | 0 | 0 | 0 | 39663.32
2022081009 | 4 | 0.65435 | 52348 | 0.09412 | 3388.32 | 0.30239 | 3628.68 | 1 | 5000 | 3388.32 | 3628.68 | 0 | 0 | 0 | 0 | 40331 | 0 | 0 | 0 | 0 | 0 | 40331
2022081010 | 4 | 0.7013 | 56104 | 0.07394 | 2661.84 | 0.53446 | 6413.52 | 1 | 5000 | 2661.84 | 6413.52 | 0 | 0 | 0 | 0 | 42028.64 | 0 | 0 | 0 | 0 | 0 | 42028.64
2022081011 | 4 | 0.75699 | 60559.2 | 0.04959 | 1785.24 | 0.63375 | 7605 | 1 | 5000 | 1785.24 | 7605 | 0 | 0 | 0 | 0 | 46168.96 | 0 | 0 | 0 | 0 | 0 | 46168.96
2022081012 | 4 | 0.81487 | 65189.6 | 0.0402 | 1447.2 | 0.65468 | 7856.16 | 1 | 5000 | 1447.2 | 7856.16 | 0 | 0 | 0 | 0 | 50886.24 | 0 | 0 | 0 | 0 | 0 | 50886.24
2022081013 | 4 | 0.86556 | 69244.8 | 0.07433 | 2675.88 | 0.64481 | 7737.72 | 1 | 5000 | 2675.88 | 7737.72 | 0 | 0 | 0 | 0 | 53831.2 | 0 | 0 | 0 | 0 | 0 | 53831.2
2022081014 | 4 | 0.90619 | 72495.2 | 0.11222 | 4039.92 | 0.63501 | 7620.12 | 1 | 5000 | 4039.92 | 7620.12 | 0 | 0 | 0 | 0 | 55835.16 | 0 | 0 | 0 | 0 | 0 | 55835.16
2022081015 | 4 | 0.93059 | 74447.2 | 0.14755 | 5311.8 | 0.56893 | 6827.16 | 1 | 5000 | 5311.8 | 6827.16 | 0 | 0 | 0 | 0 | 57308.24 | 0 | 0 | 0 | 0 | 0 | 57308.24
2022081016 | 4 | 0.94028 | 75222.4 | 0.19546 | 7036.56 | 0.52332 | 6279.84 | 1 | 5000 | 7036.56 | 6279.84 | 0 | 0 | 0 | 0 | 56906 | 0 | 0 | 0 | 0 | 0 | 56906
2022081017 | 4 | 0.92885 | 74308 | 0.18741 | 6746.76 | 0.48981 | 5877.72 | 1 | 5000 | 6746.76 | 5877.72 | 0 | 0 | 0 | 0 | 56683.52 | 0 | 0 | 0 | 0 | 0 | 56683.52
2022081018 | 4 | 0.89796 | 71836.8 | 0.178 | 6408 | 0.44323 | 5318.76 | 1 | 5000 | 6408 | 5318.76 | 0 | 0 | 0 | 0 | 55110.04 | 0 | 0 | 0 | 0 | 0 | 55110.04
2022081019 | 4 | 0.85333 | 68266.4 | 0.18733 | 6743.88 | 0.33111 | 3973.32 | 1 | 5000 | 6743.88 | 3973.32 | 0 | 0 | 0 | 0 | 52549.2 | 0 | 0 | 0 | 0 | 0 | 52549.2
2022081020 | 4 | 0.79491 | 63592.8 | 0.19028 | 6850.08 | 0.17194 | 2063.28 | 1 | 5000 | 6850.08 | 2063.28 | 0 | 0 | 0 | 0 | 49679.44 | 0 | 0 | 0 | 0 | 0 | 49679.44
2022081021 | 4 | 0.76779 | 61423.2 | 0.18259 | 6573.24 | 0.01027 | 123.24 | 1 | 5000 | 6573.24 | 123.24 | 0 | 0 | 0 | 0 | 49726.72 | 0 | 0 | 0 | 0 | 0 | 49726.72
2022081022 | 4 | 0.74164 | 59331.2 | 0.15961 | 5745.96 | 0 | 0 | 1 | 5000 | 5745.96 | 0 | 0 | 0 | 0 | 0 | 48585.24 | 0 | 0 | 0 | 0 | 0 | 48585.24
2022081023 | 4 | 0.69977 | 55981.6 | 0.14576 | 5247.36 | 0 | 0 | 1 | 5000 | 5247.36 | 0 | 0 | 0 | 0 | 0 | 45734.24 | 0 | 0 | 0 | 0 | 0 | 45734.24
2022081024 | 4 | 0.65498 | 52398.4 | 0.13444 | 4839.84 | 0 | 0 | 1 | 5000 | 4839.84 | 0 | 0 | 0 | 0 | 0 | 42558.56 | 0 | 0 | 0 | 0 | 0 | 42558.56
2022081101 | 5 | 0.61645 | 49316 | 0.12515 | 4505.4 | 0 | 0 | 1 | 5000 | 4505.4 | 0 | 0 | 0 | 0 | 0 | 39810.6 | 0 | 0 | 0 | 0 | 0 | 39810.6
2022081102 | 5 | 0.58734 | 46987.2 | 0.10001 | 3600.36 | 0 | 0 | 1 | 5000 | 3600.36 | 0 | 0 | 0 | 0 | 0 | 38386.84 | 0 | 0 | 0 | 0 | 0 | 38386.84
2022081103 | 5 | 0.56949 | 45559.2 | 0.09135 | 3288.6 | 0 | 0 | 1 | 5000 | 3288.6 | 0 | 0 | 0 | 0 | 0 | 37270.6 | 0 | 0 | 0 | 0 | 0 | 37270.6
2022081104 | 5 | 0.5586 | 44688 | 0.07043 | 2535.48 | 0 | 0 | 1 | 5000 | 2535.48 | 0 | 0 | 0 | 0 | 0 | 37152.52 | 0 | 0 | 0 | 0 | 0 | 37152.52
2022081105 | 5 | 0.55593 | 44474.4 | 0.06337 | 2281.32 | 0 | 0 | 1 | 5000 | 2281.32 | 0 | 0 | 0 | 0 | 0 | 37193.08 | 0 | 0 | 0 | 0 | 0 | 37193.08
2022081106 | 5 | 0.56831 | 45464.8 | 0.04396 | 1582.56 | 0 | 0 | 1 | 5000 | 1582.56 | 0 | 0 | 0 | 0 | 0 | 38882.24 | 0 | 0 | 0 | 0 | 0 | 38882.24
2022081107 | 5 | 0.59013 | 47210.4 | 0.0304 | 1094.4 | 0 | 0 | 1 | 5000 | 1094.4 | 0 | 0 | 0 | 0 | 0 | 41116 | 0 | 0 | 0 | 0 | 0 | 41116
2022081108 | 5 | 0.59984 | 47987.2 | 0.02297 | 826.92 | 0.0543 | 651.6 | 1 | 5000 | 826.92 | 651.6 | 0 | 0 | 0 | 0 | 41508.68 | 0 | 0 | 0 | 0 | 0 | 41508.68
2022081109 | 5 | 0.62549 | 50039.2 | 0.0128 | 460.8 | 0.36436 | 4372.32 | 1 | 5000 | 460.8 | 4372.32 | 0 | 0 | 0 | 0 | 40206.08 | 0 | 0 | 0 | 0 | 0 | 40206.08
2022081110 | 5 | 0.66784 | 53427.2 | 0.01076 | 387.36 | 0.54718 | 6566.16 | 1 | 5000 | 387.36 | 6566.16 | 0 | 0 | 0 | 0 | 41473.68 | 0 | 0 | 0 | 0 | 0 | 41473.68
2022081111 | 5 | 0.72269 | 57815.2 | 0.01128 | 406.08 | 0.60359 | 7243.08 | 1 | 5000 | 406.08 | 7243.08 | 0 | 0 | 0 | 0 | 45166.04 | 0 | 0 | 0 | 0 | 0 | 45166.04
2022081112 | 5 | 0.77841 | 62272.8 | 0.01716 | 617.76 | 0.63582 | 7629.84 | 1 | 5000 | 617.76 | 7629.84 | 0 | 0 | 0 | 0 | 49025.2 | 0 | 0 | 0 | 0 | 0 | 49025.2
2022081113 | 5 | 0.83053 | 66442.4 | 0.0242 | 871.2 | 0.64019 | 7682.28 | 1 | 5000 | 871.2 | 7682.28 | 0 | 0 | 0 | 0 | 52888.92 | 0 | 0 | 0 | 0 | 0 | 52888.92
2022081114 | 5 | 0.87346 | 69876.8 | 0.04531 | 1631.16 | 0.67465 | 8095.8 | 1 | 5000 | 1631.16 | 8095.8 | 0 | 0 | 0 | 0 | 55149.84 | 0 | 0 | 0 | 0 | 0 | 55149.84
2022081115 | 5 | 0.90087 | 72069.6 | 0.07846 | 2824.56 | 0.67651 | 8118.12 | 1 | 5000 | 2824.56 | 8118.12 | 0 | 0 | 0 | 0 | 56126.92 | 0 | 0 | 0 | 0 | 0 | 56126.92
2022081116 | 5 | 0.92221 | 73776.8 | 0.12028 | 4330.08 | 0.65777 | 7893.24 | 1 | 5000 | 4330.08 | 7893.24 | 0 | 0 | 0 | 0 | 56553.48 | 0 | 0 | 0 | 0 | 0 | 56553.48
2022081117 | 5 | 0.92898 | 74318.4 | 0.15393 | 5541.48 | 0.58681 | 7041.72 | 1 | 5000 | 5541.48 | 7041.72 | 0 | 0 | 0 | 0 | 56735.2 | 0 | 0 | 0 | 0 | 0 | 56735.2
2022081118 | 5 | 0.92039 | 73631.2 | 0.18713 | 6736.68 | 0.48773 | 5852.76 | 1 | 5000 | 6736.68 | 5852.76 | 0 | 0 | 0 | 0 | 56041.76 | 0 | 0 | 0 | 0 | 0 | 56041.76
2022081119 | 5 | 0.89375 | 71500 | 0.21216 | 7637.76 | 0.29842 | 3581.04 | 1 | 5000 | 7637.76 | 3581.04 | 0 | 0 | 0 | 0 | 55281.2 | 0 | 0 | 0 | 0 | 0 | 55281.2
2022081120 | 5 | 0.86054 | 68843.2 | 0.23413 | 8428.68 | 0.09113 | 1093.56 | 1 | 5000 | 8428.68 | 1093.56 | 0 | 0 | 0 | 0 | 54320.96 | 0 | 0 | 0 | 0 | 0 | 54320.96
2022081121 | 5 | 0.83022 | 66417.6 | 0.22015 | 7925.4 | 0.00392 | 47.04 | 1 | 5000 | 7925.4 | 47.04 | 0 | 0 | 0 | 0 | 53445.16 | 0 | 0 | 0 | 0 | 0 | 53445.16
2022081122 | 5 | 0.79768 | 63814.4 | 0.23307 | 8390.52 | 0 | 0 | 1 | 5000 | 8390.52 | 0 | 0 | 0 | 0 | 0 | 50423.88 | 0 | 0 | 0 | 0 | 0 | 50423.88
2022081123 | 5 | 0.75143 | 60114.4 | 0.2463 | 8866.8 | 0 | 0 | 1 | 5000 | 8866.8 | 0 | 0 | 0 | 0 | 0 | 46247.6 | 0 | 0 | 0 | 0 | 0 | 46247.6
2022081124 | 5 | 0.70314 | 56251.2 | 0.25878 | 9316.08 | 0 | 0 | 1 | 5000 | 9316.08 | 0 | 0 | 0 | 0 | 0 | 41935.12 | 0 | 0 | 0 | 0 | 0 | 41935.12
2022081201 | 6 | 0.66044 | 52835.2 | 0.24035 | 8652.6 | 0 | 0 | 1 | 5000 | 8652.6 | 0 | 0 | 0 | 0 | 0 | 39182.6 | 0 | 0 | 0 | 0 | 0 | 39182.6
2022081202 | 6 | 0.62725 | 50180 | 0.22417 | 8070.12 | 0 | 0 | 1 | 5000 | 8070.12 | 0 | 0 | 0 | 0 | 0 | 37109.88 | 0 | 0 | 0 | 0 | 0 | 37109.88
2022081203 | 6 | 0.60269 | 48215.2 | 0.1926 | 6933.6 | 0 | 0 | 1 | 5000 | 6933.6 | 0 | 0 | 0 | 0 | 0 | 36281.6 | 0 | 0 | 0 | 0 | 0 | 36281.6
2022081204 | 6 | 0.59047 | 47237.6 | 0.15439 | 5558.04 | 0 | 0 | 1 | 5000 | 5558.04 | 0 | 0 | 0 | 0 | 0 | 36679.56 | 0 | 0 | 0 | 0 | 0 | 36679.56
2022081205 | 6 | 0.58561 | 46848.8 | 0.1254 | 4514.4 | 0 | 0 | 1 | 5000 | 4514.4 | 0 | 0 | 0 | 0 | 0 | 37334.4 | 0 | 0 | 0 | 0 | 0 | 37334.4
2022081206 | 6 | 0.59229 | 47383.2 | 0.10822 | 3895.92 | 0 | 0 | 1 | 5000 | 3895.92 | 0 | 0 | 0 | 0 | 0 | 38487.28 | 0 | 0 | 0 | 0 | 0 | 38487.28
2022081207 | 6 | 0.60922 | 48737.6 | 0.08339 | 3002.04 | 5e-05 | 0.6 | 1 | 5000 | 3002.04 | 0.6 | 0 | 0 | 0 | 0 | 40734.96 | 0 | 0 | 0 | 0 | 0 | 40734.96
2022081208 | 6 | 0.61674 | 49339.2 | 0.05949 | 2141.64 | 0.05684 | 682.08 | 1 | 5000 | 2141.64 | 682.08 | 0 | 0 | 0 | 0 | 41515.48 | 0 | 0 | 0 | 0 | 0 | 41515.48
2022081209 | 6 | 0.64602 | 51681.6 | 0.034 | 1224 | 0.39862 | 4783.44 | 1 | 5000 | 1224 | 4783.44 | 0 | 0 | 0 | 0 | 40674.16 | 0 | 0 | 0 | 0 | 0 | 40674.16
2022081210 | 6 | 0.69116 | 55292.8 | 0.02733 | 983.88 | 0.64174 | 7700.88 | 1 | 5000 | 983.88 | 7700.88 | 0 | 0 | 0 | 0 | 41608.04 | 0 | 0 | 0 | 0 | 0 | 41608.04
2022081211 | 6 | 0.74657 | 59725.6 | 0.0496 | 1785.6 | 0.70904 | 8508.48 | 1 | 5000 | 1785.6 | 8508.48 | 0 | 0 | 0 | 0 | 44431.52 | 0 | 0 | 0 | 0 | 0 | 44431.52
2022081212 | 6 | 0.80057 | 64045.6 | 0.05413 | 1948.68 | 0.74523 | 8942.76 | 1 | 5000 | 1948.68 | 8942.76 | 0 | 0 | 0 | 0 | 48154.16 | 0 | 0 | 0 | 0 | 0 | 48154.16
2022081213 | 6 | 0.84438 | 67550.4 | 0.05366 | 1931.76 | 0.6914 | 8296.8 | 1 | 5000 | 1931.76 | 8296.8 | 0 | 0 | 0 | 0 | 52321.84 | 0 | 0 | 0 | 0 | 0 | 52321.84
2022081214 | 6 | 0.87193 | 69754.4 | 0.07751 | 2790.36 | 0.64961 | 7795.32 | 1 | 5000 | 2790.36 | 7795.32 | 0 | 0 | 0 | 0 | 54168.72 | 0 | 0 | 0 | 0 | 0 | 54168.72
2022081215 | 6 | 0.89652 | 71721.6 | 0.11164 | 4019.04 | 0.61683 | 7401.96 | 1 | 5000 | 4019.04 | 7401.96 | 0 | 0 | 0 | 0 | 55300.6 | 0 | 0 | 0 | 0 | 0 | 55300.6
2022081216 | 6 | 0.90926 | 72740.8 | 0.13492 | 4857.12 | 0.63887 | 7666.44 | 1 | 5000 | 4857.12 | 7666.44 | 0 | 0 | 0 | 0 | 55217.24 | 0 | 0 | 0 | 0 | 0 | 55217.24
2022081217 | 6 | 0.91048 | 72838.4 | 0.17188 | 6187.68 | 0.64513 | 7741.56 | 1 | 5000 | 6187.68 | 7741.56 | 0 | 0 | 0 | 0 | 53909.16 | 0 | 0 | 0 | 0 | 0 | 53909.16
2022081218 | 6 | 0.89798 | 71838.4 | 0.18202 | 6552.72 | 0.60066 | 7207.92 | 1 | 5000 | 6552.72 | 7207.92 | 0 | 0 | 0 | 0 | 53077.76 | 0 | 0 | 0 | 0 | 0 | 53077.76
2022081219 | 6 | 0.871 | 69680 | 0.1748 | 6292.8 | 0.51132 | 6135.84 | 1 | 5000 | 6292.8 | 6135.84 | 0 | 0 | 0 | 0 | 52251.36 | 0 | 0 | 0 | 0 | 0 | 52251.36
2022081220 | 6 | 0.84243 | 67394.4 | 0.18264 | 6575.04 | 0.23031 | 2763.72 | 1 | 5000 | 6575.04 | 2763.72 | 0 | 0 | 0 | 0 | 53055.64 | 0 | 0 | 0 | 0 | 0 | 53055.64
2022081221 | 6 | 0.81085 | 64868 | 0.17556 | 6320.16 | 0.01182 | 141.84 | 1 | 5000 | 6320.16 | 141.84 | 0 | 0 | 0 | 0 | 53406 | 0 | 0 | 0 | 0 | 0 | 53406
2022081222 | 6 | 0.78642 | 62913.6 | 0.20682 | 7445.52 | 0 | 0 | 1 | 5000 | 7445.52 | 0 | 0 | 0 | 0 | 0 | 50468.08 | 0 | 0 | 0 | 0 | 0 | 50468.08
2022081223 | 6 | 0.74759 | 59807.2 | 0.24358 | 8768.88 | 0 | 0 | 1 | 5000 | 8768.88 | 0 | 0 | 0 | 0 | 0 | 46038.32 | 0 | 0 | 0 | 0 | 0 | 46038.32
2022081224 | 6 | 0.70459 | 56367.2 | 0.2551 | 9183.6 | 0 | 0 | 1 | 5000 | 9183.6 | 0 | 0 | 0 | 0 | 0 | 42183.6 | 0 | 0 | 0 | 0 | 0 | 42183.6
2022081301 | 7 | 0.66379 | 53103.2 | 0.25722 | 9259.92 | 0 | 0 | 1 | 5000 | 9259.92 | 0 | 0 | 0 | 0 | 0 | 38843.28 | 0 | 0 | 0 | 0 | 0 | 38843.28
2022081302 | 7 | 0.63302 | 50641.6 | 0.23411 | 8427.96 | 0 | 0 | 1 | 5000 | 8427.96 | 0 | 0 | 0 | 0 | 0 | 37213.64 | 0 | 0 | 0 | 0 | 0 | 37213.64
2022081303 | 7 | 0.61117 | 48893.6 | 0.2097 | 7549.2 | 0 | 0 | 1 | 5000 | 7549.2 | 0 | 0 | 0 | 0 | 0 | 36344.4 | 0 | 0 | 0 | 0 | 0 | 36344.4
2022081304 | 7 | 0.59105 | 47284 | 0.1849 | 6656.4 | 0 | 0 | 1 | 5000 | 6656.4 | 0 | 0 | 0 | 0 | 0 | 35627.6 | 0 | 0 | 0 | 0 | 0 | 35627.6
2022081305 | 7 | 0.57981 | 46384.8 | 0.1624 | 5846.4 | 0 | 0 | 1 | 5000 | 5846.4 | 0 | 0 | 0 | 0 | 0 | 35538.4 | 0 | 0 | 0 | 0 | 0 | 35538.4
2022081306 | 7 | 0.57768 | 46214.4 | 0.1372 | 4939.2 | 0 | 0 | 1 | 5000 | 4939.2 | 0 | 0 | 0 | 0 | 0 | 36275.2 | 0 | 0 | 0 | 0 | 0 | 36275.2
2022081307 | 7 | 0.57737 | 46189.6 | 0.12113 | 4360.68 | 0 | 0 | 1 | 5000 | 4360.68 | 0 | 0 | 0 | 0 | 0 | 36828.92 | 0 | 0 | 0 | 0 | 0 | 36828.92
2022081308 | 7 | 0.5819 | 46552 | 0.11071 | 3985.56 | 0.07182 | 861.84 | 1 | 5000 | 3985.56 | 861.84 | 0 | 0 | 0 | 0 | 36704.6 | 0 | 0 | 0 | 0 | 0 | 36704.6
2022081309 | 7 | 0.6185 | 49480 | 0.06496 | 2338.56 | 0.45865 | 5503.8 | 1 | 5000 | 2338.56 | 5503.8 | 0 | 0 | 0 | 0 | 36637.64 | 0 | 0 | 0 | 0 | 0 | 36637.64
2022081310 | 7 | 0.66918 | 53534.4 | 0.04561 | 1641.96 | 0.68256 | 8190.72 | 1 | 5000 | 1641.96 | 8190.72 | 0 | 0 | 0 | 0 | 38701.72 | 0 | 0 | 0 | 0 | 0 | 38701.72
2022081311 | 7 | 0.72518 | 58014.4 | 0.0433 | 1558.8 | 0.74791 | 8974.92 | 1 | 5000 | 1558.8 | 8974.92 | 0 | 0 | 0 | 0 | 42480.68 | 0 | 0 | 0 | 0 | 0 | 42480.68
2022081312 | 7 | 0.77359 | 61887.2 | 0.03115 | 1121.4 | 0.69159 | 8299.08 | 1 | 5000 | 1121.4 | 8299.08 | 0 | 0 | 0 | 0 | 47466.72 | 0 | 0 | 0 | 0 | 0 | 47466.72
2022081313 | 7 | 0.81266 | 65012.8 | 0.03436 | 1236.96 | 0.6362 | 7634.4 | 1 | 5000 | 1236.96 | 7634.4 | 0 | 0 | 0 | 0 | 51141.44 | 0 | 0 | 0 | 0 | 0 | 51141.44
2022081314 | 7 | 0.84746 | 67796.8 | 0.03923 | 1412.28 | 0.67268 | 8072.16 | 1 | 5000 | 1412.28 | 8072.16 | 0 | 0 | 0 | 0 | 53312.36 | 0 | 0 | 0 | 0 | 0 | 53312.36
2022081315 | 7 | 0.86928 | 69542.4 | 0.05398 | 1943.28 | 0.62646 | 7517.52 | 1 | 5000 | 1943.28 | 7517.52 | 0 | 0 | 0 | 0 | 55081.6 | 0 | 0 | 0 | 0 | 0 | 55081.6
2022081316 | 7 | 0.87927 | 70341.6 | 0.06343 | 2283.48 | 0.59691 | 7162.92 | 1 | 5000 | 2283.48 | 7162.92 | 0 | 0 | 0 | 0 | 55895.2 | 0 | 0 | 0 | 0 | 0 | 55895.2
2022081317 | 7 | 0.88449 | 70759.2 | 0.08515 | 3065.4 | 0.58647 | 7037.64 | 1 | 5000 | 3065.4 | 7037.64 | 0 | 0 | 0 | 0 | 55656.16 | 0 | 0 | 0 | 0 | 0 | 55656.16
2022081318 | 7 | 0.88106 | 70484.8 | 0.08901 | 3204.36 | 0.56917 | 6830.04 | 1 | 5000 | 3204.36 | 6830.04 | 0 | 0 | 0 | 0 | 55450.4 | 0 | 0 | 0 | 0 | 0 | 55450.4
2022081319 | 7 | 0.86506 | 69204.8 | 0.09876 | 3555.36 | 0.49361 | 5923.32 | 1 | 5000 | 3555.36 | 5923.32 | 0 | 0 | 0 | 0 | 54726.12 | 0 | 0 | 0 | 0 | 0 | 54726.12
2022081320 | 7 | 0.83461 | 66768.8 | 0.11748 | 4229.28 | 0.20827 | 2499.24 | 1 | 5000 | 4229.28 | 2499.24 | 0 | 0 | 0 | 0 | 55040.28 | 0 | 0 | 0 | 0 | 0 | 55040.28
2022081321 | 7 | 0.80744 | 64595.2 | 0.15729 | 5662.44 | 0.00929 | 111.48 | 1 | 5000 | 5662.44 | 111.48 | 0 | 0 | 0 | 0 | 53821.28 | 0 | 0 | 0 | 0 | 0 | 53821.28
2022081322 | 7 | 0.78095 | 62476 | 0.19985 | 7194.6 | 0.00081 | 9.72 | 1 | 5000 | 7194.6 | 9.72 | 0 | 0 | 0 | 0 | 50271.68 | 0 | 0 | 0 | 0 | 0 | 50271.68
2022081323 | 7 | 0.73942 | 59153.6 | 0.24774 | 8918.64 | 0.00081 | 9.72 | 1 | 5000 | 8918.64 | 9.72 | 0 | 0 | 0 | 0 | 45225.24 | 0 | 0 | 0 | 0 | 0 | 45225.24
2022081324 | 7 | 0.69635 | 55708 | 0.26568 | 9564.48 | 0.00081 | 9.72 | 1 | 5000 | 9564.48 | 9.72 | 0 | 0 | 0 | 0 | 41133.8 | 0 | 0 | 0 | 0 | 0 | 41133.8
2022081401 | 1 | 0.65692 | 52553.6 | 0.27997 | 10078.92 | 0.00081 | 9.72 | 1 | 5000 | 10078.92 | 9.72 | 0 | 0 | 0 | 0 | 37464.96 | 0 | 0 | 0 | 0 | 0 | 37464.96
2022081402 | 1 | 0.62435 | 49948 | 0.27983 | 10073.88 | 0.00082 | 9.84 | 1 | 5000 | 10073.88 | 9.84 | 0 | 0 | 0 | 0 | 34864.28 | 0 | 0 | 0 | 0 | 0 | 34864.28
2022081403 | 1 | 0.6013 | 48104 | 0.27924 | 10052.64 | 0.00082 | 9.84 | 1 | 5000 | 10052.64 | 9.84 | 0 | 0 | 0 | 0 | 33041.52 | 0 | 0 | 0 | 0 | 0 | 33041.52
2022081404 | 1 | 0.58186 | 46548.8 | 0.26785 | 9642.6 | 0.00082 | 9.84 | 1 | 5000 | 9642.6 | 9.84 | 0 | 0 | 0 | 0 | 31896.36 | 0 | 0 | 0 | 0 | 0 | 31896.36
2022081405 | 1 | 0.56426 | 45140.8 | 0.25395 | 9142.2 | 0.00082 | 9.84 | 1 | 5000 | 9142.2 | 9.84 | 0 | 0 | 0 | 0 | 30988.76 | 0 | 0 | 0 | 0 | 0 | 30988.76
2022081406 | 1 | 0.55526 | 44420.8 | 0.24918 | 8970.48 | 9e-05 | 1.08 | 1 | 5000 | 8970.48 | 1.08 | 0 | 0 | 0 | 0 | 30449.24 | 0 | 0 | 0 | 0 | 0 | 30449.24
2022081407 | 1 | 0.55093 | 44074.4 | 0.22061 | 7941.96 | 7e-05 | 0.84 | 1 | 5000 | 7941.96 | 0.84 | 0 | 0 | 0 | 0 | 31131.6 | 0 | 0 | 0 | 0 | 0 | 31131.6
2022081408 | 1 | 0.55252 | 44201.6 | 0.1913 | 6886.8 | 0.05845 | 701.4 | 1 | 5000 | 6886.8 | 701.4 | 0 | 0 | 0 | 0 | 31613.4 | 0 | 0 | 0 | 0 | 0 | 31613.4
2022081409 | 1 | 0.58506 | 46804.8 | 0.13977 | 5031.72 | 0.39925 | 4791 | 1 | 5000 | 5031.72 | 4791 | 0 | 0 | 0 | 0 | 31982.08 | 0 | 0 | 0 | 0 | 0 | 31982.08
2022081410 | 1 | 0.63126 | 50500.8 | 0.11061 | 3981.96 | 0.64002 | 7680.24 | 1 | 5000 | 3981.96 | 7680.24 | 0 | 0 | 0 | 0 | 33838.6 | 0 | 0 | 0 | 0 | 0 | 33838.6
2022081411 | 1 | 0.68388 | 54710.4 | 0.10886 | 3918.96 | 0.69735 | 8368.2 | 1 | 5000 | 3918.96 | 8368.2 | 0 | 0 | 0 | 0 | 37423.24 | 0 | 0 | 0 | 0 | 0 | 37423.24
2022081412 | 1 | 0.73272 | 58617.6 | 0.0944 | 3398.4 | 0.69524 | 8342.88 | 1 | 5000 | 3398.4 | 8342.88 | 0 | 0 | 0 | 0 | 41876.32 | 0 | 0 | 0 | 0 | 0 | 41876.32
2022081413 | 1 | 0.77019 | 61615.2 | 0.11349 | 4085.64 | 0.64753 | 7770.36 | 1 | 5000 | 4085.64 | 7770.36 | 0 | 0 | 0 | 0 | 44759.2 | 0 | 0 | 0 | 0 | 0 | 44759.2
2022081414 | 1 | 0.80087 | 64069.6 | 0.13437 | 4837.32 | 0.65028 | 7803.36 | 1 | 5000 | 4837.32 | 7803.36 | 0 | 0 | 0 | 0 | 46428.92 | 0 | 0 | 0 | 0 | 0 | 46428.92
2022081415 | 1 | 0.82876 | 66300.8 | 0.14553 | 5239.08 | 0.65092 | 7811.04 | 1 | 5000 | 5239.08 | 7811.04 | 0 | 0 | 0 | 0 | 48250.68 | 0 | 0 | 0 | 0 | 0 | 48250.68
2022081416 | 1 | 0.84983 | 67986.4 | 0.15141 | 5450.76 | 0.65023 | 7802.76 | 1 | 5000 | 5450.76 | 7802.76 | 0 | 0 | 0 | 0 | 49732.88 | 0 | 0 | 0 | 0 | 0 | 49732.88
2022081417 | 1 | 0.86137 | 68909.6 | 0.14894 | 5361.84 | 0.63548 | 7625.76 | 1 | 5000 | 5361.84 | 7625.76 | 0 | 0 | 0 | 0 | 50922 | 0 | 0 | 0 | 0 | 0 | 50922
2022081418 | 1 | 0.8641 | 69128 | 0.16334 | 5880.24 | 0.61288 | 7354.56 | 1 | 5000 | 5880.24 | 7354.56 | 0 | 0 | 0 | 0 | 50893.2 | 0 | 0 | 0 | 0 | 0 | 50893.2
2022081419 | 1 | 0.85238 | 68190.4 | 0.18555 | 6679.8 | 0.49541 | 5944.92 | 1 | 5000 | 6679.8 | 5944.92 | 0 | 0 | 0 | 0 | 50565.68 | 0 | 0 | 0 | 0 | 0 | 50565.68
2022081420 | 1 | 0.82797 | 66237.6 | 0.22202 | 7992.72 | 0.21015 | 2521.8 | 1 | 5000 | 7992.72 | 2521.8 | 0 | 0 | 0 | 0 | 50723.08 | 0 | 0 | 0 | 0 | 0 | 50723.08
2022081421 | 1 | 0.80803 | 64642.4 | 0.29416 | 10589.76 | 0.01061 | 127.32 | 1 | 5000 | 10589.76 | 127.32 | 0 | 0 | 0 | 0 | 48925.32 | 0 | 0 | 0 | 0 | 0 | 48925.32
2022081422 | 1 | 0.78017 | 62413.6 | 0.37296 | 13426.56 | 0 | 0 | 1 | 5000 | 13426.56 | 0 | 0 | 0 | 0 | 0 | 43987.04 | 0 | 0 | 0 | 0 | 0 | 43987.04
2022081423 | 1 | 0.73387 | 58709.6 | 0.43749 | 15749.64 | 0 | 0 | 1 | 5000 | 15749.64 | 0 | 0 | 0 | 0 | 0 | 37959.96 | 0 | 0 | 0 | 0 | 0 | 37959.96
2022081424 | 1 | 0.68756 | 55004.8 | 0.48151 | 17334.36 | 0 | 0 | 1 | 5000 | 17334.36 | 0 | 0 | 0 | 0 | 0 | 32670.44 | 0 | 0 | 0 | 0 | 0 | 32670.44
2022081501 | 2 | 0.64828 | 51862.4 | 0.46394 | 16701.84 | 0 | 0 | 1 | 5000 | 16701.84 | 0 | 0 | 0 | 0 | 0 | 30160.56 | 0 | 0 | 0 | 0 | 0 | 30160.56
2022081502 | 2 | 0.61792 | 49433.6 | 0.44063 | 15862.68 | 0 | 0 | 1 | 5000 | 15862.68 | 0 | 0 | 0 | 0 | 0 | 28570.92 | 0 | 0 | 0 | 0 | 0 | 28570.92
2022081503 | 2 | 0.59955 | 47964 | 0.39754 | 14311.44 | 0 | 0 | 1 | 5000 | 14311.44 | 0 | 0 | 0 | 0 | 0 | 28652.56 | 0 | 0 | 0 | 0 | 0 | 28652.56
2022081504 | 2 | 0.58574 | 46859.2 | 0.35295 | 12706.2 | 0 | 0 | 1 | 5000 | 12706.2 | 0 | 0 | 0 | 0 | 0 | 29153 | 0 | 0 | 0 | 0 | 0 | 29153
2022081505 | 2 | 0.58179 | 46543.2 | 0.32777 | 11799.72 | 0 | 0 | 1 | 5000 | 11799.72 | 0 | 0 | 0 | 0 | 0 | 29743.48 | 0 | 0 | 0 | 0 | 0 | 29743.48
2022081506 | 2 | 0.59255 | 47404 | 0.30517 | 10986.12 | 0 | 0 | 1 | 5000 | 10986.12 | 0 | 0 | 0 | 0 | 0 | 31417.88 | 0 | 0 | 0 | 0 | 0 | 31417.88
2022081507 | 2 | 0.61062 | 48849.6 | 0.30944 | 11139.84 | 0.00012 | 1.44 | 1 | 5000 | 11139.84 | 1.44 | 0 | 0 | 0 | 0 | 32708.32 | 0 | 0 | 0 | 0 | 0 | 32708.32
2022081508 | 2 | 0.62039 | 49631.2 | 0.30233 | 10883.88 | 0.05945 | 713.4 | 1 | 5000 | 10883.88 | 713.4 | 0 | 0 | 0 | 0 | 33033.92 | 0 | 0 | 0 | 0 | 0 | 33033.92
2022081509 | 2 | 0.64611 | 51688.8 | 0.24237 | 8725.32 | 0.40032 | 4803.84 | 1 | 5000 | 8725.32 | 4803.84 | 0 | 0 | 0 | 0 | 33159.64 | 0 | 0 | 0 | 0 | 0 | 33159.64
2022081510 | 2 | 0.68698 | 54958.4 | 0.25765 | 9275.4 | 0.61959 | 7435.08 | 1 | 5000 | 9275.4 | 7435.08 | 0 | 0 | 0 | 0 | 33247.92 | 0 | 0 | 0 | 0 | 0 | 33247.92
2022081511 | 2 | 0.73642 | 58913.6 | 0.26627 | 9585.72 | 0.67154 | 8058.48 | 1 | 5000 | 9585.72 | 8058.48 | 0 | 0 | 0 | 0 | 36269.4 | 0 | 0 | 0 | 0 | 0 | 36269.4
2022081512 | 2 | 0.78626 | 62900.8 | 0.27839 | 10022.04 | 0.69151 | 8298.12 | 1 | 5000 | 10022.04 | 8298.12 | 0 | 0 | 0 | 0 | 39580.64 | 0 | 0 | 0 | 0 | 0 | 39580.64
2022081513 | 2 | 0.83183 | 66546.4 | 0.29064 | 10463.04 | 0.67453 | 8094.36 | 1 | 5000 | 10463.04 | 8094.36 | 0 | 0 | 0 | 0 | 42989 | 0 | 0 | 0 | 0 | 0 | 42989
2022081514 | 2 | 0.87257 | 69805.6 | 0.30991 | 11156.76 | 0.66481 | 7977.72 | 1 | 5000 | 11156.76 | 7977.72 | 0 | 0 | 0 | 0 | 45671.12 | 0 | 0 | 0 | 0 | 0 | 45671.12
2022081515 | 2 | 0.90493 | 72394.4 | 0.33151 | 11934.36 | 0.6655 | 7986 | 1 | 5000 | 11934.36 | 7986 | 0 | 0 | 0 | 0 | 47474.04 | 0 | 0 | 0 | 0 | 0 | 47474.04
2022081516 | 2 | 0.92353 | 73882.4 | 0.34834 | 12540.24 | 0.63612 | 7633.44 | 1 | 5000 | 12540.24 | 7633.44 | 0 | 0 | 0 | 0 | 48708.72 | 0 | 0 | 0 | 0 | 0 | 48708.72
2022081517 | 2 | 0.93111 | 74488.8 | 0.36294 | 13065.84 | 0.5706 | 6847.2 | 1 | 5000 | 13065.84 | 6847.2 | 0 | 0 | 0 | 0 | 49575.76 | 0 | 0 | 0 | 0 | 0 | 49575.76
2022081518 | 2 | 0.92428 | 73942.4 | 0.37903 | 13645.08 | 0.53547 | 6425.64 | 1 | 5000 | 13645.08 | 6425.64 | 0 | 0 | 0 | 0 | 48871.68 | 0 | 0 | 0 | 0 | 0 | 48871.68
2022081519 | 2 | 0.90275 | 72220 | 0.38703 | 13933.08 | 0.41547 | 4985.64 | 1 | 5000 | 13933.08 | 4985.64 | 0 | 0 | 0 | 0 | 48301.28 | 0 | 0 | 0 | 0 | 0 | 48301.28
2022081520 | 2 | 0.86723 | 69378.4 | 0.37479 | 13492.44 | 0.16299 | 1955.88 | 1 | 5000 | 13492.44 | 1955.88 | 0 | 0 | 0 | 0 | 48930.08 | 0 | 0 | 0 | 0 | 0 | 48930.08
2022081521 | 2 | 0.84009 | 67207.2 | 0.34262 | 12334.32 | 0.00901 | 108.12 | 1 | 5000 | 12334.32 | 108.12 | 0 | 0 | 0 | 0 | 49764.76 | 0 | 0 | 0 | 0 | 0 | 49764.76
2022081522 | 2 | 0.80493 | 64394.4 | 0.35314 | 12713.04 | 0 | 0 | 1 | 5000 | 12713.04 | 0 | 0 | 0 | 0 | 0 | 46681.36 | 0 | 0 | 0 | 0 | 0 | 46681.36
2022081523 | 2 | 0.75249 | 60199.2 | 0.36472 | 13129.92 | 0 | 0 | 1 | 5000 | 13129.92 | 0 | 0 | 0 | 0 | 0 | 42069.28 | 0 | 0 | 0 | 0 | 0 | 42069.28
2022081524 | 2 | 0.70033 | 56026.4 | 0.37578 | 13528.08 | 0 | 0 | 1 | 5000 | 13528.08 | 0 | 0 | 0 | 0 | 0 | 37498.32 | 0 | 0 | 0 | 0 | 0 | 37498.32
2022081601 | 3 | 0.65703 | 52562.4 | 0.36422 | 13111.92 | 0 | 0 | 1 | 5000 | 13111.92 | 0 | 0 | 0 | 0 | 0 | 34450.48 | 0 | 0 | 0 | 0 | 0 | 34450.48
2022081602 | 3 | 0.62607 | 50085.6 | 0.3531 | 12711.6 | 0 | 0 | 1 | 5000 | 12711.6 | 0 | 0 | 0 | 0 | 0 | 32374 | 0 | 0 | 0 | 0 | 0 | 32374
2022081603 | 3 | 0.60376 | 48300.8 | 0.3204 | 11534.4 | 0 | 0 | 1 | 5000 | 11534.4 | 0 | 0 | 0 | 0 | 0 | 31766.4 | 0 | 0 | 0 | 0 | 0 | 31766.4
2022081604 | 3 | 0.59307 | 47445.6 | 0.28916 | 10409.76 | 0 | 0 | 1 | 5000 | 10409.76 | 0 | 0 | 0 | 0 | 0 | 32035.84 | 0 | 0 | 0 | 0 | 0 | 32035.84
2022081605 | 3 | 0.58718 | 46974.4 | 0.26462 | 9526.32 | 0 | 0 | 1 | 5000 | 9526.32 | 0 | 0 | 0 | 0 | 0 | 32448.08 | 0 | 0 | 0 | 0 | 0 | 32448.08
2022081606 | 3 | 0.59741 | 47792.8 | 0.22955 | 8263.8 | 0 | 0 | 1 | 5000 | 8263.8 | 0 | 0 | 0 | 0 | 0 | 34529 | 0 | 0 | 0 | 0 | 0 | 34529
2022081607 | 3 | 0.61641 | 49312.8 | 0.19908 | 7166.88 | 7e-05 | 0.84 | 1 | 5000 | 7166.88 | 0.84 | 0 | 0 | 0 | 0 | 37145.08 | 0 | 0 | 0 | 0 | 0 | 37145.08
2022081608 | 3 | 0.62492 | 49993.6 | 0.18205 | 6553.8 | 0.05145 | 617.4 | 1 | 5000 | 6553.8 | 617.4 | 0 | 0 | 0 | 0 | 37822.4 | 0 | 0 | 0 | 0 | 0 | 37822.4
2022081609 | 3 | 0.6531 | 52248 | 0.13572 | 4885.92 | 0.25018 | 3002.16 | 1 | 5000 | 4885.92 | 3002.16 | 0 | 0 | 0 | 0 | 39359.92 | 0 | 0 | 0 | 0 | 0 | 39359.92
2022081610 | 3 | 0.69742 | 55793.6 | 0.1345 | 4842 | 0.39605 | 4752.6 | 1 | 5000 | 4842 | 4752.6 | 0 | 0 | 0 | 0 | 41199 | 0 | 0 | 0 | 0 | 0 | 41199
2022081611 | 3 | 0.7438 | 59504 | 0.14017 | 5046.12 | 0.46025 | 5523 | 1 | 5000 | 5046.12 | 5523 | 0 | 0 | 0 | 0 | 43934.88 | 0 | 0 | 0 | 0 | 0 | 43934.88
2022081612 | 3 | 0.79783 | 63826.4 | 0.13757 | 4952.52 | 0.52792 | 6335.04 | 1 | 5000 | 4952.52 | 6335.04 | 0 | 0 | 0 | 0 | 47538.84 | 0 | 0 | 0 | 0 | 0 | 47538.84
2022081613 | 3 | 0.84727 | 67781.6 | 0.14022 | 5047.92 | 0.55177 | 6621.24 | 1 | 5000 | 5047.92 | 6621.24 | 0 | 0 | 0 | 0 | 51112.44 | 0 | 0 | 0 | 0 | 0 | 51112.44
2022081614 | 3 | 0.89115 | 71292 | 0.16086 | 5790.96 | 0.58551 | 7026.12 | 1 | 5000 | 5790.96 | 7026.12 | 0 | 0 | 0 | 0 | 53474.92 | 0 | 0 | 0 | 0 | 0 | 53474.92
2022081615 | 3 | 0.92176 | 73740.8 | 0.1829 | 6584.4 | 0.54273 | 6512.76 | 1 | 5000 | 6584.4 | 6512.76 | 0 | 0 | 0 | 0 | 55643.64 | 0 | 0 | 0 | 0 | 0 | 55643.64
2022081616 | 3 | 0.93966 | 75172.8 | 0.20118 | 7242.48 | 0.48148 | 5777.76 | 1 | 5000 | 7242.48 | 5777.76 | 0 | 0 | 0 | 0 | 57152.56 | 0 | 0 | 0 | 0 | 0 | 57152.56
2022081617 | 3 | 0.94538 | 75630.4 | 0.21569 | 7764.84 | 0.41593 | 4991.16 | 1 | 5000 | 7764.84 | 4991.16 | 0 | 0 | 0 | 0 | 57874.4 | 0 | 0 | 0 | 0 | 0 | 57874.4
2022081618 | 3 | 0.94661 | 75728.8 | 0.22294 | 8025.84 | 0.40819 | 4898.28 | 1 | 5000 | 8025.84 | 4898.28 | 0 | 0 | 0 | 0 | 57804.68 | 0 | 0 | 0 | 0 | 0 | 57804.68
2022081619 | 3 | 0.92856 | 74284.8 | 0.23066 | 8303.76 | 0.29657 | 3558.84 | 1 | 5000 | 8303.76 | 3558.84 | 0 | 0 | 0 | 0 | 57422.2 | 0 | 0 | 0 | 0 | 0 | 57422.2
2022081620 | 3 | 0.89425 | 71540 | 0.22442 | 8079.12 | 0.07816 | 937.92 | 1 | 5000 | 8079.12 | 937.92 | 0 | 0 | 0 | 0 | 57522.96 | 0 | 0 | 0 | 0 | 0 | 57522.96
2022081621 | 3 | 0.86259 | 69007.2 | 0.20529 | 7390.44 | 0.00193 | 23.16 | 1 | 5000 | 7390.44 | 23.16 | 0 | 0 | 0 | 0 | 56593.6 | 0 | 0 | 0 | 0 | 0 | 56593.6
2022081622 | 3 | 0.82523 | 66018.4 | 0.21414 | 7709.04 | 0 | 0 | 1 | 5000 | 7709.04 | 0 | 0 | 0 | 0 | 0 | 53309.36 | 0 | 0 | 0 | 0 | 0 | 53309.36
2022081623 | 3 | 0.77338 | 61870.4 | 0.22703 | 8173.08 | 0 | 0 | 1 | 5000 | 8173.08 | 0 | 0 | 0 | 0 | 0 | 48697.32 | 0 | 0 | 0 | 0 | 0 | 48697.32
2022081624 | 3 | 0.71849 | 57479.2 | 0.22744 | 8187.84 | 0 | 0 | 1 | 5000 | 8187.84 | 0 | 0 | 0 | 0 | 0 | 44291.36 | 0 | 0 | 0 | 0 | 0 | 44291.36
2022081701 | 4 | 0.67386 | 53908.8 | 0.23419 | 8430.84 | 0 | 0 | 1 | 5000 | 8430.84 | 0 | 0 | 0 | 0 | 0 | 40477.96 | 0 | 0 | 0 | 0 | 0 | 40477.96
2022081702 | 4 | 0.64018 | 51214.4 | 0.24602 | 8856.72 | 0 | 0 | 1 | 5000 | 8856.72 | 0 | 0 | 0 | 0 | 0 | 37357.68 | 0 | 0 | 0 | 0 | 0 | 37357.68
2022081703 | 4 | 0.6173 | 49384 | 0.27543 | 9915.48 | 0 | 0 | 1 | 5000 | 9915.48 | 0 | 0 | 0 | 0 | 0 | 34468.52 | 0 | 0 | 0 | 0 | 0 | 34468.52
2022081704 | 4 | 0.60385 | 48308 | 0.27057 | 9740.52 | 0 | 0 | 1 | 5000 | 9740.52 | 0 | 0 | 0 | 0 | 0 | 33567.48 | 0 | 0 | 0 | 0 | 0 | 33567.48
2022081705 | 4 | 0.59887 | 47909.6 | 0.2556 | 9201.6 | 0 | 0 | 1 | 5000 | 9201.6 | 0 | 0 | 0 | 0 | 0 | 33708 | 0 | 0 | 0 | 0 | 0 | 33708
2022081706 | 4 | 0.60795 | 48636 | 0.25257 | 9092.52 | 0 | 0 | 1 | 5000 | 9092.52 | 0 | 0 | 0 | 0 | 0 | 34543.48 | 0 | 0 | 0 | 0 | 0 | 34543.48
2022081707 | 4 | 0.62949 | 50359.2 | 0.23554 | 8479.44 | 0 | 0 | 1 | 5000 | 8479.44 | 0 | 0 | 0 | 0 | 0 | 36879.76 | 0 | 0 | 0 | 0 | 0 | 36879.76
2022081708 | 4 | 0.63492 | 50793.6 | 0.20993 | 7557.48 | 0.05315 | 637.8 | 1 | 5000 | 7557.48 | 637.8 | 0 | 0 | 0 | 0 | 37598.32 | 0 | 0 | 0 | 0 | 0 | 37598.32
2022081709 | 4 | 0.6607 | 52856 | 0.13334 | 4800.24 | 0.34134 | 4096.08 | 1 | 5000 | 4800.24 | 4096.08 | 0 | 0 | 0 | 0 | 38959.68 | 0 | 0 | 0 | 0 | 0 | 38959.68
2022081710 | 4 | 0.70631 | 56504.8 | 0.098 | 3528 | 0.54594 | 6551.28 | 1 | 5000 | 3528 | 6551.28 | 0 | 0 | 0 | 0 | 41425.52 | 0 | 0 | 0 | 0 | 0 | 41425.52
2022081711 | 4 | 0.76246 | 60996.8 | 0.08501 | 3060.36 | 0.67572 | 8108.64 | 1 | 5000 | 3060.36 | 8108.64 | 0 | 0 | 0 | 0 | 44827.8 | 0 | 0 | 0 | 0 | 0 | 44827.8
2022081712 | 4 | 0.81817 | 65453.6 | 0.0713 | 2566.8 | 0.69859 | 8383.08 | 1 | 5000 | 2566.8 | 8383.08 | 0 | 0 | 0 | 0 | 49503.72 | 0 | 0 | 0 | 0 | 0 | 49503.72
2022081713 | 4 | 0.86921 | 69536.8 | 0.06473 | 2330.28 | 0.68917 | 8270.04 | 1 | 5000 | 2330.28 | 8270.04 | 0 | 0 | 0 | 0 | 53936.48 | 0 | 0 | 0 | 0 | 0 | 53936.48
2022081714 | 4 | 0.91354 | 73083.2 | 0.07991 | 2876.76 | 0.67712 | 8125.44 | 1 | 5000 | 2876.76 | 8125.44 | 0 | 0 | 0 | 0 | 57081 | 0 | 0 | 0 | 0 | 0 | 57081
2022081715 | 4 | 0.9479 | 75832 | 0.10639 | 3830.04 | 0.63689 | 7642.68 | 1 | 5000 | 3830.04 | 7642.68 | 0 | 0 | 0 | 0 | 59359.28 | 0 | 0 | 0 | 0 | 0 | 59359.28
2022081716 | 4 | 0.96115 | 76892 | 0.1235 | 4446 | 0.59167 | 7100.04 | 1 | 5000 | 4446 | 7100.04 | 0 | 0 | 0 | 0 | 60345.96 | 0 | 0 | 0 | 0 | 0 | 60345.96
2022081717 | 4 | 0.97228 | 77782.4 | 0.15603 | 5617.08 | 0.5738 | 6885.6 | 1 | 5000 | 5617.08 | 6885.6 | 0 | 0 | 0 | 0 | 60279.72 | 0 | 0 | 0 | 0 | 0 | 60279.72
2022081718 | 4 | 0.97166 | 77732.8 | 0.19855 | 7147.8 | 0.55332 | 6639.84 | 1 | 5000 | 7147.8 | 6639.84 | 0 | 0 | 0 | 0 | 58945.16 | 0 | 0 | 0 | 0 | 0 | 58945.16
2022081719 | 4 | 0.95114 | 76091.2 | 0.25486 | 9174.96 | 0.37251 | 4470.12 | 1 | 5000 | 9174.96 | 4470.12 | 0 | 0 | 0 | 0 | 57446.12 | 0 | 0 | 0 | 0 | 0 | 57446.12
2022081720 | 4 | 0.91618 | 73294.4 | 0.30744 | 11067.84 | 0.11387 | 1366.44 | 1 | 5000 | 11067.84 | 1366.44 | 0 | 0 | 0 | 0 | 55860.12 | 0 | 0 | 0 | 0 | 0 | 55860.12
2022081721 | 4 | 0.88523 | 70818.4 | 0.33337 | 12001.32 | 0.00209 | 25.08 | 1 | 5000 | 12001.32 | 25.08 | 0 | 0 | 0 | 0 | 53792 | 0 | 0 | 0 | 0 | 0 | 53792
2022081722 | 4 | 0.84015 | 67212 | 0.34357 | 12368.52 | 0 | 0 | 1 | 5000 | 12368.52 | 0 | 0 | 0 | 0 | 0 | 49843.48 | 0 | 0 | 0 | 0 | 0 | 49843.48
2022081723 | 4 | 0.7738 | 61904 | 0.3276 | 11793.6 | 0 | 0 | 1 | 5000 | 11793.6 | 0 | 0 | 0 | 0 | 0 | 45110.4 | 0 | 0 | 0 | 0 | 0 | 45110.4
2022081724 | 4 | 0.71409 | 57127.2 | 0.31787 | 11443.32 | 0 | 0 | 1 | 5000 | 11443.32 | 0 | 0 | 0 | 0 | 0 | 40683.88 | 0 | 0 | 0 | 0 | 0 | 40683.88
2022081801 | 5 | 0.6665 | 53320 | 0.28877 | 10395.72 | 0 | 0 | 1 | 5000 | 10395.72 | 0 | 0 | 0 | 0 | 0 | 37924.28 | 0 | 0 | 0 | 0 | 0 | 37924.28
2022081802 | 5 | 0.63168 | 50534.4 | 0.22875 | 8235 | 0 | 0 | 1 | 5000 | 8235 | 0 | 0 | 0 | 0 | 0 | 37299.4 | 0 | 0 | 0 | 0 | 0 | 37299.4
2022081803 | 5 | 0.60655 | 48524 | 0.16194 | 5829.84 | 0 | 0 | 1 | 5000 | 5829.84 | 0 | 0 | 0 | 0 | 0 | 37694.16 | 0 | 0 | 0 | 0 | 0 | 37694.16
2022081804 | 5 | 0.58878 | 47102.4 | 0.11952 | 4302.72 | 0 | 0 | 1 | 5000 | 4302.72 | 0 | 0 | 0 | 0 | 0 | 37799.68 | 0 | 0 | 0 | 0 | 0 | 37799.68
2022081805 | 5 | 0.58409 | 46727.2 | 0.09958 | 3584.88 | 0 | 0 | 1 | 5000 | 3584.88 | 0 | 0 | 0 | 0 | 0 | 38142.32 | 0 | 0 | 0 | 0 | 0 | 38142.32
2022081806 | 5 | 0.5942 | 47536 | 0.10111 | 3639.96 | 0 | 0 | 1 | 5000 | 3639.96 | 0 | 0 | 0 | 0 | 0 | 38896.04 | 0 | 0 | 0 | 0 | 0 | 38896.04
2022081807 | 5 | 0.61932 | 49545.6 | 0.09955 | 3583.8 | 0 | 0 | 1 | 5000 | 3583.8 | 0 | 0 | 0 | 0 | 0 | 40961.8 | 0 | 0 | 0 | 0 | 0 | 40961.8
2022081808 | 5 | 0.62246 | 49796.8 | 0.12893 | 4641.48 | 0.02756 | 330.72 | 1 | 5000 | 4641.48 | 330.72 | 0 | 0 | 0 | 0 | 39824.6 | 0 | 0 | 0 | 0 | 0 | 39824.6
2022081809 | 5 | 0.64228 | 51382.4 | 0.15821 | 5695.56 | 0.2086 | 2503.2 | 1 | 5000 | 5695.56 | 2503.2 | 0 | 0 | 0 | 0 | 38183.64 | 0 | 0 | 0 | 0 | 0 | 38183.64
2022081810 | 5 | 0.67858 | 54286.4 | 0.16495 | 5938.2 | 0.38716 | 4645.92 | 1 | 5000 | 5938.2 | 4645.92 | 0 | 0 | 0 | 0 | 38702.28 | 0 | 0 | 0 | 0 | 0 | 38702.28
2022081811 | 5 | 0.71926 | 57540.8 | 0.13951 | 5022.36 | 0.50833 | 6099.96 | 1 | 5000 | 5022.36 | 6099.96 | 0 | 0 | 0 | 0 | 41418.48 | 0 | 0 | 0 | 0 | 0 | 41418.48
2022081812 | 5 | 0.75964 | 60771.2 | 0.1071 | 3855.6 | 0.58604 | 7032.48 | 1 | 5000 | 3855.6 | 7032.48 | 0 | 0 | 0 | 0 | 44883.12 | 0 | 0 | 0 | 0 | 0 | 44883.12
2022081813 | 5 | 0.79494 | 63595.2 | 0.07575 | 2727 | 0.63918 | 7670.16 | 1 | 5000 | 2727 | 7670.16 | 0 | 0 | 0 | 0 | 48198.04 | 0 | 0 | 0 | 0 | 0 | 48198.04
2022081814 | 5 | 0.81988 | 65590.4 | 0.07231 | 2603.16 | 0.58409 | 7009.08 | 1 | 5000 | 2603.16 | 7009.08 | 0 | 0 | 0 | 0 | 50978.16 | 0 | 0 | 0 | 0 | 0 | 50978.16
2022081815 | 5 | 0.83369 | 66695.2 | 0.09535 | 3432.6 | 0.55321 | 6638.52 | 1 | 5000 | 3432.6 | 6638.52 | 0 | 0 | 0 | 0 | 51624.08 | 0 | 0 | 0 | 0 | 0 | 51624.08
2022081816 | 5 | 0.84029 | 67223.2 | 0.11342 | 4083.12 | 0.56693 | 6803.16 | 1 | 5000 | 4083.12 | 6803.16 | 0 | 0 | 0 | 0 | 51336.92 | 0 | 0 | 0 | 0 | 0 | 51336.92
2022081817 | 5 | 0.8335 | 66680 | 0.14002 | 5040.72 | 0.55472 | 6656.64 | 1 | 5000 | 5040.72 | 6656.64 | 0 | 0 | 0 | 0 | 49982.64 | 0 | 0 | 0 | 0 | 0 | 49982.64
2022081818 | 5 | 0.80241 | 64192.8 | 0.18722 | 6739.92 | 0.49957 | 5994.84 | 1 | 5000 | 6739.92 | 5994.84 | 0 | 0 | 0 | 0 | 46458.04 | 0 | 0 | 0 | 0 | 0 | 46458.04
2022081819 | 5 | 0.77345 | 61876 | 0.2297 | 8269.2 | 0.36562 | 4387.44 | 1 | 5000 | 8269.2 | 4387.44 | 0 | 0 | 0 | 0 | 44219.36 | 0 | 0 | 0 | 0 | 0 | 44219.36
2022081820 | 5 | 0.75072 | 60057.6 | 0.24492 | 8817.12 | 0.13987 | 1678.44 | 1 | 5000 | 8817.12 | 1678.44 | 0 | 0 | 0 | 0 | 44562.04 | 0 | 0 | 0 | 0 | 0 | 44562.04
2022081821 | 5 | 0.73399 | 58719.2 | 0.21555 | 7759.8 | 0.00448 | 53.76 | 1 | 5000 | 7759.8 | 53.76 | 0 | 0 | 0 | 0 | 45905.64 | 0 | 0 | 0 | 0 | 0 | 45905.64
2022081822 | 5 | 0.70907 | 56725.6 | 0.17351 | 6246.36 | 0 | 0 | 1 | 5000 | 6246.36 | 0 | 0 | 0 | 0 | 0 | 45479.24 | 0 | 0 | 0 | 0 | 0 | 45479.24
2022081823 | 5 | 0.67002 | 53601.6 | 0.16106 | 5798.16 | 0 | 0 | 1 | 5000 | 5798.16 | 0 | 0 | 0 | 0 | 0 | 42803.44 | 0 | 0 | 0 | 0 | 0 | 42803.44
2022081824 | 5 | 0.62438 | 49950.4 | 0.1656 | 5961.6 | 0 | 0 | 1 | 5000 | 5961.6 | 0 | 0 | 0 | 0 | 0 | 38988.8 | 0 | 0 | 0 | 0 | 0 | 38988.8
2022081901 | 6 | 0.58777 | 47021.6 | 0.17162 | 6178.32 | 0 | 0 | 1 | 5000 | 6178.32 | 0 | 0 | 0 | 0 | 0 | 35843.28 | 0 | 0 | 0 | 0 | 0 | 35843.28
2022081902 | 6 | 0.56278 | 45022.4 | 0.16459 | 5925.24 | 0 | 0 | 1 | 5000 | 5925.24 | 0 | 0 | 0 | 0 | 0 | 34097.16 | 0 | 0 | 0 | 0 | 0 | 34097.16
2022081903 | 6 | 0.54668 | 43734.4 | 0.15485 | 5574.6 | 0 | 0 | 1 | 5000 | 5574.6 | 0 | 0 | 0 | 0 | 0 | 33159.8 | 0 | 0 | 0 | 0 | 0 | 33159.8
2022081904 | 6 | 0.53978 | 43182.4 | 0.13298 | 4787.28 | 0 | 0 | 1 | 5000 | 4787.28 | 0 | 0 | 0 | 0 | 0 | 33395.12 | 0 | 0 | 0 | 0 | 0 | 33395.12
2022081905 | 6 | 0.53865 | 43092 | 0.1014 | 3650.4 | 0 | 0 | 1 | 5000 | 3650.4 | 0 | 0 | 0 | 0 | 0 | 34441.6 | 0 | 0 | 0 | 0 | 0 | 34441.6
2022081906 | 6 | 0.55244 | 44195.2 | 0.08273 | 2978.28 | 0 | 0 | 1 | 5000 | 2978.28 | 0 | 0 | 0 | 0 | 0 | 36216.92 | 0 | 0 | 0 | 0 | 0 | 36216.92
2022081907 | 6 | 0.58087 | 46469.6 | 0.08293 | 2985.48 | 0 | 0 | 1 | 5000 | 2985.48 | 0 | 0 | 0 | 0 | 0 | 38484.12 | 0 | 0 | 0 | 0 | 0 | 38484.12
2022081908 | 6 | 0.59006 | 47204.8 | 0.08111 | 2919.96 | 0.02556 | 306.72 | 1 | 5000 | 2919.96 | 306.72 | 0 | 0 | 0 | 0 | 38978.12 | 0 | 0 | 0 | 0 | 0 | 38978.12
2022081909 | 6 | 0.60578 | 48462.4 | 0.0619 | 2228.4 | 0.26207 | 3144.84 | 1 | 5000 | 2228.4 | 3144.84 | 0 | 0 | 0 | 0 | 38089.16 | 0 | 0 | 0 | 0 | 0 | 38089.16
2022081910 | 6 | 0.63088 | 50470.4 | 0.07379 | 2656.44 | 0.43607 | 5232.84 | 1 | 5000 | 2656.44 | 5232.84 | 0 | 0 | 0 | 0 | 37581.12 | 0 | 0 | 0 | 0 | 0 | 37581.12
2022081911 | 6 | 0.66514 | 53211.2 | 0.07163 | 2578.68 | 0.48107 | 5772.84 | 1 | 5000 | 2578.68 | 5772.84 | 0 | 0 | 0 | 0 | 39859.68 | 0 | 0 | 0 | 0 | 0 | 39859.68
2022081912 | 6 | 0.70226 | 56180.8 | 0.06024 | 2168.64 | 0.58994 | 7079.28 | 1 | 5000 | 2168.64 | 7079.28 | 0 | 0 | 0 | 0 | 41932.88 | 0 | 0 | 0 | 0 | 0 | 41932.88
2022081913 | 6 | 0.73786 | 59028.8 | 0.04996 | 1798.56 | 0.6144 | 7372.8 | 1 | 5000 | 1798.56 | 7372.8 | 0 | 0 | 0 | 0 | 44857.44 | 0 | 0 | 0 | 0 | 0 | 44857.44
2022081914 | 6 | 0.76852 | 61481.6 | 0.06521 | 2347.56 | 0.58742 | 7049.04 | 1 | 5000 | 2347.56 | 7049.04 | 0 | 0 | 0 | 0 | 47085 | 0 | 0 | 0 | 0 | 0 | 47085
2022081915 | 6 | 0.78548 | 62838.4 | 0.1012 | 3643.2 | 0.53682 | 6441.84 | 1 | 5000 | 3643.2 | 6441.84 | 0 | 0 | 0 | 0 | 47753.36 | 0 | 0 | 0 | 0 | 0 | 47753.36
2022081916 | 6 | 0.79116 | 63292.8 | 0.15536 | 5592.96 | 0.47319 | 5678.28 | 1 | 5000 | 5592.96 | 5678.28 | 0 | 0 | 0 | 0 | 47021.56 | 0 | 0 | 0 | 0 | 0 | 47021.56
2022081917 | 6 | 0.79387 | 63509.6 | 0.20787 | 7483.32 | 0.40302 | 4836.24 | 1 | 5000 | 7483.32 | 4836.24 | 0 | 0 | 0 | 0 | 46190.04 | 0 | 0 | 0 | 0 | 0 | 46190.04
2022081918 | 6 | 0.78667 | 62933.6 | 0.24772 | 8917.92 | 0.35999 | 4319.88 | 1 | 5000 | 8917.92 | 4319.88 | 0 | 0 | 0 | 0 | 44695.8 | 0 | 0 | 0 | 0 | 0 | 44695.8
2022081919 | 6 | 0.76899 | 61519.2 | 0.27384 | 9858.24 | 0.26057 | 3126.84 | 1 | 5000 | 9858.24 | 3126.84 | 0 | 0 | 0 | 0 | 43534.12 | 0 | 0 | 0 | 0 | 0 | 43534.12
2022081920 | 6 | 0.74586 | 59668.8 | 0.28186 | 10146.96 | 0.07087 | 850.44 | 1 | 5000 | 10146.96 | 850.44 | 0 | 0 | 0 | 0 | 43671.4 | 0 | 0 | 0 | 0 | 0 | 43671.4
2022081921 | 6 | 0.72824 | 58259.2 | 0.3161 | 11379.6 | 0.00042 | 5.04 | 1 | 5000 | 11379.6 | 5.04 | 0 | 0 | 0 | 0 | 41874.56 | 0 | 0 | 0 | 0 | 0 | 41874.56
2022081922 | 6 | 0.70493 | 56394.4 | 0.33709 | 12135.24 | 0 | 0 | 1 | 5000 | 12135.24 | 0 | 0 | 0 | 0 | 0 | 39259.16 | 0 | 0 | 0 | 0 | 0 | 39259.16
2022081923 | 6 | 0.67344 | 53875.2 | 0.35513 | 12784.68 | 0 | 0 | 1 | 5000 | 12784.68 | 0 | 0 | 0 | 0 | 0 | 36090.52 | 0 | 0 | 0 | 0 | 0 | 36090.52
2022081924 | 6 | 0.63608 | 50886.4 | 0.36008 | 12962.88 | 0 | 0 | 1 | 5000 | 12962.88 | 0 | 0 | 0 | 0 | 0 | 32923.52 | 0 | 0 | 0 | 0 | 0 | 32923.52
2022082001 | 7 | 0.60144 | 48115.2 | 0.3294 | 11858.4 | 0 | 0 | 1 | 5000 | 11858.4 | 0 | 0 | 0 | 0 | 0 | 31256.8 | 0 | 0 | 0 | 0 | 0 | 31256.8
2022082002 | 7 | 0.57681 | 46144.8 | 0.28241 | 10166.76 | 0 | 0 | 1 | 5000 | 10166.76 | 0 | 0 | 0 | 0 | 0 | 30978.04 | 0 | 0 | 0 | 0 | 0 | 30978.04
2022082003 | 7 | 0.55718 | 44574.4 | 0.27135 | 9768.6 | 0 | 0 | 1 | 5000 | 9768.6 | 0 | 0 | 0 | 0 | 0 | 29805.8 | 0 | 0 | 0 | 0 | 0 | 29805.8
2022082004 | 7 | 0.54543 | 43634.4 | 0.27328 | 9838.08 | 0 | 0 | 1 | 5000 | 9838.08 | 0 | 0 | 0 | 0 | 0 | 28796.32 | 0 | 0 | 0 | 0 | 0 | 28796.32
2022082005 | 7 | 0.53719 | 42975.2 | 0.26581 | 9569.16 | 0 | 0 | 1 | 5000 | 9569.16 | 0 | 0 | 0 | 0 | 0 | 28406.04 | 0 | 0 | 0 | 0 | 0 | 28406.04
2022082006 | 7 | 0.5377 | 43016 | 0.26637 | 9589.32 | 0 | 0 | 1 | 5000 | 9589.32 | 0 | 0 | 0 | 0 | 0 | 28426.68 | 0 | 0 | 0 | 0 | 0 | 28426.68
2022082007 | 7 | 0.54537 | 43629.6 | 0.26303 | 9469.08 | 0 | 0 | 1 | 5000 | 9469.08 | 0 | 0 | 0 | 0 | 0 | 29160.52 | 0 | 0 | 0 | 0 | 0 | 29160.52
2022082008 | 7 | 0.55437 | 44349.6 | 0.24034 | 8652.24 | 0.03291 | 394.92 | 1 | 5000 | 8652.24 | 394.92 | 0 | 0 | 0 | 0 | 30302.44 | 0 | 0 | 0 | 0 | 0 | 30302.44
2022082009 | 7 | 0.58534 | 46827.2 | 0.20411 | 7347.96 | 0.20469 | 2456.28 | 1 | 5000 | 7347.96 | 2456.28 | 0 | 0 | 0 | 0 | 32022.96 | 0 | 0 | 0 | 0 | 0 | 32022.96
2022082010 | 7 | 0.63039 | 50431.2 | 0.2285 | 8226 | 0.37583 | 4509.96 | 1 | 5000 | 8226 | 4509.96 | 0 | 0 | 0 | 0 | 32695.24 | 0 | 0 | 0 | 0 | 0 | 32695.24
2022082011 | 7 | 0.68188 | 54550.4 | 0.23871 | 8593.56 | 0.4197 | 5036.4 | 1 | 5000 | 8593.56 | 5036.4 | 0 | 0 | 0 | 0 | 35920.44 | 0 | 0 | 0 | 0 | 0 | 35920.44
2022082012 | 7 | 0.72848 | 58278.4 | 0.22286 | 8022.96 | 0.47839 | 5740.68 | 1 | 5000 | 8022.96 | 5740.68 | 0 | 0 | 0 | 0 | 39514.76 | 0 | 0 | 0 | 0 | 0 | 39514.76
2022082013 | 7 | 0.76317 | 61053.6 | 0.22561 | 8121.96 | 0.49641 | 5956.92 | 1 | 5000 | 8121.96 | 5956.92 | 0 | 0 | 0 | 0 | 41974.72 | 0 | 0 | 0 | 0 | 0 | 41974.72
2022082014 | 7 | 0.79057 | 63245.6 | 0.23548 | 8477.28 | 0.47203 | 5664.36 | 1 | 5000 | 8477.28 | 5664.36 | 0 | 0 | 0 | 0 | 44103.96 | 0 | 0 | 0 | 0 | 0 | 44103.96
2022082015 | 7 | 0.80611 | 64488.8 | 0.27715 | 9977.4 | 0.48902 | 5868.24 | 1 | 5000 | 9977.4 | 5868.24 | 0 | 0 | 0 | 0 | 43643.16 | 0 | 0 | 0 | 0 | 0 | 43643.16
2022082016 | 7 | 0.81234 | 64987.2 | 0.35682 | 12845.52 | 0.50983 | 6117.96 | 1 | 5000 | 12845.52 | 6117.96 | 0 | 0 | 0 | 0 | 41023.72 | 0 | 0 | 0 | 0 | 0 | 41023.72
2022082017 | 7 | 0.82138 | 65710.4 | 0.39348 | 14165.28 | 0.46587 | 5590.44 | 1 | 5000 | 14165.28 | 5590.44 | 0 | 0 | 0 | 0 | 40954.68 | 0 | 0 | 0 | 0 | 0 | 40954.68
2022082018 | 7 | 0.82071 | 65656.8 | 0.3781 | 13611.6 | 0.36807 | 4416.84 | 1 | 5000 | 13611.6 | 4416.84 | 0 | 0 | 0 | 0 | 42628.36 | 0 | 0 | 0 | 0 | 0 | 42628.36
2022082019 | 7 | 0.79847 | 63877.6 | 0.3779 | 13604.4 | 0.21209 | 2545.08 | 1 | 5000 | 13604.4 | 2545.08 | 0 | 0 | 0 | 0 | 42728.12 | 0 | 0 | 0 | 0 | 0 | 42728.12
2022082020 | 7 | 0.77139 | 61711.2 | 0.35509 | 12783.24 | 0.03766 | 451.92 | 1 | 5000 | 12783.24 | 451.92 | 0 | 0 | 0 | 0 | 43476.04 | 0 | 0 | 0 | 0 | 0 | 43476.04
2022082021 | 7 | 0.75279 | 60223.2 | 0.33666 | 12119.76 | 0.0003 | 3.6 | 1 | 5000 | 12119.76 | 3.6 | 0 | 0 | 0 | 0 | 43099.84 | 0 | 0 | 0 | 0 | 0 | 43099.84
2022082022 | 7 | 0.72587 | 58069.6 | 0.33723 | 12140.28 | 0 | 0 | 1 | 5000 | 12140.28 | 0 | 0 | 0 | 0 | 0 | 40929.32 | 0 | 0 | 0 | 0 | 0 | 40929.32
2022082023 | 7 | 0.68885 | 55108 | 0.3533 | 12718.8 | 0 | 0 | 1 | 5000 | 12718.8 | 0 | 0 | 0 | 0 | 0 | 37389.2 | 0 | 0 | 0 | 0 | 0 | 37389.2
2022082024 | 7 | 0.653 | 52240 | 0.30886 | 11118.96 | 0 | 0 | 1 | 5000 | 11118.96 | 0 | 0 | 0 | 0 | 0 | 36121.04 | 0 | 0 | 0 | 0 | 0 | 36121.04
2022082101 | 1 | 0.619 | 49520 | 0.25635 | 9228.6 | 0 | 0 | 1 | 5000 | 9228.6 | 0 | 0 | 0 | 0 | 0 | 35291.4 | 0 | 0 | 0 | 0 | 0 | 35291.4
2022082102 | 1 | 0.59137 | 47309.6 | 0.23173 | 8342.28 | 0 | 0 | 1 | 5000 | 8342.28 | 0 | 0 | 0 | 0 | 0 | 33967.32 | 0 | 0 | 0 | 0 | 0 | 33967.32
2022082103 | 1 | 0.57242 | 45793.6 | 0.24113 | 8680.68 | 0 | 0 | 1 | 5000 | 8680.68 | 0 | 0 | 0 | 0 | 0 | 32112.92 | 0 | 0 | 0 | 0 | 0 | 32112.92
2022082104 | 1 | 0.55927 | 44741.6 | 0.25155 | 9055.8 | 0 | 0 | 1 | 5000 | 9055.8 | 0 | 0 | 0 | 0 | 0 | 30685.8 | 0 | 0 | 0 | 0 | 0 | 30685.8
2022082105 | 1 | 0.55168 | 44134.4 | 0.25032 | 9011.52 | 0 | 0 | 1 | 5000 | 9011.52 | 0 | 0 | 0 | 0 | 0 | 30122.88 | 0 | 0 | 0 | 0 | 0 | 30122.88
2022082106 | 1 | 0.54899 | 43919.2 | 0.24117 | 8682.12 | 0 | 0 | 1 | 5000 | 8682.12 | 0 | 0 | 0 | 0 | 0 | 30237.08 | 0 | 0 | 0 | 0 | 0 | 30237.08
2022082107 | 1 | 0.54635 | 43708 | 0.22566 | 8123.76 | 0 | 0 | 1 | 5000 | 8123.76 | 0 | 0 | 0 | 0 | 0 | 30584.24 | 0 | 0 | 0 | 0 | 0 | 30584.24
2022082108 | 1 | 0.54947 | 43957.6 | 0.21035 | 7572.6 | 0.01623 | 194.76 | 1 | 5000 | 7572.6 | 194.76 | 0 | 0 | 0 | 0 | 31190.24 | 0 | 0 | 0 | 0 | 0 | 31190.24
2022082109 | 1 | 0.57587 | 46069.6 | 0.19777 | 7119.72 | 0.13044 | 1565.28 | 1 | 5000 | 7119.72 | 1565.28 | 0 | 0 | 0 | 0 | 32384.6 | 0 | 0 | 0 | 0 | 0 | 32384.6
2022082110 | 1 | 0.6179 | 49432 | 0.19464 | 7007.04 | 0.28029 | 3363.48 | 1 | 5000 | 7007.04 | 3363.48 | 0 | 0 | 0 | 0 | 34061.48 | 0 | 0 | 0 | 0 | 0 | 34061.48
2022082111 | 1 | 0.65608 | 52486.4 | 0.18603 | 6697.08 | 0.34962 | 4195.44 | 1 | 5000 | 6697.08 | 4195.44 | 0 | 0 | 0 | 0 | 36593.88 | 0 | 0 | 0 | 0 | 0 | 36593.88
2022082112 | 1 | 0.68581 | 54864.8 | 0.18852 | 6786.72 | 0.42133 | 5055.96 | 1 | 5000 | 6786.72 | 5055.96 | 0 | 0 | 0 | 0 | 38022.12 | 0 | 0 | 0 | 0 | 0 | 38022.12
2022082113 | 1 | 0.71225 | 56980 | 0.19089 | 6872.04 | 0.49254 | 5910.48 | 1 | 5000 | 6872.04 | 5910.48 | 0 | 0 | 0 | 0 | 39197.48 | 0 | 0 | 0 | 0 | 0 | 39197.48
2022082114 | 1 | 0.74085 | 59268 | 0.18628 | 6706.08 | 0.52557 | 6306.84 | 1 | 5000 | 6706.08 | 6306.84 | 0 | 0 | 0 | 0 | 41255.08 | 0 | 0 | 0 | 0 | 0 | 41255.08
2022082115 | 1 | 0.76704 | 61363.2 | 0.17989 | 6476.04 | 0.55868 | 6704.16 | 1 | 5000 | 6476.04 | 6704.16 | 0 | 0 | 0 | 0 | 43183 | 0 | 0 | 0 | 0 | 0 | 43183
2022082116 | 1 | 0.779 | 62320 | 0.19306 | 6950.16 | 0.51276 | 6153.12 | 1 | 5000 | 6950.16 | 6153.12 | 0 | 0 | 0 | 0 | 44216.72 | 0 | 0 | 0 | 0 | 0 | 44216.72
2022082117 | 1 | 0.78263 | 62610.4 | 0.20297 | 7306.92 | 0.44471 | 5336.52 | 1 | 5000 | 7306.92 | 5336.52 | 0 | 0 | 0 | 0 | 44966.96 | 0 | 0 | 0 | 0 | 0 | 44966.96
2022082118 | 1 | 0.78425 | 62740 | 0.21897 | 7882.92 | 0.38724 | 4646.88 | 1 | 5000 | 7882.92 | 4646.88 | 0 | 0 | 0 | 0 | 45210.2 | 0 | 0 | 0 | 0 | 0 | 45210.2
2022082119 | 1 | 0.77452 | 61961.6 | 0.24184 | 8706.24 | 0.30472 | 3656.64 | 1 | 5000 | 8706.24 | 3656.64 | 0 | 0 | 0 | 0 | 44598.72 | 0 | 0 | 0 | 0 | 0 | 44598.72
2022082120 | 1 | 0.75789 | 60631.2 | 0.25237 | 9085.32 | 0.1048 | 1257.6 | 1 | 5000 | 9085.32 | 1257.6 | 0 | 0 | 0 | 0 | 45288.28 | 0 | 0 | 0 | 0 | 0 | 45288.28
2022082121 | 1 | 0.74816 | 59852.8 | 0.25081 | 9029.16 | 0.00182 | 21.84 | 1 | 5000 | 9029.16 | 21.84 | 0 | 0 | 0 | 0 | 45801.8 | 0 | 0 | 0 | 0 | 0 | 45801.8
2022082122 | 1 | 0.72377 | 57901.6 | 0.23155 | 8335.8 | 0 | 0 | 1 | 5000 | 8335.8 | 0 | 0 | 0 | 0 | 0 | 44565.8 | 0 | 0 | 0 | 0 | 0 | 44565.8
2022082123 | 1 | 0.68339 | 54671.2 | 0.21075 | 7587 | 0 | 0 | 1 | 5000 | 7587 | 0 | 0 | 0 | 0 | 0 | 42084.2 | 0 | 0 | 0 | 0 | 0 | 42084.2
2022082124 | 1 | 0.63915 | 51132 | 0.20485 | 7374.6 | 0 | 0 | 1 | 5000 | 7374.6 | 0 | 0 | 0 | 0 | 0 | 38757.4 | 0 | 0 | 0 | 0 | 0 | 38757.4
2022082201 | 2 | 0.60583 | 48466.4 | 0.21143 | 7611.48 | 0 | 0 | 1 | 5000 | 7611.48 | 0 | 0 | 0 | 0 | 0 | 35854.92 | 0 | 0 | 0 | 0 | 0 | 35854.92
2022082202 | 2 | 0.58148 | 46518.4 | 0.21256 | 7652.16 | 0 | 0 | 1 | 5000 | 7652.16 | 0 | 0 | 0 | 0 | 0 | 33866.24 | 0 | 0 | 0 | 0 | 0 | 33866.24
2022082203 | 2 | 0.56754 | 45403.2 | 0.22567 | 8124.12 | 0 | 0 | 1 | 5000 | 8124.12 | 0 | 0 | 0 | 0 | 0 | 32279.08 | 0 | 0 | 0 | 0 | 0 | 32279.08
2022082204 | 2 | 0.56341 | 45072.8 | 0.22924 | 8252.64 | 0 | 0 | 1 | 5000 | 8252.64 | 0 | 0 | 0 | 0 | 0 | 31820.16 | 0 | 0 | 0 | 0 | 0 | 31820.16
2022082205 | 2 | 0.5636 | 45088 | 0.21775 | 7839 | 0 | 0 | 1 | 5000 | 7839 | 0 | 0 | 0 | 0 | 0 | 32249 | 0 | 0 | 0 | 0 | 0 | 32249
2022082206 | 2 | 0.58001 | 46400.8 | 0.21547 | 7756.92 | 0 | 0 | 1 | 5000 | 7756.92 | 0 | 0 | 0 | 0 | 0 | 33643.88 | 0 | 0 | 0 | 0 | 0 | 33643.88
2022082207 | 2 | 0.60776 | 48620.8 | 0.2313 | 8326.8 | 0 | 0 | 1 | 5000 | 8326.8 | 0 | 0 | 0 | 0 | 0 | 35294 | 0 | 0 | 0 | 0 | 0 | 35294
2022082208 | 2 | 0.61617 | 49293.6 | 0.23687 | 8527.32 | 0.01245 | 149.4 | 1 | 5000 | 8527.32 | 149.4 | 0 | 0 | 0 | 0 | 35616.88 | 0 | 0 | 0 | 0 | 0 | 35616.88
2022082209 | 2 | 0.63046 | 50436.8 | 0.25157 | 9056.52 | 0.09839 | 1180.68 | 1 | 5000 | 9056.52 | 1180.68 | 0 | 0 | 0 | 0 | 35199.6 | 0 | 0 | 0 | 0 | 0 | 35199.6
2022082210 | 2 | 0.65707 | 52565.6 | 0.29449 | 10601.64 | 0.1975 | 2370 | 1 | 5000 | 10601.64 | 2370 | 0 | 0 | 0 | 0 | 34593.96 | 0 | 0 | 0 | 0 | 0 | 34593.96
2022082211 | 2 | 0.68712 | 54969.6 | 0.30438 | 10957.68 | 0.29326 | 3519.12 | 1 | 5000 | 10957.68 | 3519.12 | 0 | 0 | 0 | 0 | 35492.8 | 0 | 0 | 0 | 0 | 0 | 35492.8
2022082212 | 2 | 0.71312 | 57049.6 | 0.28385 | 10218.6 | 0.39853 | 4782.36 | 1 | 5000 | 10218.6 | 4782.36 | 0 | 0 | 0 | 0 | 37048.64 | 0 | 0 | 0 | 0 | 0 | 37048.64
2022082213 | 2 | 0.73599 | 58879.2 | 0.26122 | 9403.92 | 0.42899 | 5147.88 | 1 | 5000 | 9403.92 | 5147.88 | 0 | 0 | 0 | 0 | 39327.4 | 0 | 0 | 0 | 0 | 0 | 39327.4
2022082214 | 2 | 0.75445 | 60356 | 0.24208 | 8714.88 | 0.44577 | 5349.24 | 1 | 5000 | 8714.88 | 5349.24 | 0 | 0 | 0 | 0 | 41291.88 | 0 | 0 | 0 | 0 | 0 | 41291.88
2022082215 | 2 | 0.76664 | 61331.2 | 0.25545 | 9196.2 | 0.44065 | 5287.8 | 1 | 5000 | 9196.2 | 5287.8 | 0 | 0 | 0 | 0 | 41847.2 | 0 | 0 | 0 | 0 | 0 | 41847.2
2022082216 | 2 | 0.77374 | 61899.2 | 0.26454 | 9523.44 | 0.43699 | 5243.88 | 1 | 5000 | 9523.44 | 5243.88 | 0 | 0 | 0 | 0 | 42131.88 | 0 | 0 | 0 | 0 | 0 | 42131.88
2022082217 | 2 | 0.77591 | 62072.8 | 0.26587 | 9571.32 | 0.37547 | 4505.64 | 1 | 5000 | 9571.32 | 4505.64 | 0 | 0 | 0 | 0 | 42995.84 | 0 | 0 | 0 | 0 | 0 | 42995.84
2022082218 | 2 | 0.76975 | 61580 | 0.25955 | 9343.8 | 0.29567 | 3548.04 | 1 | 5000 | 9343.8 | 3548.04 | 0 | 0 | 0 | 0 | 43688.16 | 0 | 0 | 0 | 0 | 0 | 43688.16
2022082219 | 2 | 0.74849 | 59879.2 | 0.24325 | 8757 | 0.20344 | 2441.28 | 1 | 5000 | 8757 | 2441.28 | 0 | 0 | 0 | 0 | 43680.92 | 0 | 0 | 0 | 0 | 0 | 43680.92
2022082220 | 2 | 0.72372 | 57897.6 | 0.2164 | 7790.4 | 0.06314 | 757.68 | 1 | 5000 | 7790.4 | 757.68 | 0 | 0 | 0 | 0 | 44349.52 | 0 | 0 | 0 | 0 | 0 | 44349.52
2022082221 | 2 | 0.71129 | 56903.2 | 0.18885 | 6798.6 | 0.00194 | 23.28 | 1 | 5000 | 6798.6 | 23.28 | 0 | 0 | 0 | 0 | 45081.32 | 0 | 0 | 0 | 0 | 0 | 45081.32
2022082222 | 2 | 0.69144 | 55315.2 | 0.17623 | 6344.28 | 0 | 0 | 1 | 5000 | 6344.28 | 0 | 0 | 0 | 0 | 0 | 43970.92 | 0 | 0 | 0 | 0 | 0 | 43970.92
2022082223 | 2 | 0.65593 | 52474.4 | 0.17178 | 6184.08 | 0 | 0 | 1 | 5000 | 6184.08 | 0 | 0 | 0 | 0 | 0 | 41290.32 | 0 | 0 | 0 | 0 | 0 | 41290.32
2022082224 | 2 | 0.61389 | 49111.2 | 0.13812 | 4972.32 | 0 | 0 | 1 | 5000 | 4972.32 | 0 | 0 | 0 | 0 | 0 | 39138.88 | 0 | 0 | 0 | 0 | 0 | 39138.88
2022082301 | 3 | 0.57872 | 46297.6 | 0.10788 | 3883.68 | 0 | 0 | 1 | 5000 | 3883.68 | 0 | 0 | 0 | 0 | 0 | 37413.92 | 0 | 0 | 0 | 0 | 0 | 37413.92
2022082302 | 3 | 0.55693 | 44554.4 | 0.09594 | 3453.84 | 0 | 0 | 1 | 5000 | 3453.84 | 0 | 0 | 0 | 0 | 0 | 36100.56 | 0 | 0 | 0 | 0 | 0 | 36100.56
2022082303 | 3 | 0.54223 | 43378.4 | 0.07591 | 2732.76 | 0 | 0 | 1 | 5000 | 2732.76 | 0 | 0 | 0 | 0 | 0 | 35645.64 | 0 | 0 | 0 | 0 | 0 | 35645.64
2022082304 | 3 | 0.5353 | 42824 | 0.0691 | 2487.6 | 0 | 0 | 1 | 5000 | 2487.6 | 0 | 0 | 0 | 0 | 0 | 35336.4 | 0 | 0 | 0 | 0 | 0 | 35336.4
2022082305 | 3 | 0.53566 | 42852.8 | 0.05489 | 1976.04 | 0 | 0 | 1 | 5000 | 1976.04 | 0 | 0 | 0 | 0 | 0 | 35876.76 | 0 | 0 | 0 | 0 | 0 | 35876.76
2022082306 | 3 | 0.55302 | 44241.6 | 0.05339 | 1922.04 | 0 | 0 | 1 | 5000 | 1922.04 | 0 | 0 | 0 | 0 | 0 | 37319.56 | 0 | 0 | 0 | 0 | 0 | 37319.56
2022082307 | 3 | 0.57936 | 46348.8 | 0.05182 | 1865.52 | 0 | 0 | 1 | 5000 | 1865.52 | 0 | 0 | 0 | 0 | 0 | 39483.28 | 0 | 0 | 0 | 0 | 0 | 39483.28
2022082308 | 3 | 0.59036 | 47228.8 | 0.05398 | 1943.28 | 0.01074 | 128.88 | 1 | 5000 | 1943.28 | 128.88 | 0 | 0 | 0 | 0 | 40156.64 | 0 | 0 | 0 | 0 | 0 | 40156.64
2022082309 | 3 | 0.59805 | 47844 | 0.04548 | 1637.28 | 0.12478 | 1497.36 | 1 | 5000 | 1637.28 | 1497.36 | 0 | 0 | 0 | 0 | 39709.36 | 0 | 0 | 0 | 0 | 0 | 39709.36
2022082310 | 3 | 0.6184 | 49472 | 0.04891 | 1760.76 | 0.26021 | 3122.52 | 1 | 5000 | 1760.76 | 3122.52 | 0 | 0 | 0 | 0 | 39588.72 | 0 | 0 | 0 | 0 | 0 | 39588.72
2022082311 | 3 | 0.64305 | 51444 | 0.0665 | 2394 | 0.33117 | 3974.04 | 1 | 5000 | 2394 | 3974.04 | 0 | 0 | 0 | 0 | 40075.96 | 0 | 0 | 0 | 0 | 0 | 40075.96
2022082312 | 3 | 0.66818 | 53454.4 | 0.07206 | 2594.16 | 0.38823 | 4658.76 | 1 | 5000 | 2594.16 | 4658.76 | 0 | 0 | 0 | 0 | 41201.48 | 0 | 0 | 0 | 0 | 0 | 41201.48
2022082313 | 3 | 0.69111 | 55288.8 | 0.06791 | 2444.76 | 0.46417 | 5570.04 | 1 | 5000 | 2444.76 | 5570.04 | 0 | 0 | 0 | 0 | 42274 | 0 | 0 | 0 | 0 | 0 | 42274
2022082314 | 3 | 0.71556 | 57244.8 | 0.06885 | 2478.6 | 0.49067 | 5888.04 | 1 | 5000 | 2478.6 | 5888.04 | 0 | 0 | 0 | 0 | 43878.16 | 0 | 0 | 0 | 0 | 0 | 43878.16
2022082315 | 3 | 0.73749 | 58999.2 | 0.07908 | 2846.88 | 0.49321 | 5918.52 | 1 | 5000 | 2846.88 | 5918.52 | 0 | 0 | 0 | 0 | 45233.8 | 0 | 0 | 0 | 0 | 0 | 45233.8
2022082316 | 3 | 0.7599 | 60792 | 0.08533 | 3071.88 | 0.50431 | 6051.72 | 1 | 5000 | 3071.88 | 6051.72 | 0 | 0 | 0 | 0 | 46668.4 | 0 | 0 | 0 | 0 | 0 | 46668.4
2022082317 | 3 | 0.78004 | 62403.2 | 0.10811 | 3891.96 | 0.51581 | 6189.72 | 1 | 5000 | 3891.96 | 6189.72 | 0 | 0 | 0 | 0 | 47321.52 | 0 | 0 | 0 | 0 | 0 | 47321.52
2022082318 | 3 | 0.7899 | 63192 | 0.1397 | 5029.2 | 0.45881 | 5505.72 | 1 | 5000 | 5029.2 | 5505.72 | 0 | 0 | 0 | 0 | 47657.08 | 0 | 0 | 0 | 0 | 0 | 47657.08
2022082319 | 3 | 0.77769 | 62215.2 | 0.17708 | 6374.88 | 0.35525 | 4263 | 1 | 5000 | 6374.88 | 4263 | 0 | 0 | 0 | 0 | 46577.32 | 0 | 0 | 0 | 0 | 0 | 46577.32
2022082320 | 3 | 0.75524 | 60419.2 | 0.16116 | 5801.76 | 0.10679 | 1281.48 | 1 | 5000 | 5801.76 | 1281.48 | 0 | 0 | 0 | 0 | 48335.96 | 0 | 0 | 0 | 0 | 0 | 48335.96
2022082321 | 3 | 0.73954 | 59163.2 | 0.13929 | 5014.44 | 0.00184 | 22.08 | 1 | 5000 | 5014.44 | 22.08 | 0 | 0 | 0 | 0 | 49126.68 | 0 | 0 | 0 | 0 | 0 | 49126.68
2022082322 | 3 | 0.71781 | 57424.8 | 0.13756 | 4952.16 | 0 | 0 | 1 | 5000 | 4952.16 | 0 | 0 | 0 | 0 | 0 | 47472.64 | 0 | 0 | 0 | 0 | 0 | 47472.64
2022082323 | 3 | 0.67865 | 54292 | 0.14426 | 5193.36 | 0 | 0 | 1 | 5000 | 5193.36 | 0 | 0 | 0 | 0 | 0 | 44098.64 | 0 | 0 | 0 | 0 | 0 | 44098.64
2022082324 | 3 | 0.63175 | 50540 | 0.13882 | 4997.52 | 0 | 0 | 1 | 5000 | 4997.52 | 0 | 0 | 0 | 0 | 0 | 40542.48 | 0 | 0 | 0 | 0 | 0 | 40542.48
2022082401 | 4 | 0.59625 | 47700 | 0.11684 | 4206.24 | 0 | 0 | 1 | 5000 | 4206.24 | 0 | 0 | 0 | 0 | 0 | 38493.76 | 0 | 0 | 0 | 0 | 0 | 38493.76
2022082402 | 4 | 0.57522 | 46017.6 | 0.10797 | 3886.92 | 0 | 0 | 1 | 5000 | 3886.92 | 0 | 0 | 0 | 0 | 0 | 37130.68 | 0 | 0 | 0 | 0 | 0 | 37130.68
2022082403 | 4 | 0.55994 | 44795.2 | 0.09535 | 3432.6 | 0 | 0 | 1 | 5000 | 3432.6 | 0 | 0 | 0 | 0 | 0 | 36362.6 | 0 | 0 | 0 | 0 | 0 | 36362.6
2022082404 | 4 | 0.55265 | 44212 | 0.08258 | 2972.88 | 0 | 0 | 1 | 5000 | 2972.88 | 0 | 0 | 0 | 0 | 0 | 36239.12 | 0 | 0 | 0 | 0 | 0 | 36239.12
2022082405 | 4 | 0.55108 | 44086.4 | 0.06878 | 2476.08 | 0 | 0 | 1 | 5000 | 2476.08 | 0 | 0 | 0 | 0 | 0 | 36610.32 | 0 | 0 | 0 | 0 | 0 | 36610.32
2022082406 | 4 | 0.56325 | 45060 | 0.05553 | 1999.08 | 0 | 0 | 1 | 5000 | 1999.08 | 0 | 0 | 0 | 0 | 0 | 38060.92 | 0 | 0 | 0 | 0 | 0 | 38060.92
2022082407 | 4 | 0.58888 | 47110.4 | 0.04769 | 1716.84 | 0 | 0 | 1 | 5000 | 1716.84 | 0 | 0 | 0 | 0 | 0 | 40393.56 | 0 | 0 | 0 | 0 | 0 | 40393.56
2022082408 | 4 | 0.59605 | 47684 | 0.03817 | 1374.12 | 0.02382 | 285.84 | 1 | 5000 | 1374.12 | 285.84 | 0 | 0 | 0 | 0 | 41024.04 | 0 | 0 | 0 | 0 | 0 | 41024.04
2022082409 | 4 | 0.60905 | 48724 | 0.02358 | 848.88 | 0.22815 | 2737.8 | 1 | 5000 | 848.88 | 2737.8 | 0 | 0 | 0 | 0 | 40137.32 | 0 | 0 | 0 | 0 | 0 | 40137.32
2022082410 | 4 | 0.63072 | 50457.6 | 0.01538 | 553.68 | 0.41958 | 5034.96 | 1 | 5000 | 553.68 | 5034.96 | 0 | 0 | 0 | 0 | 39868.96 | 0 | 0 | 0 | 0 | 0 | 39868.96
2022082411 | 4 | 0.65803 | 52642.4 | 0.02836 | 1020.96 | 0.49944 | 5993.28 | 1 | 5000 | 1020.96 | 5993.28 | 0 | 0 | 0 | 0 | 40628.16 | 0 | 0 | 0 | 0 | 0 | 40628.16
2022082412 | 4 | 0.6862 | 54896 | 0.03815 | 1373.4 | 0.57031 | 6843.72 | 1 | 5000 | 1373.4 | 6843.72 | 0 | 0 | 0 | 0 | 41678.88 | 0 | 0 | 0 | 0 | 0 | 41678.88
2022082413 | 4 | 0.71764 | 57411.2 | 0.03656 | 1316.16 | 0.57076 | 6849.12 | 1 | 5000 | 1316.16 | 6849.12 | 0 | 0 | 0 | 0 | 44245.92 | 0 | 0 | 0 | 0 | 0 | 44245.92
2022082414 | 4 | 0.74863 | 59890.4 | 0.04546 | 1636.56 | 0.56619 | 6794.28 | 1 | 5000 | 1636.56 | 6794.28 | 0 | 0 | 0 | 0 | 46459.56 | 0 | 0 | 0 | 0 | 0 | 46459.56
2022082415 | 4 | 0.76695 | 61356 | 0.06454 | 2323.44 | 0.57474 | 6896.88 | 1 | 5000 | 2323.44 | 6896.88 | 0 | 0 | 0 | 0 | 47135.68 | 0 | 0 | 0 | 0 | 0 | 47135.68
2022082416 | 4 | 0.77784 | 62227.2 | 0.10651 | 3834.36 | 0.55773 | 6692.76 | 1 | 5000 | 3834.36 | 6692.76 | 0 | 0 | 0 | 0 | 46700.08 | 0 | 0 | 0 | 0 | 0 | 46700.08
2022082417 | 4 | 0.78532 | 62825.6 | 0.13649 | 4913.64 | 0.44669 | 5360.28 | 1 | 5000 | 4913.64 | 5360.28 | 0 | 0 | 0 | 0 | 47551.68 | 0 | 0 | 0 | 0 | 0 | 47551.68
2022082418 | 4 | 0.78839 | 63071.2 | 0.14701 | 5292.36 | 0.42385 | 5086.2 | 1 | 5000 | 5292.36 | 5086.2 | 0 | 0 | 0 | 0 | 47692.64 | 0 | 0 | 0 | 0 | 0 | 47692.64
2022082419 | 4 | 0.77571 | 62056.8 | 0.16379 | 5896.44 | 0.30162 | 3619.44 | 1 | 5000 | 5896.44 | 3619.44 | 0 | 0 | 0 | 0 | 47540.92 | 0 | 0 | 0 | 0 | 0 | 47540.92
2022082420 | 4 | 0.75471 | 60376.8 | 0.17238 | 6205.68 | 0.09371 | 1124.52 | 1 | 5000 | 6205.68 | 1124.52 | 0 | 0 | 0 | 0 | 48046.6 | 0 | 0 | 0 | 0 | 0 | 48046.6
2022082421 | 4 | 0.74099 | 59279.2 | 0.16432 | 5915.52 | 0.01416 | 169.92 | 1 | 5000 | 5915.52 | 169.92 | 0 | 0 | 0 | 0 | 48193.76 | 0 | 0 | 0 | 0 | 0 | 48193.76
2022082422 | 4 | 0.71387 | 57109.6 | 0.15569 | 5604.84 | 0.01195 | 143.4 | 1 | 5000 | 5604.84 | 143.4 | 0 | 0 | 0 | 0 | 46361.36 | 0 | 0 | 0 | 0 | 0 | 46361.36
2022082423 | 4 | 0.66683 | 53346.4 | 0.13926 | 5013.36 | 0.00328 | 39.36 | 1 | 5000 | 5013.36 | 39.36 | 0 | 0 | 0 | 0 | 43293.68 | 0 | 0 | 0 | 0 | 0 | 43293.68
2022082424 | 4 | 0.61905 | 49524 | 0.11831 | 4259.16 | 0 | 0 | 1 | 5000 | 4259.16 | 0 | 0 | 0 | 0 | 0 | 40264.84 | 0 | 0 | 0 | 0 | 0 | 40264.84
2022082501 | 5 | 0.58243 | 46594.4 | 0.09759 | 3513.24 | 0 | 0 | 1 | 5000 | 3513.24 | 0 | 0 | 0 | 0 | 0 | 38081.16 | 0 | 0 | 0 | 0 | 0 | 38081.16
2022082502 | 5 | 0.55801 | 44640.8 | 0.08364 | 3011.04 | 0 | 0 | 1 | 5000 | 3011.04 | 0 | 0 | 0 | 0 | 0 | 36629.76 | 0 | 0 | 0 | 0 | 0 | 36629.76
2022082503 | 5 | 0.54239 | 43391.2 | 0.06654 | 2395.44 | 0 | 0 | 1 | 5000 | 2395.44 | 0 | 0 | 0 | 0 | 0 | 35995.76 | 0 | 0 | 0 | 0 | 0 | 35995.76
2022082504 | 5 | 0.53116 | 42492.8 | 0.05832 | 2099.52 | 0 | 0 | 1 | 5000 | 2099.52 | 0 | 0 | 0 | 0 | 0 | 35393.28 | 0 | 0 | 0 | 0 | 0 | 35393.28
2022082505 | 5 | 0.53126 | 42500.8 | 0.04684 | 1686.24 | 0 | 0 | 1 | 5000 | 1686.24 | 0 | 0 | 0 | 0 | 0 | 35814.56 | 0 | 0 | 0 | 0 | 0 | 35814.56
2022082506 | 5 | 0.54613 | 43690.4 | 0.0397 | 1429.2 | 0 | 0 | 1 | 5000 | 1429.2 | 0 | 0 | 0 | 0 | 0 | 37261.2 | 0 | 0 | 0 | 0 | 0 | 37261.2
2022082507 | 5 | 0.5742 | 45936 | 0.03676 | 1323.36 | 0 | 0 | 1 | 5000 | 1323.36 | 0 | 0 | 0 | 0 | 0 | 39612.64 | 0 | 0 | 0 | 0 | 0 | 39612.64
2022082508 | 5 | 0.5819 | 46552 | 0.03468 | 1248.48 | 0.03171 | 380.52 | 1 | 5000 | 1248.48 | 380.52 | 0 | 0 | 0 | 0 | 39923 | 0 | 0 | 0 | 0 | 0 | 39923
2022082509 | 5 | 0.60119 | 48095.2 | 0.02066 | 743.76 | 0.27899 | 3347.88 | 1 | 5000 | 743.76 | 3347.88 | 0 | 0 | 0 | 0 | 39003.56 | 0 | 0 | 0 | 0 | 0 | 39003.56
2022082510 | 5 | 0.63406 | 50724.8 | 0.01472 | 529.92 | 0.45322 | 5438.64 | 1 | 5000 | 529.92 | 5438.64 | 0 | 0 | 0 | 0 | 39756.24 | 0 | 0 | 0 | 0 | 0 | 39756.24
2022082511 | 5 | 0.67763 | 54210.4 | 0.02359 | 849.24 | 0.5337 | 6404.4 | 1 | 5000 | 849.24 | 6404.4 | 0 | 0 | 0 | 0 | 41956.76 | 0 | 0 | 0 | 0 | 0 | 41956.76
2022082512 | 5 | 0.71824 | 57459.2 | 0.02849 | 1025.64 | 0.56926 | 6831.12 | 1 | 5000 | 1025.64 | 6831.12 | 0 | 0 | 0 | 0 | 44602.44 | 0 | 0 | 0 | 0 | 0 | 44602.44
2022082513 | 5 | 0.75342 | 60273.6 | 0.02196 | 790.56 | 0.57282 | 6873.84 | 1 | 5000 | 790.56 | 6873.84 | 0 | 0 | 0 | 0 | 47609.2 | 0 | 0 | 0 | 0 | 0 | 47609.2
2022082514 | 5 | 0.78741 | 62992.8 | 0.02955 | 1063.8 | 0.57833 | 6939.96 | 1 | 5000 | 1063.8 | 6939.96 | 0 | 0 | 0 | 0 | 49989.04 | 0 | 0 | 0 | 0 | 0 | 49989.04
2022082515 | 5 | 0.81263 | 65010.4 | 0.06176 | 2223.36 | 0.57664 | 6919.68 | 1 | 5000 | 2223.36 | 6919.68 | 0 | 0 | 0 | 0 | 50867.36 | 0 | 0 | 0 | 0 | 0 | 50867.36
2022082516 | 5 | 0.83416 | 66732.8 | 0.08425 | 3033 | 0.5003 | 6003.6 | 1 | 5000 | 3033 | 6003.6 | 0 | 0 | 0 | 0 | 52696.2 | 0 | 0 | 0 | 0 | 0 | 52696.2
2022082517 | 5 | 0.84785 | 67828 | 0.0805 | 2898 | 0.50239 | 6028.68 | 1 | 5000 | 2898 | 6028.68 | 0 | 0 | 0 | 0 | 53901.32 | 0 | 0 | 0 | 0 | 0 | 53901.32
2022082518 | 5 | 0.84547 | 67637.6 | 0.06785 | 2442.6 | 0.49246 | 5909.52 | 1 | 5000 | 2442.6 | 5909.52 | 0 | 0 | 0 | 0 | 54285.48 | 0 | 0 | 0 | 0 | 0 | 54285.48
2022082519 | 5 | 0.82924 | 66339.2 | 0.06703 | 2413.08 | 0.39579 | 4749.48 | 1 | 5000 | 2413.08 | 4749.48 | 0 | 0 | 0 | 0 | 54176.64 | 0 | 0 | 0 | 0 | 0 | 54176.64
2022082520 | 5 | 0.79844 | 63875.2 | 0.07685 | 2766.6 | 0.13788 | 1654.56 | 1 | 5000 | 2766.6 | 1654.56 | 0 | 0 | 0 | 0 | 54454.04 | 0 | 0 | 0 | 0 | 0 | 54454.04
2022082521 | 5 | 0.77582 | 62065.6 | 0.08737 | 3145.32 | 0.0021 | 25.2 | 1 | 5000 | 3145.32 | 25.2 | 0 | 0 | 0 | 0 | 53895.08 | 0 | 0 | 0 | 0 | 0 | 53895.08
2022082522 | 5 | 0.74869 | 59895.2 | 0.10919 | 3930.84 | 0 | 0 | 1 | 5000 | 3930.84 | 0 | 0 | 0 | 0 | 0 | 50964.36 | 0 | 0 | 0 | 0 | 0 | 50964.36
2022082523 | 5 | 0.70232 | 56185.6 | 0.13267 | 4776.12 | 0 | 0 | 1 | 5000 | 4776.12 | 0 | 0 | 0 | 0 | 0 | 46409.48 | 0 | 0 | 0 | 0 | 0 | 46409.48
2022082524 | 5 | 0.6524 | 52192 | 0.1407 | 5065.2 | 0 | 0 | 1 | 5000 | 5065.2 | 0 | 0 | 0 | 0 | 0 | 42126.8 | 0 | 0 | 0 | 0 | 0 | 42126.8
2022082601 | 6 | 0.60918 | 48734.4 | 0.15169 | 5460.84 | 0 | 0 | 1 | 5000 | 5460.84 | 0 | 0 | 0 | 0 | 0 | 38273.56 | 0 | 0 | 0 | 0 | 0 | 38273.56
2022082602 | 6 | 0.58088 | 46470.4 | 0.15163 | 5458.68 | 0 | 0 | 1 | 5000 | 5458.68 | 0 | 0 | 0 | 0 | 0 | 36011.72 | 0 | 0 | 0 | 0 | 0 | 36011.72
2022082603 | 6 | 0.56296 | 45036.8 | 0.14743 | 5307.48 | 0 | 0 | 1 | 5000 | 5307.48 | 0 | 0 | 0 | 0 | 0 | 34729.32 | 0 | 0 | 0 | 0 | 0 | 34729.32
2022082604 | 6 | 0.54909 | 43927.2 | 0.12863 | 4630.68 | 0 | 0 | 1 | 5000 | 4630.68 | 0 | 0 | 0 | 0 | 0 | 34296.52 | 0 | 0 | 0 | 0 | 0 | 34296.52
2022082605 | 6 | 0.54546 | 43636.8 | 0.10741 | 3866.76 | 0 | 0 | 1 | 5000 | 3866.76 | 0 | 0 | 0 | 0 | 0 | 34770.04 | 0 | 0 | 0 | 0 | 0 | 34770.04
2022082606 | 6 | 0.55906 | 44724.8 | 0.09769 | 3516.84 | 0 | 0 | 1 | 5000 | 3516.84 | 0 | 0 | 0 | 0 | 0 | 36207.96 | 0 | 0 | 0 | 0 | 0 | 36207.96
2022082607 | 6 | 0.58498 | 46798.4 | 0.07908 | 2846.88 | 0 | 0 | 1 | 5000 | 2846.88 | 0 | 0 | 0 | 0 | 0 | 38951.52 | 0 | 0 | 0 | 0 | 0 | 38951.52
2022082608 | 6 | 0.59257 | 47405.6 | 0.06416 | 2309.76 | 0.03703 | 444.36 | 1 | 5000 | 2309.76 | 444.36 | 0 | 0 | 0 | 0 | 39651.48 | 0 | 0 | 0 | 0 | 0 | 39651.48
2022082609 | 6 | 0.61329 | 49063.2 | 0.03787 | 1363.32 | 0.3436 | 4123.2 | 1 | 5000 | 1363.32 | 4123.2 | 0 | 0 | 0 | 0 | 38576.68 | 0 | 0 | 0 | 0 | 0 | 38576.68
2022082610 | 6 | 0.655 | 52400 | 0.02209 | 795.24 | 0.61307 | 7356.84 | 1 | 5000 | 795.24 | 7356.84 | 0 | 0 | 0 | 0 | 39247.92 | 0 | 0 | 0 | 0 | 0 | 39247.92
2022082611 | 6 | 0.70126 | 56100.8 | 0.02633 | 947.88 | 0.69405 | 8328.6 | 1 | 5000 | 947.88 | 8328.6 | 0 | 0 | 0 | 0 | 41824.32 | 0 | 0 | 0 | 0 | 0 | 41824.32
2022082612 | 6 | 0.74735 | 59788 | 0.02418 | 870.48 | 0.69865 | 8383.8 | 1 | 5000 | 870.48 | 8383.8 | 0 | 0 | 0 | 0 | 45533.72 | 0 | 0 | 0 | 0 | 0 | 45533.72
2022082613 | 6 | 0.78858 | 63086.4 | 0.01962 | 706.32 | 0.65646 | 7877.52 | 1 | 5000 | 706.32 | 7877.52 | 0 | 0 | 0 | 0 | 49502.56 | 0 | 0 | 0 | 0 | 0 | 49502.56
2022082614 | 6 | 0.81956 | 65564.8 | 0.03044 | 1095.84 | 0.60953 | 7314.36 | 1 | 5000 | 1095.84 | 7314.36 | 0 | 0 | 0 | 0 | 52154.6 | 0 | 0 | 0 | 0 | 0 | 52154.6
2022082615 | 6 | 0.83969 | 67175.2 | 0.05678 | 2044.08 | 0.53159 | 6379.08 | 1 | 5000 | 2044.08 | 6379.08 | 0 | 0 | 0 | 0 | 53752.04 | 0 | 0 | 0 | 0 | 0 | 53752.04
2022082616 | 6 | 0.84855 | 67884 | 0.06305 | 2269.8 | 0.53304 | 6396.48 | 1 | 5000 | 2269.8 | 6396.48 | 0 | 0 | 0 | 0 | 54217.72 | 0 | 0 | 0 | 0 | 0 | 54217.72
2022082617 | 6 | 0.85572 | 68457.6 | 0.07578 | 2728.08 | 0.56823 | 6818.76 | 1 | 5000 | 2728.08 | 6818.76 | 0 | 0 | 0 | 0 | 53910.76 | 0 | 0 | 0 | 0 | 0 | 53910.76
2022082618 | 6 | 0.85168 | 68134.4 | 0.07697 | 2770.92 | 0.53611 | 6433.32 | 1 | 5000 | 2770.92 | 6433.32 | 0 | 0 | 0 | 0 | 53930.16 | 0 | 0 | 0 | 0 | 0 | 53930.16
2022082619 | 6 | 0.83014 | 66411.2 | 0.08678 | 3124.08 | 0.43043 | 5165.16 | 1 | 5000 | 3124.08 | 5165.16 | 0 | 0 | 0 | 0 | 53121.96 | 0 | 0 | 0 | 0 | 0 | 53121.96
2022082620 | 6 | 0.79676 | 63740.8 | 0.1122 | 4039.2 | 0.13023 | 1562.76 | 1 | 5000 | 4039.2 | 1562.76 | 0 | 0 | 0 | 0 | 53138.84 | 0 | 0 | 0 | 0 | 0 | 53138.84
2022082621 | 6 | 0.77212 | 61769.6 | 0.1509 | 5432.4 | 0.00265 | 31.8 | 1 | 5000 | 5432.4 | 31.8 | 0 | 0 | 0 | 0 | 51305.4 | 0 | 0 | 0 | 0 | 0 | 51305.4
2022082622 | 6 | 0.74261 | 59408.8 | 0.22308 | 8030.88 | 0 | 0 | 1 | 5000 | 8030.88 | 0 | 0 | 0 | 0 | 0 | 46377.92 | 0 | 0 | 0 | 0 | 0 | 46377.92
2022082623 | 6 | 0.70398 | 56318.4 | 0.29152 | 10494.72 | 0 | 0 | 1 | 5000 | 10494.72 | 0 | 0 | 0 | 0 | 0 | 40823.68 | 0 | 0 | 0 | 0 | 0 | 40823.68
2022082624 | 6 | 0.66422 | 53137.6 | 0.33839 | 12182.04 | 0 | 0 | 1 | 5000 | 12182.04 | 0 | 0 | 0 | 0 | 0 | 35955.56 | 0 | 0 | 0 | 0 | 0 | 35955.56
2022082701 | 7 | 0.62648 | 50118.4 | 0.3619 | 13028.4 | 0 | 0 | 1 | 5000 | 13028.4 | 0 | 0 | 0 | 0 | 0 | 32090 | 0 | 0 | 0 | 0 | 0 | 32090
2022082702 | 7 | 0.59585 | 47668 | 0.34596 | 12454.56 | 0 | 0 | 1 | 5000 | 12454.56 | 0 | 0 | 0 | 0 | 0 | 30213.44 | 0 | 0 | 0 | 0 | 0 | 30213.44
2022082703 | 7 | 0.57527 | 46021.6 | 0.34036 | 12252.96 | 0 | 0 | 1 | 5000 | 12252.96 | 0 | 0 | 0 | 0 | 0 | 28768.64 | 0 | 0 | 0 | 0 | 0 | 28768.64
2022082704 | 7 | 0.55895 | 44716 | 0.33245 | 11968.2 | 0 | 0 | 1 | 5000 | 11968.2 | 0 | 0 | 0 | 0 | 0 | 27747.8 | 0 | 0 | 0 | 0 | 0 | 27747.8
2022082705 | 7 | 0.54705 | 43764 | 0.29198 | 10511.28 | 0 | 0 | 1 | 5000 | 10511.28 | 0 | 0 | 0 | 0 | 0 | 28252.72 | 0 | 0 | 0 | 0 | 0 | 28252.72
2022082706 | 7 | 0.54587 | 43669.6 | 0.25949 | 9341.64 | 0 | 0 | 1 | 5000 | 9341.64 | 0 | 0 | 0 | 0 | 0 | 29327.96 | 0 | 0 | 0 | 0 | 0 | 29327.96
2022082707 | 7 | 0.54915 | 43932 | 0.25542 | 9195.12 | 0 | 0 | 1 | 5000 | 9195.12 | 0 | 0 | 0 | 0 | 0 | 29736.88 | 0 | 0 | 0 | 0 | 0 | 29736.88
2022082708 | 7 | 0.55432 | 44345.6 | 0.23363 | 8410.68 | 0.03637 | 436.44 | 1 | 5000 | 8410.68 | 436.44 | 0 | 0 | 0 | 0 | 30498.48 | 0 | 0 | 0 | 0 | 0 | 30498.48
2022082709 | 7 | 0.58846 | 47076.8 | 0.17085 | 6150.6 | 0.34396 | 4127.52 | 1 | 5000 | 6150.6 | 4127.52 | 0 | 0 | 0 | 0 | 31798.68 | 0 | 0 | 0 | 0 | 0 | 31798.68
2022082710 | 7 | 0.63842 | 51073.6 | 0.14477 | 5211.72 | 0.612 | 7344 | 1 | 5000 | 5211.72 | 7344 | 0 | 0 | 0 | 0 | 33517.88 | 0 | 0 | 0 | 0 | 0 | 33517.88
2022082711 | 7 | 0.69256 | 55404.8 | 0.1714 | 6170.4 | 0.7272 | 8726.4 | 1 | 5000 | 6170.4 | 8726.4 | 0 | 0 | 0 | 0 | 35508 | 0 | 0 | 0 | 0 | 0 | 35508
2022082712 | 7 | 0.74082 | 59265.6 | 0.17606 | 6338.16 | 0.74362 | 8923.44 | 1 | 5000 | 6338.16 | 8923.44 | 0 | 0 | 0 | 0 | 39004 | 0 | 0 | 0 | 0 | 0 | 39004
2022082713 | 7 | 0.78116 | 62492.8 | 0.1763 | 6346.8 | 0.74567 | 8948.04 | 1 | 5000 | 6346.8 | 8948.04 | 0 | 0 | 0 | 0 | 42197.96 | 0 | 0 | 0 | 0 | 0 | 42197.96
2022082714 | 7 | 0.81306 | 65044.8 | 0.19138 | 6889.68 | 0.74223 | 8906.76 | 1 | 5000 | 6889.68 | 8906.76 | 0 | 0 | 0 | 0 | 44248.36 | 0 | 0 | 0 | 0 | 0 | 44248.36
2022082715 | 7 | 0.83548 | 66838.4 | 0.19521 | 7027.56 | 0.68911 | 8269.32 | 1 | 5000 | 7027.56 | 8269.32 | 0 | 0 | 0 | 0 | 46541.52 | 0 | 0 | 0 | 0 | 0 | 46541.52
2022082716 | 7 | 0.84997 | 67997.6 | 0.20958 | 7544.88 | 0.65561 | 7867.32 | 1 | 5000 | 7544.88 | 7867.32 | 0 | 0 | 0 | 0 | 47585.4 | 0 | 0 | 0 | 0 | 0 | 47585.4
2022082717 | 7 | 0.86027 | 68821.6 | 0.22886 | 8238.96 | 0.64428 | 7731.36 | 1 | 5000 | 8238.96 | 7731.36 | 0 | 0 | 0 | 0 | 47851.28 | 0 | 0 | 0 | 0 | 0 | 47851.28
2022082718 | 7 | 0.86549 | 69239.2 | 0.26249 | 9449.64 | 0.63211 | 7585.32 | 1 | 5000 | 9449.64 | 7585.32 | 0 | 0 | 0 | 0 | 47204.24 | 0 | 0 | 0 | 0 | 0 | 47204.24
2022082719 | 7 | 0.84818 | 67854.4 | 0.31215 | 11237.4 | 0.49936 | 5992.32 | 1 | 5000 | 11237.4 | 5992.32 | 0 | 0 | 0 | 0 | 45624.68 | 0 | 0 | 0 | 0 | 0 | 45624.68
2022082720 | 7 | 0.81359 | 65087.2 | 0.31777 | 11439.72 | 0.14071 | 1688.52 | 1 | 5000 | 11439.72 | 1688.52 | 0 | 0 | 0 | 0 | 46958.96 | 0 | 0 | 0 | 0 | 0 | 46958.96
2022082721 | 7 | 0.78706 | 62964.8 | 0.34423 | 12392.28 | 0.0006 | 7.2 | 1 | 5000 | 12392.28 | 7.2 | 0 | 0 | 0 | 0 | 45565.32 | 0 | 0 | 0 | 0 | 0 | 45565.32
2022082722 | 7 | 0.75771 | 60616.8 | 0.39487 | 14215.32 | 0 | 0 | 1 | 5000 | 14215.32 | 0 | 0 | 0 | 0 | 0 | 41401.48 | 0 | 0 | 0 | 0 | 0 | 41401.48
2022082723 | 7 | 0.72025 | 57620 | 0.4343 | 15634.8 | 0 | 0 | 1 | 5000 | 15634.8 | 0 | 0 | 0 | 0 | 0 | 36985.2 | 0 | 0 | 0 | 0 | 0 | 36985.2
2022082724 | 7 | 0.68177 | 54541.6 | 0.48321 | 17395.56 | 0 | 0 | 1 | 5000 | 17395.56 | 0 | 0 | 0 | 0 | 0 | 32146.04 | 0 | 0 | 0 | 0 | 0 | 32146.04
2022082801 | 1 | 0.64461 | 51568.8 | 0.48461 | 17445.96 | 0 | 0 | 1 | 5000 | 17445.96 | 0 | 0 | 0 | 0 | 0 | 29122.84 | 0 | 0 | 0 | 0 | 0 | 29122.84
2022082802 | 1 | 0.61514 | 49211.2 | 0.50231 | 18083.16 | 0 | 0 | 1 | 5000 | 18083.16 | 0 | 0 | 0 | 0 | 0 | 26128.04 | 0 | 0 | 0 | 0 | 0 | 26128.04
2022082803 | 1 | 0.59358 | 47486.4 | 0.51094 | 18393.84 | 0 | 0 | 1 | 5000 | 18393.84 | 0 | 0 | 0 | 0 | 0 | 24092.56 | 0 | 0 | 0 | 0 | 0 | 24092.56
2022082804 | 1 | 0.57496 | 45996.8 | 0.48307 | 17390.52 | 0 | 0 | 1 | 5000 | 17390.52 | 0 | 0 | 0 | 0 | 0 | 23606.28 | 0 | 0 | 0 | 0 | 0 | 23606.28
2022082805 | 1 | 0.56177 | 44941.6 | 0.43294 | 15585.84 | 0 | 0 | 1 | 5000 | 15585.84 | 0 | 0 | 0 | 0 | 0 | 24355.76 | 0 | 0 | 0 | 0 | 0 | 24355.76
2022082806 | 1 | 0.55646 | 44516.8 | 0.40255 | 14491.8 | 0 | 0 | 1 | 5000 | 14491.8 | 0 | 0 | 0 | 0 | 0 | 25025 | 0 | 0 | 0 | 0 | 0 | 25025
2022082807 | 1 | 0.55596 | 44476.8 | 0.39579 | 14248.44 | 0 | 0 | 1 | 5000 | 14248.44 | 0 | 0 | 0 | 0 | 0 | 25228.36 | 0 | 0 | 0 | 0 | 0 | 25228.36
2022082808 | 1 | 0.55867 | 44693.6 | 0.39274 | 14138.64 | 0.04705 | 564.6 | 1 | 5000 | 14138.64 | 564.6 | 0 | 0 | 0 | 0 | 24990.36 | 0 | 0 | 0 | 0 | 0 | 24990.36
2022082809 | 1 | 0.59446 | 47556.8 | 0.34354 | 12367.44 | 0.40848 | 4901.76 | 1 | 5000 | 12367.44 | 4901.76 | 0 | 0 | 0 | 0 | 25287.6 | 0 | 0 | 0 | 0 | 0 | 25287.6
2022082810 | 1 | 0.65038 | 52030.4 | 0.34626 | 12465.36 | 0.68917 | 8270.04 | 1 | 5000 | 12465.36 | 8270.04 | 0 | 0 | 0 | 0 | 26295 | 0 | 0 | 0 | 0 | 0 | 26295
2022082811 | 1 | 0.70297 | 56237.6 | 0.30056 | 10820.16 | 0.76329 | 9159.48 | 1 | 5000 | 10820.16 | 9159.48 | 0 | 0 | 0 | 0 | 31257.96 | 0 | 0 | 0 | 0 | 0 | 31257.96
2022082812 | 1 | 0.7532 | 60256 | 0.23827 | 8577.72 | 0.78705 | 9444.6 | 1 | 5000 | 8577.72 | 9444.6 | 0 | 0 | 0 | 0 | 37233.68 | 0 | 0 | 0 | 0 | 0 | 37233.68
2022082813 | 1 | 0.79943 | 63954.4 | 0.21922 | 7891.92 | 0.78015 | 9361.8 | 1 | 5000 | 7891.92 | 9361.8 | 0 | 0 | 0 | 0 | 41700.68 | 0 | 0 | 0 | 0 | 0 | 41700.68
2022082814 | 1 | 0.83739 | 66991.2 | 0.20616 | 7421.76 | 0.75003 | 9000.36 | 1 | 5000 | 7421.76 | 9000.36 | 0 | 0 | 0 | 0 | 45569.08 | 0 | 0 | 0 | 0 | 0 | 45569.08
2022082815 | 1 | 0.8648 | 69184 | 0.20435 | 7356.6 | 0.72002 | 8640.24 | 1 | 5000 | 7356.6 | 8640.24 | 0 | 0 | 0 | 0 | 48187.16 | 0 | 0 | 0 | 0 | 0 | 48187.16
2022082816 | 1 | 0.88112 | 70489.6 | 0.2192 | 7891.2 | 0.67637 | 8116.44 | 1 | 5000 | 7891.2 | 8116.44 | 0 | 0 | 0 | 0 | 49481.96 | 0 | 0 | 0 | 0 | 0 | 49481.96
2022082817 | 1 | 0.88903 | 71122.4 | 0.25587 | 9211.32 | 0.51349 | 6161.88 | 1 | 5000 | 9211.32 | 6161.88 | 0 | 0 | 0 | 0 | 50749.2 | 0 | 0 | 0 | 0 | 0 | 50749.2
2022082818 | 1 | 0.89105 | 71284 | 0.32177 | 11583.72 | 0.47273 | 5672.76 | 1 | 5000 | 11583.72 | 5672.76 | 0 | 0 | 0 | 0 | 49027.52 | 0 | 0 | 0 | 0 | 0 | 49027.52
2022082819 | 1 | 0.87383 | 69906.4 | 0.43819 | 15774.84 | 0.38125 | 4575 | 1 | 5000 | 15774.84 | 4575 | 0 | 0 | 0 | 0 | 44556.56 | 0 | 0 | 0 | 0 | 0 | 44556.56
2022082820 | 1 | 0.84347 | 67477.6 | 0.49224 | 17720.64 | 0.11039 | 1324.68 | 1 | 5000 | 17720.64 | 1324.68 | 0 | 0 | 0 | 0 | 43432.28 | 0 | 0 | 0 | 0 | 0 | 43432.28
2022082821 | 1 | 0.81994 | 65595.2 | 0.4499 | 16196.4 | 0.00119 | 14.28 | 1 | 5000 | 16196.4 | 14.28 | 0 | 0 | 0 | 0 | 44384.52 | 0 | 0 | 0 | 0 | 0 | 44384.52
2022082822 | 1 | 0.78855 | 63084 | 0.4762 | 17143.2 | 0 | 0 | 1 | 5000 | 17143.2 | 0 | 0 | 0 | 0 | 0 | 40940.8 | 0 | 0 | 0 | 0 | 0 | 40940.8
2022082823 | 1 | 0.73773 | 59018.4 | 0.45515 | 16385.4 | 0 | 0 | 1 | 5000 | 16385.4 | 0 | 0 | 0 | 0 | 0 | 37633 | 0 | 0 | 0 | 0 | 0 | 37633
2022082824 | 1 | 0.68537 | 54829.6 | 0.40684 | 14646.24 | 0 | 0 | 1 | 5000 | 14646.24 | 0 | 0 | 0 | 0 | 0 | 35183.36 | 0 | 0 | 0 | 0 | 0 | 35183.36
2022082901 | 2 | 0.63824 | 51059.2 | 0.38642 | 13911.12 | 0 | 0 | 1 | 5000 | 13911.12 | 0 | 0 | 0 | 0 | 0 | 32148.08 | 0 | 0 | 0 | 0 | 0 | 32148.08
2022082902 | 2 | 0.60795 | 48636 | 0.34466 | 12407.76 | 0 | 0 | 1 | 5000 | 12407.76 | 0 | 0 | 0 | 0 | 0 | 31228.24 | 0 | 0 | 0 | 0 | 0 | 31228.24
2022082903 | 2 | 0.58959 | 47167.2 | 0.31155 | 11215.8 | 0 | 0 | 1 | 5000 | 11215.8 | 0 | 0 | 0 | 0 | 0 | 30951.4 | 0 | 0 | 0 | 0 | 0 | 30951.4
2022082904 | 2 | 0.57968 | 46374.4 | 0.28077 | 10107.72 | 0 | 0 | 1 | 5000 | 10107.72 | 0 | 0 | 0 | 0 | 0 | 31266.68 | 0 | 0 | 0 | 0 | 0 | 31266.68
2022082905 | 2 | 0.57905 | 46324 | 0.2645 | 9522 | 0 | 0 | 1 | 5000 | 9522 | 0 | 0 | 0 | 0 | 0 | 31802 | 0 | 0 | 0 | 0 | 0 | 31802
2022082906 | 2 | 0.59123 | 47298.4 | 0.24279 | 8740.44 | 0 | 0 | 1 | 5000 | 8740.44 | 0 | 0 | 0 | 0 | 0 | 33557.96 | 0 | 0 | 0 | 0 | 0 | 33557.96
2022082907 | 2 | 0.62079 | 49663.2 | 0.24997 | 8998.92 | 0 | 0 | 1 | 5000 | 8998.92 | 0 | 0 | 0 | 0 | 0 | 35664.28 | 0 | 0 | 0 | 0 | 0 | 35664.28
2022082908 | 2 | 0.62636 | 50108.8 | 0.24085 | 8670.6 | 0.03155 | 378.6 | 1 | 5000 | 8670.6 | 378.6 | 0 | 0 | 0 | 0 | 36059.6 | 0 | 0 | 0 | 0 | 0 | 36059.6
2022082909 | 2 | 0.63956 | 51164.8 | 0.20965 | 7547.4 | 0.29236 | 3508.32 | 1 | 5000 | 7547.4 | 3508.32 | 0 | 0 | 0 | 0 | 35109.08 | 0 | 0 | 0 | 0 | 0 | 35109.08
2022082910 | 2 | 0.67283 | 53826.4 | 0.23321 | 8395.56 | 0.52996 | 6359.52 | 1 | 5000 | 8395.56 | 6359.52 | 0 | 0 | 0 | 0 | 34071.32 | 0 | 0 | 0 | 0 | 0 | 34071.32
2022082911 | 2 | 0.71928 | 57542.4 | 0.22733 | 8183.88 | 0.64482 | 7737.84 | 1 | 5000 | 8183.88 | 7737.84 | 0 | 0 | 0 | 0 | 36620.68 | 0 | 0 | 0 | 0 | 0 | 36620.68
2022082912 | 2 | 0.75663 | 60530.4 | 0.1941 | 6987.6 | 0.68394 | 8207.28 | 1 | 5000 | 6987.6 | 8207.28 | 0 | 0 | 0 | 0 | 40335.52 | 0 | 0 | 0 | 0 | 0 | 40335.52
2022082913 | 2 | 0.79723 | 63778.4 | 0.17104 | 6157.44 | 0.69225 | 8307 | 1 | 5000 | 6157.44 | 8307 | 0 | 0 | 0 | 0 | 44313.96 | 0 | 0 | 0 | 0 | 0 | 44313.96
2022082914 | 2 | 0.83025 | 66420 | 0.17188 | 6187.68 | 0.65346 | 7841.52 | 1 | 5000 | 6187.68 | 7841.52 | 0 | 0 | 0 | 0 | 47390.8 | 0 | 0 | 0 | 0 | 0 | 47390.8
2022082915 | 2 | 0.84895 | 67916 | 0.19402 | 6984.72 | 0.62458 | 7494.96 | 1 | 5000 | 6984.72 | 7494.96 | 0 | 0 | 0 | 0 | 48436.32 | 0 | 0 | 0 | 0 | 0 | 48436.32
2022082916 | 2 | 0.85719 | 68575.2 | 0.22702 | 8172.72 | 0.57552 | 6906.24 | 1 | 5000 | 8172.72 | 6906.24 | 0 | 0 | 0 | 0 | 48496.24 | 0 | 0 | 0 | 0 | 0 | 48496.24
2022082917 | 2 | 0.86067 | 68853.6 | 0.28186 | 10146.96 | 0.51655 | 6198.6 | 1 | 5000 | 10146.96 | 6198.6 | 0 | 0 | 0 | 0 | 47508.04 | 0 | 0 | 0 | 0 | 0 | 47508.04
2022082918 | 2 | 0.85455 | 68364 | 0.3059 | 11012.4 | 0.42485 | 5098.2 | 1 | 5000 | 11012.4 | 5098.2 | 0 | 0 | 0 | 0 | 47253.4 | 0 | 0 | 0 | 0 | 0 | 47253.4
2022082919 | 2 | 0.83469 | 66775.2 | 0.3257 | 11725.2 | 0.21087 | 2530.44 | 1 | 5000 | 11725.2 | 2530.44 | 0 | 0 | 0 | 0 | 47519.56 | 0 | 0 | 0 | 0 | 0 | 47519.56
2022082920 | 2 | 0.80424 | 64339.2 | 0.33506 | 12062.16 | 0.04412 | 529.44 | 1 | 5000 | 12062.16 | 529.44 | 0 | 0 | 0 | 0 | 46747.6 | 0 | 0 | 0 | 0 | 0 | 46747.6
2022082921 | 2 | 0.78156 | 62524.8 | 0.37018 | 13326.48 | 0.00072 | 8.64 | 1 | 5000 | 13326.48 | 8.64 | 0 | 0 | 0 | 0 | 44189.68 | 0 | 0 | 0 | 0 | 0 | 44189.68
2022082922 | 2 | 0.7451 | 59608 | 0.42137 | 15169.32 | 0 | 0 | 1 | 5000 | 15169.32 | 0 | 0 | 0 | 0 | 0 | 39438.68 | 0 | 0 | 0 | 0 | 0 | 39438.68
2022082923 | 2 | 0.68943 | 55154.4 | 0.45034 | 16212.24 | 0 | 0 | 1 | 5000 | 16212.24 | 0 | 0 | 0 | 0 | 0 | 33942.16 | 0 | 0 | 0 | 0 | 0 | 33942.16
2022082924 | 2 | 0.6391 | 51128 | 0.36746 | 13228.56 | 0 | 0 | 1 | 5000 | 13228.56 | 0 | 0 | 0 | 0 | 0 | 32899.44 | 0 | 0 | 0 | 0 | 0 | 32899.44
2022083001 | 3 | 0.60409 | 48327.2 | 0.28652 | 10314.72 | 0 | 0 | 1 | 5000 | 10314.72 | 0 | 0 | 0 | 0 | 0 | 33012.48 | 0 | 0 | 0 | 0 | 0 | 33012.48
2022083002 | 3 | 0.57919 | 46335.2 | 0.21648 | 7793.28 | 0 | 0 | 1 | 5000 | 7793.28 | 0 | 0 | 0 | 0 | 0 | 33541.92 | 0 | 0 | 0 | 0 | 0 | 33541.92
2022083003 | 3 | 0.56631 | 45304.8 | 0.17922 | 6451.92 | 0 | 0 | 1 | 5000 | 6451.92 | 0 | 0 | 0 | 0 | 0 | 33852.88 | 0 | 0 | 0 | 0 | 0 | 33852.88
2022083004 | 3 | 0.56077 | 44861.6 | 0.15737 | 5665.32 | 0 | 0 | 1 | 5000 | 5665.32 | 0 | 0 | 0 | 0 | 0 | 34196.28 | 0 | 0 | 0 | 0 | 0 | 34196.28
2022083005 | 3 | 0.56214 | 44971.2 | 0.13628 | 4906.08 | 0 | 0 | 1 | 5000 | 4906.08 | 0 | 0 | 0 | 0 | 0 | 35065.12 | 0 | 0 | 0 | 0 | 0 | 35065.12
2022083006 | 3 | 0.58016 | 46412.8 | 0.12235 | 4404.6 | 0 | 0 | 1 | 5000 | 4404.6 | 0 | 0 | 0 | 0 | 0 | 37008.2 | 0 | 0 | 0 | 0 | 0 | 37008.2
2022083007 | 3 | 0.61029 | 48823.2 | 0.11158 | 4016.88 | 0 | 0 | 1 | 5000 | 4016.88 | 0 | 0 | 0 | 0 | 0 | 39806.32 | 0 | 0 | 0 | 0 | 0 | 39806.32
2022083008 | 3 | 0.61648 | 49318.4 | 0.13121 | 4723.56 | 0.00852 | 102.24 | 1 | 5000 | 4723.56 | 102.24 | 0 | 0 | 0 | 0 | 39492.6 | 0 | 0 | 0 | 0 | 0 | 39492.6
2022083009 | 3 | 0.63012 | 50409.6 | 0.1256 | 4521.6 | 0.1314 | 1576.8 | 1 | 5000 | 4521.6 | 1576.8 | 0 | 0 | 0 | 0 | 39311.2 | 0 | 0 | 0 | 0 | 0 | 39311.2
2022083010 | 3 | 0.65495 | 52396 | 0.12694 | 4569.84 | 0.32352 | 3882.24 | 1 | 5000 | 4569.84 | 3882.24 | 0 | 0 | 0 | 0 | 38943.92 | 0 | 0 | 0 | 0 | 0 | 38943.92
2022083011 | 3 | 0.68551 | 54840.8 | 0.13138 | 4729.68 | 0.36139 | 4336.68 | 1 | 5000 | 4729.68 | 4336.68 | 0 | 0 | 0 | 0 | 40774.44 | 0 | 0 | 0 | 0 | 0 | 40774.44
2022083012 | 3 | 0.71061 | 56848.8 | 0.11956 | 4304.16 | 0.41949 | 5033.88 | 1 | 5000 | 4304.16 | 5033.88 | 0 | 0 | 0 | 0 | 42510.76 | 0 | 0 | 0 | 0 | 0 | 42510.76
2022083013 | 3 | 0.72939 | 58351.2 | 0.11477 | 4131.72 | 0.4396 | 5275.2 | 1 | 5000 | 4131.72 | 5275.2 | 0 | 0 | 0 | 0 | 43944.28 | 0 | 0 | 0 | 0 | 0 | 43944.28
2022083014 | 3 | 0.74732 | 59785.6 | 0.1204 | 4334.4 | 0.45379 | 5445.48 | 1 | 5000 | 4334.4 | 5445.48 | 0 | 0 | 0 | 0 | 45005.72 | 0 | 0 | 0 | 0 | 0 | 45005.72
2022083015 | 3 | 0.75295 | 60236 | 0.1213 | 4366.8 | 0.42665 | 5119.8 | 1 | 5000 | 4366.8 | 5119.8 | 0 | 0 | 0 | 0 | 45749.4 | 0 | 0 | 0 | 0 | 0 | 45749.4
2022083016 | 3 | 0.75163 | 60130.4 | 0.1455 | 5238 | 0.40941 | 4912.92 | 1 | 5000 | 5238 | 4912.92 | 0 | 0 | 0 | 0 | 44979.48 | 0 | 0 | 0 | 0 | 0 | 44979.48
2022083017 | 3 | 0.7459 | 59672 | 0.18068 | 6504.48 | 0.317 | 3804 | 1 | 5000 | 6504.48 | 3804 | 0 | 0 | 0 | 0 | 44363.52 | 0 | 0 | 0 | 0 | 0 | 44363.52
2022083018 | 3 | 0.73014 | 58411.2 | 0.16524 | 5948.64 | 0.23441 | 2812.92 | 1 | 5000 | 5948.64 | 2812.92 | 0 | 0 | 0 | 0 | 44649.64 | 0 | 0 | 0 | 0 | 0 | 44649.64
2022083019 | 3 | 0.70962 | 56769.6 | 0.15447 | 5560.92 | 0.13901 | 1668.12 | 1 | 5000 | 5560.92 | 1668.12 | 0 | 0 | 0 | 0 | 44540.56 | 0 | 0 | 0 | 0 | 0 | 44540.56
2022083020 | 3 | 0.69365 | 55492 | 0.12353 | 4447.08 | 0.04596 | 551.52 | 1 | 5000 | 4447.08 | 551.52 | 0 | 0 | 0 | 0 | 45493.4 | 0 | 0 | 0 | 0 | 0 | 45493.4
2022083021 | 3 | 0.69296 | 55436.8 | 0.10814 | 3893.04 | 0.00146 | 17.52 | 1 | 5000 | 3893.04 | 17.52 | 0 | 0 | 0 | 0 | 46526.24 | 0 | 0 | 0 | 0 | 0 | 46526.24
2022083022 | 3 | 0.67244 | 53795.2 | 0.08749 | 3149.64 | 0 | 0 | 1 | 5000 | 3149.64 | 0 | 0 | 0 | 0 | 0 | 45645.56 | 0 | 0 | 0 | 0 | 0 | 45645.56
2022083023 | 3 | 0.63671 | 50936.8 | 0.07858 | 2828.88 | 0 | 0 | 1 | 5000 | 2828.88 | 0 | 0 | 0 | 0 | 0 | 43107.92 | 0 | 0 | 0 | 0 | 0 | 43107.92
2022083024 | 3 | 0.59907 | 47925.6 | 0.07102 | 2556.72 | 0 | 0 | 1 | 5000 | 2556.72 | 0 | 0 | 0 | 0 | 0 | 40368.88 | 0 | 0 | 0 | 0 | 0 | 40368.88
2022083101 | 4 | 0.56972 | 45577.6 | 0.06357 | 2288.52 | 0 | 0 | 1 | 5000 | 2288.52 | 0 | 0 | 0 | 0 | 0 | 38289.08 | 0 | 0 | 0 | 0 | 0 | 38289.08
2022083102 | 4 | 0.54844 | 43875.2 | 0.0511 | 1839.6 | 0 | 0 | 1 | 5000 | 1839.6 | 0 | 0 | 0 | 0 | 0 | 37035.6 | 0 | 0 | 0 | 0 | 0 | 37035.6
2022083103 | 4 | 0.53587 | 42869.6 | 0.04904 | 1765.44 | 0 | 0 | 1 | 5000 | 1765.44 | 0 | 0 | 0 | 0 | 0 | 36104.16 | 0 | 0 | 0 | 0 | 0 | 36104.16
2022083104 | 4 | 0.52864 | 42291.2 | 0.04043 | 1455.48 | 0 | 0 | 1 | 5000 | 1455.48 | 0 | 0 | 0 | 0 | 0 | 35835.72 | 0 | 0 | 0 | 0 | 0 | 35835.72
2022083105 | 4 | 0.5332 | 42656 | 0.03022 | 1087.92 | 0 | 0 | 1 | 5000 | 1087.92 | 0 | 0 | 0 | 0 | 0 | 36568.08 | 0 | 0 | 0 | 0 | 0 | 36568.08
2022083106 | 4 | 0.55128 | 44102.4 | 0.02705 | 973.8 | 0 | 0 | 1 | 5000 | 973.8 | 0 | 0 | 0 | 0 | 0 | 38128.6 | 0 | 0 | 0 | 0 | 0 | 38128.6
2022083107 | 4 | 0.58132 | 46505.6 | 0.02933 | 1055.88 | 0 | 0 | 1 | 5000 | 1055.88 | 0 | 0 | 0 | 0 | 0 | 40449.72 | 0 | 0 | 0 | 0 | 0 | 40449.72
2022083108 | 4 | 0.5885 | 47080 | 0.03718 | 1338.48 | 0.01794 | 215.28 | 1 | 5000 | 1338.48 | 215.28 | 0 | 0 | 0 | 0 | 40526.24 | 0 | 0 | 0 | 0 | 0 | 40526.24
2022083109 | 4 | 0.604 | 48320 | 0.0358 | 1288.8 | 0.13787 | 1654.44 | 1 | 5000 | 1288.8 | 1654.44 | 0 | 0 | 0 | 0 | 40376.76 | 0 | 0 | 0 | 0 | 0 | 40376.76
2022083110 | 4 | 0.63492 | 50793.6 | 0.03122 | 1123.92 | 0.243 | 2916 | 1 | 5000 | 1123.92 | 2916 | 0 | 0 | 0 | 0 | 41753.68 | 0 | 0 | 0 | 0 | 0 | 41753.68
2022083111 | 4 | 0.67475 | 53980 | 0.0481 | 1731.6 | 0.31005 | 3720.6 | 1 | 5000 | 1731.6 | 3720.6 | 0 | 0 | 0 | 0 | 43527.8 | 0 | 0 | 0 | 0 | 0 | 43527.8
2022083112 | 4 | 0.71638 | 57310.4 | 0.07097 | 2554.92 | 0.35103 | 4212.36 | 1 | 5000 | 2554.92 | 4212.36 | 0 | 0 | 0 | 0 | 45543.12 | 0 | 0 | 0 | 0 | 0 | 45543.12
2022083113 | 4 | 0.75107 | 60085.6 | 0.08334 | 3000.24 | 0.38365 | 4603.8 | 1 | 5000 | 3000.24 | 4603.8 | 0 | 0 | 0 | 0 | 47481.56 | 0 | 0 | 0 | 0 | 0 | 47481.56
2022083114 | 4 | 0.78252 | 62601.6 | 0.10575 | 3807 | 0.40452 | 4854.24 | 1 | 5000 | 3807 | 4854.24 | 0 | 0 | 0 | 0 | 48940.36 | 0 | 0 | 0 | 0 | 0 | 48940.36
2022083115 | 4 | 0.80244 | 64195.2 | 0.08644 | 3111.84 | 0.43334 | 5200.08 | 1 | 5000 | 3111.84 | 5200.08 | 0 | 0 | 0 | 0 | 50883.28 | 0 | 0 | 0 | 0 | 0 | 50883.28
2022083116 | 4 | 0.80779 | 64623.2 | 0.10249 | 3689.64 | 0.3928 | 4713.6 | 1 | 5000 | 3689.64 | 4713.6 | 0 | 0 | 0 | 0 | 51219.96 | 0 | 0 | 0 | 0 | 0 | 51219.96
2022083117 | 4 | 0.79852 | 63881.6 | 0.11447 | 4120.92 | 0.30433 | 3651.96 | 1 | 5000 | 4120.92 | 3651.96 | 0 | 0 | 0 | 0 | 51108.72 | 0 | 0 | 0 | 0 | 0 | 51108.72
2022083118 | 4 | 0.783 | 62640 | 0.13116 | 4721.76 | 0.19836 | 2380.32 | 1 | 5000 | 4721.76 | 2380.32 | 0 | 0 | 0 | 0 | 50537.92 | 0 | 0 | 0 | 0 | 0 | 50537.92
2022083119 | 4 | 0.76059 | 60847.2 | 0.13439 | 4838.04 | 0.12331 | 1479.72 | 1 | 5000 | 4838.04 | 1479.72 | 0 | 0 | 0 | 0 | 49529.44 | 0 | 0 | 0 | 0 | 0 | 49529.44
2022083120 | 4 | 0.73867 | 59093.6 | 0.11386 | 4098.96 | 0.02825 | 339 | 1 | 5000 | 4098.96 | 339 | 0 | 0 | 0 | 0 | 49655.64 | 0 | 0 | 0 | 0 | 0 | 49655.64
2022083121 | 4 | 0.72489 | 57991.2 | 0.09351 | 3366.36 | 6e-05 | 0.72 | 1 | 5000 | 3366.36 | 0.72 | 0 | 0 | 0 | 0 | 49624.12 | 0 | 0 | 0 | 0 | 0 | 49624.12
2022083122 | 4 | 0.69549 | 55639.2 | 0.08958 | 3224.88 | 0 | 0 | 1 | 5000 | 3224.88 | 0 | 0 | 0 | 0 | 0 | 47414.32 | 0 | 0 | 0 | 0 | 0 | 47414.32
2022083123 | 4 | 0.65145 | 52116 | 0.0857 | 3085.2 | 0 | 0 | 1 | 5000 | 3085.2 | 0 | 0 | 0 | 0 | 0 | 44030.8 | 0 | 0 | 0 | 0 | 0 | 44030.8
2022083124 | 4 | 0.60617 | 48493.6 | 0.09177 | 3303.72 | 0 | 0 | 1 | 5000 | 3303.72 | 0 | 0 | 0 | 0 | 0 | 40189.88 | 0 | 0 | 0 | 0 | 0 | 40189.88
2022090101 | 5 | 0.57241 | 45792.8 | 0.10358 | 3728.88 | 0 | 0 | 1 | 5000 | 3728.88 | 0 | 0 | 0 | 0 | 0 | 37063.92 | 0 | 0 | 0 | 0 | 0 | 37063.92
2022090102 | 5 | 0.54933 | 43946.4 | 0.08552 | 3078.72 | 0 | 0 | 1 | 5000 | 3078.72 | 0 | 0 | 0 | 0 | 0 | 35867.68 | 0 | 0 | 0 | 0 | 0 | 35867.68
2022090103 | 5 | 0.53219 | 42575.2 | 0.06626 | 2385.36 | 0 | 0 | 1 | 5000 | 2385.36 | 0 | 0 | 0 | 0 | 0 | 35189.84 | 0 | 0 | 0 | 0 | 0 | 35189.84
2022090104 | 5 | 0.52351 | 41880.8 | 0.04325 | 1557 | 0 | 0 | 1 | 5000 | 1557 | 0 | 0 | 0 | 0 | 0 | 35323.8 | 0 | 0 | 0 | 0 | 0 | 35323.8
2022090105 | 5 | 0.5242 | 41936 | 0.02252 | 810.72 | 0 | 0 | 1 | 5000 | 810.72 | 0 | 0 | 0 | 0 | 0 | 36125.28 | 0 | 0 | 0 | 0 | 0 | 36125.28
2022090106 | 5 | 0.53788 | 43030.4 | 0.01499 | 539.64 | 0 | 0 | 1 | 5000 | 539.64 | 0 | 0 | 0 | 0 | 0 | 37490.76 | 0 | 0 | 0 | 0 | 0 | 37490.76
2022090107 | 5 | 0.56602 | 45281.6 | 0.01833 | 659.88 | 0 | 0 | 1 | 5000 | 659.88 | 0 | 0 | 0 | 0 | 0 | 39621.72 | 0 | 0 | 0 | 0 | 0 | 39621.72
2022090108 | 5 | 0.57728 | 46182.4 | 0.0195 | 702 | 0.02064 | 247.68 | 1 | 5000 | 702 | 247.68 | 0 | 0 | 0 | 0 | 40232.72 | 0 | 0 | 0 | 0 | 0 | 40232.72
2022090109 | 5 | 0.5971 | 47768 | 0.0204 | 734.4 | 0.12866 | 1543.92 | 1 | 5000 | 734.4 | 1543.92 | 0 | 0 | 0 | 0 | 40489.68 | 0 | 0 | 0 | 0 | 0 | 40489.68
2022090110 | 5 | 0.63031 | 50424.8 | 0.02983 | 1073.88 | 0.24889 | 2986.68 | 1 | 5000 | 1073.88 | 2986.68 | 0 | 0 | 0 | 0 | 41364.24 | 0 | 0 | 0 | 0 | 0 | 41364.24
2022090111 | 5 | 0.67294 | 53835.2 | 0.03913 | 1408.68 | 0.32349 | 3881.88 | 1 | 5000 | 1408.68 | 3881.88 | 0 | 0 | 0 | 0 | 43544.64 | 0 | 0 | 0 | 0 | 0 | 43544.64
2022090112 | 5 | 0.71319 | 57055.2 | 0.06256 | 2252.16 | 0.36737 | 4408.44 | 1 | 5000 | 2252.16 | 4408.44 | 0 | 0 | 0 | 0 | 45394.6 | 0 | 0 | 0 | 0 | 0 | 45394.6
2022090113 | 5 | 0.74338 | 59470.4 | 0.09083 | 3269.88 | 0.39577 | 4749.24 | 1 | 5000 | 3269.88 | 4749.24 | 0 | 0 | 0 | 0 | 46451.28 | 0 | 0 | 0 | 0 | 0 | 46451.28
2022090114 | 5 | 0.77074 | 61659.2 | 0.09746 | 3508.56 | 0.39828 | 4779.36 | 1 | 5000 | 3508.56 | 4779.36 | 0 | 0 | 0 | 0 | 48371.28 | 0 | 0 | 0 | 0 | 0 | 48371.28
2022090115 | 5 | 0.7759 | 62072 | 0.10174 | 3662.64 | 0.38288 | 4594.56 | 1 | 5000 | 3662.64 | 4594.56 | 0 | 0 | 0 | 0 | 48814.8 | 0 | 0 | 0 | 0 | 0 | 48814.8
2022090116 | 5 | 0.7634 | 61072 | 0.11976 | 4311.36 | 0.33414 | 4009.68 | 1 | 5000 | 4311.36 | 4009.68 | 0 | 0 | 0 | 0 | 47750.96 | 0 | 0 | 0 | 0 | 0 | 47750.96
2022090117 | 5 | 0.75448 | 60358.4 | 0.14717 | 5298.12 | 0.30917 | 3710.04 | 1 | 5000 | 5298.12 | 3710.04 | 0 | 0 | 0 | 0 | 46350.24 | 0 | 0 | 0 | 0 | 0 | 46350.24
2022090118 | 5 | 0.7534 | 60272 | 0.16741 | 6026.76 | 0.23315 | 2797.8 | 1 | 5000 | 6026.76 | 2797.8 | 0 | 0 | 0 | 0 | 46447.44 | 0 | 0 | 0 | 0 | 0 | 46447.44
2022090119 | 5 | 0.7405 | 59240 | 0.15774 | 5678.64 | 0.13824 | 1658.88 | 1 | 5000 | 5678.64 | 1658.88 | 0 | 0 | 0 | 0 | 46902.48 | 0 | 0 | 0 | 0 | 0 | 46902.48
2022090120 | 5 | 0.72442 | 57953.6 | 0.15244 | 5487.84 | 0.0233 | 279.6 | 1 | 5000 | 5487.84 | 279.6 | 0 | 0 | 0 | 0 | 47186.16 | 0 | 0 | 0 | 0 | 0 | 47186.16
2022090121 | 5 | 0.71592 | 57273.6 | 0.16176 | 5823.36 | 0.00048 | 5.76 | 1 | 5000 | 5823.36 | 5.76 | 0 | 0 | 0 | 0 | 46444.48 | 0 | 0 | 0 | 0 | 0 | 46444.48
2022090122 | 5 | 0.68905 | 55124 | 0.18873 | 6794.28 | 8e-05 | 0.96 | 1 | 5000 | 6794.28 | 0.96 | 0 | 0 | 0 | 0 | 43328.76 | 0 | 0 | 0 | 0 | 0 | 43328.76
2022090123 | 5 | 0.64728 | 51782.4 | 0.17946 | 6460.56 | 8e-05 | 0.96 | 1 | 5000 | 6460.56 | 0.96 | 0 | 0 | 0 | 0 | 40320.88 | 0 | 0 | 0 | 0 | 0 | 40320.88
2022090124 | 5 | 0.60415 | 48332 | 0.17254 | 6211.44 | 9e-05 | 1.08 | 1 | 5000 | 6211.44 | 1.08 | 0 | 0 | 0 | 0 | 37119.48 | 0 | 0 | 0 | 0 | 0 | 37119.48
2022090201 | 6 | 0.57071 | 45656.8 | 0.16681 | 6005.16 | 9e-05 | 1.08 | 1 | 5000 | 6005.16 | 1.08 | 0 | 0 | 0 | 0 | 34650.56 | 0 | 0 | 0 | 0 | 0 | 34650.56
2022090202 | 6 | 0.54444 | 43555.2 | 0.17587 | 6331.32 | 0 | 0 | 1 | 5000 | 6331.32 | 0 | 0 | 0 | 0 | 0 | 32223.88 | 0 | 0 | 0 | 0 | 0 | 32223.88
2022090203 | 6 | 0.52792 | 42233.6 | 0.17452 | 6282.72 | 0 | 0 | 1 | 5000 | 6282.72 | 0 | 0 | 0 | 0 | 0 | 30950.88 | 0 | 0 | 0 | 0 | 0 | 30950.88
2022090204 | 6 | 0.51906 | 41524.8 | 0.16978 | 6112.08 | 0 | 0 | 1 | 5000 | 6112.08 | 0 | 0 | 0 | 0 | 0 | 30412.72 | 0 | 0 | 0 | 0 | 0 | 30412.72
2022090205 | 6 | 0.51925 | 41540 | 0.16124 | 5804.64 | 0 | 0 | 1 | 5000 | 5804.64 | 0 | 0 | 0 | 0 | 0 | 30735.36 | 0 | 0 | 0 | 0 | 0 | 30735.36
2022090206 | 6 | 0.53804 | 43043.2 | 0.1463 | 5266.8 | 0 | 0 | 1 | 5000 | 5266.8 | 0 | 0 | 0 | 0 | 0 | 32776.4 | 0 | 0 | 0 | 0 | 0 | 32776.4
2022090207 | 6 | 0.5632 | 45056 | 0.13905 | 5005.8 | 0 | 0 | 1 | 5000 | 5005.8 | 0 | 0 | 0 | 0 | 0 | 35050.2 | 0 | 0 | 0 | 0 | 0 | 35050.2
2022090208 | 6 | 0.57257 | 45805.6 | 0.1259 | 4532.4 | 0.01622 | 194.64 | 1 | 5000 | 4532.4 | 194.64 | 0 | 0 | 0 | 0 | 36078.56 | 0 | 0 | 0 | 0 | 0 | 36078.56
2022090209 | 6 | 0.58875 | 47100 | 0.08938 | 3217.68 | 0.15928 | 1911.36 | 1 | 5000 | 3217.68 | 1911.36 | 0 | 0 | 0 | 0 | 36970.96 | 0 | 0 | 0 | 0 | 0 | 36970.96
2022090210 | 6 | 0.61998 | 49598.4 | 0.05943 | 2139.48 | 0.30083 | 3609.96 | 1 | 5000 | 2139.48 | 3609.96 | 0 | 0 | 0 | 0 | 38848.96 | 0 | 0 | 0 | 0 | 0 | 38848.96
2022090211 | 6 | 0.65695 | 52556 | 0.06947 | 2500.92 | 0.37473 | 4496.76 | 1 | 5000 | 2500.92 | 4496.76 | 0 | 0 | 0 | 0 | 40558.32 | 0 | 0 | 0 | 0 | 0 | 40558.32
2022090212 | 6 | 0.69186 | 55348.8 | 0.08276 | 2979.36 | 0.47101 | 5652.12 | 1 | 5000 | 2979.36 | 5652.12 | 0 | 0 | 0 | 0 | 41717.32 | 0 | 0 | 0 | 0 | 0 | 41717.32
2022090213 | 6 | 0.72565 | 58052 | 0.07727 | 2781.72 | 0.57175 | 6861 | 1 | 5000 | 2781.72 | 6861 | 0 | 0 | 0 | 0 | 43409.28 | 0 | 0 | 0 | 0 | 0 | 43409.28
2022090214 | 6 | 0.75444 | 60355.2 | 0.08517 | 3066.12 | 0.57236 | 6868.32 | 1 | 5000 | 3066.12 | 6868.32 | 0 | 0 | 0 | 0 | 45420.76 | 0 | 0 | 0 | 0 | 0 | 45420.76
2022090215 | 6 | 0.7686 | 61488 | 0.08849 | 3185.64 | 0.51958 | 6234.96 | 1 | 5000 | 3185.64 | 6234.96 | 0 | 0 | 0 | 0 | 47067.4 | 0 | 0 | 0 | 0 | 0 | 47067.4
2022090216 | 6 | 0.76711 | 61368.8 | 0.09722 | 3499.92 | 0.41499 | 4979.88 | 1 | 5000 | 3499.92 | 4979.88 | 0 | 0 | 0 | 0 | 47889 | 0 | 0 | 0 | 0 | 0 | 47889
2022090217 | 6 | 0.76537 | 61229.6 | 0.13116 | 4721.76 | 0.37047 | 4445.64 | 1 | 5000 | 4721.76 | 4445.64 | 0 | 0 | 0 | 0 | 47062.2 | 0 | 0 | 0 | 0 | 0 | 47062.2
2022090218 | 6 | 0.7639 | 61112 | 0.17024 | 6128.64 | 0.36006 | 4320.72 | 1 | 5000 | 6128.64 | 4320.72 | 0 | 0 | 0 | 0 | 45662.64 | 0 | 0 | 0 | 0 | 0 | 45662.64
2022090219 | 6 | 0.74753 | 59802.4 | 0.20518 | 7386.48 | 0.22193 | 2663.16 | 1 | 5000 | 7386.48 | 2663.16 | 0 | 0 | 0 | 0 | 44752.76 | 0 | 0 | 0 | 0 | 0 | 44752.76
2022090220 | 6 | 0.72287 | 57829.6 | 0.20117 | 7242.12 | 0.04235 | 508.2 | 1 | 5000 | 7242.12 | 508.2 | 0 | 0 | 0 | 0 | 45079.28 | 0 | 0 | 0 | 0 | 0 | 45079.28
2022090221 | 6 | 0.70564 | 56451.2 | 0.19437 | 6997.32 | 0.0004 | 4.8 | 1 | 5000 | 6997.32 | 4.8 | 0 | 0 | 0 | 0 | 44449.08 | 0 | 0 | 0 | 0 | 0 | 44449.08
2022090222 | 6 | 0.67963 | 54370.4 | 0.2039 | 7340.4 | 0 | 0 | 1 | 5000 | 7340.4 | 0 | 0 | 0 | 0 | 0 | 42030 | 0 | 0 | 0 | 0 | 0 | 42030
2022090223 | 6 | 0.64757 | 51805.6 | 0.20709 | 7455.24 | 0 | 0 | 1 | 5000 | 7455.24 | 0 | 0 | 0 | 0 | 0 | 39350.36 | 0 | 0 | 0 | 0 | 0 | 39350.36
2022090224 | 6 | 0.61072 | 48857.6 | 0.21486 | 7734.96 | 0 | 0 | 1 | 5000 | 7734.96 | 0 | 0 | 0 | 0 | 0 | 36122.64 | 0 | 0 | 0 | 0 | 0 | 36122.64
2022090301 | 7 | 0.57815 | 46252 | 0.17861 | 6429.96 | 0 | 0 | 1 | 5000 | 6429.96 | 0 | 0 | 0 | 0 | 0 | 34822.04 | 0 | 0 | 0 | 0 | 0 | 34822.04
2022090302 | 7 | 0.55395 | 44316 | 0.13891 | 5000.76 | 0 | 0 | 1 | 5000 | 5000.76 | 0 | 0 | 0 | 0 | 0 | 34315.24 | 0 | 0 | 0 | 0 | 0 | 34315.24
2022090303 | 7 | 0.53501 | 42800.8 | 0.12485 | 4494.6 | 0 | 0 | 1 | 5000 | 4494.6 | 0 | 0 | 0 | 0 | 0 | 33306.2 | 0 | 0 | 0 | 0 | 0 | 33306.2
2022090304 | 7 | 0.52344 | 41875.2 | 0.09762 | 3514.32 | 0 | 0 | 1 | 5000 | 3514.32 | 0 | 0 | 0 | 0 | 0 | 33360.88 | 0 | 0 | 0 | 0 | 0 | 33360.88
2022090305 | 7 | 0.51869 | 41495.2 | 0.06795 | 2446.2 | 0 | 0 | 1 | 5000 | 2446.2 | 0 | 0 | 0 | 0 | 0 | 34049 | 0 | 0 | 0 | 0 | 0 | 34049
2022090306 | 7 | 0.51648 | 41318.4 | 0.05843 | 2103.48 | 0 | 0 | 1 | 5000 | 2103.48 | 0 | 0 | 0 | 0 | 0 | 34214.92 | 0 | 0 | 0 | 0 | 0 | 34214.92
2022090307 | 7 | 0.52061 | 41648.8 | 0.0597 | 2149.2 | 0 | 0 | 1 | 5000 | 2149.2 | 0 | 0 | 0 | 0 | 0 | 34499.6 | 0 | 0 | 0 | 0 | 0 | 34499.6
2022090308 | 7 | 0.52644 | 42115.2 | 0.05546 | 1996.56 | 0.01921 | 230.52 | 1 | 5000 | 1996.56 | 230.52 | 0 | 0 | 0 | 0 | 34888.12 | 0 | 0 | 0 | 0 | 0 | 34888.12
2022090309 | 7 | 0.55653 | 44522.4 | 0.0629 | 2264.4 | 0.19244 | 2309.28 | 1 | 5000 | 2264.4 | 2309.28 | 0 | 0 | 0 | 0 | 34948.72 | 0 | 0 | 0 | 0 | 0 | 34948.72
2022090310 | 7 | 0.59524 | 47619.2 | 0.04876 | 1755.36 | 0.39507 | 4740.84 | 1 | 5000 | 1755.36 | 4740.84 | 0 | 0 | 0 | 0 | 36123 | 0 | 0 | 0 | 0 | 0 | 36123
2022090311 | 7 | 0.64232 | 51385.6 | 0.0542 | 1951.2 | 0.5099 | 6118.8 | 1 | 5000 | 1951.2 | 6118.8 | 0 | 0 | 0 | 0 | 38315.6 | 0 | 0 | 0 | 0 | 0 | 38315.6
2022090312 | 7 | 0.68624 | 54899.2 | 0.05826 | 2097.36 | 0.63373 | 7604.76 | 1 | 5000 | 2097.36 | 7604.76 | 0 | 0 | 0 | 0 | 40197.08 | 0 | 0 | 0 | 0 | 0 | 40197.08
2022090313 | 7 | 0.71966 | 57572.8 | 0.06148 | 2213.28 | 0.63094 | 7571.28 | 1 | 5000 | 2213.28 | 7571.28 | 0 | 0 | 0 | 0 | 42788.24 | 0 | 0 | 0 | 0 | 0 | 42788.24
2022090314 | 7 | 0.74486 | 59588.8 | 0.07975 | 2871 | 0.62519 | 7502.28 | 1 | 5000 | 2871 | 7502.28 | 0 | 0 | 0 | 0 | 44215.52 | 0 | 0 | 0 | 0 | 0 | 44215.52
2022090315 | 7 | 0.75481 | 60384.8 | 0.09757 | 3512.52 | 0.59751 | 7170.12 | 1 | 5000 | 3512.52 | 7170.12 | 0 | 0 | 0 | 0 | 44702.16 | 0 | 0 | 0 | 0 | 0 | 44702.16
2022090316 | 7 | 0.75721 | 60576.8 | 0.10724 | 3860.64 | 0.5546 | 6655.2 | 1 | 5000 | 3860.64 | 6655.2 | 0 | 0 | 0 | 0 | 45060.96 | 0 | 0 | 0 | 0 | 0 | 45060.96
2022090317 | 7 | 0.75072 | 60057.6 | 0.11309 | 4071.24 | 0.50095 | 6011.4 | 1 | 5000 | 4071.24 | 6011.4 | 0 | 0 | 0 | 0 | 44974.96 | 0 | 0 | 0 | 0 | 0 | 44974.96
2022090318 | 7 | 0.72873 | 58298.4 | 0.1199 | 4316.4 | 0.41002 | 4920.24 | 1 | 5000 | 4316.4 | 4920.24 | 0 | 0 | 0 | 0 | 44061.76 | 0 | 0 | 0 | 0 | 0 | 44061.76
2022090319 | 7 | 0.69989 | 55991.2 | 0.11827 | 4257.72 | 0.26288 | 3154.56 | 1 | 5000 | 4257.72 | 3154.56 | 0 | 0 | 0 | 0 | 43578.92 | 0 | 0 | 0 | 0 | 0 | 43578.92
2022090320 | 7 | 0.67787 | 54229.6 | 0.08251 | 2970.36 | 0.06515 | 781.8 | 1 | 5000 | 2970.36 | 781.8 | 0 | 0 | 0 | 0 | 45477.44 | 0 | 0 | 0 | 0 | 0 | 45477.44
2022090321 | 7 | 0.6617 | 52936 | 0.07366 | 2651.76 | 0.00014 | 1.68 | 1 | 5000 | 2651.76 | 1.68 | 0 | 0 | 0 | 0 | 45282.56 | 0 | 0 | 0 | 0 | 0 | 45282.56
2022090322 | 7 | 0.63938 | 51150.4 | 0.09239 | 3326.04 | 0 | 0 | 1 | 5000 | 3326.04 | 0 | 0 | 0 | 0 | 0 | 42824.36 | 0 | 0 | 0 | 0 | 0 | 42824.36
2022090323 | 7 | 0.6097 | 48776 | 0.10117 | 3642.12 | 0 | 0 | 1 | 5000 | 3642.12 | 0 | 0 | 0 | 0 | 0 | 40133.88 | 0 | 0 | 0 | 0 | 0 | 40133.88
2022090324 | 7 | 0.57712 | 46169.6 | 0.09756 | 3512.16 | 0 | 0 | 1 | 5000 | 3512.16 | 0 | 0 | 0 | 0 | 0 | 37657.44 | 0 | 0 | 0 | 0 | 0 | 37657.44
2022090401 | 1 | 0.54685 | 43748 | 0.10442 | 3759.12 | 0 | 0 | 1 | 5000 | 3759.12 | 0 | 0 | 0 | 0 | 0 | 34988.88 | 0 | 0 | 0 | 0 | 0 | 34988.88
2022090402 | 1 | 0.52442 | 41953.6 | 0.11682 | 4205.52 | 0 | 0 | 1 | 5000 | 4205.52 | 0 | 0 | 0 | 0 | 0 | 32748.08 | 0 | 0 | 0 | 0 | 0 | 32748.08
2022090403 | 1 | 0.50641 | 40512.8 | 0.13725 | 4941 | 0 | 0 | 1 | 5000 | 4941 | 0 | 0 | 0 | 0 | 0 | 30571.8 | 0 | 0 | 0 | 0 | 0 | 30571.8
2022090404 | 1 | 0.49385 | 39508 | 0.1222 | 4399.2 | 0 | 0 | 1 | 5000 | 4399.2 | 0 | 0 | 0 | 0 | 0 | 30108.8 | 0 | 0 | 0 | 0 | 0 | 30108.8
2022090405 | 1 | 0.487 | 38960 | 0.09141 | 3290.76 | 0 | 0 | 1 | 5000 | 3290.76 | 0 | 0 | 0 | 0 | 0 | 30669.24 | 0 | 0 | 0 | 0 | 0 | 30669.24
2022090406 | 1 | 0.48655 | 38924 | 0.0833 | 2998.8 | 0 | 0 | 1 | 5000 | 2998.8 | 0 | 0 | 0 | 0 | 0 | 30925.2 | 0 | 0 | 0 | 0 | 0 | 30925.2
2022090407 | 1 | 0.48841 | 39072.8 | 0.08424 | 3032.64 | 0 | 0 | 1 | 5000 | 3032.64 | 0 | 0 | 0 | 0 | 0 | 31040.16 | 0 | 0 | 0 | 0 | 0 | 31040.16
2022090408 | 1 | 0.49187 | 39349.6 | 0.08099 | 2915.64 | 0.02452 | 294.24 | 1 | 5000 | 2915.64 | 294.24 | 0 | 0 | 0 | 0 | 31139.72 | 0 | 0 | 0 | 0 | 0 | 31139.72
2022090409 | 1 | 0.51427 | 41141.6 | 0.05799 | 2087.64 | 0.30457 | 3654.84 | 1 | 5000 | 2087.64 | 3654.84 | 0 | 0 | 0 | 0 | 30399.12 | 0 | 0 | 0 | 0 | 0 | 30399.12
2022090410 | 1 | 0.5509 | 44072 | 0.02739 | 986.04 | 0.57071 | 6848.52 | 1 | 5000 | 986.04 | 6848.52 | 0 | 0 | 0 | 0 | 31237.44 | 0 | 0 | 0 | 0 | 0 | 31237.44
2022090411 | 1 | 0.58917 | 47133.6 | 0.0168 | 604.8 | 0.64973 | 7796.76 | 1 | 5000 | 604.8 | 7796.76 | 0 | 0 | 0 | 0 | 33732.04 | 0 | 0 | 0 | 0 | 0 | 33732.04
2022090412 | 1 | 0.62912 | 50329.6 | 0.01583 | 569.88 | 0.67847 | 8141.64 | 1 | 5000 | 569.88 | 8141.64 | 0 | 0 | 0 | 0 | 36618.08 | 0 | 0 | 0 | 0 | 0 | 36618.08
2022090413 | 1 | 0.67096 | 53676.8 | 0.02619 | 942.84 | 0.64468 | 7736.16 | 1 | 5000 | 942.84 | 7736.16 | 0 | 0 | 0 | 0 | 39997.8 | 0 | 0 | 0 | 0 | 0 | 39997.8
2022090414 | 1 | 0.70287 | 56229.6 | 0.03361 | 1209.96 | 0.62627 | 7515.24 | 1 | 5000 | 1209.96 | 7515.24 | 0 | 0 | 0 | 0 | 42504.4 | 0 | 0 | 0 | 0 | 0 | 42504.4
2022090415 | 1 | 0.71687 | 57349.6 | 0.03736 | 1344.96 | 0.5974 | 7168.8 | 1 | 5000 | 1344.96 | 7168.8 | 0 | 0 | 0 | 0 | 43835.84 | 0 | 0 | 0 | 0 | 0 | 43835.84
2022090416 | 1 | 0.69652 | 55721.6 | 0.062 | 2232 | 0.59058 | 7086.96 | 1 | 5000 | 2232 | 7086.96 | 0 | 0 | 0 | 0 | 41402.64 | 0 | 0 | 0 | 0 | 0 | 41402.64
2022090417 | 1 | 0.68182 | 54545.6 | 0.07816 | 2813.76 | 0.52055 | 6246.6 | 1 | 5000 | 2813.76 | 6246.6 | 0 | 0 | 0 | 0 | 40485.24 | 0 | 0 | 0 | 0 | 0 | 40485.24
2022090418 | 1 | 0.6727 | 53816 | 0.11215 | 4037.4 | 0.47481 | 5697.72 | 1 | 5000 | 4037.4 | 5697.72 | 0 | 0 | 0 | 0 | 39080.88 | 0 | 0 | 0 | 0 | 0 | 39080.88
2022090419 | 1 | 0.65652 | 52521.6 | 0.15639 | 5630.04 | 0.34551 | 4146.12 | 1 | 5000 | 5630.04 | 4146.12 | 0 | 0 | 0 | 0 | 37745.44 | 0 | 0 | 0 | 0 | 0 | 37745.44
2022090420 | 1 | 0.64251 | 51400.8 | 0.16682 | 6005.52 | 0.08824 | 1058.88 | 1 | 5000 | 6005.52 | 1058.88 | 0 | 0 | 0 | 0 | 39336.4 | 0 | 0 | 0 | 0 | 0 | 39336.4
2022090421 | 1 | 0.63194 | 50555.2 | 0.18213 | 6556.68 | 0.00031 | 3.72 | 1 | 5000 | 6556.68 | 3.72 | 0 | 0 | 0 | 0 | 38994.8 | 0 | 0 | 0 | 0 | 0 | 38994.8
2022090422 | 1 | 0.61047 | 48837.6 | 0.16667 | 6000.12 | 0 | 0 | 1 | 5000 | 6000.12 | 0 | 0 | 0 | 0 | 0 | 37837.48 | 0 | 0 | 0 | 0 | 0 | 37837.48
2022090423 | 1 | 0.58326 | 46660.8 | 0.18074 | 6506.64 | 0 | 0 | 1 | 5000 | 6506.64 | 0 | 0 | 0 | 0 | 0 | 35154.16 | 0 | 0 | 0 | 0 | 0 | 35154.16
2022090424 | 1 | 0.55194 | 44155.2 | 0.22706 | 8174.16 | 0 | 0 | 1 | 5000 | 8174.16 | 0 | 0 | 0 | 0 | 0 | 30981.04 | 0 | 0 | 0 | 0 | 0 | 30981.04
2022090501 | 2 | 0.52357 | 41885.6 | 0.2541 | 9147.6 | 0 | 0 | 1 | 5000 | 9147.6 | 0 | 0 | 0 | 0 | 0 | 27738 | 0 | 0 | 0 | 0 | 0 | 27738
2022090502 | 2 | 0.50117 | 40093.6 | 0.24512 | 8824.32 | 0 | 0 | 1 | 5000 | 8824.32 | 0 | 0 | 0 | 0 | 0 | 26269.28 | 0 | 0 | 0 | 0 | 0 | 26269.28
2022090503 | 2 | 0.48515 | 38812 | 0.23799 | 8567.64 | 0 | 0 | 1 | 5000 | 8567.64 | 0 | 0 | 0 | 0 | 0 | 25244.36 | 0 | 0 | 0 | 0 | 0 | 25244.36
2022090504 | 2 | 0.47564 | 38051.2 | 0.22438 | 8077.68 | 0 | 0 | 1 | 5000 | 8077.68 | 0 | 0 | 0 | 0 | 0 | 24973.52 | 0 | 0 | 0 | 0 | 0 | 24973.52
2022090505 | 2 | 0.47364 | 37891.2 | 0.20465 | 7367.4 | 0 | 0 | 1 | 5000 | 7367.4 | 0 | 0 | 0 | 0 | 0 | 25523.8 | 0 | 0 | 0 | 0 | 0 | 25523.8
2022090506 | 2 | 0.48005 | 38404 | 0.18578 | 6688.08 | 0 | 0 | 1 | 5000 | 6688.08 | 0 | 0 | 0 | 0 | 0 | 26715.92 | 0 | 0 | 0 | 0 | 0 | 26715.92
2022090507 | 2 | 0.48285 | 38628 | 0.16475 | 5931 | 0 | 0 | 1 | 5000 | 5931 | 0 | 0 | 0 | 0 | 0 | 27697 | 0 | 0 | 0 | 0 | 0 | 27697
2022090508 | 2 | 0.48286 | 38628.8 | 0.13589 | 4892.04 | 0.02346 | 281.52 | 1 | 5000 | 4892.04 | 281.52 | 0 | 0 | 0 | 0 | 28455.24 | 0 | 0 | 0 | 0 | 0 | 28455.24
2022090509 | 2 | 0.50327 | 40261.6 | 0.10549 | 3797.64 | 0.30458 | 3654.96 | 1 | 5000 | 3797.64 | 3654.96 | 0 | 0 | 0 | 0 | 27809 | 0 | 0 | 0 | 0 | 0 | 27809
2022090510 | 2 | 0.54072 | 43257.6 | 0.05155 | 1855.8 | 0.58302 | 6996.24 | 1 | 5000 | 1855.8 | 6996.24 | 0 | 0 | 0 | 0 | 29405.56 | 0 | 0 | 0 | 0 | 0 | 29405.56
2022090511 | 2 | 0.58345 | 46676 | 0.05124 | 1844.64 | 0.67375 | 8085 | 1 | 5000 | 1844.64 | 8085 | 0 | 0 | 0 | 0 | 31746.36 | 0 | 0 | 0 | 0 | 0 | 31746.36
2022090512 | 2 | 0.62773 | 50218.4 | 0.04522 | 1627.92 | 0.7007 | 8408.4 | 1 | 5000 | 1627.92 | 8408.4 | 0 | 0 | 0 | 0 | 35182.08 | 0 | 0 | 0 | 0 | 0 | 35182.08
2022090513 | 2 | 0.67348 | 53878.4 | 0.03538 | 1273.68 | 0.7011 | 8413.2 | 1 | 5000 | 1273.68 | 8413.2 | 0 | 0 | 0 | 0 | 39191.52 | 0 | 0 | 0 | 0 | 0 | 39191.52
2022090514 | 2 | 0.71446 | 57156.8 | 0.03622 | 1303.92 | 0.70092 | 8411.04 | 1 | 5000 | 1303.92 | 8411.04 | 0 | 0 | 0 | 0 | 42441.84 | 0 | 0 | 0 | 0 | 0 | 42441.84
2022090515 | 2 | 0.74785 | 59828 | 0.04235 | 1524.6 | 0.67485 | 8098.2 | 1 | 5000 | 1524.6 | 8098.2 | 0 | 0 | 0 | 0 | 45205.2 | 0 | 0 | 0 | 0 | 0 | 45205.2
2022090516 | 2 | 0.77185 | 61748 | 0.07319 | 2634.84 | 0.64458 | 7734.96 | 1 | 5000 | 2634.84 | 7734.96 | 0 | 0 | 0 | 0 | 46378.2 | 0 | 0 | 0 | 0 | 0 | 46378.2
2022090517 | 2 | 0.7863 | 62904 | 0.1091 | 3927.6 | 0.56929 | 6831.48 | 1 | 5000 | 3927.6 | 6831.48 | 0 | 0 | 0 | 0 | 47144.92 | 0 | 0 | 0 | 0 | 0 | 47144.92
2022090518 | 2 | 0.78764 | 63011.2 | 0.12083 | 4349.88 | 0.56247 | 6749.64 | 1 | 5000 | 4349.88 | 6749.64 | 0 | 0 | 0 | 0 | 46911.68 | 0 | 0 | 0 | 0 | 0 | 46911.68
2022090519 | 2 | 0.77215 | 61772 | 0.14097 | 5074.92 | 0.40882 | 4905.84 | 1 | 5000 | 5074.92 | 4905.84 | 0 | 0 | 0 | 0 | 46791.24 | 0 | 0 | 0 | 0 | 0 | 46791.24
2022090520 | 2 | 0.74169 | 59335.2 | 0.14602 | 5256.72 | 0.09706 | 1164.72 | 1 | 5000 | 5256.72 | 1164.72 | 0 | 0 | 0 | 0 | 47913.76 | 0 | 0 | 0 | 0 | 0 | 47913.76
2022090521 | 2 | 0.72035 | 57628 | 0.17155 | 6175.8 | 0.00028 | 3.36 | 1 | 5000 | 6175.8 | 3.36 | 0 | 0 | 0 | 0 | 46448.84 | 0 | 0 | 0 | 0 | 0 | 46448.84
2022090522 | 2 | 0.68678 | 54942.4 | 0.1934 | 6962.4 | 0 | 0 | 1 | 5000 | 6962.4 | 0 | 0 | 0 | 0 | 0 | 42980 | 0 | 0 | 0 | 0 | 0 | 42980
2022090523 | 2 | 0.63735 | 50988 | 0.22151 | 7974.36 | 0 | 0 | 1 | 5000 | 7974.36 | 0 | 0 | 0 | 0 | 0 | 38013.64 | 0 | 0 | 0 | 0 | 0 | 38013.64
2022090524 | 2 | 0.58989 | 47191.2 | 0.23318 | 8394.48 | 0 | 0 | 1 | 5000 | 8394.48 | 0 | 0 | 0 | 0 | 0 | 33796.72 | 0 | 0 | 0 | 0 | 0 | 33796.72
2022090601 | 3 | 0.55235 | 44188 | 0.23282 | 8381.52 | 0 | 0 | 1 | 5000 | 8381.52 | 0 | 0 | 0 | 0 | 0 | 30806.48 | 0 | 0 | 0 | 0 | 0 | 30806.48
2022090602 | 3 | 0.52735 | 42188 | 0.21604 | 7777.44 | 0 | 0 | 1 | 5000 | 7777.44 | 0 | 0 | 0 | 0 | 0 | 29410.56 | 0 | 0 | 0 | 0 | 0 | 29410.56
2022090603 | 3 | 0.51043 | 40834.4 | 0.22174 | 7982.64 | 0 | 0 | 1 | 5000 | 7982.64 | 0 | 0 | 0 | 0 | 0 | 27851.76 | 0 | 0 | 0 | 0 | 0 | 27851.76
2022090604 | 3 | 0.50239 | 40191.2 | 0.20055 | 7219.8 | 0 | 0 | 1 | 5000 | 7219.8 | 0 | 0 | 0 | 0 | 0 | 27971.4 | 0 | 0 | 0 | 0 | 0 | 27971.4
2022090605 | 3 | 0.50454 | 40363.2 | 0.18249 | 6569.64 | 0 | 0 | 1 | 5000 | 6569.64 | 0 | 0 | 0 | 0 | 0 | 28793.56 | 0 | 0 | 0 | 0 | 0 | 28793.56
2022090606 | 3 | 0.52291 | 41832.8 | 0.16083 | 5789.88 | 0 | 0 | 1 | 5000 | 5789.88 | 0 | 0 | 0 | 0 | 0 | 31042.92 | 0 | 0 | 0 | 0 | 0 | 31042.92
2022090607 | 3 | 0.54994 | 43995.2 | 0.15141 | 5450.76 | 0 | 0 | 1 | 5000 | 5450.76 | 0 | 0 | 0 | 0 | 0 | 33544.44 | 0 | 0 | 0 | 0 | 0 | 33544.44
2022090608 | 3 | 0.56111 | 44888.8 | 0.13244 | 4767.84 | 0.02727 | 327.24 | 1 | 5000 | 4767.84 | 327.24 | 0 | 0 | 0 | 0 | 34793.72 | 0 | 0 | 0 | 0 | 0 | 34793.72
2022090609 | 3 | 0.58165 | 46532 | 0.09477 | 3411.72 | 0.34884 | 4186.08 | 1 | 5000 | 3411.72 | 4186.08 | 0 | 0 | 0 | 0 | 33934.2 | 0 | 0 | 0 | 0 | 0 | 33934.2
2022090610 | 3 | 0.61644 | 49315.2 | 0.05462 | 1966.32 | 0.62698 | 7523.76 | 1 | 5000 | 1966.32 | 7523.76 | 0 | 0 | 0 | 0 | 34825.12 | 0 | 0 | 0 | 0 | 0 | 34825.12
2022090611 | 3 | 0.65648 | 52518.4 | 0.04615 | 1661.4 | 0.67039 | 8044.68 | 1 | 5000 | 1661.4 | 8044.68 | 0 | 0 | 0 | 0 | 37812.32 | 0 | 0 | 0 | 0 | 0 | 37812.32
2022090612 | 3 | 0.70003 | 56002.4 | 0.03692 | 1329.12 | 0.6917 | 8300.4 | 1 | 5000 | 1329.12 | 8300.4 | 0 | 0 | 0 | 0 | 41372.88 | 0 | 0 | 0 | 0 | 0 | 41372.88
2022090613 | 3 | 0.74754 | 59803.2 | 0.02768 | 996.48 | 0.71918 | 8630.16 | 1 | 5000 | 996.48 | 8630.16 | 0 | 0 | 0 | 0 | 45176.56 | 0 | 0 | 0 | 0 | 0 | 45176.56
2022090614 | 3 | 0.78768 | 63014.4 | 0.02606 | 938.16 | 0.71616 | 8593.92 | 1 | 5000 | 938.16 | 8593.92 | 0 | 0 | 0 | 0 | 48482.32 | 0 | 0 | 0 | 0 | 0 | 48482.32
2022090615 | 3 | 0.81583 | 65266.4 | 0.04401 | 1584.36 | 0.68886 | 8266.32 | 1 | 5000 | 1584.36 | 8266.32 | 0 | 0 | 0 | 0 | 50415.72 | 0 | 0 | 0 | 0 | 0 | 50415.72
2022090616 | 3 | 0.8292 | 66336 | 0.06061 | 2181.96 | 0.66021 | 7922.52 | 1 | 5000 | 2181.96 | 7922.52 | 0 | 0 | 0 | 0 | 51231.52 | 0 | 0 | 0 | 0 | 0 | 51231.52
2022090617 | 3 | 0.83625 | 66900 | 0.07245 | 2608.2 | 0.65068 | 7808.16 | 1 | 5000 | 2608.2 | 7808.16 | 0 | 0 | 0 | 0 | 51483.64 | 0 | 0 | 0 | 0 | 0 | 51483.64
2022090618 | 3 | 0.83361 | 66688.8 | 0.09184 | 3306.24 | 0.59056 | 7086.72 | 1 | 5000 | 3306.24 | 7086.72 | 0 | 0 | 0 | 0 | 51295.84 | 0 | 0 | 0 | 0 | 0 | 51295.84
2022090619 | 3 | 0.81641 | 65312.8 | 0.10331 | 3719.16 | 0.38952 | 4674.24 | 1 | 5000 | 3719.16 | 4674.24 | 0 | 0 | 0 | 0 | 51919.4 | 0 | 0 | 0 | 0 | 0 | 51919.4
2022090620 | 3 | 0.78146 | 62516.8 | 0.10556 | 3800.16 | 0.08495 | 1019.4 | 1 | 5000 | 3800.16 | 1019.4 | 0 | 0 | 0 | 0 | 52697.24 | 0 | 0 | 0 | 0 | 0 | 52697.24
2022090621 | 3 | 0.76347 | 61077.6 | 0.12343 | 4443.48 | 0.00016 | 1.92 | 1 | 5000 | 4443.48 | 1.92 | 0 | 0 | 0 | 0 | 51632.2 | 0 | 0 | 0 | 0 | 0 | 51632.2
2022090622 | 3 | 0.72862 | 58289.6 | 0.15352 | 5526.72 | 0 | 0 | 1 | 5000 | 5526.72 | 0 | 0 | 0 | 0 | 0 | 47762.88 | 0 | 0 | 0 | 0 | 0 | 47762.88
2022090623 | 3 | 0.67836 | 54268.8 | 0.1898 | 6832.8 | 0 | 0 | 1 | 5000 | 6832.8 | 0 | 0 | 0 | 0 | 0 | 42436 | 0 | 0 | 0 | 0 | 0 | 42436
2022090624 | 3 | 0.62634 | 50107.2 | 0.182 | 6552 | 0 | 0 | 1 | 5000 | 6552 | 0 | 0 | 0 | 0 | 0 | 38555.2 | 0 | 0 | 0 | 0 | 0 | 38555.2
2022090701 | 4 | 0.58441 | 46752.8 | 0.16465 | 5927.4 | 0 | 0 | 1 | 5000 | 5927.4 | 0 | 0 | 0 | 0 | 0 | 35825.4 | 0 | 0 | 0 | 0 | 0 | 35825.4
2022090702 | 4 | 0.55638 | 44510.4 | 0.15133 | 5447.88 | 0 | 0 | 1 | 5000 | 5447.88 | 0 | 0 | 0 | 0 | 0 | 34062.52 | 0 | 0 | 0 | 0 | 0 | 34062.52
2022090703 | 4 | 0.53786 | 43028.8 | 0.11822 | 4255.92 | 0 | 0 | 1 | 5000 | 4255.92 | 0 | 0 | 0 | 0 | 0 | 33772.88 | 0 | 0 | 0 | 0 | 0 | 33772.88
2022090704 | 4 | 0.52678 | 42142.4 | 0.09112 | 3280.32 | 0 | 0 | 1 | 5000 | 3280.32 | 0 | 0 | 0 | 0 | 0 | 33862.08 | 0 | 0 | 0 | 0 | 0 | 33862.08
2022090705 | 4 | 0.52491 | 41992.8 | 0.07893 | 2841.48 | 0 | 0 | 1 | 5000 | 2841.48 | 0 | 0 | 0 | 0 | 0 | 34151.32 | 0 | 0 | 0 | 0 | 0 | 34151.32
2022090706 | 4 | 0.54023 | 43218.4 | 0.07096 | 2554.56 | 0 | 0 | 1 | 5000 | 2554.56 | 0 | 0 | 0 | 0 | 0 | 35663.84 | 0 | 0 | 0 | 0 | 0 | 35663.84
2022090707 | 4 | 0.56446 | 45156.8 | 0.07197 | 2590.92 | 0 | 0 | 1 | 5000 | 2590.92 | 0 | 0 | 0 | 0 | 0 | 37565.88 | 0 | 0 | 0 | 0 | 0 | 37565.88
2022090708 | 4 | 0.57162 | 45729.6 | 0.0779 | 2804.4 | 0.0261 | 313.2 | 1 | 5000 | 2804.4 | 313.2 | 0 | 0 | 0 | 0 | 37612 | 0 | 0 | 0 | 0 | 0 | 37612
2022090709 | 4 | 0.58866 | 47092.8 | 0.07012 | 2524.32 | 0.31184 | 3742.08 | 1 | 5000 | 2524.32 | 3742.08 | 0 | 0 | 0 | 0 | 35826.4 | 0 | 0 | 0 | 0 | 0 | 35826.4
2022090710 | 4 | 0.62476 | 49980.8 | 0.0396 | 1425.6 | 0.61855 | 7422.6 | 1 | 5000 | 1425.6 | 7422.6 | 0 | 0 | 0 | 0 | 36132.6 | 0 | 0 | 0 | 0 | 0 | 36132.6
2022090711 | 4 | 0.67136 | 53708.8 | 0.05212 | 1876.32 | 0.71123 | 8534.76 | 1 | 5000 | 1876.32 | 8534.76 | 0 | 0 | 0 | 0 | 38297.72 | 0 | 0 | 0 | 0 | 0 | 38297.72
2022090712 | 4 | 0.72403 | 57922.4 | 0.11875 | 4275 | 0.75193 | 9023.16 | 1 | 5000 | 4275 | 9023.16 | 0 | 0 | 0 | 0 | 39624.24 | 0 | 0 | 0 | 0 | 0 | 39624.24
2022090713 | 4 | 0.77474 | 61979.2 | 0.15605 | 5617.8 | 0.73917 | 8870.04 | 1 | 5000 | 5617.8 | 8870.04 | 0 | 0 | 0 | 0 | 42491.36 | 0 | 0 | 0 | 0 | 0 | 42491.36
2022090714 | 4 | 0.81614 | 65291.2 | 0.16288 | 5863.68 | 0.72915 | 8749.8 | 1 | 5000 | 5863.68 | 8749.8 | 0 | 0 | 0 | 0 | 45677.72 | 0 | 0 | 0 | 0 | 0 | 45677.72
2022090715 | 4 | 0.83564 | 66851.2 | 0.16888 | 6079.68 | 0.73758 | 8850.96 | 1 | 5000 | 6079.68 | 8850.96 | 0 | 0 | 0 | 0 | 46920.56 | 0 | 0 | 0 | 0 | 0 | 46920.56
2022090716 | 4 | 0.83914 | 67131.2 | 0.17846 | 6424.56 | 0.70279 | 8433.48 | 1 | 5000 | 6424.56 | 8433.48 | 0 | 0 | 0 | 0 | 47273.16 | 0 | 0 | 0 | 0 | 0 | 47273.16
2022090717 | 4 | 0.83383 | 66706.4 | 0.18015 | 6485.4 | 0.66576 | 7989.12 | 1 | 5000 | 6485.4 | 7989.12 | 0 | 0 | 0 | 0 | 47231.88 | 0 | 0 | 0 | 0 | 0 | 47231.88
2022090718 | 4 | 0.81762 | 65409.6 | 0.17822 | 6415.92 | 0.56777 | 6813.24 | 1 | 5000 | 6415.92 | 6813.24 | 0 | 0 | 0 | 0 | 47180.44 | 0 | 0 | 0 | 0 | 0 | 47180.44
2022090719 | 4 | 0.79875 | 63900 | 0.16475 | 5931 | 0.31634 | 3796.08 | 1 | 5000 | 5931 | 3796.08 | 0 | 0 | 0 | 0 | 49172.92 | 0 | 0 | 0 | 0 | 0 | 49172.92
2022090720 | 4 | 0.76775 | 61420 | 0.14411 | 5187.96 | 0.04905 | 588.6 | 1 | 5000 | 5187.96 | 588.6 | 0 | 0 | 0 | 0 | 50643.44 | 0 | 0 | 0 | 0 | 0 | 50643.44
2022090721 | 4 | 0.74429 | 59543.2 | 0.15258 | 5492.88 | 0 | 0 | 1 | 5000 | 5492.88 | 0 | 0 | 0 | 0 | 0 | 49050.32 | 0 | 0 | 0 | 0 | 0 | 49050.32
2022090722 | 4 | 0.70741 | 56592.8 | 0.18355 | 6607.8 | 0 | 0 | 1 | 5000 | 6607.8 | 0 | 0 | 0 | 0 | 0 | 44985 | 0 | 0 | 0 | 0 | 0 | 44985
2022090723 | 4 | 0.65647 | 52517.6 | 0.21077 | 7587.72 | 0 | 0 | 1 | 5000 | 7587.72 | 0 | 0 | 0 | 0 | 0 | 39929.88 | 0 | 0 | 0 | 0 | 0 | 39929.88
2022090724 | 4 | 0.60771 | 48616.8 | 0.19929 | 7174.44 | 0 | 0 | 1 | 5000 | 7174.44 | 0 | 0 | 0 | 0 | 0 | 36442.36 | 0 | 0 | 0 | 0 | 0 | 36442.36
2022090801 | 5 | 0.57021 | 45616.8 | 0.16109 | 5799.24 | 0 | 0 | 1 | 5000 | 5799.24 | 0 | 0 | 0 | 0 | 0 | 34817.56 | 0 | 0 | 0 | 0 | 0 | 34817.56
2022090802 | 5 | 0.54278 | 43422.4 | 0.12616 | 4541.76 | 0 | 0 | 1 | 5000 | 4541.76 | 0 | 0 | 0 | 0 | 0 | 33880.64 | 0 | 0 | 0 | 0 | 0 | 33880.64
2022090803 | 5 | 0.52413 | 41930.4 | 0.0971 | 3495.6 | 0 | 0 | 1 | 5000 | 3495.6 | 0 | 0 | 0 | 0 | 0 | 33434.8 | 0 | 0 | 0 | 0 | 0 | 33434.8
2022090804 | 5 | 0.51385 | 41108 | 0.07631 | 2747.16 | 0 | 0 | 1 | 5000 | 2747.16 | 0 | 0 | 0 | 0 | 0 | 33360.84 | 0 | 0 | 0 | 0 | 0 | 33360.84
2022090805 | 5 | 0.51332 | 41065.6 | 0.05857 | 2108.52 | 0 | 0 | 1 | 5000 | 2108.52 | 0 | 0 | 0 | 0 | 0 | 33957.08 | 0 | 0 | 0 | 0 | 0 | 33957.08
2022090806 | 5 | 0.5302 | 42416 | 0.0458 | 1648.8 | 0 | 0 | 1 | 5000 | 1648.8 | 0 | 0 | 0 | 0 | 0 | 35767.2 | 0 | 0 | 0 | 0 | 0 | 35767.2
2022090807 | 5 | 0.55737 | 44589.6 | 0.04421 | 1591.56 | 0 | 0 | 1 | 5000 | 1591.56 | 0 | 0 | 0 | 0 | 0 | 37998.04 | 0 | 0 | 0 | 0 | 0 | 37998.04
2022090808 | 5 | 0.5653 | 45224 | 0.04543 | 1635.48 | 0.02736 | 328.32 | 1 | 5000 | 1635.48 | 328.32 | 0 | 0 | 0 | 0 | 38260.2 | 0 | 0 | 0 | 0 | 0 | 38260.2
2022090809 | 5 | 0.58021 | 46416.8 | 0.03915 | 1409.4 | 0.34774 | 4172.88 | 1 | 5000 | 1409.4 | 4172.88 | 0 | 0 | 0 | 0 | 35834.52 | 0 | 0 | 0 | 0 | 0 | 35834.52
2022090810 | 5 | 0.61245 | 48996 | 0.01935 | 696.6 | 0.69895 | 8387.4 | 1 | 5000 | 696.6 | 8387.4 | 0 | 0 | 0 | 0 | 34912 | 0 | 0 | 0 | 0 | 0 | 34912
2022090811 | 5 | 0.65865 | 52692 | 0.02289 | 824.04 | 0.77031 | 9243.72 | 1 | 5000 | 824.04 | 9243.72 | 0 | 0 | 0 | 0 | 37624.24 | 0 | 0 | 0 | 0 | 0 | 37624.24
2022090812 | 5 | 0.70681 | 56544.8 | 0.03677 | 1323.72 | 0.77716 | 9325.92 | 1 | 5000 | 1323.72 | 9325.92 | 0 | 0 | 0 | 0 | 40895.16 | 0 | 0 | 0 | 0 | 0 | 40895.16
2022090813 | 5 | 0.75121 | 60096.8 | 0.03844 | 1383.84 | 0.74582 | 8949.84 | 1 | 5000 | 1383.84 | 8949.84 | 0 | 0 | 0 | 0 | 44763.12 | 0 | 0 | 0 | 0 | 0 | 44763.12
2022090814 | 5 | 0.78793 | 63034.4 | 0.03051 | 1098.36 | 0.73733 | 8847.96 | 1 | 5000 | 1098.36 | 8847.96 | 0 | 0 | 0 | 0 | 48088.08 | 0 | 0 | 0 | 0 | 0 | 48088.08
2022090815 | 5 | 0.80792 | 64633.6 | 0.02663 | 958.68 | 0.74161 | 8899.32 | 1 | 5000 | 958.68 | 8899.32 | 0 | 0 | 0 | 0 | 49775.6 | 0 | 0 | 0 | 0 | 0 | 49775.6
2022090816 | 5 | 0.82035 | 65628 | 0.02479 | 892.44 | 0.74595 | 8951.4 | 1 | 5000 | 892.44 | 8951.4 | 0 | 0 | 0 | 0 | 50784.16 | 0 | 0 | 0 | 0 | 0 | 50784.16
2022090817 | 5 | 0.82494 | 65995.2 | 0.03058 | 1100.88 | 0.70081 | 8409.72 | 1 | 5000 | 1100.88 | 8409.72 | 0 | 0 | 0 | 0 | 51484.6 | 0 | 0 | 0 | 0 | 0 | 51484.6
2022090818 | 5 | 0.82266 | 65812.8 | 0.04242 | 1527.12 | 0.6029 | 7234.8 | 1 | 5000 | 1527.12 | 7234.8 | 0 | 0 | 0 | 0 | 52050.88 | 0 | 0 | 0 | 0 | 0 | 52050.88
2022090819 | 5 | 0.80185 | 64148 | 0.06176 | 2223.36 | 0.37254 | 4470.48 | 1 | 5000 | 2223.36 | 4470.48 | 0 | 0 | 0 | 0 | 52454.16 | 0 | 0 | 0 | 0 | 0 | 52454.16
2022090820 | 5 | 0.7721 | 61768 | 0.08872 | 3193.92 | 0.05525 | 663 | 1 | 5000 | 3193.92 | 663 | 0 | 0 | 0 | 0 | 52911.08 | 0 | 0 | 0 | 0 | 0 | 52911.08
2022090821 | 5 | 0.74775 | 59820 | 0.12378 | 4456.08 | 0.00348 | 41.76 | 1 | 5000 | 4456.08 | 41.76 | 0 | 0 | 0 | 0 | 50322.16 | 0 | 0 | 0 | 0 | 0 | 50322.16
2022090822 | 5 | 0.70926 | 56740.8 | 0.15278 | 5500.08 | 0.00345 | 41.4 | 1 | 5000 | 5500.08 | 41.4 | 0 | 0 | 0 | 0 | 46199.32 | 0 | 0 | 0 | 0 | 0 | 46199.32
2022090823 | 5 | 0.66046 | 52836.8 | 0.20112 | 7240.32 | 0.00044 | 5.28 | 1 | 5000 | 7240.32 | 5.28 | 0 | 0 | 0 | 0 | 40591.2 | 0 | 0 | 0 | 0 | 0 | 40591.2
2022090824 | 5 | 0.60811 | 48648.8 | 0.25477 | 9171.72 | 0 | 0 | 1 | 5000 | 9171.72 | 0 | 0 | 0 | 0 | 0 | 34477.08 | 0 | 0 | 0 | 0 | 0 | 34477.08
2022090901 | 6 | 0.56777 | 45421.6 | 0.28476 | 10251.36 | 0 | 0 | 1 | 5000 | 10251.36 | 0 | 0 | 0 | 0 | 0 | 30170.24 | 0 | 0 | 0 | 0 | 0 | 30170.24
2022090902 | 6 | 0.53748 | 42998.4 | 0.30329 | 10918.44 | 0 | 0 | 1 | 5000 | 10918.44 | 0 | 0 | 0 | 0 | 0 | 27079.96 | 0 | 0 | 0 | 0 | 0 | 27079.96
2022090903 | 6 | 0.51678 | 41342.4 | 0.31165 | 11219.4 | 0 | 0 | 1 | 5000 | 11219.4 | 0 | 0 | 0 | 0 | 0 | 25123 | 0 | 0 | 0 | 0 | 0 | 25123
2022090904 | 6 | 0.50566 | 40452.8 | 0.31162 | 11218.32 | 0 | 0 | 1 | 5000 | 11218.32 | 0 | 0 | 0 | 0 | 0 | 24234.48 | 0 | 0 | 0 | 0 | 0 | 24234.48
2022090905 | 6 | 0.50369 | 40295.2 | 0.29165 | 10499.4 | 0 | 0 | 1 | 5000 | 10499.4 | 0 | 0 | 0 | 0 | 0 | 24795.8 | 0 | 0 | 0 | 0 | 0 | 24795.8
2022090906 | 6 | 0.52048 | 41638.4 | 0.25438 | 9157.68 | 0 | 0 | 1 | 5000 | 9157.68 | 0 | 0 | 0 | 0 | 0 | 27480.72 | 0 | 0 | 0 | 0 | 0 | 27480.72
2022090907 | 6 | 0.54709 | 43767.2 | 0.21544 | 7755.84 | 0 | 0 | 1 | 5000 | 7755.84 | 0 | 0 | 0 | 0 | 0 | 31011.36 | 0 | 0 | 0 | 0 | 0 | 31011.36
2022090908 | 6 | 0.55803 | 44642.4 | 0.19412 | 6988.32 | 0.03073 | 368.76 | 1 | 5000 | 6988.32 | 368.76 | 0 | 0 | 0 | 0 | 32285.32 | 0 | 0 | 0 | 0 | 0 | 32285.32
2022090909 | 6 | 0.57624 | 46099.2 | 0.1408 | 5068.8 | 0.32768 | 3932.16 | 1 | 5000 | 5068.8 | 3932.16 | 0 | 0 | 0 | 0 | 32098.24 | 0 | 0 | 0 | 0 | 0 | 32098.24
2022090910 | 6 | 0.61188 | 48950.4 | 0.07421 | 2671.56 | 0.60692 | 7283.04 | 1 | 5000 | 2671.56 | 7283.04 | 0 | 0 | 0 | 0 | 33995.8 | 0 | 0 | 0 | 0 | 0 | 33995.8
2022090911 | 6 | 0.65852 | 52681.6 | 0.0656 | 2361.6 | 0.7069 | 8482.8 | 1 | 5000 | 2361.6 | 8482.8 | 0 | 0 | 0 | 0 | 36837.2 | 0 | 0 | 0 | 0 | 0 | 36837.2
2022090912 | 6 | 0.70043 | 56034.4 | 0.05148 | 1853.28 | 0.76691 | 9202.92 | 1 | 5000 | 1853.28 | 9202.92 | 0 | 0 | 0 | 0 | 39978.2 | 0 | 0 | 0 | 0 | 0 | 39978.2
2022090913 | 6 | 0.74441 | 59552.8 | 0.0377 | 1357.2 | 0.75745 | 9089.4 | 1 | 5000 | 1357.2 | 9089.4 | 0 | 0 | 0 | 0 | 44106.2 | 0 | 0 | 0 | 0 | 0 | 44106.2
2022090914 | 6 | 0.77686 | 62148.8 | 0.03672 | 1321.92 | 0.76542 | 9185.04 | 1 | 5000 | 1321.92 | 9185.04 | 0 | 0 | 0 | 0 | 46641.84 | 0 | 0 | 0 | 0 | 0 | 46641.84
2022090915 | 6 | 0.80227 | 64181.6 | 0.0462 | 1663.2 | 0.74895 | 8987.4 | 1 | 5000 | 1663.2 | 8987.4 | 0 | 0 | 0 | 0 | 48531 | 0 | 0 | 0 | 0 | 0 | 48531
2022090916 | 6 | 0.81891 | 65512.8 | 0.07842 | 2823.12 | 0.73046 | 8765.52 | 1 | 5000 | 2823.12 | 8765.52 | 0 | 0 | 0 | 0 | 48924.16 | 0 | 0 | 0 | 0 | 0 | 48924.16
2022090917 | 6 | 0.82701 | 66160.8 | 0.10351 | 3726.36 | 0.71045 | 8525.4 | 1 | 5000 | 3726.36 | 8525.4 | 0 | 0 | 0 | 0 | 48909.04 | 0 | 0 | 0 | 0 | 0 | 48909.04
2022090918 | 6 | 0.81757 | 65405.6 | 0.09888 | 3559.68 | 0.6448 | 7737.6 | 1 | 5000 | 3559.68 | 7737.6 | 0 | 0 | 0 | 0 | 49108.32 | 0 | 0 | 0 | 0 | 0 | 49108.32
2022090919 | 6 | 0.78988 | 63190.4 | 0.1186 | 4269.6 | 0.41111 | 4933.32 | 1 | 5000 | 4269.6 | 4933.32 | 0 | 0 | 0 | 0 | 48987.48 | 0 | 0 | 0 | 0 | 0 | 48987.48
2022090920 | 6 | 0.75059 | 60047.2 | 0.1624 | 5846.4 | 0.07125 | 855 | 1 | 5000 | 5846.4 | 855 | 0 | 0 | 0 | 0 | 48345.8 | 0 | 0 | 0 | 0 | 0 | 48345.8
2022090921 | 6 | 0.72137 | 57709.6 | 0.25135 | 9048.6 | 0 | 0 | 1 | 5000 | 9048.6 | 0 | 0 | 0 | 0 | 0 | 43661 | 0 | 0 | 0 | 0 | 0 | 43661
2022090922 | 6 | 0.6881 | 55048 | 0.34151 | 12294.36 | 0 | 0 | 1 | 5000 | 12294.36 | 0 | 0 | 0 | 0 | 0 | 37753.64 | 0 | 0 | 0 | 0 | 0 | 37753.64
2022090923 | 6 | 0.65211 | 52168.8 | 0.41663 | 14998.68 | 0 | 0 | 1 | 5000 | 14998.68 | 0 | 0 | 0 | 0 | 0 | 32170.12 | 0 | 0 | 0 | 0 | 0 | 32170.12
2022090924 | 6 | 0.61092 | 48873.6 | 0.45512 | 16384.32 | 0 | 0 | 1 | 5000 | 16384.32 | 0 | 0 | 0 | 0 | 0 | 27489.28 | 0 | 0 | 0 | 0 | 0 | 27489.28
2022091001 | 7 | 0.57298 | 45838.4 | 0.4472 | 16099.2 | 0 | 0 | 1 | 5000 | 16099.2 | 0 | 0 | 0 | 0 | 0 | 24739.2 | 0 | 0 | 0 | 0 | 0 | 24739.2
2022091002 | 7 | 0.5428 | 43424 | 0.41311 | 14871.96 | 0 | 0 | 1 | 5000 | 14871.96 | 0 | 0 | 0 | 0 | 0 | 23552.04 | 0 | 0 | 0 | 0 | 0 | 23552.04
2022091003 | 7 | 0.51878 | 41502.4 | 0.36086 | 12990.96 | 0 | 0 | 1 | 5000 | 12990.96 | 0 | 0 | 0 | 0 | 0 | 23511.44 | 0 | 0 | 0 | 0 | 0 | 23511.44
2022091004 | 7 | 0.5029 | 40232 | 0.31096 | 11194.56 | 0 | 0 | 1 | 5000 | 11194.56 | 0 | 0 | 0 | 0 | 0 | 24037.44 | 0 | 0 | 0 | 0 | 0 | 24037.44
2022091005 | 7 | 0.49366 | 39492.8 | 0.25752 | 9270.72 | 0 | 0 | 1 | 5000 | 9270.72 | 0 | 0 | 0 | 0 | 0 | 25222.08 | 0 | 0 | 0 | 0 | 0 | 25222.08
2022091006 | 7 | 0.49273 | 39418.4 | 0.22633 | 8147.88 | 0 | 0 | 1 | 5000 | 8147.88 | 0 | 0 | 0 | 0 | 0 | 26270.52 | 0 | 0 | 0 | 0 | 0 | 26270.52
2022091007 | 7 | 0.49724 | 39779.2 | 0.18856 | 6788.16 | 0 | 0 | 1 | 5000 | 6788.16 | 0 | 0 | 0 | 0 | 0 | 27991.04 | 0 | 0 | 0 | 0 | 0 | 27991.04
2022091008 | 7 | 0.50453 | 40362.4 | 0.15804 | 5689.44 | 0.02642 | 317.04 | 1 | 5000 | 5689.44 | 317.04 | 0 | 0 | 0 | 0 | 29355.92 | 0 | 0 | 0 | 0 | 0 | 29355.92
2022091009 | 7 | 0.53183 | 42546.4 | 0.11419 | 4110.84 | 0.34231 | 4107.72 | 1 | 5000 | 4110.84 | 4107.72 | 0 | 0 | 0 | 0 | 29327.84 | 0 | 0 | 0 | 0 | 0 | 29327.84
2022091010 | 7 | 0.57649 | 46119.2 | 0.07837 | 2821.32 | 0.65194 | 7823.28 | 1 | 5000 | 2821.32 | 7823.28 | 0 | 0 | 0 | 0 | 30474.6 | 0 | 0 | 0 | 0 | 0 | 30474.6
2022091011 | 7 | 0.62973 | 50378.4 | 0.07946 | 2860.56 | 0.75651 | 9078.12 | 1 | 5000 | 2860.56 | 9078.12 | 0 | 0 | 0 | 0 | 33439.72 | 0 | 0 | 0 | 0 | 0 | 33439.72
2022091012 | 7 | 0.67774 | 54219.2 | 0.06402 | 2304.72 | 0.7892 | 9470.4 | 1 | 5000 | 2304.72 | 9470.4 | 0 | 0 | 0 | 0 | 37444.08 | 0 | 0 | 0 | 0 | 0 | 37444.08
2022091013 | 7 | 0.72024 | 57619.2 | 0.0507 | 1825.2 | 0.76101 | 9132.12 | 1 | 5000 | 1825.2 | 9132.12 | 0 | 0 | 0 | 0 | 41661.88 | 0 | 0 | 0 | 0 | 0 | 41661.88
2022091014 | 7 | 0.75319 | 60255.2 | 0.05541 | 1994.76 | 0.72404 | 8688.48 | 1 | 5000 | 1994.76 | 8688.48 | 0 | 0 | 0 | 0 | 44571.96 | 0 | 0 | 0 | 0 | 0 | 44571.96
2022091015 | 7 | 0.77926 | 62340.8 | 0.06776 | 2439.36 | 0.71776 | 8613.12 | 1 | 5000 | 2439.36 | 8613.12 | 0 | 0 | 0 | 0 | 46288.32 | 0 | 0 | 0 | 0 | 0 | 46288.32
2022091016 | 7 | 0.80049 | 64039.2 | 0.10178 | 3664.08 | 0.72394 | 8687.28 | 1 | 5000 | 3664.08 | 8687.28 | 0 | 0 | 0 | 0 | 46687.84 | 0 | 0 | 0 | 0 | 0 | 46687.84
2022091017 | 7 | 0.81102 | 64881.6 | 0.13758 | 4952.88 | 0.70257 | 8430.84 | 1 | 5000 | 4952.88 | 8430.84 | 0 | 0 | 0 | 0 | 46497.88 | 0 | 0 | 0 | 0 | 0 | 46497.88
2022091018 | 7 | 0.80683 | 64546.4 | 0.16257 | 5852.52 | 0.62217 | 7466.04 | 1 | 5000 | 5852.52 | 7466.04 | 0 | 0 | 0 | 0 | 46227.84 | 0 | 0 | 0 | 0 | 0 | 46227.84
2022091019 | 7 | 0.78561 | 62848.8 | 0.21984 | 7914.24 | 0.38152 | 4578.24 | 1 | 5000 | 7914.24 | 4578.24 | 0 | 0 | 0 | 0 | 45356.32 | 0 | 0 | 0 | 0 | 0 | 45356.32
2022091020 | 7 | 0.75384 | 60307.2 | 0.27947 | 10060.92 | 0.05942 | 713.04 | 1 | 5000 | 10060.92 | 713.04 | 0 | 0 | 0 | 0 | 44533.24 | 0 | 0 | 0 | 0 | 0 | 44533.24
2022091021 | 7 | 0.72559 | 58047.2 | 0.33805 | 12169.8 | 0 | 0 | 1 | 5000 | 12169.8 | 0 | 0 | 0 | 0 | 0 | 40877.4 | 0 | 0 | 0 | 0 | 0 | 40877.4
2022091022 | 7 | 0.68826 | 55060.8 | 0.39155 | 14095.8 | 0 | 0 | 1 | 5000 | 14095.8 | 0 | 0 | 0 | 0 | 0 | 35965 | 0 | 0 | 0 | 0 | 0 | 35965
2022091023 | 7 | 0.64988 | 51990.4 | 0.40721 | 14659.56 | 0 | 0 | 1 | 5000 | 14659.56 | 0 | 0 | 0 | 0 | 0 | 32330.84 | 0 | 0 | 0 | 0 | 0 | 32330.84
2022091024 | 7 | 0.6115 | 48920 | 0.41667 | 15000.12 | 0 | 0 | 1 | 5000 | 15000.12 | 0 | 0 | 0 | 0 | 0 | 28919.88 | 0 | 0 | 0 | 0 | 0 | 28919.88
2022091101 | 1 | 0.57672 | 46137.6 | 0.39886 | 14358.96 | 0 | 0 | 1 | 5000 | 14358.96 | 0 | 0 | 0 | 0 | 0 | 26778.64 | 0 | 0 | 0 | 0 | 0 | 26778.64
2022091102 | 1 | 0.55004 | 44003.2 | 0.36029 | 12970.44 | 0 | 0 | 1 | 5000 | 12970.44 | 0 | 0 | 0 | 0 | 0 | 26032.76 | 0 | 0 | 0 | 0 | 0 | 26032.76
2022091103 | 1 | 0.52772 | 42217.6 | 0.34974 | 12590.64 | 0 | 0 | 1 | 5000 | 12590.64 | 0 | 0 | 0 | 0 | 0 | 24626.96 | 0 | 0 | 0 | 0 | 0 | 24626.96
2022091104 | 1 | 0.51193 | 40954.4 | 0.33477 | 12051.72 | 0 | 0 | 1 | 5000 | 12051.72 | 0 | 0 | 0 | 0 | 0 | 23902.68 | 0 | 0 | 0 | 0 | 0 | 23902.68
2022091105 | 1 | 0.4986 | 39888 | 0.31806 | 11450.16 | 0 | 0 | 1 | 5000 | 11450.16 | 0 | 0 | 0 | 0 | 0 | 23437.84 | 0 | 0 | 0 | 0 | 0 | 23437.84
2022091106 | 1 | 0.49638 | 39710.4 | 0.30978 | 11152.08 | 0 | 0 | 1 | 5000 | 11152.08 | 0 | 0 | 0 | 0 | 0 | 23558.32 | 0 | 0 | 0 | 0 | 0 | 23558.32
2022091107 | 1 | 0.49265 | 39412 | 0.30739 | 11066.04 | 0 | 0 | 1 | 5000 | 11066.04 | 0 | 0 | 0 | 0 | 0 | 23345.96 | 0 | 0 | 0 | 0 | 0 | 23345.96
2022091108 | 1 | 0.4935 | 39480 | 0.32539 | 11714.04 | 0.01985 | 238.2 | 1 | 5000 | 11714.04 | 238.2 | 0 | 0 | 0 | 0 | 22527.76 | 0 | 0 | 0 | 0 | 0 | 22527.76
2022091109 | 1 | 0.51684 | 41347.2 | 0.33541 | 12074.76 | 0.18309 | 2197.08 | 1 | 5000 | 12074.76 | 2197.08 | 0 | 0 | 0 | 0 | 22075.36 | 0 | 0 | 0 | 0 | 0 | 22075.36
2022091110 | 1 | 0.55827 | 44661.6 | 0.32838 | 11821.68 | 0.3496 | 4195.2 | 1 | 5000 | 11821.68 | 4195.2 | 0 | 0 | 0 | 0 | 23644.72 | 0 | 0 | 0 | 0 | 0 | 23644.72
2022091111 | 1 | 0.59949 | 47959.2 | 0.26349 | 9485.64 | 0.48151 | 5778.12 | 1 | 5000 | 9485.64 | 5778.12 | 0 | 0 | 0 | 0 | 27695.44 | 0 | 0 | 0 | 0 | 0 | 27695.44
2022091112 | 1 | 0.64155 | 51324 | 0.2014 | 7250.4 | 0.57054 | 6846.48 | 1 | 5000 | 7250.4 | 6846.48 | 0 | 0 | 0 | 0 | 32227.12 | 0 | 0 | 0 | 0 | 0 | 32227.12
2022091113 | 1 | 0.68084 | 54467.2 | 0.13448 | 4841.28 | 0.65396 | 7847.52 | 1 | 5000 | 4841.28 | 7847.52 | 0 | 0 | 0 | 0 | 36778.4 | 0 | 0 | 0 | 0 | 0 | 36778.4
2022091114 | 1 | 0.71464 | 57171.2 | 0.09526 | 3429.36 | 0.68455 | 8214.6 | 1 | 5000 | 3429.36 | 8214.6 | 0 | 0 | 0 | 0 | 40527.24 | 0 | 0 | 0 | 0 | 0 | 40527.24
2022091115 | 1 | 0.742 | 59360 | 0.07851 | 2826.36 | 0.68995 | 8279.4 | 1 | 5000 | 2826.36 | 8279.4 | 0 | 0 | 0 | 0 | 43254.24 | 0 | 0 | 0 | 0 | 0 | 43254.24
2022091116 | 1 | 0.76522 | 61217.6 | 0.07283 | 2621.88 | 0.71234 | 8548.08 | 1 | 5000 | 2621.88 | 8548.08 | 0 | 0 | 0 | 0 | 45047.64 | 0 | 0 | 0 | 0 | 0 | 45047.64
2022091117 | 1 | 0.77562 | 62049.6 | 0.06462 | 2326.32 | 0.64572 | 7748.64 | 1 | 5000 | 2326.32 | 7748.64 | 0 | 0 | 0 | 0 | 46974.64 | 0 | 0 | 0 | 0 | 0 | 46974.64
2022091118 | 1 | 0.77543 | 62034.4 | 0.06361 | 2289.96 | 0.56398 | 6767.76 | 1 | 5000 | 2289.96 | 6767.76 | 0 | 0 | 0 | 0 | 47976.68 | 0 | 0 | 0 | 0 | 0 | 47976.68
2022091119 | 1 | 0.75647 | 60517.6 | 0.05626 | 2025.36 | 0.35244 | 4229.28 | 1 | 5000 | 2025.36 | 4229.28 | 0 | 0 | 0 | 0 | 49262.96 | 0 | 0 | 0 | 0 | 0 | 49262.96
2022091120 | 1 | 0.72544 | 58035.2 | 0.05209 | 1875.24 | 0.05176 | 621.12 | 1 | 5000 | 1875.24 | 621.12 | 0 | 0 | 0 | 0 | 50538.84 | 0 | 0 | 0 | 0 | 0 | 50538.84
2022091121 | 1 | 0.70981 | 56784.8 | 0.07209 | 2595.24 | 0 | 0 | 1 | 5000 | 2595.24 | 0 | 0 | 0 | 0 | 0 | 49189.56 | 0 | 0 | 0 | 0 | 0 | 49189.56
2022091122 | 1 | 0.67644 | 54115.2 | 0.09542 | 3435.12 | 0 | 0 | 1 | 5000 | 3435.12 | 0 | 0 | 0 | 0 | 0 | 45680.08 | 0 | 0 | 0 | 0 | 0 | 45680.08
2022091123 | 1 | 0.62973 | 50378.4 | 0.08892 | 3201.12 | 0 | 0 | 1 | 5000 | 3201.12 | 0 | 0 | 0 | 0 | 0 | 42177.28 | 0 | 0 | 0 | 0 | 0 | 42177.28
2022091124 | 1 | 0.58266 | 46612.8 | 0.08308 | 2990.88 | 0 | 0 | 1 | 5000 | 2990.88 | 0 | 0 | 0 | 0 | 0 | 38621.92 | 0 | 0 | 0 | 0 | 0 | 38621.92
2022091201 | 2 | 0.54331 | 43464.8 | 0.09033 | 3251.88 | 0 | 0 | 1 | 5000 | 3251.88 | 0 | 0 | 0 | 0 | 0 | 35212.92 | 0 | 0 | 0 | 0 | 0 | 35212.92
2022091202 | 2 | 0.51537 | 41229.6 | 0.09576 | 3447.36 | 0 | 0 | 1 | 5000 | 3447.36 | 0 | 0 | 0 | 0 | 0 | 32782.24 | 0 | 0 | 0 | 0 | 0 | 32782.24
2022091203 | 2 | 0.49844 | 39875.2 | 0.10048 | 3617.28 | 0 | 0 | 1 | 5000 | 3617.28 | 0 | 0 | 0 | 0 | 0 | 31257.92 | 0 | 0 | 0 | 0 | 0 | 31257.92
2022091204 | 2 | 0.48837 | 39069.6 | 0.11204 | 4033.44 | 0 | 0 | 1 | 5000 | 4033.44 | 0 | 0 | 0 | 0 | 0 | 30036.16 | 0 | 0 | 0 | 0 | 0 | 30036.16
2022091205 | 2 | 0.49064 | 39251.2 | 0.11764 | 4235.04 | 0 | 0 | 1 | 5000 | 4235.04 | 0 | 0 | 0 | 0 | 0 | 30016.16 | 0 | 0 | 0 | 0 | 0 | 30016.16
2022091206 | 2 | 0.50676 | 40540.8 | 0.1128 | 4060.8 | 0 | 0 | 1 | 5000 | 4060.8 | 0 | 0 | 0 | 0 | 0 | 31480 | 0 | 0 | 0 | 0 | 0 | 31480
2022091207 | 2 | 0.53376 | 42700.8 | 0.11946 | 4300.56 | 0 | 0 | 1 | 5000 | 4300.56 | 0 | 0 | 0 | 0 | 0 | 33400.24 | 0 | 0 | 0 | 0 | 0 | 33400.24
2022091208 | 2 | 0.54015 | 43212 | 0.12009 | 4323.24 | 0.02425 | 291 | 1 | 5000 | 4323.24 | 291 | 0 | 0 | 0 | 0 | 33597.76 | 0 | 0 | 0 | 0 | 0 | 33597.76
2022091209 | 2 | 0.55497 | 44397.6 | 0.10245 | 3688.2 | 0.28371 | 3404.52 | 1 | 5000 | 3688.2 | 3404.52 | 0 | 0 | 0 | 0 | 32304.88 | 0 | 0 | 0 | 0 | 0 | 32304.88
2022091210 | 2 | 0.58193 | 46554.4 | 0.07781 | 2801.16 | 0.57696 | 6923.52 | 1 | 5000 | 2801.16 | 6923.52 | 0 | 0 | 0 | 0 | 31829.72 | 0 | 0 | 0 | 0 | 0 | 31829.72
2022091211 | 2 | 0.62022 | 49617.6 | 0.09992 | 3597.12 | 0.66697 | 8003.64 | 1 | 5000 | 3597.12 | 8003.64 | 0 | 0 | 0 | 0 | 33016.84 | 0 | 0 | 0 | 0 | 0 | 33016.84
2022091212 | 2 | 0.66097 | 52877.6 | 0.09875 | 3555 | 0.75815 | 9097.8 | 1 | 5000 | 3555 | 9097.8 | 0 | 0 | 0 | 0 | 35224.8 | 0 | 0 | 0 | 0 | 0 | 35224.8
2022091213 | 2 | 0.70156 | 56124.8 | 0.08559 | 3081.24 | 0.77026 | 9243.12 | 1 | 5000 | 3081.24 | 9243.12 | 0 | 0 | 0 | 0 | 38800.44 | 0 | 0 | 0 | 0 | 0 | 38800.44
2022091214 | 2 | 0.74033 | 59226.4 | 0.07711 | 2775.96 | 0.76982 | 9237.84 | 1 | 5000 | 2775.96 | 9237.84 | 0 | 0 | 0 | 0 | 42212.6 | 0 | 0 | 0 | 0 | 0 | 42212.6
2022091215 | 2 | 0.77305 | 61844 | 0.06951 | 2502.36 | 0.76 | 9120 | 1 | 5000 | 2502.36 | 9120 | 0 | 0 | 0 | 0 | 45221.64 | 0 | 0 | 0 | 0 | 0 | 45221.64
2022091216 | 2 | 0.79767 | 63813.6 | 0.06204 | 2233.44 | 0.75279 | 9033.48 | 1 | 5000 | 2233.44 | 9033.48 | 0 | 0 | 0 | 0 | 47546.68 | 0 | 0 | 0 | 0 | 0 | 47546.68
2022091217 | 2 | 0.81503 | 65202.4 | 0.05884 | 2118.24 | 0.71941 | 8632.92 | 1 | 5000 | 2118.24 | 8632.92 | 0 | 0 | 0 | 0 | 49451.24 | 0 | 0 | 0 | 0 | 0 | 49451.24
2022091218 | 2 | 0.81436 | 65148.8 | 0.05662 | 2038.32 | 0.65397 | 7847.64 | 1 | 5000 | 2038.32 | 7847.64 | 0 | 0 | 0 | 0 | 50262.84 | 0 | 0 | 0 | 0 | 0 | 50262.84
2022091219 | 2 | 0.78937 | 63149.6 | 0.06574 | 2366.64 | 0.41701 | 5004.12 | 1 | 5000 | 2366.64 | 5004.12 | 0 | 0 | 0 | 0 | 50778.84 | 0 | 0 | 0 | 0 | 0 | 50778.84
2022091220 | 2 | 0.75591 | 60472.8 | 0.09571 | 3445.56 | 0.05869 | 704.28 | 1 | 5000 | 3445.56 | 704.28 | 0 | 0 | 0 | 0 | 51322.96 | 0 | 0 | 0 | 0 | 0 | 51322.96
2022091221 | 2 | 0.73454 | 58763.2 | 0.1663 | 5986.8 | 0 | 0 | 1 | 5000 | 5986.8 | 0 | 0 | 0 | 0 | 0 | 47776.4 | 0 | 0 | 0 | 0 | 0 | 47776.4
2022091222 | 2 | 0.69441 | 55552.8 | 0.27424 | 9872.64 | 0 | 0 | 1 | 5000 | 9872.64 | 0 | 0 | 0 | 0 | 0 | 40680.16 | 0 | 0 | 0 | 0 | 0 | 40680.16
2022091223 | 2 | 0.63961 | 51168.8 | 0.34598 | 12455.28 | 0 | 0 | 1 | 5000 | 12455.28 | 0 | 0 | 0 | 0 | 0 | 33713.52 | 0 | 0 | 0 | 0 | 0 | 33713.52
2022091224 | 2 | 0.58852 | 47081.6 | 0.36006 | 12962.16 | 0 | 0 | 1 | 5000 | 12962.16 | 0 | 0 | 0 | 0 | 0 | 29119.44 | 0 | 0 | 0 | 0 | 0 | 29119.44
2022091301 | 3 | 0.5499 | 43992 | 0.36985 | 13314.6 | 0 | 0 | 1 | 5000 | 13314.6 | 0 | 0 | 0 | 0 | 0 | 25677.4 | 0 | 0 | 0 | 0 | 0 | 25677.4
2022091302 | 3 | 0.52183 | 41746.4 | 0.37973 | 13670.28 | 0 | 0 | 1 | 5000 | 13670.28 | 0 | 0 | 0 | 0 | 0 | 23076.12 | 0 | 0 | 0 | 0 | 0 | 23076.12
2022091303 | 3 | 0.50489 | 40391.2 | 0.38086 | 13710.96 | 0 | 0 | 1 | 5000 | 13710.96 | 0 | 0 | 0 | 0 | 0 | 21680.24 | 0 | 0 | 0 | 0 | 0 | 21680.24
2022091304 | 3 | 0.49538 | 39630.4 | 0.37155 | 13375.8 | 0 | 0 | 1 | 5000 | 13375.8 | 0 | 0 | 0 | 0 | 0 | 21254.6 | 0 | 0 | 0 | 0 | 0 | 21254.6
2022091305 | 3 | 0.4925 | 39400 | 0.34077 | 12267.72 | 0 | 0 | 1 | 5000 | 12267.72 | 0 | 0 | 0 | 0 | 0 | 22132.28 | 0 | 0 | 0 | 0 | 0 | 22132.28
2022091306 | 3 | 0.50873 | 40698.4 | 0.30586 | 11010.96 | 0 | 0 | 1 | 5000 | 11010.96 | 0 | 0 | 0 | 0 | 0 | 24687.44 | 0 | 0 | 0 | 0 | 0 | 24687.44
2022091307 | 3 | 0.53662 | 42929.6 | 0.28252 | 10170.72 | 0 | 0 | 1 | 5000 | 10170.72 | 0 | 0 | 0 | 0 | 0 | 27758.88 | 0 | 0 | 0 | 0 | 0 | 27758.88
2022091308 | 3 | 0.54241 | 43392.8 | 0.27247 | 9808.92 | 0.02311 | 277.32 | 1 | 5000 | 9808.92 | 277.32 | 0 | 0 | 0 | 0 | 28306.56 | 0 | 0 | 0 | 0 | 0 | 28306.56
2022091309 | 3 | 0.55691 | 44552.8 | 0.22247 | 8008.92 | 0.33375 | 4005 | 1 | 5000 | 8008.92 | 4005 | 0 | 0 | 0 | 0 | 27538.88 | 0 | 0 | 0 | 0 | 0 | 27538.88
2022091310 | 3 | 0.58638 | 46910.4 | 0.1621 | 5835.6 | 0.67529 | 8103.48 | 1 | 5000 | 5835.6 | 8103.48 | 0 | 0 | 0 | 0 | 27971.32 | 0 | 0 | 0 | 0 | 0 | 27971.32
2022091311 | 3 | 0.62903 | 50322.4 | 0.16267 | 5856.12 | 0.76639 | 9196.68 | 1 | 5000 | 5856.12 | 9196.68 | 0 | 0 | 0 | 0 | 30269.6 | 0 | 0 | 0 | 0 | 0 | 30269.6
2022091312 | 3 | 0.6722 | 53776 | 0.13102 | 4716.72 | 0.77241 | 9268.92 | 1 | 5000 | 4716.72 | 9268.92 | 0 | 0 | 0 | 0 | 34790.36 | 0 | 0 | 0 | 0 | 0 | 34790.36
2022091313 | 3 | 0.71683 | 57346.4 | 0.11939 | 4298.04 | 0.77204 | 9264.48 | 1 | 5000 | 4298.04 | 9264.48 | 0 | 0 | 0 | 0 | 38783.88 | 0 | 0 | 0 | 0 | 0 | 38783.88
2022091314 | 3 | 0.75881 | 60704.8 | 0.13105 | 4717.8 | 0.76279 | 9153.48 | 1 | 5000 | 4717.8 | 9153.48 | 0 | 0 | 0 | 0 | 41833.52 | 0 | 0 | 0 | 0 | 0 | 41833.52
2022091315 | 3 | 0.78901 | 63120.8 | 0.15106 | 5438.16 | 0.73611 | 8833.32 | 1 | 5000 | 5438.16 | 8833.32 | 0 | 0 | 0 | 0 | 43849.32 | 0 | 0 | 0 | 0 | 0 | 43849.32
2022091316 | 3 | 0.81428 | 65142.4 | 0.17196 | 6190.56 | 0.72078 | 8649.36 | 1 | 5000 | 6190.56 | 8649.36 | 0 | 0 | 0 | 0 | 45302.48 | 0 | 0 | 0 | 0 | 0 | 45302.48
2022091317 | 3 | 0.82995 | 66396 | 0.20043 | 7215.48 | 0.68122 | 8174.64 | 1 | 5000 | 7215.48 | 8174.64 | 0 | 0 | 0 | 0 | 46005.88 | 0 | 0 | 0 | 0 | 0 | 46005.88
2022091318 | 3 | 0.82853 | 66282.4 | 0.23213 | 8356.68 | 0.59651 | 7158.12 | 1 | 5000 | 8356.68 | 7158.12 | 0 | 0 | 0 | 0 | 45767.6 | 0 | 0 | 0 | 0 | 0 | 45767.6
2022091319 | 3 | 0.80499 | 64399.2 | 0.28281 | 10181.16 | 0.34769 | 4172.28 | 1 | 5000 | 10181.16 | 4172.28 | 0 | 0 | 0 | 0 | 45045.76 | 0 | 0 | 0 | 0 | 0 | 45045.76
2022091320 | 3 | 0.77135 | 61708 | 0.31019 | 11166.84 | 0.03709 | 445.08 | 1 | 5000 | 11166.84 | 445.08 | 0 | 0 | 0 | 0 | 45096.08 | 0 | 0 | 0 | 0 | 0 | 45096.08
2022091321 | 3 | 0.74571 | 59656.8 | 0.35619 | 12822.84 | 0 | 0 | 1 | 5000 | 12822.84 | 0 | 0 | 0 | 0 | 0 | 41833.96 | 0 | 0 | 0 | 0 | 0 | 41833.96
2022091322 | 3 | 0.7073 | 56584 | 0.412 | 14832 | 0 | 0 | 1 | 5000 | 14832 | 0 | 0 | 0 | 0 | 0 | 36752 | 0 | 0 | 0 | 0 | 0 | 36752
2022091323 | 3 | 0.65384 | 52307.2 | 0.45851 | 16506.36 | 0 | 0 | 1 | 5000 | 16506.36 | 0 | 0 | 0 | 0 | 0 | 30800.84 | 0 | 0 | 0 | 0 | 0 | 30800.84
2022091324 | 3 | 0.60132 | 48105.6 | 0.47124 | 16964.64 | 0 | 0 | 1 | 5000 | 16964.64 | 0 | 0 | 0 | 0 | 0 | 26140.96 | 0 | 0 | 0 | 0 | 0 | 26140.96
2022091401 | 4 | 0.55864 | 44691.2 | 0.46116 | 16601.76 | 0 | 0 | 1 | 5000 | 16601.76 | 0 | 0 | 0 | 0 | 0 | 23089.44 | 0 | 0 | 0 | 0 | 0 | 23089.44
2022091402 | 4 | 0.52911 | 42328.8 | 0.44202 | 15912.72 | 0 | 0 | 1 | 5000 | 15912.72 | 0 | 0 | 0 | 0 | 0 | 21416.08 | 0 | 0 | 0 | 0 | 0 | 21416.08
2022091403 | 4 | 0.50864 | 40691.2 | 0.42741 | 15386.76 | 0 | 0 | 1 | 5000 | 15386.76 | 0 | 0 | 0 | 0 | 0 | 20304.44 | 0 | 0 | 0 | 0 | 0 | 20304.44
2022091404 | 4 | 0.49527 | 39621.6 | 0.40969 | 14748.84 | 0 | 0 | 1 | 5000 | 14748.84 | 0 | 0 | 0 | 0 | 0 | 19872.76 | 0 | 0 | 0 | 0 | 0 | 19872.76
2022091405 | 4 | 0.49287 | 39429.6 | 0.39201 | 14112.36 | 0 | 0 | 1 | 5000 | 14112.36 | 0 | 0 | 0 | 0 | 0 | 20317.24 | 0 | 0 | 0 | 0 | 0 | 20317.24
2022091406 | 4 | 0.50819 | 40655.2 | 0.35984 | 12954.24 | 0 | 0 | 1 | 5000 | 12954.24 | 0 | 0 | 0 | 0 | 0 | 22700.96 | 0 | 0 | 0 | 0 | 0 | 22700.96
2022091407 | 4 | 0.5355 | 42840 | 0.33512 | 12064.32 | 0 | 0 | 1 | 5000 | 12064.32 | 0 | 0 | 0 | 0 | 0 | 25775.68 | 0 | 0 | 0 | 0 | 0 | 25775.68
2022091408 | 4 | 0.54315 | 43452 | 0.32156 | 11576.16 | 0.02576 | 309.12 | 1 | 5000 | 11576.16 | 309.12 | 0 | 0 | 0 | 0 | 26566.72 | 0 | 0 | 0 | 0 | 0 | 26566.72
2022091409 | 4 | 0.55718 | 44574.4 | 0.2618 | 9424.8 | 0.2926 | 3511.2 | 1 | 5000 | 9424.8 | 3511.2 | 0 | 0 | 0 | 0 | 26638.4 | 0 | 0 | 0 | 0 | 0 | 26638.4
2022091410 | 4 | 0.59019 | 47215.2 | 0.24562 | 8842.32 | 0.5952 | 7142.4 | 1 | 5000 | 8842.32 | 7142.4 | 0 | 0 | 0 | 0 | 26230.48 | 0 | 0 | 0 | 0 | 0 | 26230.48
2022091411 | 4 | 0.63005 | 50404 | 0.2796 | 10065.6 | 0.70581 | 8469.72 | 1 | 5000 | 10065.6 | 8469.72 | 0 | 0 | 0 | 0 | 26868.68 | 0 | 0 | 0 | 0 | 0 | 26868.68
2022091412 | 4 | 0.66965 | 53572 | 0.28687 | 10327.32 | 0.74126 | 8895.12 | 1 | 5000 | 10327.32 | 8895.12 | 0 | 0 | 0 | 0 | 29349.56 | 0 | 0 | 0 | 0 | 0 | 29349.56
2022091413 | 4 | 0.7093 | 56744 | 0.3096 | 11145.6 | 0.75154 | 9018.48 | 1 | 5000 | 11145.6 | 9018.48 | 0 | 0 | 0 | 0 | 31579.92 | 0 | 0 | 0 | 0 | 0 | 31579.92
2022091414 | 4 | 0.74817 | 59853.6 | 0.33403 | 12025.08 | 0.72814 | 8737.68 | 1 | 5000 | 12025.08 | 8737.68 | 0 | 0 | 0 | 0 | 34090.84 | 0 | 0 | 0 | 0 | 0 | 34090.84
2022091415 | 4 | 0.77953 | 62362.4 | 0.35543 | 12795.48 | 0.71637 | 8596.44 | 1 | 5000 | 12795.48 | 8596.44 | 0 | 0 | 0 | 0 | 35970.48 | 0 | 0 | 0 | 0 | 0 | 35970.48
2022091416 | 4 | 0.80209 | 64167.2 | 0.3698 | 13312.8 | 0.65659 | 7879.08 | 1 | 5000 | 13312.8 | 7879.08 | 0 | 0 | 0 | 0 | 37975.32 | 0 | 0 | 0 | 0 | 0 | 37975.32
2022091417 | 4 | 0.81561 | 65248.8 | 0.39661 | 14277.96 | 0.59242 | 7109.04 | 1 | 5000 | 14277.96 | 7109.04 | 0 | 0 | 0 | 0 | 38861.8 | 0 | 0 | 0 | 0 | 0 | 38861.8
2022091418 | 4 | 0.81086 | 64868.8 | 0.40292 | 14505.12 | 0.4538 | 5445.6 | 1 | 5000 | 14505.12 | 5445.6 | 0 | 0 | 0 | 0 | 39918.08 | 0 | 0 | 0 | 0 | 0 | 39918.08
2022091419 | 4 | 0.78211 | 62568.8 | 0.40607 | 14618.52 | 0.25505 | 3060.6 | 1 | 5000 | 14618.52 | 3060.6 | 0 | 0 | 0 | 0 | 39889.68 | 0 | 0 | 0 | 0 | 0 | 39889.68
2022091420 | 4 | 0.74708 | 59766.4 | 0.3751 | 13503.6 | 0.03694 | 443.28 | 1 | 5000 | 13503.6 | 443.28 | 0 | 0 | 0 | 0 | 40819.52 | 0 | 0 | 0 | 0 | 0 | 40819.52
2022091421 | 4 | 0.72514 | 58011.2 | 0.39126 | 14085.36 | 0 | 0 | 1 | 5000 | 14085.36 | 0 | 0 | 0 | 0 | 0 | 38925.84 | 0 | 0 | 0 | 0 | 0 | 38925.84
2022091422 | 4 | 0.68581 | 54864.8 | 0.43501 | 15660.36 | 0 | 0 | 1 | 5000 | 15660.36 | 0 | 0 | 0 | 0 | 0 | 34204.44 | 0 | 0 | 0 | 0 | 0 | 34204.44
2022091423 | 4 | 0.63701 | 50960.8 | 0.44074 | 15866.64 | 0 | 0 | 1 | 5000 | 15866.64 | 0 | 0 | 0 | 0 | 0 | 30094.16 | 0 | 0 | 0 | 0 | 0 | 30094.16
2022091424 | 4 | 0.58608 | 46886.4 | 0.43625 | 15705 | 0 | 0 | 1 | 5000 | 15705 | 0 | 0 | 0 | 0 | 0 | 26181.4 | 0 | 0 | 0 | 0 | 0 | 26181.4
2022091501 | 5 | 0.54659 | 43727.2 | 0.42229 | 15202.44 | 0 | 0 | 1 | 5000 | 15202.44 | 0 | 0 | 0 | 0 | 0 | 23524.76 | 0 | 0 | 0 | 0 | 0 | 23524.76
2022091502 | 5 | 0.51817 | 41453.6 | 0.40875 | 14715 | 0 | 0 | 1 | 5000 | 14715 | 0 | 0 | 0 | 0 | 0 | 21738.6 | 0 | 0 | 0 | 0 | 0 | 21738.6
2022091503 | 5 | 0.49907 | 39925.6 | 0.39639 | 14270.04 | 0 | 0 | 1 | 5000 | 14270.04 | 0 | 0 | 0 | 0 | 0 | 20655.56 | 0 | 0 | 0 | 0 | 0 | 20655.56
2022091504 | 5 | 0.48826 | 39060.8 | 0.39366 | 14171.76 | 0 | 0 | 1 | 5000 | 14171.76 | 0 | 0 | 0 | 0 | 0 | 19889.04 | 0 | 0 | 0 | 0 | 0 | 19889.04
2022091505 | 5 | 0.48351 | 38680.8 | 0.38211 | 13755.96 | 0 | 0 | 1 | 5000 | 13755.96 | 0 | 0 | 0 | 0 | 0 | 19924.84 | 0 | 0 | 0 | 0 | 0 | 19924.84
2022091506 | 5 | 0.49827 | 39861.6 | 0.3613 | 13006.8 | 0 | 0 | 1 | 5000 | 13006.8 | 0 | 0 | 0 | 0 | 0 | 21854.8 | 0 | 0 | 0 | 0 | 0 | 21854.8
2022091507 | 5 | 0.52588 | 42070.4 | 0.34854 | 12547.44 | 0 | 0 | 1 | 5000 | 12547.44 | 0 | 0 | 0 | 0 | 0 | 24522.96 | 0 | 0 | 0 | 0 | 0 | 24522.96
2022091508 | 5 | 0.53395 | 42716 | 0.3562 | 12823.2 | 0.02535 | 304.2 | 1 | 5000 | 12823.2 | 304.2 | 0 | 0 | 0 | 0 | 24588.6 | 0 | 0 | 0 | 0 | 0 | 24588.6
2022091509 | 5 | 0.55014 | 44011.2 | 0.31331 | 11279.16 | 0.32409 | 3889.08 | 1 | 5000 | 11279.16 | 3889.08 | 0 | 0 | 0 | 0 | 23842.96 | 0 | 0 | 0 | 0 | 0 | 23842.96
2022091510 | 5 | 0.58255 | 46604 | 0.31564 | 11363.04 | 0.65486 | 7858.32 | 1 | 5000 | 11363.04 | 7858.32 | 0 | 0 | 0 | 0 | 22382.64 | 0 | 0 | 0 | 0 | 0 | 22382.64
2022091511 | 5 | 0.62217 | 49773.6 | 0.34571 | 12445.56 | 0.70533 | 8463.96 | 1 | 5000 | 12445.56 | 8463.96 | 0 | 0 | 0 | 0 | 23864.08 | 0 | 0 | 0 | 0 | 0 | 23864.08
2022091512 | 5 | 0.66372 | 53097.6 | 0.31052 | 11178.72 | 0.72637 | 8716.44 | 1 | 5000 | 11178.72 | 8716.44 | 0 | 0 | 0 | 0 | 28202.44 | 0 | 0 | 0 | 0 | 0 | 28202.44
2022091513 | 5 | 0.70353 | 56282.4 | 0.27434 | 9876.24 | 0.71398 | 8567.76 | 1 | 5000 | 9876.24 | 8567.76 | 0 | 0 | 0 | 0 | 32838.4 | 0 | 0 | 0 | 0 | 0 | 32838.4
2022091514 | 5 | 0.74233 | 59386.4 | 0.2657 | 9565.2 | 0.74359 | 8923.08 | 1 | 5000 | 9565.2 | 8923.08 | 0 | 0 | 0 | 0 | 35898.12 | 0 | 0 | 0 | 0 | 0 | 35898.12
2022091515 | 5 | 0.77206 | 61764.8 | 0.24694 | 8889.84 | 0.74755 | 8970.6 | 1 | 5000 | 8889.84 | 8970.6 | 0 | 0 | 0 | 0 | 38904.36 | 0 | 0 | 0 | 0 | 0 | 38904.36
2022091516 | 5 | 0.796 | 63680 | 0.25199 | 9071.64 | 0.74178 | 8901.36 | 1 | 5000 | 9071.64 | 8901.36 | 0 | 0 | 0 | 0 | 40707 | 0 | 0 | 0 | 0 | 0 | 40707
2022091517 | 5 | 0.81194 | 64955.2 | 0.2833 | 10198.8 | 0.71926 | 8631.12 | 1 | 5000 | 10198.8 | 8631.12 | 0 | 0 | 0 | 0 | 41125.28 | 0 | 0 | 0 | 0 | 0 | 41125.28
2022091518 | 5 | 0.80965 | 64772 | 0.33912 | 12208.32 | 0.66683 | 8001.96 | 1 | 5000 | 12208.32 | 8001.96 | 0 | 0 | 0 | 0 | 39561.72 | 0 | 0 | 0 | 0 | 0 | 39561.72
2022091519 | 5 | 0.78422 | 62737.6 | 0.37603 | 13537.08 | 0.42008 | 5040.96 | 1 | 5000 | 13537.08 | 5040.96 | 0 | 0 | 0 | 0 | 39159.56 | 0 | 0 | 0 | 0 | 0 | 39159.56
2022091520 | 5 | 0.7518 | 60144 | 0.37445 | 13480.2 | 0.05023 | 602.76 | 1 | 5000 | 13480.2 | 602.76 | 0 | 0 | 0 | 0 | 41061.04 | 0 | 0 | 0 | 0 | 0 | 41061.04
2022091521 | 5 | 0.73343 | 58674.4 | 0.39503 | 14221.08 | 0 | 0 | 1 | 5000 | 14221.08 | 0 | 0 | 0 | 0 | 0 | 39453.32 | 0 | 0 | 0 | 0 | 0 | 39453.32
2022091522 | 5 | 0.70035 | 56028 | 0.45476 | 16371.36 | 0 | 0 | 1 | 5000 | 16371.36 | 0 | 0 | 0 | 0 | 0 | 34656.64 | 0 | 0 | 0 | 0 | 0 | 34656.64
2022091523 | 5 | 0.65774 | 52619.2 | 0.50119 | 18042.84 | 0 | 0 | 1 | 5000 | 18042.84 | 0 | 0 | 0 | 0 | 0 | 29576.36 | 0 | 0 | 0 | 0 | 0 | 29576.36
2022091524 | 5 | 0.61222 | 48977.6 | 0.51701 | 18612.36 | 0 | 0 | 1 | 5000 | 18612.36 | 0 | 0 | 0 | 0 | 0 | 25365.24 | 0 | 0 | 0 | 0 | 0 | 25365.24
2022091601 | 6 | 0.57524 | 46019.2 | 0.51545 | 18556.2 | 0 | 0 | 1 | 5000 | 18556.2 | 0 | 0 | 0 | 0 | 0 | 22463 | 0 | 0 | 0 | 0 | 0 | 22463
2022091602 | 6 | 0.54707 | 43765.6 | 0.50417 | 18150.12 | 0 | 0 | 1 | 5000 | 18150.12 | 0 | 0 | 0 | 0 | 0 | 20615.48 | 0 | 0 | 0 | 0 | 0 | 20615.48
2022091603 | 6 | 0.52942 | 42353.6 | 0.49221 | 17719.56 | 0 | 0 | 1 | 5000 | 17719.56 | 0 | 0 | 0 | 0 | 0 | 19634.04 | 0 | 0 | 0 | 0 | 0 | 19634.04
2022091604 | 6 | 0.52025 | 41620 | 0.49349 | 17765.64 | 0 | 0 | 1 | 5000 | 17765.64 | 0 | 0 | 0 | 0 | 0 | 18854.36 | 0 | 0 | 0 | 0 | 0 | 18854.36
2022091605 | 6 | 0.51964 | 41571.2 | 0.47669 | 17160.84 | 0 | 0 | 1 | 5000 | 17160.84 | 0 | 0 | 0 | 0 | 0 | 19410.36 | 0 | 0 | 0 | 0 | 0 | 19410.36
2022091606 | 6 | 0.53608 | 42886.4 | 0.44592 | 16053.12 | 0 | 0 | 1 | 5000 | 16053.12 | 0 | 0 | 0 | 0 | 0 | 21833.28 | 0 | 0 | 0 | 0 | 0 | 21833.28
2022091607 | 6 | 0.5627 | 45016 | 0.41223 | 14840.28 | 0 | 0 | 1 | 5000 | 14840.28 | 0 | 0 | 0 | 0 | 0 | 25175.72 | 0 | 0 | 0 | 0 | 0 | 25175.72
2022091608 | 6 | 0.57266 | 45812.8 | 0.39569 | 14244.84 | 0.02111 | 253.32 | 1 | 5000 | 14244.84 | 253.32 | 0 | 0 | 0 | 0 | 26314.64 | 0 | 0 | 0 | 0 | 0 | 26314.64
2022091609 | 6 | 0.58926 | 47140.8 | 0.3204 | 11534.4 | 0.33659 | 4039.08 | 1 | 5000 | 11534.4 | 4039.08 | 0 | 0 | 0 | 0 | 26567.32 | 0 | 0 | 0 | 0 | 0 | 26567.32
2022091610 | 6 | 0.62688 | 50150.4 | 0.32351 | 11646.36 | 0.67059 | 8047.08 | 1 | 5000 | 11646.36 | 8047.08 | 0 | 0 | 0 | 0 | 25456.96 | 0 | 0 | 0 | 0 | 0 | 25456.96
2022091611 | 6 | 0.67391 | 53912.8 | 0.37972 | 13669.92 | 0.68652 | 8238.24 | 1 | 5000 | 13669.92 | 8238.24 | 0 | 0 | 0 | 0 | 27004.64 | 0 | 0 | 0 | 0 | 0 | 27004.64
2022091612 | 6 | 0.71747 | 57397.6 | 0.34305 | 12349.8 | 0.73282 | 8793.84 | 1 | 5000 | 12349.8 | 8793.84 | 0 | 0 | 0 | 0 | 31253.96 | 0 | 0 | 0 | 0 | 0 | 31253.96
2022091613 | 6 | 0.757 | 60560 | 0.30933 | 11135.88 | 0.72674 | 8720.88 | 1 | 5000 | 11135.88 | 8720.88 | 0 | 0 | 0 | 0 | 35703.24 | 0 | 0 | 0 | 0 | 0 | 35703.24
2022091614 | 6 | 0.79571 | 63656.8 | 0.29195 | 10510.2 | 0.71546 | 8585.52 | 1 | 5000 | 10510.2 | 8585.52 | 0 | 0 | 0 | 0 | 39561.08 | 0 | 0 | 0 | 0 | 0 | 39561.08
2022091615 | 6 | 0.82013 | 65610.4 | 0.28665 | 10319.4 | 0.72417 | 8690.04 | 1 | 5000 | 10319.4 | 8690.04 | 0 | 0 | 0 | 0 | 41600.96 | 0 | 0 | 0 | 0 | 0 | 41600.96
2022091616 | 6 | 0.82963 | 66370.4 | 0.28558 | 10280.88 | 0.71444 | 8573.28 | 1 | 5000 | 10280.88 | 8573.28 | 0 | 0 | 0 | 0 | 42516.24 | 0 | 0 | 0 | 0 | 0 | 42516.24
2022091617 | 6 | 0.83502 | 66801.6 | 0.29398 | 10583.28 | 0.67882 | 8145.84 | 1 | 5000 | 10583.28 | 8145.84 | 0 | 0 | 0 | 0 | 43072.48 | 0 | 0 | 0 | 0 | 0 | 43072.48
2022091618 | 6 | 0.83284 | 66627.2 | 0.33072 | 11905.92 | 0.62345 | 7481.4 | 1 | 5000 | 11905.92 | 7481.4 | 0 | 0 | 0 | 0 | 42239.88 | 0 | 0 | 0 | 0 | 0 | 42239.88
2022091619 | 6 | 0.81032 | 64825.6 | 0.38093 | 13713.48 | 0.40543 | 4865.16 | 1 | 5000 | 13713.48 | 4865.16 | 0 | 0 | 0 | 0 | 41246.96 | 0 | 0 | 0 | 0 | 0 | 41246.96
2022091620 | 6 | 0.77774 | 62219.2 | 0.4064 | 14630.4 | 0.05422 | 650.64 | 1 | 5000 | 14630.4 | 650.64 | 0 | 0 | 0 | 0 | 41938.16 | 0 | 0 | 0 | 0 | 0 | 41938.16
2022091621 | 6 | 0.75537 | 60429.6 | 0.46411 | 16707.96 | 0 | 0 | 1 | 5000 | 16707.96 | 0 | 0 | 0 | 0 | 0 | 38721.64 | 0 | 0 | 0 | 0 | 0 | 38721.64
2022091622 | 6 | 0.72589 | 58071.2 | 0.52748 | 18989.28 | 0 | 0 | 1 | 5000 | 18989.28 | 0 | 0 | 0 | 0 | 0 | 34081.92 | 0 | 0 | 0 | 0 | 0 | 34081.92
2022091623 | 6 | 0.68898 | 55118.4 | 0.55567 | 20004.12 | 0 | 0 | 1 | 5000 | 20004.12 | 0 | 0 | 0 | 0 | 0 | 30114.28 | 0 | 0 | 0 | 0 | 0 | 30114.28
2022091624 | 6 | 0.65078 | 52062.4 | 0.56721 | 20419.56 | 0 | 0 | 1 | 5000 | 20419.56 | 0 | 0 | 0 | 0 | 0 | 26642.84 | 0 | 0 | 0 | 0 | 0 | 26642.84
2022091701 | 7 | 0.61426 | 49140.8 | 0.56215 | 20237.4 | 0 | 0 | 1 | 5000 | 20237.4 | 0 | 0 | 0 | 0 | 0 | 23903.4 | 0 | 0 | 0 | 0 | 0 | 23903.4
2022091702 | 7 | 0.58568 | 46854.4 | 0.55371 | 19933.56 | 0 | 0 | 1 | 5000 | 19933.56 | 0 | 0 | 0 | 0 | 0 | 21920.84 | 0 | 0 | 0 | 0 | 0 | 21920.84
2022091703 | 7 | 0.56459 | 45167.2 | 0.54844 | 19743.84 | 0 | 0 | 1 | 5000 | 19743.84 | 0 | 0 | 0 | 0 | 0 | 20423.36 | 0 | 0 | 0 | 0 | 0 | 20423.36
2022091704 | 7 | 0.54984 | 43987.2 | 0.52749 | 18989.64 | 0 | 0 | 1 | 5000 | 18989.64 | 0 | 0 | 0 | 0 | 0 | 19997.56 | 0 | 0 | 0 | 0 | 0 | 19997.56
2022091705 | 7 | 0.54098 | 43278.4 | 0.50673 | 18242.28 | 0 | 0 | 1 | 5000 | 18242.28 | 0 | 0 | 0 | 0 | 0 | 20036.12 | 0 | 0 | 0 | 0 | 0 | 20036.12
2022091706 | 7 | 0.54284 | 43427.2 | 0.48153 | 17335.08 | 0 | 0 | 1 | 5000 | 17335.08 | 0 | 0 | 0 | 0 | 0 | 21092.12 | 0 | 0 | 0 | 0 | 0 | 21092.12
2022091707 | 7 | 0.54677 | 43741.6 | 0.45788 | 16483.68 | 0 | 0 | 1 | 5000 | 16483.68 | 0 | 0 | 0 | 0 | 0 | 22257.92 | 0 | 0 | 0 | 0 | 0 | 22257.92
2022091708 | 7 | 0.55393 | 44314.4 | 0.43491 | 15656.76 | 0.01637 | 196.44 | 1 | 5000 | 15656.76 | 196.44 | 0 | 0 | 0 | 0 | 23461.2 | 0 | 0 | 0 | 0 | 0 | 23461.2
2022091709 | 7 | 0.58358 | 46686.4 | 0.3874 | 13946.4 | 0.30145 | 3617.4 | 1 | 5000 | 13946.4 | 3617.4 | 0 | 0 | 0 | 0 | 24122.6 | 0 | 0 | 0 | 0 | 0 | 24122.6
2022091710 | 7 | 0.63222 | 50577.6 | 0.42207 | 15194.52 | 0.53448 | 6413.76 | 1 | 5000 | 15194.52 | 6413.76 | 0 | 0 | 0 | 0 | 23969.32 | 0 | 0 | 0 | 0 | 0 | 23969.32
2022091711 | 7 | 0.67897 | 54317.6 | 0.48606 | 17498.16 | 0.4388 | 5265.6 | 1 | 5000 | 17498.16 | 5265.6 | 0 | 0 | 0 | 0 | 26553.84 | 0 | 0 | 0 | 0 | 0 | 26553.84
2022091712 | 7 | 0.72531 | 58024.8 | 0.47826 | 17217.36 | 0.49382 | 5925.84 | 1 | 5000 | 17217.36 | 5925.84 | 0 | 0 | 0 | 0 | 29881.6 | 0 | 0 | 0 | 0 | 0 | 29881.6
2022091713 | 7 | 0.76905 | 61524 | 0.44543 | 16035.48 | 0.60272 | 7232.64 | 1 | 5000 | 16035.48 | 7232.64 | 0 | 0 | 0 | 0 | 33255.88 | 0 | 0 | 0 | 0 | 0 | 33255.88
2022091714 | 7 | 0.80369 | 64295.2 | 0.42836 | 15420.96 | 0.67224 | 8066.88 | 1 | 5000 | 15420.96 | 8066.88 | 0 | 0 | 0 | 0 | 35807.36 | 0 | 0 | 0 | 0 | 0 | 35807.36
2022091715 | 7 | 0.82809 | 66247.2 | 0.42369 | 15252.84 | 0.69452 | 8334.24 | 1 | 5000 | 15252.84 | 8334.24 | 0 | 0 | 0 | 0 | 37660.12 | 0 | 0 | 0 | 0 | 0 | 37660.12
2022091716 | 7 | 0.84239 | 67391.2 | 0.41997 | 15118.92 | 0.70234 | 8428.08 | 1 | 5000 | 15118.92 | 8428.08 | 0 | 0 | 0 | 0 | 38844.2 | 0 | 0 | 0 | 0 | 0 | 38844.2
2022091717 | 7 | 0.84664 | 67731.2 | 0.41611 | 14979.96 | 0.70706 | 8484.72 | 1 | 5000 | 14979.96 | 8484.72 | 0 | 0 | 0 | 0 | 39266.52 | 0 | 0 | 0 | 0 | 0 | 39266.52
2022091718 | 7 | 0.84051 | 67240.8 | 0.42678 | 15364.08 | 0.66135 | 7936.2 | 1 | 5000 | 15364.08 | 7936.2 | 0 | 0 | 0 | 0 | 38940.52 | 0 | 0 | 0 | 0 | 0 | 38940.52
2022091719 | 7 | 0.81927 | 65541.6 | 0.44426 | 15993.36 | 0.41057 | 4926.84 | 1 | 5000 | 15993.36 | 4926.84 | 0 | 0 | 0 | 0 | 39621.4 | 0 | 0 | 0 | 0 | 0 | 39621.4
2022091720 | 7 | 0.78387 | 62709.6 | 0.43036 | 15492.96 | 0.05294 | 635.28 | 1 | 5000 | 15492.96 | 635.28 | 0 | 0 | 0 | 0 | 41581.36 | 0 | 0 | 0 | 0 | 0 | 41581.36
2022091721 | 7 | 0.75928 | 60742.4 | 0.4304 | 15494.4 | 0 | 0 | 1 | 5000 | 15494.4 | 0 | 0 | 0 | 0 | 0 | 40248 | 0 | 0 | 0 | 0 | 0 | 40248
2022091722 | 7 | 0.72705 | 58164 | 0.47766 | 17195.76 | 0 | 0 | 1 | 5000 | 17195.76 | 0 | 0 | 0 | 0 | 0 | 35968.24 | 0 | 0 | 0 | 0 | 0 | 35968.24
2022091723 | 7 | 0.68987 | 55189.6 | 0.49892 | 17961.12 | 0 | 0 | 1 | 5000 | 17961.12 | 0 | 0 | 0 | 0 | 0 | 32228.48 | 0 | 0 | 0 | 0 | 0 | 32228.48
2022091724 | 7 | 0.65137 | 52109.6 | 0.49885 | 17958.6 | 0 | 0 | 1 | 5000 | 17958.6 | 0 | 0 | 0 | 0 | 0 | 29151 | 0 | 0 | 0 | 0 | 0 | 29151
2022091801 | 1 | 0.61604 | 49283.2 | 0.49758 | 17912.88 | 0 | 0 | 1 | 5000 | 17912.88 | 0 | 0 | 0 | 0 | 0 | 26370.32 | 0 | 0 | 0 | 0 | 0 | 26370.32
2022091802 | 1 | 0.58639 | 46911.2 | 0.48582 | 17489.52 | 0 | 0 | 1 | 5000 | 17489.52 | 0 | 0 | 0 | 0 | 0 | 24421.68 | 0 | 0 | 0 | 0 | 0 | 24421.68
2022091803 | 1 | 0.56047 | 44837.6 | 0.46443 | 16719.48 | 0 | 0 | 1 | 5000 | 16719.48 | 0 | 0 | 0 | 0 | 0 | 23118.12 | 0 | 0 | 0 | 0 | 0 | 23118.12
2022091804 | 1 | 0.54445 | 43556 | 0.45386 | 16338.96 | 0 | 0 | 1 | 5000 | 16338.96 | 0 | 0 | 0 | 0 | 0 | 22217.04 | 0 | 0 | 0 | 0 | 0 | 22217.04
2022091805 | 1 | 0.53441 | 42752.8 | 0.44405 | 15985.8 | 0 | 0 | 1 | 5000 | 15985.8 | 0 | 0 | 0 | 0 | 0 | 21767 | 0 | 0 | 0 | 0 | 0 | 21767
2022091806 | 1 | 0.53288 | 42630.4 | 0.44009 | 15843.24 | 0 | 0 | 1 | 5000 | 15843.24 | 0 | 0 | 0 | 0 | 0 | 21787.16 | 0 | 0 | 0 | 0 | 0 | 21787.16
2022091807 | 1 | 0.53054 | 42443.2 | 0.43655 | 15715.8 | 0 | 0 | 1 | 5000 | 15715.8 | 0 | 0 | 0 | 0 | 0 | 21727.4 | 0 | 0 | 0 | 0 | 0 | 21727.4
2022091808 | 1 | 0.53294 | 42635.2 | 0.41394 | 14901.84 | 0.02207 | 264.84 | 1 | 5000 | 14901.84 | 264.84 | 0 | 0 | 0 | 0 | 22468.52 | 0 | 0 | 0 | 0 | 0 | 22468.52
2022091809 | 1 | 0.5636 | 45088 | 0.36084 | 12990.24 | 0.32649 | 3917.88 | 1 | 5000 | 12990.24 | 3917.88 | 0 | 0 | 0 | 0 | 23179.88 | 0 | 0 | 0 | 0 | 0 | 23179.88
2022091810 | 1 | 0.6183 | 49464 | 0.38577 | 13887.72 | 0.50614 | 6073.68 | 1 | 5000 | 13887.72 | 6073.68 | 0 | 0 | 0 | 0 | 24502.6 | 0 | 0 | 0 | 0 | 0 | 24502.6
2022091811 | 1 | 0.66793 | 53434.4 | 0.39194 | 14109.84 | 0.46264 | 5551.68 | 1 | 5000 | 14109.84 | 5551.68 | 0 | 0 | 0 | 0 | 28772.88 | 0 | 0 | 0 | 0 | 0 | 28772.88
2022091812 | 1 | 0.71731 | 57384.8 | 0.35183 | 12665.88 | 0.57065 | 6847.8 | 1 | 5000 | 12665.88 | 6847.8 | 0 | 0 | 0 | 0 | 32871.12 | 0 | 0 | 0 | 0 | 0 | 32871.12
2022091813 | 1 | 0.76543 | 61234.4 | 0.31409 | 11307.24 | 0.65695 | 7883.4 | 1 | 5000 | 11307.24 | 7883.4 | 0 | 0 | 0 | 0 | 37043.76 | 0 | 0 | 0 | 0 | 0 | 37043.76
2022091814 | 1 | 0.80511 | 64408.8 | 0.28499 | 10259.64 | 0.72837 | 8740.44 | 1 | 5000 | 10259.64 | 8740.44 | 0 | 0 | 0 | 0 | 40408.72 | 0 | 0 | 0 | 0 | 0 | 40408.72
2022091815 | 1 | 0.83555 | 66844 | 0.26609 | 9579.24 | 0.73661 | 8839.32 | 1 | 5000 | 9579.24 | 8839.32 | 0 | 0 | 0 | 0 | 43425.44 | 0 | 0 | 0 | 0 | 0 | 43425.44
2022091816 | 1 | 0.8501 | 68008 | 0.25801 | 9288.36 | 0.74578 | 8949.36 | 1 | 5000 | 9288.36 | 8949.36 | 0 | 0 | 0 | 0 | 44770.28 | 0 | 0 | 0 | 0 | 0 | 44770.28
2022091817 | 1 | 0.85981 | 68784.8 | 0.27796 | 10006.56 | 0.72568 | 8708.16 | 1 | 5000 | 10006.56 | 8708.16 | 0 | 0 | 0 | 0 | 45070.08 | 0 | 0 | 0 | 0 | 0 | 45070.08
2022091818 | 1 | 0.85875 | 68700 | 0.30981 | 11153.16 | 0.65756 | 7890.72 | 1 | 5000 | 11153.16 | 7890.72 | 0 | 0 | 0 | 0 | 44656.12 | 0 | 0 | 0 | 0 | 0 | 44656.12
2022091819 | 1 | 0.84255 | 67404 | 0.35027 | 12609.72 | 0.40969 | 4916.28 | 1 | 5000 | 12609.72 | 4916.28 | 0 | 0 | 0 | 0 | 44878 | 0 | 0 | 0 | 0 | 0 | 44878
2022091820 | 1 | 0.81438 | 65150.4 | 0.38549 | 13877.64 | 0.04351 | 522.12 | 1 | 5000 | 13877.64 | 522.12 | 0 | 0 | 0 | 0 | 45750.64 | 0 | 0 | 0 | 0 | 0 | 45750.64
2022091821 | 1 | 0.79119 | 63295.2 | 0.41999 | 15119.64 | 0 | 0 | 1 | 5000 | 15119.64 | 0 | 0 | 0 | 0 | 0 | 43175.56 | 0 | 0 | 0 | 0 | 0 | 43175.56
2022091822 | 1 | 0.75593 | 60474.4 | 0.46252 | 16650.72 | 0 | 0 | 1 | 5000 | 16650.72 | 0 | 0 | 0 | 0 | 0 | 38823.68 | 0 | 0 | 0 | 0 | 0 | 38823.68
2022091823 | 1 | 0.70708 | 56566.4 | 0.47205 | 16993.8 | 0 | 0 | 1 | 5000 | 16993.8 | 0 | 0 | 0 | 0 | 0 | 34572.6 | 0 | 0 | 0 | 0 | 0 | 34572.6
2022091824 | 1 | 0.65637 | 52509.6 | 0.46431 | 16715.16 | 0 | 0 | 1 | 5000 | 16715.16 | 0 | 0 | 0 | 0 | 0 | 30794.44 | 0 | 0 | 0 | 0 | 0 | 30794.44
2022091901 | 2 | 0.61254 | 49003.2 | 0.44487 | 16015.32 | 0 | 0 | 1 | 5000 | 16015.32 | 0 | 0 | 0 | 0 | 0 | 27987.88 | 0 | 0 | 0 | 0 | 0 | 27987.88
2022091902 | 2 | 0.58164 | 46531.2 | 0.4313 | 15526.8 | 0 | 0 | 1 | 5000 | 15526.8 | 0 | 0 | 0 | 0 | 0 | 26004.4 | 0 | 0 | 0 | 0 | 0 | 26004.4
2022091903 | 2 | 0.5609 | 44872 | 0.41832 | 15059.52 | 0 | 0 | 1 | 5000 | 15059.52 | 0 | 0 | 0 | 0 | 0 | 24812.48 | 0 | 0 | 0 | 0 | 0 | 24812.48
2022091904 | 2 | 0.55069 | 44055.2 | 0.41369 | 14892.84 | 0 | 0 | 1 | 5000 | 14892.84 | 0 | 0 | 0 | 0 | 0 | 24162.36 | 0 | 0 | 0 | 0 | 0 | 24162.36
2022091905 | 2 | 0.5495 | 43960 | 0.38679 | 13924.44 | 0 | 0 | 1 | 5000 | 13924.44 | 0 | 0 | 0 | 0 | 0 | 25035.56 | 0 | 0 | 0 | 0 | 0 | 25035.56
2022091906 | 2 | 0.56584 | 45267.2 | 0.33944 | 12219.84 | 0 | 0 | 1 | 5000 | 12219.84 | 0 | 0 | 0 | 0 | 0 | 28047.36 | 0 | 0 | 0 | 0 | 0 | 28047.36
2022091907 | 2 | 0.58957 | 47165.6 | 0.30128 | 10846.08 | 0 | 0 | 1 | 5000 | 10846.08 | 0 | 0 | 0 | 0 | 0 | 31319.52 | 0 | 0 | 0 | 0 | 0 | 31319.52
2022091908 | 2 | 0.59716 | 47772.8 | 0.26218 | 9438.48 | 0.02023 | 242.76 | 1 | 5000 | 9438.48 | 242.76 | 0 | 0 | 0 | 0 | 33091.56 | 0 | 0 | 0 | 0 | 0 | 33091.56
2022091909 | 2 | 0.61773 | 49418.4 | 0.20368 | 7332.48 | 0.29056 | 3486.72 | 1 | 5000 | 7332.48 | 3486.72 | 0 | 0 | 0 | 0 | 33599.2 | 0 | 0 | 0 | 0 | 0 | 33599.2
2022091910 | 2 | 0.66215 | 52972 | 0.19853 | 7147.08 | 0.56385 | 6766.2 | 1 | 5000 | 7147.08 | 6766.2 | 0 | 0 | 0 | 0 | 34058.72 | 0 | 0 | 0 | 0 | 0 | 34058.72
2022091911 | 2 | 0.71406 | 57124.8 | 0.22714 | 8177.04 | 0.65886 | 7906.32 | 1 | 5000 | 8177.04 | 7906.32 | 0 | 0 | 0 | 0 | 36041.44 | 0 | 0 | 0 | 0 | 0 | 36041.44
2022091912 | 2 | 0.76437 | 61149.6 | 0.20348 | 7325.28 | 0.69857 | 8382.84 | 1 | 5000 | 7325.28 | 8382.84 | 0 | 0 | 0 | 0 | 40441.48 | 0 | 0 | 0 | 0 | 0 | 40441.48
2022091913 | 2 | 0.80651 | 64520.8 | 0.19971 | 7189.56 | 0.68234 | 8188.08 | 1 | 5000 | 7189.56 | 8188.08 | 0 | 0 | 0 | 0 | 44143.16 | 0 | 0 | 0 | 0 | 0 | 44143.16
2022091914 | 2 | 0.85013 | 68010.4 | 0.21786 | 7842.96 | 0.66046 | 7925.52 | 1 | 5000 | 7842.96 | 7925.52 | 0 | 0 | 0 | 0 | 47241.92 | 0 | 0 | 0 | 0 | 0 | 47241.92
2022091915 | 2 | 0.86745 | 69396 | 0.22468 | 8088.48 | 0.67849 | 8141.88 | 1 | 5000 | 8088.48 | 8141.88 | 0 | 0 | 0 | 0 | 48165.64 | 0 | 0 | 0 | 0 | 0 | 48165.64
2022091916 | 2 | 0.8736 | 69888 | 0.23116 | 8321.76 | 0.66657 | 7998.84 | 1 | 5000 | 8321.76 | 7998.84 | 0 | 0 | 0 | 0 | 48567.4 | 0 | 0 | 0 | 0 | 0 | 48567.4
2022091917 | 2 | 0.87918 | 70334.4 | 0.24396 | 8782.56 | 0.65375 | 7845 | 1 | 5000 | 8782.56 | 7845 | 0 | 0 | 0 | 0 | 48706.84 | 0 | 0 | 0 | 0 | 0 | 48706.84
2022091918 | 2 | 0.87492 | 69993.6 | 0.27019 | 9726.84 | 0.61254 | 7350.48 | 1 | 5000 | 9726.84 | 7350.48 | 0 | 0 | 0 | 0 | 47916.28 | 0 | 0 | 0 | 0 | 0 | 47916.28
2022091919 | 2 | 0.86163 | 68930.4 | 0.27995 | 10078.2 | 0.35782 | 4293.84 | 1 | 5000 | 10078.2 | 4293.84 | 0 | 0 | 0 | 0 | 49558.36 | 0 | 0 | 0 | 0 | 0 | 49558.36
2022091920 | 2 | 0.83345 | 66676 | 0.25973 | 9350.28 | 0.03477 | 417.24 | 1 | 5000 | 9350.28 | 417.24 | 0 | 0 | 0 | 0 | 51908.48 | 0 | 0 | 0 | 0 | 0 | 51908.48
2022091921 | 2 | 0.81098 | 64878.4 | 0.29835 | 10740.6 | 0 | 0 | 1 | 5000 | 10740.6 | 0 | 0 | 0 | 0 | 0 | 49137.8 | 0 | 0 | 0 | 0 | 0 | 49137.8
2022091922 | 2 | 0.76998 | 61598.4 | 0.36228 | 13042.08 | 0 | 0 | 1 | 5000 | 13042.08 | 0 | 0 | 0 | 0 | 0 | 43556.32 | 0 | 0 | 0 | 0 | 0 | 43556.32
2022091923 | 2 | 0.71692 | 57353.6 | 0.40801 | 14688.36 | 0 | 0 | 1 | 5000 | 14688.36 | 0 | 0 | 0 | 0 | 0 | 37665.24 | 0 | 0 | 0 | 0 | 0 | 37665.24
2022091924 | 2 | 0.66543 | 53234.4 | 0.42435 | 15276.6 | 0 | 0 | 1 | 5000 | 15276.6 | 0 | 0 | 0 | 0 | 0 | 32957.8 | 0 | 0 | 0 | 0 | 0 | 32957.8
2022092001 | 3 | 0.62346 | 49876.8 | 0.42115 | 15161.4 | 0 | 0 | 1 | 5000 | 15161.4 | 0 | 0 | 0 | 0 | 0 | 29715.4 | 0 | 0 | 0 | 0 | 0 | 29715.4
2022092002 | 3 | 0.5927 | 47416 | 0.40698 | 14651.28 | 0 | 0 | 1 | 5000 | 14651.28 | 0 | 0 | 0 | 0 | 0 | 27764.72 | 0 | 0 | 0 | 0 | 0 | 27764.72
2022092003 | 3 | 0.57089 | 45671.2 | 0.37308 | 13430.88 | 0 | 0 | 1 | 5000 | 13430.88 | 0 | 0 | 0 | 0 | 0 | 27240.32 | 0 | 0 | 0 | 0 | 0 | 27240.32
2022092004 | 3 | 0.55762 | 44609.6 | 0.35117 | 12642.12 | 0 | 0 | 1 | 5000 | 12642.12 | 0 | 0 | 0 | 0 | 0 | 26967.48 | 0 | 0 | 0 | 0 | 0 | 26967.48
2022092005 | 3 | 0.55575 | 44460 | 0.33172 | 11941.92 | 0 | 0 | 1 | 5000 | 11941.92 | 0 | 0 | 0 | 0 | 0 | 27518.08 | 0 | 0 | 0 | 0 | 0 | 27518.08
2022092006 | 3 | 0.57263 | 45810.4 | 0.31414 | 11309.04 | 0 | 0 | 1 | 5000 | 11309.04 | 0 | 0 | 0 | 0 | 0 | 29501.36 | 0 | 0 | 0 | 0 | 0 | 29501.36
2022092007 | 3 | 0.59762 | 47809.6 | 0.31313 | 11272.68 | 0 | 0 | 1 | 5000 | 11272.68 | 0 | 0 | 0 | 0 | 0 | 31536.92 | 0 | 0 | 0 | 0 | 0 | 31536.92
2022092008 | 3 | 0.60439 | 48351.2 | 0.29885 | 10758.6 | 0.01997 | 239.64 | 1 | 5000 | 10758.6 | 239.64 | 0 | 0 | 0 | 0 | 32352.96 | 0 | 0 | 0 | 0 | 0 | 32352.96
2022092009 | 3 | 0.62324 | 49859.2 | 0.24236 | 8724.96 | 0.32875 | 3945 | 1 | 5000 | 8724.96 | 3945 | 0 | 0 | 0 | 0 | 32189.24 | 0 | 0 | 0 | 0 | 0 | 32189.24
2022092010 | 3 | 0.66987 | 53589.6 | 0.21777 | 7839.72 | 0.67384 | 8086.08 | 1 | 5000 | 7839.72 | 8086.08 | 0 | 0 | 0 | 0 | 32663.8 | 0 | 0 | 0 | 0 | 0 | 32663.8
2022092011 | 3 | 0.72294 | 57835.2 | 0.22404 | 8065.44 | 0.73583 | 8829.96 | 1 | 5000 | 8065.44 | 8829.96 | 0 | 0 | 0 | 0 | 35939.8 | 0 | 0 | 0 | 0 | 0 | 35939.8
2022092012 | 3 | 0.76868 | 61494.4 | 0.2093 | 7534.8 | 0.74888 | 8986.56 | 1 | 5000 | 7534.8 | 8986.56 | 0 | 0 | 0 | 0 | 39973.04 | 0 | 0 | 0 | 0 | 0 | 39973.04
2022092013 | 3 | 0.81432 | 65145.6 | 0.20885 | 7518.6 | 0.71916 | 8629.92 | 1 | 5000 | 7518.6 | 8629.92 | 0 | 0 | 0 | 0 | 43997.08 | 0 | 0 | 0 | 0 | 0 | 43997.08
2022092014 | 3 | 0.8557 | 68456 | 0.19947 | 7180.92 | 0.70956 | 8514.72 | 1 | 5000 | 7180.92 | 8514.72 | 0 | 0 | 0 | 0 | 47760.36 | 0 | 0 | 0 | 0 | 0 | 47760.36
2022092015 | 3 | 0.87852 | 70281.6 | 0.20028 | 7210.08 | 0.70381 | 8445.72 | 1 | 5000 | 7210.08 | 8445.72 | 0 | 0 | 0 | 0 | 49625.8 | 0 | 0 | 0 | 0 | 0 | 49625.8
2022092016 | 3 | 0.88301 | 70640.8 | 0.21026 | 7569.36 | 0.68795 | 8255.4 | 1 | 5000 | 7569.36 | 8255.4 | 0 | 0 | 0 | 0 | 49816.04 | 0 | 0 | 0 | 0 | 0 | 49816.04
2022092017 | 3 | 0.88924 | 71139.2 | 0.22331 | 8039.16 | 0.67081 | 8049.72 | 1 | 5000 | 8039.16 | 8049.72 | 0 | 0 | 0 | 0 | 50050.32 | 0 | 0 | 0 | 0 | 0 | 50050.32
2022092018 | 3 | 0.88522 | 70817.6 | 0.24146 | 8692.56 | 0.62352 | 7482.24 | 1 | 5000 | 8692.56 | 7482.24 | 0 | 0 | 0 | 0 | 49642.8 | 0 | 0 | 0 | 0 | 0 | 49642.8
2022092019 | 3 | 0.86916 | 69532.8 | 0.24954 | 8983.44 | 0.35996 | 4319.52 | 1 | 5000 | 8983.44 | 4319.52 | 0 | 0 | 0 | 0 | 51229.84 | 0 | 0 | 0 | 0 | 0 | 51229.84
2022092020 | 3 | 0.83843 | 67074.4 | 0.2455 | 8838 | 0.04025 | 483 | 1 | 5000 | 8838 | 483 | 0 | 0 | 0 | 0 | 52753.4 | 0 | 0 | 0 | 0 | 0 | 52753.4
2022092021 | 3 | 0.81095 | 64876 | 0.28818 | 10374.48 | 0 | 0 | 1 | 5000 | 10374.48 | 0 | 0 | 0 | 0 | 0 | 49501.52 | 0 | 0 | 0 | 0 | 0 | 49501.52
2022092022 | 3 | 0.76823 | 61458.4 | 0.36196 | 13030.56 | 0 | 0 | 1 | 5000 | 13030.56 | 0 | 0 | 0 | 0 | 0 | 43427.84 | 0 | 0 | 0 | 0 | 0 | 43427.84
2022092023 | 3 | 0.71354 | 57083.2 | 0.40256 | 14492.16 | 0 | 0 | 1 | 5000 | 14492.16 | 0 | 0 | 0 | 0 | 0 | 37591.04 | 0 | 0 | 0 | 0 | 0 | 37591.04
2022092024 | 3 | 0.66228 | 52982.4 | 0.41117 | 14802.12 | 0 | 0 | 1 | 5000 | 14802.12 | 0 | 0 | 0 | 0 | 0 | 33180.28 | 0 | 0 | 0 | 0 | 0 | 33180.28
2022092101 | 4 | 0.61625 | 49300 | 0.39845 | 14344.2 | 0 | 0 | 1 | 5000 | 14344.2 | 0 | 0 | 0 | 0 | 0 | 29955.8 | 0 | 0 | 0 | 0 | 0 | 29955.8
2022092102 | 4 | 0.58319 | 46655.2 | 0.38063 | 13702.68 | 0 | 0 | 1 | 5000 | 13702.68 | 0 | 0 | 0 | 0 | 0 | 27952.52 | 0 | 0 | 0 | 0 | 0 | 27952.52
2022092103 | 4 | 0.56289 | 45031.2 | 0.36386 | 13098.96 | 0 | 0 | 1 | 5000 | 13098.96 | 0 | 0 | 0 | 0 | 0 | 26932.24 | 0 | 0 | 0 | 0 | 0 | 26932.24
2022092104 | 4 | 0.5485 | 43880 | 0.35955 | 12943.8 | 0 | 0 | 1 | 5000 | 12943.8 | 0 | 0 | 0 | 0 | 0 | 25936.2 | 0 | 0 | 0 | 0 | 0 | 25936.2
2022092105 | 4 | 0.54532 | 43625.6 | 0.36319 | 13074.84 | 0 | 0 | 1 | 5000 | 13074.84 | 0 | 0 | 0 | 0 | 0 | 25550.76 | 0 | 0 | 0 | 0 | 0 | 25550.76
2022092106 | 4 | 0.55669 | 44535.2 | 0.34828 | 12538.08 | 0 | 0 | 1 | 5000 | 12538.08 | 0 | 0 | 0 | 0 | 0 | 26997.12 | 0 | 0 | 0 | 0 | 0 | 26997.12
2022092107 | 4 | 0.57979 | 46383.2 | 0.32045 | 11536.2 | 0 | 0 | 1 | 5000 | 11536.2 | 0 | 0 | 0 | 0 | 0 | 29847 | 0 | 0 | 0 | 0 | 0 | 29847
2022092108 | 4 | 0.58519 | 46815.2 | 0.28673 | 10322.28 | 0.02085 | 250.2 | 1 | 5000 | 10322.28 | 250.2 | 0 | 0 | 0 | 0 | 31242.72 | 0 | 0 | 0 | 0 | 0 | 31242.72
2022092109 | 4 | 0.60398 | 48318.4 | 0.21882 | 7877.52 | 0.36153 | 4338.36 | 1 | 5000 | 7877.52 | 4338.36 | 0 | 0 | 0 | 0 | 31102.52 | 0 | 0 | 0 | 0 | 0 | 31102.52
2022092110 | 4 | 0.64718 | 51774.4 | 0.17594 | 6333.84 | 0.72185 | 8662.2 | 1 | 5000 | 6333.84 | 8662.2 | 0 | 0 | 0 | 0 | 31778.36 | 0 | 0 | 0 | 0 | 0 | 31778.36
2022092111 | 4 | 0.7003 | 56024 | 0.19727 | 7101.72 | 0.78187 | 9382.44 | 1 | 5000 | 7101.72 | 9382.44 | 0 | 0 | 0 | 0 | 34539.84 | 0 | 0 | 0 | 0 | 0 | 34539.84
2022092112 | 4 | 0.75275 | 60220 | 0.17528 | 6310.08 | 0.77933 | 9351.96 | 1 | 5000 | 6310.08 | 9351.96 | 0 | 0 | 0 | 0 | 39557.96 | 0 | 0 | 0 | 0 | 0 | 39557.96
2022092113 | 4 | 0.8007 | 64056 | 0.16906 | 6086.16 | 0.75545 | 9065.4 | 1 | 5000 | 6086.16 | 9065.4 | 0 | 0 | 0 | 0 | 43904.44 | 0 | 0 | 0 | 0 | 0 | 43904.44
2022092114 | 4 | 0.84573 | 67658.4 | 0.16941 | 6098.76 | 0.75833 | 9099.96 | 1 | 5000 | 6098.76 | 9099.96 | 0 | 0 | 0 | 0 | 47459.68 | 0 | 0 | 0 | 0 | 0 | 47459.68
2022092115 | 4 | 0.87303 | 69842.4 | 0.14979 | 5392.44 | 0.756 | 9072 | 1 | 5000 | 5392.44 | 9072 | 0 | 0 | 0 | 0 | 50377.96 | 0 | 0 | 0 | 0 | 0 | 50377.96
2022092116 | 4 | 0.88088 | 70470.4 | 0.13769 | 4956.84 | 0.76017 | 9122.04 | 1 | 5000 | 4956.84 | 9122.04 | 0 | 0 | 0 | 0 | 51391.52 | 0 | 0 | 0 | 0 | 0 | 51391.52
2022092117 | 4 | 0.88516 | 70812.8 | 0.13371 | 4813.56 | 0.75309 | 9037.08 | 1 | 5000 | 4813.56 | 9037.08 | 0 | 0 | 0 | 0 | 51962.16 | 0 | 0 | 0 | 0 | 0 | 51962.16
2022092118 | 4 | 0.88341 | 70672.8 | 0.13939 | 5018.04 | 0.70047 | 8405.64 | 1 | 5000 | 5018.04 | 8405.64 | 0 | 0 | 0 | 0 | 52249.12 | 0 | 0 | 0 | 0 | 0 | 52249.12
2022092119 | 4 | 0.86591 | 69272.8 | 0.14612 | 5260.32 | 0.39879 | 4785.48 | 1 | 5000 | 5260.32 | 4785.48 | 0 | 0 | 0 | 0 | 54227 | 0 | 0 | 0 | 0 | 0 | 54227
2022092120 | 4 | 0.83173 | 66538.4 | 0.15493 | 5577.48 | 0.03958 | 474.96 | 1 | 5000 | 5577.48 | 474.96 | 0 | 0 | 0 | 0 | 55485.96 | 0 | 0 | 0 | 0 | 0 | 55485.96
2022092121 | 4 | 0.79922 | 63937.6 | 0.21195 | 7630.2 | 0 | 0 | 1 | 5000 | 7630.2 | 0 | 0 | 0 | 0 | 0 | 51307.4 | 0 | 0 | 0 | 0 | 0 | 51307.4
2022092122 | 4 | 0.7539 | 60312 | 0.28542 | 10275.12 | 0 | 0 | 1 | 5000 | 10275.12 | 0 | 0 | 0 | 0 | 0 | 45036.88 | 0 | 0 | 0 | 0 | 0 | 45036.88
2022092123 | 4 | 0.69674 | 55739.2 | 0.34326 | 12357.36 | 0 | 0 | 1 | 5000 | 12357.36 | 0 | 0 | 0 | 0 | 0 | 38381.84 | 0 | 0 | 0 | 0 | 0 | 38381.84
2022092124 | 4 | 0.64345 | 51476 | 0.38176 | 13743.36 | 0 | 0 | 1 | 5000 | 13743.36 | 0 | 0 | 0 | 0 | 0 | 32732.64 | 0 | 0 | 0 | 0 | 0 | 32732.64
2022092201 | 5 | 0.59971 | 47976.8 | 0.38428 | 13834.08 | 0 | 0 | 1 | 5000 | 13834.08 | 0 | 0 | 0 | 0 | 0 | 29142.72 | 0 | 0 | 0 | 0 | 0 | 29142.72
2022092202 | 5 | 0.56545 | 45236 | 0.36459 | 13125.24 | 0 | 0 | 1 | 5000 | 13125.24 | 0 | 0 | 0 | 0 | 0 | 27110.76 | 0 | 0 | 0 | 0 | 0 | 27110.76
2022092203 | 5 | 0.54259 | 43407.2 | 0.32851 | 11826.36 | 0 | 0 | 1 | 5000 | 11826.36 | 0 | 0 | 0 | 0 | 0 | 26580.84 | 0 | 0 | 0 | 0 | 0 | 26580.84
2022092204 | 5 | 0.52833 | 42266.4 | 0.30827 | 11097.72 | 0 | 0 | 1 | 5000 | 11097.72 | 0 | 0 | 0 | 0 | 0 | 26168.68 | 0 | 0 | 0 | 0 | 0 | 26168.68
2022092205 | 5 | 0.52456 | 41964.8 | 0.28499 | 10259.64 | 0 | 0 | 1 | 5000 | 10259.64 | 0 | 0 | 0 | 0 | 0 | 26705.16 | 0 | 0 | 0 | 0 | 0 | 26705.16
2022092206 | 5 | 0.53694 | 42955.2 | 0.24714 | 8897.04 | 0 | 0 | 1 | 5000 | 8897.04 | 0 | 0 | 0 | 0 | 0 | 29058.16 | 0 | 0 | 0 | 0 | 0 | 29058.16
2022092207 | 5 | 0.56178 | 44942.4 | 0.21257 | 7652.52 | 0 | 0 | 1 | 5000 | 7652.52 | 0 | 0 | 0 | 0 | 0 | 32289.88 | 0 | 0 | 0 | 0 | 0 | 32289.88
2022092208 | 5 | 0.56826 | 45460.8 | 0.19479 | 7012.44 | 0.01915 | 229.8 | 1 | 5000 | 7012.44 | 229.8 | 0 | 0 | 0 | 0 | 33218.56 | 0 | 0 | 0 | 0 | 0 | 33218.56
2022092209 | 5 | 0.58581 | 46864.8 | 0.1511 | 5439.6 | 0.34621 | 4154.52 | 1 | 5000 | 5439.6 | 4154.52 | 0 | 0 | 0 | 0 | 32270.68 | 0 | 0 | 0 | 0 | 0 | 32270.68
2022092210 | 5 | 0.63113 | 50490.4 | 0.10106 | 3638.16 | 0.72392 | 8687.04 | 1 | 5000 | 3638.16 | 8687.04 | 0 | 0 | 0 | 0 | 33165.2 | 0 | 0 | 0 | 0 | 0 | 33165.2
2022092211 | 5 | 0.68425 | 54740 | 0.07082 | 2549.52 | 0.78163 | 9379.56 | 1 | 5000 | 2549.52 | 9379.56 | 0 | 0 | 0 | 0 | 37810.92 | 0 | 0 | 0 | 0 | 0 | 37810.92
2022092212 | 5 | 0.73969 | 59175.2 | 0.0538 | 1936.8 | 0.789 | 9468 | 1 | 5000 | 1936.8 | 9468 | 0 | 0 | 0 | 0 | 42770.4 | 0 | 0 | 0 | 0 | 0 | 42770.4
2022092213 | 5 | 0.79401 | 63520.8 | 0.04682 | 1685.52 | 0.78535 | 9424.2 | 1 | 5000 | 1685.52 | 9424.2 | 0 | 0 | 0 | 0 | 47411.08 | 0 | 0 | 0 | 0 | 0 | 47411.08
2022092214 | 5 | 0.84135 | 67308 | 0.05084 | 1830.24 | 0.76798 | 9215.76 | 1 | 5000 | 1830.24 | 9215.76 | 0 | 0 | 0 | 0 | 51262 | 0 | 0 | 0 | 0 | 0 | 51262
2022092215 | 5 | 0.87196 | 69756.8 | 0.05431 | 1955.16 | 0.76122 | 9134.64 | 1 | 5000 | 1955.16 | 9134.64 | 0 | 0 | 0 | 0 | 53667 | 0 | 0 | 0 | 0 | 0 | 53667
2022092216 | 5 | 0.87958 | 70366.4 | 0.05063 | 1822.68 | 0.7546 | 9055.2 | 1 | 5000 | 1822.68 | 9055.2 | 0 | 0 | 0 | 0 | 54488.52 | 0 | 0 | 0 | 0 | 0 | 54488.52
2022092217 | 5 | 0.88316 | 70652.8 | 0.05651 | 2034.36 | 0.75249 | 9029.88 | 1 | 5000 | 2034.36 | 9029.88 | 0 | 0 | 0 | 0 | 54588.56 | 0 | 0 | 0 | 0 | 0 | 54588.56
2022092218 | 5 | 0.87881 | 70304.8 | 0.07265 | 2615.4 | 0.66901 | 8028.12 | 1 | 5000 | 2615.4 | 8028.12 | 0 | 0 | 0 | 0 | 54661.28 | 0 | 0 | 0 | 0 | 0 | 54661.28
2022092219 | 5 | 0.85677 | 68541.6 | 0.08581 | 3089.16 | 0.37294 | 4475.28 | 1 | 5000 | 3089.16 | 4475.28 | 0 | 0 | 0 | 0 | 55977.16 | 0 | 0 | 0 | 0 | 0 | 55977.16
2022092220 | 5 | 0.82148 | 65718.4 | 0.11782 | 4241.52 | 0.03631 | 435.72 | 1 | 5000 | 4241.52 | 435.72 | 0 | 0 | 0 | 0 | 56041.16 | 0 | 0 | 0 | 0 | 0 | 56041.16
2022092221 | 5 | 0.78629 | 62903.2 | 0.16957 | 6104.52 | 8e-05 | 0.96 | 1 | 5000 | 6104.52 | 0.96 | 0 | 0 | 0 | 0 | 51797.72 | 0 | 0 | 0 | 0 | 0 | 51797.72
2022092222 | 5 | 0.74144 | 59315.2 | 0.2209 | 7952.4 | 0 | 0 | 1 | 5000 | 7952.4 | 0 | 0 | 0 | 0 | 0 | 46362.8 | 0 | 0 | 0 | 0 | 0 | 46362.8
2022092223 | 5 | 0.68862 | 55089.6 | 0.23839 | 8582.04 | 0 | 0 | 1 | 5000 | 8582.04 | 0 | 0 | 0 | 0 | 0 | 41507.56 | 0 | 0 | 0 | 0 | 0 | 41507.56
2022092224 | 5 | 0.63698 | 50958.4 | 0.23646 | 8512.56 | 0 | 0 | 1 | 5000 | 8512.56 | 0 | 0 | 0 | 0 | 0 | 37445.84 | 0 | 0 | 0 | 0 | 0 | 37445.84
2022092301 | 6 | 0.59396 | 47516.8 | 0.21383 | 7697.88 | 4e-05 | 0.48 | 1 | 5000 | 7697.88 | 0.48 | 0 | 0 | 0 | 0 | 34818.44 | 0 | 0 | 0 | 0 | 0 | 34818.44
2022092302 | 6 | 0.5617 | 44936 | 0.20528 | 7390.08 | 4e-05 | 0.48 | 1 | 5000 | 7390.08 | 0.48 | 0 | 0 | 0 | 0 | 32545.44 | 0 | 0 | 0 | 0 | 0 | 32545.44
2022092303 | 6 | 0.54391 | 43512.8 | 0.17679 | 6364.44 | 4e-05 | 0.48 | 1 | 5000 | 6364.44 | 0.48 | 0 | 0 | 0 | 0 | 32147.88 | 0 | 0 | 0 | 0 | 0 | 32147.88
2022092304 | 6 | 0.53185 | 42548 | 0.15675 | 5643 | 5e-05 | 0.6 | 1 | 5000 | 5643 | 0.6 | 0 | 0 | 0 | 0 | 31904.4 | 0 | 0 | 0 | 0 | 0 | 31904.4
2022092305 | 6 | 0.52811 | 42248.8 | 0.12745 | 4588.2 | 5e-05 | 0.6 | 1 | 5000 | 4588.2 | 0.6 | 0 | 0 | 0 | 0 | 32660 | 0 | 0 | 0 | 0 | 0 | 32660
2022092306 | 6 | 0.54097 | 43277.6 | 0.12532 | 4511.52 | 5e-05 | 0.6 | 1 | 5000 | 4511.52 | 0.6 | 0 | 0 | 0 | 0 | 33765.48 | 0 | 0 | 0 | 0 | 0 | 33765.48
2022092307 | 6 | 0.5672 | 45376 | 0.13288 | 4783.68 | 5e-05 | 0.6 | 1 | 5000 | 4783.68 | 0.6 | 0 | 0 | 0 | 0 | 35591.72 | 0 | 0 | 0 | 0 | 0 | 35591.72
2022092308 | 6 | 0.57282 | 45825.6 | 0.13016 | 4685.76 | 0.01563 | 187.56 | 1 | 5000 | 4685.76 | 187.56 | 0 | 0 | 0 | 0 | 35952.28 | 0 | 0 | 0 | 0 | 0 | 35952.28
2022092309 | 6 | 0.59039 | 47231.2 | 0.12292 | 4425.12 | 0.31615 | 3793.8 | 1 | 5000 | 4425.12 | 3793.8 | 0 | 0 | 0 | 0 | 34012.28 | 0 | 0 | 0 | 0 | 0 | 34012.28
2022092310 | 6 | 0.63501 | 50800.8 | 0.10118 | 3642.48 | 0.70028 | 8403.36 | 1 | 5000 | 3642.48 | 8403.36 | 0 | 0 | 0 | 0 | 33754.96 | 0 | 0 | 0 | 0 | 0 | 33754.96
2022092311 | 6 | 0.68722 | 54977.6 | 0.12071 | 4345.56 | 0.78078 | 9369.36 | 1 | 5000 | 4345.56 | 9369.36 | 0 | 0 | 0 | 0 | 36262.68 | 0 | 0 | 0 | 0 | 0 | 36262.68
2022092312 | 6 | 0.73777 | 59021.6 | 0.19905 | 7165.8 | 0.77403 | 9288.36 | 1 | 5000 | 7165.8 | 9288.36 | 0 | 0 | 0 | 0 | 37567.44 | 0 | 0 | 0 | 0 | 0 | 37567.44
2022092313 | 6 | 0.79606 | 63684.8 | 0.2763 | 9946.8 | 0.75926 | 9111.12 | 1 | 5000 | 9946.8 | 9111.12 | 0 | 0 | 0 | 0 | 39626.88 | 0 | 0 | 0 | 0 | 0 | 39626.88
2022092314 | 6 | 0.84347 | 67477.6 | 0.30122 | 10843.92 | 0.75449 | 9053.88 | 1 | 5000 | 10843.92 | 9053.88 | 0 | 0 | 0 | 0 | 42579.8 | 0 | 0 | 0 | 0 | 0 | 42579.8
2022092315 | 6 | 0.87439 | 69951.2 | 0.33353 | 12007.08 | 0.77018 | 9242.16 | 1 | 5000 | 12007.08 | 9242.16 | 0 | 0 | 0 | 0 | 43701.96 | 0 | 0 | 0 | 0 | 0 | 43701.96
2022092316 | 6 | 0.87984 | 70387.2 | 0.32267 | 11616.12 | 0.76571 | 9188.52 | 1 | 5000 | 11616.12 | 9188.52 | 0 | 0 | 0 | 0 | 44582.56 | 0 | 0 | 0 | 0 | 0 | 44582.56
2022092317 | 6 | 0.88179 | 70543.2 | 0.31073 | 11186.28 | 0.76463 | 9175.56 | 1 | 5000 | 11186.28 | 9175.56 | 0 | 0 | 0 | 0 | 45181.36 | 0 | 0 | 0 | 0 | 0 | 45181.36
2022092318 | 6 | 0.87558 | 70046.4 | 0.29809 | 10731.24 | 0.69424 | 8330.88 | 1 | 5000 | 10731.24 | 8330.88 | 0 | 0 | 0 | 0 | 45984.28 | 0 | 0 | 0 | 0 | 0 | 45984.28
2022092319 | 6 | 0.84757 | 67805.6 | 0.28034 | 10092.24 | 0.37603 | 4512.36 | 1 | 5000 | 10092.24 | 4512.36 | 0 | 0 | 0 | 0 | 48201 | 0 | 0 | 0 | 0 | 0 | 48201
2022092320 | 6 | 0.81081 | 64864.8 | 0.24436 | 8796.96 | 0.03405 | 408.6 | 1 | 5000 | 8796.96 | 408.6 | 0 | 0 | 0 | 0 | 50659.24 | 0 | 0 | 0 | 0 | 0 | 50659.24
2022092321 | 6 | 0.77659 | 62127.2 | 0.29138 | 10489.68 | 0 | 0 | 1 | 5000 | 10489.68 | 0 | 0 | 0 | 0 | 0 | 46637.52 | 0 | 0 | 0 | 0 | 0 | 46637.52
2022092322 | 6 | 0.73844 | 59075.2 | 0.34714 | 12497.04 | 0 | 0 | 1 | 5000 | 12497.04 | 0 | 0 | 0 | 0 | 0 | 41578.16 | 0 | 0 | 0 | 0 | 0 | 41578.16
2022092323 | 6 | 0.69764 | 55811.2 | 0.39594 | 14253.84 | 0 | 0 | 1 | 5000 | 14253.84 | 0 | 0 | 0 | 0 | 0 | 36557.36 | 0 | 0 | 0 | 0 | 0 | 36557.36
2022092324 | 6 | 0.6551 | 52408 | 0.42997 | 15478.92 | 0 | 0 | 1 | 5000 | 15478.92 | 0 | 0 | 0 | 0 | 0 | 31929.08 | 0 | 0 | 0 | 0 | 0 | 31929.08
2022092401 | 7 | 0.6178 | 49424 | 0.45448 | 16361.28 | 0 | 0 | 1 | 5000 | 16361.28 | 0 | 0 | 0 | 0 | 0 | 28062.72 | 0 | 0 | 0 | 0 | 0 | 28062.72
2022092402 | 7 | 0.58641 | 46912.8 | 0.46054 | 16579.44 | 0 | 0 | 1 | 5000 | 16579.44 | 0 | 0 | 0 | 0 | 0 | 25333.36 | 0 | 0 | 0 | 0 | 0 | 25333.36
2022092403 | 7 | 0.56315 | 45052 | 0.45422 | 16351.92 | 0 | 0 | 1 | 5000 | 16351.92 | 0 | 0 | 0 | 0 | 0 | 23700.08 | 0 | 0 | 0 | 0 | 0 | 23700.08
2022092404 | 7 | 0.54611 | 43688.8 | 0.43671 | 15721.56 | 0 | 0 | 1 | 5000 | 15721.56 | 0 | 0 | 0 | 0 | 0 | 22967.24 | 0 | 0 | 0 | 0 | 0 | 22967.24
2022092405 | 7 | 0.53424 | 42739.2 | 0.41196 | 14830.56 | 0 | 0 | 1 | 5000 | 14830.56 | 0 | 0 | 0 | 0 | 0 | 22908.64 | 0 | 0 | 0 | 0 | 0 | 22908.64
2022092406 | 7 | 0.52887 | 42309.6 | 0.40049 | 14417.64 | 0 | 0 | 1 | 5000 | 14417.64 | 0 | 0 | 0 | 0 | 0 | 22891.96 | 0 | 0 | 0 | 0 | 0 | 22891.96
2022092407 | 7 | 0.53138 | 42510.4 | 0.3983 | 14338.8 | 0 | 0 | 1 | 5000 | 14338.8 | 0 | 0 | 0 | 0 | 0 | 23171.6 | 0 | 0 | 0 | 0 | 0 | 23171.6
2022092408 | 7 | 0.53385 | 42708 | 0.36185 | 13026.6 | 0.01648 | 197.76 | 1 | 5000 | 13026.6 | 197.76 | 0 | 0 | 0 | 0 | 24483.64 | 0 | 0 | 0 | 0 | 0 | 24483.64
2022092409 | 7 | 0.55993 | 44794.4 | 0.28764 | 10355.04 | 0.3279 | 3934.8 | 1 | 5000 | 10355.04 | 3934.8 | 0 | 0 | 0 | 0 | 25504.56 | 0 | 0 | 0 | 0 | 0 | 25504.56
2022092410 | 7 | 0.61124 | 48899.2 | 0.20709 | 7455.24 | 0.70088 | 8410.56 | 1 | 5000 | 7455.24 | 8410.56 | 0 | 0 | 0 | 0 | 28033.4 | 0 | 0 | 0 | 0 | 0 | 28033.4
2022092411 | 7 | 0.66388 | 53110.4 | 0.20741 | 7466.76 | 0.7654 | 9184.8 | 1 | 5000 | 7466.76 | 9184.8 | 0 | 0 | 0 | 0 | 31458.84 | 0 | 0 | 0 | 0 | 0 | 31458.84
2022092412 | 7 | 0.71509 | 57207.2 | 0.18695 | 6730.2 | 0.78638 | 9436.56 | 1 | 5000 | 6730.2 | 9436.56 | 0 | 0 | 0 | 0 | 36040.44 | 0 | 0 | 0 | 0 | 0 | 36040.44
2022092413 | 7 | 0.76006 | 60804.8 | 0.1796 | 6465.6 | 0.76501 | 9180.12 | 1 | 5000 | 6465.6 | 9180.12 | 0 | 0 | 0 | 0 | 40159.08 | 0 | 0 | 0 | 0 | 0 | 40159.08
2022092414 | 7 | 0.79672 | 63737.6 | 0.14055 | 5059.8 | 0.75828 | 9099.36 | 1 | 5000 | 5059.8 | 9099.36 | 0 | 0 | 0 | 0 | 44578.44 | 0 | 0 | 0 | 0 | 0 | 44578.44
2022092415 | 7 | 0.82413 | 65930.4 | 0.11332 | 4079.52 | 0.75847 | 9101.64 | 1 | 5000 | 4079.52 | 9101.64 | 0 | 0 | 0 | 0 | 47749.24 | 0 | 0 | 0 | 0 | 0 | 47749.24
2022092416 | 7 | 0.84448 | 67558.4 | 0.11062 | 3982.32 | 0.75944 | 9113.28 | 1 | 5000 | 3982.32 | 9113.28 | 0 | 0 | 0 | 0 | 49462.8 | 0 | 0 | 0 | 0 | 0 | 49462.8
2022092417 | 7 | 0.85403 | 68322.4 | 0.12336 | 4440.96 | 0.75756 | 9090.72 | 1 | 5000 | 4440.96 | 9090.72 | 0 | 0 | 0 | 0 | 49790.72 | 0 | 0 | 0 | 0 | 0 | 49790.72
2022092418 | 7 | 0.84686 | 67748.8 | 0.12578 | 4528.08 | 0.69239 | 8308.68 | 1 | 5000 | 4528.08 | 8308.68 | 0 | 0 | 0 | 0 | 49912.04 | 0 | 0 | 0 | 0 | 0 | 49912.04
2022092419 | 7 | 0.81939 | 65551.2 | 0.14581 | 5249.16 | 0.35314 | 4237.68 | 1 | 5000 | 5249.16 | 4237.68 | 0 | 0 | 0 | 0 | 51064.36 | 0 | 0 | 0 | 0 | 0 | 51064.36
2022092420 | 7 | 0.78198 | 62558.4 | 0.1733 | 6238.8 | 0.02807 | 336.84 | 1 | 5000 | 6238.8 | 336.84 | 0 | 0 | 0 | 0 | 50982.76 | 0 | 0 | 0 | 0 | 0 | 50982.76
2022092421 | 7 | 0.74881 | 59904.8 | 0.24105 | 8677.8 | 0 | 0 | 1 | 5000 | 8677.8 | 0 | 0 | 0 | 0 | 0 | 46227 | 0 | 0 | 0 | 0 | 0 | 46227
2022092422 | 7 | 0.71194 | 56955.2 | 0.32456 | 11684.16 | 0 | 0 | 1 | 5000 | 11684.16 | 0 | 0 | 0 | 0 | 0 | 40271.04 | 0 | 0 | 0 | 0 | 0 | 40271.04
2022092423 | 7 | 0.6724 | 53792 | 0.39019 | 14046.84 | 0 | 0 | 1 | 5000 | 14046.84 | 0 | 0 | 0 | 0 | 0 | 34745.16 | 0 | 0 | 0 | 0 | 0 | 34745.16
2022092424 | 7 | 0.63356 | 50684.8 | 0.40773 | 14678.28 | 0 | 0 | 1 | 5000 | 14678.28 | 0 | 0 | 0 | 0 | 0 | 31006.52 | 0 | 0 | 0 | 0 | 0 | 31006.52
2022092501 | 1 | 0.59576 | 47660.8 | 0.39424 | 14192.64 | 0 | 0 | 1 | 5000 | 14192.64 | 0 | 0 | 0 | 0 | 0 | 28468.16 | 0 | 0 | 0 | 0 | 0 | 28468.16
2022092502 | 1 | 0.56603 | 45282.4 | 0.3712 | 13363.2 | 0 | 0 | 1 | 5000 | 13363.2 | 0 | 0 | 0 | 0 | 0 | 26919.2 | 0 | 0 | 0 | 0 | 0 | 26919.2
2022092503 | 1 | 0.54603 | 43682.4 | 0.3411 | 12279.6 | 0 | 0 | 1 | 5000 | 12279.6 | 0 | 0 | 0 | 0 | 0 | 26402.8 | 0 | 0 | 0 | 0 | 0 | 26402.8
2022092504 | 1 | 0.52977 | 42381.6 | 0.30762 | 11074.32 | 0 | 0 | 1 | 5000 | 11074.32 | 0 | 0 | 0 | 0 | 0 | 26307.28 | 0 | 0 | 0 | 0 | 0 | 26307.28
2022092505 | 1 | 0.51892 | 41513.6 | 0.25477 | 9171.72 | 0 | 0 | 1 | 5000 | 9171.72 | 0 | 0 | 0 | 0 | 0 | 27341.88 | 0 | 0 | 0 | 0 | 0 | 27341.88
2022092506 | 1 | 0.51254 | 41003.2 | 0.21706 | 7814.16 | 0 | 0 | 1 | 5000 | 7814.16 | 0 | 0 | 0 | 0 | 0 | 28189.04 | 0 | 0 | 0 | 0 | 0 | 28189.04
2022092507 | 1 | 0.51234 | 40987.2 | 0.18758 | 6752.88 | 0 | 0 | 1 | 5000 | 6752.88 | 0 | 0 | 0 | 0 | 0 | 29234.32 | 0 | 0 | 0 | 0 | 0 | 29234.32
2022092508 | 1 | 0.51504 | 41203.2 | 0.16149 | 5813.64 | 0.01052 | 126.24 | 1 | 5000 | 5813.64 | 126.24 | 0 | 0 | 0 | 0 | 30263.32 | 0 | 0 | 0 | 0 | 0 | 30263.32
2022092509 | 1 | 0.53973 | 43178.4 | 0.13534 | 4872.24 | 0.24248 | 2909.76 | 1 | 5000 | 4872.24 | 2909.76 | 0 | 0 | 0 | 0 | 30396.4 | 0 | 0 | 0 | 0 | 0 | 30396.4
2022092510 | 1 | 0.59166 | 47332.8 | 0.10517 | 3786.12 | 0.538 | 6456 | 1 | 5000 | 3786.12 | 6456 | 0 | 0 | 0 | 0 | 32090.68 | 0 | 0 | 0 | 0 | 0 | 32090.68
2022092511 | 1 | 0.64426 | 51540.8 | 0.09775 | 3519 | 0.63903 | 7668.36 | 1 | 5000 | 3519 | 7668.36 | 0 | 0 | 0 | 0 | 35353.44 | 0 | 0 | 0 | 0 | 0 | 35353.44
2022092512 | 1 | 0.69573 | 55658.4 | 0.10114 | 3641.04 | 0.67459 | 8095.08 | 1 | 5000 | 3641.04 | 8095.08 | 0 | 0 | 0 | 0 | 38922.28 | 0 | 0 | 0 | 0 | 0 | 38922.28
2022092513 | 1 | 0.75169 | 60135.2 | 0.11642 | 4191.12 | 0.65701 | 7884.12 | 1 | 5000 | 4191.12 | 7884.12 | 0 | 0 | 0 | 0 | 43059.96 | 0 | 0 | 0 | 0 | 0 | 43059.96
2022092514 | 1 | 0.79858 | 63886.4 | 0.16033 | 5771.88 | 0.63735 | 7648.2 | 1 | 5000 | 5771.88 | 7648.2 | 0 | 0 | 0 | 0 | 45466.32 | 0 | 0 | 0 | 0 | 0 | 45466.32
2022092515 | 1 | 0.83201 | 66560.8 | 0.2144 | 7718.4 | 0.65916 | 7909.92 | 1 | 5000 | 7718.4 | 7909.92 | 0 | 0 | 0 | 0 | 45932.48 | 0 | 0 | 0 | 0 | 0 | 45932.48
2022092516 | 1 | 0.85539 | 68431.2 | 0.26574 | 9566.64 | 0.64944 | 7793.28 | 1 | 5000 | 9566.64 | 7793.28 | 0 | 0 | 0 | 0 | 46071.28 | 0 | 0 | 0 | 0 | 0 | 46071.28
2022092517 | 1 | 0.86242 | 68993.6 | 0.29018 | 10446.48 | 0.61448 | 7373.76 | 1 | 5000 | 10446.48 | 7373.76 | 0 | 0 | 0 | 0 | 46173.36 | 0 | 0 | 0 | 0 | 0 | 46173.36
2022092518 | 1 | 0.85156 | 68124.8 | 0.3168 | 11404.8 | 0.49871 | 5984.52 | 1 | 5000 | 11404.8 | 5984.52 | 0 | 0 | 0 | 0 | 45735.48 | 0 | 0 | 0 | 0 | 0 | 45735.48
2022092519 | 1 | 0.81911 | 65528.8 | 0.30158 | 10856.88 | 0.25549 | 3065.88 | 1 | 5000 | 10856.88 | 3065.88 | 0 | 0 | 0 | 0 | 46606.04 | 0 | 0 | 0 | 0 | 0 | 46606.04
2022092520 | 1 | 0.78516 | 62812.8 | 0.26588 | 9571.68 | 0.01407 | 168.84 | 1 | 5000 | 9571.68 | 168.84 | 0 | 0 | 0 | 0 | 48072.28 | 0 | 0 | 0 | 0 | 0 | 48072.28
2022092521 | 1 | 0.75701 | 60560.8 | 0.25489 | 9176.04 | 0 | 0 | 1 | 5000 | 9176.04 | 0 | 0 | 0 | 0 | 0 | 46384.76 | 0 | 0 | 0 | 0 | 0 | 46384.76
2022092522 | 1 | 0.71577 | 57261.6 | 0.25817 | 9294.12 | 0 | 0 | 1 | 5000 | 9294.12 | 0 | 0 | 0 | 0 | 0 | 42967.48 | 0 | 0 | 0 | 0 | 0 | 42967.48
2022092523 | 1 | 0.66629 | 53303.2 | 0.27768 | 9996.48 | 0 | 0 | 1 | 5000 | 9996.48 | 0 | 0 | 0 | 0 | 0 | 38306.72 | 0 | 0 | 0 | 0 | 0 | 38306.72
2022092524 | 1 | 0.61696 | 49356.8 | 0.30393 | 10941.48 | 0 | 0 | 1 | 5000 | 10941.48 | 0 | 0 | 0 | 0 | 0 | 33415.32 | 0 | 0 | 0 | 0 | 0 | 33415.32
2022092601 | 2 | 0.57538 | 46030.4 | 0.31723 | 11420.28 | 0 | 0 | 1 | 5000 | 11420.28 | 0 | 0 | 0 | 0 | 0 | 29610.12 | 0 | 0 | 0 | 0 | 0 | 29610.12
2022092602 | 2 | 0.54477 | 43581.6 | 0.32101 | 11556.36 | 0 | 0 | 1 | 5000 | 11556.36 | 0 | 0 | 0 | 0 | 0 | 27025.24 | 0 | 0 | 0 | 0 | 0 | 27025.24
2022092603 | 2 | 0.52853 | 42282.4 | 0.32642 | 11751.12 | 0 | 0 | 1 | 5000 | 11751.12 | 0 | 0 | 0 | 0 | 0 | 25531.28 | 0 | 0 | 0 | 0 | 0 | 25531.28
2022092604 | 2 | 0.51945 | 41556 | 0.32815 | 11813.4 | 0 | 0 | 1 | 5000 | 11813.4 | 0 | 0 | 0 | 0 | 0 | 24742.6 | 0 | 0 | 0 | 0 | 0 | 24742.6
2022092605 | 2 | 0.51763 | 41410.4 | 0.31847 | 11464.92 | 0 | 0 | 1 | 5000 | 11464.92 | 0 | 0 | 0 | 0 | 0 | 24945.48 | 0 | 0 | 0 | 0 | 0 | 24945.48
2022092606 | 2 | 0.5304 | 42432 | 0.29358 | 10568.88 | 0 | 0 | 1 | 5000 | 10568.88 | 0 | 0 | 0 | 0 | 0 | 26863.12 | 0 | 0 | 0 | 0 | 0 | 26863.12
2022092607 | 2 | 0.55642 | 44513.6 | 0.2708 | 9748.8 | 0 | 0 | 1 | 5000 | 9748.8 | 0 | 0 | 0 | 0 | 0 | 29764.8 | 0 | 0 | 0 | 0 | 0 | 29764.8
2022092608 | 2 | 0.56153 | 44922.4 | 0.24303 | 8749.08 | 0.01291 | 154.92 | 1 | 5000 | 8749.08 | 154.92 | 0 | 0 | 0 | 0 | 31018.4 | 0 | 0 | 0 | 0 | 0 | 31018.4
2022092609 | 2 | 0.57019 | 45615.2 | 0.20187 | 7267.32 | 0.29021 | 3482.52 | 1 | 5000 | 7267.32 | 3482.52 | 0 | 0 | 0 | 0 | 29865.36 | 0 | 0 | 0 | 0 | 0 | 29865.36
2022092610 | 2 | 0.60383 | 48306.4 | 0.1413 | 5086.8 | 0.66725 | 8007 | 1 | 5000 | 5086.8 | 8007 | 0 | 0 | 0 | 0 | 30212.6 | 0 | 0 | 0 | 0 | 0 | 30212.6
2022092611 | 2 | 0.63765 | 51012 | 0.14596 | 5254.56 | 0.76206 | 9144.72 | 1 | 5000 | 5254.56 | 9144.72 | 0 | 0 | 0 | 0 | 31612.72 | 0 | 0 | 0 | 0 | 0 | 31612.72
2022092612 | 2 | 0.67441 | 53952.8 | 0.15591 | 5612.76 | 0.76508 | 9180.96 | 1 | 5000 | 5612.76 | 9180.96 | 0 | 0 | 0 | 0 | 34159.08 | 0 | 0 | 0 | 0 | 0 | 34159.08
2022092613 | 2 | 0.70915 | 56732 | 0.14941 | 5378.76 | 0.77671 | 9320.52 | 1 | 5000 | 5378.76 | 9320.52 | 0 | 0 | 0 | 0 | 37032.72 | 0 | 0 | 0 | 0 | 0 | 37032.72
2022092614 | 2 | 0.74567 | 59653.6 | 0.13423 | 4832.28 | 0.77268 | 9272.16 | 1 | 5000 | 4832.28 | 9272.16 | 0 | 0 | 0 | 0 | 40549.16 | 0 | 0 | 0 | 0 | 0 | 40549.16
2022092615 | 2 | 0.77215 | 61772 | 0.12419 | 4470.84 | 0.77786 | 9334.32 | 1 | 5000 | 4470.84 | 9334.32 | 0 | 0 | 0 | 0 | 42966.84 | 0 | 0 | 0 | 0 | 0 | 42966.84
2022092616 | 2 | 0.79128 | 63302.4 | 0.11789 | 4244.04 | 0.77008 | 9240.96 | 1 | 5000 | 4244.04 | 9240.96 | 0 | 0 | 0 | 0 | 44817.4 | 0 | 0 | 0 | 0 | 0 | 44817.4
2022092617 | 2 | 0.79903 | 63922.4 | 0.1114 | 4010.4 | 0.74656 | 8958.72 | 1 | 5000 | 4010.4 | 8958.72 | 0 | 0 | 0 | 0 | 45953.28 | 0 | 0 | 0 | 0 | 0 | 45953.28
2022092618 | 2 | 0.78991 | 63192.8 | 0.09986 | 3594.96 | 0.67204 | 8064.48 | 1 | 5000 | 3594.96 | 8064.48 | 0 | 0 | 0 | 0 | 46533.36 | 0 | 0 | 0 | 0 | 0 | 46533.36
2022092619 | 2 | 0.76067 | 60853.6 | 0.08649 | 3113.64 | 0.32369 | 3884.28 | 1 | 5000 | 3113.64 | 3884.28 | 0 | 0 | 0 | 0 | 48855.68 | 0 | 0 | 0 | 0 | 0 | 48855.68
2022092620 | 2 | 0.7276 | 58208 | 0.08692 | 3129.12 | 0.02111 | 253.32 | 1 | 5000 | 3129.12 | 253.32 | 0 | 0 | 0 | 0 | 49825.56 | 0 | 0 | 0 | 0 | 0 | 49825.56
2022092621 | 2 | 0.6956 | 55648 | 0.11989 | 4316.04 | 0 | 0 | 1 | 5000 | 4316.04 | 0 | 0 | 0 | 0 | 0 | 46331.96 | 0 | 0 | 0 | 0 | 0 | 46331.96
2022092622 | 2 | 0.6542 | 52336 | 0.14551 | 5238.36 | 0 | 0 | 1 | 5000 | 5238.36 | 0 | 0 | 0 | 0 | 0 | 42097.64 | 0 | 0 | 0 | 0 | 0 | 42097.64
2022092623 | 2 | 0.60152 | 48121.6 | 0.17792 | 6405.12 | 0 | 0 | 1 | 5000 | 6405.12 | 0 | 0 | 0 | 0 | 0 | 36716.48 | 0 | 0 | 0 | 0 | 0 | 36716.48
2022092624 | 2 | 0.55117 | 44093.6 | 0.21907 | 7886.52 | 0 | 0 | 1 | 5000 | 7886.52 | 0 | 0 | 0 | 0 | 0 | 31207.08 | 0 | 0 | 0 | 0 | 0 | 31207.08
2022092701 | 3 | 0.5115 | 40920 | 0.2682 | 9655.2 | 0 | 0 | 1 | 5000 | 9655.2 | 0 | 0 | 0 | 0 | 0 | 26264.8 | 0 | 0 | 0 | 0 | 0 | 26264.8
2022092702 | 3 | 0.48155 | 38524 | 0.28201 | 10152.36 | 0 | 0 | 1 | 5000 | 10152.36 | 0 | 0 | 0 | 0 | 0 | 23371.64 | 0 | 0 | 0 | 0 | 0 | 23371.64
2022092703 | 3 | 0.46648 | 37318.4 | 0.29427 | 10593.72 | 0 | 0 | 1 | 5000 | 10593.72 | 0 | 0 | 0 | 0 | 0 | 21724.68 | 0 | 0 | 0 | 0 | 0 | 21724.68
2022092704 | 3 | 0.45677 | 36541.6 | 0.2945 | 10602 | 0 | 0 | 1 | 5000 | 10602 | 0 | 0 | 0 | 0 | 0 | 20939.6 | 0 | 0 | 0 | 0 | 0 | 20939.6
2022092705 | 3 | 0.45438 | 36350.4 | 0.29699 | 10691.64 | 0 | 0 | 1 | 5000 | 10691.64 | 0 | 0 | 0 | 0 | 0 | 20658.76 | 0 | 0 | 0 | 0 | 0 | 20658.76
2022092706 | 3 | 0.46505 | 37204 | 0.29741 | 10706.76 | 0 | 0 | 1 | 5000 | 10706.76 | 0 | 0 | 0 | 0 | 0 | 21497.24 | 0 | 0 | 0 | 0 | 0 | 21497.24
2022092707 | 3 | 0.49418 | 39534.4 | 0.28521 | 10267.56 | 0 | 0 | 1 | 5000 | 10267.56 | 0 | 0 | 0 | 0 | 0 | 24266.84 | 0 | 0 | 0 | 0 | 0 | 24266.84
2022092708 | 3 | 0.50099 | 40079.2 | 0.2754 | 9914.4 | 0.01748 | 209.76 | 1 | 5000 | 9914.4 | 209.76 | 0 | 0 | 0 | 0 | 24955.04 | 0 | 0 | 0 | 0 | 0 | 24955.04
2022092709 | 3 | 0.51254 | 41003.2 | 0.245 | 8820 | 0.3163 | 3795.6 | 1 | 5000 | 8820 | 3795.6 | 0 | 0 | 0 | 0 | 23387.6 | 0 | 0 | 0 | 0 | 0 | 23387.6
2022092710 | 3 | 0.5377 | 43016 | 0.16534 | 5952.24 | 0.68156 | 8178.72 | 1 | 5000 | 5952.24 | 8178.72 | 0 | 0 | 0 | 0 | 23885.04 | 0 | 0 | 0 | 0 | 0 | 23885.04
2022092711 | 3 | 0.56469 | 45175.2 | 0.1762 | 6343.2 | 0.77636 | 9316.32 | 1 | 5000 | 6343.2 | 9316.32 | 0 | 0 | 0 | 0 | 24515.68 | 0 | 0 | 0 | 0 | 0 | 24515.68
2022092712 | 3 | 0.5985 | 47880 | 0.17744 | 6387.84 | 0.79389 | 9526.68 | 1 | 5000 | 6387.84 | 9526.68 | 0 | 0 | 0 | 0 | 26965.48 | 0 | 0 | 0 | 0 | 0 | 26965.48
2022092713 | 3 | 0.63307 | 50645.6 | 0.16239 | 5846.04 | 0.78571 | 9428.52 | 1 | 5000 | 5846.04 | 9428.52 | 0 | 0 | 0 | 0 | 30371.04 | 0 | 0 | 0 | 0 | 0 | 30371.04
2022092714 | 3 | 0.67331 | 53864.8 | 0.12812 | 4612.32 | 0.77836 | 9340.32 | 1 | 5000 | 4612.32 | 9340.32 | 0 | 0 | 0 | 0 | 34912.16 | 0 | 0 | 0 | 0 | 0 | 34912.16
2022092715 | 3 | 0.70683 | 56546.4 | 0.0982 | 3535.2 | 0.79541 | 9544.92 | 1 | 5000 | 3535.2 | 9544.92 | 0 | 0 | 0 | 0 | 38466.28 | 0 | 0 | 0 | 0 | 0 | 38466.28
2022092716 | 3 | 0.73423 | 58738.4 | 0.08393 | 3021.48 | 0.78341 | 9400.92 | 1 | 5000 | 3021.48 | 9400.92 | 0 | 0 | 0 | 0 | 41316 | 0 | 0 | 0 | 0 | 0 | 41316
2022092717 | 3 | 0.75182 | 60145.6 | 0.08136 | 2928.96 | 0.75714 | 9085.68 | 1 | 5000 | 2928.96 | 9085.68 | 0 | 0 | 0 | 0 | 43130.96 | 0 | 0 | 0 | 0 | 0 | 43130.96
2022092718 | 3 | 0.75397 | 60317.6 | 0.09288 | 3343.68 | 0.67026 | 8043.12 | 1 | 5000 | 3343.68 | 8043.12 | 0 | 0 | 0 | 0 | 43930.8 | 0 | 0 | 0 | 0 | 0 | 43930.8
2022092719 | 3 | 0.72875 | 58300 | 0.10746 | 3868.56 | 0.33875 | 4065 | 1 | 5000 | 3868.56 | 4065 | 0 | 0 | 0 | 0 | 45366.44 | 0 | 0 | 0 | 0 | 0 | 45366.44
2022092720 | 3 | 0.69562 | 55649.6 | 0.16015 | 5765.4 | 0.02456 | 294.72 | 1 | 5000 | 5765.4 | 294.72 | 0 | 0 | 0 | 0 | 44589.48 | 0 | 0 | 0 | 0 | 0 | 44589.48
2022092721 | 3 | 0.67087 | 53669.6 | 0.2687 | 9673.2 | 0 | 0 | 1 | 5000 | 9673.2 | 0 | 0 | 0 | 0 | 0 | 38996.4 | 0 | 0 | 0 | 0 | 0 | 38996.4
2022092722 | 3 | 0.63563 | 50850.4 | 0.36391 | 13100.76 | 0 | 0 | 1 | 5000 | 13100.76 | 0 | 0 | 0 | 0 | 0 | 32749.64 | 0 | 0 | 0 | 0 | 0 | 32749.64
2022092723 | 3 | 0.59318 | 47454.4 | 0.4223 | 15202.8 | 0 | 0 | 1 | 5000 | 15202.8 | 0 | 0 | 0 | 0 | 0 | 27251.6 | 0 | 0 | 0 | 0 | 0 | 27251.6
2022092724 | 3 | 0.54427 | 43541.6 | 0.43811 | 15771.96 | 0 | 0 | 1 | 5000 | 15771.96 | 0 | 0 | 0 | 0 | 0 | 22769.64 | 0 | 0 | 0 | 0 | 0 | 22769.64
2022092801 | 4 | 0.50834 | 40667.2 | 0.41717 | 15018.12 | 0 | 0 | 1 | 5000 | 15018.12 | 0 | 0 | 0 | 0 | 0 | 20649.08 | 0 | 0 | 0 | 0 | 0 | 20649.08
2022092802 | 4 | 0.48325 | 38660 | 0.39762 | 14314.32 | 0 | 0 | 1 | 5000 | 14314.32 | 0 | 0 | 0 | 0 | 0 | 19345.68 | 0 | 0 | 0 | 0 | 0 | 19345.68
2022092803 | 4 | 0.46748 | 37398.4 | 0.37399 | 13463.64 | 0 | 0 | 1 | 5000 | 13463.64 | 0 | 0 | 0 | 0 | 0 | 18934.76 | 0 | 0 | 0 | 0 | 0 | 18934.76
2022092804 | 4 | 0.45924 | 36739.2 | 0.33937 | 12217.32 | 0 | 0 | 1 | 5000 | 12217.32 | 0 | 0 | 0 | 0 | 0 | 19521.88 | 0 | 0 | 0 | 0 | 0 | 19521.88
2022092805 | 4 | 0.45615 | 36492 | 0.29979 | 10792.44 | 0 | 0 | 1 | 5000 | 10792.44 | 0 | 0 | 0 | 0 | 0 | 20699.56 | 0 | 0 | 0 | 0 | 0 | 20699.56
2022092806 | 4 | 0.46652 | 37321.6 | 0.2623 | 9442.8 | 0 | 0 | 1 | 5000 | 9442.8 | 0 | 0 | 0 | 0 | 0 | 22878.8 | 0 | 0 | 0 | 0 | 0 | 22878.8
2022092807 | 4 | 0.49295 | 39436 | 0.24317 | 8754.12 | 0 | 0 | 1 | 5000 | 8754.12 | 0 | 0 | 0 | 0 | 0 | 25681.88 | 0 | 0 | 0 | 0 | 0 | 25681.88
2022092808 | 4 | 0.50448 | 40358.4 | 0.23145 | 8332.2 | 0.01437 | 172.44 | 1 | 5000 | 8332.2 | 172.44 | 0 | 0 | 0 | 0 | 26853.76 | 0 | 0 | 0 | 0 | 0 | 26853.76
2022092809 | 4 | 0.51749 | 41399.2 | 0.19674 | 7082.64 | 0.28555 | 3426.6 | 1 | 5000 | 7082.64 | 3426.6 | 0 | 0 | 0 | 0 | 25889.96 | 0 | 0 | 0 | 0 | 0 | 25889.96
2022092810 | 4 | 0.53882 | 43105.6 | 0.1081 | 3891.6 | 0.68543 | 8225.16 | 1 | 5000 | 3891.6 | 8225.16 | 0 | 0 | 0 | 0 | 25988.84 | 0 | 0 | 0 | 0 | 0 | 25988.84
2022092811 | 4 | 0.56769 | 45415.2 | 0.11205 | 4033.8 | 0.78478 | 9417.36 | 1 | 5000 | 4033.8 | 9417.36 | 0 | 0 | 0 | 0 | 26964.04 | 0 | 0 | 0 | 0 | 0 | 26964.04
2022092812 | 4 | 0.59952 | 47961.6 | 0.14278 | 5140.08 | 0.7897 | 9476.4 | 1 | 5000 | 5140.08 | 9476.4 | 0 | 0 | 0 | 0 | 28345.12 | 0 | 0 | 0 | 0 | 0 | 28345.12
2022092813 | 4 | 0.63322 | 50657.6 | 0.15283 | 5501.88 | 0.79392 | 9527.04 | 1 | 5000 | 5501.88 | 9527.04 | 0 | 0 | 0 | 0 | 30628.68 | 0 | 0 | 0 | 0 | 0 | 30628.68
2022092814 | 4 | 0.67233 | 53786.4 | 0.14216 | 5117.76 | 0.78962 | 9475.44 | 1 | 5000 | 5117.76 | 9475.44 | 0 | 0 | 0 | 0 | 34193.2 | 0 | 0 | 0 | 0 | 0 | 34193.2
2022092815 | 4 | 0.70793 | 56634.4 | 0.12539 | 4514.04 | 0.79393 | 9527.16 | 1 | 5000 | 4514.04 | 9527.16 | 0 | 0 | 0 | 0 | 37593.2 | 0 | 0 | 0 | 0 | 0 | 37593.2
2022092816 | 4 | 0.73907 | 59125.6 | 0.11979 | 4312.44 | 0.78742 | 9449.04 | 1 | 5000 | 4312.44 | 9449.04 | 0 | 0 | 0 | 0 | 40364.12 | 0 | 0 | 0 | 0 | 0 | 40364.12
2022092817 | 4 | 0.76262 | 61009.6 | 0.12625 | 4545 | 0.7769 | 9322.8 | 1 | 5000 | 4545 | 9322.8 | 0 | 0 | 0 | 0 | 42141.8 | 0 | 0 | 0 | 0 | 0 | 42141.8
2022092818 | 4 | 0.76484 | 61187.2 | 0.12985 | 4674.6 | 0.68442 | 8213.04 | 1 | 5000 | 4674.6 | 8213.04 | 0 | 0 | 0 | 0 | 43299.56 | 0 | 0 | 0 | 0 | 0 | 43299.56
2022092819 | 4 | 0.73886 | 59108.8 | 0.14117 | 5082.12 | 0.32574 | 3908.88 | 1 | 5000 | 5082.12 | 3908.88 | 0 | 0 | 0 | 0 | 45117.8 | 0 | 0 | 0 | 0 | 0 | 45117.8
2022092820 | 4 | 0.70401 | 56320.8 | 0.16715 | 6017.4 | 0.02004 | 240.48 | 1 | 5000 | 6017.4 | 240.48 | 0 | 0 | 0 | 0 | 45062.92 | 0 | 0 | 0 | 0 | 0 | 45062.92
2022092821 | 4 | 0.6764 | 54112 | 0.21994 | 7917.84 | 4e-05 | 0.48 | 1 | 5000 | 7917.84 | 0.48 | 0 | 0 | 0 | 0 | 41193.68 | 0 | 0 | 0 | 0 | 0 | 41193.68
2022092822 | 4 | 0.63638 | 50910.4 | 0.25535 | 9192.6 | 0 | 0 | 1 | 5000 | 9192.6 | 0 | 0 | 0 | 0 | 0 | 36717.8 | 0 | 0 | 0 | 0 | 0 | 36717.8
2022092823 | 4 | 0.5882 | 47056 | 0.29431 | 10595.16 | 0 | 0 | 1 | 5000 | 10595.16 | 0 | 0 | 0 | 0 | 0 | 31460.84 | 0 | 0 | 0 | 0 | 0 | 31460.84
2022092824 | 4 | 0.54172 | 43337.6 | 0.31167 | 11220.12 | 0 | 0 | 1 | 5000 | 11220.12 | 0 | 0 | 0 | 0 | 0 | 27117.48 | 0 | 0 | 0 | 0 | 0 | 27117.48
2022092901 | 5 | 0.50759 | 40607.2 | 0.32039 | 11534.04 | 0 | 0 | 1 | 5000 | 11534.04 | 0 | 0 | 0 | 0 | 0 | 24073.16 | 0 | 0 | 0 | 0 | 0 | 24073.16
2022092902 | 5 | 0.48121 | 38496.8 | 0.31956 | 11504.16 | 0 | 0 | 1 | 5000 | 11504.16 | 0 | 0 | 0 | 0 | 0 | 21992.64 | 0 | 0 | 0 | 0 | 0 | 21992.64
2022092903 | 5 | 0.46749 | 37399.2 | 0.30829 | 11098.44 | 0 | 0 | 1 | 5000 | 11098.44 | 0 | 0 | 0 | 0 | 0 | 21300.76 | 0 | 0 | 0 | 0 | 0 | 21300.76
2022092904 | 5 | 0.45874 | 36699.2 | 0.30081 | 10829.16 | 0 | 0 | 1 | 5000 | 10829.16 | 0 | 0 | 0 | 0 | 0 | 20870.04 | 0 | 0 | 0 | 0 | 0 | 20870.04
2022092905 | 5 | 0.458 | 36640 | 0.2942 | 10591.2 | 0 | 0 | 1 | 5000 | 10591.2 | 0 | 0 | 0 | 0 | 0 | 21048.8 | 0 | 0 | 0 | 0 | 0 | 21048.8
2022092906 | 5 | 0.46986 | 37588.8 | 0.29833 | 10739.88 | 0 | 0 | 1 | 5000 | 10739.88 | 0 | 0 | 0 | 0 | 0 | 21848.92 | 0 | 0 | 0 | 0 | 0 | 21848.92
2022092907 | 5 | 0.49932 | 39945.6 | 0.27962 | 10066.32 | 0 | 0 | 1 | 5000 | 10066.32 | 0 | 0 | 0 | 0 | 0 | 24879.28 | 0 | 0 | 0 | 0 | 0 | 24879.28
2022092908 | 5 | 0.5091 | 40728 | 0.26424 | 9512.64 | 0.01323 | 158.76 | 1 | 5000 | 9512.64 | 158.76 | 0 | 0 | 0 | 0 | 26056.6 | 0 | 0 | 0 | 0 | 0 | 26056.6
2022092909 | 5 | 0.51563 | 41250.4 | 0.21796 | 7846.56 | 0.3068 | 3681.6 | 1 | 5000 | 7846.56 | 3681.6 | 0 | 0 | 0 | 0 | 24722.24 | 0 | 0 | 0 | 0 | 0 | 24722.24
2022092910 | 5 | 0.53412 | 42729.6 | 0.12482 | 4493.52 | 0.7081 | 8497.2 | 1 | 5000 | 4493.52 | 8497.2 | 0 | 0 | 0 | 0 | 24738.88 | 0 | 0 | 0 | 0 | 0 | 24738.88
2022092911 | 5 | 0.55653 | 44522.4 | 0.12271 | 4417.56 | 0.79496 | 9539.52 | 1 | 5000 | 4417.56 | 9539.52 | 0 | 0 | 0 | 0 | 25565.32 | 0 | 0 | 0 | 0 | 0 | 25565.32
2022092912 | 5 | 0.58013 | 46410.4 | 0.11366 | 4091.76 | 0.8053 | 9663.6 | 1 | 5000 | 4091.76 | 9663.6 | 0 | 0 | 0 | 0 | 27655.04 | 0 | 0 | 0 | 0 | 0 | 27655.04
2022092913 | 5 | 0.60829 | 48663.2 | 0.08809 | 3171.24 | 0.79754 | 9570.48 | 1 | 5000 | 3171.24 | 9570.48 | 0 | 0 | 0 | 0 | 30921.48 | 0 | 0 | 0 | 0 | 0 | 30921.48
2022092914 | 5 | 0.64246 | 51396.8 | 0.06311 | 2271.96 | 0.78958 | 9474.96 | 1 | 5000 | 2271.96 | 9474.96 | 0 | 0 | 0 | 0 | 34649.88 | 0 | 0 | 0 | 0 | 0 | 34649.88
2022092915 | 5 | 0.67361 | 53888.8 | 0.05764 | 2075.04 | 0.79304 | 9516.48 | 1 | 5000 | 2075.04 | 9516.48 | 0 | 0 | 0 | 0 | 37297.28 | 0 | 0 | 0 | 0 | 0 | 37297.28
2022092916 | 5 | 0.70377 | 56301.6 | 0.06093 | 2193.48 | 0.79647 | 9557.64 | 1 | 5000 | 2193.48 | 9557.64 | 0 | 0 | 0 | 0 | 39550.48 | 0 | 0 | 0 | 0 | 0 | 39550.48
2022092917 | 5 | 0.72765 | 58212 | 0.0652 | 2347.2 | 0.78253 | 9390.36 | 1 | 5000 | 2347.2 | 9390.36 | 0 | 0 | 0 | 0 | 41474.44 | 0 | 0 | 0 | 0 | 0 | 41474.44
2022092918 | 5 | 0.72903 | 58322.4 | 0.07605 | 2737.8 | 0.67285 | 8074.2 | 1 | 5000 | 2737.8 | 8074.2 | 0 | 0 | 0 | 0 | 42510.4 | 0 | 0 | 0 | 0 | 0 | 42510.4
2022092919 | 5 | 0.70497 | 56397.6 | 0.09371 | 3373.56 | 0.2995 | 3594 | 1 | 5000 | 3373.56 | 3594 | 0 | 0 | 0 | 0 | 44430.04 | 0 | 0 | 0 | 0 | 0 | 44430.04
2022092920 | 5 | 0.67815 | 54252 | 0.1178 | 4240.8 | 0.0152 | 182.4 | 1 | 5000 | 4240.8 | 182.4 | 0 | 0 | 0 | 0 | 44828.8 | 0 | 0 | 0 | 0 | 0 | 44828.8
2022092921 | 5 | 0.65063 | 52050.4 | 0.19375 | 6975 | 0 | 0 | 1 | 5000 | 6975 | 0 | 0 | 0 | 0 | 0 | 40075.4 | 0 | 0 | 0 | 0 | 0 | 40075.4
2022092922 | 5 | 0.616 | 49280 | 0.26213 | 9436.68 | 0 | 0 | 1 | 5000 | 9436.68 | 0 | 0 | 0 | 0 | 0 | 34843.32 | 0 | 0 | 0 | 0 | 0 | 34843.32
2022092923 | 5 | 0.5732 | 45856 | 0.29952 | 10782.72 | 0 | 0 | 1 | 5000 | 10782.72 | 0 | 0 | 0 | 0 | 0 | 30073.28 | 0 | 0 | 0 | 0 | 0 | 30073.28
2022092924 | 5 | 0.53033 | 42426.4 | 0.33188 | 11947.68 | 0 | 0 | 1 | 5000 | 11947.68 | 0 | 0 | 0 | 0 | 0 | 25478.72 | 0 | 0 | 0 | 0 | 0 | 25478.72
2022093001 | 6 | 0.49463 | 39570.4 | 0.37016 | 13325.76 | 0 | 0 | 1 | 5000 | 13325.76 | 0 | 0 | 0 | 0 | 0 | 21244.64 | 0 | 0 | 0 | 0 | 0 | 21244.64
2022093002 | 6 | 0.46888 | 37510.4 | 0.36153 | 13015.08 | 0 | 0 | 1 | 5000 | 13015.08 | 0 | 0 | 0 | 0 | 0 | 19495.32 | 0 | 0 | 0 | 0 | 0 | 19495.32
2022093003 | 6 | 0.45352 | 36281.6 | 0.34827 | 12537.72 | 0 | 0 | 1 | 5000 | 12537.72 | 0 | 0 | 0 | 0 | 0 | 18743.88 | 0 | 0 | 0 | 0 | 0 | 18743.88
2022093004 | 6 | 0.44325 | 35460 | 0.3281 | 11811.6 | 0 | 0 | 1 | 5000 | 11811.6 | 0 | 0 | 0 | 0 | 0 | 18648.4 | 0 | 0 | 0 | 0 | 0 | 18648.4
2022093005 | 6 | 0.44262 | 35409.6 | 0.30397 | 10942.92 | 0 | 0 | 1 | 5000 | 10942.92 | 0 | 0 | 0 | 0 | 0 | 19466.68 | 0 | 0 | 0 | 0 | 0 | 19466.68
2022093006 | 6 | 0.45403 | 36322.4 | 0.27725 | 9981 | 0 | 0 | 1 | 5000 | 9981 | 0 | 0 | 0 | 0 | 0 | 21341.4 | 0 | 0 | 0 | 0 | 0 | 21341.4
2022093007 | 6 | 0.48063 | 38450.4 | 0.24268 | 8736.48 | 0 | 0 | 1 | 5000 | 8736.48 | 0 | 0 | 0 | 0 | 0 | 24713.92 | 0 | 0 | 0 | 0 | 0 | 24713.92
2022093008 | 6 | 0.49224 | 39379.2 | 0.20799 | 7487.64 | 0.01467 | 176.04 | 1 | 5000 | 7487.64 | 176.04 | 0 | 0 | 0 | 0 | 26715.52 | 0 | 0 | 0 | 0 | 0 | 26715.52
2022093009 | 6 | 0.50193 | 40154.4 | 0.16262 | 5854.32 | 0.31563 | 3787.56 | 1 | 5000 | 5854.32 | 3787.56 | 0 | 0 | 0 | 0 | 25512.52 | 0 | 0 | 0 | 0 | 0 | 25512.52
2022093010 | 6 | 0.52323 | 41858.4 | 0.09148 | 3293.28 | 0.71543 | 8585.16 | 1 | 5000 | 3293.28 | 8585.16 | 0 | 0 | 0 | 0 | 24979.96 | 0 | 0 | 0 | 0 | 0 | 24979.96
2022093011 | 6 | 0.53944 | 43155.2 | 0.06609 | 2379.24 | 0.78906 | 9468.72 | 1 | 5000 | 2379.24 | 9468.72 | 0 | 0 | 0 | 0 | 26307.24 | 0 | 0 | 0 | 0 | 0 | 26307.24
2022093012 | 6 | 0.56286 | 45028.8 | 0.05965 | 2147.4 | 0.79019 | 9482.28 | 1 | 5000 | 2147.4 | 9482.28 | 0 | 0 | 0 | 0 | 28399.12 | 0 | 0 | 0 | 0 | 0 | 28399.12
2022093013 | 6 | 0.58956 | 47164.8 | 0.06086 | 2190.96 | 0.79308 | 9516.96 | 1 | 5000 | 2190.96 | 9516.96 | 0 | 0 | 0 | 0 | 30456.88 | 0 | 0 | 0 | 0 | 0 | 30456.88
2022093014 | 6 | 0.62267 | 49813.6 | 0.06594 | 2373.84 | 0.76845 | 9221.4 | 1 | 5000 | 2373.84 | 9221.4 | 0 | 0 | 0 | 0 | 33218.36 | 0 | 0 | 0 | 0 | 0 | 33218.36
2022093015 | 6 | 0.65281 | 52224.8 | 0.079 | 2844 | 0.76586 | 9190.32 | 1 | 5000 | 2844 | 9190.32 | 0 | 0 | 0 | 0 | 35190.48 | 0 | 0 | 0 | 0 | 0 | 35190.48
2022093016 | 6 | 0.6803 | 54424 | 0.09684 | 3486.24 | 0.76691 | 9202.92 | 1 | 5000 | 3486.24 | 9202.92 | 0 | 0 | 0 | 0 | 36734.84 | 0 | 0 | 0 | 0 | 0 | 36734.84
2022093017 | 6 | 0.70003 | 56002.4 | 0.13095 | 4714.2 | 0.76994 | 9239.28 | 1 | 5000 | 4714.2 | 9239.28 | 0 | 0 | 0 | 0 | 37048.92 | 0 | 0 | 0 | 0 | 0 | 37048.92
2022093018 | 6 | 0.7003 | 56024 | 0.15634 | 5628.24 | 0.6771 | 8125.2 | 1 | 5000 | 5628.24 | 8125.2 | 0 | 0 | 0 | 0 | 37270.56 | 0 | 0 | 0 | 0 | 0 | 37270.56
2022093019 | 6 | 0.67217 | 53773.6 | 0.19178 | 6904.08 | 0.311 | 3732 | 1 | 5000 | 6904.08 | 3732 | 0 | 0 | 0 | 0 | 38137.52 | 0 | 0 | 0 | 0 | 0 | 38137.52
2022093020 | 6 | 0.63702 | 50961.6 | 0.21228 | 7642.08 | 0.01353 | 162.36 | 1 | 5000 | 7642.08 | 162.36 | 0 | 0 | 0 | 0 | 38157.16 | 0 | 0 | 0 | 0 | 0 | 38157.16
2022093021 | 6 | 0.61172 | 48937.6 | 0.30102 | 10836.72 | 0 | 0 | 1 | 5000 | 10836.72 | 0 | 0 | 0 | 0 | 0 | 33100.88 | 0 | 0 | 0 | 0 | 0 | 33100.88
2022093022 | 6 | 0.58405 | 46724 | 0.39698 | 14291.28 | 0 | 0 | 1 | 5000 | 14291.28 | 0 | 0 | 0 | 0 | 0 | 27432.72 | 0 | 0 | 0 | 0 | 0 | 27432.72
2022093023 | 6 | 0.55158 | 44126.4 | 0.44327 | 15957.72 | 0 | 0 | 1 | 5000 | 15957.72 | 0 | 0 | 0 | 0 | 0 | 23168.68 | 0 | 0 | 0 | 0 | 0 | 23168.68
2022093024 | 6 | 0.516 | 41280 | 0.46112 | 16600.32 | 0 | 0 | 1 | 5000 | 16600.32 | 0 | 0 | 0 | 0 | 0 | 19679.68 | 0 | 0 | 0 | 0 | 0 | 19679.68
2022100101 | 7 | 0.48266 | 38612.8 | 0.44886 | 16158.96 | 0 | 0 | 1 | 5000 | 16158.96 | 0 | 0 | 0 | 0 | 0 | 17453.84 | 0 | 0 | 0 | 0 | 0 | 17453.84
2022100102 | 7 | 0.45785 | 36628 | 0.41895 | 15082.2 | 0 | 0 | 1 | 5000 | 15082.2 | 0 | 0 | 0 | 0 | 0 | 16545.8 | 0 | 0 | 0 | 0 | 0 | 16545.8
2022100103 | 7 | 0.44111 | 35288.8 | 0.38219 | 13758.84 | 0 | 0 | 1 | 5000 | 13758.84 | 0 | 0 | 0 | 0 | 0 | 16529.96 | 0 | 0 | 0 | 0 | 0 | 16529.96
2022100104 | 7 | 0.42964 | 34371.2 | 0.35202 | 12672.72 | 0 | 0 | 1 | 5000 | 12672.72 | 0 | 0 | 0 | 0 | 0 | 16698.48 | 0 | 0 | 0 | 0 | 0 | 16698.48
2022100105 | 7 | 0.42522 | 34017.6 | 0.32856 | 11828.16 | 0 | 0 | 1 | 5000 | 11828.16 | 0 | 0 | 0 | 0 | 0 | 17189.44 | 0 | 0 | 0 | 0 | 0 | 17189.44
2022100106 | 7 | 0.42475 | 33980 | 0.30502 | 10980.72 | 0 | 0 | 1 | 5000 | 10980.72 | 0 | 0 | 0 | 0 | 0 | 17999.28 | 0 | 0 | 0 | 0 | 0 | 17999.28
2022100107 | 7 | 0.43239 | 34591.2 | 0.27535 | 9912.6 | 0 | 0 | 1 | 5000 | 9912.6 | 0 | 0 | 0 | 0 | 0 | 19678.6 | 0 | 0 | 0 | 0 | 0 | 19678.6
2022100108 | 7 | 0.43994 | 35195.2 | 0.2489 | 8960.4 | 0.01557 | 186.84 | 1 | 5000 | 8960.4 | 186.84 | 0 | 0 | 0 | 0 | 21047.96 | 0 | 0 | 0 | 0 | 0 | 21047.96
2022100109 | 7 | 0.45839 | 36671.2 | 0.20717 | 7458.12 | 0.32122 | 3854.64 | 1 | 5000 | 7458.12 | 3854.64 | 0 | 0 | 0 | 0 | 20358.44 | 0 | 0 | 0 | 0 | 0 | 20358.44
2022100110 | 7 | 0.48419 | 38735.2 | 0.11667 | 4200.12 | 0.71671 | 8600.52 | 1 | 5000 | 4200.12 | 8600.52 | 0 | 0 | 0 | 0 | 20934.56 | 0 | 0 | 0 | 0 | 0 | 20934.56
2022100111 | 7 | 0.50925 | 40740 | 0.10537 | 3793.32 | 0.80802 | 9696.24 | 1 | 5000 | 3793.32 | 9696.24 | 0 | 0 | 0 | 0 | 22250.44 | 0 | 0 | 0 | 0 | 0 | 22250.44
2022100112 | 7 | 0.53254 | 42603.2 | 0.08719 | 3138.84 | 0.80984 | 9718.08 | 1 | 5000 | 3138.84 | 9718.08 | 0 | 0 | 0 | 0 | 24746.28 | 0 | 0 | 0 | 0 | 0 | 24746.28
2022100113 | 7 | 0.55966 | 44772.8 | 0.06911 | 2487.96 | 0.80132 | 9615.84 | 1 | 5000 | 2487.96 | 9615.84 | 0 | 0 | 0 | 0 | 27669 | 0 | 0 | 0 | 0 | 0 | 27669
2022100114 | 7 | 0.58828 | 47062.4 | 0.08044 | 2895.84 | 0.79763 | 9571.56 | 1 | 5000 | 2895.84 | 9571.56 | 0 | 0 | 0 | 0 | 29595 | 0 | 0 | 0 | 0 | 0 | 29595
2022100115 | 7 | 0.61831 | 49464.8 | 0.10299 | 3707.64 | 0.80476 | 9657.12 | 1 | 5000 | 3707.64 | 9657.12 | 0 | 0 | 0 | 0 | 31100.04 | 0 | 0 | 0 | 0 | 0 | 31100.04
2022100116 | 7 | 0.64614 | 51691.2 | 0.1214 | 4370.4 | 0.80121 | 9614.52 | 1 | 5000 | 4370.4 | 9614.52 | 0 | 0 | 0 | 0 | 32706.28 | 0 | 0 | 0 | 0 | 0 | 32706.28
2022100117 | 7 | 0.66451 | 53160.8 | 0.1371 | 4935.6 | 0.77531 | 9303.72 | 1 | 5000 | 4935.6 | 9303.72 | 0 | 0 | 0 | 0 | 33921.48 | 0 | 0 | 0 | 0 | 0 | 33921.48
2022100118 | 7 | 0.66658 | 53326.4 | 0.15929 | 5734.44 | 0.65623 | 7874.76 | 1 | 5000 | 5734.44 | 7874.76 | 0 | 0 | 0 | 0 | 34717.2 | 0 | 0 | 0 | 0 | 0 | 34717.2
2022100119 | 7 | 0.64345 | 51476 | 0.18123 | 6524.28 | 0.24905 | 2988.6 | 1 | 5000 | 6524.28 | 2988.6 | 0 | 0 | 0 | 0 | 36963.12 | 0 | 0 | 0 | 0 | 0 | 36963.12
2022100120 | 7 | 0.61331 | 49064.8 | 0.21662 | 7798.32 | 0.00803 | 96.36 | 1 | 5000 | 7798.32 | 96.36 | 0 | 0 | 0 | 0 | 36170.12 | 0 | 0 | 0 | 0 | 0 | 36170.12
2022100121 | 7 | 0.58838 | 47070.4 | 0.29961 | 10785.96 | 0 | 0 | 1 | 5000 | 10785.96 | 0 | 0 | 0 | 0 | 0 | 31284.44 | 0 | 0 | 0 | 0 | 0 | 31284.44
2022100122 | 7 | 0.56086 | 44868.8 | 0.37431 | 13475.16 | 0 | 0 | 1 | 5000 | 13475.16 | 0 | 0 | 0 | 0 | 0 | 26393.64 | 0 | 0 | 0 | 0 | 0 | 26393.64
2022100123 | 7 | 0.53011 | 42408.8 | 0.40196 | 14470.56 | 0 | 0 | 1 | 5000 | 14470.56 | 0 | 0 | 0 | 0 | 0 | 22938.24 | 0 | 0 | 0 | 0 | 0 | 22938.24
2022100124 | 7 | 0.49769 | 39815.2 | 0.39938 | 14377.68 | 0 | 0 | 1 | 5000 | 14377.68 | 0 | 0 | 0 | 0 | 0 | 20437.52 | 0 | 0 | 0 | 0 | 0 | 20437.52
2022100201 | 1 | 0.46992 | 37593.6 | 0.37751 | 13590.36 | 0 | 0 | 1 | 5000 | 13590.36 | 0 | 0 | 0 | 0 | 0 | 19003.24 | 0 | 0 | 0 | 0 | 0 | 19003.24
2022100202 | 1 | 0.44728 | 35782.4 | 0.34724 | 12500.64 | 0 | 0 | 1 | 5000 | 12500.64 | 0 | 0 | 0 | 0 | 0 | 18281.76 | 0 | 0 | 0 | 0 | 0 | 18281.76
2022100203 | 1 | 0.43096 | 34476.8 | 0.31218 | 11238.48 | 0 | 0 | 1 | 5000 | 11238.48 | 0 | 0 | 0 | 0 | 0 | 18238.32 | 0 | 0 | 0 | 0 | 0 | 18238.32
2022100204 | 1 | 0.42256 | 33804.8 | 0.27348 | 9845.28 | 0 | 0 | 1 | 5000 | 9845.28 | 0 | 0 | 0 | 0 | 0 | 18959.52 | 0 | 0 | 0 | 0 | 0 | 18959.52
2022100205 | 1 | 0.4167 | 33336 | 0.22832 | 8219.52 | 0 | 0 | 1 | 5000 | 8219.52 | 0 | 0 | 0 | 0 | 0 | 20116.48 | 0 | 0 | 0 | 0 | 0 | 20116.48
2022100206 | 1 | 0.41399 | 33119.2 | 0.18215 | 6557.4 | 0 | 0 | 1 | 5000 | 6557.4 | 0 | 0 | 0 | 0 | 0 | 21561.8 | 0 | 0 | 0 | 0 | 0 | 21561.8
2022100207 | 1 | 0.42041 | 33632.8 | 0.1521 | 5475.6 | 0 | 0 | 1 | 5000 | 5475.6 | 0 | 0 | 0 | 0 | 0 | 23157.2 | 0 | 0 | 0 | 0 | 0 | 23157.2
2022100208 | 1 | 0.42705 | 34164 | 0.12792 | 4605.12 | 0.01286 | 154.32 | 1 | 5000 | 4605.12 | 154.32 | 0 | 0 | 0 | 0 | 24404.56 | 0 | 0 | 0 | 0 | 0 | 24404.56
2022100209 | 1 | 0.44412 | 35529.6 | 0.10398 | 3743.28 | 0.28783 | 3453.96 | 1 | 5000 | 3743.28 | 3453.96 | 0 | 0 | 0 | 0 | 23332.36 | 0 | 0 | 0 | 0 | 0 | 23332.36
2022100210 | 1 | 0.47026 | 37620.8 | 0.05351 | 1926.36 | 0.66235 | 7948.2 | 1 | 5000 | 1926.36 | 7948.2 | 0 | 0 | 0 | 0 | 22746.24 | 0 | 0 | 0 | 0 | 0 | 22746.24
2022100211 | 1 | 0.49684 | 39747.2 | 0.05514 | 1985.04 | 0.74665 | 8959.8 | 1 | 5000 | 1985.04 | 8959.8 | 0 | 0 | 0 | 0 | 23802.36 | 0 | 0 | 0 | 0 | 0 | 23802.36
2022100212 | 1 | 0.52645 | 42116 | 0.0546 | 1965.6 | 0.76139 | 9136.68 | 1 | 5000 | 1965.6 | 9136.68 | 0 | 0 | 0 | 0 | 26013.72 | 0 | 0 | 0 | 0 | 0 | 26013.72
2022100213 | 1 | 0.55533 | 44426.4 | 0.03806 | 1370.16 | 0.75848 | 9101.76 | 1 | 5000 | 1370.16 | 9101.76 | 0 | 0 | 0 | 0 | 28954.48 | 0 | 0 | 0 | 0 | 0 | 28954.48
2022100214 | 1 | 0.58408 | 46726.4 | 0.04221 | 1519.56 | 0.77414 | 9289.68 | 1 | 5000 | 1519.56 | 9289.68 | 0 | 0 | 0 | 0 | 30917.16 | 0 | 0 | 0 | 0 | 0 | 30917.16
2022100215 | 1 | 0.61332 | 49065.6 | 0.05003 | 1801.08 | 0.75327 | 9039.24 | 1 | 5000 | 1801.08 | 9039.24 | 0 | 0 | 0 | 0 | 33225.28 | 0 | 0 | 0 | 0 | 0 | 33225.28
2022100216 | 1 | 0.64074 | 51259.2 | 0.05669 | 2040.84 | 0.75144 | 9017.28 | 1 | 5000 | 2040.84 | 9017.28 | 0 | 0 | 0 | 0 | 35201.08 | 0 | 0 | 0 | 0 | 0 | 35201.08
2022100217 | 1 | 0.65659 | 52527.2 | 0.06534 | 2352.24 | 0.69841 | 8380.92 | 1 | 5000 | 2352.24 | 8380.92 | 0 | 0 | 0 | 0 | 36794.04 | 0 | 0 | 0 | 0 | 0 | 36794.04
2022100218 | 1 | 0.65879 | 52703.2 | 0.07986 | 2874.96 | 0.5968 | 7161.6 | 1 | 5000 | 2874.96 | 7161.6 | 0 | 0 | 0 | 0 | 37666.64 | 0 | 0 | 0 | 0 | 0 | 37666.64
2022100219 | 1 | 0.64272 | 51417.6 | 0.10092 | 3633.12 | 0.27204 | 3264.48 | 1 | 5000 | 3633.12 | 3264.48 | 0 | 0 | 0 | 0 | 39520 | 0 | 0 | 0 | 0 | 0 | 39520
2022100220 | 1 | 0.62769 | 50215.2 | 0.15315 | 5513.4 | 0.01282 | 153.84 | 1 | 5000 | 5513.4 | 153.84 | 0 | 0 | 0 | 0 | 39547.96 | 0 | 0 | 0 | 0 | 0 | 39547.96
2022100221 | 1 | 0.60499 | 48399.2 | 0.23319 | 8394.84 | 0 | 0 | 1 | 5000 | 8394.84 | 0 | 0 | 0 | 0 | 0 | 35004.36 | 0 | 0 | 0 | 0 | 0 | 35004.36
2022100222 | 1 | 0.57715 | 46172 | 0.29141 | 10490.76 | 0 | 0 | 1 | 5000 | 10490.76 | 0 | 0 | 0 | 0 | 0 | 30681.24 | 0 | 0 | 0 | 0 | 0 | 30681.24
2022100223 | 1 | 0.53457 | 42765.6 | 0.31841 | 11462.76 | 0 | 0 | 1 | 5000 | 11462.76 | 0 | 0 | 0 | 0 | 0 | 26302.84 | 0 | 0 | 0 | 0 | 0 | 26302.84
2022100224 | 1 | 0.49488 | 39590.4 | 0.33442 | 12039.12 | 0 | 0 | 1 | 5000 | 12039.12 | 0 | 0 | 0 | 0 | 0 | 22551.28 | 0 | 0 | 0 | 0 | 0 | 22551.28
2022100301 | 2 | 0.46167 | 36933.6 | 0.31752 | 11430.72 | 0 | 0 | 1 | 5000 | 11430.72 | 0 | 0 | 0 | 0 | 0 | 20502.88 | 0 | 0 | 0 | 0 | 0 | 20502.88
2022100302 | 2 | 0.4417 | 35336 | 0.30352 | 10926.72 | 0 | 0 | 1 | 5000 | 10926.72 | 0 | 0 | 0 | 0 | 0 | 19409.28 | 0 | 0 | 0 | 0 | 0 | 19409.28
2022100303 | 2 | 0.42956 | 34364.8 | 0.26744 | 9627.84 | 0 | 0 | 1 | 5000 | 9627.84 | 0 | 0 | 0 | 0 | 0 | 19736.96 | 0 | 0 | 0 | 0 | 0 | 19736.96
2022100304 | 2 | 0.42494 | 33995.2 | 0.22286 | 8022.96 | 0 | 0 | 1 | 5000 | 8022.96 | 0 | 0 | 0 | 0 | 0 | 20972.24 | 0 | 0 | 0 | 0 | 0 | 20972.24
2022100305 | 2 | 0.42776 | 34220.8 | 0.18292 | 6585.12 | 0 | 0 | 1 | 5000 | 6585.12 | 0 | 0 | 0 | 0 | 0 | 22635.68 | 0 | 0 | 0 | 0 | 0 | 22635.68
2022100306 | 2 | 0.44651 | 35720.8 | 0.15048 | 5417.28 | 0 | 0 | 1 | 5000 | 5417.28 | 0 | 0 | 0 | 0 | 0 | 25303.52 | 0 | 0 | 0 | 0 | 0 | 25303.52
2022100307 | 2 | 0.47684 | 38147.2 | 0.12822 | 4615.92 | 0 | 0 | 1 | 5000 | 4615.92 | 0 | 0 | 0 | 0 | 0 | 28531.28 | 0 | 0 | 0 | 0 | 0 | 28531.28
2022100308 | 2 | 0.4897 | 39176 | 0.11981 | 4313.16 | 0.01267 | 152.04 | 1 | 5000 | 4313.16 | 152.04 | 0 | 0 | 0 | 0 | 29710.8 | 0 | 0 | 0 | 0 | 0 | 29710.8
2022100309 | 2 | 0.4995 | 39960 | 0.11524 | 4148.64 | 0.23747 | 2849.64 | 1 | 5000 | 4148.64 | 2849.64 | 0 | 0 | 0 | 0 | 27961.72 | 0 | 0 | 0 | 0 | 0 | 27961.72
2022100310 | 2 | 0.51963 | 41570.4 | 0.0677 | 2437.2 | 0.57664 | 6919.68 | 1 | 5000 | 2437.2 | 6919.68 | 0 | 0 | 0 | 0 | 27213.52 | 0 | 0 | 0 | 0 | 0 | 27213.52
2022100311 | 2 | 0.53855 | 43084 | 0.07097 | 2554.92 | 0.70803 | 8496.36 | 1 | 5000 | 2554.92 | 8496.36 | 0 | 0 | 0 | 0 | 27032.72 | 0 | 0 | 0 | 0 | 0 | 27032.72
2022100312 | 2 | 0.5605 | 44840 | 0.07502 | 2700.72 | 0.76779 | 9213.48 | 1 | 5000 | 2700.72 | 9213.48 | 0 | 0 | 0 | 0 | 27925.8 | 0 | 0 | 0 | 0 | 0 | 27925.8
2022100313 | 2 | 0.58933 | 47146.4 | 0.06377 | 2295.72 | 0.74075 | 8889 | 1 | 5000 | 2295.72 | 8889 | 0 | 0 | 0 | 0 | 30961.68 | 0 | 0 | 0 | 0 | 0 | 30961.68
2022100314 | 2 | 0.62086 | 49668.8 | 0.06065 | 2183.4 | 0.75009 | 9001.08 | 1 | 5000 | 2183.4 | 9001.08 | 0 | 0 | 0 | 0 | 33484.32 | 0 | 0 | 0 | 0 | 0 | 33484.32
2022100315 | 2 | 0.65276 | 52220.8 | 0.06258 | 2252.88 | 0.7474 | 8968.8 | 1 | 5000 | 2252.88 | 8968.8 | 0 | 0 | 0 | 0 | 35999.12 | 0 | 0 | 0 | 0 | 0 | 35999.12
2022100316 | 2 | 0.6814 | 54512 | 0.07118 | 2562.48 | 0.74833 | 8979.96 | 1 | 5000 | 2562.48 | 8979.96 | 0 | 0 | 0 | 0 | 37969.56 | 0 | 0 | 0 | 0 | 0 | 37969.56
2022100317 | 2 | 0.7009 | 56072 | 0.08051 | 2898.36 | 0.69394 | 8327.28 | 1 | 5000 | 2898.36 | 8327.28 | 0 | 0 | 0 | 0 | 39846.36 | 0 | 0 | 0 | 0 | 0 | 39846.36
2022100318 | 2 | 0.70095 | 56076 | 0.0916 | 3297.6 | 0.53987 | 6478.44 | 1 | 5000 | 3297.6 | 6478.44 | 0 | 0 | 0 | 0 | 41299.96 | 0 | 0 | 0 | 0 | 0 | 41299.96
2022100319 | 2 | 0.67909 | 54327.2 | 0.10525 | 3789 | 0.18896 | 2267.52 | 1 | 5000 | 3789 | 2267.52 | 0 | 0 | 0 | 0 | 43270.68 | 0 | 0 | 0 | 0 | 0 | 43270.68
2022100320 | 2 | 0.65689 | 52551.2 | 0.13965 | 5027.4 | 0.00604 | 72.48 | 1 | 5000 | 5027.4 | 72.48 | 0 | 0 | 0 | 0 | 42451.32 | 0 | 0 | 0 | 0 | 0 | 42451.32
2022100321 | 2 | 0.63276 | 50620.8 | 0.19959 | 7185.24 | 0 | 0 | 1 | 5000 | 7185.24 | 0 | 0 | 0 | 0 | 0 | 38435.56 | 0 | 0 | 0 | 0 | 0 | 38435.56
2022100322 | 2 | 0.5977 | 47816 | 0.25949 | 9341.64 | 0 | 0 | 1 | 5000 | 9341.64 | 0 | 0 | 0 | 0 | 0 | 33474.36 | 0 | 0 | 0 | 0 | 0 | 33474.36
2022100323 | 2 | 0.55496 | 44396.8 | 0.30279 | 10900.44 | 0 | 0 | 1 | 5000 | 10900.44 | 0 | 0 | 0 | 0 | 0 | 28496.36 | 0 | 0 | 0 | 0 | 0 | 28496.36
2022100324 | 2 | 0.51245 | 40996 | 0.33023 | 11888.28 | 0 | 0 | 1 | 5000 | 11888.28 | 0 | 0 | 0 | 0 | 0 | 24107.72 | 0 | 0 | 0 | 0 | 0 | 24107.72
2022100401 | 3 | 0.48206 | 38564.8 | 0.32945 | 11860.2 | 0 | 0 | 1 | 5000 | 11860.2 | 0 | 0 | 0 | 0 | 0 | 21704.6 | 0 | 0 | 0 | 0 | 0 | 21704.6
2022100402 | 3 | 0.46129 | 36903.2 | 0.29988 | 10795.68 | 0 | 0 | 1 | 5000 | 10795.68 | 0 | 0 | 0 | 0 | 0 | 21107.52 | 0 | 0 | 0 | 0 | 0 | 21107.52
2022100403 | 3 | 0.44609 | 35687.2 | 0.27447 | 9880.92 | 0 | 0 | 1 | 5000 | 9880.92 | 0 | 0 | 0 | 0 | 0 | 20806.28 | 0 | 0 | 0 | 0 | 0 | 20806.28
2022100404 | 3 | 0.44016 | 35212.8 | 0.24575 | 8847 | 0 | 0 | 1 | 5000 | 8847 | 0 | 0 | 0 | 0 | 0 | 21365.8 | 0 | 0 | 0 | 0 | 0 | 21365.8
2022100405 | 3 | 0.44205 | 35364 | 0.20598 | 7415.28 | 0 | 0 | 1 | 5000 | 7415.28 | 0 | 0 | 0 | 0 | 0 | 22948.72 | 0 | 0 | 0 | 0 | 0 | 22948.72
2022100406 | 3 | 0.45644 | 36515.2 | 0.19065 | 6863.4 | 0 | 0 | 1 | 5000 | 6863.4 | 0 | 0 | 0 | 0 | 0 | 24651.8 | 0 | 0 | 0 | 0 | 0 | 24651.8
2022100407 | 3 | 0.48604 | 38883.2 | 0.17413 | 6268.68 | 0 | 0 | 1 | 5000 | 6268.68 | 0 | 0 | 0 | 0 | 0 | 27614.52 | 0 | 0 | 0 | 0 | 0 | 27614.52
2022100408 | 3 | 0.49962 | 39969.6 | 0.16826 | 6057.36 | 0.0068 | 81.6 | 1 | 5000 | 6057.36 | 81.6 | 0 | 0 | 0 | 0 | 28830.64 | 0 | 0 | 0 | 0 | 0 | 28830.64
2022100409 | 3 | 0.50503 | 40402.4 | 0.15052 | 5418.72 | 0.20154 | 2418.48 | 1 | 5000 | 5418.72 | 2418.48 | 0 | 0 | 0 | 0 | 27565.2 | 0 | 0 | 0 | 0 | 0 | 27565.2
2022100410 | 3 | 0.52329 | 41863.2 | 0.08908 | 3206.88 | 0.55587 | 6670.44 | 1 | 5000 | 3206.88 | 6670.44 | 0 | 0 | 0 | 0 | 26985.88 | 0 | 0 | 0 | 0 | 0 | 26985.88
2022100411 | 3 | 0.54432 | 43545.6 | 0.10259 | 3693.24 | 0.6738 | 8085.6 | 1 | 5000 | 3693.24 | 8085.6 | 0 | 0 | 0 | 0 | 26766.76 | 0 | 0 | 0 | 0 | 0 | 26766.76
2022100412 | 3 | 0.56955 | 45564 | 0.14185 | 5106.6 | 0.6862 | 8234.4 | 1 | 5000 | 5106.6 | 8234.4 | 0 | 0 | 0 | 0 | 27223 | 0 | 0 | 0 | 0 | 0 | 27223
2022100413 | 3 | 0.59818 | 47854.4 | 0.11568 | 4164.48 | 0.7064 | 8476.8 | 1 | 5000 | 4164.48 | 8476.8 | 0 | 0 | 0 | 0 | 30213.12 | 0 | 0 | 0 | 0 | 0 | 30213.12
2022100414 | 3 | 0.63143 | 50514.4 | 0.0877 | 3157.2 | 0.70768 | 8492.16 | 1 | 5000 | 3157.2 | 8492.16 | 0 | 0 | 0 | 0 | 33865.04 | 0 | 0 | 0 | 0 | 0 | 33865.04
2022100415 | 3 | 0.66317 | 53053.6 | 0.07607 | 2738.52 | 0.71608 | 8592.96 | 1 | 5000 | 2738.52 | 8592.96 | 0 | 0 | 0 | 0 | 36722.12 | 0 | 0 | 0 | 0 | 0 | 36722.12
2022100416 | 3 | 0.68927 | 55141.6 | 0.07156 | 2576.16 | 0.71773 | 8612.76 | 1 | 5000 | 2576.16 | 8612.76 | 0 | 0 | 0 | 0 | 38952.68 | 0 | 0 | 0 | 0 | 0 | 38952.68
2022100417 | 3 | 0.70612 | 56489.6 | 0.07003 | 2521.08 | 0.67034 | 8044.08 | 1 | 5000 | 2521.08 | 8044.08 | 0 | 0 | 0 | 0 | 40924.44 | 0 | 0 | 0 | 0 | 0 | 40924.44
2022100418 | 3 | 0.70618 | 56494.4 | 0.07914 | 2849.04 | 0.53328 | 6399.36 | 1 | 5000 | 2849.04 | 6399.36 | 0 | 0 | 0 | 0 | 42246 | 0 | 0 | 0 | 0 | 0 | 42246
2022100419 | 3 | 0.68319 | 54655.2 | 0.10308 | 3710.88 | 0.18218 | 2186.16 | 1 | 5000 | 3710.88 | 2186.16 | 0 | 0 | 0 | 0 | 43758.16 | 0 | 0 | 0 | 0 | 0 | 43758.16
2022100420 | 3 | 0.66146 | 52916.8 | 0.14125 | 5085 | 0.00279 | 33.48 | 1 | 5000 | 5085 | 33.48 | 0 | 0 | 0 | 0 | 42798.32 | 0 | 0 | 0 | 0 | 0 | 42798.32
2022100421 | 3 | 0.63734 | 50987.2 | 0.21215 | 7637.4 | 0 | 0 | 1 | 5000 | 7637.4 | 0 | 0 | 0 | 0 | 0 | 38349.8 | 0 | 0 | 0 | 0 | 0 | 38349.8
2022100422 | 3 | 0.60268 | 48214.4 | 0.28861 | 10389.96 | 0 | 0 | 1 | 5000 | 10389.96 | 0 | 0 | 0 | 0 | 0 | 32824.44 | 0 | 0 | 0 | 0 | 0 | 32824.44
2022100423 | 3 | 0.56225 | 44980 | 0.34216 | 12317.76 | 0 | 0 | 1 | 5000 | 12317.76 | 0 | 0 | 0 | 0 | 0 | 27662.24 | 0 | 0 | 0 | 0 | 0 | 27662.24
2022100424 | 3 | 0.51887 | 41509.6 | 0.35926 | 12933.36 | 0 | 0 | 1 | 5000 | 12933.36 | 0 | 0 | 0 | 0 | 0 | 23576.24 | 0 | 0 | 0 | 0 | 0 | 23576.24
2022100501 | 4 | 0.48302 | 38641.6 | 0.36127 | 13005.72 | 0 | 0 | 1 | 5000 | 13005.72 | 0 | 0 | 0 | 0 | 0 | 20635.88 | 0 | 0 | 0 | 0 | 0 | 20635.88
2022100502 | 4 | 0.46047 | 36837.6 | 0.34941 | 12578.76 | 0 | 0 | 1 | 5000 | 12578.76 | 0 | 0 | 0 | 0 | 0 | 19258.84 | 0 | 0 | 0 | 0 | 0 | 19258.84
2022100503 | 4 | 0.44755 | 35804 | 0.31134 | 11208.24 | 0 | 0 | 1 | 5000 | 11208.24 | 0 | 0 | 0 | 0 | 0 | 19595.76 | 0 | 0 | 0 | 0 | 0 | 19595.76
2022100504 | 4 | 0.43877 | 35101.6 | 0.25878 | 9316.08 | 0 | 0 | 1 | 5000 | 9316.08 | 0 | 0 | 0 | 0 | 0 | 20785.52 | 0 | 0 | 0 | 0 | 0 | 20785.52
2022100505 | 4 | 0.43958 | 35166.4 | 0.21547 | 7756.92 | 0 | 0 | 1 | 5000 | 7756.92 | 0 | 0 | 0 | 0 | 0 | 22409.48 | 0 | 0 | 0 | 0 | 0 | 22409.48
2022100506 | 4 | 0.4542 | 36336 | 0.18196 | 6550.56 | 0 | 0 | 1 | 5000 | 6550.56 | 0 | 0 | 0 | 0 | 0 | 24785.44 | 0 | 0 | 0 | 0 | 0 | 24785.44
2022100507 | 4 | 0.48419 | 38735.2 | 0.15184 | 5466.24 | 0 | 0 | 1 | 5000 | 5466.24 | 0 | 0 | 0 | 0 | 0 | 28268.96 | 0 | 0 | 0 | 0 | 0 | 28268.96
2022100508 | 4 | 0.49672 | 39737.6 | 0.13052 | 4698.72 | 0.01087 | 130.44 | 1 | 5000 | 4698.72 | 130.44 | 0 | 0 | 0 | 0 | 29908.44 | 0 | 0 | 0 | 0 | 0 | 29908.44
2022100509 | 4 | 0.5042 | 40336 | 0.11008 | 3962.88 | 0.23975 | 2877 | 1 | 5000 | 3962.88 | 2877 | 0 | 0 | 0 | 0 | 28496.12 | 0 | 0 | 0 | 0 | 0 | 28496.12
2022100510 | 4 | 0.52501 | 42000.8 | 0.07018 | 2526.48 | 0.50693 | 6083.16 | 1 | 5000 | 2526.48 | 6083.16 | 0 | 0 | 0 | 0 | 28391.16 | 0 | 0 | 0 | 0 | 0 | 28391.16
2022100511 | 4 | 0.55305 | 44244 | 0.07293 | 2625.48 | 0.65773 | 7892.76 | 1 | 5000 | 2625.48 | 7892.76 | 0 | 0 | 0 | 0 | 28725.76 | 0 | 0 | 0 | 0 | 0 | 28725.76
2022100512 | 4 | 0.58589 | 46871.2 | 0.05636 | 2028.96 | 0.73041 | 8764.92 | 1 | 5000 | 2028.96 | 8764.92 | 0 | 0 | 0 | 0 | 31077.32 | 0 | 0 | 0 | 0 | 0 | 31077.32
2022100513 | 4 | 0.6221 | 49768 | 0.04678 | 1684.08 | 0.72716 | 8725.92 | 1 | 5000 | 1684.08 | 8725.92 | 0 | 0 | 0 | 0 | 34358 | 0 | 0 | 0 | 0 | 0 | 34358
2022100514 | 4 | 0.65948 | 52758.4 | 0.04776 | 1719.36 | 0.68623 | 8234.76 | 1 | 5000 | 1719.36 | 8234.76 | 0 | 0 | 0 | 0 | 37804.28 | 0 | 0 | 0 | 0 | 0 | 37804.28
2022100515 | 4 | 0.69221 | 55376.8 | 0.06028 | 2170.08 | 0.65943 | 7913.16 | 1 | 5000 | 2170.08 | 7913.16 | 0 | 0 | 0 | 0 | 40293.56 | 0 | 0 | 0 | 0 | 0 | 40293.56
2022100516 | 4 | 0.71894 | 57515.2 | 0.08258 | 2972.88 | 0.61569 | 7388.28 | 1 | 5000 | 2972.88 | 7388.28 | 0 | 0 | 0 | 0 | 42154.04 | 0 | 0 | 0 | 0 | 0 | 42154.04
2022100517 | 4 | 0.73781 | 59024.8 | 0.09049 | 3257.64 | 0.58605 | 7032.6 | 1 | 5000 | 3257.64 | 7032.6 | 0 | 0 | 0 | 0 | 43734.56 | 0 | 0 | 0 | 0 | 0 | 43734.56
2022100518 | 4 | 0.73426 | 58740.8 | 0.10379 | 3736.44 | 0.44458 | 5334.96 | 1 | 5000 | 3736.44 | 5334.96 | 0 | 0 | 0 | 0 | 44669.4 | 0 | 0 | 0 | 0 | 0 | 44669.4
2022100519 | 4 | 0.70439 | 56351.2 | 0.14134 | 5088.24 | 0.11144 | 1337.28 | 1 | 5000 | 5088.24 | 1337.28 | 0 | 0 | 0 | 0 | 44925.68 | 0 | 0 | 0 | 0 | 0 | 44925.68
2022100520 | 4 | 0.6815 | 54520 | 0.1704 | 6134.4 | 0.00245 | 29.4 | 1 | 5000 | 6134.4 | 29.4 | 0 | 0 | 0 | 0 | 43356.2 | 0 | 0 | 0 | 0 | 0 | 43356.2
2022100521 | 4 | 0.65615 | 52492 | 0.20478 | 7372.08 | 0 | 0 | 1 | 5000 | 7372.08 | 0 | 0 | 0 | 0 | 0 | 40119.92 | 0 | 0 | 0 | 0 | 0 | 40119.92
2022100522 | 4 | 0.61756 | 49404.8 | 0.21246 | 7648.56 | 0 | 0 | 1 | 5000 | 7648.56 | 0 | 0 | 0 | 0 | 0 | 36756.24 | 0 | 0 | 0 | 0 | 0 | 36756.24
2022100523 | 4 | 0.57372 | 45897.6 | 0.20291 | 7304.76 | 0 | 0 | 1 | 5000 | 7304.76 | 0 | 0 | 0 | 0 | 0 | 33592.84 | 0 | 0 | 0 | 0 | 0 | 33592.84
2022100524 | 4 | 0.52611 | 42088.8 | 0.17146 | 6172.56 | 0 | 0 | 1 | 5000 | 6172.56 | 0 | 0 | 0 | 0 | 0 | 30916.24 | 0 | 0 | 0 | 0 | 0 | 30916.24
2022100601 | 5 | 0.49067 | 39253.6 | 0.15148 | 5453.28 | 0 | 0 | 1 | 5000 | 5453.28 | 0 | 0 | 0 | 0 | 0 | 28800.32 | 0 | 0 | 0 | 0 | 0 | 28800.32
2022100602 | 5 | 0.4675 | 37400 | 0.14313 | 5152.68 | 0 | 0 | 1 | 5000 | 5152.68 | 0 | 0 | 0 | 0 | 0 | 27247.32 | 0 | 0 | 0 | 0 | 0 | 27247.32
2022100603 | 5 | 0.45242 | 36193.6 | 0.12811 | 4611.96 | 0 | 0 | 1 | 5000 | 4611.96 | 0 | 0 | 0 | 0 | 0 | 26581.64 | 0 | 0 | 0 | 0 | 0 | 26581.64
2022100604 | 5 | 0.44549 | 35639.2 | 0.11332 | 4079.52 | 0 | 0 | 1 | 5000 | 4079.52 | 0 | 0 | 0 | 0 | 0 | 26559.68 | 0 | 0 | 0 | 0 | 0 | 26559.68
2022100605 | 5 | 0.44707 | 35765.6 | 0.09794 | 3525.84 | 0 | 0 | 1 | 5000 | 3525.84 | 0 | 0 | 0 | 0 | 0 | 27239.76 | 0 | 0 | 0 | 0 | 0 | 27239.76
2022100606 | 5 | 0.46232 | 36985.6 | 0.09191 | 3308.76 | 0 | 0 | 1 | 5000 | 3308.76 | 0 | 0 | 0 | 0 | 0 | 28676.84 | 0 | 0 | 0 | 0 | 0 | 28676.84
2022100607 | 5 | 0.492 | 39360 | 0.07275 | 2619 | 0 | 0 | 1 | 5000 | 2619 | 0 | 0 | 0 | 0 | 0 | 31741 | 0 | 0 | 0 | 0 | 0 | 31741
2022100608 | 5 | 0.50523 | 40418.4 | 0.05965 | 2147.4 | 0.00955 | 114.6 | 1 | 5000 | 2147.4 | 114.6 | 0 | 0 | 0 | 0 | 33156.4 | 0 | 0 | 0 | 0 | 0 | 33156.4
2022100609 | 5 | 0.51614 | 41291.2 | 0.05426 | 1953.36 | 0.21944 | 2633.28 | 1 | 5000 | 1953.36 | 2633.28 | 0 | 0 | 0 | 0 | 31704.56 | 0 | 0 | 0 | 0 | 0 | 31704.56
2022100610 | 5 | 0.53998 | 43198.4 | 0.03359 | 1209.24 | 0.52107 | 6252.84 | 1 | 5000 | 1209.24 | 6252.84 | 0 | 0 | 0 | 0 | 30736.32 | 0 | 0 | 0 | 0 | 0 | 30736.32
2022100611 | 5 | 0.57078 | 45662.4 | 0.02381 | 857.16 | 0.62742 | 7529.04 | 1 | 5000 | 857.16 | 7529.04 | 0 | 0 | 0 | 0 | 32276.2 | 0 | 0 | 0 | 0 | 0 | 32276.2
2022100612 | 5 | 0.60443 | 48354.4 | 0.0211 | 759.6 | 0.6374 | 7648.8 | 1 | 5000 | 759.6 | 7648.8 | 0 | 0 | 0 | 0 | 34946 | 0 | 0 | 0 | 0 | 0 | 34946
2022100613 | 5 | 0.64521 | 51616.8 | 0.02271 | 817.56 | 0.64842 | 7781.04 | 1 | 5000 | 817.56 | 7781.04 | 0 | 0 | 0 | 0 | 38018.2 | 0 | 0 | 0 | 0 | 0 | 38018.2
2022100614 | 5 | 0.68302 | 54641.6 | 0.02507 | 902.52 | 0.64781 | 7773.72 | 1 | 5000 | 902.52 | 7773.72 | 0 | 0 | 0 | 0 | 40965.36 | 0 | 0 | 0 | 0 | 0 | 40965.36
2022100615 | 5 | 0.71317 | 57053.6 | 0.02603 | 937.08 | 0.63662 | 7639.44 | 1 | 5000 | 937.08 | 7639.44 | 0 | 0 | 0 | 0 | 43477.08 | 0 | 0 | 0 | 0 | 0 | 43477.08
2022100616 | 5 | 0.73553 | 58842.4 | 0.0345 | 1242 | 0.60128 | 7215.36 | 1 | 5000 | 1242 | 7215.36 | 0 | 0 | 0 | 0 | 45385.04 | 0 | 0 | 0 | 0 | 0 | 45385.04
2022100617 | 5 | 0.74573 | 59658.4 | 0.04803 | 1729.08 | 0.50536 | 6064.32 | 1 | 5000 | 1729.08 | 6064.32 | 0 | 0 | 0 | 0 | 46865 | 0 | 0 | 0 | 0 | 0 | 46865
2022100618 | 5 | 0.73913 | 59130.4 | 0.06893 | 2481.48 | 0.38573 | 4628.76 | 1 | 5000 | 2481.48 | 4628.76 | 0 | 0 | 0 | 0 | 47020.16 | 0 | 0 | 0 | 0 | 0 | 47020.16
2022100619 | 5 | 0.70954 | 56763.2 | 0.0721 | 2595.6 | 0.1383 | 1659.6 | 1 | 5000 | 2595.6 | 1659.6 | 0 | 0 | 0 | 0 | 47508 | 0 | 0 | 0 | 0 | 0 | 47508
2022100620 | 5 | 0.68461 | 54768.8 | 0.09069 | 3264.84 | 0.00762 | 91.44 | 1 | 5000 | 3264.84 | 91.44 | 0 | 0 | 0 | 0 | 46412.52 | 0 | 0 | 0 | 0 | 0 | 46412.52
2022100621 | 5 | 0.66141 | 52912.8 | 0.1134 | 4082.4 | 0 | 0 | 1 | 5000 | 4082.4 | 0 | 0 | 0 | 0 | 0 | 43830.4 | 0 | 0 | 0 | 0 | 0 | 43830.4
2022100622 | 5 | 0.62503 | 50002.4 | 0.13512 | 4864.32 | 0 | 0 | 1 | 5000 | 4864.32 | 0 | 0 | 0 | 0 | 0 | 40138.08 | 0 | 0 | 0 | 0 | 0 | 40138.08
2022100623 | 5 | 0.58327 | 46661.6 | 0.1377 | 4957.2 | 0 | 0 | 1 | 5000 | 4957.2 | 0 | 0 | 0 | 0 | 0 | 36704.4 | 0 | 0 | 0 | 0 | 0 | 36704.4
2022100624 | 5 | 0.54118 | 43294.4 | 0.14375 | 5175 | 0 | 0 | 1 | 5000 | 5175 | 0 | 0 | 0 | 0 | 0 | 33119.4 | 0 | 0 | 0 | 0 | 0 | 33119.4
2022100701 | 6 | 0.50683 | 40546.4 | 0.13931 | 5015.16 | 0 | 0 | 1 | 5000 | 5015.16 | 0 | 0 | 0 | 0 | 0 | 30531.24 | 0 | 0 | 0 | 0 | 0 | 30531.24
2022100702 | 6 | 0.48152 | 38521.6 | 0.13404 | 4825.44 | 0 | 0 | 1 | 5000 | 4825.44 | 0 | 0 | 0 | 0 | 0 | 28696.16 | 0 | 0 | 0 | 0 | 0 | 28696.16
2022100703 | 6 | 0.46615 | 37292 | 0.13639 | 4910.04 | 0 | 0 | 1 | 5000 | 4910.04 | 0 | 0 | 0 | 0 | 0 | 27381.96 | 0 | 0 | 0 | 0 | 0 | 27381.96
2022100704 | 6 | 0.45698 | 36558.4 | 0.12403 | 4465.08 | 0 | 0 | 1 | 5000 | 4465.08 | 0 | 0 | 0 | 0 | 0 | 27093.32 | 0 | 0 | 0 | 0 | 0 | 27093.32
2022100705 | 6 | 0.4584 | 36672 | 0.104 | 3744 | 0 | 0 | 1 | 5000 | 3744 | 0 | 0 | 0 | 0 | 0 | 27928 | 0 | 0 | 0 | 0 | 0 | 27928
2022100706 | 6 | 0.47424 | 37939.2 | 0.09329 | 3358.44 | 0 | 0 | 1 | 5000 | 3358.44 | 0 | 0 | 0 | 0 | 0 | 29580.76 | 0 | 0 | 0 | 0 | 0 | 29580.76
2022100707 | 6 | 0.50057 | 40045.6 | 0.09134 | 3288.24 | 0 | 0 | 1 | 5000 | 3288.24 | 0 | 0 | 0 | 0 | 0 | 31757.36 | 0 | 0 | 0 | 0 | 0 | 31757.36
2022100708 | 6 | 0.51251 | 41000.8 | 0.09932 | 3575.52 | 0.00603 | 72.36 | 1 | 5000 | 3575.52 | 72.36 | 0 | 0 | 0 | 0 | 32352.92 | 0 | 0 | 0 | 0 | 0 | 32352.92
2022100709 | 6 | 0.5221 | 41768 | 0.1026 | 3693.6 | 0.11499 | 1379.88 | 1 | 5000 | 3693.6 | 1379.88 | 0 | 0 | 0 | 0 | 31694.52 | 0 | 0 | 0 | 0 | 0 | 31694.52
2022100710 | 6 | 0.54691 | 43752.8 | 0.0798 | 2872.8 | 0.31849 | 3821.88 | 1 | 5000 | 2872.8 | 3821.88 | 0 | 0 | 0 | 0 | 32058.12 | 0 | 0 | 0 | 0 | 0 | 32058.12
2022100711 | 6 | 0.57119 | 45695.2 | 0.08437 | 3037.32 | 0.44655 | 5358.6 | 1 | 5000 | 3037.32 | 5358.6 | 0 | 0 | 0 | 0 | 32299.28 | 0 | 0 | 0 | 0 | 0 | 32299.28
2022100712 | 6 | 0.596 | 47680 | 0.09248 | 3329.28 | 0.56309 | 6757.08 | 1 | 5000 | 3329.28 | 6757.08 | 0 | 0 | 0 | 0 | 32593.64 | 0 | 0 | 0 | 0 | 0 | 32593.64
2022100713 | 6 | 0.62271 | 49816.8 | 0.10583 | 3809.88 | 0.57128 | 6855.36 | 1 | 5000 | 3809.88 | 6855.36 | 0 | 0 | 0 | 0 | 34151.56 | 0 | 0 | 0 | 0 | 0 | 34151.56
2022100714 | 6 | 0.64799 | 51839.2 | 0.12756 | 4592.16 | 0.54443 | 6533.16 | 1 | 5000 | 4592.16 | 6533.16 | 0 | 0 | 0 | 0 | 35713.88 | 0 | 0 | 0 | 0 | 0 | 35713.88
2022100715 | 6 | 0.66644 | 53315.2 | 0.15474 | 5570.64 | 0.46951 | 5634.12 | 1 | 5000 | 5570.64 | 5634.12 | 0 | 0 | 0 | 0 | 37110.44 | 0 | 0 | 0 | 0 | 0 | 37110.44
2022100716 | 6 | 0.6787 | 54296 | 0.19211 | 6915.96 | 0.36073 | 4328.76 | 1 | 5000 | 6915.96 | 4328.76 | 0 | 0 | 0 | 0 | 38051.28 | 0 | 0 | 0 | 0 | 0 | 38051.28
2022100717 | 6 | 0.68237 | 54589.6 | 0.24832 | 8939.52 | 0.29918 | 3590.16 | 1 | 5000 | 8939.52 | 3590.16 | 0 | 0 | 0 | 0 | 37059.92 | 0 | 0 | 0 | 0 | 0 | 37059.92
2022100718 | 6 | 0.67145 | 53716 | 0.25812 | 9292.32 | 0.21291 | 2554.92 | 1 | 5000 | 9292.32 | 2554.92 | 0 | 0 | 0 | 0 | 36868.76 | 0 | 0 | 0 | 0 | 0 | 36868.76
2022100719 | 6 | 0.64892 | 51913.6 | 0.27246 | 9808.56 | 0.06267 | 752.04 | 1 | 5000 | 9808.56 | 752.04 | 0 | 0 | 0 | 0 | 36353 | 0 | 0 | 0 | 0 | 0 | 36353
2022100720 | 6 | 0.63556 | 50844.8 | 0.27273 | 9818.28 | 0.0016 | 19.2 | 1 | 5000 | 9818.28 | 19.2 | 0 | 0 | 0 | 0 | 36007.32 | 0 | 0 | 0 | 0 | 0 | 36007.32
2022100721 | 6 | 0.61721 | 49376.8 | 0.28104 | 10117.44 | 0 | 0 | 1 | 5000 | 10117.44 | 0 | 0 | 0 | 0 | 0 | 34259.36 | 0 | 0 | 0 | 0 | 0 | 34259.36
2022100722 | 6 | 0.59424 | 47539.2 | 0.25904 | 9325.44 | 0 | 0 | 1 | 5000 | 9325.44 | 0 | 0 | 0 | 0 | 0 | 33213.76 | 0 | 0 | 0 | 0 | 0 | 33213.76
2022100723 | 6 | 0.56349 | 45079.2 | 0.23286 | 8382.96 | 0 | 0 | 1 | 5000 | 8382.96 | 0 | 0 | 0 | 0 | 0 | 31696.24 | 0 | 0 | 0 | 0 | 0 | 31696.24
2022100724 | 6 | 0.5319 | 42552 | 0.214 | 7704 | 0 | 0 | 1 | 5000 | 7704 | 0 | 0 | 0 | 0 | 0 | 29848 | 0 | 0 | 0 | 0 | 0 | 29848
2022100801 | 7 | 0.50065 | 40052 | 0.19278 | 6940.08 | 0 | 0 | 1 | 5000 | 6940.08 | 0 | 0 | 0 | 0 | 0 | 28111.92 | 0 | 0 | 0 | 0 | 0 | 28111.92
2022100802 | 7 | 0.47839 | 38271.2 | 0.1861 | 6699.6 | 0 | 0 | 1 | 5000 | 6699.6 | 0 | 0 | 0 | 0 | 0 | 26571.6 | 0 | 0 | 0 | 0 | 0 | 26571.6
2022100803 | 7 | 0.46007 | 36805.6 | 0.19282 | 6941.52 | 0 | 0 | 1 | 5000 | 6941.52 | 0 | 0 | 0 | 0 | 0 | 24864.08 | 0 | 0 | 0 | 0 | 0 | 24864.08
2022100804 | 7 | 0.44691 | 35752.8 | 0.19973 | 7190.28 | 0 | 0 | 1 | 5000 | 7190.28 | 0 | 0 | 0 | 0 | 0 | 23562.52 | 0 | 0 | 0 | 0 | 0 | 23562.52
2022100805 | 7 | 0.44339 | 35471.2 | 0.2196 | 7905.6 | 0 | 0 | 1 | 5000 | 7905.6 | 0 | 0 | 0 | 0 | 0 | 22565.6 | 0 | 0 | 0 | 0 | 0 | 22565.6
2022100806 | 7 | 0.44576 | 35660.8 | 0.2316 | 8337.6 | 0 | 0 | 1 | 5000 | 8337.6 | 0 | 0 | 0 | 0 | 0 | 22323.2 | 0 | 0 | 0 | 0 | 0 | 22323.2
2022100807 | 7 | 0.45337 | 36269.6 | 0.23269 | 8376.84 | 0 | 0 | 1 | 5000 | 8376.84 | 0 | 0 | 0 | 0 | 0 | 22892.76 | 0 | 0 | 0 | 0 | 0 | 22892.76
2022100808 | 7 | 0.46271 | 37016.8 | 0.24071 | 8665.56 | 0.00419 | 50.28 | 1 | 5000 | 8665.56 | 50.28 | 0 | 0 | 0 | 0 | 23300.96 | 0 | 0 | 0 | 0 | 0 | 23300.96
2022100809 | 7 | 0.47604 | 38083.2 | 0.22222 | 7999.92 | 0.15011 | 1801.32 | 1 | 5000 | 7999.92 | 1801.32 | 0 | 0 | 0 | 0 | 23281.96 | 0 | 0 | 0 | 0 | 0 | 23281.96
2022100810 | 7 | 0.4991 | 39928 | 0.17627 | 6345.72 | 0.4227 | 5072.4 | 1 | 5000 | 6345.72 | 5072.4 | 0 | 0 | 0 | 0 | 23509.88 | 0 | 0 | 0 | 0 | 0 | 23509.88
2022100811 | 7 | 0.52883 | 42306.4 | 0.14357 | 5168.52 | 0.49482 | 5937.84 | 1 | 5000 | 5168.52 | 5937.84 | 0 | 0 | 0 | 0 | 26200.04 | 0 | 0 | 0 | 0 | 0 | 26200.04
2022100812 | 7 | 0.5554 | 44432 | 0.11512 | 4144.32 | 0.55385 | 6646.2 | 1 | 5000 | 4144.32 | 6646.2 | 0 | 0 | 0 | 0 | 28641.48 | 0 | 0 | 0 | 0 | 0 | 28641.48
2022100813 | 7 | 0.58339 | 46671.2 | 0.10238 | 3685.68 | 0.59078 | 7089.36 | 1 | 5000 | 3685.68 | 7089.36 | 0 | 0 | 0 | 0 | 30896.16 | 0 | 0 | 0 | 0 | 0 | 30896.16
2022100814 | 7 | 0.61241 | 48992.8 | 0.0989 | 3560.4 | 0.57295 | 6875.4 | 1 | 5000 | 3560.4 | 6875.4 | 0 | 0 | 0 | 0 | 33557 | 0 | 0 | 0 | 0 | 0 | 33557
2022100815 | 7 | 0.6367 | 50936 | 0.09148 | 3293.28 | 0.55754 | 6690.48 | 1 | 5000 | 3293.28 | 6690.48 | 0 | 0 | 0 | 0 | 35952.24 | 0 | 0 | 0 | 0 | 0 | 35952.24
2022100816 | 7 | 0.65577 | 52461.6 | 0.08893 | 3201.48 | 0.50867 | 6104.04 | 1 | 5000 | 3201.48 | 6104.04 | 0 | 0 | 0 | 0 | 38156.08 | 0 | 0 | 0 | 0 | 0 | 38156.08
2022100817 | 7 | 0.66295 | 53036 | 0.09881 | 3557.16 | 0.36575 | 4389 | 1 | 5000 | 3557.16 | 4389 | 0 | 0 | 0 | 0 | 40089.84 | 0 | 0 | 0 | 0 | 0 | 40089.84
2022100818 | 7 | 0.6569 | 52552 | 0.1135 | 4086 | 0.23866 | 2863.92 | 1 | 5000 | 4086 | 2863.92 | 0 | 0 | 0 | 0 | 40602.08 | 0 | 0 | 0 | 0 | 0 | 40602.08
2022100819 | 7 | 0.63448 | 50758.4 | 0.12842 | 4623.12 | 0.06982 | 837.84 | 1 | 5000 | 4623.12 | 837.84 | 0 | 0 | 0 | 0 | 40297.44 | 0 | 0 | 0 | 0 | 0 | 40297.44
2022100820 | 7 | 0.62037 | 49629.6 | 0.14577 | 5247.72 | 0.00071 | 8.52 | 1 | 5000 | 5247.72 | 8.52 | 0 | 0 | 0 | 0 | 39373.36 | 0 | 0 | 0 | 0 | 0 | 39373.36
2022100821 | 7 | 0.59899 | 47919.2 | 0.16904 | 6085.44 | 0.00017 | 2.04 | 1 | 5000 | 6085.44 | 2.04 | 0 | 0 | 0 | 0 | 36831.72 | 0 | 0 | 0 | 0 | 0 | 36831.72
2022100822 | 7 | 0.57174 | 45739.2 | 0.17286 | 6222.96 | 0.00017 | 2.04 | 1 | 5000 | 6222.96 | 2.04 | 0 | 0 | 0 | 0 | 34514.2 | 0 | 0 | 0 | 0 | 0 | 34514.2
2022100823 | 7 | 0.54184 | 43347.2 | 0.16515 | 5945.4 | 0.00011 | 1.32 | 1 | 5000 | 5945.4 | 1.32 | 0 | 0 | 0 | 0 | 32400.48 | 0 | 0 | 0 | 0 | 0 | 32400.48
2022100824 | 7 | 0.51231 | 40984.8 | 0.1395 | 5022 | 0 | 0 | 1 | 5000 | 5022 | 0 | 0 | 0 | 0 | 0 | 30962.8 | 0 | 0 | 0 | 0 | 0 | 30962.8
2022100901 | 1 | 0.48398 | 38718.4 | 0.12816 | 4613.76 | 0 | 0 | 1 | 5000 | 4613.76 | 0 | 0 | 0 | 0 | 0 | 29104.64 | 0 | 0 | 0 | 0 | 0 | 29104.64
2022100902 | 1 | 0.4614 | 36912 | 0.10773 | 3878.28 | 0 | 0 | 1 | 5000 | 3878.28 | 0 | 0 | 0 | 0 | 0 | 28033.72 | 0 | 0 | 0 | 0 | 0 | 28033.72
2022100903 | 1 | 0.4468 | 35744 | 0.09384 | 3378.24 | 0 | 0 | 1 | 5000 | 3378.24 | 0 | 0 | 0 | 0 | 0 | 27365.76 | 0 | 0 | 0 | 0 | 0 | 27365.76
2022100904 | 1 | 0.43541 | 34832.8 | 0.0885 | 3186 | 0 | 0 | 1 | 5000 | 3186 | 0 | 0 | 0 | 0 | 0 | 26646.8 | 0 | 0 | 0 | 0 | 0 | 26646.8
2022100905 | 1 | 0.42774 | 34219.2 | 0.08284 | 2982.24 | 0 | 0 | 1 | 5000 | 2982.24 | 0 | 0 | 0 | 0 | 0 | 26236.96 | 0 | 0 | 0 | 0 | 0 | 26236.96
2022100906 | 1 | 0.42846 | 34276.8 | 0.08342 | 3003.12 | 0 | 0 | 1 | 5000 | 3003.12 | 0 | 0 | 0 | 0 | 0 | 26273.68 | 0 | 0 | 0 | 0 | 0 | 26273.68
2022100907 | 1 | 0.43247 | 34597.6 | 0.08081 | 2909.16 | 0 | 0 | 1 | 5000 | 2909.16 | 0 | 0 | 0 | 0 | 0 | 26688.44 | 0 | 0 | 0 | 0 | 0 | 26688.44
2022100908 | 1 | 0.4372 | 34976 | 0.09184 | 3306.24 | 0.00471 | 56.52 | 1 | 5000 | 3306.24 | 56.52 | 0 | 0 | 0 | 0 | 26613.24 | 0 | 0 | 0 | 0 | 0 | 26613.24
2022100909 | 1 | 0.45686 | 36548.8 | 0.0883 | 3178.8 | 0.13712 | 1645.44 | 1 | 5000 | 3178.8 | 1645.44 | 0 | 0 | 0 | 0 | 26724.56 | 0 | 0 | 0 | 0 | 0 | 26724.56
2022100910 | 1 | 0.48463 | 38770.4 | 0.0545 | 1962 | 0.34562 | 4147.44 | 1 | 5000 | 1962 | 4147.44 | 0 | 0 | 0 | 0 | 27660.96 | 0 | 0 | 0 | 0 | 0 | 27660.96
2022100911 | 1 | 0.51284 | 41027.2 | 0.05108 | 1838.88 | 0.47812 | 5737.44 | 1 | 5000 | 1838.88 | 5737.44 | 0 | 0 | 0 | 0 | 28450.88 | 0 | 0 | 0 | 0 | 0 | 28450.88
2022100912 | 1 | 0.54367 | 43493.6 | 0.08214 | 2957.04 | 0.529 | 6348 | 1 | 5000 | 2957.04 | 6348 | 0 | 0 | 0 | 0 | 29188.56 | 0 | 0 | 0 | 0 | 0 | 29188.56
2022100913 | 1 | 0.57719 | 46175.2 | 0.11112 | 4000.32 | 0.54377 | 6525.24 | 1 | 5000 | 4000.32 | 6525.24 | 0 | 0 | 0 | 0 | 30649.64 | 0 | 0 | 0 | 0 | 0 | 30649.64
2022100914 | 1 | 0.60804 | 48643.2 | 0.12071 | 4345.56 | 0.54135 | 6496.2 | 1 | 5000 | 4345.56 | 6496.2 | 0 | 0 | 0 | 0 | 32801.44 | 0 | 0 | 0 | 0 | 0 | 32801.44
2022100915 | 1 | 0.63605 | 50884 | 0.119 | 4284 | 0.52965 | 6355.8 | 1 | 5000 | 4284 | 6355.8 | 0 | 0 | 0 | 0 | 35244.2 | 0 | 0 | 0 | 0 | 0 | 35244.2
2022100916 | 1 | 0.65736 | 52588.8 | 0.11399 | 4103.64 | 0.52073 | 6248.76 | 1 | 5000 | 4103.64 | 6248.76 | 0 | 0 | 0 | 0 | 37236.4 | 0 | 0 | 0 | 0 | 0 | 37236.4
2022100917 | 1 | 0.66907 | 53525.6 | 0.12642 | 4551.12 | 0.37539 | 4504.68 | 1 | 5000 | 4551.12 | 4504.68 | 0 | 0 | 0 | 0 | 39469.8 | 0 | 0 | 0 | 0 | 0 | 39469.8
2022100918 | 1 | 0.66791 | 53432.8 | 0.14348 | 5165.28 | 0.24798 | 2975.76 | 1 | 5000 | 5165.28 | 2975.76 | 0 | 0 | 0 | 0 | 40291.76 | 0 | 0 | 0 | 0 | 0 | 40291.76
2022100919 | 1 | 0.65116 | 52092.8 | 0.15525 | 5589 | 0.08633 | 1035.96 | 1 | 5000 | 5589 | 1035.96 | 0 | 0 | 0 | 0 | 40467.84 | 0 | 0 | 0 | 0 | 0 | 40467.84
2022100920 | 1 | 0.63811 | 51048.8 | 0.15174 | 5462.64 | 0.00139 | 16.68 | 1 | 5000 | 5462.64 | 16.68 | 0 | 0 | 0 | 0 | 40569.48 | 0 | 0 | 0 | 0 | 0 | 40569.48
2022100921 | 1 | 0.61821 | 49456.8 | 0.19183 | 6905.88 | 0 | 0 | 1 | 5000 | 6905.88 | 0 | 0 | 0 | 0 | 0 | 37550.92 | 0 | 0 | 0 | 0 | 0 | 37550.92
2022100922 | 1 | 0.58933 | 47146.4 | 0.22069 | 7944.84 | 0 | 0 | 1 | 5000 | 7944.84 | 0 | 0 | 0 | 0 | 0 | 34201.56 | 0 | 0 | 0 | 0 | 0 | 34201.56
2022100923 | 1 | 0.55466 | 44372.8 | 0.23739 | 8546.04 | 0 | 0 | 1 | 5000 | 8546.04 | 0 | 0 | 0 | 0 | 0 | 30826.76 | 0 | 0 | 0 | 0 | 0 | 30826.76
2022100924 | 1 | 0.51696 | 41356.8 | 0.2332 | 8395.2 | 0 | 0 | 1 | 5000 | 8395.2 | 0 | 0 | 0 | 0 | 0 | 27961.6 | 0 | 0 | 0 | 0 | 0 | 27961.6
2022101001 | 2 | 0.48535 | 38828 | 0.21702 | 7812.72 | 0 | 0 | 1 | 5000 | 7812.72 | 0 | 0 | 0 | 0 | 0 | 26015.28 | 0 | 0 | 0 | 0 | 0 | 26015.28
2022101002 | 2 | 0.46376 | 37100.8 | 0.23365 | 8411.4 | 0 | 0 | 1 | 5000 | 8411.4 | 0 | 0 | 0 | 0 | 0 | 23689.4 | 0 | 0 | 0 | 0 | 0 | 23689.4
2022101003 | 2 | 0.45181 | 36144.8 | 0.23587 | 8491.32 | 0 | 0 | 1 | 5000 | 8491.32 | 0 | 0 | 0 | 0 | 0 | 22653.48 | 0 | 0 | 0 | 0 | 0 | 22653.48
2022101004 | 2 | 0.44367 | 35493.6 | 0.23173 | 8342.28 | 0 | 0 | 1 | 5000 | 8342.28 | 0 | 0 | 0 | 0 | 0 | 22151.32 | 0 | 0 | 0 | 0 | 0 | 22151.32
2022101005 | 2 | 0.4442 | 35536 | 0.21419 | 7710.84 | 0 | 0 | 1 | 5000 | 7710.84 | 0 | 0 | 0 | 0 | 0 | 22825.16 | 0 | 0 | 0 | 0 | 0 | 22825.16
2022101006 | 2 | 0.45913 | 36730.4 | 0.21624 | 7784.64 | 0 | 0 | 1 | 5000 | 7784.64 | 0 | 0 | 0 | 0 | 0 | 23945.76 | 0 | 0 | 0 | 0 | 0 | 23945.76
2022101007 | 2 | 0.48021 | 38416.8 | 0.20674 | 7442.64 | 0 | 0 | 1 | 5000 | 7442.64 | 0 | 0 | 0 | 0 | 0 | 25974.16 | 0 | 0 | 0 | 0 | 0 | 25974.16
2022101008 | 2 | 0.49472 | 39577.6 | 0.19241 | 6926.76 | 0.00623 | 74.76 | 1 | 5000 | 6926.76 | 74.76 | 0 | 0 | 0 | 0 | 27576.08 | 0 | 0 | 0 | 0 | 0 | 27576.08
2022101009 | 2 | 0.5092 | 40736 | 0.18183 | 6545.88 | 0.13762 | 1651.44 | 1 | 5000 | 6545.88 | 1651.44 | 0 | 0 | 0 | 0 | 27538.68 | 0 | 0 | 0 | 0 | 0 | 27538.68
2022101010 | 2 | 0.5383 | 43064 | 0.1336 | 4809.6 | 0.3192 | 3830.4 | 1 | 5000 | 4809.6 | 3830.4 | 0 | 0 | 0 | 0 | 29424 | 0 | 0 | 0 | 0 | 0 | 29424
2022101011 | 2 | 0.57172 | 45737.6 | 0.16699 | 6011.64 | 0.45045 | 5405.4 | 1 | 5000 | 6011.64 | 5405.4 | 0 | 0 | 0 | 0 | 29320.56 | 0 | 0 | 0 | 0 | 0 | 29320.56
2022101012 | 2 | 0.60529 | 48423.2 | 0.19427 | 6993.72 | 0.51026 | 6123.12 | 1 | 5000 | 6993.72 | 6123.12 | 0 | 0 | 0 | 0 | 30306.36 | 0 | 0 | 0 | 0 | 0 | 30306.36
2022101013 | 2 | 0.63816 | 51052.8 | 0.19957 | 7184.52 | 0.56357 | 6762.84 | 1 | 5000 | 7184.52 | 6762.84 | 0 | 0 | 0 | 0 | 32105.44 | 0 | 0 | 0 | 0 | 0 | 32105.44
2022101014 | 2 | 0.67132 | 53705.6 | 0.21275 | 7659 | 0.57415 | 6889.8 | 1 | 5000 | 7659 | 6889.8 | 0 | 0 | 0 | 0 | 34156.8 | 0 | 0 | 0 | 0 | 0 | 34156.8
2022101015 | 2 | 0.69916 | 55932.8 | 0.19563 | 7042.68 | 0.55559 | 6667.08 | 1 | 5000 | 7042.68 | 6667.08 | 0 | 0 | 0 | 0 | 37223.04 | 0 | 0 | 0 | 0 | 0 | 37223.04
2022101016 | 2 | 0.71774 | 57419.2 | 0.21544 | 7755.84 | 0.54055 | 6486.6 | 1 | 5000 | 7755.84 | 6486.6 | 0 | 0 | 0 | 0 | 38176.76 | 0 | 0 | 0 | 0 | 0 | 38176.76
2022101017 | 2 | 0.72394 | 57915.2 | 0.24203 | 8713.08 | 0.51386 | 6166.32 | 1 | 5000 | 8713.08 | 6166.32 | 0 | 0 | 0 | 0 | 38035.8 | 0 | 0 | 0 | 0 | 0 | 38035.8
2022101018 | 2 | 0.714 | 57120 | 0.24235 | 8724.6 | 0.33158 | 3978.96 | 1 | 5000 | 8724.6 | 3978.96 | 0 | 0 | 0 | 0 | 39416.44 | 0 | 0 | 0 | 0 | 0 | 39416.44
2022101019 | 2 | 0.68813 | 55050.4 | 0.25504 | 9181.44 | 0.08543 | 1025.16 | 1 | 5000 | 9181.44 | 1025.16 | 0 | 0 | 0 | 0 | 39843.8 | 0 | 0 | 0 | 0 | 0 | 39843.8
2022101020 | 2 | 0.67255 | 53804 | 0.25822 | 9295.92 | 0.00357 | 42.84 | 1 | 5000 | 9295.92 | 42.84 | 0 | 0 | 0 | 0 | 39465.24 | 0 | 0 | 0 | 0 | 0 | 39465.24
2022101021 | 2 | 0.6508 | 52064 | 0.27776 | 9999.36 | 0 | 0 | 1 | 5000 | 9999.36 | 0 | 0 | 0 | 0 | 0 | 37064.64 | 0 | 0 | 0 | 0 | 0 | 37064.64
2022101022 | 2 | 0.61825 | 49460 | 0.2949 | 10616.4 | 0 | 0 | 1 | 5000 | 10616.4 | 0 | 0 | 0 | 0 | 0 | 33843.6 | 0 | 0 | 0 | 0 | 0 | 33843.6
2022101023 | 2 | 0.57642 | 46113.6 | 0.32539 | 11714.04 | 0 | 0 | 1 | 5000 | 11714.04 | 0 | 0 | 0 | 0 | 0 | 29399.56 | 0 | 0 | 0 | 0 | 0 | 29399.56
2022101024 | 2 | 0.53792 | 43033.6 | 0.3375 | 12150 | 0 | 0 | 1 | 5000 | 12150 | 0 | 0 | 0 | 0 | 0 | 25883.6 | 0 | 0 | 0 | 0 | 0 | 25883.6
2022101101 | 3 | 0.5026 | 40208 | 0.34033 | 12251.88 | 0 | 0 | 1 | 5000 | 12251.88 | 0 | 0 | 0 | 0 | 0 | 22956.12 | 0 | 0 | 0 | 0 | 0 | 22956.12
2022101102 | 3 | 0.48101 | 38480.8 | 0.32961 | 11865.96 | 0 | 0 | 1 | 5000 | 11865.96 | 0 | 0 | 0 | 0 | 0 | 21614.84 | 0 | 0 | 0 | 0 | 0 | 21614.84
2022101103 | 3 | 0.46299 | 37039.2 | 0.31612 | 11380.32 | 0 | 0 | 1 | 5000 | 11380.32 | 0 | 0 | 0 | 0 | 0 | 20658.88 | 0 | 0 | 0 | 0 | 0 | 20658.88
2022101104 | 3 | 0.45371 | 36296.8 | 0.3067 | 11041.2 | 0 | 0 | 1 | 5000 | 11041.2 | 0 | 0 | 0 | 0 | 0 | 20255.6 | 0 | 0 | 0 | 0 | 0 | 20255.6
2022101105 | 3 | 0.45386 | 36308.8 | 0.31334 | 11280.24 | 0 | 0 | 1 | 5000 | 11280.24 | 0 | 0 | 0 | 0 | 0 | 20028.56 | 0 | 0 | 0 | 0 | 0 | 20028.56
2022101106 | 3 | 0.47099 | 37679.2 | 0.3321 | 11955.6 | 0 | 0 | 1 | 5000 | 11955.6 | 0 | 0 | 0 | 0 | 0 | 20723.6 | 0 | 0 | 0 | 0 | 0 | 20723.6
2022101107 | 3 | 0.50168 | 40134.4 | 0.37631 | 13547.16 | 0 | 0 | 1 | 5000 | 13547.16 | 0 | 0 | 0 | 0 | 0 | 21587.24 | 0 | 0 | 0 | 0 | 0 | 21587.24
2022101108 | 3 | 0.51585 | 41268 | 0.3895 | 14022 | 0.00533 | 63.96 | 1 | 5000 | 14022 | 63.96 | 0 | 0 | 0 | 0 | 22182.04 | 0 | 0 | 0 | 0 | 0 | 22182.04
2022101109 | 3 | 0.52479 | 41983.2 | 0.36146 | 13012.56 | 0.17404 | 2088.48 | 1 | 5000 | 13012.56 | 2088.48 | 0 | 0 | 0 | 0 | 21882.16 | 0 | 0 | 0 | 0 | 0 | 21882.16
2022101110 | 3 | 0.54959 | 43967.2 | 0.3106 | 11181.6 | 0.46783 | 5613.96 | 1 | 5000 | 11181.6 | 5613.96 | 0 | 0 | 0 | 0 | 22171.64 | 0 | 0 | 0 | 0 | 0 | 22171.64
2022101111 | 3 | 0.57966 | 46372.8 | 0.36429 | 13114.44 | 0.59212 | 7105.44 | 1 | 5000 | 13114.44 | 7105.44 | 0 | 0 | 0 | 0 | 21152.92 | 0 | 0 | 0 | 0 | 0 | 21152.92
2022101112 | 3 | 0.61385 | 49108 | 0.4179 | 15044.4 | 0.56205 | 6744.6 | 1 | 5000 | 15044.4 | 6744.6 | 0 | 0 | 0 | 0 | 22319 | 0 | 0 | 0 | 0 | 0 | 22319
2022101113 | 3 | 0.64161 | 51328.8 | 0.42821 | 15415.56 | 0.54957 | 6594.84 | 1 | 5000 | 15415.56 | 6594.84 | 0 | 0 | 0 | 0 | 24318.4 | 0 | 0 | 0 | 0 | 0 | 24318.4
2022101114 | 3 | 0.6631 | 53048 | 0.43813 | 15772.68 | 0.53159 | 6379.08 | 1 | 5000 | 15772.68 | 6379.08 | 0 | 0 | 0 | 0 | 25896.24 | 0 | 0 | 0 | 0 | 0 | 25896.24
2022101115 | 3 | 0.68082 | 54465.6 | 0.43559 | 15681.24 | 0.55015 | 6601.8 | 1 | 5000 | 15681.24 | 6601.8 | 0 | 0 | 0 | 0 | 27182.56 | 0 | 0 | 0 | 0 | 0 | 27182.56
2022101116 | 3 | 0.7002 | 56016 | 0.42538 | 15313.68 | 0.58473 | 7016.76 | 1 | 5000 | 15313.68 | 7016.76 | 0 | 0 | 0 | 0 | 28685.56 | 0 | 0 | 0 | 0 | 0 | 28685.56
2022101117 | 3 | 0.71322 | 57057.6 | 0.42488 | 15295.68 | 0.57331 | 6879.72 | 1 | 5000 | 15295.68 | 6879.72 | 0 | 0 | 0 | 0 | 29882.2 | 0 | 0 | 0 | 0 | 0 | 29882.2
2022101118 | 3 | 0.71105 | 56884 | 0.42376 | 15255.36 | 0.49 | 5880 | 1 | 5000 | 15255.36 | 5880 | 0 | 0 | 0 | 0 | 30748.64 | 0 | 0 | 0 | 0 | 0 | 30748.64
2022101119 | 3 | 0.6919 | 55352 | 0.40647 | 14632.92 | 0.18278 | 2193.36 | 1 | 5000 | 14632.92 | 2193.36 | 0 | 0 | 0 | 0 | 33525.72 | 0 | 0 | 0 | 0 | 0 | 33525.72
2022101120 | 3 | 0.67974 | 54379.2 | 0.39332 | 14159.52 | 0.00283 | 33.96 | 1 | 5000 | 14159.52 | 33.96 | 0 | 0 | 0 | 0 | 35185.72 | 0 | 0 | 0 | 0 | 0 | 35185.72
2022101121 | 3 | 0.6665 | 53320 | 0.47885 | 17238.6 | 0 | 0 | 1 | 5000 | 17238.6 | 0 | 0 | 0 | 0 | 0 | 31081.4 | 0 | 0 | 0 | 0 | 0 | 31081.4
2022101122 | 3 | 0.64239 | 51391.2 | 0.53983 | 19433.88 | 0 | 0 | 1 | 5000 | 19433.88 | 0 | 0 | 0 | 0 | 0 | 26957.32 | 0 | 0 | 0 | 0 | 0 | 26957.32
2022101123 | 3 | 0.6064 | 48512 | 0.56321 | 20275.56 | 0 | 0 | 1 | 5000 | 20275.56 | 0 | 0 | 0 | 0 | 0 | 23236.44 | 0 | 0 | 0 | 0 | 0 | 23236.44
2022101124 | 3 | 0.5647 | 45176 | 0.55387 | 19939.32 | 0 | 0 | 1 | 5000 | 19939.32 | 0 | 0 | 0 | 0 | 0 | 20236.68 | 0 | 0 | 0 | 0 | 0 | 20236.68
2022101201 | 4 | 0.53113 | 42490.4 | 0.53835 | 19380.6 | 0 | 0 | 1 | 5000 | 19380.6 | 0 | 0 | 0 | 0 | 0 | 18109.8 | 0 | 0 | 0 | 0 | 0 | 18109.8
2022101202 | 4 | 0.50974 | 40779.2 | 0.5178 | 18640.8 | 0 | 0 | 1 | 5000 | 18640.8 | 0 | 0 | 0 | 0 | 0 | 17138.4 | 0 | 0 | 0 | 0 | 0 | 17138.4
2022101203 | 4 | 0.49742 | 39793.6 | 0.49791 | 17924.76 | 0 | 0 | 1 | 5000 | 17924.76 | 0 | 0 | 0 | 0 | 0 | 16868.84 | 0 | 0 | 0 | 0 | 0 | 16868.84
2022101204 | 4 | 0.48947 | 39157.6 | 0.48758 | 17552.88 | 0 | 0 | 1 | 5000 | 17552.88 | 0 | 0 | 0 | 0 | 0 | 16604.72 | 0 | 0 | 0 | 0 | 0 | 16604.72
2022101205 | 4 | 0.49116 | 39292.8 | 0.4837 | 17413.2 | 0 | 0 | 1 | 5000 | 17413.2 | 0 | 0 | 0 | 0 | 0 | 16879.6 | 0 | 0 | 0 | 0 | 0 | 16879.6
2022101206 | 4 | 0.50864 | 40691.2 | 0.48382 | 17417.52 | 0 | 0 | 1 | 5000 | 17417.52 | 0 | 0 | 0 | 0 | 0 | 18273.68 | 0 | 0 | 0 | 0 | 0 | 18273.68
2022101207 | 4 | 0.5382 | 43056 | 0.47705 | 17173.8 | 0 | 0 | 1 | 5000 | 17173.8 | 0 | 0 | 0 | 0 | 0 | 20882.2 | 0 | 0 | 0 | 0 | 0 | 20882.2
2022101208 | 4 | 0.55477 | 44381.6 | 0.45449 | 16361.64 | 0.00438 | 52.56 | 1 | 5000 | 16361.64 | 52.56 | 0 | 0 | 0 | 0 | 22967.4 | 0 | 0 | 0 | 0 | 0 | 22967.4
2022101209 | 4 | 0.56485 | 45188 | 0.3927 | 14137.2 | 0.22252 | 2670.24 | 1 | 5000 | 14137.2 | 2670.24 | 0 | 0 | 0 | 0 | 23380.56 | 0 | 0 | 0 | 0 | 0 | 23380.56
2022101210 | 4 | 0.59706 | 47764.8 | 0.30811 | 11091.96 | 0.61354 | 7362.48 | 1 | 5000 | 11091.96 | 7362.48 | 0 | 0 | 0 | 0 | 24310.36 | 0 | 0 | 0 | 0 | 0 | 24310.36
2022101211 | 4 | 0.63454 | 50763.2 | 0.29676 | 10683.36 | 0.71873 | 8624.76 | 1 | 5000 | 10683.36 | 8624.76 | 0 | 0 | 0 | 0 | 26455.08 | 0 | 0 | 0 | 0 | 0 | 26455.08
2022101212 | 4 | 0.6757 | 54056 | 0.24942 | 8979.12 | 0.72842 | 8741.04 | 1 | 5000 | 8979.12 | 8741.04 | 0 | 0 | 0 | 0 | 31335.84 | 0 | 0 | 0 | 0 | 0 | 31335.84
2022101213 | 4 | 0.71788 | 57430.4 | 0.20561 | 7401.96 | 0.73065 | 8767.8 | 1 | 5000 | 7401.96 | 8767.8 | 0 | 0 | 0 | 0 | 36260.64 | 0 | 0 | 0 | 0 | 0 | 36260.64
2022101214 | 4 | 0.7612 | 60896 | 0.16682 | 6005.52 | 0.71301 | 8556.12 | 1 | 5000 | 6005.52 | 8556.12 | 0 | 0 | 0 | 0 | 41334.36 | 0 | 0 | 0 | 0 | 0 | 41334.36
2022101215 | 4 | 0.79579 | 63663.2 | 0.15318 | 5514.48 | 0.70943 | 8513.16 | 1 | 5000 | 5514.48 | 8513.16 | 0 | 0 | 0 | 0 | 44635.56 | 0 | 0 | 0 | 0 | 0 | 44635.56
2022101216 | 4 | 0.81799 | 65439.2 | 0.15181 | 5465.16 | 0.71392 | 8567.04 | 1 | 5000 | 5465.16 | 8567.04 | 0 | 0 | 0 | 0 | 46407 | 0 | 0 | 0 | 0 | 0 | 46407
2022101217 | 4 | 0.82753 | 66202.4 | 0.148 | 5328 | 0.69397 | 8327.64 | 1 | 5000 | 5328 | 8327.64 | 0 | 0 | 0 | 0 | 47546.76 | 0 | 0 | 0 | 0 | 0 | 47546.76
2022101218 | 4 | 0.8166 | 65328 | 0.14621 | 5263.56 | 0.5727 | 6872.4 | 1 | 5000 | 5263.56 | 6872.4 | 0 | 0 | 0 | 0 | 48192.04 | 0 | 0 | 0 | 0 | 0 | 48192.04
2022101219 | 4 | 0.77575 | 62060 | 0.1357 | 4885.2 | 0.19555 | 2346.6 | 1 | 5000 | 4885.2 | 2346.6 | 0 | 0 | 0 | 0 | 49828.2 | 0 | 0 | 0 | 0 | 0 | 49828.2
2022101220 | 4 | 0.74307 | 59445.6 | 0.14421 | 5191.56 | 0.00303 | 36.36 | 1 | 5000 | 5191.56 | 36.36 | 0 | 0 | 0 | 0 | 49217.68 | 0 | 0 | 0 | 0 | 0 | 49217.68
2022101221 | 4 | 0.72192 | 57753.6 | 0.19153 | 6895.08 | 0 | 0 | 1 | 5000 | 6895.08 | 0 | 0 | 0 | 0 | 0 | 45858.52 | 0 | 0 | 0 | 0 | 0 | 45858.52
2022101222 | 4 | 0.68631 | 54904.8 | 0.22235 | 8004.6 | 0 | 0 | 1 | 5000 | 8004.6 | 0 | 0 | 0 | 0 | 0 | 41900.2 | 0 | 0 | 0 | 0 | 0 | 41900.2
2022101223 | 4 | 0.63812 | 51049.6 | 0.2362 | 8503.2 | 0 | 0 | 1 | 5000 | 8503.2 | 0 | 0 | 0 | 0 | 0 | 37546.4 | 0 | 0 | 0 | 0 | 0 | 37546.4
2022101224 | 4 | 0.58766 | 47012.8 | 0.24487 | 8815.32 | 0 | 0 | 1 | 5000 | 8815.32 | 0 | 0 | 0 | 0 | 0 | 33197.48 | 0 | 0 | 0 | 0 | 0 | 33197.48
2022101301 | 5 | 0.54601 | 43680.8 | 0.23758 | 8552.88 | 0 | 0 | 1 | 5000 | 8552.88 | 0 | 0 | 0 | 0 | 0 | 30127.92 | 0 | 0 | 0 | 0 | 0 | 30127.92
2022101302 | 5 | 0.51854 | 41483.2 | 0.23793 | 8565.48 | 0 | 0 | 1 | 5000 | 8565.48 | 0 | 0 | 0 | 0 | 0 | 27917.72 | 0 | 0 | 0 | 0 | 0 | 27917.72
2022101303 | 5 | 0.49959 | 39967.2 | 0.23745 | 8548.2 | 0 | 0 | 1 | 5000 | 8548.2 | 0 | 0 | 0 | 0 | 0 | 26419 | 0 | 0 | 0 | 0 | 0 | 26419
2022101304 | 5 | 0.48848 | 39078.4 | 0.25243 | 9087.48 | 0 | 0 | 1 | 5000 | 9087.48 | 0 | 0 | 0 | 0 | 0 | 24990.92 | 0 | 0 | 0 | 0 | 0 | 24990.92
2022101305 | 5 | 0.48532 | 38825.6 | 0.2512 | 9043.2 | 0 | 0 | 1 | 5000 | 9043.2 | 0 | 0 | 0 | 0 | 0 | 24782.4 | 0 | 0 | 0 | 0 | 0 | 24782.4
2022101306 | 5 | 0.49973 | 39978.4 | 0.24876 | 8955.36 | 0 | 0 | 1 | 5000 | 8955.36 | 0 | 0 | 0 | 0 | 0 | 26023.04 | 0 | 0 | 0 | 0 | 0 | 26023.04
2022101307 | 5 | 0.52797 | 42237.6 | 0.2443 | 8794.8 | 0 | 0 | 1 | 5000 | 8794.8 | 0 | 0 | 0 | 0 | 0 | 28442.8 | 0 | 0 | 0 | 0 | 0 | 28442.8
2022101308 | 5 | 0.53722 | 42977.6 | 0.2315 | 8334 | 0.00432 | 51.84 | 1 | 5000 | 8334 | 51.84 | 0 | 0 | 0 | 0 | 29591.76 | 0 | 0 | 0 | 0 | 0 | 29591.76
2022101309 | 5 | 0.54074 | 43259.2 | 0.19602 | 7056.72 | 0.21099 | 2531.88 | 1 | 5000 | 7056.72 | 2531.88 | 0 | 0 | 0 | 0 | 28670.6 | 0 | 0 | 0 | 0 | 0 | 28670.6
2022101310 | 5 | 0.55917 | 44733.6 | 0.12775 | 4599 | 0.59812 | 7177.44 | 1 | 5000 | 4599 | 7177.44 | 0 | 0 | 0 | 0 | 27957.16 | 0 | 0 | 0 | 0 | 0 | 27957.16
2022101311 | 5 | 0.58126 | 46500.8 | 0.11043 | 3975.48 | 0.67826 | 8139.12 | 1 | 5000 | 3975.48 | 8139.12 | 0 | 0 | 0 | 0 | 29386.2 | 0 | 0 | 0 | 0 | 0 | 29386.2
2022101312 | 5 | 0.61079 | 48863.2 | 0.09392 | 3381.12 | 0.67115 | 8053.8 | 1 | 5000 | 3381.12 | 8053.8 | 0 | 0 | 0 | 0 | 32428.28 | 0 | 0 | 0 | 0 | 0 | 32428.28
2022101313 | 5 | 0.64087 | 51269.6 | 0.06928 | 2494.08 | 0.70016 | 8401.92 | 1 | 5000 | 2494.08 | 8401.92 | 0 | 0 | 0 | 0 | 35373.6 | 0 | 0 | 0 | 0 | 0 | 35373.6
2022101314 | 5 | 0.67389 | 53911.2 | 0.05312 | 1912.32 | 0.70551 | 8466.12 | 1 | 5000 | 1912.32 | 8466.12 | 0 | 0 | 0 | 0 | 38532.76 | 0 | 0 | 0 | 0 | 0 | 38532.76
2022101315 | 5 | 0.70251 | 56200.8 | 0.04381 | 1577.16 | 0.69479 | 8337.48 | 1 | 5000 | 1577.16 | 8337.48 | 0 | 0 | 0 | 0 | 41286.16 | 0 | 0 | 0 | 0 | 0 | 41286.16
2022101316 | 5 | 0.72453 | 57962.4 | 0.07042 | 2535.12 | 0.6713 | 8055.6 | 1 | 5000 | 2535.12 | 8055.6 | 0 | 0 | 0 | 0 | 42371.68 | 0 | 0 | 0 | 0 | 0 | 42371.68
2022101317 | 5 | 0.73418 | 58734.4 | 0.08468 | 3048.48 | 0.61632 | 7395.84 | 1 | 5000 | 3048.48 | 7395.84 | 0 | 0 | 0 | 0 | 43290.08 | 0 | 0 | 0 | 0 | 0 | 43290.08
2022101318 | 5 | 0.7232 | 57856 | 0.07308 | 2630.88 | 0.48234 | 5788.08 | 1 | 5000 | 2630.88 | 5788.08 | 0 | 0 | 0 | 0 | 44437.04 | 0 | 0 | 0 | 0 | 0 | 44437.04
2022101319 | 5 | 0.68574 | 54859.2 | 0.06207 | 2234.52 | 0.14543 | 1745.16 | 1 | 5000 | 2234.52 | 1745.16 | 0 | 0 | 0 | 0 | 45879.52 | 0 | 0 | 0 | 0 | 0 | 45879.52
2022101320 | 5 | 0.66524 | 53219.2 | 0.0816 | 2937.6 | 0.00157 | 18.84 | 1 | 5000 | 2937.6 | 18.84 | 0 | 0 | 0 | 0 | 45262.76 | 0 | 0 | 0 | 0 | 0 | 45262.76
2022101321 | 5 | 0.64375 | 51500 | 0.1222 | 4399.2 | 0.00018 | 2.16 | 1 | 5000 | 4399.2 | 2.16 | 0 | 0 | 0 | 0 | 42098.64 | 0 | 0 | 0 | 0 | 0 | 42098.64
2022101322 | 5 | 0.60991 | 48792.8 | 0.13989 | 5036.04 | 0.00018 | 2.16 | 1 | 5000 | 5036.04 | 2.16 | 0 | 0 | 0 | 0 | 38754.6 | 0 | 0 | 0 | 0 | 0 | 38754.6
2022101323 | 5 | 0.56833 | 45466.4 | 0.15359 | 5529.24 | 0.00018 | 2.16 | 1 | 5000 | 5529.24 | 2.16 | 0 | 0 | 0 | 0 | 34935 | 0 | 0 | 0 | 0 | 0 | 34935
2022101324 | 5 | 0.52719 | 42175.2 | 0.16339 | 5882.04 | 0.00018 | 2.16 | 1 | 5000 | 5882.04 | 2.16 | 0 | 0 | 0 | 0 | 31291 | 0 | 0 | 0 | 0 | 0 | 31291
2022101401 | 6 | 0.49331 | 39464.8 | 0.17175 | 6183 | 0.00018 | 2.16 | 1 | 5000 | 6183 | 2.16 | 0 | 0 | 0 | 0 | 28279.64 | 0 | 0 | 0 | 0 | 0 | 28279.64
2022101402 | 6 | 0.46941 | 37552.8 | 0.17978 | 6472.08 | 0.00018 | 2.16 | 1 | 5000 | 6472.08 | 2.16 | 0 | 0 | 0 | 0 | 26078.56 | 0 | 0 | 0 | 0 | 0 | 26078.56
2022101403 | 6 | 0.45602 | 36481.6 | 0.18571 | 6685.56 | 0.00018 | 2.16 | 1 | 5000 | 6685.56 | 2.16 | 0 | 0 | 0 | 0 | 24793.88 | 0 | 0 | 0 | 0 | 0 | 24793.88
2022101404 | 6 | 0.44803 | 35842.4 | 0.185 | 6660 | 0.00018 | 2.16 | 1 | 5000 | 6660 | 2.16 | 0 | 0 | 0 | 0 | 24180.24 | 0 | 0 | 0 | 0 | 0 | 24180.24
2022101405 | 6 | 0.45086 | 36068.8 | 0.19352 | 6966.72 | 0.00018 | 2.16 | 1 | 5000 | 6966.72 | 2.16 | 0 | 0 | 0 | 0 | 24099.92 | 0 | 0 | 0 | 0 | 0 | 24099.92
2022101406 | 6 | 0.46342 | 37073.6 | 0.20354 | 7327.44 | 0.00018 | 2.16 | 1 | 5000 | 7327.44 | 2.16 | 0 | 0 | 0 | 0 | 24744 | 0 | 0 | 0 | 0 | 0 | 24744
2022101407 | 6 | 0.49124 | 39299.2 | 0.21023 | 7568.28 | 0.00018 | 2.16 | 1 | 5000 | 7568.28 | 2.16 | 0 | 0 | 0 | 0 | 26728.76 | 0 | 0 | 0 | 0 | 0 | 26728.76
2022101408 | 6 | 0.50541 | 40432.8 | 0.23075 | 8307 | 0.00531 | 63.72 | 1 | 5000 | 8307 | 63.72 | 0 | 0 | 0 | 0 | 27062.08 | 0 | 0 | 0 | 0 | 0 | 27062.08
2022101409 | 6 | 0.51395 | 41116 | 0.26211 | 9435.96 | 0.22046 | 2645.52 | 1 | 5000 | 9435.96 | 2645.52 | 0 | 0 | 0 | 0 | 24034.52 | 0 | 0 | 0 | 0 | 0 | 24034.52
2022101410 | 6 | 0.53846 | 43076.8 | 0.21572 | 7765.92 | 0.62888 | 7546.56 | 1 | 5000 | 7765.92 | 7546.56 | 0 | 0 | 0 | 0 | 22764.32 | 0 | 0 | 0 | 0 | 0 | 22764.32
2022101411 | 6 | 0.56598 | 45278.4 | 0.22362 | 8050.32 | 0.7478 | 8973.6 | 1 | 5000 | 8050.32 | 8973.6 | 0 | 0 | 0 | 0 | 23254.48 | 0 | 0 | 0 | 0 | 0 | 23254.48
2022101412 | 6 | 0.59578 | 47662.4 | 0.28738 | 10345.68 | 0.75198 | 9023.76 | 1 | 5000 | 10345.68 | 9023.76 | 0 | 0 | 0 | 0 | 23292.96 | 0 | 0 | 0 | 0 | 0 | 23292.96
2022101413 | 6 | 0.62607 | 50085.6 | 0.30047 | 10816.92 | 0.741 | 8892 | 1 | 5000 | 10816.92 | 8892 | 0 | 0 | 0 | 0 | 25376.68 | 0 | 0 | 0 | 0 | 0 | 25376.68
2022101414 | 6 | 0.65761 | 52608.8 | 0.30022 | 10807.92 | 0.73371 | 8804.52 | 1 | 5000 | 10807.92 | 8804.52 | 0 | 0 | 0 | 0 | 27996.36 | 0 | 0 | 0 | 0 | 0 | 27996.36
2022101415 | 6 | 0.68932 | 55145.6 | 0.28475 | 10251 | 0.71538 | 8584.56 | 1 | 5000 | 10251 | 8584.56 | 0 | 0 | 0 | 0 | 31310.04 | 0 | 0 | 0 | 0 | 0 | 31310.04
2022101416 | 6 | 0.71352 | 57081.6 | 0.2915 | 10494 | 0.68063 | 8167.56 | 1 | 5000 | 10494 | 8167.56 | 0 | 0 | 0 | 0 | 33420.04 | 0 | 0 | 0 | 0 | 0 | 33420.04
2022101417 | 6 | 0.72823 | 58258.4 | 0.32429 | 11674.44 | 0.59116 | 7093.92 | 1 | 5000 | 11674.44 | 7093.92 | 0 | 0 | 0 | 0 | 34490.04 | 0 | 0 | 0 | 0 | 0 | 34490.04
2022101418 | 6 | 0.72061 | 57648.8 | 0.35507 | 12782.52 | 0.35463 | 4255.56 | 1 | 5000 | 12782.52 | 4255.56 | 0 | 0 | 0 | 0 | 35610.72 | 0 | 0 | 0 | 0 | 0 | 35610.72
2022101419 | 6 | 0.6857 | 54856 | 0.30964 | 11147.04 | 0.06973 | 836.76 | 1 | 5000 | 11147.04 | 836.76 | 0 | 0 | 0 | 0 | 37872.2 | 0 | 0 | 0 | 0 | 0 | 37872.2
2022101420 | 6 | 0.66334 | 53067.2 | 0.31791 | 11444.76 | 0.00037 | 4.44 | 1 | 5000 | 11444.76 | 4.44 | 0 | 0 | 0 | 0 | 36618 | 0 | 0 | 0 | 0 | 0 | 36618
2022101421 | 6 | 0.64002 | 51201.6 | 0.39004 | 14041.44 | 0 | 0 | 1 | 5000 | 14041.44 | 0 | 0 | 0 | 0 | 0 | 32160.16 | 0 | 0 | 0 | 0 | 0 | 32160.16
2022101422 | 6 | 0.61687 | 49349.6 | 0.44272 | 15937.92 | 0 | 0 | 1 | 5000 | 15937.92 | 0 | 0 | 0 | 0 | 0 | 28411.68 | 0 | 0 | 0 | 0 | 0 | 28411.68
2022101423 | 6 | 0.59039 | 47231.2 | 0.47644 | 17151.84 | 0 | 0 | 1 | 5000 | 17151.84 | 0 | 0 | 0 | 0 | 0 | 25079.36 | 0 | 0 | 0 | 0 | 0 | 25079.36
2022101424 | 6 | 0.56057 | 44845.6 | 0.50964 | 18347.04 | 0 | 0 | 1 | 5000 | 18347.04 | 0 | 0 | 0 | 0 | 0 | 21498.56 | 0 | 0 | 0 | 0 | 0 | 21498.56
2022101501 | 7 | 0.53426 | 42740.8 | 0.54064 | 19463.04 | 0 | 0 | 1 | 5000 | 19463.04 | 0 | 0 | 0 | 0 | 0 | 18277.76 | 0 | 0 | 0 | 0 | 0 | 18277.76
2022101502 | 7 | 0.5122 | 40976 | 0.54181 | 19505.16 | 0 | 0 | 1 | 5000 | 19505.16 | 0 | 0 | 0 | 0 | 0 | 16470.84 | 0 | 0 | 0 | 0 | 0 | 16470.84
2022101503 | 7 | 0.498 | 39840 | 0.53334 | 19200.24 | 0 | 0 | 1 | 5000 | 19200.24 | 0 | 0 | 0 | 0 | 0 | 15639.76 | 0 | 0 | 0 | 0 | 0 | 15639.76
2022101504 | 7 | 0.48834 | 39067.2 | 0.51028 | 18370.08 | 0 | 0 | 1 | 5000 | 18370.08 | 0 | 0 | 0 | 0 | 0 | 15697.12 | 0 | 0 | 0 | 0 | 0 | 15697.12
2022101505 | 7 | 0.48254 | 38603.2 | 0.50478 | 18172.08 | 0 | 0 | 1 | 5000 | 18172.08 | 0 | 0 | 0 | 0 | 0 | 15431.12 | 0 | 0 | 0 | 0 | 0 | 15431.12
2022101506 | 7 | 0.48451 | 38760.8 | 0.48572 | 17485.92 | 0 | 0 | 1 | 5000 | 17485.92 | 0 | 0 | 0 | 0 | 0 | 16274.88 | 0 | 0 | 0 | 0 | 0 | 16274.88
2022101507 | 7 | 0.49356 | 39484.8 | 0.45725 | 16461 | 0 | 0 | 1 | 5000 | 16461 | 0 | 0 | 0 | 0 | 0 | 18023.8 | 0 | 0 | 0 | 0 | 0 | 18023.8
2022101508 | 7 | 0.50374 | 40299.2 | 0.43385 | 15618.6 | 0.00434 | 52.08 | 1 | 5000 | 15618.6 | 52.08 | 0 | 0 | 0 | 0 | 19628.52 | 0 | 0 | 0 | 0 | 0 | 19628.52
2022101509 | 7 | 0.52474 | 41979.2 | 0.39149 | 14093.64 | 0.14621 | 1754.52 | 1 | 5000 | 14093.64 | 1754.52 | 0 | 0 | 0 | 0 | 21131.04 | 0 | 0 | 0 | 0 | 0 | 21131.04
2022101510 | 7 | 0.56158 | 44926.4 | 0.34854 | 12547.44 | 0.42722 | 5126.64 | 1 | 5000 | 12547.44 | 5126.64 | 0 | 0 | 0 | 0 | 22252.32 | 0 | 0 | 0 | 0 | 0 | 22252.32
2022101511 | 7 | 0.60708 | 48566.4 | 0.38106 | 13718.16 | 0.59616 | 7153.92 | 1 | 5000 | 13718.16 | 7153.92 | 0 | 0 | 0 | 0 | 22694.32 | 0 | 0 | 0 | 0 | 0 | 22694.32
2022101512 | 7 | 0.65064 | 52051.2 | 0.38622 | 13903.92 | 0.6761 | 8113.2 | 1 | 5000 | 13903.92 | 8113.2 | 0 | 0 | 0 | 0 | 25034.08 | 0 | 0 | 0 | 0 | 0 | 25034.08
2022101513 | 7 | 0.68788 | 55030.4 | 0.33568 | 12084.48 | 0.67836 | 8140.32 | 1 | 5000 | 12084.48 | 8140.32 | 0 | 0 | 0 | 0 | 29805.6 | 0 | 0 | 0 | 0 | 0 | 29805.6
2022101514 | 7 | 0.71969 | 57575.2 | 0.29533 | 10631.88 | 0.67895 | 8147.4 | 1 | 5000 | 10631.88 | 8147.4 | 0 | 0 | 0 | 0 | 33795.92 | 0 | 0 | 0 | 0 | 0 | 33795.92
2022101515 | 7 | 0.74889 | 59911.2 | 0.27952 | 10062.72 | 0.68606 | 8232.72 | 1 | 5000 | 10062.72 | 8232.72 | 0 | 0 | 0 | 0 | 36615.76 | 0 | 0 | 0 | 0 | 0 | 36615.76
2022101516 | 7 | 0.76914 | 61531.2 | 0.27725 | 9981 | 0.67702 | 8124.24 | 1 | 5000 | 9981 | 8124.24 | 0 | 0 | 0 | 0 | 38425.96 | 0 | 0 | 0 | 0 | 0 | 38425.96
2022101517 | 7 | 0.77665 | 62132 | 0.29302 | 10548.72 | 0.63801 | 7656.12 | 1 | 5000 | 10548.72 | 7656.12 | 0 | 0 | 0 | 0 | 38927.16 | 0 | 0 | 0 | 0 | 0 | 38927.16
2022101518 | 7 | 0.76688 | 61350.4 | 0.30006 | 10802.16 | 0.4929 | 5914.8 | 1 | 5000 | 10802.16 | 5914.8 | 0 | 0 | 0 | 0 | 39633.44 | 0 | 0 | 0 | 0 | 0 | 39633.44
2022101519 | 7 | 0.7257 | 58056 | 0.29151 | 10494.36 | 0.11004 | 1320.48 | 1 | 5000 | 10494.36 | 1320.48 | 0 | 0 | 0 | 0 | 41241.16 | 0 | 0 | 0 | 0 | 0 | 41241.16
2022101520 | 7 | 0.70079 | 56063.2 | 0.31471 | 11329.56 | 0.00585 | 70.2 | 1 | 5000 | 11329.56 | 70.2 | 0 | 0 | 0 | 0 | 39663.44 | 0 | 0 | 0 | 0 | 0 | 39663.44
2022101521 | 7 | 0.6801 | 54408 | 0.42537 | 15313.32 | 0.00095 | 11.4 | 1 | 5000 | 15313.32 | 11.4 | 0 | 0 | 0 | 0 | 34083.28 | 0 | 0 | 0 | 0 | 0 | 34083.28
2022101522 | 7 | 0.65487 | 52389.6 | 0.52372 | 18853.92 | 0 | 0 | 1 | 5000 | 18853.92 | 0 | 0 | 0 | 0 | 0 | 28535.68 | 0 | 0 | 0 | 0 | 0 | 28535.68
2022101523 | 7 | 0.62383 | 49906.4 | 0.54932 | 19775.52 | 0 | 0 | 1 | 5000 | 19775.52 | 0 | 0 | 0 | 0 | 0 | 25130.88 | 0 | 0 | 0 | 0 | 0 | 25130.88
2022101524 | 7 | 0.59016 | 47212.8 | 0.55945 | 20140.2 | 0 | 0 | 1 | 5000 | 20140.2 | 0 | 0 | 0 | 0 | 0 | 22072.6 | 0 | 0 | 0 | 0 | 0 | 22072.6
2022101601 | 1 | 0.55899 | 44719.2 | 0.53136 | 19128.96 | 0 | 0 | 1 | 5000 | 19128.96 | 0 | 0 | 0 | 0 | 0 | 20590.24 | 0 | 0 | 0 | 0 | 0 | 20590.24
2022101602 | 1 | 0.53387 | 42709.6 | 0.50542 | 18195.12 | 0 | 0 | 1 | 5000 | 18195.12 | 0 | 0 | 0 | 0 | 0 | 19514.48 | 0 | 0 | 0 | 0 | 0 | 19514.48
2022101603 | 1 | 0.51187 | 40949.6 | 0.42094 | 15153.84 | 0 | 0 | 1 | 5000 | 15153.84 | 0 | 0 | 0 | 0 | 0 | 20795.76 | 0 | 0 | 0 | 0 | 0 | 20795.76
2022101604 | 1 | 0.49685 | 39748 | 0.34259 | 12333.24 | 0 | 0 | 1 | 5000 | 12333.24 | 0 | 0 | 0 | 0 | 0 | 22414.76 | 0 | 0 | 0 | 0 | 0 | 22414.76
2022101605 | 1 | 0.48976 | 39180.8 | 0.30809 | 11091.24 | 0 | 0 | 1 | 5000 | 11091.24 | 0 | 0 | 0 | 0 | 0 | 23089.56 | 0 | 0 | 0 | 0 | 0 | 23089.56
2022101606 | 1 | 0.48692 | 38953.6 | 0.27811 | 10011.96 | 0 | 0 | 1 | 5000 | 10011.96 | 0 | 0 | 0 | 0 | 0 | 23941.64 | 0 | 0 | 0 | 0 | 0 | 23941.64
2022101607 | 1 | 0.48605 | 38884 | 0.27555 | 9919.8 | 0 | 0 | 1 | 5000 | 9919.8 | 0 | 0 | 0 | 0 | 0 | 23964.2 | 0 | 0 | 0 | 0 | 0 | 23964.2
2022101608 | 1 | 0.48948 | 39158.4 | 0.27965 | 10067.4 | 0.00241 | 28.92 | 1 | 5000 | 10067.4 | 28.92 | 0 | 0 | 0 | 0 | 24062.08 | 0 | 0 | 0 | 0 | 0 | 24062.08
2022101609 | 1 | 0.50375 | 40300 | 0.25828 | 9298.08 | 0.07351 | 882.12 | 1 | 5000 | 9298.08 | 882.12 | 0 | 0 | 0 | 0 | 25119.8 | 0 | 0 | 0 | 0 | 0 | 25119.8
2022101610 | 1 | 0.53804 | 43043.2 | 0.23408 | 8426.88 | 0.1906 | 2287.2 | 1 | 5000 | 8426.88 | 2287.2 | 0 | 0 | 0 | 0 | 27329.12 | 0 | 0 | 0 | 0 | 0 | 27329.12
2022101611 | 1 | 0.56913 | 45530.4 | 0.22193 | 7989.48 | 0.23559 | 2827.08 | 1 | 5000 | 7989.48 | 2827.08 | 0 | 0 | 0 | 0 | 29713.84 | 0 | 0 | 0 | 0 | 0 | 29713.84
2022101612 | 1 | 0.59506 | 47604.8 | 0.19837 | 7141.32 | 0.26138 | 3136.56 | 1 | 5000 | 7141.32 | 3136.56 | 0 | 0 | 0 | 0 | 32326.92 | 0 | 0 | 0 | 0 | 0 | 32326.92
2022101613 | 1 | 0.62577 | 50061.6 | 0.21938 | 7897.68 | 0.30987 | 3718.44 | 1 | 5000 | 7897.68 | 3718.44 | 0 | 0 | 0 | 0 | 33445.48 | 0 | 0 | 0 | 0 | 0 | 33445.48
2022101614 | 1 | 0.65439 | 52351.2 | 0.2693 | 9694.8 | 0.32669 | 3920.28 | 1 | 5000 | 9694.8 | 3920.28 | 0 | 0 | 0 | 0 | 33736.12 | 0 | 0 | 0 | 0 | 0 | 33736.12
2022101615 | 1 | 0.67302 | 53841.6 | 0.32158 | 11576.88 | 0.29406 | 3528.72 | 1 | 5000 | 11576.88 | 3528.72 | 0 | 0 | 0 | 0 | 33736 | 0 | 0 | 0 | 0 | 0 | 33736
2022101616 | 1 | 0.68578 | 54862.4 | 0.38696 | 13930.56 | 0.27024 | 3242.88 | 1 | 5000 | 13930.56 | 3242.88 | 0 | 0 | 0 | 0 | 32688.96 | 0 | 0 | 0 | 0 | 0 | 32688.96
2022101617 | 1 | 0.69403 | 55522.4 | 0.45178 | 16264.08 | 0.18732 | 2247.84 | 1 | 5000 | 16264.08 | 2247.84 | 0 | 0 | 0 | 0 | 32010.48 | 0 | 0 | 0 | 0 | 0 | 32010.48
2022101618 | 1 | 0.68936 | 55148.8 | 0.4472 | 16099.2 | 0.10555 | 1266.6 | 1 | 5000 | 16099.2 | 1266.6 | 0 | 0 | 0 | 0 | 32783 | 0 | 0 | 0 | 0 | 0 | 32783
2022101619 | 1 | 0.67392 | 53913.6 | 0.42687 | 15367.32 | 0.03006 | 360.72 | 1 | 5000 | 15367.32 | 360.72 | 0 | 0 | 0 | 0 | 33185.56 | 0 | 0 | 0 | 0 | 0 | 33185.56
2022101620 | 1 | 0.66641 | 53312.8 | 0.42101 | 15156.36 | 0.01271 | 152.52 | 1 | 5000 | 15156.36 | 152.52 | 0 | 0 | 0 | 0 | 33003.92 | 0 | 0 | 0 | 0 | 0 | 33003.92
2022101621 | 1 | 0.64642 | 51713.6 | 0.40681 | 14645.16 | 0.00601 | 72.12 | 1 | 5000 | 14645.16 | 72.12 | 0 | 0 | 0 | 0 | 31996.32 | 0 | 0 | 0 | 0 | 0 | 31996.32
2022101622 | 1 | 0.6179 | 49432 | 0.38146 | 13732.56 | 0 | 0 | 1 | 5000 | 13732.56 | 0 | 0 | 0 | 0 | 0 | 30699.44 | 0 | 0 | 0 | 0 | 0 | 30699.44
2022101623 | 1 | 0.58354 | 46683.2 | 0.37294 | 13425.84 | 0 | 0 | 1 | 5000 | 13425.84 | 0 | 0 | 0 | 0 | 0 | 28257.36 | 0 | 0 | 0 | 0 | 0 | 28257.36
2022101624 | 1 | 0.54507 | 43605.6 | 0.37026 | 13329.36 | 0 | 0 | 1 | 5000 | 13329.36 | 0 | 0 | 0 | 0 | 0 | 25276.24 | 0 | 0 | 0 | 0 | 0 | 25276.24
2022101701 | 2 | 0.51083 | 40866.4 | 0.35013 | 12604.68 | 0 | 0 | 1 | 5000 | 12604.68 | 0 | 0 | 0 | 0 | 0 | 23261.72 | 0 | 0 | 0 | 0 | 0 | 23261.72
2022101702 | 2 | 0.48845 | 39076 | 0.31788 | 11443.68 | 0 | 0 | 1 | 5000 | 11443.68 | 0 | 0 | 0 | 0 | 0 | 22632.32 | 0 | 0 | 0 | 0 | 0 | 22632.32
2022101703 | 2 | 0.47491 | 37992.8 | 0.29646 | 10672.56 | 0 | 0 | 1 | 5000 | 10672.56 | 0 | 0 | 0 | 0 | 0 | 22320.24 | 0 | 0 | 0 | 0 | 0 | 22320.24
2022101704 | 2 | 0.46854 | 37483.2 | 0.28982 | 10433.52 | 0 | 0 | 1 | 5000 | 10433.52 | 0 | 0 | 0 | 0 | 0 | 22049.68 | 0 | 0 | 0 | 0 | 0 | 22049.68
2022101705 | 2 | 0.47108 | 37686.4 | 0.32378 | 11656.08 | 0 | 0 | 1 | 5000 | 11656.08 | 0 | 0 | 0 | 0 | 0 | 21030.32 | 0 | 0 | 0 | 0 | 0 | 21030.32
2022101706 | 2 | 0.48496 | 38796.8 | 0.32608 | 11738.88 | 0 | 0 | 1 | 5000 | 11738.88 | 0 | 0 | 0 | 0 | 0 | 22057.92 | 0 | 0 | 0 | 0 | 0 | 22057.92
2022101707 | 2 | 0.51035 | 40828 | 0.30619 | 11022.84 | 0 | 0 | 1 | 5000 | 11022.84 | 0 | 0 | 0 | 0 | 0 | 24805.16 | 0 | 0 | 0 | 0 | 0 | 24805.16
2022101708 | 2 | 0.52478 | 41982.4 | 0.2907 | 10465.2 | 0.00137 | 16.44 | 1 | 5000 | 10465.2 | 16.44 | 0 | 0 | 0 | 0 | 26500.76 | 0 | 0 | 0 | 0 | 0 | 26500.76
2022101709 | 2 | 0.52705 | 42164 | 0.27764 | 9995.04 | 0.05295 | 635.4 | 1 | 5000 | 9995.04 | 635.4 | 0 | 0 | 0 | 0 | 26533.56 | 0 | 0 | 0 | 0 | 0 | 26533.56
2022101710 | 2 | 0.53874 | 43099.2 | 0.25812 | 9292.32 | 0.13616 | 1633.92 | 1 | 5000 | 9292.32 | 1633.92 | 0 | 0 | 0 | 0 | 27172.96 | 0 | 0 | 0 | 0 | 0 | 27172.96
2022101711 | 2 | 0.54574 | 43659.2 | 0.27068 | 9744.48 | 0.21437 | 2572.44 | 1 | 5000 | 9744.48 | 2572.44 | 0 | 0 | 0 | 0 | 26342.28 | 0 | 0 | 0 | 0 | 0 | 26342.28
2022101712 | 2 | 0.54971 | 43976.8 | 0.2796 | 10065.6 | 0.26078 | 3129.36 | 1 | 5000 | 10065.6 | 3129.36 | 0 | 0 | 0 | 0 | 25781.84 | 0 | 0 | 0 | 0 | 0 | 25781.84
2022101713 | 2 | 0.55083 | 44066.4 | 0.28385 | 10218.6 | 0.30586 | 3670.32 | 1 | 5000 | 10218.6 | 3670.32 | 0 | 0 | 0 | 0 | 25177.48 | 0 | 0 | 0 | 0 | 0 | 25177.48
2022101714 | 2 | 0.55386 | 44308.8 | 0.28888 | 10399.68 | 0.33411 | 4009.32 | 1 | 5000 | 10399.68 | 4009.32 | 0 | 0 | 0 | 0 | 24899.8 | 0 | 0 | 0 | 0 | 0 | 24899.8
2022101715 | 2 | 0.55282 | 44225.6 | 0.28627 | 10305.72 | 0.3348 | 4017.6 | 1 | 5000 | 10305.72 | 4017.6 | 0 | 0 | 0 | 0 | 24902.28 | 0 | 0 | 0 | 0 | 0 | 24902.28
2022101716 | 2 | 0.5527 | 44216 | 0.2995 | 10782 | 0.35208 | 4224.96 | 1 | 5000 | 10782 | 4224.96 | 0 | 0 | 0 | 0 | 24209.04 | 0 | 0 | 0 | 0 | 0 | 24209.04
2022101717 | 2 | 0.55829 | 44663.2 | 0.30579 | 11008.44 | 0.32966 | 3955.92 | 1 | 5000 | 11008.44 | 3955.92 | 0 | 0 | 0 | 0 | 24698.84 | 0 | 0 | 0 | 0 | 0 | 24698.84
2022101718 | 2 | 0.55778 | 44622.4 | 0.2994 | 10778.4 | 0.23842 | 2861.04 | 1 | 5000 | 10778.4 | 2861.04 | 0 | 0 | 0 | 0 | 25982.96 | 0 | 0 | 0 | 0 | 0 | 25982.96
2022101719 | 2 | 0.55363 | 44290.4 | 0.26183 | 9425.88 | 0.04819 | 578.28 | 1 | 5000 | 9425.88 | 578.28 | 0 | 0 | 0 | 0 | 29286.24 | 0 | 0 | 0 | 0 | 0 | 29286.24
2022101720 | 2 | 0.55979 | 44783.2 | 0.24308 | 8750.88 | 8e-05 | 0.96 | 1 | 5000 | 8750.88 | 0.96 | 0 | 0 | 0 | 0 | 31031.36 | 0 | 0 | 0 | 0 | 0 | 31031.36
2022101721 | 2 | 0.54999 | 43999.2 | 0.25587 | 9211.32 | 0 | 0 | 1 | 5000 | 9211.32 | 0 | 0 | 0 | 0 | 0 | 29787.88 | 0 | 0 | 0 | 0 | 0 | 29787.88
2022101722 | 2 | 0.52695 | 42156 | 0.261 | 9396 | 0 | 0 | 1 | 5000 | 9396 | 0 | 0 | 0 | 0 | 0 | 27760 | 0 | 0 | 0 | 0 | 0 | 27760
2022101723 | 2 | 0.49304 | 39443.2 | 0.25588 | 9211.68 | 0 | 0 | 1 | 5000 | 9211.68 | 0 | 0 | 0 | 0 | 0 | 25231.52 | 0 | 0 | 0 | 0 | 0 | 25231.52
2022101724 | 2 | 0.4604 | 36832 | 0.24152 | 8694.72 | 0 | 0 | 1 | 5000 | 8694.72 | 0 | 0 | 0 | 0 | 0 | 23137.28 | 0 | 0 | 0 | 0 | 0 | 23137.28
2022101801 | 3 | 0.43847 | 35077.6 | 0.2315 | 8334 | 0 | 0 | 1 | 5000 | 8334 | 0 | 0 | 0 | 0 | 0 | 21743.6 | 0 | 0 | 0 | 0 | 0 | 21743.6
2022101802 | 3 | 0.42605 | 34084 | 0.21654 | 7795.44 | 0 | 0 | 1 | 5000 | 7795.44 | 0 | 0 | 0 | 0 | 0 | 21288.56 | 0 | 0 | 0 | 0 | 0 | 21288.56
2022101803 | 3 | 0.41684 | 33347.2 | 0.20636 | 7428.96 | 0 | 0 | 1 | 5000 | 7428.96 | 0 | 0 | 0 | 0 | 0 | 20918.24 | 0 | 0 | 0 | 0 | 0 | 20918.24
2022101804 | 3 | 0.41239 | 32991.2 | 0.19448 | 7001.28 | 0 | 0 | 1 | 5000 | 7001.28 | 0 | 0 | 0 | 0 | 0 | 20989.92 | 0 | 0 | 0 | 0 | 0 | 20989.92
2022101805 | 3 | 0.41819 | 33455.2 | 0.17263 | 6214.68 | 0 | 0 | 1 | 5000 | 6214.68 | 0 | 0 | 0 | 0 | 0 | 22240.52 | 0 | 0 | 0 | 0 | 0 | 22240.52
2022101806 | 3 | 0.43687 | 34949.6 | 0.16325 | 5877 | 0 | 0 | 1 | 5000 | 5877 | 0 | 0 | 0 | 0 | 0 | 24072.6 | 0 | 0 | 0 | 0 | 0 | 24072.6
2022101807 | 3 | 0.47338 | 37870.4 | 0.16731 | 6023.16 | 0 | 0 | 1 | 5000 | 6023.16 | 0 | 0 | 0 | 0 | 0 | 26847.24 | 0 | 0 | 0 | 0 | 0 | 26847.24
2022101808 | 3 | 0.49217 | 39373.6 | 0.1729 | 6224.4 | 0.0032 | 38.4 | 1 | 5000 | 6224.4 | 38.4 | 0 | 0 | 0 | 0 | 28110.8 | 0 | 0 | 0 | 0 | 0 | 28110.8
2022101809 | 3 | 0.49351 | 39480.8 | 0.16438 | 5917.68 | 0.1001 | 1201.2 | 1 | 5000 | 5917.68 | 1201.2 | 0 | 0 | 0 | 0 | 27361.92 | 0 | 0 | 0 | 0 | 0 | 27361.92
2022101810 | 3 | 0.4987 | 39896 | 0.14154 | 5095.44 | 0.25367 | 3044.04 | 1 | 5000 | 5095.44 | 3044.04 | 0 | 0 | 0 | 0 | 26756.52 | 0 | 0 | 0 | 0 | 0 | 26756.52
2022101811 | 3 | 0.50106 | 40084.8 | 0.13771 | 4957.56 | 0.33286 | 3994.32 | 1 | 5000 | 4957.56 | 3994.32 | 0 | 0 | 0 | 0 | 26132.92 | 0 | 0 | 0 | 0 | 0 | 26132.92
2022101812 | 3 | 0.49623 | 39698.4 | 0.112 | 4032 | 0.44747 | 5369.64 | 1 | 5000 | 4032 | 5369.64 | 0 | 0 | 0 | 0 | 25296.76 | 0 | 0 | 0 | 0 | 0 | 25296.76
2022101813 | 3 | 0.49242 | 39393.6 | 0.09319 | 3354.84 | 0.54627 | 6555.24 | 1 | 5000 | 3354.84 | 6555.24 | 0 | 0 | 0 | 0 | 24483.52 | 0 | 0 | 0 | 0 | 0 | 24483.52
2022101814 | 3 | 0.4958 | 39664 | 0.08935 | 3216.6 | 0.59846 | 7181.52 | 1 | 5000 | 3216.6 | 7181.52 | 0 | 0 | 0 | 0 | 24265.88 | 0 | 0 | 0 | 0 | 0 | 24265.88
2022101815 | 3 | 0.4952 | 39616 | 0.07718 | 2778.48 | 0.59956 | 7194.72 | 1 | 5000 | 2778.48 | 7194.72 | 0 | 0 | 0 | 0 | 24642.8 | 0 | 0 | 0 | 0 | 0 | 24642.8
2022101816 | 3 | 0.4982 | 39856 | 0.07088 | 2551.68 | 0.57483 | 6897.96 | 1 | 5000 | 2551.68 | 6897.96 | 0 | 0 | 0 | 0 | 25406.36 | 0 | 0 | 0 | 0 | 0 | 25406.36
2022101817 | 3 | 0.50521 | 40416.8 | 0.06349 | 2285.64 | 0.55291 | 6634.92 | 1 | 5000 | 2285.64 | 6634.92 | 0 | 0 | 0 | 0 | 26496.24 | 0 | 0 | 0 | 0 | 0 | 26496.24
2022101818 | 3 | 0.5074 | 40592 | 0.06141 | 2210.76 | 0.41179 | 4941.48 | 1 | 5000 | 2210.76 | 4941.48 | 0 | 0 | 0 | 0 | 28439.76 | 0 | 0 | 0 | 0 | 0 | 28439.76
2022101819 | 3 | 0.51355 | 41084 | 0.06333 | 2279.88 | 0.11234 | 1348.08 | 1 | 5000 | 2279.88 | 1348.08 | 0 | 0 | 0 | 0 | 32456.04 | 0 | 0 | 0 | 0 | 0 | 32456.04
2022101820 | 3 | 0.52303 | 41842.4 | 0.07754 | 2791.44 | 0.00443 | 53.16 | 1 | 5000 | 2791.44 | 53.16 | 0 | 0 | 0 | 0 | 33997.8 | 0 | 0 | 0 | 0 | 0 | 33997.8
2022101821 | 3 | 0.51968 | 41574.4 | 0.10491 | 3776.76 | 0.00291 | 34.92 | 1 | 5000 | 3776.76 | 34.92 | 0 | 0 | 0 | 0 | 32762.72 | 0 | 0 | 0 | 0 | 0 | 32762.72
2022101822 | 3 | 0.50268 | 40214.4 | 0.13404 | 4825.44 | 0 | 0 | 1 | 5000 | 4825.44 | 0 | 0 | 0 | 0 | 0 | 30388.96 | 0 | 0 | 0 | 0 | 0 | 30388.96
2022101823 | 3 | 0.47548 | 38038.4 | 0.14554 | 5239.44 | 0 | 0 | 1 | 5000 | 5239.44 | 0 | 0 | 0 | 0 | 0 | 27798.96 | 0 | 0 | 0 | 0 | 0 | 27798.96
2022101824 | 3 | 0.44807 | 35845.6 | 0.15341 | 5522.76 | 0 | 0 | 1 | 5000 | 5522.76 | 0 | 0 | 0 | 0 | 0 | 25322.84 | 0 | 0 | 0 | 0 | 0 | 25322.84
2022101901 | 4 | 0.43202 | 34561.6 | 0.15365 | 5531.4 | 0 | 0 | 1 | 5000 | 5531.4 | 0 | 0 | 0 | 0 | 0 | 24030.2 | 0 | 0 | 0 | 0 | 0 | 24030.2
2022101902 | 4 | 0.4231 | 33848 | 0.15329 | 5518.44 | 0 | 0 | 1 | 5000 | 5518.44 | 0 | 0 | 0 | 0 | 0 | 23329.56 | 0 | 0 | 0 | 0 | 0 | 23329.56
2022101903 | 4 | 0.41862 | 33489.6 | 0.15765 | 5675.4 | 0 | 0 | 1 | 5000 | 5675.4 | 0 | 0 | 0 | 0 | 0 | 22814.2 | 0 | 0 | 0 | 0 | 0 | 22814.2
2022101904 | 4 | 0.4188 | 33504 | 0.15169 | 5460.84 | 0 | 0 | 1 | 5000 | 5460.84 | 0 | 0 | 0 | 0 | 0 | 23043.16 | 0 | 0 | 0 | 0 | 0 | 23043.16
2022101905 | 4 | 0.4274 | 34192 | 0.15007 | 5402.52 | 0 | 0 | 1 | 5000 | 5402.52 | 0 | 0 | 0 | 0 | 0 | 23789.48 | 0 | 0 | 0 | 0 | 0 | 23789.48
2022101906 | 4 | 0.44936 | 35948.8 | 0.15503 | 5581.08 | 0 | 0 | 1 | 5000 | 5581.08 | 0 | 0 | 0 | 0 | 0 | 25367.72 | 0 | 0 | 0 | 0 | 0 | 25367.72
2022101907 | 4 | 0.48859 | 39087.2 | 0.162 | 5832 | 0 | 0 | 1 | 5000 | 5832 | 0 | 0 | 0 | 0 | 0 | 28255.2 | 0 | 0 | 0 | 0 | 0 | 28255.2
2022101908 | 4 | 0.50996 | 40796.8 | 0.16211 | 5835.96 | 0.00516 | 61.92 | 1 | 5000 | 5835.96 | 61.92 | 0 | 0 | 0 | 0 | 29898.92 | 0 | 0 | 0 | 0 | 0 | 29898.92
2022101909 | 4 | 0.50839 | 40671.2 | 0.15615 | 5621.4 | 0.21378 | 2565.36 | 1 | 5000 | 5621.4 | 2565.36 | 0 | 0 | 0 | 0 | 27484.44 | 0 | 0 | 0 | 0 | 0 | 27484.44
2022101910 | 4 | 0.50541 | 40432.8 | 0.11293 | 4065.48 | 0.64213 | 7705.56 | 1 | 5000 | 4065.48 | 7705.56 | 0 | 0 | 0 | 0 | 23661.76 | 0 | 0 | 0 | 0 | 0 | 23661.76
2022101911 | 4 | 0.49997 | 39997.6 | 0.09537 | 3433.32 | 0.77127 | 9255.24 | 1 | 5000 | 3433.32 | 9255.24 | 0 | 0 | 0 | 0 | 22309.04 | 0 | 0 | 0 | 0 | 0 | 22309.04
2022101912 | 4 | 0.49616 | 39692.8 | 0.1164 | 4190.4 | 0.77965 | 9355.8 | 1 | 5000 | 4190.4 | 9355.8 | 0 | 0 | 0 | 0 | 21146.6 | 0 | 0 | 0 | 0 | 0 | 21146.6
2022101913 | 4 | 0.4936 | 39488 | 0.12805 | 4609.8 | 0.76907 | 9228.84 | 1 | 5000 | 4609.8 | 9228.84 | 0 | 0 | 0 | 0 | 20649.36 | 0 | 0 | 0 | 0 | 0 | 20649.36
2022101914 | 4 | 0.49774 | 39819.2 | 0.12392 | 4461.12 | 0.76491 | 9178.92 | 1 | 5000 | 4461.12 | 9178.92 | 0 | 0 | 0 | 0 | 21179.16 | 0 | 0 | 0 | 0 | 0 | 21179.16
2022101915 | 4 | 0.49907 | 39925.6 | 0.11156 | 4016.16 | 0.77323 | 9278.76 | 1 | 5000 | 4016.16 | 9278.76 | 0 | 0 | 0 | 0 | 21630.68 | 0 | 0 | 0 | 0 | 0 | 21630.68
2022101916 | 4 | 0.50442 | 40353.6 | 0.09804 | 3529.44 | 0.78931 | 9471.72 | 1 | 5000 | 3529.44 | 9471.72 | 0 | 0 | 0 | 0 | 22352.44 | 0 | 0 | 0 | 0 | 0 | 22352.44
2022101917 | 4 | 0.51366 | 41092.8 | 0.09316 | 3353.76 | 0.77641 | 9316.92 | 1 | 5000 | 3353.76 | 9316.92 | 0 | 0 | 0 | 0 | 23422.12 | 0 | 0 | 0 | 0 | 0 | 23422.12
2022101918 | 4 | 0.51874 | 41499.2 | 0.0934 | 3362.4 | 0.61014 | 7321.68 | 1 | 5000 | 3362.4 | 7321.68 | 0 | 0 | 0 | 0 | 25815.12 | 0 | 0 | 0 | 0 | 0 | 25815.12
2022101919 | 4 | 0.51817 | 41453.6 | 0.08445 | 3040.2 | 0.1659 | 1990.8 | 1 | 5000 | 3040.2 | 1990.8 | 0 | 0 | 0 | 0 | 31422.6 | 0 | 0 | 0 | 0 | 0 | 31422.6
2022101920 | 4 | 0.52447 | 41957.6 | 0.12202 | 4392.72 | 0.00092 | 11.04 | 1 | 5000 | 4392.72 | 11.04 | 0 | 0 | 0 | 0 | 32553.84 | 0 | 0 | 0 | 0 | 0 | 32553.84
2022101921 | 4 | 0.5178 | 41424 | 0.21563 | 7762.68 | 0 | 0 | 1 | 5000 | 7762.68 | 0 | 0 | 0 | 0 | 0 | 28661.32 | 0 | 0 | 0 | 0 | 0 | 28661.32
2022101922 | 4 | 0.50094 | 40075.2 | 0.32278 | 11620.08 | 0 | 0 | 1 | 5000 | 11620.08 | 0 | 0 | 0 | 0 | 0 | 23455.12 | 0 | 0 | 0 | 0 | 0 | 23455.12
2022101923 | 4 | 0.47435 | 37948 | 0.4219 | 15188.4 | 0 | 0 | 1 | 5000 | 15188.4 | 0 | 0 | 0 | 0 | 0 | 17759.6 | 0 | 0 | 0 | 0 | 0 | 17759.6
2022101924 | 4 | 0.45256 | 36204.8 | 0.47512 | 17104.32 | 0 | 0 | 1 | 5000 | 17104.32 | 0 | 0 | 0 | 0 | 0 | 14100.48 | 0 | 0 | 0 | 0 | 0 | 14100.48
2022102001 | 5 | 0.43298 | 34638.4 | 0.48901 | 17604.36 | 0 | 0 | 1 | 5000 | 17604.36 | 0 | 0 | 0 | 0 | 0 | 12034.04 | 0 | 0 | 0 | 0 | 0 | 12034.04
2022102002 | 5 | 0.42445 | 33956 | 0.49597 | 17854.92 | 0 | 0 | 1 | 5000 | 17854.92 | 0 | 0 | 0 | 0 | 0 | 11101.08 | 0 | 0 | 0 | 0 | 0 | 11101.08
2022102003 | 5 | 0.42027 | 33621.6 | 0.49745 | 17908.2 | 0 | 0 | 1 | 5000 | 17908.2 | 0 | 0 | 0 | 0 | 0 | 10713.4 | 0 | 0 | 0 | 0 | 0 | 10713.4
2022102004 | 5 | 0.41918 | 33534.4 | 0.49406 | 17786.16 | 0 | 0 | 1 | 5000 | 17786.16 | 0 | 0 | 0 | 0 | 0 | 10748.24 | 0 | 0 | 0 | 0 | 0 | 10748.24
2022102005 | 5 | 0.42513 | 34010.4 | 0.4895 | 17622 | 0 | 0 | 1 | 5000 | 17622 | 0 | 0 | 0 | 0 | 0 | 11388.4 | 0 | 0 | 0 | 0 | 0 | 11388.4
2022102006 | 5 | 0.44942 | 35953.6 | 0.50941 | 18338.76 | 0 | 0 | 1 | 5000 | 18338.76 | 0 | 0 | 0 | 0 | 0 | 12614.84 | 0 | 0 | 0 | 0 | 0 | 12614.84
2022102007 | 5 | 0.48524 | 38819.2 | 0.48252 | 17370.72 | 0 | 0 | 1 | 5000 | 17370.72 | 0 | 0 | 0 | 0 | 0 | 16448.48 | 0 | 0 | 0 | 0 | 0 | 16448.48
2022102008 | 5 | 0.50435 | 40348 | 0.44006 | 15842.16 | 0.00392 | 47.04 | 1 | 5000 | 15842.16 | 47.04 | 0 | 0 | 0 | 0 | 19458.8 | 0 | 0 | 0 | 0 | 0 | 19458.8
2022102009 | 5 | 0.50406 | 40324.8 | 0.37405 | 13465.8 | 0.22418 | 2690.16 | 1 | 5000 | 13465.8 | 2690.16 | 0 | 0 | 0 | 0 | 19168.84 | 0 | 0 | 0 | 0 | 0 | 19168.84
2022102010 | 5 | 0.50291 | 40232.8 | 0.24441 | 8798.76 | 0.67731 | 8127.72 | 1 | 5000 | 8798.76 | 8127.72 | 0 | 0 | 0 | 0 | 18306.32 | 0 | 0 | 0 | 0 | 0 | 18306.32
2022102011 | 5 | 0.50334 | 40267.2 | 0.14853 | 5347.08 | 0.79108 | 9492.96 | 1 | 5000 | 5347.08 | 9492.96 | 0 | 0 | 0 | 0 | 20427.16 | 0 | 0 | 0 | 0 | 0 | 20427.16
2022102012 | 5 | 0.50796 | 40636.8 | 0.11054 | 3979.44 | 0.79119 | 9494.28 | 1 | 5000 | 3979.44 | 9494.28 | 0 | 0 | 0 | 0 | 22163.08 | 0 | 0 | 0 | 0 | 0 | 22163.08
2022102013 | 5 | 0.51612 | 41289.6 | 0.07493 | 2697.48 | 0.77538 | 9304.56 | 1 | 5000 | 2697.48 | 9304.56 | 0 | 0 | 0 | 0 | 24287.56 | 0 | 0 | 0 | 0 | 0 | 24287.56
2022102014 | 5 | 0.5306 | 42448 | 0.05379 | 1936.44 | 0.76643 | 9197.16 | 1 | 5000 | 1936.44 | 9197.16 | 0 | 0 | 0 | 0 | 26314.4 | 0 | 0 | 0 | 0 | 0 | 26314.4
2022102015 | 5 | 0.54585 | 43668 | 0.04677 | 1683.72 | 0.77073 | 9248.76 | 1 | 5000 | 1683.72 | 9248.76 | 0 | 0 | 0 | 0 | 27735.52 | 0 | 0 | 0 | 0 | 0 | 27735.52
2022102016 | 5 | 0.56414 | 45131.2 | 0.04818 | 1734.48 | 0.77974 | 9356.88 | 1 | 5000 | 1734.48 | 9356.88 | 0 | 0 | 0 | 0 | 29039.84 | 0 | 0 | 0 | 0 | 0 | 29039.84
2022102017 | 5 | 0.58117 | 46493.6 | 0.05734 | 2064.24 | 0.76426 | 9171.12 | 1 | 5000 | 2064.24 | 9171.12 | 0 | 0 | 0 | 0 | 30258.24 | 0 | 0 | 0 | 0 | 0 | 30258.24
2022102018 | 5 | 0.58669 | 46935.2 | 0.06898 | 2483.28 | 0.60034 | 7204.08 | 1 | 5000 | 2483.28 | 7204.08 | 0 | 0 | 0 | 0 | 32247.84 | 0 | 0 | 0 | 0 | 0 | 32247.84
2022102019 | 5 | 0.57278 | 45822.4 | 0.07916 | 2849.76 | 0.16774 | 2012.88 | 1 | 5000 | 2849.76 | 2012.88 | 0 | 0 | 0 | 0 | 35959.76 | 0 | 0 | 0 | 0 | 0 | 35959.76
2022102020 | 5 | 0.56696 | 45356.8 | 0.10494 | 3777.84 | 0.01284 | 154.08 | 1 | 5000 | 3777.84 | 154.08 | 0 | 0 | 0 | 0 | 36424.88 | 0 | 0 | 0 | 0 | 0 | 36424.88
2022102021 | 5 | 0.55737 | 44589.6 | 0.14588 | 5251.68 | 0 | 0 | 1 | 5000 | 5251.68 | 0 | 0 | 0 | 0 | 0 | 34337.92 | 0 | 0 | 0 | 0 | 0 | 34337.92
2022102022 | 5 | 0.53968 | 43174.4 | 0.21542 | 7755.12 | 0 | 0 | 1 | 5000 | 7755.12 | 0 | 0 | 0 | 0 | 0 | 30419.28 | 0 | 0 | 0 | 0 | 0 | 30419.28
2022102023 | 5 | 0.50777 | 40621.6 | 0.26813 | 9652.68 | 0 | 0 | 1 | 5000 | 9652.68 | 0 | 0 | 0 | 0 | 0 | 25968.92 | 0 | 0 | 0 | 0 | 0 | 25968.92
2022102024 | 5 | 0.47424 | 37939.2 | 0.3166 | 11397.6 | 0 | 0 | 1 | 5000 | 11397.6 | 0 | 0 | 0 | 0 | 0 | 21541.6 | 0 | 0 | 0 | 0 | 0 | 21541.6
2022102101 | 6 | 0.45081 | 36064.8 | 0.40313 | 14512.68 | 0 | 0 | 1 | 5000 | 14512.68 | 0 | 0 | 0 | 0 | 0 | 16552.12 | 0 | 0 | 0 | 0 | 0 | 16552.12
2022102102 | 6 | 0.43657 | 34925.6 | 0.45513 | 16384.68 | 0 | 0 | 1 | 5000 | 16384.68 | 0 | 0 | 0 | 0 | 0 | 13540.92 | 0 | 0 | 0 | 0 | 0 | 13540.92
2022102103 | 6 | 0.42701 | 34160.8 | 0.46407 | 16706.52 | 0 | 0 | 1 | 5000 | 16706.52 | 0 | 0 | 0 | 0 | 0 | 12454.28 | 0 | 0 | 0 | 0 | 0 | 12454.28
2022102104 | 6 | 0.42446 | 33956.8 | 0.4734 | 17042.4 | 0 | 0 | 1 | 5000 | 17042.4 | 0 | 0 | 0 | 0 | 0 | 11914.4 | 0 | 0 | 0 | 0 | 0 | 11914.4
2022102105 | 6 | 0.42859 | 34287.2 | 0.486 | 17496 | 0 | 0 | 1 | 5000 | 17496 | 0 | 0 | 0 | 0 | 0 | 11791.2 | 0 | 0 | 0 | 0 | 0 | 11791.2
2022102106 | 6 | 0.44546 | 35636.8 | 0.48106 | 17318.16 | 4e-05 | 0.48 | 1 | 5000 | 17318.16 | 0.48 | 0 | 0 | 0 | 0 | 13318.16 | 0 | 0 | 0 | 0 | 0 | 13318.16
2022102107 | 6 | 0.47906 | 38324.8 | 0.45604 | 16417.44 | 0 | 0 | 1 | 5000 | 16417.44 | 0 | 0 | 0 | 0 | 0 | 16907.36 | 0 | 0 | 0 | 0 | 0 | 16907.36
2022102108 | 6 | 0.49607 | 39685.6 | 0.45677 | 16443.72 | 0.00388 | 46.56 | 1 | 5000 | 16443.72 | 46.56 | 0 | 0 | 0 | 0 | 18195.32 | 0 | 0 | 0 | 0 | 0 | 18195.32
2022102109 | 6 | 0.50038 | 40030.4 | 0.43876 | 15795.36 | 0.22518 | 2702.16 | 1 | 5000 | 15795.36 | 2702.16 | 0 | 0 | 0 | 0 | 16532.88 | 0 | 0 | 0 | 0 | 0 | 16532.88
2022102110 | 6 | 0.51083 | 40866.4 | 0.30875 | 11115 | 0.68578 | 8229.36 | 1 | 5000 | 11115 | 8229.36 | 0 | 0 | 0 | 0 | 16522.04 | 0 | 0 | 0 | 0 | 0 | 16522.04
2022102111 | 6 | 0.52256 | 41804.8 | 0.21927 | 7893.72 | 0.78689 | 9442.68 | 1 | 5000 | 7893.72 | 9442.68 | 0 | 0 | 0 | 0 | 19468.4 | 0 | 0 | 0 | 0 | 0 | 19468.4
2022102112 | 6 | 0.53584 | 42867.2 | 0.22074 | 7946.64 | 0.77791 | 9334.92 | 1 | 5000 | 7946.64 | 9334.92 | 0 | 0 | 0 | 0 | 20585.64 | 0 | 0 | 0 | 0 | 0 | 20585.64
2022102113 | 6 | 0.55745 | 44596 | 0.25829 | 9298.44 | 0.74824 | 8978.88 | 1 | 5000 | 9298.44 | 8978.88 | 0 | 0 | 0 | 0 | 21318.68 | 0 | 0 | 0 | 0 | 0 | 21318.68
2022102114 | 6 | 0.58724 | 46979.2 | 0.36391 | 13100.76 | 0.74377 | 8925.24 | 1 | 5000 | 13100.76 | 8925.24 | 0 | 0 | 0 | 0 | 19953.2 | 0 | 0 | 0 | 0 | 0 | 19953.2
2022102115 | 6 | 0.6157 | 49256 | 0.46311 | 16671.96 | 0.65327 | 7839.24 | 1 | 5000 | 16671.96 | 7839.24 | 0 | 0 | 0 | 0 | 19744.8 | 0 | 0 | 0 | 0 | 0 | 19744.8
2022102116 | 6 | 0.64 | 51200 | 0.52843 | 19023.48 | 0.53846 | 6461.52 | 1 | 5000 | 19023.48 | 6461.52 | 0 | 0 | 0 | 0 | 20715 | 0 | 0 | 0 | 0 | 0 | 20715
2022102117 | 6 | 0.65569 | 52455.2 | 0.5328 | 19180.8 | 0.54607 | 6552.84 | 1 | 5000 | 19180.8 | 6552.84 | 0 | 0 | 0 | 0 | 21721.56 | 0 | 0 | 0 | 0 | 0 | 21721.56
2022102118 | 6 | 0.65444 | 52355.2 | 0.55175 | 19863 | 0.39079 | 4689.48 | 1 | 5000 | 19863 | 4689.48 | 0 | 0 | 0 | 0 | 22802.72 | 0 | 0 | 0 | 0 | 0 | 22802.72
2022102119 | 6 | 0.63154 | 50523.2 | 0.54852 | 19746.72 | 0.12763 | 1531.56 | 1 | 5000 | 19746.72 | 1531.56 | 0 | 0 | 0 | 0 | 24244.92 | 0 | 0 | 0 | 0 | 0 | 24244.92
2022102120 | 6 | 0.61547 | 49237.6 | 0.58335 | 21000.6 | 0.00046 | 5.52 | 1 | 5000 | 21000.6 | 5.52 | 0 | 0 | 0 | 0 | 23231.48 | 0 | 0 | 0 | 0 | 0 | 23231.48
2022102121 | 6 | 0.59593 | 47674.4 | 0.66267 | 23856.12 | 0 | 0 | 1 | 5000 | 23856.12 | 0 | 0 | 0 | 0 | 0 | 18818.28 | 0 | 0 | 0 | 0 | 0 | 18818.28
2022102122 | 6 | 0.57469 | 45975.2 | 0.6736 | 24249.6 | 0 | 0 | 1 | 5000 | 24249.6 | 0 | 0 | 0 | 0 | 0 | 16725.6 | 0 | 0 | 0 | 0 | 0 | 16725.6
2022102123 | 6 | 0.54834 | 43867.2 | 0.67373 | 24254.28 | 0 | 0 | 1 | 5000 | 24254.28 | 0 | 0 | 0 | 0 | 0 | 14612.92 | 0 | 0 | 0 | 0 | 0 | 14612.92
2022102124 | 6 | 0.51794 | 41435.2 | 0.66824 | 24056.64 | 0 | 0 | 1 | 5000 | 24056.64 | 0 | 0 | 0 | 0 | 0 | 12378.56 | 0 | 0 | 0 | 0 | 0 | 12378.56
2022102201 | 7 | 0.49211 | 39368.8 | 0.66391 | 23900.76 | 0 | 0 | 1 | 5000 | 23900.76 | 0 | 0 | 0 | 0 | 0 | 10468.04 | 0 | 0 | 0 | 0 | 0 | 10468.04
2022102202 | 7 | 0.46938 | 37550.4 | 0.65535 | 23592.6 | 0 | 0 | 1 | 5000 | 23592.6 | 0 | 0 | 0 | 0 | 0 | 8957.8 | 0 | 0 | 0 | 0 | 0 | 8957.8
2022102203 | 7 | 0.45544 | 36435.2 | 0.64883 | 23357.88 | 0 | 0 | 1 | 5000 | 23357.88 | 0 | 0 | 0 | 0 | 0 | 8077.32 | 0 | 0 | 0 | 0 | 0 | 8077.32
2022102204 | 7 | 0.44671 | 35736.8 | 0.6427 | 23137.2 | 0 | 0 | 1 | 5000 | 23137.2 | 0 | 0 | 0 | 0 | 0 | 7599.6 | 0 | 0 | 0 | 0 | 0 | 7599.6
2022102205 | 7 | 0.44302 | 35441.6 | 0.64307 | 23150.52 | 0 | 0 | 1 | 5000 | 23150.52 | 0 | 0 | 0 | 0 | 0 | 7291.08 | 0 | 0 | 0 | 0 | 0 | 7291.08
2022102206 | 7 | 0.44681 | 35744.8 | 0.64615 | 23261.4 | 0 | 0 | 1 | 5000 | 23261.4 | 0 | 0 | 0 | 0 | 0 | 7483.4 | 0 | 0 | 0 | 0 | 0 | 7483.4
2022102207 | 7 | 0.45844 | 36675.2 | 0.65039 | 23414.04 | 0 | 0 | 1 | 5000 | 23414.04 | 0 | 0 | 0 | 0 | 0 | 8261.16 | 0 | 0 | 0 | 0 | 0 | 8261.16
2022102208 | 7 | 0.46979 | 37583.2 | 0.6405 | 23058 | 0.00316 | 37.92 | 1 | 5000 | 23058 | 37.92 | 0 | 0 | 0 | 0 | 9487.28 | 0 | 0 | 0 | 0 | 0 | 9487.28
2022102209 | 7 | 0.48683 | 38946.4 | 0.6104 | 21974.4 | 0.15647 | 1877.64 | 1 | 5000 | 21974.4 | 1877.64 | 0 | 0 | 0 | 0 | 10094.36 | 0 | 0 | 0 | 0 | 0 | 10094.36
2022102210 | 7 | 0.51221 | 40976.8 | 0.53499 | 19259.64 | 0.45593 | 5471.16 | 1 | 5000 | 19259.64 | 5471.16 | 0 | 0 | 0 | 0 | 11246 | 0 | 0 | 0 | 0 | 0 | 11246
2022102211 | 7 | 0.53601 | 42880.8 | 0.52307 | 18830.52 | 0.59921 | 7190.52 | 1 | 5000 | 18830.52 | 7190.52 | 0 | 0 | 0 | 0 | 11859.76 | 0 | 0 | 0 | 0 | 0 | 11859.76
2022102212 | 7 | 0.5629 | 45032 | 0.52563 | 18922.68 | 0.62947 | 7553.64 | 1 | 5000 | 18922.68 | 7553.64 | 0 | 0 | 0 | 0 | 13555.68 | 0 | 0 | 0 | 0 | 0 | 13555.68
2022102213 | 7 | 0.59074 | 47259.2 | 0.53366 | 19211.76 | 0.65654 | 7878.48 | 1 | 5000 | 19211.76 | 7878.48 | 0 | 0 | 0 | 0 | 15168.96 | 0 | 0 | 0 | 0 | 0 | 15168.96
2022102214 | 7 | 0.61537 | 49229.6 | 0.55098 | 19835.28 | 0.64922 | 7790.64 | 1 | 5000 | 19835.28 | 7790.64 | 0 | 0 | 0 | 0 | 16603.68 | 0 | 0 | 0 | 0 | 0 | 16603.68
2022102215 | 7 | 0.63904 | 51123.2 | 0.56428 | 20314.08 | 0.61837 | 7420.44 | 1 | 5000 | 20314.08 | 7420.44 | 0 | 0 | 0 | 0 | 18388.68 | 0 | 0 | 0 | 0 | 0 | 18388.68
2022102216 | 7 | 0.65637 | 52509.6 | 0.57946 | 20860.56 | 0.58024 | 6962.88 | 1 | 5000 | 20860.56 | 6962.88 | 0 | 0 | 0 | 0 | 19686.16 | 0 | 0 | 0 | 0 | 0 | 19686.16
2022102217 | 7 | 0.66437 | 53149.6 | 0.6106 | 21981.6 | 0.4859 | 5830.8 | 1 | 5000 | 21981.6 | 5830.8 | 0 | 0 | 0 | 0 | 20337.2 | 0 | 0 | 0 | 0 | 0 | 20337.2
2022102218 | 7 | 0.65838 | 52670.4 | 0.62291 | 22424.76 | 0.35167 | 4220.04 | 1 | 5000 | 22424.76 | 4220.04 | 0 | 0 | 0 | 0 | 21025.6 | 0 | 0 | 0 | 0 | 0 | 21025.6
2022102219 | 7 | 0.63635 | 50908 | 0.61887 | 22279.32 | 0.08127 | 975.24 | 1 | 5000 | 22279.32 | 975.24 | 0 | 0 | 0 | 0 | 22653.44 | 0 | 0 | 0 | 0 | 0 | 22653.44
2022102220 | 7 | 0.63047 | 50437.6 | 0.66882 | 24077.52 | 0.0004 | 4.8 | 1 | 5000 | 24077.52 | 4.8 | 0 | 0 | 0 | 0 | 21355.28 | 0 | 0 | 0 | 0 | 0 | 21355.28
2022102221 | 7 | 0.61444 | 49155.2 | 0.69301 | 24948.36 | 0 | 0 | 1 | 5000 | 24948.36 | 0 | 0 | 0 | 0 | 0 | 19206.84 | 0 | 0 | 0 | 0 | 0 | 19206.84
2022102222 | 7 | 0.59395 | 47516 | 0.69897 | 25162.92 | 0 | 0 | 1 | 5000 | 25162.92 | 0 | 0 | 0 | 0 | 0 | 17353.08 | 0 | 0 | 0 | 0 | 0 | 17353.08
2022102223 | 7 | 0.57 | 45600 | 0.69285 | 24942.6 | 0 | 0 | 1 | 5000 | 24942.6 | 0 | 0 | 0 | 0 | 0 | 15657.4 | 0 | 0 | 0 | 0 | 0 | 15657.4
2022102224 | 7 | 0.54383 | 43506.4 | 0.6915 | 24894 | 0 | 0 | 1 | 5000 | 24894 | 0 | 0 | 0 | 0 | 0 | 13612.4 | 0 | 0 | 0 | 0 | 0 | 13612.4
2022102301 | 1 | 0.51582 | 41265.6 | 0.68162 | 24538.32 | 0 | 0 | 1 | 5000 | 24538.32 | 0 | 0 | 0 | 0 | 0 | 11727.28 | 0 | 0 | 0 | 0 | 0 | 11727.28
2022102302 | 1 | 0.49465 | 39572 | 0.67446 | 24280.56 | 0 | 0 | 1 | 5000 | 24280.56 | 0 | 0 | 0 | 0 | 0 | 10291.44 | 0 | 0 | 0 | 0 | 0 | 10291.44
2022102303 | 1 | 0.47832 | 38265.6 | 0.6662 | 23983.2 | 0 | 0 | 1 | 5000 | 23983.2 | 0 | 0 | 0 | 0 | 0 | 9282.4 | 0 | 0 | 0 | 0 | 0 | 9282.4
2022102304 | 1 | 0.4689 | 37512 | 0.66207 | 23834.52 | 0 | 0 | 1 | 5000 | 23834.52 | 0 | 0 | 0 | 0 | 0 | 8677.48 | 0 | 0 | 0 | 0 | 0 | 8677.48
2022102305 | 1 | 0.46302 | 37041.6 | 0.65598 | 23615.28 | 0 | 0 | 1 | 5000 | 23615.28 | 0 | 0 | 0 | 0 | 0 | 8426.32 | 0 | 0 | 0 | 0 | 0 | 8426.32
2022102306 | 1 | 0.46378 | 37102.4 | 0.6567 | 23641.2 | 0 | 0 | 1 | 5000 | 23641.2 | 0 | 0 | 0 | 0 | 0 | 8461.2 | 0 | 0 | 0 | 0 | 0 | 8461.2
2022102307 | 1 | 0.46991 | 37592.8 | 0.66132 | 23807.52 | 0 | 0 | 1 | 5000 | 23807.52 | 0 | 0 | 0 | 0 | 0 | 8785.28 | 0 | 0 | 0 | 0 | 0 | 8785.28
2022102308 | 1 | 0.47791 | 38232.8 | 0.66169 | 23820.84 | 0.00229 | 27.48 | 1 | 5000 | 23820.84 | 27.48 | 0 | 0 | 0 | 0 | 9384.48 | 0 | 0 | 0 | 0 | 0 | 9384.48
2022102309 | 1 | 0.49607 | 39685.6 | 0.64976 | 23391.36 | 0.09953 | 1194.36 | 1 | 5000 | 23391.36 | 1194.36 | 0 | 0 | 0 | 0 | 10099.88 | 0 | 0 | 0 | 0 | 0 | 10099.88
2022102310 | 1 | 0.52669 | 42135.2 | 0.63023 | 22688.28 | 0.30738 | 3688.56 | 1 | 5000 | 22688.28 | 3688.56 | 0 | 0 | 0 | 0 | 10758.36 | 0 | 0 | 0 | 0 | 0 | 10758.36
2022102311 | 1 | 0.55891 | 44712.8 | 0.66217 | 23838.12 | 0.32167 | 3860.04 | 1 | 5000 | 23838.12 | 3860.04 | 0 | 0 | 0 | 0 | 12014.64 | 0 | 0 | 0 | 0 | 0 | 12014.64
2022102312 | 1 | 0.59177 | 47341.6 | 0.66777 | 24039.72 | 0.29014 | 3481.68 | 1 | 5000 | 24039.72 | 3481.68 | 0 | 0 | 0 | 0 | 14820.2 | 0 | 0 | 0 | 0 | 0 | 14820.2
2022102313 | 1 | 0.61831 | 49464.8 | 0.67309 | 24231.24 | 0.30965 | 3715.8 | 1 | 5000 | 24231.24 | 3715.8 | 0 | 0 | 0 | 0 | 16517.76 | 0 | 0 | 0 | 0 | 0 | 16517.76
2022102314 | 1 | 0.64032 | 51225.6 | 0.67579 | 24328.44 | 0.31264 | 3751.68 | 1 | 5000 | 24328.44 | 3751.68 | 0 | 0 | 0 | 0 | 18145.48 | 0 | 0 | 0 | 0 | 0 | 18145.48
2022102315 | 1 | 0.66096 | 52876.8 | 0.6753 | 24310.8 | 0.31006 | 3720.72 | 1 | 5000 | 24310.8 | 3720.72 | 0 | 0 | 0 | 0 | 19845.28 | 0 | 0 | 0 | 0 | 0 | 19845.28
2022102316 | 1 | 0.67637 | 54109.6 | 0.6758 | 24328.8 | 0.29878 | 3585.36 | 1 | 5000 | 24328.8 | 3585.36 | 0 | 0 | 0 | 0 | 21195.44 | 0 | 0 | 0 | 0 | 0 | 21195.44
2022102317 | 1 | 0.68385 | 54708 | 0.67844 | 24423.84 | 0.27211 | 3265.32 | 1 | 5000 | 24423.84 | 3265.32 | 0 | 0 | 0 | 0 | 22018.84 | 0 | 0 | 0 | 0 | 0 | 22018.84
2022102318 | 1 | 0.68003 | 54402.4 | 0.68126 | 24525.36 | 0.17367 | 2084.04 | 1 | 5000 | 24525.36 | 2084.04 | 0 | 0 | 0 | 0 | 22793 | 0 | 0 | 0 | 0 | 0 | 22793
2022102319 | 1 | 0.66659 | 53327.2 | 0.694 | 24984 | 0.04064 | 487.68 | 1 | 5000 | 24984 | 487.68 | 0 | 0 | 0 | 0 | 22855.52 | 0 | 0 | 0 | 0 | 0 | 22855.52
2022102320 | 1 | 0.66692 | 53353.6 | 0.70734 | 25464.24 | 0.00022 | 2.64 | 1 | 5000 | 25464.24 | 2.64 | 0 | 0 | 0 | 0 | 22886.72 | 0 | 0 | 0 | 0 | 0 | 22886.72
2022102321 | 1 | 0.65374 | 52299.2 | 0.70573 | 25406.28 | 0 | 0 | 1 | 5000 | 25406.28 | 0 | 0 | 0 | 0 | 0 | 21892.92 | 0 | 0 | 0 | 0 | 0 | 21892.92
2022102322 | 1 | 0.63173 | 50538.4 | 0.70174 | 25262.64 | 0 | 0 | 1 | 5000 | 25262.64 | 0 | 0 | 0 | 0 | 0 | 20275.76 | 0 | 0 | 0 | 0 | 0 | 20275.76
2022102323 | 1 | 0.60274 | 48219.2 | 0.70196 | 25270.56 | 0 | 0 | 1 | 5000 | 25270.56 | 0 | 0 | 0 | 0 | 0 | 17948.64 | 0 | 0 | 0 | 0 | 0 | 17948.64
2022102324 | 1 | 0.56916 | 45532.8 | 0.69139 | 24890.04 | 0 | 0 | 1 | 5000 | 24890.04 | 0 | 0 | 0 | 0 | 0 | 15642.76 | 0 | 0 | 0 | 0 | 0 | 15642.76
2022102401 | 2 | 0.54121 | 43296.8 | 0.68101 | 24516.36 | 0 | 0 | 1 | 5000 | 24516.36 | 0 | 0 | 0 | 0 | 0 | 13780.44 | 0 | 0 | 0 | 0 | 0 | 13780.44
2022102402 | 2 | 0.5213 | 41704 | 0.67176 | 24183.36 | 0 | 0 | 1 | 5000 | 24183.36 | 0 | 0 | 0 | 0 | 0 | 12520.64 | 0 | 0 | 0 | 0 | 0 | 12520.64
2022102403 | 2 | 0.51073 | 40858.4 | 0.66479 | 23932.44 | 0 | 0 | 1 | 5000 | 23932.44 | 0 | 0 | 0 | 0 | 0 | 11925.96 | 0 | 0 | 0 | 0 | 0 | 11925.96
2022102404 | 2 | 0.50592 | 40473.6 | 0.64092 | 23073.12 | 0 | 0 | 1 | 5000 | 23073.12 | 0 | 0 | 0 | 0 | 0 | 12400.48 | 0 | 0 | 0 | 0 | 0 | 12400.48
2022102405 | 2 | 0.50893 | 40714.4 | 0.63752 | 22950.72 | 0 | 0 | 1 | 5000 | 22950.72 | 0 | 0 | 0 | 0 | 0 | 12763.68 | 0 | 0 | 0 | 0 | 0 | 12763.68
2022102406 | 2 | 0.52734 | 42187.2 | 0.58738 | 21145.68 | 0 | 0 | 1 | 5000 | 21145.68 | 0 | 0 | 0 | 0 | 0 | 16041.52 | 0 | 0 | 0 | 0 | 0 | 16041.52
2022102407 | 2 | 0.56009 | 44807.2 | 0.558 | 20088 | 0 | 0 | 1 | 5000 | 20088 | 0 | 0 | 0 | 0 | 0 | 19719.2 | 0 | 0 | 0 | 0 | 0 | 19719.2
2022102408 | 2 | 0.57446 | 45956.8 | 0.41173 | 14822.28 | 0.00065 | 7.8 | 1 | 5000 | 14822.28 | 7.8 | 0 | 0 | 0 | 0 | 26126.72 | 0 | 0 | 0 | 0 | 0 | 26126.72
2022102409 | 2 | 0.57647 | 46117.6 | 0.32967 | 11868.12 | 0.06722 | 806.64 | 1 | 5000 | 11868.12 | 806.64 | 0 | 0 | 0 | 0 | 28442.84 | 0 | 0 | 0 | 0 | 0 | 28442.84
2022102410 | 2 | 0.59 | 47200 | 0.29335 | 10560.6 | 0.26712 | 3205.44 | 1 | 5000 | 10560.6 | 3205.44 | 0 | 0 | 0 | 0 | 28433.96 | 0 | 0 | 0 | 0 | 0 | 28433.96
2022102411 | 2 | 0.60355 | 48284 | 0.28445 | 10240.2 | 0.41102 | 4932.24 | 1 | 5000 | 10240.2 | 4932.24 | 0 | 0 | 0 | 0 | 28111.56 | 0 | 0 | 0 | 0 | 0 | 28111.56
2022102412 | 2 | 0.61222 | 48977.6 | 0.29215 | 10517.4 | 0.45889 | 5506.68 | 1 | 5000 | 10517.4 | 5506.68 | 0 | 0 | 0 | 0 | 27953.52 | 0 | 0 | 0 | 0 | 0 | 27953.52
2022102413 | 2 | 0.61533 | 49226.4 | 0.29964 | 10787.04 | 0.47072 | 5648.64 | 1 | 5000 | 10787.04 | 5648.64 | 0 | 0 | 0 | 0 | 27790.72 | 0 | 0 | 0 | 0 | 0 | 27790.72
2022102414 | 2 | 0.61977 | 49581.6 | 0.31079 | 11188.44 | 0.40078 | 4809.36 | 1 | 5000 | 11188.44 | 4809.36 | 0 | 0 | 0 | 0 | 28583.8 | 0 | 0 | 0 | 0 | 0 | 28583.8
2022102415 | 2 | 0.62366 | 49892.8 | 0.34605 | 12457.8 | 0.38452 | 4614.24 | 1 | 5000 | 12457.8 | 4614.24 | 0 | 0 | 0 | 0 | 27820.76 | 0 | 0 | 0 | 0 | 0 | 27820.76
2022102416 | 2 | 0.63178 | 50542.4 | 0.41166 | 14819.76 | 0.39516 | 4741.92 | 1 | 5000 | 14819.76 | 4741.92 | 0 | 0 | 0 | 0 | 25980.72 | 0 | 0 | 0 | 0 | 0 | 25980.72
2022102417 | 2 | 0.63901 | 51120.8 | 0.48882 | 17597.52 | 0.27717 | 3326.04 | 1 | 5000 | 17597.52 | 3326.04 | 0 | 0 | 0 | 0 | 25197.24 | 0 | 0 | 0 | 0 | 0 | 25197.24
2022102418 | 2 | 0.64106 | 51284.8 | 0.51252 | 18450.72 | 0.23496 | 2819.52 | 1 | 5000 | 18450.72 | 2819.52 | 0 | 0 | 0 | 0 | 25014.56 | 0 | 0 | 0 | 0 | 0 | 25014.56
2022102419 | 2 | 0.63821 | 51056.8 | 0.56352 | 20286.72 | 0.08186 | 982.32 | 1 | 5000 | 20286.72 | 982.32 | 0 | 0 | 0 | 0 | 24787.76 | 0 | 0 | 0 | 0 | 0 | 24787.76
2022102420 | 2 | 0.64243 | 51394.4 | 0.60018 | 21606.48 | 0.0035 | 42 | 1 | 5000 | 21606.48 | 42 | 0 | 0 | 0 | 0 | 24745.92 | 0 | 0 | 0 | 0 | 0 | 24745.92
2022102421 | 2 | 0.62927 | 50341.6 | 0.61921 | 22291.56 | 0 | 0 | 1 | 5000 | 22291.56 | 0 | 0 | 0 | 0 | 0 | 23050.04 | 0 | 0 | 0 | 0 | 0 | 23050.04
2022102422 | 2 | 0.60126 | 48100.8 | 0.61895 | 22282.2 | 0 | 0 | 1 | 5000 | 22282.2 | 0 | 0 | 0 | 0 | 0 | 20818.6 | 0 | 0 | 0 | 0 | 0 | 20818.6
2022102423 | 2 | 0.55515 | 44412 | 0.62185 | 22386.6 | 0 | 0 | 1 | 5000 | 22386.6 | 0 | 0 | 0 | 0 | 0 | 17025.4 | 0 | 0 | 0 | 0 | 0 | 17025.4
2022102424 | 2 | 0.51776 | 41420.8 | 0.62158 | 22376.88 | 0 | 0 | 1 | 5000 | 22376.88 | 0 | 0 | 0 | 0 | 0 | 14043.92 | 0 | 0 | 0 | 0 | 0 | 14043.92
2022102501 | 3 | 0.48549 | 38839.2 | 0.60343 | 21723.48 | 0 | 0 | 1 | 5000 | 21723.48 | 0 | 0 | 0 | 0 | 0 | 12115.72 | 0 | 0 | 0 | 0 | 0 | 12115.72
2022102502 | 3 | 0.45243 | 36194.4 | 0.56495 | 20338.2 | 0 | 0 | 1 | 5000 | 20338.2 | 0 | 0 | 0 | 0 | 0 | 10856.2 | 0 | 0 | 0 | 0 | 0 | 10856.2
2022102503 | 3 | 0.43443 | 34754.4 | 0.53249 | 19169.64 | 0 | 0 | 1 | 5000 | 19169.64 | 0 | 0 | 0 | 0 | 0 | 10584.76 | 0 | 0 | 0 | 0 | 0 | 10584.76
2022102504 | 3 | 0.42466 | 33972.8 | 0.4974 | 17906.4 | 0 | 0 | 1 | 5000 | 17906.4 | 0 | 0 | 0 | 0 | 0 | 11066.4 | 0 | 0 | 0 | 0 | 0 | 11066.4
2022102505 | 3 | 0.42572 | 34057.6 | 0.47429 | 17074.44 | 0 | 0 | 1 | 5000 | 17074.44 | 0 | 0 | 0 | 0 | 0 | 11983.16 | 0 | 0 | 0 | 0 | 0 | 11983.16
2022102506 | 3 | 0.44561 | 35648.8 | 0.46192 | 16629.12 | 0 | 0 | 1 | 5000 | 16629.12 | 0 | 0 | 0 | 0 | 0 | 14019.68 | 0 | 0 | 0 | 0 | 0 | 14019.68
2022102507 | 3 | 0.47835 | 38268 | 0.45476 | 16371.36 | 0 | 0 | 1 | 5000 | 16371.36 | 0 | 0 | 0 | 0 | 0 | 16896.64 | 0 | 0 | 0 | 0 | 0 | 16896.64
2022102508 | 3 | 0.49257 | 39405.6 | 0.42247 | 15208.92 | 0.00182 | 21.84 | 1 | 5000 | 15208.92 | 21.84 | 0 | 0 | 0 | 0 | 19174.84 | 0 | 0 | 0 | 0 | 0 | 19174.84
2022102509 | 3 | 0.49112 | 39289.6 | 0.38978 | 14032.08 | 0.16748 | 2009.76 | 1 | 5000 | 14032.08 | 2009.76 | 0 | 0 | 0 | 0 | 18247.76 | 0 | 0 | 0 | 0 | 0 | 18247.76
2022102510 | 3 | 0.49556 | 39644.8 | 0.30134 | 10848.24 | 0.61245 | 7349.4 | 1 | 5000 | 10848.24 | 7349.4 | 0 | 0 | 0 | 0 | 16447.16 | 0 | 0 | 0 | 0 | 0 | 16447.16
2022102511 | 3 | 0.50037 | 40029.6 | 0.26112 | 9400.32 | 0.75028 | 9003.36 | 1 | 5000 | 9400.32 | 9003.36 | 0 | 0 | 0 | 0 | 16625.92 | 0 | 0 | 0 | 0 | 0 | 16625.92
2022102512 | 3 | 0.50363 | 40290.4 | 0.23463 | 8446.68 | 0.76857 | 9222.84 | 1 | 5000 | 8446.68 | 9222.84 | 0 | 0 | 0 | 0 | 17620.88 | 0 | 0 | 0 | 0 | 0 | 17620.88
2022102513 | 3 | 0.50865 | 40692 | 0.1907 | 6865.2 | 0.76223 | 9146.76 | 1 | 5000 | 6865.2 | 9146.76 | 0 | 0 | 0 | 0 | 19680.04 | 0 | 0 | 0 | 0 | 0 | 19680.04
2022102514 | 3 | 0.51603 | 41282.4 | 0.14379 | 5176.44 | 0.75656 | 9078.72 | 1 | 5000 | 5176.44 | 9078.72 | 0 | 0 | 0 | 0 | 22027.24 | 0 | 0 | 0 | 0 | 0 | 22027.24
2022102515 | 3 | 0.52286 | 41828.8 | 0.10899 | 3923.64 | 0.76674 | 9200.88 | 1 | 5000 | 3923.64 | 9200.88 | 0 | 0 | 0 | 0 | 23704.28 | 0 | 0 | 0 | 0 | 0 | 23704.28
2022102516 | 3 | 0.53608 | 42886.4 | 0.07281 | 2621.16 | 0.78107 | 9372.84 | 1 | 5000 | 2621.16 | 9372.84 | 0 | 0 | 0 | 0 | 25892.4 | 0 | 0 | 0 | 0 | 0 | 25892.4
2022102517 | 3 | 0.54593 | 43674.4 | 0.04024 | 1448.64 | 0.77005 | 9240.6 | 1 | 5000 | 1448.64 | 9240.6 | 0 | 0 | 0 | 0 | 27985.16 | 0 | 0 | 0 | 0 | 0 | 27985.16
2022102518 | 3 | 0.54968 | 43974.4 | 0.0227 | 817.2 | 0.58777 | 7053.24 | 1 | 5000 | 817.2 | 7053.24 | 0 | 0 | 0 | 0 | 31103.96 | 0 | 0 | 0 | 0 | 0 | 31103.96
2022102519 | 3 | 0.54097 | 43277.6 | 0.01791 | 644.76 | 0.14023 | 1682.76 | 1 | 5000 | 644.76 | 1682.76 | 0 | 0 | 0 | 0 | 35950.08 | 0 | 0 | 0 | 0 | 0 | 35950.08
2022102520 | 3 | 0.54046 | 43236.8 | 0.03044 | 1095.84 | 0.00267 | 32.04 | 1 | 5000 | 1095.84 | 32.04 | 0 | 0 | 0 | 0 | 37108.92 | 0 | 0 | 0 | 0 | 0 | 37108.92
2022102521 | 3 | 0.53467 | 42773.6 | 0.04844 | 1743.84 | 0.00243 | 29.16 | 1 | 5000 | 1743.84 | 29.16 | 0 | 0 | 0 | 0 | 36000.6 | 0 | 0 | 0 | 0 | 0 | 36000.6
2022102522 | 3 | 0.51542 | 41233.6 | 0.06876 | 2475.36 | 0.0006 | 7.2 | 1 | 5000 | 2475.36 | 7.2 | 0 | 0 | 0 | 0 | 33751.04 | 0 | 0 | 0 | 0 | 0 | 33751.04
2022102523 | 3 | 0.48318 | 38654.4 | 0.09441 | 3398.76 | 0 | 0 | 1 | 5000 | 3398.76 | 0 | 0 | 0 | 0 | 0 | 30255.64 | 0 | 0 | 0 | 0 | 0 | 30255.64
2022102524 | 3 | 0.45297 | 36237.6 | 0.12719 | 4578.84 | 0 | 0 | 1 | 5000 | 4578.84 | 0 | 0 | 0 | 0 | 0 | 26658.76 | 0 | 0 | 0 | 0 | 0 | 26658.76
2022102601 | 4 | 0.43281 | 34624.8 | 0.15301 | 5508.36 | 0 | 0 | 1 | 5000 | 5508.36 | 0 | 0 | 0 | 0 | 0 | 24116.44 | 0 | 0 | 0 | 0 | 0 | 24116.44
2022102602 | 4 | 0.42067 | 33653.6 | 0.18751 | 6750.36 | 0 | 0 | 1 | 5000 | 6750.36 | 0 | 0 | 0 | 0 | 0 | 21903.24 | 0 | 0 | 0 | 0 | 0 | 21903.24
2022102603 | 4 | 0.4144 | 33152 | 0.22373 | 8054.28 | 0 | 0 | 1 | 5000 | 8054.28 | 0 | 0 | 0 | 0 | 0 | 20097.72 | 0 | 0 | 0 | 0 | 0 | 20097.72
2022102604 | 4 | 0.41422 | 33137.6 | 0.23541 | 8474.76 | 0 | 0 | 1 | 5000 | 8474.76 | 0 | 0 | 0 | 0 | 0 | 19662.84 | 0 | 0 | 0 | 0 | 0 | 19662.84
2022102605 | 4 | 0.41954 | 33563.2 | 0.22707 | 8174.52 | 0 | 0 | 1 | 5000 | 8174.52 | 0 | 0 | 0 | 0 | 0 | 20388.68 | 0 | 0 | 0 | 0 | 0 | 20388.68
2022102606 | 4 | 0.44306 | 35444.8 | 0.23096 | 8314.56 | 0 | 0 | 1 | 5000 | 8314.56 | 0 | 0 | 0 | 0 | 0 | 22130.24 | 0 | 0 | 0 | 0 | 0 | 22130.24
2022102607 | 4 | 0.48105 | 38484 | 0.24746 | 8908.56 | 0 | 0 | 1 | 5000 | 8908.56 | 0 | 0 | 0 | 0 | 0 | 24575.44 | 0 | 0 | 0 | 0 | 0 | 24575.44
2022102608 | 4 | 0.50272 | 40217.6 | 0.26367 | 9492.12 | 0.0027 | 32.4 | 1 | 5000 | 9492.12 | 32.4 | 0 | 0 | 0 | 0 | 25693.08 | 0 | 0 | 0 | 0 | 0 | 25693.08
2022102609 | 4 | 0.50348 | 40278.4 | 0.26805 | 9649.8 | 0.19732 | 2367.84 | 1 | 5000 | 9649.8 | 2367.84 | 0 | 0 | 0 | 0 | 23260.76 | 0 | 0 | 0 | 0 | 0 | 23260.76
2022102610 | 4 | 0.50335 | 40268 | 0.2162 | 7783.2 | 0.64546 | 7745.52 | 1 | 5000 | 7783.2 | 7745.52 | 0 | 0 | 0 | 0 | 19739.28 | 0 | 0 | 0 | 0 | 0 | 19739.28
2022102611 | 4 | 0.5036 | 40288 | 0.18617 | 6702.12 | 0.75794 | 9095.28 | 1 | 5000 | 6702.12 | 9095.28 | 0 | 0 | 0 | 0 | 19490.6 | 0 | 0 | 0 | 0 | 0 | 19490.6
2022102612 | 4 | 0.50642 | 40513.6 | 0.28325 | 10197 | 0.7076 | 8491.2 | 1 | 5000 | 10197 | 8491.2 | 0 | 0 | 0 | 0 | 16825.4 | 0 | 0 | 0 | 0 | 0 | 16825.4
2022102613 | 4 | 0.51046 | 40836.8 | 0.3468 | 12484.8 | 0.61075 | 7329 | 1 | 5000 | 12484.8 | 7329 | 0 | 0 | 0 | 0 | 16023 | 0 | 0 | 0 | 0 | 0 | 16023
2022102614 | 4 | 0.5201 | 41608 | 0.3622 | 13039.2 | 0.64539 | 7744.68 | 1 | 5000 | 13039.2 | 7744.68 | 0 | 0 | 0 | 0 | 15824.12 | 0 | 0 | 0 | 0 | 0 | 15824.12
2022102615 | 4 | 0.53024 | 42419.2 | 0.36672 | 13201.92 | 0.66178 | 7941.36 | 1 | 5000 | 13201.92 | 7941.36 | 0 | 0 | 0 | 0 | 16275.92 | 0 | 0 | 0 | 0 | 0 | 16275.92
2022102616 | 4 | 0.54384 | 43507.2 | 0.36937 | 13297.32 | 0.68253 | 8190.36 | 1 | 5000 | 13297.32 | 8190.36 | 0 | 0 | 0 | 0 | 17019.52 | 0 | 0 | 0 | 0 | 0 | 17019.52
2022102617 | 4 | 0.55562 | 44449.6 | 0.38596 | 13894.56 | 0.64485 | 7738.2 | 1 | 5000 | 13894.56 | 7738.2 | 0 | 0 | 0 | 0 | 17816.84 | 0 | 0 | 0 | 0 | 0 | 17816.84
2022102618 | 4 | 0.5577 | 44616 | 0.39372 | 14173.92 | 0.5018 | 6021.6 | 1 | 5000 | 14173.92 | 6021.6 | 0 | 0 | 0 | 0 | 19420.48 | 0 | 0 | 0 | 0 | 0 | 19420.48
2022102619 | 4 | 0.55093 | 44074.4 | 0.37677 | 13563.72 | 0.13249 | 1589.88 | 1 | 5000 | 13563.72 | 1589.88 | 0 | 0 | 0 | 0 | 23920.8 | 0 | 0 | 0 | 0 | 0 | 23920.8
2022102620 | 4 | 0.55198 | 44158.4 | 0.42525 | 15309 | 0.01072 | 128.64 | 1 | 5000 | 15309 | 128.64 | 0 | 0 | 0 | 0 | 23720.76 | 0 | 0 | 0 | 0 | 0 | 23720.76
2022102621 | 4 | 0.54292 | 43433.6 | 0.50492 | 18177.12 | 0 | 0 | 1 | 5000 | 18177.12 | 0 | 0 | 0 | 0 | 0 | 20256.48 | 0 | 0 | 0 | 0 | 0 | 20256.48
2022102622 | 4 | 0.52469 | 41975.2 | 0.52902 | 19044.72 | 0 | 0 | 1 | 5000 | 19044.72 | 0 | 0 | 0 | 0 | 0 | 17930.48 | 0 | 0 | 0 | 0 | 0 | 17930.48
2022102623 | 4 | 0.49274 | 39419.2 | 0.53196 | 19150.56 | 0 | 0 | 1 | 5000 | 19150.56 | 0 | 0 | 0 | 0 | 0 | 15268.64 | 0 | 0 | 0 | 0 | 0 | 15268.64
2022102624 | 4 | 0.46151 | 36920.8 | 0.53243 | 19167.48 | 0 | 0 | 1 | 5000 | 19167.48 | 0 | 0 | 0 | 0 | 0 | 12753.32 | 0 | 0 | 0 | 0 | 0 | 12753.32
2022102701 | 5 | 0.43944 | 35155.2 | 0.53965 | 19427.4 | 0 | 0 | 1 | 5000 | 19427.4 | 0 | 0 | 0 | 0 | 0 | 10727.8 | 0 | 0 | 0 | 0 | 0 | 10727.8
2022102702 | 5 | 0.42712 | 34169.6 | 0.54293 | 19545.48 | 0 | 0 | 1 | 5000 | 19545.48 | 0 | 0 | 0 | 0 | 0 | 9624.12 | 0 | 0 | 0 | 0 | 0 | 9624.12
2022102703 | 5 | 0.42029 | 33623.2 | 0.53918 | 19410.48 | 0 | 0 | 1 | 5000 | 19410.48 | 0 | 0 | 0 | 0 | 0 | 9212.72 | 0 | 0 | 0 | 0 | 0 | 9212.72
2022102704 | 5 | 0.41683 | 33346.4 | 0.53371 | 19213.56 | 0 | 0 | 1 | 5000 | 19213.56 | 0 | 0 | 0 | 0 | 0 | 9132.84 | 0 | 0 | 0 | 0 | 0 | 9132.84
2022102705 | 5 | 0.4243 | 33944 | 0.53009 | 19083.24 | 0 | 0 | 1 | 5000 | 19083.24 | 0 | 0 | 0 | 0 | 0 | 9860.76 | 0 | 0 | 0 | 0 | 0 | 9860.76
2022102706 | 5 | 0.44702 | 35761.6 | 0.53042 | 19095.12 | 0 | 0 | 1 | 5000 | 19095.12 | 0 | 0 | 0 | 0 | 0 | 11666.48 | 0 | 0 | 0 | 0 | 0 | 11666.48
2022102707 | 5 | 0.48394 | 38715.2 | 0.52548 | 18917.28 | 0 | 0 | 1 | 5000 | 18917.28 | 0 | 0 | 0 | 0 | 0 | 14797.92 | 0 | 0 | 0 | 0 | 0 | 14797.92
2022102708 | 5 | 0.50271 | 40216.8 | 0.52648 | 18953.28 | 0.00231 | 27.72 | 1 | 5000 | 18953.28 | 27.72 | 0 | 0 | 0 | 0 | 16235.8 | 0 | 0 | 0 | 0 | 0 | 16235.8
2022102709 | 5 | 0.50413 | 40330.4 | 0.51477 | 18531.72 | 0.1309 | 1570.8 | 1 | 5000 | 18531.72 | 1570.8 | 0 | 0 | 0 | 0 | 15227.88 | 0 | 0 | 0 | 0 | 0 | 15227.88
2022102710 | 5 | 0.50897 | 40717.6 | 0.46686 | 16806.96 | 0.37768 | 4532.16 | 1 | 5000 | 16806.96 | 4532.16 | 0 | 0 | 0 | 0 | 14378.48 | 0 | 0 | 0 | 0 | 0 | 14378.48
2022102711 | 5 | 0.51235 | 40988 | 0.49199 | 17711.64 | 0.42331 | 5079.72 | 1 | 5000 | 17711.64 | 5079.72 | 0 | 0 | 0 | 0 | 13196.64 | 0 | 0 | 0 | 0 | 0 | 13196.64
2022102712 | 5 | 0.51715 | 41372 | 0.50552 | 18198.72 | 0.40947 | 4913.64 | 1 | 5000 | 18198.72 | 4913.64 | 0 | 0 | 0 | 0 | 13259.64 | 0 | 0 | 0 | 0 | 0 | 13259.64
2022102713 | 5 | 0.52256 | 41804.8 | 0.50453 | 18163.08 | 0.41724 | 5006.88 | 1 | 5000 | 18163.08 | 5006.88 | 0 | 0 | 0 | 0 | 13634.84 | 0 | 0 | 0 | 0 | 0 | 13634.84
2022102714 | 5 | 0.53296 | 42636.8 | 0.50522 | 18187.92 | 0.41515 | 4981.8 | 1 | 5000 | 18187.92 | 4981.8 | 0 | 0 | 0 | 0 | 14467.08 | 0 | 0 | 0 | 0 | 0 | 14467.08
2022102715 | 5 | 0.54479 | 43583.2 | 0.49431 | 17795.16 | 0.44675 | 5361 | 1 | 5000 | 17795.16 | 5361 | 0 | 0 | 0 | 0 | 15427.04 | 0 | 0 | 0 | 0 | 0 | 15427.04
2022102716 | 5 | 0.55537 | 44429.6 | 0.47084 | 16950.24 | 0.45142 | 5417.04 | 1 | 5000 | 16950.24 | 5417.04 | 0 | 0 | 0 | 0 | 17062.32 | 0 | 0 | 0 | 0 | 0 | 17062.32
2022102717 | 5 | 0.5637 | 45096 | 0.44683 | 16085.88 | 0.42638 | 5116.56 | 1 | 5000 | 16085.88 | 5116.56 | 0 | 0 | 0 | 0 | 18893.56 | 0 | 0 | 0 | 0 | 0 | 18893.56
2022102718 | 5 | 0.56062 | 44849.6 | 0.43387 | 15619.32 | 0.32445 | 3893.4 | 1 | 5000 | 15619.32 | 3893.4 | 0 | 0 | 0 | 0 | 20336.88 | 0 | 0 | 0 | 0 | 0 | 20336.88
2022102719 | 5 | 0.55684 | 44547.2 | 0.43163 | 15538.68 | 0.08502 | 1020.24 | 1 | 5000 | 15538.68 | 1020.24 | 0 | 0 | 0 | 0 | 22988.28 | 0 | 0 | 0 | 0 | 0 | 22988.28
2022102720 | 5 | 0.56231 | 44984.8 | 0.4779 | 17204.4 | 0.00033 | 3.96 | 1 | 5000 | 17204.4 | 3.96 | 0 | 0 | 0 | 0 | 22776.44 | 0 | 0 | 0 | 0 | 0 | 22776.44
2022102721 | 5 | 0.55949 | 44759.2 | 0.54329 | 19558.44 | 0 | 0 | 1 | 5000 | 19558.44 | 0 | 0 | 0 | 0 | 0 | 20200.76 | 0 | 0 | 0 | 0 | 0 | 20200.76
2022102722 | 5 | 0.54292 | 43433.6 | 0.55569 | 20004.84 | 0 | 0 | 1 | 5000 | 20004.84 | 0 | 0 | 0 | 0 | 0 | 18428.76 | 0 | 0 | 0 | 0 | 0 | 18428.76
2022102723 | 5 | 0.51414 | 41131.2 | 0.52391 | 18860.76 | 4e-05 | 0.48 | 1 | 5000 | 18860.76 | 0.48 | 0 | 0 | 0 | 0 | 17269.96 | 0 | 0 | 0 | 0 | 0 | 17269.96
2022102724 | 5 | 0.4804 | 38432 | 0.45862 | 16510.32 | 4e-05 | 0.48 | 1 | 5000 | 16510.32 | 0.48 | 0 | 0 | 0 | 0 | 16921.2 | 0 | 0 | 0 | 0 | 0 | 16921.2
2022102801 | 6 | 0.45495 | 36396 | 0.40381 | 14537.16 | 4e-05 | 0.48 | 1 | 5000 | 14537.16 | 0.48 | 0 | 0 | 0 | 0 | 16858.36 | 0 | 0 | 0 | 0 | 0 | 16858.36
2022102802 | 6 | 0.43965 | 35172 | 0.39065 | 14063.4 | 0 | 0 | 1 | 5000 | 14063.4 | 0 | 0 | 0 | 0 | 0 | 16108.6 | 0 | 0 | 0 | 0 | 0 | 16108.6
2022102803 | 6 | 0.43127 | 34501.6 | 0.38592 | 13893.12 | 4e-05 | 0.48 | 1 | 5000 | 13893.12 | 0.48 | 0 | 0 | 0 | 0 | 15608 | 0 | 0 | 0 | 0 | 0 | 15608
2022102804 | 6 | 0.42531 | 34024.8 | 0.33737 | 12145.32 | 4e-05 | 0.48 | 1 | 5000 | 12145.32 | 0.48 | 0 | 0 | 0 | 0 | 16879 | 0 | 0 | 0 | 0 | 0 | 16879
2022102805 | 6 | 0.43395 | 34716 | 0.38567 | 13884.12 | 0 | 0 | 1 | 5000 | 13884.12 | 0 | 0 | 0 | 0 | 0 | 15831.88 | 0 | 0 | 0 | 0 | 0 | 15831.88
2022102806 | 6 | 0.45359 | 36287.2 | 0.4233 | 15238.8 | 0 | 0 | 1 | 5000 | 15238.8 | 0 | 0 | 0 | 0 | 0 | 16048.4 | 0 | 0 | 0 | 0 | 0 | 16048.4
2022102807 | 6 | 0.48742 | 38993.6 | 0.44376 | 15975.36 | 4e-05 | 0.48 | 1 | 5000 | 15975.36 | 0.48 | 0 | 0 | 0 | 0 | 18017.76 | 0 | 0 | 0 | 0 | 0 | 18017.76
2022102808 | 6 | 0.50684 | 40547.2 | 0.40065 | 14423.4 | 0.00013 | 1.56 | 1 | 5000 | 14423.4 | 1.56 | 0 | 0 | 0 | 0 | 21122.24 | 0 | 0 | 0 | 0 | 0 | 21122.24
2022102809 | 6 | 0.5126 | 41008 | 0.37241 | 13406.76 | 0.03587 | 430.44 | 1 | 5000 | 13406.76 | 430.44 | 0 | 0 | 0 | 0 | 22170.8 | 0 | 0 | 0 | 0 | 0 | 22170.8
2022102810 | 6 | 0.52803 | 42242.4 | 0.37495 | 13498.2 | 0.21761 | 2611.32 | 1 | 5000 | 13498.2 | 2611.32 | 0 | 0 | 0 | 0 | 21132.88 | 0 | 0 | 0 | 0 | 0 | 21132.88
2022102811 | 6 | 0.53839 | 43071.2 | 0.39145 | 14092.2 | 0.30169 | 3620.28 | 1 | 5000 | 14092.2 | 3620.28 | 0 | 0 | 0 | 0 | 20358.72 | 0 | 0 | 0 | 0 | 0 | 20358.72
2022102812 | 6 | 0.53922 | 43137.6 | 0.37568 | 13524.48 | 0.2592 | 3110.4 | 1 | 5000 | 13524.48 | 3110.4 | 0 | 0 | 0 | 0 | 21502.72 | 0 | 0 | 0 | 0 | 0 | 21502.72
2022102813 | 6 | 0.5441 | 43528 | 0.41368 | 14892.48 | 0.28493 | 3419.16 | 1 | 5000 | 14892.48 | 3419.16 | 0 | 0 | 0 | 0 | 20216.36 | 0 | 0 | 0 | 0 | 0 | 20216.36
2022102814 | 6 | 0.55016 | 44012.8 | 0.475 | 17100 | 0.2768 | 3321.6 | 1 | 5000 | 17100 | 3321.6 | 0 | 0 | 0 | 0 | 18591.2 | 0 | 0 | 0 | 0 | 0 | 18591.2
2022102815 | 6 | 0.54748 | 43798.4 | 0.52714 | 18977.04 | 0.31414 | 3769.68 | 1 | 5000 | 18977.04 | 3769.68 | 0 | 0 | 0 | 0 | 16051.68 | 0 | 0 | 0 | 0 | 0 | 16051.68
2022102816 | 6 | 0.54659 | 43727.2 | 0.56265 | 20255.4 | 0.30264 | 3631.68 | 1 | 5000 | 20255.4 | 3631.68 | 0 | 0 | 0 | 0 | 14840.12 | 0 | 0 | 0 | 0 | 0 | 14840.12
2022102817 | 6 | 0.54714 | 43771.2 | 0.56169 | 20220.84 | 0.23917 | 2870.04 | 1 | 5000 | 20220.84 | 2870.04 | 0 | 0 | 0 | 0 | 15680.32 | 0 | 0 | 0 | 0 | 0 | 15680.32
2022102818 | 6 | 0.545 | 43600 | 0.54183 | 19505.88 | 0.18652 | 2238.24 | 1 | 5000 | 19505.88 | 2238.24 | 0 | 0 | 0 | 0 | 16855.88 | 0 | 0 | 0 | 0 | 0 | 16855.88
2022102819 | 6 | 0.54405 | 43524 | 0.52741 | 18986.76 | 0.04962 | 595.44 | 1 | 5000 | 18986.76 | 595.44 | 0 | 0 | 0 | 0 | 18941.8 | 0 | 0 | 0 | 0 | 0 | 18941.8
2022102820 | 6 | 0.53999 | 43199.2 | 0.46365 | 16691.4 | 9e-05 | 1.08 | 1 | 5000 | 16691.4 | 1.08 | 0 | 0 | 0 | 0 | 21506.72 | 0 | 0 | 0 | 0 | 0 | 21506.72
2022102821 | 6 | 0.52485 | 41988 | 0.42142 | 15171.12 | 0 | 0 | 1 | 5000 | 15171.12 | 0 | 0 | 0 | 0 | 0 | 21816.88 | 0 | 0 | 0 | 0 | 0 | 21816.88
2022102822 | 6 | 0.50718 | 40574.4 | 0.36006 | 12962.16 | 0 | 0 | 1 | 5000 | 12962.16 | 0 | 0 | 0 | 0 | 0 | 22612.24 | 0 | 0 | 0 | 0 | 0 | 22612.24
2022102823 | 6 | 0.48518 | 38814.4 | 0.31503 | 11341.08 | 0 | 0 | 1 | 5000 | 11341.08 | 0 | 0 | 0 | 0 | 0 | 22473.32 | 0 | 0 | 0 | 0 | 0 | 22473.32
2022102824 | 6 | 0.46224 | 36979.2 | 0.29231 | 10523.16 | 0 | 0 | 1 | 5000 | 10523.16 | 0 | 0 | 0 | 0 | 0 | 21456.04 | 0 | 0 | 0 | 0 | 0 | 21456.04
2022102901 | 7 | 0.43962 | 35169.6 | 0.27216 | 9797.76 | 0 | 0 | 1 | 5000 | 9797.76 | 0 | 0 | 0 | 0 | 0 | 20371.84 | 0 | 0 | 0 | 0 | 0 | 20371.84
2022102902 | 7 | 0.42647 | 34117.6 | 0.27175 | 9783 | 0 | 0 | 1 | 5000 | 9783 | 0 | 0 | 0 | 0 | 0 | 19334.6 | 0 | 0 | 0 | 0 | 0 | 19334.6
2022102903 | 7 | 0.41745 | 33396 | 0.27048 | 9737.28 | 0 | 0 | 1 | 5000 | 9737.28 | 0 | 0 | 0 | 0 | 0 | 18658.72 | 0 | 0 | 0 | 0 | 0 | 18658.72
2022102904 | 7 | 0.41205 | 32964 | 0.26718 | 9618.48 | 0 | 0 | 1 | 5000 | 9618.48 | 0 | 0 | 0 | 0 | 0 | 18345.52 | 0 | 0 | 0 | 0 | 0 | 18345.52
2022102905 | 7 | 0.41063 | 32850.4 | 0.25284 | 9102.24 | 0 | 0 | 1 | 5000 | 9102.24 | 0 | 0 | 0 | 0 | 0 | 18748.16 | 0 | 0 | 0 | 0 | 0 | 18748.16
2022102906 | 7 | 0.41736 | 33388.8 | 0.24698 | 8891.28 | 0 | 0 | 1 | 5000 | 8891.28 | 0 | 0 | 0 | 0 | 0 | 19497.52 | 0 | 0 | 0 | 0 | 0 | 19497.52
2022102907 | 7 | 0.42814 | 34251.2 | 0.24974 | 8990.64 | 0 | 0 | 1 | 5000 | 8990.64 | 0 | 0 | 0 | 0 | 0 | 20260.56 | 0 | 0 | 0 | 0 | 0 | 20260.56
2022102908 | 7 | 0.44679 | 35743.2 | 0.25611 | 9219.96 | 0.00122 | 14.64 | 1 | 5000 | 9219.96 | 14.64 | 0 | 0 | 0 | 0 | 21508.6 | 0 | 0 | 0 | 0 | 0 | 21508.6
2022102909 | 7 | 0.46286 | 37028.8 | 0.25851 | 9306.36 | 0.10961 | 1315.32 | 1 | 5000 | 9306.36 | 1315.32 | 0 | 0 | 0 | 0 | 21407.12 | 0 | 0 | 0 | 0 | 0 | 21407.12
2022102910 | 7 | 0.47709 | 38167.2 | 0.19517 | 7026.12 | 0.38138 | 4576.56 | 1 | 5000 | 7026.12 | 4576.56 | 0 | 0 | 0 | 0 | 21564.52 | 0 | 0 | 0 | 0 | 0 | 21564.52
2022102911 | 7 | 0.48683 | 38946.4 | 0.2105 | 7578 | 0.53041 | 6364.92 | 1 | 5000 | 7578 | 6364.92 | 0 | 0 | 0 | 0 | 20003.48 | 0 | 0 | 0 | 0 | 0 | 20003.48
2022102912 | 7 | 0.48865 | 39092 | 0.21414 | 7709.04 | 0.57471 | 6896.52 | 1 | 5000 | 7709.04 | 6896.52 | 0 | 0 | 0 | 0 | 19486.44 | 0 | 0 | 0 | 0 | 0 | 19486.44
2022102913 | 7 | 0.49044 | 39235.2 | 0.22821 | 8215.56 | 0.61328 | 7359.36 | 1 | 5000 | 8215.56 | 7359.36 | 0 | 0 | 0 | 0 | 18660.28 | 0 | 0 | 0 | 0 | 0 | 18660.28
2022102914 | 7 | 0.4905 | 39240 | 0.22214 | 7997.04 | 0.60736 | 7288.32 | 1 | 5000 | 7997.04 | 7288.32 | 0 | 0 | 0 | 0 | 18954.64 | 0 | 0 | 0 | 0 | 0 | 18954.64
2022102915 | 7 | 0.49018 | 39214.4 | 0.20858 | 7508.88 | 0.58881 | 7065.72 | 1 | 5000 | 7508.88 | 7065.72 | 0 | 0 | 0 | 0 | 19639.8 | 0 | 0 | 0 | 0 | 0 | 19639.8
2022102916 | 7 | 0.49071 | 39256.8 | 0.18572 | 6685.92 | 0.58835 | 7060.2 | 1 | 5000 | 6685.92 | 7060.2 | 0 | 0 | 0 | 0 | 20510.68 | 0 | 0 | 0 | 0 | 0 | 20510.68
2022102917 | 7 | 0.49372 | 39497.6 | 0.14969 | 5388.84 | 0.57337 | 6880.44 | 1 | 5000 | 5388.84 | 6880.44 | 0 | 0 | 0 | 0 | 22228.32 | 0 | 0 | 0 | 0 | 0 | 22228.32
2022102918 | 7 | 0.49441 | 39552.8 | 0.10242 | 3687.12 | 0.43649 | 5237.88 | 1 | 5000 | 3687.12 | 5237.88 | 0 | 0 | 0 | 0 | 25627.8 | 0 | 0 | 0 | 0 | 0 | 25627.8
2022102919 | 7 | 0.49675 | 39740 | 0.05239 | 1886.04 | 0.09735 | 1168.2 | 1 | 5000 | 1886.04 | 1168.2 | 0 | 0 | 0 | 0 | 31685.76 | 0 | 0 | 0 | 0 | 0 | 31685.76
2022102920 | 7 | 0.49738 | 39790.4 | 0.03476 | 1251.36 | 0.0001 | 1.2 | 1 | 5000 | 1251.36 | 1.2 | 0 | 0 | 0 | 0 | 33537.84 | 0 | 0 | 0 | 0 | 0 | 33537.84
2022102921 | 7 | 0.4915 | 39320 | 0.03096 | 1114.56 | 0 | 0 | 1 | 5000 | 1114.56 | 0 | 0 | 0 | 0 | 0 | 33205.44 | 0 | 0 | 0 | 0 | 0 | 33205.44
2022102922 | 7 | 0.47934 | 38347.2 | 0.03437 | 1237.32 | 0 | 0 | 1 | 5000 | 1237.32 | 0 | 0 | 0 | 0 | 0 | 32109.88 | 0 | 0 | 0 | 0 | 0 | 32109.88
2022102923 | 7 | 0.46389 | 37111.2 | 0.04374 | 1574.64 | 0 | 0 | 1 | 5000 | 1574.64 | 0 | 0 | 0 | 0 | 0 | 30536.56 | 0 | 0 | 0 | 0 | 0 | 30536.56
2022102924 | 7 | 0.44619 | 35695.2 | 0.0464 | 1670.4 | 0 | 0 | 1 | 5000 | 1670.4 | 0 | 0 | 0 | 0 | 0 | 29024.8 | 0 | 0 | 0 | 0 | 0 | 29024.8
2022103001 | 1 | 0.43032 | 34425.6 | 0.0469 | 1688.4 | 0 | 0 | 1 | 5000 | 1688.4 | 0 | 0 | 0 | 0 | 0 | 27737.2 | 0 | 0 | 0 | 0 | 0 | 27737.2
2022103002 | 1 | 0.41862 | 33489.6 | 0.04832 | 1739.52 | 0 | 0 | 1 | 5000 | 1739.52 | 0 | 0 | 0 | 0 | 0 | 26750.08 | 0 | 0 | 0 | 0 | 0 | 26750.08
2022103003 | 1 | 0.41046 | 32836.8 | 0.05373 | 1934.28 | 0 | 0 | 1 | 5000 | 1934.28 | 0 | 0 | 0 | 0 | 0 | 25902.52 | 0 | 0 | 0 | 0 | 0 | 25902.52
2022103004 | 1 | 0.40753 | 32602.4 | 0.05734 | 2064.24 | 0 | 0 | 1 | 5000 | 2064.24 | 0 | 0 | 0 | 0 | 0 | 25538.16 | 0 | 0 | 0 | 0 | 0 | 25538.16
2022103005 | 1 | 0.40733 | 32586.4 | 0.07097 | 2554.92 | 0 | 0 | 1 | 5000 | 2554.92 | 0 | 0 | 0 | 0 | 0 | 25031.48 | 0 | 0 | 0 | 0 | 0 | 25031.48
2022103006 | 1 | 0.40848 | 32678.4 | 0.08147 | 2932.92 | 0 | 0 | 1 | 5000 | 2932.92 | 0 | 0 | 0 | 0 | 0 | 24745.48 | 0 | 0 | 0 | 0 | 0 | 24745.48
2022103007 | 1 | 0.41571 | 33256.8 | 0.09277 | 3339.72 | 0 | 0 | 1 | 5000 | 3339.72 | 0 | 0 | 0 | 0 | 0 | 24917.08 | 0 | 0 | 0 | 0 | 0 | 24917.08
2022103008 | 1 | 0.42729 | 34183.2 | 0.09181 | 3305.16 | 0.00118 | 14.16 | 1 | 5000 | 3305.16 | 14.16 | 0 | 0 | 0 | 0 | 25863.88 | 0 | 0 | 0 | 0 | 0 | 25863.88
2022103009 | 1 | 0.44212 | 35369.6 | 0.08114 | 2921.04 | 0.1467 | 1760.4 | 1 | 5000 | 2921.04 | 1760.4 | 0 | 0 | 0 | 0 | 25688.16 | 0 | 0 | 0 | 0 | 0 | 25688.16
2022103010 | 1 | 0.46033 | 36826.4 | 0.05232 | 1883.52 | 0.57656 | 6918.72 | 1 | 5000 | 1883.52 | 6918.72 | 0 | 0 | 0 | 0 | 23024.16 | 0 | 0 | 0 | 0 | 0 | 23024.16
2022103011 | 1 | 0.467 | 37360 | 0.02232 | 803.52 | 0.69785 | 8374.2 | 1 | 5000 | 803.52 | 8374.2 | 0 | 0 | 0 | 0 | 23182.28 | 0 | 0 | 0 | 0 | 0 | 23182.28
2022103012 | 1 | 0.47319 | 37855.2 | 0.01736 | 624.96 | 0.68676 | 8241.12 | 1 | 5000 | 624.96 | 8241.12 | 0 | 0 | 0 | 0 | 23989.12 | 0 | 0 | 0 | 0 | 0 | 23989.12
2022103013 | 1 | 0.48422 | 38737.6 | 0.0158 | 568.8 | 0.67737 | 8128.44 | 1 | 5000 | 568.8 | 8128.44 | 0 | 0 | 0 | 0 | 25040.36 | 0 | 0 | 0 | 0 | 0 | 25040.36
2022103014 | 1 | 0.49582 | 39665.6 | 0.01444 | 519.84 | 0.66532 | 7983.84 | 1 | 5000 | 519.84 | 7983.84 | 0 | 0 | 0 | 0 | 26161.92 | 0 | 0 | 0 | 0 | 0 | 26161.92
2022103015 | 1 | 0.50645 | 40516 | 0.01424 | 512.64 | 0.66438 | 7972.56 | 1 | 5000 | 512.64 | 7972.56 | 0 | 0 | 0 | 0 | 27030.8 | 0 | 0 | 0 | 0 | 0 | 27030.8
2022103016 | 1 | 0.51839 | 41471.2 | 0.01732 | 623.52 | 0.6509 | 7810.8 | 1 | 5000 | 623.52 | 7810.8 | 0 | 0 | 0 | 0 | 28036.88 | 0 | 0 | 0 | 0 | 0 | 28036.88
2022103017 | 1 | 0.52843 | 42274.4 | 0.02284 | 822.24 | 0.58657 | 7038.84 | 1 | 5000 | 822.24 | 7038.84 | 0 | 0 | 0 | 0 | 29413.32 | 0 | 0 | 0 | 0 | 0 | 29413.32
2022103018 | 1 | 0.53229 | 42583.2 | 0.03116 | 1121.76 | 0.43439 | 5212.68 | 1 | 5000 | 1121.76 | 5212.68 | 0 | 0 | 0 | 0 | 31248.76 | 0 | 0 | 0 | 0 | 0 | 31248.76
2022103019 | 1 | 0.53461 | 42768.8 | 0.03688 | 1327.68 | 0.06907 | 828.84 | 1 | 5000 | 1327.68 | 828.84 | 0 | 0 | 0 | 0 | 35612.28 | 0 | 0 | 0 | 0 | 0 | 35612.28
2022103020 | 1 | 0.54243 | 43394.4 | 0.05265 | 1895.4 | 0 | 0 | 1 | 5000 | 1895.4 | 0 | 0 | 0 | 0 | 0 | 36499 | 0 | 0 | 0 | 0 | 0 | 36499
2022103021 | 1 | 0.53157 | 42525.6 | 0.06824 | 2456.64 | 0 | 0 | 1 | 5000 | 2456.64 | 0 | 0 | 0 | 0 | 0 | 35068.96 | 0 | 0 | 0 | 0 | 0 | 35068.96
2022103022 | 1 | 0.51159 | 40927.2 | 0.09787 | 3523.32 | 0 | 0 | 1 | 5000 | 3523.32 | 0 | 0 | 0 | 0 | 0 | 32403.88 | 0 | 0 | 0 | 0 | 0 | 32403.88
2022103023 | 1 | 0.48414 | 38731.2 | 0.10599 | 3815.64 | 0 | 0 | 1 | 5000 | 3815.64 | 0 | 0 | 0 | 0 | 0 | 29915.56 | 0 | 0 | 0 | 0 | 0 | 29915.56
2022103024 | 1 | 0.45311 | 36248.8 | 0.11362 | 4090.32 | 0 | 0 | 1 | 5000 | 4090.32 | 0 | 0 | 0 | 0 | 0 | 27158.48 | 0 | 0 | 0 | 0 | 0 | 27158.48
2022103101 | 2 | 0.42946 | 34356.8 | 0.11998 | 4319.28 | 0 | 0 | 1 | 5000 | 4319.28 | 0 | 0 | 0 | 0 | 0 | 25037.52 | 0 | 0 | 0 | 0 | 0 | 25037.52
2022103102 | 2 | 0.41519 | 33215.2 | 0.11885 | 4278.6 | 0 | 0 | 1 | 5000 | 4278.6 | 0 | 0 | 0 | 0 | 0 | 23936.6 | 0 | 0 | 0 | 0 | 0 | 23936.6
2022103103 | 2 | 0.40924 | 32739.2 | 0.12386 | 4458.96 | 0 | 0 | 1 | 5000 | 4458.96 | 0 | 0 | 0 | 0 | 0 | 23280.24 | 0 | 0 | 0 | 0 | 0 | 23280.24
2022103104 | 2 | 0.40707 | 32565.6 | 0.12086 | 4350.96 | 0 | 0 | 1 | 5000 | 4350.96 | 0 | 0 | 0 | 0 | 0 | 23214.64 | 0 | 0 | 0 | 0 | 0 | 23214.64
2022103105 | 2 | 0.41534 | 33227.2 | 0.11193 | 4029.48 | 0 | 0 | 1 | 5000 | 4029.48 | 0 | 0 | 0 | 0 | 0 | 24197.72 | 0 | 0 | 0 | 0 | 0 | 24197.72
2022103106 | 2 | 0.4355 | 34840 | 0.09598 | 3455.28 | 0 | 0 | 1 | 5000 | 3455.28 | 0 | 0 | 0 | 0 | 0 | 26384.72 | 0 | 0 | 0 | 0 | 0 | 26384.72
2022103107 | 2 | 0.47329 | 37863.2 | 0.08769 | 3156.84 | 0 | 0 | 1 | 5000 | 3156.84 | 0 | 0 | 0 | 0 | 0 | 29706.36 | 0 | 0 | 0 | 0 | 0 | 29706.36
2022103108 | 2 | 0.49667 | 39733.6 | 0.08875 | 3195 | 0.00108 | 12.96 | 1 | 5000 | 3195 | 12.96 | 0 | 0 | 0 | 0 | 31525.64 | 0 | 0 | 0 | 0 | 0 | 31525.64
2022103109 | 2 | 0.49981 | 39984.8 | 0.09033 | 3251.88 | 0.09913 | 1189.56 | 1 | 5000 | 3251.88 | 1189.56 | 0 | 0 | 0 | 0 | 30543.36 | 0 | 0 | 0 | 0 | 0 | 30543.36
2022103110 | 2 | 0.50546 | 40436.8 | 0.08189 | 2948.04 | 0.36678 | 4401.36 | 1 | 5000 | 2948.04 | 4401.36 | 0 | 0 | 0 | 0 | 28087.4 | 0 | 0 | 0 | 0 | 0 | 28087.4
2022103111 | 2 | 0.51107 | 40885.6 | 0.07485 | 2694.6 | 0.51077 | 6129.24 | 1 | 5000 | 2694.6 | 6129.24 | 0 | 0 | 0 | 0 | 27061.76 | 0 | 0 | 0 | 0 | 0 | 27061.76
2022103112 | 2 | 0.51814 | 41451.2 | 0.09461 | 3405.96 | 0.54946 | 6593.52 | 1 | 5000 | 3405.96 | 6593.52 | 0 | 0 | 0 | 0 | 26451.72 | 0 | 0 | 0 | 0 | 0 | 26451.72
2022103113 | 2 | 0.52743 | 42194.4 | 0.11197 | 4030.92 | 0.5782 | 6938.4 | 1 | 5000 | 4030.92 | 6938.4 | 0 | 0 | 0 | 0 | 26225.08 | 0 | 0 | 0 | 0 | 0 | 26225.08
2022103114 | 2 | 0.54091 | 43272.8 | 0.1282 | 4615.2 | 0.56033 | 6723.96 | 1 | 5000 | 4615.2 | 6723.96 | 0 | 0 | 0 | 0 | 26933.64 | 0 | 0 | 0 | 0 | 0 | 26933.64
2022103115 | 2 | 0.55045 | 44036 | 0.13571 | 4885.56 | 0.5622 | 6746.4 | 1 | 5000 | 4885.56 | 6746.4 | 0 | 0 | 0 | 0 | 27404.04 | 0 | 0 | 0 | 0 | 0 | 27404.04
2022103116 | 2 | 0.56025 | 44820 | 0.13647 | 4912.92 | 0.53396 | 6407.52 | 1 | 5000 | 4912.92 | 6407.52 | 0 | 0 | 0 | 0 | 28499.56 | 0 | 0 | 0 | 0 | 0 | 28499.56
2022103117 | 2 | 0.56945 | 45556 | 0.13737 | 4945.32 | 0.44522 | 5342.64 | 1 | 5000 | 4945.32 | 5342.64 | 0 | 0 | 0 | 0 | 30268.04 | 0 | 0 | 0 | 0 | 0 | 30268.04
2022103118 | 2 | 0.56735 | 45388 | 0.13972 | 5029.92 | 0.27809 | 3337.08 | 1 | 5000 | 5029.92 | 3337.08 | 0 | 0 | 0 | 0 | 32021 | 0 | 0 | 0 | 0 | 0 | 32021
2022103119 | 2 | 0.55025 | 44020 | 0.16441 | 5918.76 | 0.04597 | 551.64 | 1 | 5000 | 5918.76 | 551.64 | 0 | 0 | 0 | 0 | 32549.6 | 0 | 0 | 0 | 0 | 0 | 32549.6
2022103120 | 2 | 0.5431 | 43448 | 0.2017 | 7261.2 | 5e-05 | 0.6 | 1 | 5000 | 7261.2 | 0.6 | 0 | 0 | 0 | 0 | 31186.2 | 0 | 0 | 0 | 0 | 0 | 31186.2
2022103121 | 2 | 0.53477 | 42781.6 | 0.234 | 8424 | 0 | 0 | 1 | 5000 | 8424 | 0 | 0 | 0 | 0 | 0 | 29357.6 | 0 | 0 | 0 | 0 | 0 | 29357.6
2022103122 | 2 | 0.5247 | 41976 | 0.26345 | 9484.2 | 0 | 0 | 1 | 5000 | 9484.2 | 0 | 0 | 0 | 0 | 0 | 27491.8 | 0 | 0 | 0 | 0 | 0 | 27491.8
2022103123 | 2 | 0.49781 | 39824.8 | 0.312 | 11232 | 0 | 0 | 1 | 5000 | 11232 | 0 | 0 | 0 | 0 | 0 | 23592.8 | 0 | 0 | 0 | 0 | 0 | 23592.8
2022103124 | 2 | 0.46402 | 37121.6 | 0.34009 | 12243.24 | 0 | 0 | 1 | 5000 | 12243.24 | 0 | 0 | 0 | 0 | 0 | 19878.36 | 0 | 0 | 0 | 0 | 0 | 19878.36
2022110101 | 3 | 0.44353 | 35482.4 | 0.372 | 13392 | 0 | 0 | 1 | 5000 | 13392 | 0 | 0 | 0 | 0 | 0 | 17090.4 | 0 | 0 | 0 | 0 | 0 | 17090.4
2022110102 | 3 | 0.4312 | 34496 | 0.3793 | 13654.8 | 0 | 0 | 1 | 5000 | 13654.8 | 0 | 0 | 0 | 0 | 0 | 15841.2 | 0 | 0 | 0 | 0 | 0 | 15841.2
2022110103 | 3 | 0.42371 | 33896.8 | 0.36629 | 13186.44 | 0 | 0 | 1 | 5000 | 13186.44 | 0 | 0 | 0 | 0 | 0 | 15710.36 | 0 | 0 | 0 | 0 | 0 | 15710.36
2022110104 | 3 | 0.42013 | 33610.4 | 0.32356 | 11648.16 | 0 | 0 | 1 | 5000 | 11648.16 | 0 | 0 | 0 | 0 | 0 | 16962.24 | 0 | 0 | 0 | 0 | 0 | 16962.24
2022110105 | 3 | 0.42273 | 33818.4 | 0.29923 | 10772.28 | 0 | 0 | 1 | 5000 | 10772.28 | 0 | 0 | 0 | 0 | 0 | 18046.12 | 0 | 0 | 0 | 0 | 0 | 18046.12
2022110106 | 3 | 0.44082 | 35265.6 | 0.30002 | 10800.72 | 0 | 0 | 1 | 5000 | 10800.72 | 0 | 0 | 0 | 0 | 0 | 19464.88 | 0 | 0 | 0 | 0 | 0 | 19464.88
2022110107 | 3 | 0.47503 | 38002.4 | 0.29779 | 10720.44 | 0 | 0 | 1 | 5000 | 10720.44 | 0 | 0 | 0 | 0 | 0 | 22281.96 | 0 | 0 | 0 | 0 | 0 | 22281.96
2022110108 | 3 | 0.49573 | 39658.4 | 0.27389 | 9860.04 | 0.00011 | 1.32 | 1 | 5000 | 9860.04 | 1.32 | 0 | 0 | 0 | 0 | 24797.04 | 0 | 0 | 0 | 0 | 0 | 24797.04
2022110109 | 3 | 0.49798 | 39838.4 | 0.24824 | 8936.64 | 0.06905 | 828.6 | 1 | 5000 | 8936.64 | 828.6 | 0 | 0 | 0 | 0 | 25073.16 | 0 | 0 | 0 | 0 | 0 | 25073.16
2022110110 | 3 | 0.50498 | 40398.4 | 0.19557 | 7040.52 | 0.34832 | 4179.84 | 1 | 5000 | 7040.52 | 4179.84 | 0 | 0 | 0 | 0 | 24178.04 | 0 | 0 | 0 | 0 | 0 | 24178.04
2022110111 | 3 | 0.51416 | 41132.8 | 0.15445 | 5560.2 | 0.50164 | 6019.68 | 1 | 5000 | 5560.2 | 6019.68 | 0 | 0 | 0 | 0 | 24552.92 | 0 | 0 | 0 | 0 | 0 | 24552.92
2022110112 | 3 | 0.52171 | 41736.8 | 0.15896 | 5722.56 | 0.54887 | 6586.44 | 1 | 5000 | 5722.56 | 6586.44 | 0 | 0 | 0 | 0 | 24427.8 | 0 | 0 | 0 | 0 | 0 | 24427.8
2022110113 | 3 | 0.52727 | 42181.6 | 0.17414 | 6269.04 | 0.55018 | 6602.16 | 1 | 5000 | 6269.04 | 6602.16 | 0 | 0 | 0 | 0 | 24310.4 | 0 | 0 | 0 | 0 | 0 | 24310.4
2022110114 | 3 | 0.53408 | 42726.4 | 0.18735 | 6744.6 | 0.55315 | 6637.8 | 1 | 5000 | 6744.6 | 6637.8 | 0 | 0 | 0 | 0 | 24344 | 0 | 0 | 0 | 0 | 0 | 24344
2022110115 | 3 | 0.53821 | 43056.8 | 0.22189 | 7988.04 | 0.55177 | 6621.24 | 1 | 5000 | 7988.04 | 6621.24 | 0 | 0 | 0 | 0 | 23447.52 | 0 | 0 | 0 | 0 | 0 | 23447.52
2022110116 | 3 | 0.5422 | 43376 | 0.262 | 9432 | 0.54334 | 6520.08 | 1 | 5000 | 9432 | 6520.08 | 0 | 0 | 0 | 0 | 22423.92 | 0 | 0 | 0 | 0 | 0 | 22423.92
2022110117 | 3 | 0.54878 | 43902.4 | 0.29389 | 10580.04 | 0.53307 | 6396.84 | 1 | 5000 | 10580.04 | 6396.84 | 0 | 0 | 0 | 0 | 21925.52 | 0 | 0 | 0 | 0 | 0 | 21925.52
2022110118 | 3 | 0.54864 | 43891.2 | 0.304 | 10944 | 0.41133 | 4935.96 | 1 | 5000 | 10944 | 4935.96 | 0 | 0 | 0 | 0 | 23011.24 | 0 | 0 | 0 | 0 | 0 | 23011.24
2022110119 | 3 | 0.54988 | 43990.4 | 0.30905 | 11125.8 | 0.0821 | 985.2 | 1 | 5000 | 11125.8 | 985.2 | 0 | 0 | 0 | 0 | 26879.4 | 0 | 0 | 0 | 0 | 0 | 26879.4
2022110120 | 3 | 0.55557 | 44445.6 | 0.36932 | 13295.52 | 0.00299 | 35.88 | 1 | 5000 | 13295.52 | 35.88 | 0 | 0 | 0 | 0 | 26114.2 | 0 | 0 | 0 | 0 | 0 | 26114.2
2022110121 | 3 | 0.54648 | 43718.4 | 0.44294 | 15945.84 | 0 | 0 | 1 | 5000 | 15945.84 | 0 | 0 | 0 | 0 | 0 | 22772.56 | 0 | 0 | 0 | 0 | 0 | 22772.56
2022110122 | 3 | 0.52809 | 42247.2 | 0.48376 | 17415.36 | 0 | 0 | 1 | 5000 | 17415.36 | 0 | 0 | 0 | 0 | 0 | 19831.84 | 0 | 0 | 0 | 0 | 0 | 19831.84
2022110123 | 3 | 0.50273 | 40218.4 | 0.50325 | 18117 | 0 | 0 | 1 | 5000 | 18117 | 0 | 0 | 0 | 0 | 0 | 17101.4 | 0 | 0 | 0 | 0 | 0 | 17101.4
2022110124 | 3 | 0.47137 | 37709.6 | 0.49285 | 17742.6 | 0 | 0 | 1 | 5000 | 17742.6 | 0 | 0 | 0 | 0 | 0 | 14967 | 0 | 0 | 0 | 0 | 0 | 14967
2022110201 | 4 | 0.44815 | 35852 | 0.48103 | 17317.08 | 0 | 0 | 1 | 5000 | 17317.08 | 0 | 0 | 0 | 0 | 0 | 13534.92 | 0 | 0 | 0 | 0 | 0 | 13534.92
2022110202 | 4 | 0.43435 | 34748 | 0.47304 | 17029.44 | 0 | 0 | 1 | 5000 | 17029.44 | 0 | 0 | 0 | 0 | 0 | 12718.56 | 0 | 0 | 0 | 0 | 0 | 12718.56
2022110203 | 4 | 0.42738 | 34190.4 | 0.46301 | 16668.36 | 0 | 0 | 1 | 5000 | 16668.36 | 0 | 0 | 0 | 0 | 0 | 12522.04 | 0 | 0 | 0 | 0 | 0 | 12522.04
2022110204 | 4 | 0.42343 | 33874.4 | 0.45696 | 16450.56 | 0 | 0 | 1 | 5000 | 16450.56 | 0 | 0 | 0 | 0 | 0 | 12423.84 | 0 | 0 | 0 | 0 | 0 | 12423.84
2022110205 | 4 | 0.42874 | 34299.2 | 0.45687 | 16447.32 | 0 | 0 | 1 | 5000 | 16447.32 | 0 | 0 | 0 | 0 | 0 | 12851.88 | 0 | 0 | 0 | 0 | 0 | 12851.88
2022110206 | 4 | 0.44928 | 35942.4 | 0.45745 | 16468.2 | 0 | 0 | 1 | 5000 | 16468.2 | 0 | 0 | 0 | 0 | 0 | 14474.2 | 0 | 0 | 0 | 0 | 0 | 14474.2
2022110207 | 4 | 0.48278 | 38622.4 | 0.45055 | 16219.8 | 0 | 0 | 1 | 5000 | 16219.8 | 0 | 0 | 0 | 0 | 0 | 17402.6 | 0 | 0 | 0 | 0 | 0 | 17402.6
2022110208 | 4 | 0.50488 | 40390.4 | 0.42967 | 15468.12 | 0.0002 | 2.4 | 1 | 5000 | 15468.12 | 2.4 | 0 | 0 | 0 | 0 | 19919.88 | 0 | 0 | 0 | 0 | 0 | 19919.88
2022110209 | 4 | 0.50621 | 40496.8 | 0.39672 | 14281.92 | 0.03334 | 400.08 | 1 | 5000 | 14281.92 | 400.08 | 0 | 0 | 0 | 0 | 20814.8 | 0 | 0 | 0 | 0 | 0 | 20814.8
2022110210 | 4 | 0.51304 | 41043.2 | 0.36387 | 13099.32 | 0.16489 | 1978.68 | 1 | 5000 | 13099.32 | 1978.68 | 0 | 0 | 0 | 0 | 20965.2 | 0 | 0 | 0 | 0 | 0 | 20965.2
2022110211 | 4 | 0.51921 | 41536.8 | 0.38483 | 13853.88 | 0.30483 | 3657.96 | 1 | 5000 | 13853.88 | 3657.96 | 0 | 0 | 0 | 0 | 19024.96 | 0 | 0 | 0 | 0 | 0 | 19024.96
2022110212 | 4 | 0.529 | 42320 | 0.38683 | 13925.88 | 0.41164 | 4939.68 | 1 | 5000 | 13925.88 | 4939.68 | 0 | 0 | 0 | 0 | 18454.44 | 0 | 0 | 0 | 0 | 0 | 18454.44
2022110213 | 4 | 0.53933 | 43146.4 | 0.37 | 13320 | 0.46593 | 5591.16 | 1 | 5000 | 13320 | 5591.16 | 0 | 0 | 0 | 0 | 19235.24 | 0 | 0 | 0 | 0 | 0 | 19235.24
2022110214 | 4 | 0.55434 | 44347.2 | 0.37584 | 13530.24 | 0.46103 | 5532.36 | 1 | 5000 | 13530.24 | 5532.36 | 0 | 0 | 0 | 0 | 20284.6 | 0 | 0 | 0 | 0 | 0 | 20284.6
2022110215 | 4 | 0.56569 | 45255.2 | 0.39728 | 14302.08 | 0.40182 | 4821.84 | 1 | 5000 | 14302.08 | 4821.84 | 0 | 0 | 0 | 0 | 21131.28 | 0 | 0 | 0 | 0 | 0 | 21131.28
2022110216 | 4 | 0.57437 | 45949.6 | 0.41275 | 14859 | 0.32008 | 3840.96 | 1 | 5000 | 14859 | 3840.96 | 0 | 0 | 0 | 0 | 22249.64 | 0 | 0 | 0 | 0 | 0 | 22249.64
2022110217 | 4 | 0.58345 | 46676 | 0.41486 | 14934.96 | 0.25722 | 3086.64 | 1 | 5000 | 14934.96 | 3086.64 | 0 | 0 | 0 | 0 | 23654.4 | 0 | 0 | 0 | 0 | 0 | 23654.4
2022110218 | 4 | 0.5854 | 46832 | 0.4289 | 15440.4 | 0.14664 | 1759.68 | 1 | 5000 | 15440.4 | 1759.68 | 0 | 0 | 0 | 0 | 24631.92 | 0 | 0 | 0 | 0 | 0 | 24631.92
2022110219 | 4 | 0.58344 | 46675.2 | 0.4205 | 15138 | 0.03871 | 464.52 | 1 | 5000 | 15138 | 464.52 | 0 | 0 | 0 | 0 | 26072.68 | 0 | 0 | 0 | 0 | 0 | 26072.68
2022110220 | 4 | 0.58916 | 47132.8 | 0.44623 | 16064.28 | 0 | 0 | 1 | 5000 | 16064.28 | 0 | 0 | 0 | 0 | 0 | 26068.52 | 0 | 0 | 0 | 0 | 0 | 26068.52
2022110221 | 4 | 0.57827 | 46261.6 | 0.47899 | 17243.64 | 0 | 0 | 1 | 5000 | 17243.64 | 0 | 0 | 0 | 0 | 0 | 24017.96 | 0 | 0 | 0 | 0 | 0 | 24017.96
2022110222 | 4 | 0.56082 | 44865.6 | 0.48305 | 17389.8 | 0 | 0 | 1 | 5000 | 17389.8 | 0 | 0 | 0 | 0 | 0 | 22475.8 | 0 | 0 | 0 | 0 | 0 | 22475.8
2022110223 | 4 | 0.53378 | 42702.4 | 0.50114 | 18041.04 | 0 | 0 | 1 | 5000 | 18041.04 | 0 | 0 | 0 | 0 | 0 | 19661.36 | 0 | 0 | 0 | 0 | 0 | 19661.36
2022110224 | 4 | 0.50244 | 40195.2 | 0.50353 | 18127.08 | 0 | 0 | 1 | 5000 | 18127.08 | 0 | 0 | 0 | 0 | 0 | 17068.12 | 0 | 0 | 0 | 0 | 0 | 17068.12
2022110301 | 5 | 0.47711 | 38168.8 | 0.50244 | 18087.84 | 0 | 0 | 1 | 5000 | 18087.84 | 0 | 0 | 0 | 0 | 0 | 15080.96 | 0 | 0 | 0 | 0 | 0 | 15080.96
2022110302 | 5 | 0.45986 | 36788.8 | 0.4993 | 17974.8 | 0 | 0 | 1 | 5000 | 17974.8 | 0 | 0 | 0 | 0 | 0 | 13814 | 0 | 0 | 0 | 0 | 0 | 13814
2022110303 | 5 | 0.45115 | 36092 | 0.49354 | 17767.44 | 0 | 0 | 1 | 5000 | 17767.44 | 0 | 0 | 0 | 0 | 0 | 13324.56 | 0 | 0 | 0 | 0 | 0 | 13324.56
2022110304 | 5 | 0.44846 | 35876.8 | 0.49093 | 17673.48 | 0 | 0 | 1 | 5000 | 17673.48 | 0 | 0 | 0 | 0 | 0 | 13203.32 | 0 | 0 | 0 | 0 | 0 | 13203.32
2022110305 | 5 | 0.45399 | 36319.2 | 0.49178 | 17704.08 | 0 | 0 | 1 | 5000 | 17704.08 | 0 | 0 | 0 | 0 | 0 | 13615.12 | 0 | 0 | 0 | 0 | 0 | 13615.12
2022110306 | 5 | 0.47588 | 38070.4 | 0.50431 | 18155.16 | 0 | 0 | 1 | 5000 | 18155.16 | 0 | 0 | 0 | 0 | 0 | 14915.24 | 0 | 0 | 0 | 0 | 0 | 14915.24
2022110307 | 5 | 0.51274 | 41019.2 | 0.51532 | 18551.52 | 0 | 0 | 1 | 5000 | 18551.52 | 0 | 0 | 0 | 0 | 0 | 17467.68 | 0 | 0 | 0 | 0 | 0 | 17467.68
2022110308 | 5 | 0.53421 | 42736.8 | 0.52439 | 18878.04 | 0.00029 | 3.48 | 1 | 5000 | 18878.04 | 3.48 | 0 | 0 | 0 | 0 | 18855.28 | 0 | 0 | 0 | 0 | 0 | 18855.28
2022110309 | 5 | 0.5402 | 43216 | 0.52885 | 19038.6 | 0.02547 | 305.64 | 1 | 5000 | 19038.6 | 305.64 | 0 | 0 | 0 | 0 | 18871.76 | 0 | 0 | 0 | 0 | 0 | 18871.76
2022110310 | 5 | 0.5512 | 44096 | 0.51527 | 18549.72 | 0.11267 | 1352.04 | 1 | 5000 | 18549.72 | 1352.04 | 0 | 0 | 0 | 0 | 19194.24 | 0 | 0 | 0 | 0 | 0 | 19194.24
2022110311 | 5 | 0.56808 | 45446.4 | 0.53564 | 19283.04 | 0.13605 | 1632.6 | 1 | 5000 | 19283.04 | 1632.6 | 0 | 0 | 0 | 0 | 19530.76 | 0 | 0 | 0 | 0 | 0 | 19530.76
2022110312 | 5 | 0.5842 | 46736 | 0.57748 | 20789.28 | 0.14948 | 1793.76 | 1 | 5000 | 20789.28 | 1793.76 | 0 | 0 | 0 | 0 | 19152.96 | 0 | 0 | 0 | 0 | 0 | 19152.96
2022110313 | 5 | 0.59884 | 47907.2 | 0.58726 | 21141.36 | 0.20087 | 2410.44 | 1 | 5000 | 21141.36 | 2410.44 | 0 | 0 | 0 | 0 | 19355.4 | 0 | 0 | 0 | 0 | 0 | 19355.4
2022110314 | 5 | 0.61479 | 49183.2 | 0.59184 | 21306.24 | 0.24837 | 2980.44 | 1 | 5000 | 21306.24 | 2980.44 | 0 | 0 | 0 | 0 | 19896.52 | 0 | 0 | 0 | 0 | 0 | 19896.52
2022110315 | 5 | 0.6285 | 50280 | 0.61085 | 21990.6 | 0.24896 | 2987.52 | 1 | 5000 | 21990.6 | 2987.52 | 0 | 0 | 0 | 0 | 20301.88 | 0 | 0 | 0 | 0 | 0 | 20301.88
2022110316 | 5 | 0.64274 | 51419.2 | 0.64079 | 23068.44 | 0.2133 | 2559.6 | 1 | 5000 | 23068.44 | 2559.6 | 0 | 0 | 0 | 0 | 20791.16 | 0 | 0 | 0 | 0 | 0 | 20791.16
2022110317 | 5 | 0.6529 | 52232 | 0.66389 | 23900.04 | 0.17839 | 2140.68 | 1 | 5000 | 23900.04 | 2140.68 | 0 | 0 | 0 | 0 | 21191.28 | 0 | 0 | 0 | 0 | 0 | 21191.28
2022110318 | 5 | 0.65188 | 52150.4 | 0.66843 | 24063.48 | 0.10628 | 1275.36 | 1 | 5000 | 24063.48 | 1275.36 | 0 | 0 | 0 | 0 | 21811.56 | 0 | 0 | 0 | 0 | 0 | 21811.56
2022110319 | 5 | 0.64229 | 51383.2 | 0.66691 | 24008.76 | 0.01935 | 232.2 | 1 | 5000 | 24008.76 | 232.2 | 0 | 0 | 0 | 0 | 22142.24 | 0 | 0 | 0 | 0 | 0 | 22142.24
2022110320 | 5 | 0.64265 | 51412 | 0.66811 | 24051.96 | 0 | 0 | 1 | 5000 | 24051.96 | 0 | 0 | 0 | 0 | 0 | 22360.04 | 0 | 0 | 0 | 0 | 0 | 22360.04
2022110321 | 5 | 0.63027 | 50421.6 | 0.65574 | 23606.64 | 0 | 0 | 1 | 5000 | 23606.64 | 0 | 0 | 0 | 0 | 0 | 21814.96 | 0 | 0 | 0 | 0 | 0 | 21814.96
2022110322 | 5 | 0.6107 | 48856 | 0.65278 | 23500.08 | 0 | 0 | 1 | 5000 | 23500.08 | 0 | 0 | 0 | 0 | 0 | 20355.92 | 0 | 0 | 0 | 0 | 0 | 20355.92
2022110323 | 5 | 0.5822 | 46576 | 0.65162 | 23458.32 | 0 | 0 | 1 | 5000 | 23458.32 | 0 | 0 | 0 | 0 | 0 | 18117.68 | 0 | 0 | 0 | 0 | 0 | 18117.68
2022110324 | 5 | 0.55164 | 44131.2 | 0.64694 | 23289.84 | 0 | 0 | 1 | 5000 | 23289.84 | 0 | 0 | 0 | 0 | 0 | 15841.36 | 0 | 0 | 0 | 0 | 0 | 15841.36
2022110401 | 6 | 0.5262 | 42096 | 0.64768 | 23316.48 | 0 | 0 | 1 | 5000 | 23316.48 | 0 | 0 | 0 | 0 | 0 | 13779.52 | 0 | 0 | 0 | 0 | 0 | 13779.52
2022110402 | 6 | 0.50658 | 40526.4 | 0.65227 | 23481.72 | 0 | 0 | 1 | 5000 | 23481.72 | 0 | 0 | 0 | 0 | 0 | 12044.68 | 0 | 0 | 0 | 0 | 0 | 12044.68
2022110403 | 6 | 0.49234 | 39387.2 | 0.64849 | 23345.64 | 0 | 0 | 1 | 5000 | 23345.64 | 0 | 0 | 0 | 0 | 0 | 11041.56 | 0 | 0 | 0 | 0 | 0 | 11041.56
2022110404 | 6 | 0.48627 | 38901.6 | 0.64653 | 23275.08 | 0 | 0 | 1 | 5000 | 23275.08 | 0 | 0 | 0 | 0 | 0 | 10626.52 | 0 | 0 | 0 | 0 | 0 | 10626.52
2022110405 | 6 | 0.49205 | 39364 | 0.64843 | 23343.48 | 0 | 0 | 1 | 5000 | 23343.48 | 0 | 0 | 0 | 0 | 0 | 11020.52 | 0 | 0 | 0 | 0 | 0 | 11020.52
2022110406 | 6 | 0.51011 | 40808.8 | 0.63573 | 22886.28 | 0 | 0 | 1 | 5000 | 22886.28 | 0 | 0 | 0 | 0 | 0 | 12922.52 | 0 | 0 | 0 | 0 | 0 | 12922.52
2022110407 | 6 | 0.54165 | 43332 | 0.60045 | 21616.2 | 0 | 0 | 1 | 5000 | 21616.2 | 0 | 0 | 0 | 0 | 0 | 16715.8 | 0 | 0 | 0 | 0 | 0 | 16715.8
2022110408 | 6 | 0.56207 | 44965.6 | 0.57803 | 20809.08 | 0.00026 | 3.12 | 1 | 5000 | 20809.08 | 3.12 | 0 | 0 | 0 | 0 | 19153.4 | 0 | 0 | 0 | 0 | 0 | 19153.4
2022110409 | 6 | 0.56583 | 45266.4 | 0.57051 | 20538.36 | 0.0528 | 633.6 | 1 | 5000 | 20538.36 | 633.6 | 0 | 0 | 0 | 0 | 19094.44 | 0 | 0 | 0 | 0 | 0 | 19094.44
2022110410 | 6 | 0.58638 | 46910.4 | 0.55969 | 20148.84 | 0.27959 | 3355.08 | 1 | 5000 | 20148.84 | 3355.08 | 0 | 0 | 0 | 0 | 18406.48 | 0 | 0 | 0 | 0 | 0 | 18406.48
2022110411 | 6 | 0.60522 | 48417.6 | 0.59605 | 21457.8 | 0.25942 | 3113.04 | 1 | 5000 | 21457.8 | 3113.04 | 0 | 0 | 0 | 0 | 18846.76 | 0 | 0 | 0 | 0 | 0 | 18846.76
2022110412 | 6 | 0.62267 | 49813.6 | 0.62828 | 22618.08 | 0.20099 | 2411.88 | 1 | 5000 | 22618.08 | 2411.88 | 0 | 0 | 0 | 0 | 19783.64 | 0 | 0 | 0 | 0 | 0 | 19783.64
2022110413 | 6 | 0.63653 | 50922.4 | 0.63813 | 22972.68 | 0.20309 | 2437.08 | 1 | 5000 | 22972.68 | 2437.08 | 0 | 0 | 0 | 0 | 20512.64 | 0 | 0 | 0 | 0 | 0 | 20512.64
2022110414 | 6 | 0.64849 | 51879.2 | 0.64251 | 23130.36 | 0.20397 | 2447.64 | 1 | 5000 | 23130.36 | 2447.64 | 0 | 0 | 0 | 0 | 21301.2 | 0 | 0 | 0 | 0 | 0 | 21301.2
2022110415 | 6 | 0.6546 | 52368 | 0.62535 | 22512.6 | 0.22562 | 2707.44 | 1 | 5000 | 22512.6 | 2707.44 | 0 | 0 | 0 | 0 | 22147.96 | 0 | 0 | 0 | 0 | 0 | 22147.96
2022110416 | 6 | 0.65956 | 52764.8 | 0.61055 | 21979.8 | 0.24422 | 2930.64 | 1 | 5000 | 21979.8 | 2930.64 | 0 | 0 | 0 | 0 | 22854.36 | 0 | 0 | 0 | 0 | 0 | 22854.36
2022110417 | 6 | 0.66127 | 52901.6 | 0.60263 | 21694.68 | 0.21649 | 2597.88 | 1 | 5000 | 21694.68 | 2597.88 | 0 | 0 | 0 | 0 | 23609.04 | 0 | 0 | 0 | 0 | 0 | 23609.04
2022110418 | 6 | 0.64769 | 51815.2 | 0.5783 | 20818.8 | 0.19006 | 2280.72 | 1 | 5000 | 20818.8 | 2280.72 | 0 | 0 | 0 | 0 | 23715.68 | 0 | 0 | 0 | 0 | 0 | 23715.68
2022110419 | 6 | 0.62591 | 50072.8 | 0.54317 | 19554.12 | 0.05485 | 658.2 | 1 | 5000 | 19554.12 | 658.2 | 0 | 0 | 0 | 0 | 24860.48 | 0 | 0 | 0 | 0 | 0 | 24860.48
2022110420 | 6 | 0.61585 | 49268 | 0.47368 | 17052.48 | 0 | 0 | 1 | 5000 | 17052.48 | 0 | 0 | 0 | 0 | 0 | 27215.52 | 0 | 0 | 0 | 0 | 0 | 27215.52
2022110421 | 6 | 0.59265 | 47412 | 0.44404 | 15985.44 | 0 | 0 | 1 | 5000 | 15985.44 | 0 | 0 | 0 | 0 | 0 | 26426.56 | 0 | 0 | 0 | 0 | 0 | 26426.56
2022110422 | 6 | 0.57061 | 45648.8 | 0.43606 | 15698.16 | 0 | 0 | 1 | 5000 | 15698.16 | 0 | 0 | 0 | 0 | 0 | 24950.64 | 0 | 0 | 0 | 0 | 0 | 24950.64
2022110423 | 6 | 0.54459 | 43567.2 | 0.40958 | 14744.88 | 0 | 0 | 1 | 5000 | 14744.88 | 0 | 0 | 0 | 0 | 0 | 23822.32 | 0 | 0 | 0 | 0 | 0 | 23822.32
2022110424 | 6 | 0.51475 | 41180 | 0.34781 | 12521.16 | 0 | 0 | 1 | 5000 | 12521.16 | 0 | 0 | 0 | 0 | 0 | 23658.84 | 0 | 0 | 0 | 0 | 0 | 23658.84
2022110501 | 7 | 0.4771 | 38168 | 0.30855 | 11107.8 | 0 | 0 | 1 | 5000 | 11107.8 | 0 | 0 | 0 | 0 | 0 | 22060.2 | 0 | 0 | 0 | 0 | 0 | 22060.2
2022110502 | 7 | 0.45038 | 36030.4 | 0.3134 | 11282.4 | 0 | 0 | 1 | 5000 | 11282.4 | 0 | 0 | 0 | 0 | 0 | 19748 | 0 | 0 | 0 | 0 | 0 | 19748
2022110503 | 7 | 0.43696 | 34956.8 | 0.32417 | 11670.12 | 0 | 0 | 1 | 5000 | 11670.12 | 0 | 0 | 0 | 0 | 0 | 18286.68 | 0 | 0 | 0 | 0 | 0 | 18286.68
2022110504 | 7 | 0.4289 | 34312 | 0.29251 | 10530.36 | 0 | 0 | 1 | 5000 | 10530.36 | 0 | 0 | 0 | 0 | 0 | 18781.64 | 0 | 0 | 0 | 0 | 0 | 18781.64
2022110505 | 7 | 0.42567 | 34053.6 | 0.25136 | 9048.96 | 0 | 0 | 1 | 5000 | 9048.96 | 0 | 0 | 0 | 0 | 0 | 20004.64 | 0 | 0 | 0 | 0 | 0 | 20004.64
2022110506 | 7 | 0.43027 | 34421.6 | 0.24862 | 8950.32 | 0 | 0 | 1 | 5000 | 8950.32 | 0 | 0 | 0 | 0 | 0 | 20471.28 | 0 | 0 | 0 | 0 | 0 | 20471.28
2022110507 | 7 | 0.44194 | 35355.2 | 0.2403 | 8650.8 | 0 | 0 | 1 | 5000 | 8650.8 | 0 | 0 | 0 | 0 | 0 | 21704.4 | 0 | 0 | 0 | 0 | 0 | 21704.4
2022110508 | 7 | 0.4589 | 36712 | 0.24517 | 8826.12 | 0.00014 | 1.68 | 1 | 5000 | 8826.12 | 1.68 | 0 | 0 | 0 | 0 | 22884.2 | 0 | 0 | 0 | 0 | 0 | 22884.2
2022110509 | 7 | 0.47722 | 38177.6 | 0.2415 | 8694 | 0.09478 | 1137.36 | 1 | 5000 | 8694 | 1137.36 | 0 | 0 | 0 | 0 | 23346.24 | 0 | 0 | 0 | 0 | 0 | 23346.24
2022110510 | 7 | 0.48888 | 39110.4 | 0.22089 | 7952.04 | 0.48616 | 5833.92 | 1 | 5000 | 7952.04 | 5833.92 | 0 | 0 | 0 | 0 | 20324.44 | 0 | 0 | 0 | 0 | 0 | 20324.44
2022110511 | 7 | 0.49693 | 39754.4 | 0.20055 | 7219.8 | 0.65459 | 7855.08 | 1 | 5000 | 7219.8 | 7855.08 | 0 | 0 | 0 | 0 | 19679.52 | 0 | 0 | 0 | 0 | 0 | 19679.52
2022110512 | 7 | 0.5002 | 40016 | 0.2806 | 10101.6 | 0.66506 | 7980.72 | 1 | 5000 | 10101.6 | 7980.72 | 0 | 0 | 0 | 0 | 16933.68 | 0 | 0 | 0 | 0 | 0 | 16933.68
2022110513 | 7 | 0.50391 | 40312.8 | 0.33553 | 12079.08 | 0.67249 | 8069.88 | 1 | 5000 | 12079.08 | 8069.88 | 0 | 0 | 0 | 0 | 15163.84 | 0 | 0 | 0 | 0 | 0 | 15163.84
2022110514 | 7 | 0.50991 | 40792.8 | 0.3805 | 13698 | 0.63613 | 7633.56 | 1 | 5000 | 13698 | 7633.56 | 0 | 0 | 0 | 0 | 14461.24 | 0 | 0 | 0 | 0 | 0 | 14461.24
2022110515 | 7 | 0.51821 | 41456.8 | 0.42984 | 15474.24 | 0.48382 | 5805.84 | 1 | 5000 | 15474.24 | 5805.84 | 0 | 0 | 0 | 0 | 15176.72 | 0 | 0 | 0 | 0 | 0 | 15176.72
2022110516 | 7 | 0.5274 | 42192 | 0.44372 | 15973.92 | 0.41094 | 4931.28 | 1 | 5000 | 15973.92 | 4931.28 | 0 | 0 | 0 | 0 | 16286.8 | 0 | 0 | 0 | 0 | 0 | 16286.8
2022110517 | 7 | 0.53277 | 42621.6 | 0.44196 | 15910.56 | 0.37216 | 4465.92 | 1 | 5000 | 15910.56 | 4465.92 | 0 | 0 | 0 | 0 | 17245.12 | 0 | 0 | 0 | 0 | 0 | 17245.12
2022110518 | 7 | 0.5332 | 42656 | 0.43819 | 15774.84 | 0.23826 | 2859.12 | 1 | 5000 | 15774.84 | 2859.12 | 0 | 0 | 0 | 0 | 19022.04 | 0 | 0 | 0 | 0 | 0 | 19022.04
2022110519 | 7 | 0.52944 | 42355.2 | 0.44731 | 16103.16 | 0.04604 | 552.48 | 1 | 5000 | 16103.16 | 552.48 | 0 | 0 | 0 | 0 | 20699.56 | 0 | 0 | 0 | 0 | 0 | 20699.56
2022110520 | 7 | 0.53222 | 42577.6 | 0.52718 | 18978.48 | 0 | 0 | 1 | 5000 | 18978.48 | 0 | 0 | 0 | 0 | 0 | 18599.12 | 0 | 0 | 0 | 0 | 0 | 18599.12
2022110521 | 7 | 0.52072 | 41657.6 | 0.55393 | 19941.48 | 0 | 0 | 1 | 5000 | 19941.48 | 0 | 0 | 0 | 0 | 0 | 16716.12 | 0 | 0 | 0 | 0 | 0 | 16716.12
2022110522 | 7 | 0.50597 | 40477.6 | 0.53868 | 19392.48 | 0 | 0 | 1 | 5000 | 19392.48 | 0 | 0 | 0 | 0 | 0 | 16085.12 | 0 | 0 | 0 | 0 | 0 | 16085.12
2022110523 | 7 | 0.48866 | 39092.8 | 0.53783 | 19361.88 | 0 | 0 | 1 | 5000 | 19361.88 | 0 | 0 | 0 | 0 | 0 | 14730.92 | 0 | 0 | 0 | 0 | 0 | 14730.92
2022110524 | 7 | 0.47357 | 37885.6 | 0.52921 | 19051.56 | 4e-05 | 0.48 | 1 | 5000 | 19051.56 | 0.48 | 0 | 0 | 0 | 0 | 13833.56 | 0 | 0 | 0 | 0 | 0 | 13833.56
2022110601 | 1 | 0.4514 | 36112 | 0.52712 | 18976.32 | 4e-05 | 0.48 | 1 | 5000 | 18976.32 | 0.48 | 0 | 0 | 0 | 0 | 12135.2 | 0 | 0 | 0 | 0 | 0 | 12135.2
2022110602 | 1 | 0.43717 | 34973.6 | 0.52492 | 18897.12 | 0 | 0 | 1 | 5000 | 18897.12 | 0 | 0 | 0 | 0 | 0 | 11076.48 | 0 | 0 | 0 | 0 | 0 | 11076.48
2022110602 | 1 | 0.42895 | 34316 | 0.5239 | 18860.4 | 0 | 0 | 1 | 5000 | 18860.4 | 0 | 0 | 0 | 0 | 0 | 10455.6 | 0 | 0 | 0 | 0 | 0 | 10455.6
2022110603 | 1 | 0.42522 | 34017.6 | 0.52088 | 18751.68 | 4e-05 | 0.48 | 1 | 5000 | 18751.68 | 0.48 | 0 | 0 | 0 | 0 | 10265.44 | 0 | 0 | 0 | 0 | 0 | 10265.44
2022110604 | 1 | 0.42182 | 33745.6 | 0.50969 | 18348.84 | 4e-05 | 0.48 | 1 | 5000 | 18348.84 | 0.48 | 0 | 0 | 0 | 0 | 10396.28 | 0 | 0 | 0 | 0 | 0 | 10396.28
2022110605 | 1 | 0.4225 | 33800 | 0.50434 | 18156.24 | 0 | 0 | 1 | 5000 | 18156.24 | 0 | 0 | 0 | 0 | 0 | 10643.76 | 0 | 0 | 0 | 0 | 0 | 10643.76
2022110606 | 1 | 0.42994 | 34395.2 | 0.49967 | 17988.12 | 4e-05 | 0.48 | 1 | 5000 | 17988.12 | 0.48 | 0 | 0 | 0 | 0 | 11406.6 | 0 | 0 | 0 | 0 | 0 | 11406.6
2022110607 | 1 | 0.44169 | 35335.2 | 0.49593 | 17853.48 | 0.0002 | 2.4 | 1 | 5000 | 17853.48 | 2.4 | 0 | 0 | 0 | 0 | 12479.32 | 0 | 0 | 0 | 0 | 0 | 12479.32
2022110608 | 1 | 0.45757 | 36605.6 | 0.47067 | 16944.12 | 0.08514 | 1021.68 | 1 | 5000 | 16944.12 | 1021.68 | 0 | 0 | 0 | 0 | 13639.8 | 0 | 0 | 0 | 0 | 0 | 13639.8
2022110609 | 1 | 0.47825 | 38260 | 0.36611 | 13179.96 | 0.41334 | 4960.08 | 1 | 5000 | 13179.96 | 4960.08 | 0 | 0 | 0 | 0 | 15119.96 | 0 | 0 | 0 | 0 | 0 | 15119.96
2022110610 | 1 | 0.49863 | 39890.4 | 0.26473 | 9530.28 | 0.61016 | 7321.92 | 1 | 5000 | 9530.28 | 7321.92 | 0 | 0 | 0 | 0 | 18038.2 | 0 | 0 | 0 | 0 | 0 | 18038.2
2022110611 | 1 | 0.51696 | 41356.8 | 0.234 | 8424 | 0.63967 | 7676.04 | 1 | 5000 | 8424 | 7676.04 | 0 | 0 | 0 | 0 | 20256.76 | 0 | 0 | 0 | 0 | 0 | 20256.76
2022110612 | 1 | 0.53555 | 42844 | 0.2075 | 7470 | 0.62593 | 7511.16 | 1 | 5000 | 7470 | 7511.16 | 0 | 0 | 0 | 0 | 22862.84 | 0 | 0 | 0 | 0 | 0 | 22862.84
2022110613 | 1 | 0.55697 | 44557.6 | 0.17723 | 6380.28 | 0.6323 | 7587.6 | 1 | 5000 | 6380.28 | 7587.6 | 0 | 0 | 0 | 0 | 25589.72 | 0 | 0 | 0 | 0 | 0 | 25589.72
2022110614 | 1 | 0.58052 | 46441.6 | 0.16531 | 5951.16 | 0.64894 | 7787.28 | 1 | 5000 | 5951.16 | 7787.28 | 0 | 0 | 0 | 0 | 27703.16 | 0 | 0 | 0 | 0 | 0 | 27703.16
2022110615 | 1 | 0.59844 | 47875.2 | 0.16046 | 5776.56 | 0.66103 | 7932.36 | 1 | 5000 | 5776.56 | 7932.36 | 0 | 0 | 0 | 0 | 29166.28 | 0 | 0 | 0 | 0 | 0 | 29166.28
2022110616 | 1 | 0.60551 | 48440.8 | 0.14654 | 5275.44 | 0.63096 | 7571.52 | 1 | 5000 | 5275.44 | 7571.52 | 0 | 0 | 0 | 0 | 30593.84 | 0 | 0 | 0 | 0 | 0 | 30593.84
2022110617 | 1 | 0.60795 | 48636 | 0.13158 | 4736.88 | 0.42232 | 5067.84 | 1 | 5000 | 4736.88 | 5067.84 | 0 | 0 | 0 | 0 | 33831.28 | 0 | 0 | 0 | 0 | 0 | 33831.28
2022110618 | 1 | 0.59781 | 47824.8 | 0.13782 | 4961.52 | 0.07007 | 840.84 | 1 | 5000 | 4961.52 | 840.84 | 0 | 0 | 0 | 0 | 37022.44 | 0 | 0 | 0 | 0 | 0 | 37022.44
2022110619 | 1 | 0.59954 | 47963.2 | 0.18876 | 6795.36 | 0 | 0 | 1 | 5000 | 6795.36 | 0 | 0 | 0 | 0 | 0 | 36167.84 | 0 | 0 | 0 | 0 | 0 | 36167.84
2022110620 | 1 | 0.59586 | 47668.8 | 0.27451 | 9882.36 | 0 | 0 | 1 | 5000 | 9882.36 | 0 | 0 | 0 | 0 | 0 | 32786.44 | 0 | 0 | 0 | 0 | 0 | 32786.44
2022110621 | 1 | 0.57992 | 46393.6 | 0.33612 | 12100.32 | 0 | 0 | 1 | 5000 | 12100.32 | 0 | 0 | 0 | 0 | 0 | 29293.28 | 0 | 0 | 0 | 0 | 0 | 29293.28
2022110622 | 1 | 0.56278 | 45022.4 | 0.36949 | 13301.64 | 0 | 0 | 1 | 5000 | 13301.64 | 0 | 0 | 0 | 0 | 0 | 26720.76 | 0 | 0 | 0 | 0 | 0 | 26720.76
2022110623 | 1 | 0.5366 | 42928 | 0.39911 | 14367.96 | 0 | 0 | 1 | 5000 | 14367.96 | 0 | 0 | 0 | 0 | 0 | 23560.04 | 0 | 0 | 0 | 0 | 0 | 23560.04
2022110624 | 1 | 0.50931 | 40744.8 | 0.39278 | 14140.08 | 0 | 0 | 1 | 5000 | 14140.08 | 0 | 0 | 0 | 0 | 0 | 21604.72 | 0 | 0 | 0 | 0 | 0 | 21604.72
2022110701 | 2 | 0.48547 | 38837.6 | 0.34607 | 12458.52 | 0 | 0 | 1 | 5000 | 12458.52 | 0 | 0 | 0 | 0 | 0 | 21379.08 | 0 | 0 | 0 | 0 | 0 | 21379.08
2022110702 | 2 | 0.47185 | 37748 | 0.31483 | 11333.88 | 0 | 0 | 1 | 5000 | 11333.88 | 0 | 0 | 0 | 0 | 0 | 21414.12 | 0 | 0 | 0 | 0 | 0 | 21414.12
2022110703 | 2 | 0.46433 | 37146.4 | 0.27626 | 9945.36 | 0 | 0 | 1 | 5000 | 9945.36 | 0 | 0 | 0 | 0 | 0 | 22201.04 | 0 | 0 | 0 | 0 | 0 | 22201.04
2022110704 | 2 | 0.46161 | 36928.8 | 0.25625 | 9225 | 0 | 0 | 1 | 5000 | 9225 | 0 | 0 | 0 | 0 | 0 | 22703.8 | 0 | 0 | 0 | 0 | 0 | 22703.8
2022110705 | 2 | 0.46994 | 37595.2 | 0.23582 | 8489.52 | 0 | 0 | 1 | 5000 | 8489.52 | 0 | 0 | 0 | 0 | 0 | 24105.68 | 0 | 0 | 0 | 0 | 0 | 24105.68
2022110706 | 2 | 0.49005 | 39204 | 0.2046 | 7365.6 | 0 | 0 | 1 | 5000 | 7365.6 | 0 | 0 | 0 | 0 | 0 | 26838.4 | 0 | 0 | 0 | 0 | 0 | 26838.4
2022110707 | 2 | 0.52175 | 41740 | 0.18426 | 6633.36 | 0.00013 | 1.56 | 1 | 5000 | 6633.36 | 1.56 | 0 | 0 | 0 | 0 | 30105.08 | 0 | 0 | 0 | 0 | 0 | 30105.08
2022110708 | 2 | 0.54403 | 43522.4 | 0.16087 | 5791.32 | 0.04115 | 493.8 | 1 | 5000 | 5791.32 | 493.8 | 0 | 0 | 0 | 0 | 32237.28 | 0 | 0 | 0 | 0 | 0 | 32237.28
2022110709 | 2 | 0.55967 | 44773.6 | 0.11955 | 4303.8 | 0.21557 | 2586.84 | 1 | 5000 | 4303.8 | 2586.84 | 0 | 0 | 0 | 0 | 32882.96 | 0 | 0 | 0 | 0 | 0 | 32882.96
2022110710 | 2 | 0.57865 | 46292 | 0.11268 | 4056.48 | 0.29502 | 3540.24 | 1 | 5000 | 4056.48 | 3540.24 | 0 | 0 | 0 | 0 | 33695.28 | 0 | 0 | 0 | 0 | 0 | 33695.28
2022110711 | 2 | 0.5984 | 47872 | 0.1121 | 4035.6 | 0.36222 | 4346.64 | 1 | 5000 | 4035.6 | 4346.64 | 0 | 0 | 0 | 0 | 34489.76 | 0 | 0 | 0 | 0 | 0 | 34489.76
2022110712 | 2 | 0.62122 | 49697.6 | 0.11147 | 4012.92 | 0.43083 | 5169.96 | 1 | 5000 | 4012.92 | 5169.96 | 0 | 0 | 0 | 0 | 35514.72 | 0 | 0 | 0 | 0 | 0 | 35514.72
2022110713 | 2 | 0.64494 | 51595.2 | 0.11978 | 4312.08 | 0.47343 | 5681.16 | 1 | 5000 | 4312.08 | 5681.16 | 0 | 0 | 0 | 0 | 36601.96 | 0 | 0 | 0 | 0 | 0 | 36601.96
2022110714 | 2 | 0.66192 | 52953.6 | 0.14302 | 5148.72 | 0.48119 | 5774.28 | 1 | 5000 | 5148.72 | 5774.28 | 0 | 0 | 0 | 0 | 37030.6 | 0 | 0 | 0 | 0 | 0 | 37030.6
2022110715 | 2 | 0.66795 | 53436 | 0.17527 | 6309.72 | 0.4669 | 5602.8 | 1 | 5000 | 6309.72 | 5602.8 | 0 | 0 | 0 | 0 | 36523.48 | 0 | 0 | 0 | 0 | 0 | 36523.48
2022110716 | 2 | 0.66786 | 53428.8 | 0.19964 | 7187.04 | 0.43182 | 5181.84 | 1 | 5000 | 7187.04 | 5181.84 | 0 | 0 | 0 | 0 | 36059.92 | 0 | 0 | 0 | 0 | 0 | 36059.92
2022110717 | 2 | 0.66053 | 52842.4 | 0.21238 | 7645.68 | 0.25974 | 3116.88 | 1 | 5000 | 7645.68 | 3116.88 | 0 | 0 | 0 | 0 | 37079.84 | 0 | 0 | 0 | 0 | 0 | 37079.84
2022110718 | 2 | 0.65187 | 52149.6 | 0.23517 | 8466.12 | 0.03332 | 399.84 | 1 | 5000 | 8466.12 | 399.84 | 0 | 0 | 0 | 0 | 38283.64 | 0 | 0 | 0 | 0 | 0 | 38283.64
2022110719 | 2 | 0.64719 | 51775.2 | 0.28946 | 10420.56 | 0 | 0 | 1 | 5000 | 10420.56 | 0 | 0 | 0 | 0 | 0 | 36354.64 | 0 | 0 | 0 | 0 | 0 | 36354.64
2022110720 | 2 | 0.63017 | 50413.6 | 0.34987 | 12595.32 | 0 | 0 | 1 | 5000 | 12595.32 | 0 | 0 | 0 | 0 | 0 | 32818.28 | 0 | 0 | 0 | 0 | 0 | 32818.28
2022110721 | 2 | 0.6096 | 48768 | 0.38579 | 13888.44 | 0 | 0 | 1 | 5000 | 13888.44 | 0 | 0 | 0 | 0 | 0 | 29879.56 | 0 | 0 | 0 | 0 | 0 | 29879.56
2022110722 | 2 | 0.58568 | 46854.4 | 0.40329 | 14518.44 | 0 | 0 | 1 | 5000 | 14518.44 | 0 | 0 | 0 | 0 | 0 | 27335.96 | 0 | 0 | 0 | 0 | 0 | 27335.96
2022110723 | 2 | 0.55029 | 44023.2 | 0.41484 | 14934.24 | 0 | 0 | 1 | 5000 | 14934.24 | 0 | 0 | 0 | 0 | 0 | 24088.96 | 0 | 0 | 0 | 0 | 0 | 24088.96
2022110724 | 2 | 0.51833 | 41466.4 | 0.44518 | 16026.48 | 0 | 0 | 1 | 5000 | 16026.48 | 0 | 0 | 0 | 0 | 0 | 20439.92 | 0 | 0 | 0 | 0 | 0 | 20439.92
2022110801 | 3 | 0.49212 | 39369.6 | 0.44885 | 16158.6 | 0 | 0 | 1 | 5000 | 16158.6 | 0 | 0 | 0 | 0 | 0 | 18211 | 0 | 0 | 0 | 0 | 0 | 18211
2022110802 | 3 | 0.47618 | 38094.4 | 0.43796 | 15766.56 | 0 | 0 | 1 | 5000 | 15766.56 | 0 | 0 | 0 | 0 | 0 | 17327.84 | 0 | 0 | 0 | 0 | 0 | 17327.84
2022110803 | 3 | 0.46354 | 37083.2 | 0.41959 | 15105.24 | 0 | 0 | 1 | 5000 | 15105.24 | 0 | 0 | 0 | 0 | 0 | 16977.96 | 0 | 0 | 0 | 0 | 0 | 16977.96
2022110804 | 3 | 0.45867 | 36693.6 | 0.41747 | 15028.92 | 0 | 0 | 1 | 5000 | 15028.92 | 0 | 0 | 0 | 0 | 0 | 16664.68 | 0 | 0 | 0 | 0 | 0 | 16664.68
2022110805 | 3 | 0.46345 | 37076 | 0.42452 | 15282.72 | 0 | 0 | 1 | 5000 | 15282.72 | 0 | 0 | 0 | 0 | 0 | 16793.28 | 0 | 0 | 0 | 0 | 0 | 16793.28
2022110806 | 3 | 0.47607 | 38085.6 | 0.42139 | 15170.04 | 0 | 0 | 1 | 5000 | 15170.04 | 0 | 0 | 0 | 0 | 0 | 17915.56 | 0 | 0 | 0 | 0 | 0 | 17915.56
2022110807 | 3 | 0.51692 | 41353.6 | 0.41564 | 14963.04 | 0.0001 | 1.2 | 1 | 5000 | 14963.04 | 1.2 | 0 | 0 | 0 | 0 | 21389.36 | 0 | 0 | 0 | 0 | 0 | 21389.36
2022110808 | 3 | 0.53375 | 42700 | 0.39675 | 14283 | 0.037 | 444 | 1 | 5000 | 14283 | 444 | 0 | 0 | 0 | 0 | 22973 | 0 | 0 | 0 | 0 | 0 | 22973
2022110809 | 3 | 0.54934 | 43947.2 | 0.36963 | 13306.68 | 0.1673 | 2007.6 | 1 | 5000 | 13306.68 | 2007.6 | 0 | 0 | 0 | 0 | 23632.92 | 0 | 0 | 0 | 0 | 0 | 23632.92
2022110810 | 3 | 0.57247 | 45797.6 | 0.39254 | 14131.44 | 0.26219 | 3146.28 | 1 | 5000 | 14131.44 | 3146.28 | 0 | 0 | 0 | 0 | 23519.88 | 0 | 0 | 0 | 0 | 0 | 23519.88
2022110811 | 3 | 0.59889 | 47911.2 | 0.43689 | 15728.04 | 0.30508 | 3660.96 | 1 | 5000 | 15728.04 | 3660.96 | 0 | 0 | 0 | 0 | 23522.2 | 0 | 0 | 0 | 0 | 0 | 23522.2
2022110812 | 3 | 0.61971 | 49576.8 | 0.43813 | 15772.68 | 0.34599 | 4151.88 | 1 | 5000 | 15772.68 | 4151.88 | 0 | 0 | 0 | 0 | 24652.24 | 0 | 0 | 0 | 0 | 0 | 24652.24
2022110813 | 3 | 0.63784 | 51027.2 | 0.43111 | 15519.96 | 0.37874 | 4544.88 | 1 | 5000 | 15519.96 | 4544.88 | 0 | 0 | 0 | 0 | 25962.36 | 0 | 0 | 0 | 0 | 0 | 25962.36
2022110814 | 3 | 0.65181 | 52144.8 | 0.43708 | 15734.88 | 0.39174 | 4700.88 | 1 | 5000 | 15734.88 | 4700.88 | 0 | 0 | 0 | 0 | 26709.04 | 0 | 0 | 0 | 0 | 0 | 26709.04
2022110815 | 3 | 0.66143 | 52914.4 | 0.45894 | 16521.84 | 0.34852 | 4182.24 | 1 | 5000 | 16521.84 | 4182.24 | 0 | 0 | 0 | 0 | 27210.32 | 0 | 0 | 0 | 0 | 0 | 27210.32
2022110816 | 3 | 0.6672 | 53376 | 0.47686 | 17166.96 | 0.26554 | 3186.48 | 1 | 5000 | 17166.96 | 3186.48 | 0 | 0 | 0 | 0 | 28022.56 | 0 | 0 | 0 | 0 | 0 | 28022.56
2022110817 | 3 | 0.66293 | 53034.4 | 0.49694 | 17889.84 | 0.1469 | 1762.8 | 1 | 5000 | 17889.84 | 1762.8 | 0 | 0 | 0 | 0 | 28381.76 | 0 | 0 | 0 | 0 | 0 | 28381.76
2022110818 | 3 | 0.65561 | 52448.8 | 0.50867 | 18312.12 | 0.02576 | 309.12 | 1 | 5000 | 18312.12 | 309.12 | 0 | 0 | 0 | 0 | 28827.56 | 0 | 0 | 0 | 0 | 0 | 28827.56
2022110819 | 3 | 0.65345 | 52276 | 0.51639 | 18590.04 | 0 | 0 | 1 | 5000 | 18590.04 | 0 | 0 | 0 | 0 | 0 | 28685.96 | 0 | 0 | 0 | 0 | 0 | 28685.96
2022110820 | 3 | 0.63732 | 50985.6 | 0.54024 | 19448.64 | 0 | 0 | 1 | 5000 | 19448.64 | 0 | 0 | 0 | 0 | 0 | 26536.96 | 0 | 0 | 0 | 0 | 0 | 26536.96
2022110821 | 3 | 0.61864 | 49491.2 | 0.55184 | 19866.24 | 0 | 0 | 1 | 5000 | 19866.24 | 0 | 0 | 0 | 0 | 0 | 24624.96 | 0 | 0 | 0 | 0 | 0 | 24624.96
2022110822 | 3 | 0.59438 | 47550.4 | 0.55973 | 20150.28 | 0 | 0 | 1 | 5000 | 20150.28 | 0 | 0 | 0 | 0 | 0 | 22400.12 | 0 | 0 | 0 | 0 | 0 | 22400.12
2022110823 | 3 | 0.55869 | 44695.2 | 0.55381 | 19937.16 | 0 | 0 | 1 | 5000 | 19937.16 | 0 | 0 | 0 | 0 | 0 | 19758.04 | 0 | 0 | 0 | 0 | 0 | 19758.04
2022110824 | 3 | 0.52265 | 41812 | 0.54473 | 19610.28 | 0 | 0 | 1 | 5000 | 19610.28 | 0 | 0 | 0 | 0 | 0 | 17201.72 | 0 | 0 | 0 | 0 | 0 | 17201.72
2022110901 | 4 | 0.49634 | 39707.2 | 0.53022 | 19087.92 | 0 | 0 | 1 | 5000 | 19087.92 | 0 | 0 | 0 | 0 | 0 | 15619.28 | 0 | 0 | 0 | 0 | 0 | 15619.28
2022110902 | 4 | 0.47831 | 38264.8 | 0.52343 | 18843.48 | 0 | 0 | 1 | 5000 | 18843.48 | 0 | 0 | 0 | 0 | 0 | 14421.32 | 0 | 0 | 0 | 0 | 0 | 14421.32
2022110903 | 4 | 0.46758 | 37406.4 | 0.51887 | 18679.32 | 0 | 0 | 1 | 5000 | 18679.32 | 0 | 0 | 0 | 0 | 0 | 13727.08 | 0 | 0 | 0 | 0 | 0 | 13727.08
2022110904 | 4 | 0.46234 | 36987.2 | 0.51273 | 18458.28 | 0 | 0 | 1 | 5000 | 18458.28 | 0 | 0 | 0 | 0 | 0 | 13528.92 | 0 | 0 | 0 | 0 | 0 | 13528.92
2022110905 | 4 | 0.46639 | 37311.2 | 0.51009 | 18363.24 | 0 | 0 | 1 | 5000 | 18363.24 | 0 | 0 | 0 | 0 | 0 | 13947.96 | 0 | 0 | 0 | 0 | 0 | 13947.96
2022110906 | 4 | 0.48672 | 38937.6 | 0.50491 | 18176.76 | 0 | 0 | 1 | 5000 | 18176.76 | 0 | 0 | 0 | 0 | 0 | 15760.84 | 0 | 0 | 0 | 0 | 0 | 15760.84
2022110907 | 4 | 0.52035 | 41628 | 0.51442 | 18519.12 | 0.00028 | 3.36 | 1 | 5000 | 18519.12 | 3.36 | 0 | 0 | 0 | 0 | 18105.52 | 0 | 0 | 0 | 0 | 0 | 18105.52
2022110908 | 4 | 0.53538 | 42830.4 | 0.51363 | 18490.68 | 0.0391 | 469.2 | 1 | 5000 | 18490.68 | 469.2 | 0 | 0 | 0 | 0 | 18870.52 | 0 | 0 | 0 | 0 | 0 | 18870.52
2022110909 | 4 | 0.55134 | 44107.2 | 0.49795 | 17926.2 | 0.16627 | 1995.24 | 1 | 5000 | 17926.2 | 1995.24 | 0 | 0 | 0 | 0 | 19185.76 | 0 | 0 | 0 | 0 | 0 | 19185.76
2022110910 | 4 | 0.57094 | 45675.2 | 0.52435 | 18876.6 | 0.21254 | 2550.48 | 1 | 5000 | 18876.6 | 2550.48 | 0 | 0 | 0 | 0 | 19248.12 | 0 | 0 | 0 | 0 | 0 | 19248.12
2022110911 | 4 | 0.59388 | 47510.4 | 0.53745 | 19348.2 | 0.2418 | 2901.6 | 1 | 5000 | 19348.2 | 2901.6 | 0 | 0 | 0 | 0 | 20260.6 | 0 | 0 | 0 | 0 | 0 | 20260.6
2022110912 | 4 | 0.61814 | 49451.2 | 0.55067 | 19824.12 | 0.23104 | 2772.48 | 1 | 5000 | 19824.12 | 2772.48 | 0 | 0 | 0 | 0 | 21854.6 | 0 | 0 | 0 | 0 | 0 | 21854.6
2022110913 | 4 | 0.638 | 51040 | 0.54813 | 19732.68 | 0.22741 | 2728.92 | 1 | 5000 | 19732.68 | 2728.92 | 0 | 0 | 0 | 0 | 23578.4 | 0 | 0 | 0 | 0 | 0 | 23578.4
2022110914 | 4 | 0.65528 | 52422.4 | 0.5422 | 19519.2 | 0.2353 | 2823.6 | 1 | 5000 | 19519.2 | 2823.6 | 0 | 0 | 0 | 0 | 25079.6 | 0 | 0 | 0 | 0 | 0 | 25079.6
2022110915 | 4 | 0.66763 | 53410.4 | 0.55605 | 20017.8 | 0.22546 | 2705.52 | 1 | 5000 | 20017.8 | 2705.52 | 0 | 0 | 0 | 0 | 25687.08 | 0 | 0 | 0 | 0 | 0 | 25687.08
2022110916 | 4 | 0.66842 | 53473.6 | 0.56362 | 20290.32 | 0.21498 | 2579.76 | 1 | 5000 | 20290.32 | 2579.76 | 0 | 0 | 0 | 0 | 25603.52 | 0 | 0 | 0 | 0 | 0 | 25603.52
2022110917 | 4 | 0.66624 | 53299.2 | 0.57566 | 20723.76 | 0.10325 | 1239 | 1 | 5000 | 20723.76 | 1239 | 0 | 0 | 0 | 0 | 26336.44 | 0 | 0 | 0 | 0 | 0 | 26336.44
2022110918 | 4 | 0.65512 | 52409.6 | 0.58613 | 21100.68 | 0.01695 | 203.4 | 1 | 5000 | 21100.68 | 203.4 | 0 | 0 | 0 | 0 | 26105.52 | 0 | 0 | 0 | 0 | 0 | 26105.52
2022110919 | 4 | 0.64985 | 51988 | 0.60408 | 21746.88 | 0.00013 | 1.56 | 1 | 5000 | 21746.88 | 1.56 | 0 | 0 | 0 | 0 | 25239.56 | 0 | 0 | 0 | 0 | 0 | 25239.56
2022110920 | 4 | 0.62821 | 50256.8 | 0.61557 | 22160.52 | 0 | 0 | 1 | 5000 | 22160.52 | 0 | 0 | 0 | 0 | 0 | 23096.28 | 0 | 0 | 0 | 0 | 0 | 23096.28
2022110921 | 4 | 0.6076 | 48608 | 0.60018 | 21606.48 | 0 | 0 | 1 | 5000 | 21606.48 | 0 | 0 | 0 | 0 | 0 | 22001.52 | 0 | 0 | 0 | 0 | 0 | 22001.52
2022110922 | 4 | 0.58298 | 46638.4 | 0.5797 | 20869.2 | 0 | 0 | 1 | 5000 | 20869.2 | 0 | 0 | 0 | 0 | 0 | 20769.2 | 0 | 0 | 0 | 0 | 0 | 20769.2
2022110923 | 4 | 0.5515 | 44120 | 0.56873 | 20474.28 | 0.00027 | 3.24 | 1 | 5000 | 20474.28 | 3.24 | 0 | 0 | 0 | 0 | 18642.48 | 0 | 0 | 0 | 0 | 0 | 18642.48
2022110924 | 4 | 0.5164 | 41312 | 0.56129 | 20206.44 | 0 | 0 | 1 | 5000 | 20206.44 | 0 | 0 | 0 | 0 | 0 | 16105.56 | 0 | 0 | 0 | 0 | 0 | 16105.56
2022111001 | 5 | 0.48977 | 39181.6 | 0.56022 | 20167.92 | 0 | 0 | 1 | 5000 | 20167.92 | 0 | 0 | 0 | 0 | 0 | 14013.68 | 0 | 0 | 0 | 0 | 0 | 14013.68
2022111002 | 5 | 0.47217 | 37773.6 | 0.56144 | 20211.84 | 0 | 0 | 1 | 5000 | 20211.84 | 0 | 0 | 0 | 0 | 0 | 12561.76 | 0 | 0 | 0 | 0 | 0 | 12561.76
2022111003 | 5 | 0.46131 | 36904.8 | 0.54965 | 19787.4 | 0 | 0 | 1 | 5000 | 19787.4 | 0 | 0 | 0 | 0 | 0 | 12117.4 | 0 | 0 | 0 | 0 | 0 | 12117.4
2022111004 | 5 | 0.45758 | 36606.4 | 0.5445 | 19602 | 0 | 0 | 1 | 5000 | 19602 | 0 | 0 | 0 | 0 | 0 | 12004.4 | 0 | 0 | 0 | 0 | 0 | 12004.4
2022111005 | 5 | 0.46165 | 36932 | 0.53456 | 19244.16 | 0 | 0 | 1 | 5000 | 19244.16 | 0 | 0 | 0 | 0 | 0 | 12687.84 | 0 | 0 | 0 | 0 | 0 | 12687.84
2022111006 | 5 | 0.48081 | 38464.8 | 0.514 | 18504 | 0 | 0 | 1 | 5000 | 18504 | 0 | 0 | 0 | 0 | 0 | 14960.8 | 0 | 0 | 0 | 0 | 0 | 14960.8
2022111007 | 5 | 0.51253 | 41002.4 | 0.46175 | 16623 | 0.00015 | 1.8 | 1 | 5000 | 16623 | 1.8 | 0 | 0 | 0 | 0 | 19377.6 | 0 | 0 | 0 | 0 | 0 | 19377.6
2022111008 | 5 | 0.52337 | 41869.6 | 0.39916 | 14369.76 | 0.05611 | 673.32 | 1 | 5000 | 14369.76 | 673.32 | 0 | 0 | 0 | 0 | 21826.52 | 0 | 0 | 0 | 0 | 0 | 21826.52
2022111009 | 5 | 0.5396 | 43168 | 0.31976 | 11511.36 | 0.31535 | 3784.2 | 1 | 5000 | 11511.36 | 3784.2 | 0 | 0 | 0 | 0 | 22872.44 | 0 | 0 | 0 | 0 | 0 | 22872.44
2022111010 | 5 | 0.564 | 45120 | 0.32923 | 11852.28 | 0.49736 | 5968.32 | 1 | 5000 | 11852.28 | 5968.32 | 0 | 0 | 0 | 0 | 22299.4 | 0 | 0 | 0 | 0 | 0 | 22299.4
2022111011 | 5 | 0.58239 | 46591.2 | 0.32964 | 11867.04 | 0.51362 | 6163.44 | 1 | 5000 | 11867.04 | 6163.44 | 0 | 0 | 0 | 0 | 23560.72 | 0 | 0 | 0 | 0 | 0 | 23560.72
2022111012 | 5 | 0.59536 | 47628.8 | 0.26162 | 9418.32 | 0.5066 | 6079.2 | 1 | 5000 | 9418.32 | 6079.2 | 0 | 0 | 0 | 0 | 27131.28 | 0 | 0 | 0 | 0 | 0 | 27131.28
2022111013 | 5 | 0.60801 | 48640.8 | 0.1938 | 6976.8 | 0.50734 | 6088.08 | 1 | 5000 | 6976.8 | 6088.08 | 0 | 0 | 0 | 0 | 30575.92 | 0 | 0 | 0 | 0 | 0 | 30575.92
2022111014 | 5 | 0.62028 | 49622.4 | 0.14846 | 5344.56 | 0.5275 | 6330 | 1 | 5000 | 5344.56 | 6330 | 0 | 0 | 0 | 0 | 32947.84 | 0 | 0 | 0 | 0 | 0 | 32947.84
2022111015 | 5 | 0.62882 | 50305.6 | 0.1349 | 4856.4 | 0.54923 | 6590.76 | 1 | 5000 | 4856.4 | 6590.76 | 0 | 0 | 0 | 0 | 33858.44 | 0 | 0 | 0 | 0 | 0 | 33858.44
2022111016 | 5 | 0.63159 | 50527.2 | 0.14243 | 5127.48 | 0.52185 | 6262.2 | 1 | 5000 | 5127.48 | 6262.2 | 0 | 0 | 0 | 0 | 34137.52 | 0 | 0 | 0 | 0 | 0 | 34137.52
2022111017 | 5 | 0.62338 | 49870.4 | 0.16403 | 5905.08 | 0.31214 | 3745.68 | 1 | 5000 | 5905.08 | 3745.68 | 0 | 0 | 0 | 0 | 35219.64 | 0 | 0 | 0 | 0 | 0 | 35219.64
2022111018 | 5 | 0.6143 | 49144 | 0.19688 | 7087.68 | 0.03458 | 414.96 | 1 | 5000 | 7087.68 | 414.96 | 0 | 0 | 0 | 0 | 36641.36 | 0 | 0 | 0 | 0 | 0 | 36641.36
2022111019 | 5 | 0.61576 | 49260.8 | 0.24154 | 8695.44 | 0 | 0 | 1 | 5000 | 8695.44 | 0 | 0 | 0 | 0 | 0 | 35565.36 | 0 | 0 | 0 | 0 | 0 | 35565.36
2022111020 | 5 | 0.60264 | 48211.2 | 0.2677 | 9637.2 | 0 | 0 | 1 | 5000 | 9637.2 | 0 | 0 | 0 | 0 | 0 | 33574 | 0 | 0 | 0 | 0 | 0 | 33574
2022111021 | 5 | 0.58424 | 46739.2 | 0.2945 | 10602 | 0 | 0 | 1 | 5000 | 10602 | 0 | 0 | 0 | 0 | 0 | 31137.2 | 0 | 0 | 0 | 0 | 0 | 31137.2
2022111022 | 5 | 0.56636 | 45308.8 | 0.34808 | 12530.88 | 0 | 0 | 1 | 5000 | 12530.88 | 0 | 0 | 0 | 0 | 0 | 27777.92 | 0 | 0 | 0 | 0 | 0 | 27777.92
2022111023 | 5 | 0.53285 | 42628 | 0.38124 | 13724.64 | 0 | 0 | 1 | 5000 | 13724.64 | 0 | 0 | 0 | 0 | 0 | 23903.36 | 0 | 0 | 0 | 0 | 0 | 23903.36
2022111024 | 5 | 0.49871 | 39896.8 | 0.35475 | 12771 | 0 | 0 | 1 | 5000 | 12771 | 0 | 0 | 0 | 0 | 0 | 22125.8 | 0 | 0 | 0 | 0 | 0 | 22125.8
2022111101 | 6 | 0.47273 | 37818.4 | 0.35923 | 12932.28 | 0 | 0 | 1 | 5000 | 12932.28 | 0 | 0 | 0 | 0 | 0 | 19886.12 | 0 | 0 | 0 | 0 | 0 | 19886.12
2022111102 | 6 | 0.45541 | 36432.8 | 0.36089 | 12992.04 | 0 | 0 | 1 | 5000 | 12992.04 | 0 | 0 | 0 | 0 | 0 | 18440.76 | 0 | 0 | 0 | 0 | 0 | 18440.76
2022111103 | 6 | 0.44413 | 35530.4 | 0.3959 | 14252.4 | 0 | 0 | 1 | 5000 | 14252.4 | 0 | 0 | 0 | 0 | 0 | 16278 | 0 | 0 | 0 | 0 | 0 | 16278
2022111104 | 6 | 0.43939 | 35151.2 | 0.41435 | 14916.6 | 0 | 0 | 1 | 5000 | 14916.6 | 0 | 0 | 0 | 0 | 0 | 15234.6 | 0 | 0 | 0 | 0 | 0 | 15234.6
2022111105 | 6 | 0.44525 | 35620 | 0.47531 | 17111.16 | 0 | 0 | 1 | 5000 | 17111.16 | 0 | 0 | 0 | 0 | 0 | 13508.84 | 0 | 0 | 0 | 0 | 0 | 13508.84
2022111106 | 6 | 0.46505 | 37204 | 0.53602 | 19296.72 | 0 | 0 | 1 | 5000 | 19296.72 | 0 | 0 | 0 | 0 | 0 | 12907.28 | 0 | 0 | 0 | 0 | 0 | 12907.28
2022111107 | 6 | 0.4999 | 39992 | 0.56089 | 20192.04 | 0.00014 | 1.68 | 1 | 5000 | 20192.04 | 1.68 | 0 | 0 | 0 | 0 | 14798.28 | 0 | 0 | 0 | 0 | 0 | 14798.28
2022111108 | 6 | 0.5166 | 41328 | 0.53973 | 19430.28 | 0.03671 | 440.52 | 1 | 5000 | 19430.28 | 440.52 | 0 | 0 | 0 | 0 | 16457.2 | 0 | 0 | 0 | 0 | 0 | 16457.2
2022111109 | 6 | 0.53754 | 43003.2 | 0.5185 | 18666 | 0.12366 | 1483.92 | 1 | 5000 | 18666 | 1483.92 | 0 | 0 | 0 | 0 | 17853.28 | 0 | 0 | 0 | 0 | 0 | 17853.28
2022111110 | 6 | 0.56143 | 44914.4 | 0.54583 | 19649.88 | 0.13548 | 1625.76 | 1 | 5000 | 19649.88 | 1625.76 | 0 | 0 | 0 | 0 | 18638.76 | 0 | 0 | 0 | 0 | 0 | 18638.76
2022111111 | 6 | 0.57746 | 46196.8 | 0.54067 | 19464.12 | 0.13474 | 1616.88 | 1 | 5000 | 19464.12 | 1616.88 | 0 | 0 | 0 | 0 | 20115.8 | 0 | 0 | 0 | 0 | 0 | 20115.8
2022111112 | 6 | 0.5898 | 47184 | 0.52989 | 19076.04 | 0.14546 | 1745.52 | 1 | 5000 | 19076.04 | 1745.52 | 0 | 0 | 0 | 0 | 21362.44 | 0 | 0 | 0 | 0 | 0 | 21362.44
2022111113 | 6 | 0.59511 | 47608.8 | 0.52162 | 18778.32 | 0.1562 | 1874.4 | 1 | 5000 | 18778.32 | 1874.4 | 0 | 0 | 0 | 0 | 21956.08 | 0 | 0 | 0 | 0 | 0 | 21956.08
2022111114 | 6 | 0.59566 | 47652.8 | 0.51446 | 18520.56 | 0.16627 | 1995.24 | 1 | 5000 | 18520.56 | 1995.24 | 0 | 0 | 0 | 0 | 22137 | 0 | 0 | 0 | 0 | 0 | 22137
2022111115 | 6 | 0.59168 | 47334.4 | 0.51036 | 18372.96 | 0.16979 | 2037.48 | 1 | 5000 | 18372.96 | 2037.48 | 0 | 0 | 0 | 0 | 21923.96 | 0 | 0 | 0 | 0 | 0 | 21923.96
2022111116 | 6 | 0.58863 | 47090.4 | 0.50535 | 18192.6 | 0.1751 | 2101.2 | 1 | 5000 | 18192.6 | 2101.2 | 0 | 0 | 0 | 0 | 21796.6 | 0 | 0 | 0 | 0 | 0 | 21796.6
2022111117 | 6 | 0.5818 | 46544 | 0.51117 | 18402.12 | 0.1354 | 1624.8 | 1 | 5000 | 18402.12 | 1624.8 | 0 | 0 | 0 | 0 | 21517.08 | 0 | 0 | 0 | 0 | 0 | 21517.08
2022111118 | 6 | 0.58176 | 46540.8 | 0.48095 | 17314.2 | 0.04391 | 526.92 | 1 | 5000 | 17314.2 | 526.92 | 0 | 0 | 0 | 0 | 23699.68 | 0 | 0 | 0 | 0 | 0 | 23699.68
2022111119 | 6 | 0.57711 | 46168.8 | 0.45266 | 16295.76 | 0 | 0 | 1 | 5000 | 16295.76 | 0 | 0 | 0 | 0 | 0 | 24873.04 | 0 | 0 | 0 | 0 | 0 | 24873.04
2022111120 | 6 | 0.56392 | 45113.6 | 0.45402 | 16344.72 | 0 | 0 | 1 | 5000 | 16344.72 | 0 | 0 | 0 | 0 | 0 | 23768.88 | 0 | 0 | 0 | 0 | 0 | 23768.88
2022111121 | 6 | 0.55089 | 44071.2 | 0.45228 | 16282.08 | 0 | 0 | 1 | 5000 | 16282.08 | 0 | 0 | 0 | 0 | 0 | 22789.12 | 0 | 0 | 0 | 0 | 0 | 22789.12
2022111122 | 6 | 0.53705 | 42964 | 0.44092 | 15873.12 | 0 | 0 | 1 | 5000 | 15873.12 | 0 | 0 | 0 | 0 | 0 | 22090.88 | 0 | 0 | 0 | 0 | 0 | 22090.88
2022111123 | 6 | 0.51857 | 41485.6 | 0.41242 | 14847.12 | 0 | 0 | 1 | 5000 | 14847.12 | 0 | 0 | 0 | 0 | 0 | 21638.48 | 0 | 0 | 0 | 0 | 0 | 21638.48
2022111124 | 6 | 0.49639 | 39711.2 | 0.37839 | 13622.04 | 0 | 0 | 1 | 5000 | 13622.04 | 0 | 0 | 0 | 0 | 0 | 21089.16 | 0 | 0 | 0 | 0 | 0 | 21089.16
2022111201 | 7 | 0.48051 | 38440.8 | 0.34439 | 12398.04 | 0 | 0 | 1 | 5000 | 12398.04 | 0 | 0 | 0 | 0 | 0 | 21042.76 | 0 | 0 | 0 | 0 | 0 | 21042.76
2022111202 | 7 | 0.47273 | 37818.4 | 0.3312 | 11923.2 | 0 | 0 | 1 | 5000 | 11923.2 | 0 | 0 | 0 | 0 | 0 | 20895.2 | 0 | 0 | 0 | 0 | 0 | 20895.2
2022111203 | 7 | 0.46912 | 37529.6 | 0.3342 | 12031.2 | 0 | 0 | 1 | 5000 | 12031.2 | 0 | 0 | 0 | 0 | 0 | 20498.4 | 0 | 0 | 0 | 0 | 0 | 20498.4
2022111204 | 7 | 0.47148 | 37718.4 | 0.31768 | 11436.48 | 0 | 0 | 1 | 5000 | 11436.48 | 0 | 0 | 0 | 0 | 0 | 21281.92 | 0 | 0 | 0 | 0 | 0 | 21281.92
2022111205 | 7 | 0.47786 | 38228.8 | 0.29133 | 10487.88 | 0 | 0 | 1 | 5000 | 10487.88 | 0 | 0 | 0 | 0 | 0 | 22740.92 | 0 | 0 | 0 | 0 | 0 | 22740.92
2022111206 | 7 | 0.49402 | 39521.6 | 0.27811 | 10011.96 | 0 | 0 | 1 | 5000 | 10011.96 | 0 | 0 | 0 | 0 | 0 | 24509.64 | 0 | 0 | 0 | 0 | 0 | 24509.64
2022111207 | 7 | 0.51657 | 41325.6 | 0.24411 | 8787.96 | 0.00013 | 1.56 | 1 | 5000 | 8787.96 | 1.56 | 0 | 0 | 0 | 0 | 27536.08 | 0 | 0 | 0 | 0 | 0 | 27536.08
2022111208 | 7 | 0.53612 | 42889.6 | 0.22025 | 7929 | 0.07498 | 899.76 | 1 | 5000 | 7929 | 899.76 | 0 | 0 | 0 | 0 | 29060.84 | 0 | 0 | 0 | 0 | 0 | 29060.84
2022111209 | 7 | 0.55091 | 44072.8 | 0.17701 | 6372.36 | 0.45621 | 5474.52 | 1 | 5000 | 6372.36 | 5474.52 | 0 | 0 | 0 | 0 | 27225.92 | 0 | 0 | 0 | 0 | 0 | 27225.92
2022111210 | 7 | 0.55094 | 44075.2 | 0.15866 | 5711.76 | 0.64047 | 7685.64 | 1 | 5000 | 5711.76 | 7685.64 | 0 | 0 | 0 | 0 | 25677.8 | 0 | 0 | 0 | 0 | 0 | 25677.8
2022111211 | 7 | 0.54035 | 43228 | 0.1571 | 5655.6 | 0.6635 | 7962 | 1 | 5000 | 5655.6 | 7962 | 0 | 0 | 0 | 0 | 24610.4 | 0 | 0 | 0 | 0 | 0 | 24610.4
2022111212 | 7 | 0.52549 | 42039.2 | 0.15438 | 5557.68 | 0.65655 | 7878.6 | 1 | 5000 | 5557.68 | 7878.6 | 0 | 0 | 0 | 0 | 23602.92 | 0 | 0 | 0 | 0 | 0 | 23602.92
2022111213 | 7 | 0.51054 | 40843.2 | 0.13913 | 5008.68 | 0.65076 | 7809.12 | 1 | 5000 | 5008.68 | 7809.12 | 0 | 0 | 0 | 0 | 23025.4 | 0 | 0 | 0 | 0 | 0 | 23025.4
2022111214 | 7 | 0.49757 | 39805.6 | 0.13023 | 4688.28 | 0.6637 | 7964.4 | 1 | 5000 | 4688.28 | 7964.4 | 0 | 0 | 0 | 0 | 22152.92 | 0 | 0 | 0 | 0 | 0 | 22152.92
2022111215 | 7 | 0.49042 | 39233.6 | 0.12495 | 4498.2 | 0.68172 | 8180.64 | 1 | 5000 | 4498.2 | 8180.64 | 0 | 0 | 0 | 0 | 21554.76 | 0 | 0 | 0 | 0 | 0 | 21554.76
2022111216 | 7 | 0.49083 | 39266.4 | 0.11346 | 4084.56 | 0.67628 | 8115.36 | 1 | 5000 | 4084.56 | 8115.36 | 0 | 0 | 0 | 0 | 22066.48 | 0 | 0 | 0 | 0 | 0 | 22066.48
2022111217 | 7 | 0.49538 | 39630.4 | 0.10135 | 3648.6 | 0.43142 | 5177.04 | 1 | 5000 | 3648.6 | 5177.04 | 0 | 0 | 0 | 0 | 25804.76 | 0 | 0 | 0 | 0 | 0 | 25804.76
2022111218 | 7 | 0.51978 | 41582.4 | 0.10008 | 3602.88 | 0.05685 | 682.2 | 1 | 5000 | 3602.88 | 682.2 | 0 | 0 | 0 | 0 | 32297.32 | 0 | 0 | 0 | 0 | 0 | 32297.32
2022111219 | 7 | 0.5397 | 43176 | 0.14941 | 5378.76 | 5e-05 | 0.6 | 1 | 5000 | 5378.76 | 0.6 | 0 | 0 | 0 | 0 | 32796.64 | 0 | 0 | 0 | 0 | 0 | 32796.64
2022111220 | 7 | 0.54132 | 43305.6 | 0.21886 | 7878.96 | 0 | 0 | 1 | 5000 | 7878.96 | 0 | 0 | 0 | 0 | 0 | 30426.64 | 0 | 0 | 0 | 0 | 0 | 30426.64
2022111221 | 7 | 0.53969 | 43175.2 | 0.26574 | 9566.64 | 0 | 0 | 1 | 5000 | 9566.64 | 0 | 0 | 0 | 0 | 0 | 28608.56 | 0 | 0 | 0 | 0 | 0 | 28608.56
2022111222 | 7 | 0.53599 | 42879.2 | 0.29844 | 10743.84 | 0 | 0 | 1 | 5000 | 10743.84 | 0 | 0 | 0 | 0 | 0 | 27135.36 | 0 | 0 | 0 | 0 | 0 | 27135.36
2022111223 | 7 | 0.52679 | 42143.2 | 0.34485 | 12414.6 | 0 | 0 | 1 | 5000 | 12414.6 | 0 | 0 | 0 | 0 | 0 | 24728.6 | 0 | 0 | 0 | 0 | 0 | 24728.6
2022111224 | 7 | 0.51748 | 41398.4 | 0.40573 | 14606.28 | 0 | 0 | 1 | 5000 | 14606.28 | 0 | 0 | 0 | 0 | 0 | 21792.12 | 0 | 0 | 0 | 0 | 0 | 21792.12
2022111301 | 1 | 0.51012 | 40809.6 | 0.45 | 16200 | 0 | 0 | 1 | 5000 | 16200 | 0 | 0 | 0 | 0 | 0 | 19609.6 | 0 | 0 | 0 | 0 | 0 | 19609.6
2022111302 | 1 | 0.50752 | 40601.6 | 0.47219 | 16998.84 | 0 | 0 | 1 | 5000 | 16998.84 | 0 | 0 | 0 | 0 | 0 | 18602.76 | 0 | 0 | 0 | 0 | 0 | 18602.76
2022111303 | 1 | 0.50692 | 40553.6 | 0.48938 | 17617.68 | 0 | 0 | 1 | 5000 | 17617.68 | 0 | 0 | 0 | 0 | 0 | 17935.92 | 0 | 0 | 0 | 0 | 0 | 17935.92
2022111304 | 1 | 0.51095 | 40876 | 0.50019 | 18006.84 | 0 | 0 | 1 | 5000 | 18006.84 | 0 | 0 | 0 | 0 | 0 | 17869.16 | 0 | 0 | 0 | 0 | 0 | 17869.16
2022111305 | 1 | 0.51739 | 41391.2 | 0.49016 | 17645.76 | 0 | 0 | 1 | 5000 | 17645.76 | 0 | 0 | 0 | 0 | 0 | 18745.44 | 0 | 0 | 0 | 0 | 0 | 18745.44
2022111306 | 1 | 0.52983 | 42386.4 | 0.48503 | 17461.08 | 0 | 0 | 1 | 5000 | 17461.08 | 0 | 0 | 0 | 0 | 0 | 19925.32 | 0 | 0 | 0 | 0 | 0 | 19925.32
2022111307 | 1 | 0.54675 | 43740 | 0.48996 | 17638.56 | 0.0002 | 2.4 | 1 | 5000 | 17638.56 | 2.4 | 0 | 0 | 0 | 0 | 21099.04 | 0 | 0 | 0 | 0 | 0 | 21099.04
2022111308 | 1 | 0.56158 | 44926.4 | 0.49054 | 17659.44 | 0.09199 | 1103.88 | 1 | 5000 | 17659.44 | 1103.88 | 0 | 0 | 0 | 0 | 21163.08 | 0 | 0 | 0 | 0 | 0 | 21163.08
2022111309 | 1 | 0.56239 | 44991.2 | 0.42961 | 15465.96 | 0.42002 | 5040.24 | 1 | 5000 | 15465.96 | 5040.24 | 0 | 0 | 0 | 0 | 19485 | 0 | 0 | 0 | 0 | 0 | 19485
2022111310 | 1 | 0.55536 | 44428.8 | 0.40997 | 14758.92 | 0.50047 | 6005.64 | 1 | 5000 | 14758.92 | 6005.64 | 0 | 0 | 0 | 0 | 18664.24 | 0 | 0 | 0 | 0 | 0 | 18664.24
2022111311 | 1 | 0.53986 | 43188.8 | 0.4438 | 15976.8 | 0.44794 | 5375.28 | 1 | 5000 | 15976.8 | 5375.28 | 0 | 0 | 0 | 0 | 16836.72 | 0 | 0 | 0 | 0 | 0 | 16836.72
2022111312 | 1 | 0.52423 | 41938.4 | 0.44369 | 15972.84 | 0.43987 | 5278.44 | 1 | 5000 | 15972.84 | 5278.44 | 0 | 0 | 0 | 0 | 15687.12 | 0 | 0 | 0 | 0 | 0 | 15687.12
2022111313 | 1 | 0.51169 | 40935.2 | 0.44751 | 16110.36 | 0.43036 | 5164.32 | 1 | 5000 | 16110.36 | 5164.32 | 0 | 0 | 0 | 0 | 14660.52 | 0 | 0 | 0 | 0 | 0 | 14660.52
2022111314 | 1 | 0.50322 | 40257.6 | 0.45085 | 16230.6 | 0.42074 | 5048.88 | 1 | 5000 | 16230.6 | 5048.88 | 0 | 0 | 0 | 0 | 13978.12 | 0 | 0 | 0 | 0 | 0 | 13978.12
2022111315 | 1 | 0.49949 | 39959.2 | 0.45802 | 16488.72 | 0.39793 | 4775.16 | 1 | 5000 | 16488.72 | 4775.16 | 0 | 0 | 0 | 0 | 13695.32 | 0 | 0 | 0 | 0 | 0 | 13695.32
2022111316 | 1 | 0.49963 | 39970.4 | 0.46407 | 16706.52 | 0.35159 | 4219.08 | 1 | 5000 | 16706.52 | 4219.08 | 0 | 0 | 0 | 0 | 14044.8 | 0 | 0 | 0 | 0 | 0 | 14044.8
2022111317 | 1 | 0.50912 | 40729.6 | 0.47986 | 17274.96 | 0.16263 | 1951.56 | 1 | 5000 | 17274.96 | 1951.56 | 0 | 0 | 0 | 0 | 16503.08 | 0 | 0 | 0 | 0 | 0 | 16503.08
2022111318 | 1 | 0.53352 | 42681.6 | 0.44939 | 16178.04 | 0.02016 | 241.92 | 1 | 5000 | 16178.04 | 241.92 | 0 | 0 | 0 | 0 | 21261.64 | 0 | 0 | 0 | 0 | 0 | 21261.64
2022111319 | 1 | 0.55272 | 44217.6 | 0.45331 | 16319.16 | 0 | 0 | 1 | 5000 | 16319.16 | 0 | 0 | 0 | 0 | 0 | 22898.44 | 0 | 0 | 0 | 0 | 0 | 22898.44
2022111320 | 1 | 0.55797 | 44637.6 | 0.48726 | 17541.36 | 0 | 0 | 1 | 5000 | 17541.36 | 0 | 0 | 0 | 0 | 0 | 22096.24 | 0 | 0 | 0 | 0 | 0 | 22096.24
2022111321 | 1 | 0.55402 | 44321.6 | 0.51654 | 18595.44 | 0 | 0 | 1 | 5000 | 18595.44 | 0 | 0 | 0 | 0 | 0 | 20726.16 | 0 | 0 | 0 | 0 | 0 | 20726.16
2022111322 | 1 | 0.54152 | 43321.6 | 0.52765 | 18995.4 | 0 | 0 | 1 | 5000 | 18995.4 | 0 | 0 | 0 | 0 | 0 | 19326.2 | 0 | 0 | 0 | 0 | 0 | 19326.2
2022111323 | 1 | 0.52024 | 41619.2 | 0.52687 | 18967.32 | 0 | 0 | 1 | 5000 | 18967.32 | 0 | 0 | 0 | 0 | 0 | 17651.88 | 0 | 0 | 0 | 0 | 0 | 17651.88
2022111324 | 1 | 0.49698 | 39758.4 | 0.53303 | 19189.08 | 0 | 0 | 1 | 5000 | 19189.08 | 0 | 0 | 0 | 0 | 0 | 15569.32 | 0 | 0 | 0 | 0 | 0 | 15569.32
2022111401 | 2 | 0.47931 | 38344.8 | 0.53612 | 19300.32 | 0 | 0 | 1 | 5000 | 19300.32 | 0 | 0 | 0 | 0 | 0 | 14044.48 | 0 | 0 | 0 | 0 | 0 | 14044.48
2022111402 | 2 | 0.47171 | 37736.8 | 0.5273 | 18982.8 | 0 | 0 | 1 | 5000 | 18982.8 | 0 | 0 | 0 | 0 | 0 | 13754 | 0 | 0 | 0 | 0 | 0 | 13754
2022111403 | 2 | 0.46656 | 37324.8 | 0.49509 | 17823.24 | 0 | 0 | 1 | 5000 | 17823.24 | 0 | 0 | 0 | 0 | 0 | 14501.56 | 0 | 0 | 0 | 0 | 0 | 14501.56
2022111404 | 2 | 0.4684 | 37472 | 0.457 | 16452 | 0 | 0 | 1 | 5000 | 16452 | 0 | 0 | 0 | 0 | 0 | 16020 | 0 | 0 | 0 | 0 | 0 | 16020
2022111405 | 2 | 0.47862 | 38289.6 | 0.41414 | 14909.04 | 0 | 0 | 1 | 5000 | 14909.04 | 0 | 0 | 0 | 0 | 0 | 18380.56 | 0 | 0 | 0 | 0 | 0 | 18380.56
2022111406 | 2 | 0.50665 | 40532 | 0.3719 | 13388.4 | 0 | 0 | 1 | 5000 | 13388.4 | 0 | 0 | 0 | 0 | 0 | 22143.6 | 0 | 0 | 0 | 0 | 0 | 22143.6
2022111407 | 2 | 0.54748 | 43798.4 | 0.30506 | 10982.16 | 4e-05 | 0.48 | 1 | 5000 | 10982.16 | 0.48 | 0 | 0 | 0 | 0 | 27815.76 | 0 | 0 | 0 | 0 | 0 | 27815.76
2022111408 | 2 | 0.56535 | 45228 | 0.23776 | 8559.36 | 0.01452 | 174.24 | 1 | 5000 | 8559.36 | 174.24 | 0 | 0 | 0 | 0 | 31494.4 | 0 | 0 | 0 | 0 | 0 | 31494.4
2022111409 | 2 | 0.57366 | 45892.8 | 0.23168 | 8340.48 | 0.09152 | 1098.24 | 1 | 5000 | 8340.48 | 1098.24 | 0 | 0 | 0 | 0 | 31454.08 | 0 | 0 | 0 | 0 | 0 | 31454.08
2022111410 | 2 | 0.58214 | 46571.2 | 0.20456 | 7364.16 | 0.21482 | 2577.84 | 1 | 5000 | 7364.16 | 2577.84 | 0 | 0 | 0 | 0 | 31629.2 | 0 | 0 | 0 | 0 | 0 | 31629.2
2022111411 | 2 | 0.58698 | 46958.4 | 0.19435 | 6996.6 | 0.32066 | 3847.92 | 1 | 5000 | 6996.6 | 3847.92 | 0 | 0 | 0 | 0 | 31113.88 | 0 | 0 | 0 | 0 | 0 | 31113.88
2022111412 | 2 | 0.59147 | 47317.6 | 0.25909 | 9327.24 | 0.36131 | 4335.72 | 1 | 5000 | 9327.24 | 4335.72 | 0 | 0 | 0 | 0 | 28654.64 | 0 | 0 | 0 | 0 | 0 | 28654.64
2022111413 | 2 | 0.59279 | 47423.2 | 0.32717 | 11778.12 | 0.34019 | 4082.28 | 1 | 5000 | 11778.12 | 4082.28 | 0 | 0 | 0 | 0 | 26562.8 | 0 | 0 | 0 | 0 | 0 | 26562.8
2022111414 | 2 | 0.59685 | 47748 | 0.39339 | 14162.04 | 0.34482 | 4137.84 | 1 | 5000 | 14162.04 | 4137.84 | 0 | 0 | 0 | 0 | 24448.12 | 0 | 0 | 0 | 0 | 0 | 24448.12
2022111415 | 2 | 0.59384 | 47507.2 | 0.46091 | 16592.76 | 0.29875 | 3585 | 1 | 5000 | 16592.76 | 3585 | 0 | 0 | 0 | 0 | 22329.44 | 0 | 0 | 0 | 0 | 0 | 22329.44
2022111416 | 2 | 0.59074 | 47259.2 | 0.51968 | 18708.48 | 0.20742 | 2489.04 | 1 | 5000 | 18708.48 | 2489.04 | 0 | 0 | 0 | 0 | 21061.68 | 0 | 0 | 0 | 0 | 0 | 21061.68
2022111417 | 2 | 0.59527 | 47621.6 | 0.53201 | 19152.36 | 0.12926 | 1551.12 | 1 | 5000 | 19152.36 | 1551.12 | 0 | 0 | 0 | 0 | 21918.12 | 0 | 0 | 0 | 0 | 0 | 21918.12
2022111418 | 2 | 0.6154 | 49232 | 0.53797 | 19366.92 | 0.03021 | 362.52 | 1 | 5000 | 19366.92 | 362.52 | 0 | 0 | 0 | 0 | 24502.56 | 0 | 0 | 0 | 0 | 0 | 24502.56
2022111419 | 2 | 0.62312 | 49849.6 | 0.52587 | 18931.32 | 0.00047 | 5.64 | 1 | 5000 | 18931.32 | 5.64 | 0 | 0 | 0 | 0 | 25912.64 | 0 | 0 | 0 | 0 | 0 | 25912.64
2022111420 | 2 | 0.61041 | 48832.8 | 0.50137 | 18049.32 | 0 | 0 | 1 | 5000 | 18049.32 | 0 | 0 | 0 | 0 | 0 | 25783.48 | 0 | 0 | 0 | 0 | 0 | 25783.48
2022111421 | 2 | 0.59766 | 47812.8 | 0.44617 | 16062.12 | 0 | 0 | 1 | 5000 | 16062.12 | 0 | 0 | 0 | 0 | 0 | 26750.68 | 0 | 0 | 0 | 0 | 0 | 26750.68
2022111422 | 2 | 0.57609 | 46087.2 | 0.39769 | 14316.84 | 0 | 0 | 1 | 5000 | 14316.84 | 0 | 0 | 0 | 0 | 0 | 26770.36 | 0 | 0 | 0 | 0 | 0 | 26770.36
2022111423 | 2 | 0.54793 | 43834.4 | 0.36613 | 13180.68 | 0 | 0 | 1 | 5000 | 13180.68 | 0 | 0 | 0 | 0 | 0 | 25653.72 | 0 | 0 | 0 | 0 | 0 | 25653.72
2022111424 | 2 | 0.52323 | 41858.4 | 0.34093 | 12273.48 | 0 | 0 | 1 | 5000 | 12273.48 | 0 | 0 | 0 | 0 | 0 | 24584.92 | 0 | 0 | 0 | 0 | 0 | 24584.92
2022111501 | 3 | 0.51065 | 40852 | 0.3394 | 12218.4 | 0 | 0 | 1 | 5000 | 12218.4 | 0 | 0 | 0 | 0 | 0 | 23633.6 | 0 | 0 | 0 | 0 | 0 | 23633.6
2022111502 | 3 | 0.50345 | 40276 | 0.34596 | 12454.56 | 0 | 0 | 1 | 5000 | 12454.56 | 0 | 0 | 0 | 0 | 0 | 22821.44 | 0 | 0 | 0 | 0 | 0 | 22821.44
2022111503 | 3 | 0.50175 | 40140 | 0.33392 | 12021.12 | 0 | 0 | 1 | 5000 | 12021.12 | 0 | 0 | 0 | 0 | 0 | 23118.88 | 0 | 0 | 0 | 0 | 0 | 23118.88
2022111504 | 3 | 0.50436 | 40348.8 | 0.32374 | 11654.64 | 0 | 0 | 1 | 5000 | 11654.64 | 0 | 0 | 0 | 0 | 0 | 23694.16 | 0 | 0 | 0 | 0 | 0 | 23694.16
2022111505 | 3 | 0.51982 | 41585.6 | 0.30705 | 11053.8 | 0 | 0 | 1 | 5000 | 11053.8 | 0 | 0 | 0 | 0 | 0 | 25531.8 | 0 | 0 | 0 | 0 | 0 | 25531.8
2022111506 | 3 | 0.55612 | 44489.6 | 0.30355 | 10927.8 | 0 | 0 | 1 | 5000 | 10927.8 | 0 | 0 | 0 | 0 | 0 | 28561.8 | 0 | 0 | 0 | 0 | 0 | 28561.8
2022111507 | 3 | 0.60968 | 48774.4 | 0.32243 | 11607.48 | 4e-05 | 0.48 | 1 | 5000 | 11607.48 | 0.48 | 0 | 0 | 0 | 0 | 32166.44 | 0 | 0 | 0 | 0 | 0 | 32166.44
2022111508 | 3 | 0.62338 | 49870.4 | 0.31535 | 11352.6 | 0.03631 | 435.72 | 1 | 5000 | 11352.6 | 435.72 | 0 | 0 | 0 | 0 | 33082.08 | 0 | 0 | 0 | 0 | 0 | 33082.08
2022111509 | 3 | 0.62185 | 49748 | 0.28172 | 10141.92 | 0.23249 | 2789.88 | 1 | 5000 | 10141.92 | 2789.88 | 0 | 0 | 0 | 0 | 31816.2 | 0 | 0 | 0 | 0 | 0 | 31816.2
2022111510 | 3 | 0.61626 | 49300.8 | 0.2648 | 9532.8 | 0.37744 | 4529.28 | 1 | 5000 | 9532.8 | 4529.28 | 0 | 0 | 0 | 0 | 30238.72 | 0 | 0 | 0 | 0 | 0 | 30238.72
2022111511 | 3 | 0.60638 | 48510.4 | 0.24717 | 8898.12 | 0.46481 | 5577.72 | 1 | 5000 | 8898.12 | 5577.72 | 0 | 0 | 0 | 0 | 29034.56 | 0 | 0 | 0 | 0 | 0 | 29034.56
2022111512 | 3 | 0.5904 | 47232 | 0.22035 | 7932.6 | 0.50388 | 6046.56 | 1 | 5000 | 7932.6 | 6046.56 | 0 | 0 | 0 | 0 | 28252.84 | 0 | 0 | 0 | 0 | 0 | 28252.84
2022111513 | 3 | 0.5777 | 46216 | 0.1917 | 6901.2 | 0.48839 | 5860.68 | 1 | 5000 | 6901.2 | 5860.68 | 0 | 0 | 0 | 0 | 28454.12 | 0 | 0 | 0 | 0 | 0 | 28454.12
2022111514 | 3 | 0.5668 | 45344 | 0.16724 | 6020.64 | 0.49193 | 5903.16 | 1 | 5000 | 6020.64 | 5903.16 | 0 | 0 | 0 | 0 | 28420.2 | 0 | 0 | 0 | 0 | 0 | 28420.2
2022111515 | 3 | 0.55811 | 44648.8 | 0.1373 | 4942.8 | 0.44633 | 5355.96 | 1 | 5000 | 4942.8 | 5355.96 | 0 | 0 | 0 | 0 | 29350.04 | 0 | 0 | 0 | 0 | 0 | 29350.04
2022111516 | 3 | 0.55534 | 44427.2 | 0.11631 | 4187.16 | 0.35767 | 4292.04 | 1 | 5000 | 4187.16 | 4292.04 | 0 | 0 | 0 | 0 | 30948 | 0 | 0 | 0 | 0 | 0 | 30948
2022111517 | 3 | 0.56949 | 45559.2 | 0.10954 | 3943.44 | 0.14967 | 1796.04 | 1 | 5000 | 3943.44 | 1796.04 | 0 | 0 | 0 | 0 | 34819.72 | 0 | 0 | 0 | 0 | 0 | 34819.72
2022111518 | 3 | 0.59971 | 47976.8 | 0.10426 | 3753.36 | 0.01296 | 155.52 | 1 | 5000 | 3753.36 | 155.52 | 0 | 0 | 0 | 0 | 39067.92 | 0 | 0 | 0 | 0 | 0 | 39067.92
2022111519 | 3 | 0.61965 | 49572 | 0.12627 | 4545.72 | 0 | 0 | 1 | 5000 | 4545.72 | 0 | 0 | 0 | 0 | 0 | 40026.28 | 0 | 0 | 0 | 0 | 0 | 40026.28
2022111520 | 3 | 0.62213 | 49770.4 | 0.1625 | 5850 | 0 | 0 | 1 | 5000 | 5850 | 0 | 0 | 0 | 0 | 0 | 38920.4 | 0 | 0 | 0 | 0 | 0 | 38920.4
2022111521 | 3 | 0.61726 | 49380.8 | 0.1645 | 5922 | 0 | 0 | 1 | 5000 | 5922 | 0 | 0 | 0 | 0 | 0 | 38458.8 | 0 | 0 | 0 | 0 | 0 | 38458.8
2022111522 | 3 | 0.60024 | 48019.2 | 0.15988 | 5755.68 | 0 | 0 | 1 | 5000 | 5755.68 | 0 | 0 | 0 | 0 | 0 | 37263.52 | 0 | 0 | 0 | 0 | 0 | 37263.52
2022111523 | 3 | 0.57155 | 45724 | 0.15419 | 5550.84 | 0 | 0 | 1 | 5000 | 5550.84 | 0 | 0 | 0 | 0 | 0 | 35173.16 | 0 | 0 | 0 | 0 | 0 | 35173.16
2022111524 | 3 | 0.54999 | 43999.2 | 0.1511 | 5439.6 | 0 | 0 | 1 | 5000 | 5439.6 | 0 | 0 | 0 | 0 | 0 | 33559.6 | 0 | 0 | 0 | 0 | 0 | 33559.6
2022111601 | 4 | 0.53214 | 42571.2 | 0.14536 | 5232.96 | 0 | 0 | 1 | 5000 | 5232.96 | 0 | 0 | 0 | 0 | 0 | 32338.24 | 0 | 0 | 0 | 0 | 0 | 32338.24
2022111602 | 4 | 0.52661 | 42128.8 | 0.1531 | 5511.6 | 0 | 0 | 1 | 5000 | 5511.6 | 0 | 0 | 0 | 0 | 0 | 31617.2 | 0 | 0 | 0 | 0 | 0 | 31617.2
2022111603 | 4 | 0.52757 | 42205.6 | 0.15491 | 5576.76 | 0 | 0 | 1 | 5000 | 5576.76 | 0 | 0 | 0 | 0 | 0 | 31628.84 | 0 | 0 | 0 | 0 | 0 | 31628.84
2022111604 | 4 | 0.53151 | 42520.8 | 0.16212 | 5836.32 | 0 | 0 | 1 | 5000 | 5836.32 | 0 | 0 | 0 | 0 | 0 | 31684.48 | 0 | 0 | 0 | 0 | 0 | 31684.48
2022111605 | 4 | 0.54719 | 43775.2 | 0.15671 | 5641.56 | 0 | 0 | 1 | 5000 | 5641.56 | 0 | 0 | 0 | 0 | 0 | 33133.64 | 0 | 0 | 0 | 0 | 0 | 33133.64
2022111606 | 4 | 0.57514 | 46011.2 | 0.14741 | 5306.76 | 0 | 0 | 1 | 5000 | 5306.76 | 0 | 0 | 0 | 0 | 0 | 35704.44 | 0 | 0 | 0 | 0 | 0 | 35704.44
2022111607 | 4 | 0.6188 | 49504 | 0.12793 | 4605.48 | 0 | 0 | 1 | 5000 | 4605.48 | 0 | 0 | 0 | 0 | 0 | 39898.52 | 0 | 0 | 0 | 0 | 0 | 39898.52
2022111608 | 4 | 0.63572 | 50857.6 | 0.11193 | 4029.48 | 0.01996 | 239.52 | 1 | 5000 | 4029.48 | 239.52 | 0 | 0 | 0 | 0 | 41588.6 | 0 | 0 | 0 | 0 | 0 | 41588.6
2022111609 | 4 | 0.62965 | 50372 | 0.10127 | 3645.72 | 0.16744 | 2009.28 | 1 | 5000 | 3645.72 | 2009.28 | 0 | 0 | 0 | 0 | 39717 | 0 | 0 | 0 | 0 | 0 | 39717
2022111610 | 4 | 0.61266 | 49012.8 | 0.0993 | 3574.8 | 0.29746 | 3569.52 | 1 | 5000 | 3574.8 | 3569.52 | 0 | 0 | 0 | 0 | 36868.48 | 0 | 0 | 0 | 0 | 0 | 36868.48
2022111611 | 4 | 0.5944 | 47552 | 0.10512 | 3784.32 | 0.38787 | 4654.44 | 1 | 5000 | 3784.32 | 4654.44 | 0 | 0 | 0 | 0 | 34113.24 | 0 | 0 | 0 | 0 | 0 | 34113.24
2022111612 | 4 | 0.57563 | 46050.4 | 0.11122 | 4003.92 | 0.45459 | 5455.08 | 1 | 5000 | 4003.92 | 5455.08 | 0 | 0 | 0 | 0 | 31591.4 | 0 | 0 | 0 | 0 | 0 | 31591.4
2022111613 | 4 | 0.56224 | 44979.2 | 0.1155 | 4158 | 0.50556 | 6066.72 | 1 | 5000 | 4158 | 6066.72 | 0 | 0 | 0 | 0 | 29754.48 | 0 | 0 | 0 | 0 | 0 | 29754.48
2022111614 | 4 | 0.55349 | 44279.2 | 0.11249 | 4049.64 | 0.52697 | 6323.64 | 1 | 5000 | 4049.64 | 6323.64 | 0 | 0 | 0 | 0 | 28905.92 | 0 | 0 | 0 | 0 | 0 | 28905.92
2022111615 | 4 | 0.54676 | 43740.8 | 0.11137 | 4009.32 | 0.507 | 6084 | 1 | 5000 | 4009.32 | 6084 | 0 | 0 | 0 | 0 | 28647.48 | 0 | 0 | 0 | 0 | 0 | 28647.48
2022111616 | 4 | 0.54405 | 43524 | 0.11298 | 4067.28 | 0.3806 | 4567.2 | 1 | 5000 | 4067.28 | 4567.2 | 0 | 0 | 0 | 0 | 29889.52 | 0 | 0 | 0 | 0 | 0 | 29889.52
2022111617 | 4 | 0.55389 | 44311.2 | 0.10843 | 3903.48 | 0.15347 | 1841.64 | 1 | 5000 | 3903.48 | 1841.64 | 0 | 0 | 0 | 0 | 33566.08 | 0 | 0 | 0 | 0 | 0 | 33566.08
2022111618 | 4 | 0.5809 | 46472 | 0.09301 | 3348.36 | 0.01461 | 175.32 | 1 | 5000 | 3348.36 | 175.32 | 0 | 0 | 0 | 0 | 37948.32 | 0 | 0 | 0 | 0 | 0 | 37948.32
2022111619 | 4 | 0.59715 | 47772 | 0.08801 | 3168.36 | 0 | 0 | 1 | 5000 | 3168.36 | 0 | 0 | 0 | 0 | 0 | 39603.64 | 0 | 0 | 0 | 0 | 0 | 39603.64
2022111620 | 4 | 0.60322 | 48257.6 | 0.09236 | 3324.96 | 0 | 0 | 1 | 5000 | 3324.96 | 0 | 0 | 0 | 0 | 0 | 39932.64 | 0 | 0 | 0 | 0 | 0 | 39932.64
2022111621 | 4 | 0.60449 | 48359.2 | 0.09754 | 3511.44 | 0 | 0 | 1 | 5000 | 3511.44 | 0 | 0 | 0 | 0 | 0 | 39847.76 | 0 | 0 | 0 | 0 | 0 | 39847.76
2022111622 | 4 | 0.59148 | 47318.4 | 0.11282 | 4061.52 | 0 | 0 | 1 | 5000 | 4061.52 | 0 | 0 | 0 | 0 | 0 | 38256.88 | 0 | 0 | 0 | 0 | 0 | 38256.88
2022111623 | 4 | 0.56968 | 45574.4 | 0.1311 | 4719.6 | 0 | 0 | 1 | 5000 | 4719.6 | 0 | 0 | 0 | 0 | 0 | 35854.8 | 0 | 0 | 0 | 0 | 0 | 35854.8
2022111624 | 4 | 0.54861 | 43888.8 | 0.14284 | 5142.24 | 0 | 0 | 1 | 5000 | 5142.24 | 0 | 0 | 0 | 0 | 0 | 33746.56 | 0 | 0 | 0 | 0 | 0 | 33746.56
2022111701 | 5 | 0.53058 | 42446.4 | 0.15261 | 5493.96 | 0 | 0 | 1 | 5000 | 5493.96 | 0 | 0 | 0 | 0 | 0 | 31952.44 | 0 | 0 | 0 | 0 | 0 | 31952.44
2022111702 | 5 | 0.52581 | 42064.8 | 0.17381 | 6257.16 | 0 | 0 | 1 | 5000 | 6257.16 | 0 | 0 | 0 | 0 | 0 | 30807.64 | 0 | 0 | 0 | 0 | 0 | 30807.64
2022111703 | 5 | 0.52507 | 42005.6 | 0.20001 | 7200.36 | 0 | 0 | 1 | 5000 | 7200.36 | 0 | 0 | 0 | 0 | 0 | 29805.24 | 0 | 0 | 0 | 0 | 0 | 29805.24
2022111704 | 5 | 0.53081 | 42464.8 | 0.22303 | 8029.08 | 0 | 0 | 1 | 5000 | 8029.08 | 0 | 0 | 0 | 0 | 0 | 29435.72 | 0 | 0 | 0 | 0 | 0 | 29435.72
2022111705 | 5 | 0.54603 | 43682.4 | 0.23283 | 8381.88 | 0 | 0 | 1 | 5000 | 8381.88 | 0 | 0 | 0 | 0 | 0 | 30300.52 | 0 | 0 | 0 | 0 | 0 | 30300.52
2022111706 | 5 | 0.5786 | 46288 | 0.24768 | 8916.48 | 0 | 0 | 1 | 5000 | 8916.48 | 0 | 0 | 0 | 0 | 0 | 32371.52 | 0 | 0 | 0 | 0 | 0 | 32371.52
2022111707 | 5 | 0.62533 | 50026.4 | 0.27381 | 9857.16 | 0 | 0 | 1 | 5000 | 9857.16 | 0 | 0 | 0 | 0 | 0 | 35169.24 | 0 | 0 | 0 | 0 | 0 | 35169.24
2022111708 | 5 | 0.63734 | 50987.2 | 0.2906 | 10461.6 | 0.04552 | 546.24 | 1 | 5000 | 10461.6 | 546.24 | 0 | 0 | 0 | 0 | 34979.36 | 0 | 0 | 0 | 0 | 0 | 34979.36
2022111709 | 5 | 0.62195 | 49756 | 0.2686 | 9669.6 | 0.36697 | 4403.64 | 1 | 5000 | 9669.6 | 4403.64 | 0 | 0 | 0 | 0 | 30682.76 | 0 | 0 | 0 | 0 | 0 | 30682.76
2022111710 | 5 | 0.60473 | 48378.4 | 0.22753 | 8191.08 | 0.55181 | 6621.72 | 1 | 5000 | 8191.08 | 6621.72 | 0 | 0 | 0 | 0 | 28565.6 | 0 | 0 | 0 | 0 | 0 | 28565.6
2022111711 | 5 | 0.58128 | 46502.4 | 0.27679 | 9964.44 | 0.55228 | 6627.36 | 1 | 5000 | 9964.44 | 6627.36 | 0 | 0 | 0 | 0 | 24910.6 | 0 | 0 | 0 | 0 | 0 | 24910.6
2022111712 | 5 | 0.56059 | 44847.2 | 0.27143 | 9771.48 | 0.54716 | 6565.92 | 1 | 5000 | 9771.48 | 6565.92 | 0 | 0 | 0 | 0 | 23509.8 | 0 | 0 | 0 | 0 | 0 | 23509.8
2022111713 | 5 | 0.5449 | 43592 | 0.25033 | 9011.88 | 0.55435 | 6652.2 | 1 | 5000 | 9011.88 | 6652.2 | 0 | 0 | 0 | 0 | 22927.92 | 0 | 0 | 0 | 0 | 0 | 22927.92
2022111714 | 5 | 0.53418 | 42734.4 | 0.24066 | 8663.76 | 0.56504 | 6780.48 | 1 | 5000 | 8663.76 | 6780.48 | 0 | 0 | 0 | 0 | 22290.16 | 0 | 0 | 0 | 0 | 0 | 22290.16
2022111715 | 5 | 0.52731 | 42184.8 | 0.22458 | 8084.88 | 0.59059 | 7087.08 | 1 | 5000 | 8084.88 | 7087.08 | 0 | 0 | 0 | 0 | 22012.84 | 0 | 0 | 0 | 0 | 0 | 22012.84
2022111716 | 5 | 0.52578 | 42062.4 | 0.20563 | 7402.68 | 0.54573 | 6548.76 | 1 | 5000 | 7402.68 | 6548.76 | 0 | 0 | 0 | 0 | 23110.96 | 0 | 0 | 0 | 0 | 0 | 23110.96
2022111717 | 5 | 0.53488 | 42790.4 | 0.19511 | 7023.96 | 0.33981 | 4077.72 | 1 | 5000 | 7023.96 | 4077.72 | 0 | 0 | 0 | 0 | 26688.72 | 0 | 0 | 0 | 0 | 0 | 26688.72
2022111718 | 5 | 0.5603 | 44824 | 0.1842 | 6631.2 | 0.04205 | 504.6 | 1 | 5000 | 6631.2 | 504.6 | 0 | 0 | 0 | 0 | 32688.2 | 0 | 0 | 0 | 0 | 0 | 32688.2
2022111719 | 5 | 0.57663 | 46130.4 | 0.20449 | 7361.64 | 0 | 0 | 1 | 5000 | 7361.64 | 0 | 0 | 0 | 0 | 0 | 33768.76 | 0 | 0 | 0 | 0 | 0 | 33768.76
2022111720 | 5 | 0.57872 | 46297.6 | 0.2422 | 8719.2 | 0 | 0 | 1 | 5000 | 8719.2 | 0 | 0 | 0 | 0 | 0 | 32578.4 | 0 | 0 | 0 | 0 | 0 | 32578.4
2022111721 | 5 | 0.57492 | 45993.6 | 0.2977 | 10717.2 | 0 | 0 | 1 | 5000 | 10717.2 | 0 | 0 | 0 | 0 | 0 | 30276.4 | 0 | 0 | 0 | 0 | 0 | 30276.4
2022111722 | 5 | 0.56527 | 45221.6 | 0.35797 | 12886.92 | 0 | 0 | 1 | 5000 | 12886.92 | 0 | 0 | 0 | 0 | 0 | 27334.68 | 0 | 0 | 0 | 0 | 0 | 27334.68
2022111723 | 5 | 0.54505 | 43604 | 0.40217 | 14478.12 | 0 | 0 | 1 | 5000 | 14478.12 | 0 | 0 | 0 | 0 | 0 | 24125.88 | 0 | 0 | 0 | 0 | 0 | 24125.88
2022111724 | 5 | 0.5244 | 41952 | 0.43425 | 15633 | 0 | 0 | 1 | 5000 | 15633 | 0 | 0 | 0 | 0 | 0 | 21319 | 0 | 0 | 0 | 0 | 0 | 21319
2022111801 | 6 | 0.51067 | 40853.6 | 0.45979 | 16552.44 | 0 | 0 | 1 | 5000 | 16552.44 | 0 | 0 | 0 | 0 | 0 | 19301.16 | 0 | 0 | 0 | 0 | 0 | 19301.16
2022111802 | 6 | 0.50403 | 40322.4 | 0.45609 | 16419.24 | 0 | 0 | 1 | 5000 | 16419.24 | 0 | 0 | 0 | 0 | 0 | 18903.16 | 0 | 0 | 0 | 0 | 0 | 18903.16
2022111803 | 6 | 0.50155 | 40124 | 0.42298 | 15227.28 | 0 | 0 | 1 | 5000 | 15227.28 | 0 | 0 | 0 | 0 | 0 | 19896.72 | 0 | 0 | 0 | 0 | 0 | 19896.72
2022111804 | 6 | 0.50544 | 40435.2 | 0.3941 | 14187.6 | 0 | 0 | 1 | 5000 | 14187.6 | 0 | 0 | 0 | 0 | 0 | 21247.6 | 0 | 0 | 0 | 0 | 0 | 21247.6
2022111805 | 6 | 0.51976 | 41580.8 | 0.38843 | 13983.48 | 0 | 0 | 1 | 5000 | 13983.48 | 0 | 0 | 0 | 0 | 0 | 22597.32 | 0 | 0 | 0 | 0 | 0 | 22597.32
2022111806 | 6 | 0.55075 | 44060 | 0.3911 | 14079.6 | 0 | 0 | 1 | 5000 | 14079.6 | 0 | 0 | 0 | 0 | 0 | 24980.4 | 0 | 0 | 0 | 0 | 0 | 24980.4
2022111807 | 6 | 0.59546 | 47636.8 | 0.39355 | 14167.8 | 5e-05 | 0.6 | 1 | 5000 | 14167.8 | 0.6 | 0 | 0 | 0 | 0 | 28468.4 | 0 | 0 | 0 | 0 | 0 | 28468.4
2022111808 | 6 | 0.61203 | 48962.4 | 0.37782 | 13601.52 | 0.02125 | 255 | 1 | 5000 | 13601.52 | 255 | 0 | 0 | 0 | 0 | 30105.88 | 0 | 0 | 0 | 0 | 0 | 30105.88
2022111809 | 6 | 0.60949 | 48759.2 | 0.3669 | 13208.4 | 0.16773 | 2012.76 | 1 | 5000 | 13208.4 | 2012.76 | 0 | 0 | 0 | 0 | 28538.04 | 0 | 0 | 0 | 0 | 0 | 28538.04
2022111810 | 6 | 0.60242 | 48193.6 | 0.37491 | 13496.76 | 0.29267 | 3512.04 | 1 | 5000 | 13496.76 | 3512.04 | 0 | 0 | 0 | 0 | 26184.8 | 0 | 0 | 0 | 0 | 0 | 26184.8
2022111811 | 6 | 0.58919 | 47135.2 | 0.34876 | 12555.36 | 0.33111 | 3973.32 | 1 | 5000 | 12555.36 | 3973.32 | 0 | 0 | 0 | 0 | 25606.52 | 0 | 0 | 0 | 0 | 0 | 25606.52
2022111812 | 6 | 0.57795 | 46236 | 0.31133 | 11207.88 | 0.37217 | 4466.04 | 1 | 5000 | 11207.88 | 4466.04 | 0 | 0 | 0 | 0 | 25562.08 | 0 | 0 | 0 | 0 | 0 | 25562.08
2022111813 | 6 | 0.56567 | 45253.6 | 0.2812 | 10123.2 | 0.38133 | 4575.96 | 1 | 5000 | 10123.2 | 4575.96 | 0 | 0 | 0 | 0 | 25554.44 | 0 | 0 | 0 | 0 | 0 | 25554.44
2022111814 | 6 | 0.56194 | 44955.2 | 0.25804 | 9289.44 | 0.34856 | 4182.72 | 1 | 5000 | 9289.44 | 4182.72 | 0 | 0 | 0 | 0 | 26483.04 | 0 | 0 | 0 | 0 | 0 | 26483.04
2022111815 | 6 | 0.55954 | 44763.2 | 0.27566 | 9923.76 | 0.30156 | 3618.72 | 1 | 5000 | 9923.76 | 3618.72 | 0 | 0 | 0 | 0 | 26220.72 | 0 | 0 | 0 | 0 | 0 | 26220.72
2022111816 | 6 | 0.56112 | 44889.6 | 0.30388 | 10939.68 | 0.21764 | 2611.68 | 1 | 5000 | 10939.68 | 2611.68 | 0 | 0 | 0 | 0 | 26338.24 | 0 | 0 | 0 | 0 | 0 | 26338.24
2022111817 | 6 | 0.57071 | 45656.8 | 0.3241 | 11667.6 | 0.1242 | 1490.4 | 1 | 5000 | 11667.6 | 1490.4 | 0 | 0 | 0 | 0 | 27498.8 | 0 | 0 | 0 | 0 | 0 | 27498.8
2022111818 | 6 | 0.59453 | 47562.4 | 0.32722 | 11779.92 | 0.01447 | 173.64 | 1 | 5000 | 11779.92 | 173.64 | 0 | 0 | 0 | 0 | 30608.84 | 0 | 0 | 0 | 0 | 0 | 30608.84
2022111819 | 6 | 0.60029 | 48023.2 | 0.29863 | 10750.68 | 5e-05 | 0.6 | 1 | 5000 | 10750.68 | 0.6 | 0 | 0 | 0 | 0 | 32271.92 | 0 | 0 | 0 | 0 | 0 | 32271.92
2022111820 | 6 | 0.597 | 47760 | 0.272 | 9792 | 0.00012 | 1.44 | 1 | 5000 | 9792 | 1.44 | 0 | 0 | 0 | 0 | 32966.56 | 0 | 0 | 0 | 0 | 0 | 32966.56
2022111821 | 6 | 0.59315 | 47452 | 0.25748 | 9269.28 | 6e-05 | 0.72 | 1 | 5000 | 9269.28 | 0.72 | 0 | 0 | 0 | 0 | 33182 | 0 | 0 | 0 | 0 | 0 | 33182
2022111822 | 6 | 0.58311 | 46648.8 | 0.23603 | 8497.08 | 0 | 0 | 1 | 5000 | 8497.08 | 0 | 0 | 0 | 0 | 0 | 33151.72 | 0 | 0 | 0 | 0 | 0 | 33151.72
2022111823 | 6 | 0.56547 | 45237.6 | 0.22994 | 8277.84 | 0 | 0 | 1 | 5000 | 8277.84 | 0 | 0 | 0 | 0 | 0 | 31959.76 | 0 | 0 | 0 | 0 | 0 | 31959.76
2022111824 | 6 | 0.54682 | 43745.6 | 0.22609 | 8139.24 | 0 | 0 | 1 | 5000 | 8139.24 | 0 | 0 | 0 | 0 | 0 | 30606.36 | 0 | 0 | 0 | 0 | 0 | 30606.36
2022111901 | 7 | 0.5331 | 42648 | 0.22774 | 8198.64 | 0 | 0 | 1 | 5000 | 8198.64 | 0 | 0 | 0 | 0 | 0 | 29449.36 | 0 | 0 | 0 | 0 | 0 | 29449.36
2022111902 | 7 | 0.52653 | 42122.4 | 0.22918 | 8250.48 | 0 | 0 | 1 | 5000 | 8250.48 | 0 | 0 | 0 | 0 | 0 | 28871.92 | 0 | 0 | 0 | 0 | 0 | 28871.92
2022111903 | 7 | 0.52694 | 42155.2 | 0.22718 | 8178.48 | 0 | 0 | 1 | 5000 | 8178.48 | 0 | 0 | 0 | 0 | 0 | 28976.72 | 0 | 0 | 0 | 0 | 0 | 28976.72
2022111904 | 7 | 0.53063 | 42450.4 | 0.2226 | 8013.6 | 0 | 0 | 1 | 5000 | 8013.6 | 0 | 0 | 0 | 0 | 0 | 29436.8 | 0 | 0 | 0 | 0 | 0 | 29436.8
2022111905 | 7 | 0.53921 | 43136.8 | 0.22395 | 8062.2 | 0 | 0 | 1 | 5000 | 8062.2 | 0 | 0 | 0 | 0 | 0 | 30074.6 | 0 | 0 | 0 | 0 | 0 | 30074.6
2022111906 | 7 | 0.55376 | 44300.8 | 0.2231 | 8031.6 | 0 | 0 | 1 | 5000 | 8031.6 | 0 | 0 | 0 | 0 | 0 | 31269.2 | 0 | 0 | 0 | 0 | 0 | 31269.2
2022111907 | 7 | 0.5722 | 45776 | 0.22646 | 8152.56 | 0 | 0 | 1 | 5000 | 8152.56 | 0 | 0 | 0 | 0 | 0 | 32623.44 | 0 | 0 | 0 | 0 | 0 | 32623.44
2022111908 | 7 | 0.59574 | 47659.2 | 0.22814 | 8213.04 | 0.00449 | 53.88 | 1 | 5000 | 8213.04 | 53.88 | 0 | 0 | 0 | 0 | 34392.28 | 0 | 0 | 0 | 0 | 0 | 34392.28
2022111909 | 7 | 0.61949 | 49559.2 | 0.21957 | 7904.52 | 0.03066 | 367.92 | 1 | 5000 | 7904.52 | 367.92 | 0 | 0 | 0 | 0 | 36286.76 | 0 | 0 | 0 | 0 | 0 | 36286.76
2022111910 | 7 | 0.63822 | 51057.6 | 0.23799 | 8567.64 | 0.05911 | 709.32 | 1 | 5000 | 8567.64 | 709.32 | 0 | 0 | 0 | 0 | 36780.64 | 0 | 0 | 0 | 0 | 0 | 36780.64
2022111911 | 7 | 0.64625 | 51700 | 0.25226 | 9081.36 | 0.0977 | 1172.4 | 1 | 5000 | 9081.36 | 1172.4 | 0 | 0 | 0 | 0 | 36446.24 | 0 | 0 | 0 | 0 | 0 | 36446.24
2022111912 | 7 | 0.64747 | 51797.6 | 0.26068 | 9384.48 | 0.14016 | 1681.92 | 1 | 5000 | 9384.48 | 1681.92 | 0 | 0 | 0 | 0 | 35731.2 | 0 | 0 | 0 | 0 | 0 | 35731.2
2022111913 | 7 | 0.64219 | 51375.2 | 0.27433 | 9875.88 | 0.16901 | 2028.12 | 1 | 5000 | 9875.88 | 2028.12 | 0 | 0 | 0 | 0 | 34471.2 | 0 | 0 | 0 | 0 | 0 | 34471.2
2022111914 | 7 | 0.63344 | 50675.2 | 0.25461 | 9165.96 | 0.19191 | 2302.92 | 1 | 5000 | 9165.96 | 2302.92 | 0 | 0 | 0 | 0 | 34206.32 | 0 | 0 | 0 | 0 | 0 | 34206.32
2022111915 | 7 | 0.62234 | 49787.2 | 0.23897 | 8602.92 | 0.20181 | 2421.72 | 1 | 5000 | 8602.92 | 2421.72 | 0 | 0 | 0 | 0 | 33762.56 | 0 | 0 | 0 | 0 | 0 | 33762.56
2022111916 | 7 | 0.61831 | 49464.8 | 0.21849 | 7865.64 | 0.15885 | 1906.2 | 1 | 5000 | 7865.64 | 1906.2 | 0 | 0 | 0 | 0 | 34692.96 | 0 | 0 | 0 | 0 | 0 | 34692.96
2022111917 | 7 | 0.62212 | 49769.6 | 0.19155 | 6895.8 | 0.07524 | 902.88 | 1 | 5000 | 6895.8 | 902.88 | 0 | 0 | 0 | 0 | 36970.92 | 0 | 0 | 0 | 0 | 0 | 36970.92
2022111918 | 7 | 0.64299 | 51439.2 | 0.16936 | 6096.96 | 0.0064 | 76.8 | 1 | 5000 | 6096.96 | 76.8 | 0 | 0 | 0 | 0 | 40265.44 | 0 | 0 | 0 | 0 | 0 | 40265.44
2022111919 | 7 | 0.65275 | 52220 | 0.16201 | 5832.36 | 0 | 0 | 1 | 5000 | 5832.36 | 0 | 0 | 0 | 0 | 0 | 41387.64 | 0 | 0 | 0 | 0 | 0 | 41387.64
2022111920 | 7 | 0.65033 | 52026.4 | 0.15999 | 5759.64 | 0 | 0 | 1 | 5000 | 5759.64 | 0 | 0 | 0 | 0 | 0 | 41266.76 | 0 | 0 | 0 | 0 | 0 | 41266.76
2022111921 | 7 | 0.64504 | 51603.2 | 0.16097 | 5794.92 | 0 | 0 | 1 | 5000 | 5794.92 | 0 | 0 | 0 | 0 | 0 | 40808.28 | 0 | 0 | 0 | 0 | 0 | 40808.28
2022111922 | 7 | 0.63427 | 50741.6 | 0.1589 | 5720.4 | 4e-05 | 0.48 | 1 | 5000 | 5720.4 | 0.48 | 0 | 0 | 0 | 0 | 40020.72 | 0 | 0 | 0 | 0 | 0 | 40020.72
2022111923 | 7 | 0.61846 | 49476.8 | 0.15564 | 5603.04 | 0 | 0 | 1 | 5000 | 5603.04 | 0 | 0 | 0 | 0 | 0 | 38873.76 | 0 | 0 | 0 | 0 | 0 | 38873.76
2022111924 | 7 | 0.60135 | 48108 | 0.16088 | 5791.68 | 0 | 0 | 1 | 5000 | 5791.68 | 0 | 0 | 0 | 0 | 0 | 37316.32 | 0 | 0 | 0 | 0 | 0 | 37316.32
2022112001 | 1 | 0.58798 | 47038.4 | 0.15922 | 5731.92 | 0 | 0 | 1 | 5000 | 5731.92 | 0 | 0 | 0 | 0 | 0 | 36306.48 | 0 | 0 | 0 | 0 | 0 | 36306.48
2022112002 | 1 | 0.58323 | 46658.4 | 0.16561 | 5961.96 | 0 | 0 | 1 | 5000 | 5961.96 | 0 | 0 | 0 | 0 | 0 | 35696.44 | 0 | 0 | 0 | 0 | 0 | 35696.44
2022112003 | 1 | 0.57983 | 46386.4 | 0.17127 | 6165.72 | 0 | 0 | 1 | 5000 | 6165.72 | 0 | 0 | 0 | 0 | 0 | 35220.68 | 0 | 0 | 0 | 0 | 0 | 35220.68
2022112004 | 1 | 0.58172 | 46537.6 | 0.16737 | 6025.32 | 0 | 0 | 1 | 5000 | 6025.32 | 0 | 0 | 0 | 0 | 0 | 35512.28 | 0 | 0 | 0 | 0 | 0 | 35512.28
2022112005 | 1 | 0.58837 | 47069.6 | 0.16603 | 5977.08 | 4e-05 | 0.48 | 1 | 5000 | 5977.08 | 0.48 | 0 | 0 | 0 | 0 | 36092.04 | 0 | 0 | 0 | 0 | 0 | 36092.04
2022112006 | 1 | 0.60415 | 48332 | 0.15648 | 5633.28 | 0 | 0 | 1 | 5000 | 5633.28 | 0 | 0 | 0 | 0 | 0 | 37698.72 | 0 | 0 | 0 | 0 | 0 | 37698.72
2022112007 | 1 | 0.62235 | 49788 | 0.15059 | 5421.24 | 6e-05 | 0.72 | 1 | 5000 | 5421.24 | 0.72 | 0 | 0 | 0 | 0 | 39366.04 | 0 | 0 | 0 | 0 | 0 | 39366.04
2022112008 | 1 | 0.6369 | 50952 | 0.15492 | 5577.12 | 0.0316 | 379.2 | 1 | 5000 | 5577.12 | 379.2 | 0 | 0 | 0 | 0 | 39995.68 | 0 | 0 | 0 | 0 | 0 | 39995.68
2022112009 | 1 | 0.63813 | 51050.4 | 0.15411 | 5547.96 | 0.16833 | 2019.96 | 1 | 5000 | 5547.96 | 2019.96 | 0 | 0 | 0 | 0 | 38482.48 | 0 | 0 | 0 | 0 | 0 | 38482.48
2022112010 | 1 | 0.62945 | 50356 | 0.14192 | 5109.12 | 0.26227 | 3147.24 | 1 | 5000 | 5109.12 | 3147.24 | 0 | 0 | 0 | 0 | 37099.64 | 0 | 0 | 0 | 0 | 0 | 37099.64
2022112011 | 1 | 0.61134 | 48907.2 | 0.16735 | 6024.6 | 0.27257 | 3270.84 | 1 | 5000 | 6024.6 | 3270.84 | 0 | 0 | 0 | 0 | 34611.76 | 0 | 0 | 0 | 0 | 0 | 34611.76
2022112012 | 1 | 0.59348 | 47478.4 | 0.18327 | 6597.72 | 0.28373 | 3404.76 | 1 | 5000 | 6597.72 | 3404.76 | 0 | 0 | 0 | 0 | 32475.92 | 0 | 0 | 0 | 0 | 0 | 32475.92
2022112013 | 1 | 0.58039 | 46431.2 | 0.16534 | 5952.24 | 0.29569 | 3548.28 | 1 | 5000 | 5952.24 | 3548.28 | 0 | 0 | 0 | 0 | 31930.68 | 0 | 0 | 0 | 0 | 0 | 31930.68
2022112014 | 1 | 0.57255 | 45804 | 0.16002 | 5760.72 | 0.25894 | 3107.28 | 1 | 5000 | 5760.72 | 3107.28 | 0 | 0 | 0 | 0 | 31936 | 0 | 0 | 0 | 0 | 0 | 31936
2022112015 | 1 | 0.57095 | 45676 | 0.15361 | 5529.96 | 0.21864 | 2623.68 | 1 | 5000 | 5529.96 | 2623.68 | 0 | 0 | 0 | 0 | 32522.36 | 0 | 0 | 0 | 0 | 0 | 32522.36
2022112016 | 1 | 0.57099 | 45679.2 | 0.15295 | 5506.2 | 0.15332 | 1839.84 | 1 | 5000 | 5506.2 | 1839.84 | 0 | 0 | 0 | 0 | 33333.16 | 0 | 0 | 0 | 0 | 0 | 33333.16
2022112017 | 1 | 0.58025 | 46420 | 0.15458 | 5564.88 | 0.07477 | 897.24 | 1 | 5000 | 5564.88 | 897.24 | 0 | 0 | 0 | 0 | 34957.88 | 0 | 0 | 0 | 0 | 0 | 34957.88
2022112018 | 1 | 0.59867 | 47893.6 | 0.16418 | 5910.48 | 0.00847 | 101.64 | 1 | 5000 | 5910.48 | 101.64 | 0 | 0 | 0 | 0 | 36881.48 | 0 | 0 | 0 | 0 | 0 | 36881.48
2022112019 | 1 | 0.61174 | 48939.2 | 0.20675 | 7443 | 0 | 0 | 1 | 5000 | 7443 | 0 | 0 | 0 | 0 | 0 | 36496.2 | 0 | 0 | 0 | 0 | 0 | 36496.2
2022112020 | 1 | 0.61141 | 48912.8 | 0.24826 | 8937.36 | 0 | 0 | 1 | 5000 | 8937.36 | 0 | 0 | 0 | 0 | 0 | 34975.44 | 0 | 0 | 0 | 0 | 0 | 34975.44
2022112021 | 1 | 0.60599 | 48479.2 | 0.25546 | 9196.56 | 4e-05 | 0.48 | 1 | 5000 | 9196.56 | 0.48 | 0 | 0 | 0 | 0 | 34282.16 | 0 | 0 | 0 | 0 | 0 | 34282.16
2022112022 | 1 | 0.59281 | 47424.8 | 0.25796 | 9286.56 | 0 | 0 | 1 | 5000 | 9286.56 | 0 | 0 | 0 | 0 | 0 | 33138.24 | 0 | 0 | 0 | 0 | 0 | 33138.24
2022112023 | 1 | 0.57288 | 45830.4 | 0.26583 | 9569.88 | 0 | 0 | 1 | 5000 | 9569.88 | 0 | 0 | 0 | 0 | 0 | 31260.52 | 0 | 0 | 0 | 0 | 0 | 31260.52
2022112024 | 1 | 0.55257 | 44205.6 | 0.28021 | 10087.56 | 0 | 0 | 1 | 5000 | 10087.56 | 0 | 0 | 0 | 0 | 0 | 29118.04 | 0 | 0 | 0 | 0 | 0 | 29118.04
2022112101 | 2 | 0.53838 | 43070.4 | 0.27846 | 10024.56 | 0 | 0 | 1 | 5000 | 10024.56 | 0 | 0 | 0 | 0 | 0 | 28045.84 | 0 | 0 | 0 | 0 | 0 | 28045.84
2022112102 | 2 | 0.53364 | 42691.2 | 0.28035 | 10092.6 | 0 | 0 | 1 | 5000 | 10092.6 | 0 | 0 | 0 | 0 | 0 | 27598.6 | 0 | 0 | 0 | 0 | 0 | 27598.6
2022112103 | 2 | 0.52918 | 42334.4 | 0.26336 | 9480.96 | 0 | 0 | 1 | 5000 | 9480.96 | 0 | 0 | 0 | 0 | 0 | 27853.44 | 0 | 0 | 0 | 0 | 0 | 27853.44
2022112104 | 2 | 0.53192 | 42553.6 | 0.23867 | 8592.12 | 0 | 0 | 1 | 5000 | 8592.12 | 0 | 0 | 0 | 0 | 0 | 28961.48 | 0 | 0 | 0 | 0 | 0 | 28961.48
2022112105 | 2 | 0.54449 | 43559.2 | 0.22166 | 7979.76 | 0 | 0 | 1 | 5000 | 7979.76 | 0 | 0 | 0 | 0 | 0 | 30579.44 | 0 | 0 | 0 | 0 | 0 | 30579.44
2022112106 | 2 | 0.56817 | 45453.6 | 0.20573 | 7406.28 | 0 | 0 | 1 | 5000 | 7406.28 | 0 | 0 | 0 | 0 | 0 | 33047.32 | 0 | 0 | 0 | 0 | 0 | 33047.32
2022112107 | 2 | 0.6003 | 48024 | 0.18575 | 6687 | 0 | 0 | 1 | 5000 | 6687 | 0 | 0 | 0 | 0 | 0 | 36337 | 0 | 0 | 0 | 0 | 0 | 36337
2022112108 | 2 | 0.62489 | 49991.2 | 0.16792 | 6045.12 | 0.00943 | 113.16 | 1 | 5000 | 6045.12 | 113.16 | 0 | 0 | 0 | 0 | 38832.92 | 0 | 0 | 0 | 0 | 0 | 38832.92
2022112109 | 2 | 0.63508 | 50806.4 | 0.15384 | 5538.24 | 0.12033 | 1443.96 | 1 | 5000 | 5538.24 | 1443.96 | 0 | 0 | 0 | 0 | 38824.2 | 0 | 0 | 0 | 0 | 0 | 38824.2
2022112110 | 2 | 0.64098 | 51278.4 | 0.12981 | 4673.16 | 0.23271 | 2792.52 | 1 | 5000 | 4673.16 | 2792.52 | 0 | 0 | 0 | 0 | 38812.72 | 0 | 0 | 0 | 0 | 0 | 38812.72
2022112111 | 2 | 0.64142 | 51313.6 | 0.11233 | 4043.88 | 0.34665 | 4159.8 | 1 | 5000 | 4043.88 | 4159.8 | 0 | 0 | 0 | 0 | 38109.92 | 0 | 0 | 0 | 0 | 0 | 38109.92
2022112112 | 2 | 0.63738 | 50990.4 | 0.10961 | 3945.96 | 0.40518 | 4862.16 | 1 | 5000 | 3945.96 | 4862.16 | 0 | 0 | 0 | 0 | 37182.28 | 0 | 0 | 0 | 0 | 0 | 37182.28
2022112113 | 2 | 0.62802 | 50241.6 | 0.12002 | 4320.72 | 0.4281 | 5137.2 | 1 | 5000 | 4320.72 | 5137.2 | 0 | 0 | 0 | 0 | 35783.68 | 0 | 0 | 0 | 0 | 0 | 35783.68
2022112114 | 2 | 0.62161 | 49728.8 | 0.12812 | 4612.32 | 0.41922 | 5030.64 | 1 | 5000 | 4612.32 | 5030.64 | 0 | 0 | 0 | 0 | 35085.84 | 0 | 0 | 0 | 0 | 0 | 35085.84
2022112115 | 2 | 0.61617 | 49293.6 | 0.13173 | 4742.28 | 0.41407 | 4968.84 | 1 | 5000 | 4742.28 | 4968.84 | 0 | 0 | 0 | 0 | 34582.48 | 0 | 0 | 0 | 0 | 0 | 34582.48
2022112116 | 2 | 0.61194 | 48955.2 | 0.1307 | 4705.2 | 0.39652 | 4758.24 | 1 | 5000 | 4705.2 | 4758.24 | 0 | 0 | 0 | 0 | 34491.76 | 0 | 0 | 0 | 0 | 0 | 34491.76
2022112117 | 2 | 0.6149 | 49192 | 0.13095 | 4714.2 | 0.27126 | 3255.12 | 1 | 5000 | 4714.2 | 3255.12 | 0 | 0 | 0 | 0 | 36222.68 | 0 | 0 | 0 | 0 | 0 | 36222.68
2022112118 | 2 | 0.63254 | 50603.2 | 0.15812 | 5692.32 | 0.03499 | 419.88 | 1 | 5000 | 5692.32 | 419.88 | 0 | 0 | 0 | 0 | 39491 | 0 | 0 | 0 | 0 | 0 | 39491
2022112119 | 2 | 0.64191 | 51352.8 | 0.20937 | 7537.32 | 0 | 0 | 1 | 5000 | 7537.32 | 0 | 0 | 0 | 0 | 0 | 38815.48 | 0 | 0 | 0 | 0 | 0 | 38815.48
2022112120 | 2 | 0.63513 | 50810.4 | 0.26619 | 9582.84 | 4e-05 | 0.48 | 1 | 5000 | 9582.84 | 0.48 | 0 | 0 | 0 | 0 | 36227.08 | 0 | 0 | 0 | 0 | 0 | 36227.08
2022112121 | 2 | 0.62985 | 50388 | 0.30102 | 10836.72 | 4e-05 | 0.48 | 1 | 5000 | 10836.72 | 0.48 | 0 | 0 | 0 | 0 | 34550.8 | 0 | 0 | 0 | 0 | 0 | 34550.8
2022112122 | 2 | 0.61473 | 49178.4 | 0.33147 | 11932.92 | 4e-05 | 0.48 | 1 | 5000 | 11932.92 | 0.48 | 0 | 0 | 0 | 0 | 32245 | 0 | 0 | 0 | 0 | 0 | 32245
2022112123 | 2 | 0.58719 | 46975.2 | 0.33857 | 12188.52 | 4e-05 | 0.48 | 1 | 5000 | 12188.52 | 0.48 | 0 | 0 | 0 | 0 | 29786.2 | 0 | 0 | 0 | 0 | 0 | 29786.2
2022112124 | 2 | 0.56213 | 44970.4 | 0.32822 | 11815.92 | 0 | 0 | 1 | 5000 | 11815.92 | 0 | 0 | 0 | 0 | 0 | 28154.48 | 0 | 0 | 0 | 0 | 0 | 28154.48
2022112201 | 3 | 0.54621 | 43696.8 | 0.31491 | 11336.76 | 0 | 0 | 1 | 5000 | 11336.76 | 0 | 0 | 0 | 0 | 0 | 27360.04 | 0 | 0 | 0 | 0 | 0 | 27360.04
2022112202 | 3 | 0.5363 | 42904 | 0.28156 | 10136.16 | 0 | 0 | 1 | 5000 | 10136.16 | 0 | 0 | 0 | 0 | 0 | 27767.84 | 0 | 0 | 0 | 0 | 0 | 27767.84
2022112203 | 3 | 0.53096 | 42476.8 | 0.26578 | 9568.08 | 0 | 0 | 1 | 5000 | 9568.08 | 0 | 0 | 0 | 0 | 0 | 27908.72 | 0 | 0 | 0 | 0 | 0 | 27908.72
2022112204 | 3 | 0.52752 | 42201.6 | 0.2559 | 9212.4 | 0 | 0 | 1 | 5000 | 9212.4 | 0 | 0 | 0 | 0 | 0 | 27989.2 | 0 | 0 | 0 | 0 | 0 | 27989.2
2022112205 | 3 | 0.53656 | 42924.8 | 0.24145 | 8692.2 | 0 | 0 | 1 | 5000 | 8692.2 | 0 | 0 | 0 | 0 | 0 | 29232.6 | 0 | 0 | 0 | 0 | 0 | 29232.6
2022112206 | 3 | 0.55662 | 44529.6 | 0.23624 | 8504.64 | 4e-05 | 0.48 | 1 | 5000 | 8504.64 | 0.48 | 0 | 0 | 0 | 0 | 31024.48 | 0 | 0 | 0 | 0 | 0 | 31024.48
2022112207 | 3 | 0.5868 | 46944 | 0.21913 | 7888.68 | 0 | 0 | 1 | 5000 | 7888.68 | 0 | 0 | 0 | 0 | 0 | 34055.32 | 0 | 0 | 0 | 0 | 0 | 34055.32
2022112208 | 3 | 0.60683 | 48546.4 | 0.2236 | 8049.6 | 0.01628 | 195.36 | 1 | 5000 | 8049.6 | 195.36 | 0 | 0 | 0 | 0 | 35301.44 | 0 | 0 | 0 | 0 | 0 | 35301.44
2022112209 | 3 | 0.61185 | 48948 | 0.21058 | 7580.88 | 0.21758 | 2610.96 | 1 | 5000 | 7580.88 | 2610.96 | 0 | 0 | 0 | 0 | 33756.16 | 0 | 0 | 0 | 0 | 0 | 33756.16
2022112210 | 3 | 0.60899 | 48719.2 | 0.14438 | 5197.68 | 0.3907 | 4688.4 | 1 | 5000 | 5197.68 | 4688.4 | 0 | 0 | 0 | 0 | 33833.12 | 0 | 0 | 0 | 0 | 0 | 33833.12
2022112211 | 3 | 0.5997 | 47976 | 0.12418 | 4470.48 | 0.44793 | 5375.16 | 1 | 5000 | 4470.48 | 5375.16 | 0 | 0 | 0 | 0 | 33130.36 | 0 | 0 | 0 | 0 | 0 | 33130.36
2022112212 | 3 | 0.58397 | 46717.6 | 0.14089 | 5072.04 | 0.48248 | 5789.76 | 1 | 5000 | 5072.04 | 5789.76 | 0 | 0 | 0 | 0 | 30855.8 | 0 | 0 | 0 | 0 | 0 | 30855.8
2022112213 | 3 | 0.56945 | 45556 | 0.154 | 5544 | 0.50135 | 6016.2 | 1 | 5000 | 5544 | 6016.2 | 0 | 0 | 0 | 0 | 28995.8 | 0 | 0 | 0 | 0 | 0 | 28995.8
2022112214 | 3 | 0.56027 | 44821.6 | 0.1565 | 5634 | 0.49652 | 5958.24 | 1 | 5000 | 5634 | 5958.24 | 0 | 0 | 0 | 0 | 28229.36 | 0 | 0 | 0 | 0 | 0 | 28229.36
2022112215 | 3 | 0.55351 | 44280.8 | 0.17229 | 6202.44 | 0.49611 | 5953.32 | 1 | 5000 | 6202.44 | 5953.32 | 0 | 0 | 0 | 0 | 27125.04 | 0 | 0 | 0 | 0 | 0 | 27125.04
2022112216 | 3 | 0.54868 | 43894.4 | 0.18158 | 6536.88 | 0.43133 | 5175.96 | 1 | 5000 | 6536.88 | 5175.96 | 0 | 0 | 0 | 0 | 27181.56 | 0 | 0 | 0 | 0 | 0 | 27181.56
2022112217 | 3 | 0.54845 | 43876 | 0.18278 | 6580.08 | 0.24357 | 2922.84 | 1 | 5000 | 6580.08 | 2922.84 | 0 | 0 | 0 | 0 | 29373.08 | 0 | 0 | 0 | 0 | 0 | 29373.08
2022112218 | 3 | 0.56561 | 45248.8 | 0.19488 | 7015.68 | 0.02961 | 355.32 | 1 | 5000 | 7015.68 | 355.32 | 0 | 0 | 0 | 0 | 32877.8 | 0 | 0 | 0 | 0 | 0 | 32877.8
2022112219 | 3 | 0.57727 | 46181.6 | 0.25377 | 9135.72 | 0 | 0 | 1 | 5000 | 9135.72 | 0 | 0 | 0 | 0 | 0 | 32045.88 | 0 | 0 | 0 | 0 | 0 | 32045.88
2022112220 | 3 | 0.57663 | 46130.4 | 0.32152 | 11574.72 | 0 | 0 | 1 | 5000 | 11574.72 | 0 | 0 | 0 | 0 | 0 | 29555.68 | 0 | 0 | 0 | 0 | 0 | 29555.68
2022112221 | 3 | 0.57213 | 45770.4 | 0.35563 | 12802.68 | 0 | 0 | 1 | 5000 | 12802.68 | 0 | 0 | 0 | 0 | 0 | 27967.72 | 0 | 0 | 0 | 0 | 0 | 27967.72
2022112222 | 3 | 0.56025 | 44820 | 0.36482 | 13133.52 | 0 | 0 | 1 | 5000 | 13133.52 | 0 | 0 | 0 | 0 | 0 | 26686.48 | 0 | 0 | 0 | 0 | 0 | 26686.48
2022112223 | 3 | 0.53929 | 43143.2 | 0.34851 | 12546.36 | 0 | 0 | 1 | 5000 | 12546.36 | 0 | 0 | 0 | 0 | 0 | 25596.84 | 0 | 0 | 0 | 0 | 0 | 25596.84
2022112224 | 3 | 0.51836 | 41468.8 | 0.32214 | 11597.04 | 0 | 0 | 1 | 5000 | 11597.04 | 0 | 0 | 0 | 0 | 0 | 24871.76 | 0 | 0 | 0 | 0 | 0 | 24871.76
2022112301 | 4 | 0.49893 | 39914.4 | 0.3181 | 11451.6 | 0 | 0 | 1 | 5000 | 11451.6 | 0 | 0 | 0 | 0 | 0 | 23462.8 | 0 | 0 | 0 | 0 | 0 | 23462.8
2022112302 | 4 | 0.48752 | 39001.6 | 0.29328 | 10558.08 | 0 | 0 | 1 | 5000 | 10558.08 | 0 | 0 | 0 | 0 | 0 | 23443.52 | 0 | 0 | 0 | 0 | 0 | 23443.52
2022112303 | 4 | 0.47931 | 38344.8 | 0.24804 | 8929.44 | 0 | 0 | 1 | 5000 | 8929.44 | 0 | 0 | 0 | 0 | 0 | 24415.36 | 0 | 0 | 0 | 0 | 0 | 24415.36
2022112304 | 4 | 0.47666 | 38132.8 | 0.21513 | 7744.68 | 0 | 0 | 1 | 5000 | 7744.68 | 0 | 0 | 0 | 0 | 0 | 25388.12 | 0 | 0 | 0 | 0 | 0 | 25388.12
2022112305 | 4 | 0.48568 | 38854.4 | 0.20451 | 7362.36 | 0 | 0 | 1 | 5000 | 7362.36 | 0 | 0 | 0 | 0 | 0 | 26492.04 | 0 | 0 | 0 | 0 | 0 | 26492.04
2022112306 | 4 | 0.50455 | 40364 | 0.21603 | 7777.08 | 0 | 0 | 1 | 5000 | 7777.08 | 0 | 0 | 0 | 0 | 0 | 27586.92 | 0 | 0 | 0 | 0 | 0 | 27586.92
2022112307 | 4 | 0.53086 | 42468.8 | 0.21825 | 7857 | 4e-05 | 0.48 | 1 | 5000 | 7857 | 0.48 | 0 | 0 | 0 | 0 | 29611.32 | 0 | 0 | 0 | 0 | 0 | 29611.32
2022112308 | 4 | 0.54503 | 43602.4 | 0.21706 | 7814.16 | 0.02206 | 264.72 | 1 | 5000 | 7814.16 | 264.72 | 0 | 0 | 0 | 0 | 30523.52 | 0 | 0 | 0 | 0 | 0 | 30523.52
2022112309 | 4 | 0.55106 | 44084.8 | 0.20877 | 7515.72 | 0.10627 | 1275.24 | 1 | 5000 | 7515.72 | 1275.24 | 0 | 0 | 0 | 0 | 30293.84 | 0 | 0 | 0 | 0 | 0 | 30293.84
2022112310 | 4 | 0.55593 | 44474.4 | 0.19882 | 7157.52 | 0.17148 | 2057.76 | 1 | 5000 | 7157.52 | 2057.76 | 0 | 0 | 0 | 0 | 30259.12 | 0 | 0 | 0 | 0 | 0 | 30259.12
2022112311 | 4 | 0.55504 | 44403.2 | 0.21455 | 7723.8 | 0.23717 | 2846.04 | 1 | 5000 | 7723.8 | 2846.04 | 0 | 0 | 0 | 0 | 28833.36 | 0 | 0 | 0 | 0 | 0 | 28833.36
2022112312 | 4 | 0.55382 | 44305.6 | 0.2537 | 9133.2 | 0.31195 | 3743.4 | 1 | 5000 | 9133.2 | 3743.4 | 0 | 0 | 0 | 0 | 26429 | 0 | 0 | 0 | 0 | 0 | 26429
2022112313 | 4 | 0.54787 | 43829.6 | 0.27614 | 9941.04 | 0.35574 | 4268.88 | 1 | 5000 | 9941.04 | 4268.88 | 0 | 0 | 0 | 0 | 24619.68 | 0 | 0 | 0 | 0 | 0 | 24619.68
2022112314 | 4 | 0.54377 | 43501.6 | 0.28614 | 10301.04 | 0.35289 | 4234.68 | 1 | 5000 | 10301.04 | 4234.68 | 0 | 0 | 0 | 0 | 23965.88 | 0 | 0 | 0 | 0 | 0 | 23965.88
2022112315 | 4 | 0.54175 | 43340 | 0.29358 | 10568.88 | 0.35079 | 4209.48 | 1 | 5000 | 10568.88 | 4209.48 | 0 | 0 | 0 | 0 | 23561.64 | 0 | 0 | 0 | 0 | 0 | 23561.64
2022112316 | 4 | 0.53821 | 43056.8 | 0.30349 | 10925.64 | 0.34457 | 4134.84 | 1 | 5000 | 10925.64 | 4134.84 | 0 | 0 | 0 | 0 | 22996.32 | 0 | 0 | 0 | 0 | 0 | 22996.32
2022112317 | 4 | 0.54018 | 43214.4 | 0.32218 | 11598.48 | 0.20086 | 2410.32 | 1 | 5000 | 11598.48 | 2410.32 | 0 | 0 | 0 | 0 | 24205.6 | 0 | 0 | 0 | 0 | 0 | 24205.6
2022112318 | 4 | 0.54977 | 43981.6 | 0.34785 | 12522.6 | 0.02971 | 356.52 | 1 | 5000 | 12522.6 | 356.52 | 0 | 0 | 0 | 0 | 26102.48 | 0 | 0 | 0 | 0 | 0 | 26102.48
2022112319 | 4 | 0.55539 | 44431.2 | 0.39677 | 14283.72 | 0 | 0 | 1 | 5000 | 14283.72 | 0 | 0 | 0 | 0 | 0 | 25147.48 | 0 | 0 | 0 | 0 | 0 | 25147.48
2022112320 | 4 | 0.55042 | 44033.6 | 0.44319 | 15954.84 | 0 | 0 | 1 | 5000 | 15954.84 | 0 | 0 | 0 | 0 | 0 | 23078.76 | 0 | 0 | 0 | 0 | 0 | 23078.76
2022112321 | 4 | 0.54304 | 43443.2 | 0.48251 | 17370.36 | 0 | 0 | 1 | 5000 | 17370.36 | 0 | 0 | 0 | 0 | 0 | 21072.84 | 0 | 0 | 0 | 0 | 0 | 21072.84
2022112322 | 4 | 0.53273 | 42618.4 | 0.4868 | 17524.8 | 0 | 0 | 1 | 5000 | 17524.8 | 0 | 0 | 0 | 0 | 0 | 20093.6 | 0 | 0 | 0 | 0 | 0 | 20093.6
2022112323 | 4 | 0.51122 | 40897.6 | 0.46622 | 16783.92 | 0 | 0 | 1 | 5000 | 16783.92 | 0 | 0 | 0 | 0 | 0 | 19113.68 | 0 | 0 | 0 | 0 | 0 | 19113.68
2022112324 | 4 | 0.4872 | 38976 | 0.43242 | 15567.12 | 0 | 0 | 1 | 5000 | 15567.12 | 0 | 0 | 0 | 0 | 0 | 18408.88 | 0 | 0 | 0 | 0 | 0 | 18408.88
2022112401 | 5 | 0.46369 | 37095.2 | 0.3921 | 14115.6 | 0 | 0 | 1 | 5000 | 14115.6 | 0 | 0 | 0 | 0 | 0 | 17979.6 | 0 | 0 | 0 | 0 | 0 | 17979.6
2022112402 | 5 | 0.44982 | 35985.6 | 0.34518 | 12426.48 | 0 | 0 | 1 | 5000 | 12426.48 | 0 | 0 | 0 | 0 | 0 | 18559.12 | 0 | 0 | 0 | 0 | 0 | 18559.12
2022112403 | 5 | 0.43871 | 35096.8 | 0.32314 | 11633.04 | 0 | 0 | 1 | 5000 | 11633.04 | 0 | 0 | 0 | 0 | 0 | 18463.76 | 0 | 0 | 0 | 0 | 0 | 18463.76
2022112404 | 5 | 0.42997 | 34397.6 | 0.29299 | 10547.64 | 0 | 0 | 1 | 5000 | 10547.64 | 0 | 0 | 0 | 0 | 0 | 18849.96 | 0 | 0 | 0 | 0 | 0 | 18849.96
2022112405 | 5 | 0.4305 | 34440 | 0.26236 | 9444.96 | 0 | 0 | 1 | 5000 | 9444.96 | 0 | 0 | 0 | 0 | 0 | 19995.04 | 0 | 0 | 0 | 0 | 0 | 19995.04
2022112406 | 5 | 0.43958 | 35166.4 | 0.23421 | 8431.56 | 0 | 0 | 1 | 5000 | 8431.56 | 0 | 0 | 0 | 0 | 0 | 21734.84 | 0 | 0 | 0 | 0 | 0 | 21734.84
2022112407 | 5 | 0.4545 | 36360 | 0.20998 | 7559.28 | 0 | 0 | 1 | 5000 | 7559.28 | 0 | 0 | 0 | 0 | 0 | 23800.72 | 0 | 0 | 0 | 0 | 0 | 23800.72
2022112408 | 5 | 0.46553 | 37242.4 | 0.1796 | 6465.6 | 0.007 | 84 | 1 | 5000 | 6465.6 | 84 | 0 | 0 | 0 | 0 | 25692.8 | 0 | 0 | 0 | 0 | 0 | 25692.8
2022112409 | 5 | 0.4865 | 38920 | 0.16547 | 5956.92 | 0.12496 | 1499.52 | 1 | 5000 | 5956.92 | 1499.52 | 0 | 0 | 0 | 0 | 26463.56 | 0 | 0 | 0 | 0 | 0 | 26463.56
2022112410 | 5 | 0.51262 | 41009.6 | 0.16462 | 5926.32 | 0.20983 | 2517.96 | 1 | 5000 | 5926.32 | 2517.96 | 0 | 0 | 0 | 0 | 27565.32 | 0 | 0 | 0 | 0 | 0 | 27565.32
2022112411 | 5 | 0.52946 | 42356.8 | 0.18089 | 6512.04 | 0.25348 | 3041.76 | 1 | 5000 | 6512.04 | 3041.76 | 0 | 0 | 0 | 0 | 27803 | 0 | 0 | 0 | 0 | 0 | 27803
2022112412 | 5 | 0.54025 | 43220 | 0.22599 | 8135.64 | 0.26395 | 3167.4 | 1 | 5000 | 8135.64 | 3167.4 | 0 | 0 | 0 | 0 | 26916.96 | 0 | 0 | 0 | 0 | 0 | 26916.96
2022112413 | 5 | 0.54135 | 43308 | 0.29611 | 10659.96 | 0.25305 | 3036.6 | 1 | 5000 | 10659.96 | 3036.6 | 0 | 0 | 0 | 0 | 24611.44 | 0 | 0 | 0 | 0 | 0 | 24611.44
2022112414 | 5 | 0.53322 | 42657.6 | 0.35693 | 12849.48 | 0.25367 | 3044.04 | 1 | 5000 | 12849.48 | 3044.04 | 0 | 0 | 0 | 0 | 21764.08 | 0 | 0 | 0 | 0 | 0 | 21764.08
2022112415 | 5 | 0.52305 | 41844 | 0.4026 | 14493.6 | 0.22102 | 2652.24 | 1 | 5000 | 14493.6 | 2652.24 | 0 | 0 | 0 | 0 | 19698.16 | 0 | 0 | 0 | 0 | 0 | 19698.16
2022112416 | 5 | 0.51069 | 40855.2 | 0.42801 | 15408.36 | 0.15764 | 1891.68 | 1 | 5000 | 15408.36 | 1891.68 | 0 | 0 | 0 | 0 | 18555.16 | 0 | 0 | 0 | 0 | 0 | 18555.16
2022112417 | 5 | 0.50145 | 40116 | 0.45398 | 16343.28 | 0.08943 | 1073.16 | 1 | 5000 | 16343.28 | 1073.16 | 0 | 0 | 0 | 0 | 17699.56 | 0 | 0 | 0 | 0 | 0 | 17699.56
2022112418 | 5 | 0.50418 | 40334.4 | 0.43692 | 15729.12 | 0.01502 | 180.24 | 1 | 5000 | 15729.12 | 180.24 | 0 | 0 | 0 | 0 | 19425.04 | 0 | 0 | 0 | 0 | 0 | 19425.04
2022112419 | 5 | 0.50288 | 40230.4 | 0.46313 | 16672.68 | 0 | 0 | 1 | 5000 | 16672.68 | 0 | 0 | 0 | 0 | 0 | 18557.72 | 0 | 0 | 0 | 0 | 0 | 18557.72
2022112420 | 5 | 0.49676 | 39740.8 | 0.48662 | 17518.32 | 0 | 0 | 1 | 5000 | 17518.32 | 0 | 0 | 0 | 0 | 0 | 17222.48 | 0 | 0 | 0 | 0 | 0 | 17222.48
2022112421 | 5 | 0.49162 | 39329.6 | 0.50172 | 18061.92 | 0 | 0 | 1 | 5000 | 18061.92 | 0 | 0 | 0 | 0 | 0 | 16267.68 | 0 | 0 | 0 | 0 | 0 | 16267.68
2022112422 | 5 | 0.48427 | 38741.6 | 0.52076 | 18747.36 | 0 | 0 | 1 | 5000 | 18747.36 | 0 | 0 | 0 | 0 | 0 | 14994.24 | 0 | 0 | 0 | 0 | 0 | 14994.24
2022112423 | 5 | 0.47126 | 37700.8 | 0.53497 | 19258.92 | 0 | 0 | 1 | 5000 | 19258.92 | 0 | 0 | 0 | 0 | 0 | 13441.88 | 0 | 0 | 0 | 0 | 0 | 13441.88
2022112424 | 5 | 0.45649 | 36519.2 | 0.53495 | 19258.2 | 0 | 0 | 1 | 5000 | 19258.2 | 0 | 0 | 0 | 0 | 0 | 12261 | 0 | 0 | 0 | 0 | 0 | 12261
2022112501 | 6 | 0.44228 | 35382.4 | 0.53358 | 19208.88 | 0 | 0 | 1 | 5000 | 19208.88 | 0 | 0 | 0 | 0 | 0 | 11173.52 | 0 | 0 | 0 | 0 | 0 | 11173.52
2022112502 | 6 | 0.43305 | 34644 | 0.54689 | 19688.04 | 0 | 0 | 1 | 5000 | 19688.04 | 0 | 0 | 0 | 0 | 0 | 9955.96 | 0 | 0 | 0 | 0 | 0 | 9955.96
2022112503 | 6 | 0.42691 | 34152.8 | 0.53729 | 19342.44 | 0 | 0 | 1 | 5000 | 19342.44 | 0 | 0 | 0 | 0 | 0 | 9810.36 | 0 | 0 | 0 | 0 | 0 | 9810.36
2022112504 | 6 | 0.42613 | 34090.4 | 0.53522 | 19267.92 | 0 | 0 | 1 | 5000 | 19267.92 | 0 | 0 | 0 | 0 | 0 | 9822.48 | 0 | 0 | 0 | 0 | 0 | 9822.48
2022112505 | 6 | 0.43006 | 34404.8 | 0.5267 | 18961.2 | 0 | 0 | 1 | 5000 | 18961.2 | 0 | 0 | 0 | 0 | 0 | 10443.6 | 0 | 0 | 0 | 0 | 0 | 10443.6
2022112506 | 6 | 0.44131 | 35304.8 | 0.53408 | 19226.88 | 0 | 0 | 1 | 5000 | 19226.88 | 0 | 0 | 0 | 0 | 0 | 11077.92 | 0 | 0 | 0 | 0 | 0 | 11077.92
2022112507 | 6 | 0.45653 | 36522.4 | 0.52499 | 18899.64 | 0 | 0 | 1 | 5000 | 18899.64 | 0 | 0 | 0 | 0 | 0 | 12622.76 | 0 | 0 | 0 | 0 | 0 | 12622.76
2022112508 | 6 | 0.47049 | 37639.2 | 0.51837 | 18661.32 | 0.00251 | 30.12 | 1 | 5000 | 18661.32 | 30.12 | 0 | 0 | 0 | 0 | 13947.76 | 0 | 0 | 0 | 0 | 0 | 13947.76
2022112509 | 6 | 0.48799 | 39039.2 | 0.52253 | 18811.08 | 0.01751 | 210.12 | 1 | 5000 | 18811.08 | 210.12 | 0 | 0 | 0 | 0 | 15018 | 0 | 0 | 0 | 0 | 0 | 15018
2022112510 | 6 | 0.50527 | 40421.6 | 0.49237 | 17725.32 | 0.04187 | 502.44 | 1 | 5000 | 17725.32 | 502.44 | 0 | 0 | 0 | 0 | 17193.84 | 0 | 0 | 0 | 0 | 0 | 17193.84
2022112511 | 6 | 0.5182 | 41456 | 0.49918 | 17970.48 | 0.06512 | 781.44 | 1 | 5000 | 17970.48 | 781.44 | 0 | 0 | 0 | 0 | 17704.08 | 0 | 0 | 0 | 0 | 0 | 17704.08
2022112512 | 6 | 0.52357 | 41885.6 | 0.52554 | 18919.44 | 0.08606 | 1032.72 | 1 | 5000 | 18919.44 | 1032.72 | 0 | 0 | 0 | 0 | 16933.44 | 0 | 0 | 0 | 0 | 0 | 16933.44
2022112513 | 6 | 0.52302 | 41841.6 | 0.51458 | 18524.88 | 0.09764 | 1171.68 | 1 | 5000 | 18524.88 | 1171.68 | 0 | 0 | 0 | 0 | 17145.04 | 0 | 0 | 0 | 0 | 0 | 17145.04
2022112514 | 6 | 0.51831 | 41464.8 | 0.51245 | 18448.2 | 0.08746 | 1049.52 | 1 | 5000 | 18448.2 | 1049.52 | 0 | 0 | 0 | 0 | 16967.08 | 0 | 0 | 0 | 0 | 0 | 16967.08
2022112515 | 6 | 0.51242 | 40993.6 | 0.49297 | 17746.92 | 0.0642 | 770.4 | 1 | 5000 | 17746.92 | 770.4 | 0 | 0 | 0 | 0 | 17476.28 | 0 | 0 | 0 | 0 | 0 | 17476.28
2022112516 | 6 | 0.51234 | 40987.2 | 0.47236 | 17004.96 | 0.03127 | 375.24 | 1 | 5000 | 17004.96 | 375.24 | 0 | 0 | 0 | 0 | 18607 | 0 | 0 | 0 | 0 | 0 | 18607
2022112517 | 6 | 0.5189 | 41512 | 0.42066 | 15143.76 | 0.0104 | 124.8 | 1 | 5000 | 15143.76 | 124.8 | 0 | 0 | 0 | 0 | 21243.44 | 0 | 0 | 0 | 0 | 0 | 21243.44
2022112518 | 6 | 0.53376 | 42700.8 | 0.39481 | 14213.16 | 0.00025 | 3 | 1 | 5000 | 14213.16 | 3 | 0 | 0 | 0 | 0 | 23484.64 | 0 | 0 | 0 | 0 | 0 | 23484.64
2022112519 | 6 | 0.53505 | 42804 | 0.37371 | 13453.56 | 0 | 0 | 1 | 5000 | 13453.56 | 0 | 0 | 0 | 0 | 0 | 24350.44 | 0 | 0 | 0 | 0 | 0 | 24350.44
2022112520 | 6 | 0.52812 | 42249.6 | 0.30193 | 10869.48 | 0 | 0 | 1 | 5000 | 10869.48 | 0 | 0 | 0 | 0 | 0 | 26380.12 | 0 | 0 | 0 | 0 | 0 | 26380.12
2022112521 | 6 | 0.5194 | 41552 | 0.27246 | 9808.56 | 0 | 0 | 1 | 5000 | 9808.56 | 0 | 0 | 0 | 0 | 0 | 26743.44 | 0 | 0 | 0 | 0 | 0 | 26743.44
2022112522 | 6 | 0.51055 | 40844 | 0.24138 | 8689.68 | 0 | 0 | 1 | 5000 | 8689.68 | 0 | 0 | 0 | 0 | 0 | 27154.32 | 0 | 0 | 0 | 0 | 0 | 27154.32
2022112523 | 6 | 0.4949 | 39592 | 0.27847 | 10024.92 | 0 | 0 | 1 | 5000 | 10024.92 | 0 | 0 | 0 | 0 | 0 | 24567.08 | 0 | 0 | 0 | 0 | 0 | 24567.08
2022112524 | 6 | 0.47982 | 38385.6 | 0.31412 | 11308.32 | 0 | 0 | 1 | 5000 | 11308.32 | 0 | 0 | 0 | 0 | 0 | 22077.28 | 0 | 0 | 0 | 0 | 0 | 22077.28
2022112601 | 7 | 0.46473 | 37178.4 | 0.30765 | 11075.4 | 0 | 0 | 1 | 5000 | 11075.4 | 0 | 0 | 0 | 0 | 0 | 21103 | 0 | 0 | 0 | 0 | 0 | 21103
2022112602 | 7 | 0.45115 | 36092 | 0.25539 | 9194.04 | 0 | 0 | 1 | 5000 | 9194.04 | 0 | 0 | 0 | 0 | 0 | 21897.96 | 0 | 0 | 0 | 0 | 0 | 21897.96
2022112603 | 7 | 0.44207 | 35365.6 | 0.20708 | 7454.88 | 0 | 0 | 1 | 5000 | 7454.88 | 0 | 0 | 0 | 0 | 0 | 22910.72 | 0 | 0 | 0 | 0 | 0 | 22910.72
2022112604 | 7 | 0.44025 | 35220 | 0.19984 | 7194.24 | 0 | 0 | 1 | 5000 | 7194.24 | 0 | 0 | 0 | 0 | 0 | 23025.76 | 0 | 0 | 0 | 0 | 0 | 23025.76
2022112605 | 7 | 0.44338 | 35470.4 | 0.2051 | 7383.6 | 0 | 0 | 1 | 5000 | 7383.6 | 0 | 0 | 0 | 0 | 0 | 23086.8 | 0 | 0 | 0 | 0 | 0 | 23086.8
2022112606 | 7 | 0.44998 | 35998.4 | 0.20076 | 7227.36 | 0 | 0 | 1 | 5000 | 7227.36 | 0 | 0 | 0 | 0 | 0 | 23771.04 | 0 | 0 | 0 | 0 | 0 | 23771.04
2022112607 | 7 | 0.46438 | 37150.4 | 0.19022 | 6847.92 | 0 | 0 | 1 | 5000 | 6847.92 | 0 | 0 | 0 | 0 | 0 | 25302.48 | 0 | 0 | 0 | 0 | 0 | 25302.48
2022112608 | 7 | 0.48145 | 38516 | 0.21826 | 7857.36 | 0.00777 | 93.24 | 1 | 5000 | 7857.36 | 93.24 | 0 | 0 | 0 | 0 | 25565.4 | 0 | 0 | 0 | 0 | 0 | 25565.4
2022112609 | 7 | 0.49682 | 39745.6 | 0.24135 | 8688.6 | 0.08601 | 1032.12 | 1 | 5000 | 8688.6 | 1032.12 | 0 | 0 | 0 | 0 | 25024.88 | 0 | 0 | 0 | 0 | 0 | 25024.88
2022112610 | 7 | 0.50889 | 40711.2 | 0.27211 | 9795.96 | 0.22078 | 2649.36 | 1 | 5000 | 9795.96 | 2649.36 | 0 | 0 | 0 | 0 | 23265.88 | 0 | 0 | 0 | 0 | 0 | 23265.88
2022112611 | 7 | 0.51056 | 40844.8 | 0.29842 | 10743.12 | 0.34059 | 4087.08 | 1 | 5000 | 10743.12 | 4087.08 | 0 | 0 | 0 | 0 | 21014.6 | 0 | 0 | 0 | 0 | 0 | 21014.6
2022112612 | 7 | 0.51062 | 40849.6 | 0.34804 | 12529.44 | 0.39478 | 4737.36 | 1 | 5000 | 12529.44 | 4737.36 | 0 | 0 | 0 | 0 | 18582.8 | 0 | 0 | 0 | 0 | 0 | 18582.8
2022112613 | 7 | 0.5124 | 40992 | 0.40038 | 14413.68 | 0.40825 | 4899 | 1 | 5000 | 14413.68 | 4899 | 0 | 0 | 0 | 0 | 16679.32 | 0 | 0 | 0 | 0 | 0 | 16679.32
2022112614 | 7 | 0.50747 | 40597.6 | 0.42107 | 15158.52 | 0.40207 | 4824.84 | 1 | 5000 | 15158.52 | 4824.84 | 0 | 0 | 0 | 0 | 15614.24 | 0 | 0 | 0 | 0 | 0 | 15614.24
2022112615 | 7 | 0.50306 | 40244.8 | 0.38587 | 13891.32 | 0.43915 | 5269.8 | 1 | 5000 | 13891.32 | 5269.8 | 0 | 0 | 0 | 0 | 16083.68 | 0 | 0 | 0 | 0 | 0 | 16083.68
2022112616 | 7 | 0.5038 | 40304 | 0.32318 | 11634.48 | 0.43868 | 5264.16 | 1 | 5000 | 11634.48 | 5264.16 | 0 | 0 | 0 | 0 | 18405.36 | 0 | 0 | 0 | 0 | 0 | 18405.36
2022112617 | 7 | 0.50523 | 40418.4 | 0.26653 | 9595.08 | 0.31739 | 3808.68 | 1 | 5000 | 9595.08 | 3808.68 | 0 | 0 | 0 | 0 | 22014.64 | 0 | 0 | 0 | 0 | 0 | 22014.64
2022112618 | 7 | 0.51957 | 41565.6 | 0.19091 | 6872.76 | 0.03388 | 406.56 | 1 | 5000 | 6872.76 | 406.56 | 0 | 0 | 0 | 0 | 29286.28 | 0 | 0 | 0 | 0 | 0 | 29286.28
2022112619 | 7 | 0.53222 | 42577.6 | 0.22164 | 7979.04 | 0 | 0 | 1 | 5000 | 7979.04 | 0 | 0 | 0 | 0 | 0 | 29598.56 | 0 | 0 | 0 | 0 | 0 | 29598.56
2022112620 | 7 | 0.53369 | 42695.2 | 0.29786 | 10722.96 | 0 | 0 | 1 | 5000 | 10722.96 | 0 | 0 | 0 | 0 | 0 | 26972.24 | 0 | 0 | 0 | 0 | 0 | 26972.24
2022112621 | 7 | 0.53451 | 42760.8 | 0.37708 | 13574.88 | 0 | 0 | 1 | 5000 | 13574.88 | 0 | 0 | 0 | 0 | 0 | 24185.92 | 0 | 0 | 0 | 0 | 0 | 24185.92
2022112622 | 7 | 0.52962 | 42369.6 | 0.4168 | 15004.8 | 0 | 0 | 1 | 5000 | 15004.8 | 0 | 0 | 0 | 0 | 0 | 22364.8 | 0 | 0 | 0 | 0 | 0 | 22364.8
2022112623 | 7 | 0.52047 | 41637.6 | 0.45674 | 16442.64 | 0 | 0 | 1 | 5000 | 16442.64 | 0 | 0 | 0 | 0 | 0 | 20194.96 | 0 | 0 | 0 | 0 | 0 | 20194.96
2022112624 | 7 | 0.50649 | 40519.2 | 0.47663 | 17158.68 | 0 | 0 | 1 | 5000 | 17158.68 | 0 | 0 | 0 | 0 | 0 | 18360.52 | 0 | 0 | 0 | 0 | 0 | 18360.52
2022112701 | 1 | 0.49457 | 39565.6 | 0.48443 | 17439.48 | 0 | 0 | 1 | 5000 | 17439.48 | 0 | 0 | 0 | 0 | 0 | 17126.12 | 0 | 0 | 0 | 0 | 0 | 17126.12
2022112702 | 1 | 0.48566 | 38852.8 | 0.48261 | 17373.96 | 0 | 0 | 1 | 5000 | 17373.96 | 0 | 0 | 0 | 0 | 0 | 16478.84 | 0 | 0 | 0 | 0 | 0 | 16478.84
2022112703 | 1 | 0.4799 | 38392 | 0.4638 | 16696.8 | 0 | 0 | 1 | 5000 | 16696.8 | 0 | 0 | 0 | 0 | 0 | 16695.2 | 0 | 0 | 0 | 0 | 0 | 16695.2
2022112704 | 1 | 0.47606 | 38084.8 | 0.44455 | 16003.8 | 0 | 0 | 1 | 5000 | 16003.8 | 0 | 0 | 0 | 0 | 0 | 17081 | 0 | 0 | 0 | 0 | 0 | 17081
2022112705 | 1 | 0.47908 | 38326.4 | 0.43069 | 15504.84 | 0 | 0 | 1 | 5000 | 15504.84 | 0 | 0 | 0 | 0 | 0 | 17821.56 | 0 | 0 | 0 | 0 | 0 | 17821.56
2022112706 | 1 | 0.48664 | 38931.2 | 0.38374 | 13814.64 | 0 | 0 | 1 | 5000 | 13814.64 | 0 | 0 | 0 | 0 | 0 | 20116.56 | 0 | 0 | 0 | 0 | 0 | 20116.56
2022112707 | 1 | 0.50149 | 40119.2 | 0.33869 | 12192.84 | 0 | 0 | 1 | 5000 | 12192.84 | 0 | 0 | 0 | 0 | 0 | 22926.36 | 0 | 0 | 0 | 0 | 0 | 22926.36
2022112708 | 1 | 0.50983 | 40786.4 | 0.29454 | 10603.44 | 0.04463 | 535.56 | 1 | 5000 | 10603.44 | 535.56 | 0 | 0 | 0 | 0 | 24647.4 | 0 | 0 | 0 | 0 | 0 | 24647.4
2022112709 | 1 | 0.51473 | 41178.4 | 0.21467 | 7728.12 | 0.38182 | 4581.84 | 1 | 5000 | 7728.12 | 4581.84 | 0 | 0 | 0 | 0 | 23868.44 | 0 | 0 | 0 | 0 | 0 | 23868.44
2022112710 | 1 | 0.50994 | 40795.2 | 0.14381 | 5177.16 | 0.60464 | 7255.68 | 1 | 5000 | 5177.16 | 7255.68 | 0 | 0 | 0 | 0 | 23362.36 | 0 | 0 | 0 | 0 | 0 | 23362.36
2022112711 | 1 | 0.49914 | 39931.2 | 0.13594 | 4893.84 | 0.62164 | 7459.68 | 1 | 5000 | 4893.84 | 7459.68 | 0 | 0 | 0 | 0 | 22577.68 | 0 | 0 | 0 | 0 | 0 | 22577.68
2022112712 | 1 | 0.48798 | 39038.4 | 0.1137 | 4093.2 | 0.60202 | 7224.24 | 1 | 5000 | 4093.2 | 7224.24 | 0 | 0 | 0 | 0 | 22720.96 | 0 | 0 | 0 | 0 | 0 | 22720.96
2022112713 | 1 | 0.48571 | 38856.8 | 0.10717 | 3858.12 | 0.59584 | 7150.08 | 1 | 5000 | 3858.12 | 7150.08 | 0 | 0 | 0 | 0 | 22848.6 | 0 | 0 | 0 | 0 | 0 | 22848.6
2022112714 | 1 | 0.48609 | 38887.2 | 0.09962 | 3586.32 | 0.60946 | 7313.52 | 1 | 5000 | 3586.32 | 7313.52 | 0 | 0 | 0 | 0 | 22987.36 | 0 | 0 | 0 | 0 | 0 | 22987.36
2022112715 | 1 | 0.49043 | 39234.4 | 0.08355 | 3007.8 | 0.6296 | 7555.2 | 1 | 5000 | 3007.8 | 7555.2 | 0 | 0 | 0 | 0 | 23671.4 | 0 | 0 | 0 | 0 | 0 | 23671.4
2022112716 | 1 | 0.49276 | 39420.8 | 0.07597 | 2734.92 | 0.6159 | 7390.8 | 1 | 5000 | 2734.92 | 7390.8 | 0 | 0 | 0 | 0 | 24295.08 | 0 | 0 | 0 | 0 | 0 | 24295.08
2022112717 | 1 | 0.5007 | 40056 | 0.06544 | 2355.84 | 0.36725 | 4407 | 1 | 5000 | 2355.84 | 4407 | 0 | 0 | 0 | 0 | 28293.16 | 0 | 0 | 0 | 0 | 0 | 28293.16
2022112718 | 1 | 0.51967 | 41573.6 | 0.07072 | 2545.92 | 0.0364 | 436.8 | 1 | 5000 | 2545.92 | 436.8 | 0 | 0 | 0 | 0 | 33590.88 | 0 | 0 | 0 | 0 | 0 | 33590.88
2022112719 | 1 | 0.53777 | 43021.6 | 0.06777 | 2439.72 | 0 | 0 | 1 | 5000 | 2439.72 | 0 | 0 | 0 | 0 | 0 | 35581.88 | 0 | 0 | 0 | 0 | 0 | 35581.88
2022112720 | 1 | 0.53685 | 42948 | 0.07744 | 2787.84 | 0 | 0 | 1 | 5000 | 2787.84 | 0 | 0 | 0 | 0 | 0 | 35160.16 | 0 | 0 | 0 | 0 | 0 | 35160.16
2022112721 | 1 | 0.53231 | 42584.8 | 0.08585 | 3090.6 | 0 | 0 | 1 | 5000 | 3090.6 | 0 | 0 | 0 | 0 | 0 | 34494.2 | 0 | 0 | 0 | 0 | 0 | 34494.2
2022112722 | 1 | 0.52122 | 41697.6 | 0.09609 | 3459.24 | 0 | 0 | 1 | 5000 | 3459.24 | 0 | 0 | 0 | 0 | 0 | 33238.36 | 0 | 0 | 0 | 0 | 0 | 33238.36
2022112723 | 1 | 0.49914 | 39931.2 | 0.11663 | 4198.68 | 0 | 0 | 1 | 5000 | 4198.68 | 0 | 0 | 0 | 0 | 0 | 30732.52 | 0 | 0 | 0 | 0 | 0 | 30732.52
2022112724 | 1 | 0.47667 | 38133.6 | 0.14803 | 5329.08 | 0 | 0 | 1 | 5000 | 5329.08 | 0 | 0 | 0 | 0 | 0 | 27804.52 | 0 | 0 | 0 | 0 | 0 | 27804.52
2022112801 | 2 | 0.46192 | 36953.6 | 0.18299 | 6587.64 | 0 | 0 | 1 | 5000 | 6587.64 | 0 | 0 | 0 | 0 | 0 | 25365.96 | 0 | 0 | 0 | 0 | 0 | 25365.96
2022112802 | 2 | 0.45969 | 36775.2 | 0.24229 | 8722.44 | 0 | 0 | 1 | 5000 | 8722.44 | 0 | 0 | 0 | 0 | 0 | 23052.76 | 0 | 0 | 0 | 0 | 0 | 23052.76
2022112803 | 2 | 0.46644 | 37315.2 | 0.30646 | 11032.56 | 0 | 0 | 1 | 5000 | 11032.56 | 0 | 0 | 0 | 0 | 0 | 21282.64 | 0 | 0 | 0 | 0 | 0 | 21282.64
2022112804 | 2 | 0.47599 | 38079.2 | 0.36954 | 13303.44 | 0 | 0 | 1 | 5000 | 13303.44 | 0 | 0 | 0 | 0 | 0 | 19775.76 | 0 | 0 | 0 | 0 | 0 | 19775.76
2022112805 | 2 | 0.49299 | 39439.2 | 0.42293 | 15225.48 | 0 | 0 | 1 | 5000 | 15225.48 | 0 | 0 | 0 | 0 | 0 | 19213.72 | 0 | 0 | 0 | 0 | 0 | 19213.72
2022112806 | 2 | 0.52768 | 42214.4 | 0.47302 | 17028.72 | 0 | 0 | 1 | 5000 | 17028.72 | 0 | 0 | 0 | 0 | 0 | 20185.68 | 0 | 0 | 0 | 0 | 0 | 20185.68
2022112807 | 2 | 0.57659 | 46127.2 | 0.49625 | 17865 | 0 | 0 | 1 | 5000 | 17865 | 0 | 0 | 0 | 0 | 0 | 23262.2 | 0 | 0 | 0 | 0 | 0 | 23262.2
2022112808 | 2 | 0.59753 | 47802.4 | 0.50056 | 18020.16 | 0.03742 | 449.04 | 1 | 5000 | 18020.16 | 449.04 | 0 | 0 | 0 | 0 | 24333.2 | 0 | 0 | 0 | 0 | 0 | 24333.2
2022112809 | 2 | 0.5843 | 46744 | 0.47548 | 17117.28 | 0.26719 | 3206.28 | 1 | 5000 | 17117.28 | 3206.28 | 0 | 0 | 0 | 0 | 21420.44 | 0 | 0 | 0 | 0 | 0 | 21420.44
2022112810 | 2 | 0.56659 | 45327.2 | 0.4199 | 15116.4 | 0.46826 | 5619.12 | 1 | 5000 | 15116.4 | 5619.12 | 0 | 0 | 0 | 0 | 19591.68 | 0 | 0 | 0 | 0 | 0 | 19591.68
2022112811 | 2 | 0.55019 | 44015.2 | 0.37986 | 13674.96 | 0.5496 | 6595.2 | 1 | 5000 | 13674.96 | 6595.2 | 0 | 0 | 0 | 0 | 18745.04 | 0 | 0 | 0 | 0 | 0 | 18745.04
2022112812 | 2 | 0.53925 | 43140 | 0.39654 | 14275.44 | 0.51891 | 6226.92 | 1 | 5000 | 14275.44 | 6226.92 | 0 | 0 | 0 | 0 | 17637.64 | 0 | 0 | 0 | 0 | 0 | 17637.64
2022112813 | 2 | 0.53314 | 42651.2 | 0.44855 | 16147.8 | 0.39676 | 4761.12 | 1 | 5000 | 16147.8 | 4761.12 | 0 | 0 | 0 | 0 | 16742.28 | 0 | 0 | 0 | 0 | 0 | 16742.28
2022112814 | 2 | 0.53364 | 42691.2 | 0.47397 | 17062.92 | 0.34417 | 4130.04 | 1 | 5000 | 17062.92 | 4130.04 | 0 | 0 | 0 | 0 | 16498.24 | 0 | 0 | 0 | 0 | 0 | 16498.24
2022112815 | 2 | 0.53473 | 42778.4 | 0.48198 | 17351.28 | 0.34361 | 4123.32 | 1 | 5000 | 17351.28 | 4123.32 | 0 | 0 | 0 | 0 | 16303.8 | 0 | 0 | 0 | 0 | 0 | 16303.8
2022112816 | 2 | 0.53613 | 42890.4 | 0.48638 | 17509.68 | 0.34201 | 4104.12 | 1 | 5000 | 17509.68 | 4104.12 | 0 | 0 | 0 | 0 | 16276.6 | 0 | 0 | 0 | 0 | 0 | 16276.6
2022112817 | 2 | 0.53858 | 43086.4 | 0.47606 | 17138.16 | 0.23607 | 2832.84 | 1 | 5000 | 17138.16 | 2832.84 | 0 | 0 | 0 | 0 | 18115.4 | 0 | 0 | 0 | 0 | 0 | 18115.4
2022112818 | 2 | 0.55093 | 44074.4 | 0.48716 | 17537.76 | 0.03321 | 398.52 | 1 | 5000 | 17537.76 | 398.52 | 0 | 0 | 0 | 0 | 21138.12 | 0 | 0 | 0 | 0 | 0 | 21138.12
2022112819 | 2 | 0.56814 | 45451.2 | 0.56057 | 20180.52 | 0 | 0 | 1 | 5000 | 20180.52 | 0 | 0 | 0 | 0 | 0 | 20270.68 | 0 | 0 | 0 | 0 | 0 | 20270.68
2022112820 | 2 | 0.56415 | 45132 | 0.59485 | 21414.6 | 0 | 0 | 1 | 5000 | 21414.6 | 0 | 0 | 0 | 0 | 0 | 18717.4 | 0 | 0 | 0 | 0 | 0 | 18717.4
2022112821 | 2 | 0.55389 | 44311.2 | 0.59794 | 21525.84 | 0 | 0 | 1 | 5000 | 21525.84 | 0 | 0 | 0 | 0 | 0 | 17785.36 | 0 | 0 | 0 | 0 | 0 | 17785.36
2022112822 | 2 | 0.53824 | 43059.2 | 0.60969 | 21948.84 | 0 | 0 | 1 | 5000 | 21948.84 | 0 | 0 | 0 | 0 | 0 | 16110.36 | 0 | 0 | 0 | 0 | 0 | 16110.36
2022112823 | 2 | 0.51297 | 41037.6 | 0.62266 | 22415.76 | 0 | 0 | 1 | 5000 | 22415.76 | 0 | 0 | 0 | 0 | 0 | 13621.84 | 0 | 0 | 0 | 0 | 0 | 13621.84
2022112824 | 2 | 0.48632 | 38905.6 | 0.64137 | 23089.32 | 0 | 0 | 1 | 5000 | 23089.32 | 0 | 0 | 0 | 0 | 0 | 10816.28 | 0 | 0 | 0 | 0 | 0 | 10816.28
2022112901 | 3 | 0.46626 | 37300.8 | 0.6421 | 23115.6 | 0 | 0 | 1 | 5000 | 23115.6 | 0 | 0 | 0 | 0 | 0 | 9185.2 | 0 | 0 | 0 | 0 | 0 | 9185.2
2022112902 | 3 | 0.45395 | 36316 | 0.62961 | 22665.96 | 0 | 0 | 1 | 5000 | 22665.96 | 0 | 0 | 0 | 0 | 0 | 8650.04 | 0 | 0 | 0 | 0 | 0 | 8650.04
2022112903 | 3 | 0.44599 | 35679.2 | 0.62253 | 22411.08 | 0 | 0 | 1 | 5000 | 22411.08 | 0 | 0 | 0 | 0 | 0 | 8268.12 | 0 | 0 | 0 | 0 | 0 | 8268.12
2022112904 | 3 | 0.44512 | 35609.6 | 0.62044 | 22335.84 | 0 | 0 | 1 | 5000 | 22335.84 | 0 | 0 | 0 | 0 | 0 | 8273.76 | 0 | 0 | 0 | 0 | 0 | 8273.76
2022112905 | 3 | 0.45321 | 36256.8 | 0.61686 | 22206.96 | 0 | 0 | 1 | 5000 | 22206.96 | 0 | 0 | 0 | 0 | 0 | 9049.84 | 0 | 0 | 0 | 0 | 0 | 9049.84
2022112906 | 3 | 0.47454 | 37963.2 | 0.60797 | 21886.92 | 0 | 0 | 1 | 5000 | 21886.92 | 0 | 0 | 0 | 0 | 0 | 11076.28 | 0 | 0 | 0 | 0 | 0 | 11076.28
2022112907 | 3 | 0.51083 | 40866.4 | 0.6098 | 21952.8 | 0 | 0 | 1 | 5000 | 21952.8 | 0 | 0 | 0 | 0 | 0 | 13913.6 | 0 | 0 | 0 | 0 | 0 | 13913.6
2022112908 | 3 | 0.52895 | 42316 | 0.60117 | 21642.12 | 0.01299 | 155.88 | 1 | 5000 | 21642.12 | 155.88 | 0 | 0 | 0 | 0 | 15518 | 0 | 0 | 0 | 0 | 0 | 15518
2022112909 | 3 | 0.53296 | 42636.8 | 0.55025 | 19809 | 0.18412 | 2209.44 | 1 | 5000 | 19809 | 2209.44 | 0 | 0 | 0 | 0 | 15618.36 | 0 | 0 | 0 | 0 | 0 | 15618.36
2022112910 | 3 | 0.54214 | 43371.2 | 0.49056 | 17660.16 | 0.35159 | 4219.08 | 1 | 5000 | 17660.16 | 4219.08 | 0 | 0 | 0 | 0 | 16491.96 | 0 | 0 | 0 | 0 | 0 | 16491.96
2022112911 | 3 | 0.55084 | 44067.2 | 0.46507 | 16742.52 | 0.47664 | 5719.68 | 1 | 5000 | 16742.52 | 5719.68 | 0 | 0 | 0 | 0 | 16605 | 0 | 0 | 0 | 0 | 0 | 16605
2022112912 | 3 | 0.56109 | 44887.2 | 0.4712 | 16963.2 | 0.47843 | 5741.16 | 1 | 5000 | 16963.2 | 5741.16 | 0 | 0 | 0 | 0 | 17182.84 | 0 | 0 | 0 | 0 | 0 | 17182.84
2022112913 | 3 | 0.56844 | 45475.2 | 0.50299 | 18107.64 | 0.39179 | 4701.48 | 1 | 5000 | 18107.64 | 4701.48 | 0 | 0 | 0 | 0 | 17666.08 | 0 | 0 | 0 | 0 | 0 | 17666.08
2022112914 | 3 | 0.57617 | 46093.6 | 0.51206 | 18434.16 | 0.32246 | 3869.52 | 1 | 5000 | 18434.16 | 3869.52 | 0 | 0 | 0 | 0 | 18789.92 | 0 | 0 | 0 | 0 | 0 | 18789.92
2022112915 | 3 | 0.58394 | 46715.2 | 0.49598 | 17855.28 | 0.30519 | 3662.28 | 1 | 5000 | 17855.28 | 3662.28 | 0 | 0 | 0 | 0 | 20197.64 | 0 | 0 | 0 | 0 | 0 | 20197.64
2022112916 | 3 | 0.58994 | 47195.2 | 0.48085 | 17310.6 | 0.2728 | 3273.6 | 1 | 5000 | 17310.6 | 3273.6 | 0 | 0 | 0 | 0 | 21611 | 0 | 0 | 0 | 0 | 0 | 21611
2022112917 | 3 | 0.59197 | 47357.6 | 0.42632 | 15347.52 | 0.20771 | 2492.52 | 1 | 5000 | 15347.52 | 2492.52 | 0 | 0 | 0 | 0 | 24517.56 | 0 | 0 | 0 | 0 | 0 | 24517.56
2022112918 | 3 | 0.59896 | 47916.8 | 0.38976 | 14031.36 | 0.03499 | 419.88 | 1 | 5000 | 14031.36 | 419.88 | 0 | 0 | 0 | 0 | 28465.56 | 0 | 0 | 0 | 0 | 0 | 28465.56
2022112919 | 3 | 0.60369 | 48295.2 | 0.40285 | 14502.6 | 0.0043 | 51.6 | 1 | 5000 | 14502.6 | 51.6 | 0 | 0 | 0 | 0 | 28741 | 0 | 0 | 0 | 0 | 0 | 28741
2022112920 | 3 | 0.59074 | 47259.2 | 0.4774 | 17186.4 | 0.00431 | 51.72 | 1 | 5000 | 17186.4 | 51.72 | 0 | 0 | 0 | 0 | 25021.08 | 0 | 0 | 0 | 0 | 0 | 25021.08
2022112921 | 3 | 0.578 | 46240 | 0.54082 | 19469.52 | 0.00431 | 51.72 | 1 | 5000 | 19469.52 | 51.72 | 0 | 0 | 0 | 0 | 21718.76 | 0 | 0 | 0 | 0 | 0 | 21718.76
2022112922 | 3 | 0.55769 | 44615.2 | 0.55419 | 19950.84 | 0.00431 | 51.72 | 1 | 5000 | 19950.84 | 51.72 | 0 | 0 | 0 | 0 | 19612.64 | 0 | 0 | 0 | 0 | 0 | 19612.64
2022112923 | 3 | 0.53013 | 42410.4 | 0.5455 | 19638 | 0.00431 | 51.72 | 1 | 5000 | 19638 | 51.72 | 0 | 0 | 0 | 0 | 17720.68 | 0 | 0 | 0 | 0 | 0 | 17720.68
2022112924 | 3 | 0.50281 | 40224.8 | 0.52988 | 19075.68 | 0.00393 | 47.16 | 1 | 5000 | 19075.68 | 47.16 | 0 | 0 | 0 | 0 | 16101.96 | 0 | 0 | 0 | 0 | 0 | 16101.96
2022113001 | 4 | 0.48004 | 38403.2 | 0.49109 | 17679.24 | 0 | 0 | 1 | 5000 | 17679.24 | 0 | 0 | 0 | 0 | 0 | 15723.96 | 0 | 0 | 0 | 0 | 0 | 15723.96
2022113002 | 4 | 0.47116 | 37692.8 | 0.44441 | 15998.76 | 0 | 0 | 1 | 5000 | 15998.76 | 0 | 0 | 0 | 0 | 0 | 16694.04 | 0 | 0 | 0 | 0 | 0 | 16694.04
2022113003 | 4 | 0.46893 | 37514.4 | 0.38601 | 13896.36 | 0 | 0 | 1 | 5000 | 13896.36 | 0 | 0 | 0 | 0 | 0 | 18618.04 | 0 | 0 | 0 | 0 | 0 | 18618.04
2022113004 | 4 | 0.46919 | 37535.2 | 0.34358 | 12368.88 | 0 | 0 | 1 | 5000 | 12368.88 | 0 | 0 | 0 | 0 | 0 | 20166.32 | 0 | 0 | 0 | 0 | 0 | 20166.32
2022113005 | 4 | 0.48197 | 38557.6 | 0.33391 | 12020.76 | 0 | 0 | 1 | 5000 | 12020.76 | 0 | 0 | 0 | 0 | 0 | 21536.84 | 0 | 0 | 0 | 0 | 0 | 21536.84
2022113006 | 4 | 0.51346 | 41076.8 | 0.34439 | 12398.04 | 0 | 0 | 1 | 5000 | 12398.04 | 0 | 0 | 0 | 0 | 0 | 23678.76 | 0 | 0 | 0 | 0 | 0 | 23678.76
2022113007 | 4 | 0.56483 | 45186.4 | 0.30542 | 10995.12 | 0 | 0 | 1 | 5000 | 10995.12 | 0 | 0 | 0 | 0 | 0 | 29191.28 | 0 | 0 | 0 | 0 | 0 | 29191.28
2022113008 | 4 | 0.59179 | 47343.2 | 0.28579 | 10288.44 | 0.03626 | 435.12 | 1 | 5000 | 10288.44 | 435.12 | 0 | 0 | 0 | 0 | 31619.64 | 0 | 0 | 0 | 0 | 0 | 31619.64
2022113009 | 4 | 0.59217 | 47373.6 | 0.25328 | 9118.08 | 0.35754 | 4290.48 | 1 | 5000 | 9118.08 | 4290.48 | 0 | 0 | 0 | 0 | 28965.04 | 0 | 0 | 0 | 0 | 0 | 28965.04
2022113010 | 4 | 0.58533 | 46826.4 | 0.23665 | 8519.4 | 0.58489 | 7018.68 | 1 | 5000 | 8519.4 | 7018.68 | 0 | 0 | 0 | 0 | 26288.32 | 0 | 0 | 0 | 0 | 0 | 26288.32
2022113011 | 4 | 0.57342 | 45873.6 | 0.21456 | 7724.16 | 0.59343 | 7121.16 | 1 | 5000 | 7724.16 | 7121.16 | 0 | 0 | 0 | 0 | 26028.28 | 0 | 0 | 0 | 0 | 0 | 26028.28
2022113012 | 4 | 0.5624 | 44992 | 0.19393 | 6981.48 | 0.58702 | 7044.24 | 1 | 5000 | 6981.48 | 7044.24 | 0 | 0 | 0 | 0 | 25966.28 | 0 | 0 | 0 | 0 | 0 | 25966.28
2022113013 | 4 | 0.55045 | 44036 | 0.1868 | 6724.8 | 0.58087 | 6970.44 | 1 | 5000 | 6724.8 | 6970.44 | 0 | 0 | 0 | 0 | 25340.76 | 0 | 0 | 0 | 0 | 0 | 25340.76
2022113014 | 4 | 0.5395 | 43160 | 0.18583 | 6689.88 | 0.58797 | 7055.64 | 1 | 5000 | 6689.88 | 7055.64 | 0 | 0 | 0 | 0 | 24414.48 | 0 | 0 | 0 | 0 | 0 | 24414.48
2022113015 | 4 | 0.53313 | 42650.4 | 0.19991 | 7196.76 | 0.59613 | 7153.56 | 1 | 5000 | 7196.76 | 7153.56 | 0 | 0 | 0 | 0 | 23300.08 | 0 | 0 | 0 | 0 | 0 | 23300.08
2022113016 | 4 | 0.53174 | 42539.2 | 0.22005 | 7921.8 | 0.55282 | 6633.84 | 1 | 5000 | 7921.8 | 6633.84 | 0 | 0 | 0 | 0 | 22983.56 | 0 | 0 | 0 | 0 | 0 | 22983.56
2022113017 | 4 | 0.54263 | 43410.4 | 0.23742 | 8547.12 | 0.28491 | 3418.92 | 1 | 5000 | 8547.12 | 3418.92 | 0 | 0 | 0 | 0 | 26444.36 | 0 | 0 | 0 | 0 | 0 | 26444.36
2022113018 | 4 | 0.57221 | 45776.8 | 0.2337 | 8413.2 | 0.02486 | 298.32 | 1 | 5000 | 8413.2 | 298.32 | 0 | 0 | 0 | 0 | 32065.28 | 0 | 0 | 0 | 0 | 0 | 32065.28
2022113019 | 4 | 0.59569 | 47655.2 | 0.26356 | 9488.16 | 0 | 0 | 1 | 5000 | 9488.16 | 0 | 0 | 0 | 0 | 0 | 33167.04 | 0 | 0 | 0 | 0 | 0 | 33167.04
2022113020 | 4 | 0.60143 | 48114.4 | 0.29792 | 10725.12 | 0 | 0 | 1 | 5000 | 10725.12 | 0 | 0 | 0 | 0 | 0 | 32389.28 | 0 | 0 | 0 | 0 | 0 | 32389.28
2022113021 | 4 | 0.60363 | 48290.4 | 0.33926 | 12213.36 | 0 | 0 | 1 | 5000 | 12213.36 | 0 | 0 | 0 | 0 | 0 | 31077.04 | 0 | 0 | 0 | 0 | 0 | 31077.04
2022113022 | 4 | 0.59369 | 47495.2 | 0.35665 | 12839.4 | 0 | 0 | 1 | 5000 | 12839.4 | 0 | 0 | 0 | 0 | 0 | 29655.8 | 0 | 0 | 0 | 0 | 0 | 29655.8
2022113023 | 4 | 0.57146 | 45716.8 | 0.36125 | 13005 | 0 | 0 | 1 | 5000 | 13005 | 0 | 0 | 0 | 0 | 0 | 27711.8 | 0 | 0 | 0 | 0 | 0 | 27711.8
2022113024 | 4 | 0.54661 | 43728.8 | 0.35661 | 12837.96 | 0 | 0 | 1 | 5000 | 12837.96 | 0 | 0 | 0 | 0 | 0 | 25890.84 | 0 | 0 | 0 | 0 | 0 | 25890.84
2022120101 | 5 | 0.53326 | 42660.8 | 0.33469 | 12048.84 | 0 | 0 | 1 | 5000 | 12048.84 | 0 | 0 | 0 | 0 | 0 | 25611.96 | 0 | 0 | 0 | 0 | 0 | 25611.96
2022120102 | 5 | 0.52668 | 42134.4 | 0.32473 | 11690.28 | 0 | 0 | 1 | 5000 | 11690.28 | 0 | 0 | 0 | 0 | 0 | 25444.12 | 0 | 0 | 0 | 0 | 0 | 25444.12
2022120103 | 5 | 0.52668 | 42134.4 | 0.33328 | 11998.08 | 0 | 0 | 1 | 5000 | 11998.08 | 0 | 0 | 0 | 0 | 0 | 25136.32 | 0 | 0 | 0 | 0 | 0 | 25136.32
2022120104 | 5 | 0.53095 | 42476 | 0.33243 | 11967.48 | 0 | 0 | 1 | 5000 | 11967.48 | 0 | 0 | 0 | 0 | 0 | 25508.52 | 0 | 0 | 0 | 0 | 0 | 25508.52
2022120105 | 5 | 0.54796 | 43836.8 | 0.32687 | 11767.32 | 0 | 0 | 1 | 5000 | 11767.32 | 0 | 0 | 0 | 0 | 0 | 27069.48 | 0 | 0 | 0 | 0 | 0 | 27069.48
2022120106 | 5 | 0.57862 | 46289.6 | 0.31592 | 11373.12 | 0 | 0 | 1 | 5000 | 11373.12 | 0 | 0 | 0 | 0 | 0 | 29916.48 | 0 | 0 | 0 | 0 | 0 | 29916.48
2022120107 | 5 | 0.62259 | 49807.2 | 0.31998 | 11519.28 | 0 | 0 | 1 | 5000 | 11519.28 | 0 | 0 | 0 | 0 | 0 | 33287.92 | 0 | 0 | 0 | 0 | 0 | 33287.92
2022120108 | 5 | 0.63969 | 51175.2 | 0.34839 | 12542.04 | 0.02477 | 297.24 | 1 | 5000 | 12542.04 | 297.24 | 0 | 0 | 0 | 0 | 33335.92 | 0 | 0 | 0 | 0 | 0 | 33335.92
2022120109 | 5 | 0.63155 | 50524 | 0.33853 | 12187.08 | 0.20838 | 2500.56 | 1 | 5000 | 12187.08 | 2500.56 | 0 | 0 | 0 | 0 | 30836.36 | 0 | 0 | 0 | 0 | 0 | 30836.36
2022120110 | 5 | 0.61765 | 49412 | 0.3559 | 12812.4 | 0.36308 | 4356.96 | 1 | 5000 | 12812.4 | 4356.96 | 0 | 0 | 0 | 0 | 27242.64 | 0 | 0 | 0 | 0 | 0 | 27242.64
2022120111 | 5 | 0.60089 | 48071.2 | 0.35236 | 12684.96 | 0.36828 | 4419.36 | 1 | 5000 | 12684.96 | 4419.36 | 0 | 0 | 0 | 0 | 25966.88 | 0 | 0 | 0 | 0 | 0 | 25966.88
2022120112 | 5 | 0.5879 | 47032 | 0.34138 | 12289.68 | 0.40024 | 4802.88 | 1 | 5000 | 12289.68 | 4802.88 | 0 | 0 | 0 | 0 | 24939.44 | 0 | 0 | 0 | 0 | 0 | 24939.44
2022120113 | 5 | 0.57828 | 46262.4 | 0.30652 | 11034.72 | 0.39872 | 4784.64 | 1 | 5000 | 11034.72 | 4784.64 | 0 | 0 | 0 | 0 | 25443.04 | 0 | 0 | 0 | 0 | 0 | 25443.04
2022120114 | 5 | 0.57297 | 45837.6 | 0.29617 | 10662.12 | 0.38009 | 4561.08 | 1 | 5000 | 10662.12 | 4561.08 | 0 | 0 | 0 | 0 | 25614.4 | 0 | 0 | 0 | 0 | 0 | 25614.4
2022120115 | 5 | 0.5712 | 45696 | 0.32769 | 11796.84 | 0.39606 | 4752.72 | 1 | 5000 | 11796.84 | 4752.72 | 0 | 0 | 0 | 0 | 24146.44 | 0 | 0 | 0 | 0 | 0 | 24146.44
2022120116 | 5 | 0.57081 | 45664.8 | 0.35579 | 12808.44 | 0.35534 | 4264.08 | 1 | 5000 | 12808.44 | 4264.08 | 0 | 0 | 0 | 0 | 23592.28 | 0 | 0 | 0 | 0 | 0 | 23592.28
2022120117 | 5 | 0.57566 | 46052.8 | 0.36043 | 12975.48 | 0.22036 | 2644.32 | 1 | 5000 | 12975.48 | 2644.32 | 0 | 0 | 0 | 0 | 25433 | 0 | 0 | 0 | 0 | 0 | 25433
2022120118 | 5 | 0.58944 | 47155.2 | 0.36234 | 13044.24 | 0.02594 | 311.28 | 1 | 5000 | 13044.24 | 311.28 | 0 | 0 | 0 | 0 | 28799.68 | 0 | 0 | 0 | 0 | 0 | 28799.68
2022120119 | 5 | 0.6048 | 48384 | 0.44135 | 15888.6 | 0.00137 | 16.44 | 1 | 5000 | 15888.6 | 16.44 | 0 | 0 | 0 | 0 | 27478.96 | 0 | 0 | 0 | 0 | 0 | 27478.96
2022120120 | 5 | 0.60503 | 48402.4 | 0.50405 | 18145.8 | 0.00046 | 5.52 | 1 | 5000 | 18145.8 | 5.52 | 0 | 0 | 0 | 0 | 25251.08 | 0 | 0 | 0 | 0 | 0 | 25251.08
2022120121 | 5 | 0.59805 | 47844 | 0.51372 | 18493.92 | 0 | 0 | 1 | 5000 | 18493.92 | 0 | 0 | 0 | 0 | 0 | 24350.08 | 0 | 0 | 0 | 0 | 0 | 24350.08
2022120122 | 5 | 0.57979 | 46383.2 | 0.51083 | 18389.88 | 0 | 0 | 1 | 5000 | 18389.88 | 0 | 0 | 0 | 0 | 0 | 22993.32 | 0 | 0 | 0 | 0 | 0 | 22993.32
2022120123 | 5 | 0.55143 | 44114.4 | 0.52338 | 18841.68 | 0 | 0 | 1 | 5000 | 18841.68 | 0 | 0 | 0 | 0 | 0 | 20272.72 | 0 | 0 | 0 | 0 | 0 | 20272.72
2022120124 | 5 | 0.52269 | 41815.2 | 0.52688 | 18967.68 | 4e-05 | 0.48 | 1 | 5000 | 18967.68 | 0.48 | 0 | 0 | 0 | 0 | 17847.04 | 0 | 0 | 0 | 0 | 0 | 17847.04
2022120201 | 6 | 0.50061 | 40048.8 | 0.51522 | 18547.92 | 4e-05 | 0.48 | 1 | 5000 | 18547.92 | 0.48 | 0 | 0 | 0 | 0 | 16500.4 | 0 | 0 | 0 | 0 | 0 | 16500.4
2022120202 | 6 | 0.48919 | 39135.2 | 0.51849 | 18665.64 | 0 | 0 | 1 | 5000 | 18665.64 | 0 | 0 | 0 | 0 | 0 | 15469.56 | 0 | 0 | 0 | 0 | 0 | 15469.56
2022120203 | 6 | 0.48209 | 38567.2 | 0.51337 | 18481.32 | 0 | 0 | 1 | 5000 | 18481.32 | 0 | 0 | 0 | 0 | 0 | 15085.88 | 0 | 0 | 0 | 0 | 0 | 15085.88
2022120204 | 6 | 0.48225 | 38580 | 0.51265 | 18455.4 | 4e-05 | 0.48 | 1 | 5000 | 18455.4 | 0.48 | 0 | 0 | 0 | 0 | 15124.12 | 0 | 0 | 0 | 0 | 0 | 15124.12
2022120205 | 6 | 0.49013 | 39210.4 | 0.51485 | 18534.6 | 4e-05 | 0.48 | 1 | 5000 | 18534.6 | 0.48 | 0 | 0 | 0 | 0 | 15675.32 | 0 | 0 | 0 | 0 | 0 | 15675.32
2022120206 | 6 | 0.5139 | 41112 | 0.52094 | 18753.84 | 4e-05 | 0.48 | 1 | 5000 | 18753.84 | 0.48 | 0 | 0 | 0 | 0 | 17357.68 | 0 | 0 | 0 | 0 | 0 | 17357.68
2022120207 | 6 | 0.54955 | 43964 | 0.51208 | 18434.88 | 4e-05 | 0.48 | 1 | 5000 | 18434.88 | 0.48 | 0 | 0 | 0 | 0 | 20528.64 | 0 | 0 | 0 | 0 | 0 | 20528.64
2022120208 | 6 | 0.56619 | 45295.2 | 0.50436 | 18156.96 | 0.00665 | 79.8 | 1 | 5000 | 18156.96 | 79.8 | 0 | 0 | 0 | 0 | 22058.44 | 0 | 0 | 0 | 0 | 0 | 22058.44
2022120209 | 6 | 0.5669 | 45352 | 0.48477 | 17451.72 | 0.08577 | 1029.24 | 1 | 5000 | 17451.72 | 1029.24 | 0 | 0 | 0 | 0 | 21871.04 | 0 | 0 | 0 | 0 | 0 | 21871.04
2022120210 | 6 | 0.56916 | 45532.8 | 0.45326 | 16317.36 | 0.18046 | 2165.52 | 1 | 5000 | 16317.36 | 2165.52 | 0 | 0 | 0 | 0 | 22049.92 | 0 | 0 | 0 | 0 | 0 | 22049.92
2022120211 | 6 | 0.56599 | 45279.2 | 0.41821 | 15055.56 | 0.28852 | 3462.24 | 1 | 5000 | 15055.56 | 3462.24 | 0 | 0 | 0 | 0 | 21761.4 | 0 | 0 | 0 | 0 | 0 | 21761.4
2022120212 | 6 | 0.56266 | 45012.8 | 0.40037 | 14413.32 | 0.35716 | 4285.92 | 1 | 5000 | 14413.32 | 4285.92 | 0 | 0 | 0 | 0 | 21313.56 | 0 | 0 | 0 | 0 | 0 | 21313.56
2022120213 | 6 | 0.55834 | 44667.2 | 0.40711 | 14655.96 | 0.34151 | 4098.12 | 1 | 5000 | 14655.96 | 4098.12 | 0 | 0 | 0 | 0 | 20913.12 | 0 | 0 | 0 | 0 | 0 | 20913.12
2022120214 | 6 | 0.55363 | 44290.4 | 0.43581 | 15689.16 | 0.29104 | 3492.48 | 1 | 5000 | 15689.16 | 3492.48 | 0 | 0 | 0 | 0 | 20108.76 | 0 | 0 | 0 | 0 | 0 | 20108.76
2022120215 | 6 | 0.54906 | 43924.8 | 0.45096 | 16234.56 | 0.23618 | 2834.16 | 1 | 5000 | 16234.56 | 2834.16 | 0 | 0 | 0 | 0 | 19856.08 | 0 | 0 | 0 | 0 | 0 | 19856.08
2022120216 | 6 | 0.54597 | 43677.6 | 0.44692 | 16089.12 | 0.22191 | 2662.92 | 1 | 5000 | 16089.12 | 2662.92 | 0 | 0 | 0 | 0 | 19925.56 | 0 | 0 | 0 | 0 | 0 | 19925.56
2022120217 | 6 | 0.54272 | 43417.6 | 0.40756 | 14672.16 | 0.16986 | 2038.32 | 1 | 5000 | 14672.16 | 2038.32 | 0 | 0 | 0 | 0 | 21707.12 | 0 | 0 | 0 | 0 | 0 | 21707.12
2022120218 | 6 | 0.54645 | 43716 | 0.36127 | 13005.72 | 0.02116 | 253.92 | 1 | 5000 | 13005.72 | 253.92 | 0 | 0 | 0 | 0 | 25456.36 | 0 | 0 | 0 | 0 | 0 | 25456.36
2022120219 | 6 | 0.55345 | 44276 | 0.36078 | 12988.08 | 0 | 0 | 1 | 5000 | 12988.08 | 0 | 0 | 0 | 0 | 0 | 26287.92 | 0 | 0 | 0 | 0 | 0 | 26287.92
2022120220 | 6 | 0.54746 | 43796.8 | 0.36891 | 13280.76 | 0 | 0 | 1 | 5000 | 13280.76 | 0 | 0 | 0 | 0 | 0 | 25516.04 | 0 | 0 | 0 | 0 | 0 | 25516.04
2022120221 | 6 | 0.53764 | 43011.2 | 0.34299 | 12347.64 | 0 | 0 | 1 | 5000 | 12347.64 | 0 | 0 | 0 | 0 | 0 | 25663.56 | 0 | 0 | 0 | 0 | 0 | 25663.56
2022120222 | 6 | 0.52293 | 41834.4 | 0.31351 | 11286.36 | 0 | 0 | 1 | 5000 | 11286.36 | 0 | 0 | 0 | 0 | 0 | 25548.04 | 0 | 0 | 0 | 0 | 0 | 25548.04
2022120223 | 6 | 0.50503 | 40402.4 | 0.29007 | 10442.52 | 0 | 0 | 1 | 5000 | 10442.52 | 0 | 0 | 0 | 0 | 0 | 24959.88 | 0 | 0 | 0 | 0 | 0 | 24959.88
2022120224 | 6 | 0.48306 | 38644.8 | 0.26758 | 9632.88 | 0 | 0 | 1 | 5000 | 9632.88 | 0 | 0 | 0 | 0 | 0 | 24011.92 | 0 | 0 | 0 | 0 | 0 | 24011.92
2022120301 | 7 | 0.46411 | 37128.8 | 0.26788 | 9643.68 | 0 | 0 | 1 | 5000 | 9643.68 | 0 | 0 | 0 | 0 | 0 | 22485.12 | 0 | 0 | 0 | 0 | 0 | 22485.12
2022120302 | 7 | 0.44995 | 35996 | 0.32078 | 11548.08 | 0 | 0 | 1 | 5000 | 11548.08 | 0 | 0 | 0 | 0 | 0 | 19447.92 | 0 | 0 | 0 | 0 | 0 | 19447.92
2022120303 | 7 | 0.44205 | 35364 | 0.38114 | 13721.04 | 0 | 0 | 1 | 5000 | 13721.04 | 0 | 0 | 0 | 0 | 0 | 16642.96 | 0 | 0 | 0 | 0 | 0 | 16642.96
2022120304 | 7 | 0.44234 | 35387.2 | 0.43974 | 15830.64 | 0 | 0 | 1 | 5000 | 15830.64 | 0 | 0 | 0 | 0 | 0 | 14556.56 | 0 | 0 | 0 | 0 | 0 | 14556.56
2022120305 | 7 | 0.44947 | 35957.6 | 0.46267 | 16656.12 | 0 | 0 | 1 | 5000 | 16656.12 | 0 | 0 | 0 | 0 | 0 | 14301.48 | 0 | 0 | 0 | 0 | 0 | 14301.48
2022120306 | 7 | 0.46115 | 36892 | 0.47034 | 16932.24 | 0 | 0 | 1 | 5000 | 16932.24 | 0 | 0 | 0 | 0 | 0 | 14959.76 | 0 | 0 | 0 | 0 | 0 | 14959.76
2022120307 | 7 | 0.47939 | 38351.2 | 0.46027 | 16569.72 | 0 | 0 | 1 | 5000 | 16569.72 | 0 | 0 | 0 | 0 | 0 | 16781.48 | 0 | 0 | 0 | 0 | 0 | 16781.48
2022120308 | 7 | 0.4992 | 39936 | 0.45176 | 16263.36 | 0.01096 | 131.52 | 1 | 5000 | 16263.36 | 131.52 | 0 | 0 | 0 | 0 | 18541.12 | 0 | 0 | 0 | 0 | 0 | 18541.12
2022120309 | 7 | 0.52354 | 41883.2 | 0.41392 | 14901.12 | 0.17046 | 2045.52 | 1 | 5000 | 14901.12 | 2045.52 | 0 | 0 | 0 | 0 | 19936.56 | 0 | 0 | 0 | 0 | 0 | 19936.56
2022120310 | 7 | 0.53784 | 43027.2 | 0.3881 | 13971.6 | 0.28296 | 3395.52 | 1 | 5000 | 13971.6 | 3395.52 | 0 | 0 | 0 | 0 | 20660.08 | 0 | 0 | 0 | 0 | 0 | 20660.08
2022120311 | 7 | 0.54446 | 43556.8 | 0.3272 | 11779.2 | 0.39448 | 4733.76 | 1 | 5000 | 11779.2 | 4733.76 | 0 | 0 | 0 | 0 | 22043.84 | 0 | 0 | 0 | 0 | 0 | 22043.84
2022120312 | 7 | 0.54255 | 43404 | 0.23571 | 8485.56 | 0.46426 | 5571.12 | 1 | 5000 | 8485.56 | 5571.12 | 0 | 0 | 0 | 0 | 24347.32 | 0 | 0 | 0 | 0 | 0 | 24347.32
2022120313 | 7 | 0.53868 | 43094.4 | 0.17205 | 6193.8 | 0.48287 | 5794.44 | 1 | 5000 | 6193.8 | 5794.44 | 0 | 0 | 0 | 0 | 26106.16 | 0 | 0 | 0 | 0 | 0 | 26106.16
2022120314 | 7 | 0.53399 | 42719.2 | 0.14665 | 5279.4 | 0.47379 | 5685.48 | 1 | 5000 | 5279.4 | 5685.48 | 0 | 0 | 0 | 0 | 26754.32 | 0 | 0 | 0 | 0 | 0 | 26754.32
2022120315 | 7 | 0.53181 | 42544.8 | 0.1441 | 5187.6 | 0.46546 | 5585.52 | 1 | 5000 | 5187.6 | 5585.52 | 0 | 0 | 0 | 0 | 26771.68 | 0 | 0 | 0 | 0 | 0 | 26771.68
2022120316 | 7 | 0.5318 | 42544 | 0.13773 | 4958.28 | 0.43895 | 5267.4 | 1 | 5000 | 4958.28 | 5267.4 | 0 | 0 | 0 | 0 | 27318.32 | 0 | 0 | 0 | 0 | 0 | 27318.32
2022120317 | 7 | 0.53397 | 42717.6 | 0.12923 | 4652.28 | 0.24833 | 2979.96 | 1 | 5000 | 4652.28 | 2979.96 | 0 | 0 | 0 | 0 | 30085.36 | 0 | 0 | 0 | 0 | 0 | 30085.36
2022120318 | 7 | 0.54921 | 43936.8 | 0.11677 | 4203.72 | 0.01965 | 235.8 | 1 | 5000 | 4203.72 | 235.8 | 0 | 0 | 0 | 0 | 34497.28 | 0 | 0 | 0 | 0 | 0 | 34497.28
2022120319 | 7 | 0.55614 | 44491.2 | 0.12542 | 4515.12 | 0 | 0 | 1 | 5000 | 4515.12 | 0 | 0 | 0 | 0 | 0 | 34976.08 | 0 | 0 | 0 | 0 | 0 | 34976.08
2022120320 | 7 | 0.55339 | 44271.2 | 0.11567 | 4164.12 | 0 | 0 | 1 | 5000 | 4164.12 | 0 | 0 | 0 | 0 | 0 | 35107.08 | 0 | 0 | 0 | 0 | 0 | 35107.08
2022120321 | 7 | 0.54755 | 43804 | 0.11419 | 4110.84 | 0 | 0 | 1 | 5000 | 4110.84 | 0 | 0 | 0 | 0 | 0 | 34693.16 | 0 | 0 | 0 | 0 | 0 | 34693.16
2022120322 | 7 | 0.53744 | 42995.2 | 0.10685 | 3846.6 | 0 | 0 | 1 | 5000 | 3846.6 | 0 | 0 | 0 | 0 | 0 | 34148.6 | 0 | 0 | 0 | 0 | 0 | 34148.6
2022120323 | 7 | 0.51843 | 41474.4 | 0.09102 | 3276.72 | 0 | 0 | 1 | 5000 | 3276.72 | 0 | 0 | 0 | 0 | 0 | 33197.68 | 0 | 0 | 0 | 0 | 0 | 33197.68
2022120324 | 7 | 0.49839 | 39871.2 | 0.09373 | 3374.28 | 0 | 0 | 1 | 5000 | 3374.28 | 0 | 0 | 0 | 0 | 0 | 31496.92 | 0 | 0 | 0 | 0 | 0 | 31496.92
2022120401 | 1 | 0.47892 | 38313.6 | 0.08901 | 3204.36 | 0 | 0 | 1 | 5000 | 3204.36 | 0 | 0 | 0 | 0 | 0 | 30109.24 | 0 | 0 | 0 | 0 | 0 | 30109.24
2022120402 | 1 | 0.4639 | 37112 | 0.0947 | 3409.2 | 0 | 0 | 1 | 5000 | 3409.2 | 0 | 0 | 0 | 0 | 0 | 28702.8 | 0 | 0 | 0 | 0 | 0 | 28702.8
2022120403 | 1 | 0.45427 | 36341.6 | 0.10484 | 3774.24 | 0 | 0 | 1 | 5000 | 3774.24 | 0 | 0 | 0 | 0 | 0 | 27567.36 | 0 | 0 | 0 | 0 | 0 | 27567.36
2022120404 | 1 | 0.45146 | 36116.8 | 0.11393 | 4101.48 | 0 | 0 | 1 | 5000 | 4101.48 | 0 | 0 | 0 | 0 | 0 | 27015.32 | 0 | 0 | 0 | 0 | 0 | 27015.32
2022120405 | 1 | 0.45328 | 36262.4 | 0.11316 | 4073.76 | 0 | 0 | 1 | 5000 | 4073.76 | 0 | 0 | 0 | 0 | 0 | 27188.64 | 0 | 0 | 0 | 0 | 0 | 27188.64
2022120406 | 1 | 0.45835 | 36668 | 0.13394 | 4821.84 | 0 | 0 | 1 | 5000 | 4821.84 | 0 | 0 | 0 | 0 | 0 | 26846.16 | 0 | 0 | 0 | 0 | 0 | 26846.16
2022120407 | 1 | 0.47089 | 37671.2 | 0.15204 | 5473.44 | 0 | 0 | 1 | 5000 | 5473.44 | 0 | 0 | 0 | 0 | 0 | 27197.76 | 0 | 0 | 0 | 0 | 0 | 27197.76
2022120408 | 1 | 0.48433 | 38746.4 | 0.17801 | 6408.36 | 0.00695 | 83.4 | 1 | 5000 | 6408.36 | 83.4 | 0 | 0 | 0 | 0 | 27254.64 | 0 | 0 | 0 | 0 | 0 | 27254.64
2022120409 | 1 | 0.50201 | 40160.8 | 0.1576 | 5673.6 | 0.10545 | 1265.4 | 1 | 5000 | 5673.6 | 1265.4 | 0 | 0 | 0 | 0 | 28221.8 | 0 | 0 | 0 | 0 | 0 | 28221.8
2022120410 | 1 | 0.51557 | 41245.6 | 0.13217 | 4758.12 | 0.29096 | 3491.52 | 1 | 5000 | 4758.12 | 3491.52 | 0 | 0 | 0 | 0 | 27995.96 | 0 | 0 | 0 | 0 | 0 | 27995.96
2022120411 | 1 | 0.5218 | 41744 | 0.13151 | 4734.36 | 0.37285 | 4474.2 | 1 | 5000 | 4734.36 | 4474.2 | 0 | 0 | 0 | 0 | 27535.44 | 0 | 0 | 0 | 0 | 0 | 27535.44
2022120412 | 1 | 0.52152 | 41721.6 | 0.13464 | 4847.04 | 0.4223 | 5067.6 | 1 | 5000 | 4847.04 | 5067.6 | 0 | 0 | 0 | 0 | 26806.96 | 0 | 0 | 0 | 0 | 0 | 26806.96
2022120413 | 1 | 0.51896 | 41516.8 | 0.16309 | 5871.24 | 0.43395 | 5207.4 | 1 | 5000 | 5871.24 | 5207.4 | 0 | 0 | 0 | 0 | 25438.16 | 0 | 0 | 0 | 0 | 0 | 25438.16
2022120414 | 1 | 0.51609 | 41287.2 | 0.17294 | 6225.84 | 0.41111 | 4933.32 | 1 | 5000 | 6225.84 | 4933.32 | 0 | 0 | 0 | 0 | 25128.04 | 0 | 0 | 0 | 0 | 0 | 25128.04
2022120415 | 1 | 0.51741 | 41392.8 | 0.14345 | 5164.2 | 0.3727 | 4472.4 | 1 | 5000 | 5164.2 | 4472.4 | 0 | 0 | 0 | 0 | 26756.2 | 0 | 0 | 0 | 0 | 0 | 26756.2
2022120416 | 1 | 0.52025 | 41620 | 0.13111 | 4719.96 | 0.31538 | 3784.56 | 1 | 5000 | 4719.96 | 3784.56 | 0 | 0 | 0 | 0 | 28115.48 | 0 | 0 | 0 | 0 | 0 | 28115.48
2022120417 | 1 | 0.52654 | 42123.2 | 0.12046 | 4336.56 | 0.15952 | 1914.24 | 1 | 5000 | 4336.56 | 1914.24 | 0 | 0 | 0 | 0 | 30872.4 | 0 | 0 | 0 | 0 | 0 | 30872.4
2022120418 | 1 | 0.5488 | 43904 | 0.14925 | 5373 | 0.01048 | 125.76 | 1 | 5000 | 5373 | 125.76 | 0 | 0 | 0 | 0 | 33405.24 | 0 | 0 | 0 | 0 | 0 | 33405.24
2022120419 | 1 | 0.56338 | 45070.4 | 0.21148 | 7613.28 | 0 | 0 | 1 | 5000 | 7613.28 | 0 | 0 | 0 | 0 | 0 | 32457.12 | 0 | 0 | 0 | 0 | 0 | 32457.12
2022120420 | 1 | 0.56094 | 44875.2 | 0.27385 | 9858.6 | 0 | 0 | 1 | 5000 | 9858.6 | 0 | 0 | 0 | 0 | 0 | 30016.6 | 0 | 0 | 0 | 0 | 0 | 30016.6
2022120421 | 1 | 0.55447 | 44357.6 | 0.34504 | 12421.44 | 0 | 0 | 1 | 5000 | 12421.44 | 0 | 0 | 0 | 0 | 0 | 26936.16 | 0 | 0 | 0 | 0 | 0 | 26936.16
2022120422 | 1 | 0.5431 | 43448 | 0.39919 | 14370.84 | 0 | 0 | 1 | 5000 | 14370.84 | 0 | 0 | 0 | 0 | 0 | 24077.16 | 0 | 0 | 0 | 0 | 0 | 24077.16
2022120423 | 1 | 0.52147 | 41717.6 | 0.44197 | 15910.92 | 0 | 0 | 1 | 5000 | 15910.92 | 0 | 0 | 0 | 0 | 0 | 20806.68 | 0 | 0 | 0 | 0 | 0 | 20806.68
2022120424 | 1 | 0.49426 | 39540.8 | 0.47051 | 16938.36 | 0 | 0 | 1 | 5000 | 16938.36 | 0 | 0 | 0 | 0 | 0 | 17602.44 | 0 | 0 | 0 | 0 | 0 | 17602.44
2022120501 | 2 | 0.47046 | 37636.8 | 0.49445 | 17800.2 | 0 | 0 | 1 | 5000 | 17800.2 | 0 | 0 | 0 | 0 | 0 | 14836.6 | 0 | 0 | 0 | 0 | 0 | 14836.6
2022120502 | 2 | 0.4542 | 36336 | 0.49887 | 17959.32 | 0 | 0 | 1 | 5000 | 17959.32 | 0 | 0 | 0 | 0 | 0 | 13376.68 | 0 | 0 | 0 | 0 | 0 | 13376.68
2022120503 | 2 | 0.44854 | 35883.2 | 0.49921 | 17971.56 | 0 | 0 | 1 | 5000 | 17971.56 | 0 | 0 | 0 | 0 | 0 | 12911.64 | 0 | 0 | 0 | 0 | 0 | 12911.64
2022120504 | 2 | 0.4455 | 35640 | 0.48912 | 17608.32 | 0 | 0 | 1 | 5000 | 17608.32 | 0 | 0 | 0 | 0 | 0 | 13031.68 | 0 | 0 | 0 | 0 | 0 | 13031.68
2022120505 | 2 | 0.45408 | 36326.4 | 0.48342 | 17403.12 | 0 | 0 | 1 | 5000 | 17403.12 | 0 | 0 | 0 | 0 | 0 | 13923.28 | 0 | 0 | 0 | 0 | 0 | 13923.28
2022120506 | 2 | 0.47636 | 38108.8 | 0.46702 | 16812.72 | 0 | 0 | 1 | 5000 | 16812.72 | 0 | 0 | 0 | 0 | 0 | 16296.08 | 0 | 0 | 0 | 0 | 0 | 16296.08
2022120507 | 2 | 0.51286 | 41028.8 | 0.46047 | 16576.92 | 0 | 0 | 1 | 5000 | 16576.92 | 0 | 0 | 0 | 0 | 0 | 19451.88 | 0 | 0 | 0 | 0 | 0 | 19451.88
2022120508 | 2 | 0.52839 | 42271.2 | 0.4467 | 16081.2 | 0.00498 | 59.76 | 1 | 5000 | 16081.2 | 59.76 | 0 | 0 | 0 | 0 | 21130.24 | 0 | 0 | 0 | 0 | 0 | 21130.24
2022120509 | 2 | 0.53631 | 42904.8 | 0.44012 | 15844.32 | 0.10257 | 1230.84 | 1 | 5000 | 15844.32 | 1230.84 | 0 | 0 | 0 | 0 | 20829.64 | 0 | 0 | 0 | 0 | 0 | 20829.64
2022120510 | 2 | 0.54536 | 43628.8 | 0.40928 | 14734.08 | 0.25848 | 3101.76 | 1 | 5000 | 14734.08 | 3101.76 | 0 | 0 | 0 | 0 | 20792.96 | 0 | 0 | 0 | 0 | 0 | 20792.96
2022120511 | 2 | 0.55047 | 44037.6 | 0.4278 | 15400.8 | 0.33503 | 4020.36 | 1 | 5000 | 15400.8 | 4020.36 | 0 | 0 | 0 | 0 | 19616.44 | 0 | 0 | 0 | 0 | 0 | 19616.44
2022120512 | 2 | 0.55474 | 44379.2 | 0.42342 | 15243.12 | 0.37013 | 4441.56 | 1 | 5000 | 15243.12 | 4441.56 | 0 | 0 | 0 | 0 | 19694.52 | 0 | 0 | 0 | 0 | 0 | 19694.52
2022120513 | 2 | 0.55818 | 44654.4 | 0.42914 | 15449.04 | 0.35724 | 4286.88 | 1 | 5000 | 15449.04 | 4286.88 | 0 | 0 | 0 | 0 | 19918.48 | 0 | 0 | 0 | 0 | 0 | 19918.48
2022120514 | 2 | 0.56375 | 45100 | 0.42749 | 15389.64 | 0.36789 | 4414.68 | 1 | 5000 | 15389.64 | 4414.68 | 0 | 0 | 0 | 0 | 20295.68 | 0 | 0 | 0 | 0 | 0 | 20295.68
2022120515 | 2 | 0.57057 | 45645.6 | 0.43733 | 15743.88 | 0.33749 | 4049.88 | 1 | 5000 | 15743.88 | 4049.88 | 0 | 0 | 0 | 0 | 20851.84 | 0 | 0 | 0 | 0 | 0 | 20851.84
2022120516 | 2 | 0.57355 | 45884 | 0.44816 | 16133.76 | 0.29955 | 3594.6 | 1 | 5000 | 16133.76 | 3594.6 | 0 | 0 | 0 | 0 | 21155.64 | 0 | 0 | 0 | 0 | 0 | 21155.64
2022120517 | 2 | 0.57604 | 46083.2 | 0.44727 | 16101.72 | 0.18239 | 2188.68 | 1 | 5000 | 16101.72 | 2188.68 | 0 | 0 | 0 | 0 | 22792.8 | 0 | 0 | 0 | 0 | 0 | 22792.8
2022120518 | 2 | 0.58803 | 47042.4 | 0.44743 | 16107.48 | 0.01029 | 123.48 | 1 | 5000 | 16107.48 | 123.48 | 0 | 0 | 0 | 0 | 25811.44 | 0 | 0 | 0 | 0 | 0 | 25811.44
2022120519 | 2 | 0.59854 | 47883.2 | 0.4945 | 17802 | 0 | 0 | 1 | 5000 | 17802 | 0 | 0 | 0 | 0 | 0 | 25081.2 | 0 | 0 | 0 | 0 | 0 | 25081.2
2022120520 | 2 | 0.59248 | 47398.4 | 0.52106 | 18758.16 | 0 | 0 | 1 | 5000 | 18758.16 | 0 | 0 | 0 | 0 | 0 | 23640.24 | 0 | 0 | 0 | 0 | 0 | 23640.24
2022120521 | 2 | 0.57974 | 46379.2 | 0.54015 | 19445.4 | 0 | 0 | 1 | 5000 | 19445.4 | 0 | 0 | 0 | 0 | 0 | 21933.8 | 0 | 0 | 0 | 0 | 0 | 21933.8
2022120522 | 2 | 0.56106 | 44884.8 | 0.53758 | 19352.88 | 0 | 0 | 1 | 5000 | 19352.88 | 0 | 0 | 0 | 0 | 0 | 20531.92 | 0 | 0 | 0 | 0 | 0 | 20531.92
2022120523 | 2 | 0.52879 | 42303.2 | 0.51114 | 18401.04 | 0 | 0 | 1 | 5000 | 18401.04 | 0 | 0 | 0 | 0 | 0 | 18902.16 | 0 | 0 | 0 | 0 | 0 | 18902.16
2022120524 | 2 | 0.49229 | 39383.2 | 0.48645 | 17512.2 | 0 | 0 | 1 | 5000 | 17512.2 | 0 | 0 | 0 | 0 | 0 | 16871 | 0 | 0 | 0 | 0 | 0 | 16871
2022120601 | 3 | 0.46883 | 37506.4 | 0.45626 | 16425.36 | 0 | 0 | 1 | 5000 | 16425.36 | 0 | 0 | 0 | 0 | 0 | 16081.04 | 0 | 0 | 0 | 0 | 0 | 16081.04
2022120602 | 3 | 0.45027 | 36021.6 | 0.4334 | 15602.4 | 0 | 0 | 1 | 5000 | 15602.4 | 0 | 0 | 0 | 0 | 0 | 15419.2 | 0 | 0 | 0 | 0 | 0 | 15419.2
2022120603 | 3 | 0.44041 | 35232.8 | 0.41313 | 14872.68 | 0 | 0 | 1 | 5000 | 14872.68 | 0 | 0 | 0 | 0 | 0 | 15360.12 | 0 | 0 | 0 | 0 | 0 | 15360.12
2022120604 | 3 | 0.43789 | 35031.2 | 0.38781 | 13961.16 | 0 | 0 | 1 | 5000 | 13961.16 | 0 | 0 | 0 | 0 | 0 | 16070.04 | 0 | 0 | 0 | 0 | 0 | 16070.04
2022120605 | 3 | 0.44272 | 35417.6 | 0.37316 | 13433.76 | 0 | 0 | 1 | 5000 | 13433.76 | 0 | 0 | 0 | 0 | 0 | 16983.84 | 0 | 0 | 0 | 0 | 0 | 16983.84
2022120606 | 3 | 0.46349 | 37079.2 | 0.34378 | 12376.08 | 0 | 0 | 1 | 5000 | 12376.08 | 0 | 0 | 0 | 0 | 0 | 19703.12 | 0 | 0 | 0 | 0 | 0 | 19703.12
2022120607 | 3 | 0.50238 | 40190.4 | 0.31351 | 11286.36 | 0 | 0 | 1 | 5000 | 11286.36 | 0 | 0 | 0 | 0 | 0 | 23904.04 | 0 | 0 | 0 | 0 | 0 | 23904.04
2022120608 | 3 | 0.51861 | 41488.8 | 0.28111 | 10119.96 | 0.00924 | 110.88 | 1 | 5000 | 10119.96 | 110.88 | 0 | 0 | 0 | 0 | 26257.96 | 0 | 0 | 0 | 0 | 0 | 26257.96
2022120609 | 3 | 0.52292 | 41833.6 | 0.23411 | 8427.96 | 0.0737 | 884.4 | 1 | 5000 | 8427.96 | 884.4 | 0 | 0 | 0 | 0 | 27521.24 | 0 | 0 | 0 | 0 | 0 | 27521.24
2022120610 | 3 | 0.53235 | 42588 | 0.20853 | 7507.08 | 0.13763 | 1651.56 | 1 | 5000 | 7507.08 | 1651.56 | 0 | 0 | 0 | 0 | 28429.36 | 0 | 0 | 0 | 0 | 0 | 28429.36
2022120611 | 3 | 0.54627 | 43701.6 | 0.20327 | 7317.72 | 0.20728 | 2487.36 | 1 | 5000 | 7317.72 | 2487.36 | 0 | 0 | 0 | 0 | 28896.52 | 0 | 0 | 0 | 0 | 0 | 28896.52
2022120612 | 3 | 0.55509 | 44407.2 | 0.18986 | 6834.96 | 0.26162 | 3139.44 | 1 | 5000 | 6834.96 | 3139.44 | 0 | 0 | 0 | 0 | 29432.8 | 0 | 0 | 0 | 0 | 0 | 29432.8
2022120613 | 3 | 0.56485 | 45188 | 0.19189 | 6908.04 | 0.30453 | 3654.36 | 1 | 5000 | 6908.04 | 3654.36 | 0 | 0 | 0 | 0 | 29625.6 | 0 | 0 | 0 | 0 | 0 | 29625.6
2022120614 | 3 | 0.57761 | 46208.8 | 0.20447 | 7360.92 | 0.30712 | 3685.44 | 1 | 5000 | 7360.92 | 3685.44 | 0 | 0 | 0 | 0 | 30162.44 | 0 | 0 | 0 | 0 | 0 | 30162.44
2022120615 | 3 | 0.58391 | 46712.8 | 0.2149 | 7736.4 | 0.26014 | 3121.68 | 1 | 5000 | 7736.4 | 3121.68 | 0 | 0 | 0 | 0 | 30854.72 | 0 | 0 | 0 | 0 | 0 | 30854.72
2022120616 | 3 | 0.586 | 46880 | 0.21392 | 7701.12 | 0.16163 | 1939.56 | 1 | 5000 | 7701.12 | 1939.56 | 0 | 0 | 0 | 0 | 32239.32 | 0 | 0 | 0 | 0 | 0 | 32239.32
2022120617 | 3 | 0.58227 | 46581.6 | 0.21303 | 7669.08 | 0.0611 | 733.2 | 1 | 5000 | 7669.08 | 733.2 | 0 | 0 | 0 | 0 | 33179.32 | 0 | 0 | 0 | 0 | 0 | 33179.32
2022120618 | 3 | 0.59063 | 47250.4 | 0.2218 | 7984.8 | 0.00518 | 62.16 | 1 | 5000 | 7984.8 | 62.16 | 0 | 0 | 0 | 0 | 34203.44 | 0 | 0 | 0 | 0 | 0 | 34203.44
2022120619 | 3 | 0.59964 | 47971.2 | 0.25648 | 9233.28 | 0 | 0 | 1 | 5000 | 9233.28 | 0 | 0 | 0 | 0 | 0 | 33737.92 | 0 | 0 | 0 | 0 | 0 | 33737.92
2022120620 | 3 | 0.59495 | 47596 | 0.29754 | 10711.44 | 0 | 0 | 1 | 5000 | 10711.44 | 0 | 0 | 0 | 0 | 0 | 31884.56 | 0 | 0 | 0 | 0 | 0 | 31884.56
2022120621 | 3 | 0.58318 | 46654.4 | 0.32546 | 11716.56 | 0 | 0 | 1 | 5000 | 11716.56 | 0 | 0 | 0 | 0 | 0 | 29937.84 | 0 | 0 | 0 | 0 | 0 | 29937.84
2022120622 | 3 | 0.56921 | 45536.8 | 0.36937 | 13297.32 | 0 | 0 | 1 | 5000 | 13297.32 | 0 | 0 | 0 | 0 | 0 | 27239.48 | 0 | 0 | 0 | 0 | 0 | 27239.48
2022120623 | 3 | 0.53801 | 43040.8 | 0.39714 | 14297.04 | 0 | 0 | 1 | 5000 | 14297.04 | 0 | 0 | 0 | 0 | 0 | 23743.76 | 0 | 0 | 0 | 0 | 0 | 23743.76
2022120624 | 3 | 0.50091 | 40072.8 | 0.3834 | 13802.4 | 0 | 0 | 1 | 5000 | 13802.4 | 0 | 0 | 0 | 0 | 0 | 21270.4 | 0 | 0 | 0 | 0 | 0 | 21270.4
2022120701 | 4 | 0.47309 | 37847.2 | 0.35518 | 12786.48 | 0 | 0 | 1 | 5000 | 12786.48 | 0 | 0 | 0 | 0 | 0 | 20060.72 | 0 | 0 | 0 | 0 | 0 | 20060.72
2022120702 | 4 | 0.45691 | 36552.8 | 0.32525 | 11709 | 0 | 0 | 1 | 5000 | 11709 | 0 | 0 | 0 | 0 | 0 | 19843.8 | 0 | 0 | 0 | 0 | 0 | 19843.8
2022120703 | 4 | 0.44787 | 35829.6 | 0.28773 | 10358.28 | 0 | 0 | 1 | 5000 | 10358.28 | 0 | 0 | 0 | 0 | 0 | 20471.32 | 0 | 0 | 0 | 0 | 0 | 20471.32
2022120704 | 4 | 0.44124 | 35299.2 | 0.24198 | 8711.28 | 0 | 0 | 1 | 5000 | 8711.28 | 0 | 0 | 0 | 0 | 0 | 21587.92 | 0 | 0 | 0 | 0 | 0 | 21587.92
2022120705 | 4 | 0.4312 | 34496 | 0.21887 | 7879.32 | 0 | 0 | 1 | 5000 | 7879.32 | 0 | 0 | 0 | 0 | 0 | 21616.68 | 0 | 0 | 0 | 0 | 0 | 21616.68
2022120706 | 4 | 0.45886 | 36708.8 | 0.18787 | 6763.32 | 0 | 0 | 1 | 5000 | 6763.32 | 0 | 0 | 0 | 0 | 0 | 24945.48 | 0 | 0 | 0 | 0 | 0 | 24945.48
2022120707 | 4 | 0.4997 | 39976 | 0.17028 | 6130.08 | 0 | 0 | 1 | 5000 | 6130.08 | 0 | 0 | 0 | 0 | 0 | 28845.92 | 0 | 0 | 0 | 0 | 0 | 28845.92
2022120708 | 4 | 0.51819 | 41455.2 | 0.16432 | 5915.52 | 0.00468 | 56.16 | 1 | 5000 | 5915.52 | 56.16 | 0 | 0 | 0 | 0 | 30483.52 | 0 | 0 | 0 | 0 | 0 | 30483.52
2022120709 | 4 | 0.52722 | 42177.6 | 0.16255 | 5851.8 | 0.05369 | 644.28 | 1 | 5000 | 5851.8 | 644.28 | 0 | 0 | 0 | 0 | 30681.52 | 0 | 0 | 0 | 0 | 0 | 30681.52
2022120710 | 4 | 0.54189 | 43351.2 | 0.16654 | 5995.44 | 0.17207 | 2064.84 | 1 | 5000 | 5995.44 | 2064.84 | 0 | 0 | 0 | 0 | 30290.92 | 0 | 0 | 0 | 0 | 0 | 30290.92
2022120711 | 4 | 0.55612 | 44489.6 | 0.1983 | 7138.8 | 0.27205 | 3264.6 | 1 | 5000 | 7138.8 | 3264.6 | 0 | 0 | 0 | 0 | 29086.2 | 0 | 0 | 0 | 0 | 0 | 29086.2
2022120712 | 4 | 0.56987 | 45589.6 | 0.20805 | 7489.8 | 0.30641 | 3676.92 | 1 | 5000 | 7489.8 | 3676.92 | 0 | 0 | 0 | 0 | 29422.88 | 0 | 0 | 0 | 0 | 0 | 29422.88
2022120713 | 4 | 0.5819 | 46552 | 0.20233 | 7283.88 | 0.31844 | 3821.28 | 1 | 5000 | 7283.88 | 3821.28 | 0 | 0 | 0 | 0 | 30446.84 | 0 | 0 | 0 | 0 | 0 | 30446.84
2022120714 | 4 | 0.58813 | 47050.4 | 0.2024 | 7286.4 | 0.30727 | 3687.24 | 1 | 5000 | 7286.4 | 3687.24 | 0 | 0 | 0 | 0 | 31076.76 | 0 | 0 | 0 | 0 | 0 | 31076.76
2022120715 | 4 | 0.58941 | 47152.8 | 0.19934 | 7176.24 | 0.22103 | 2652.36 | 1 | 5000 | 7176.24 | 2652.36 | 0 | 0 | 0 | 0 | 32324.2 | 0 | 0 | 0 | 0 | 0 | 32324.2
2022120716 | 4 | 0.58934 | 47147.2 | 0.20115 | 7241.4 | 0.17669 | 2120.28 | 1 | 5000 | 7241.4 | 2120.28 | 0 | 0 | 0 | 0 | 32785.52 | 0 | 0 | 0 | 0 | 0 | 32785.52
2022120717 | 4 | 0.58998 | 47198.4 | 0.2029 | 7304.4 | 0.08321 | 998.52 | 1 | 5000 | 7304.4 | 998.52 | 0 | 0 | 0 | 0 | 33895.48 | 0 | 0 | 0 | 0 | 0 | 33895.48
2022120718 | 4 | 0.59641 | 47712.8 | 0.2042 | 7351.2 | 0.0076 | 91.2 | 1 | 5000 | 7351.2 | 91.2 | 0 | 0 | 0 | 0 | 35270.4 | 0 | 0 | 0 | 0 | 0 | 35270.4
2022120719 | 4 | 0.60099 | 48079.2 | 0.2201 | 7923.6 | 0 | 0 | 1 | 5000 | 7923.6 | 0 | 0 | 0 | 0 | 0 | 35155.6 | 0 | 0 | 0 | 0 | 0 | 35155.6
2022120720 | 4 | 0.59373 | 47498.4 | 0.23003 | 8281.08 | 0 | 0 | 1 | 5000 | 8281.08 | 0 | 0 | 0 | 0 | 0 | 34217.32 | 0 | 0 | 0 | 0 | 0 | 34217.32
2022120721 | 4 | 0.58222 | 46577.6 | 0.23944 | 8619.84 | 0 | 0 | 1 | 5000 | 8619.84 | 0 | 0 | 0 | 0 | 0 | 32957.76 | 0 | 0 | 0 | 0 | 0 | 32957.76
2022120722 | 4 | 0.56501 | 45200.8 | 0.25476 | 9171.36 | 0 | 0 | 1 | 5000 | 9171.36 | 0 | 0 | 0 | 0 | 0 | 31029.44 | 0 | 0 | 0 | 0 | 0 | 31029.44
2022120723 | 4 | 0.53792 | 43033.6 | 0.2567 | 9241.2 | 0 | 0 | 1 | 5000 | 9241.2 | 0 | 0 | 0 | 0 | 0 | 28792.4 | 0 | 0 | 0 | 0 | 0 | 28792.4
2022120724 | 4 | 0.50796 | 40636.8 | 0.25893 | 9321.48 | 0 | 0 | 1 | 5000 | 9321.48 | 0 | 0 | 0 | 0 | 0 | 26315.32 | 0 | 0 | 0 | 0 | 0 | 26315.32
2022120801 | 5 | 0.48322 | 38657.6 | 0.26968 | 9708.48 | 0 | 0 | 1 | 5000 | 9708.48 | 0 | 0 | 0 | 0 | 0 | 23949.12 | 0 | 0 | 0 | 0 | 0 | 23949.12
2022120802 | 5 | 0.46748 | 37398.4 | 0.26444 | 9519.84 | 0 | 0 | 1 | 5000 | 9519.84 | 0 | 0 | 0 | 0 | 0 | 22878.56 | 0 | 0 | 0 | 0 | 0 | 22878.56
2022120803 | 5 | 0.45855 | 36684 | 0.24289 | 8744.04 | 0 | 0 | 1 | 5000 | 8744.04 | 0 | 0 | 0 | 0 | 0 | 22939.96 | 0 | 0 | 0 | 0 | 0 | 22939.96
2022120804 | 5 | 0.45361 | 36288.8 | 0.23777 | 8559.72 | 0 | 0 | 1 | 5000 | 8559.72 | 0 | 0 | 0 | 0 | 0 | 22729.08 | 0 | 0 | 0 | 0 | 0 | 22729.08
2022120805 | 5 | 0.45693 | 36554.4 | 0.25355 | 9127.8 | 0 | 0 | 1 | 5000 | 9127.8 | 0 | 0 | 0 | 0 | 0 | 22426.6 | 0 | 0 | 0 | 0 | 0 | 22426.6
2022120806 | 5 | 0.47746 | 38196.8 | 0.26002 | 9360.72 | 0 | 0 | 1 | 5000 | 9360.72 | 0 | 0 | 0 | 0 | 0 | 23836.08 | 0 | 0 | 0 | 0 | 0 | 23836.08
2022120807 | 5 | 0.51562 | 41249.6 | 0.24862 | 8950.32 | 0 | 0 | 1 | 5000 | 8950.32 | 0 | 0 | 0 | 0 | 0 | 27299.28 | 0 | 0 | 0 | 0 | 0 | 27299.28
2022120808 | 5 | 0.53162 | 42529.6 | 0.24963 | 8986.68 | 0.005 | 60 | 1 | 5000 | 8986.68 | 60 | 0 | 0 | 0 | 0 | 28482.92 | 0 | 0 | 0 | 0 | 0 | 28482.92
2022120809 | 5 | 0.53608 | 42886.4 | 0.22586 | 8130.96 | 0.11815 | 1417.8 | 1 | 5000 | 8130.96 | 1417.8 | 0 | 0 | 0 | 0 | 28337.64 | 0 | 0 | 0 | 0 | 0 | 28337.64
2022120810 | 5 | 0.54996 | 43996.8 | 0.22489 | 8096.04 | 0.30103 | 3612.36 | 1 | 5000 | 8096.04 | 3612.36 | 0 | 0 | 0 | 0 | 27288.4 | 0 | 0 | 0 | 0 | 0 | 27288.4
2022120811 | 5 | 0.56365 | 45092 | 0.23939 | 8618.04 | 0.3929 | 4714.8 | 1 | 5000 | 8618.04 | 4714.8 | 0 | 0 | 0 | 0 | 26759.16 | 0 | 0 | 0 | 0 | 0 | 26759.16
2022120812 | 5 | 0.57537 | 46029.6 | 0.23385 | 8418.6 | 0.41569 | 4988.28 | 1 | 5000 | 8418.6 | 4988.28 | 0 | 0 | 0 | 0 | 27622.72 | 0 | 0 | 0 | 0 | 0 | 27622.72
2022120813 | 5 | 0.58595 | 46876 | 0.21269 | 7656.84 | 0.42107 | 5052.84 | 1 | 5000 | 7656.84 | 5052.84 | 0 | 0 | 0 | 0 | 29166.32 | 0 | 0 | 0 | 0 | 0 | 29166.32
2022120814 | 5 | 0.59749 | 47799.2 | 0.19587 | 7051.32 | 0.42357 | 5082.84 | 1 | 5000 | 7051.32 | 5082.84 | 0 | 0 | 0 | 0 | 30665.04 | 0 | 0 | 0 | 0 | 0 | 30665.04
2022120815 | 5 | 0.60164 | 48131.2 | 0.18478 | 6652.08 | 0.41321 | 4958.52 | 1 | 5000 | 6652.08 | 4958.52 | 0 | 0 | 0 | 0 | 31520.6 | 0 | 0 | 0 | 0 | 0 | 31520.6
2022120816 | 5 | 0.60269 | 48215.2 | 0.17865 | 6431.4 | 0.41483 | 4977.96 | 1 | 5000 | 6431.4 | 4977.96 | 0 | 0 | 0 | 0 | 31805.84 | 0 | 0 | 0 | 0 | 0 | 31805.84
2022120817 | 5 | 0.60199 | 48159.2 | 0.14891 | 5360.76 | 0.25888 | 3106.56 | 1 | 5000 | 5360.76 | 3106.56 | 0 | 0 | 0 | 0 | 34691.88 | 0 | 0 | 0 | 0 | 0 | 34691.88
2022120818 | 5 | 0.60304 | 48243.2 | 0.1309 | 4712.4 | 0.02601 | 312.12 | 1 | 5000 | 4712.4 | 312.12 | 0 | 0 | 0 | 0 | 38218.68 | 0 | 0 | 0 | 0 | 0 | 38218.68
2022120819 | 5 | 0.60646 | 48516.8 | 0.14055 | 5059.8 | 0.00171 | 20.52 | 1 | 5000 | 5059.8 | 20.52 | 0 | 0 | 0 | 0 | 38436.48 | 0 | 0 | 0 | 0 | 0 | 38436.48
2022120820 | 5 | 0.59479 | 47583.2 | 0.14189 | 5108.04 | 0.0009 | 10.8 | 1 | 5000 | 5108.04 | 10.8 | 0 | 0 | 0 | 0 | 37464.36 | 0 | 0 | 0 | 0 | 0 | 37464.36
2022120821 | 5 | 0.58648 | 46918.4 | 0.14773 | 5318.28 | 0 | 0 | 1 | 5000 | 5318.28 | 0 | 0 | 0 | 0 | 0 | 36600.12 | 0 | 0 | 0 | 0 | 0 | 36600.12
2022120822 | 5 | 0.56932 | 45545.6 | 0.1541 | 5547.6 | 0 | 0 | 1 | 5000 | 5547.6 | 0 | 0 | 0 | 0 | 0 | 34998 | 0 | 0 | 0 | 0 | 0 | 34998
2022120823 | 5 | 0.53983 | 43186.4 | 0.16013 | 5764.68 | 0 | 0 | 1 | 5000 | 5764.68 | 0 | 0 | 0 | 0 | 0 | 32421.72 | 0 | 0 | 0 | 0 | 0 | 32421.72
2022120824 | 5 | 0.5089 | 40712 | 0.15797 | 5686.92 | 0 | 0 | 1 | 5000 | 5686.92 | 0 | 0 | 0 | 0 | 0 | 30025.08 | 0 | 0 | 0 | 0 | 0 | 30025.08
2022120901 | 6 | 0.48223 | 38578.4 | 0.14422 | 5191.92 | 0 | 0 | 1 | 5000 | 5191.92 | 0 | 0 | 0 | 0 | 0 | 28386.48 | 0 | 0 | 0 | 0 | 0 | 28386.48
2022120902 | 6 | 0.46595 | 37276 | 0.13262 | 4774.32 | 0 | 0 | 1 | 5000 | 4774.32 | 0 | 0 | 0 | 0 | 0 | 27501.68 | 0 | 0 | 0 | 0 | 0 | 27501.68
2022120903 | 6 | 0.45333 | 36266.4 | 0.12223 | 4400.28 | 0 | 0 | 1 | 5000 | 4400.28 | 0 | 0 | 0 | 0 | 0 | 26866.12 | 0 | 0 | 0 | 0 | 0 | 26866.12
2022120904 | 6 | 0.44859 | 35887.2 | 0.11298 | 4067.28 | 0 | 0 | 1 | 5000 | 4067.28 | 0 | 0 | 0 | 0 | 0 | 26819.92 | 0 | 0 | 0 | 0 | 0 | 26819.92
2022120905 | 6 | 0.45497 | 36397.6 | 0.10475 | 3771 | 0 | 0 | 1 | 5000 | 3771 | 0 | 0 | 0 | 0 | 0 | 27626.6 | 0 | 0 | 0 | 0 | 0 | 27626.6
2022120906 | 6 | 0.47141 | 37712.8 | 0.11276 | 4059.36 | 0 | 0 | 1 | 5000 | 4059.36 | 0 | 0 | 0 | 0 | 0 | 28653.44 | 0 | 0 | 0 | 0 | 0 | 28653.44
2022120907 | 6 | 0.5085 | 40680 | 0.11786 | 4242.96 | 0 | 0 | 1 | 5000 | 4242.96 | 0 | 0 | 0 | 0 | 0 | 31437.04 | 0 | 0 | 0 | 0 | 0 | 31437.04
2022120908 | 6 | 0.52584 | 42067.2 | 0.11024 | 3968.64 | 0.00333 | 39.96 | 1 | 5000 | 3968.64 | 39.96 | 0 | 0 | 0 | 0 | 33058.6 | 0 | 0 | 0 | 0 | 0 | 33058.6
2022120909 | 6 | 0.53114 | 42491.2 | 0.09964 | 3587.04 | 0.04044 | 485.28 | 1 | 5000 | 3587.04 | 485.28 | 0 | 0 | 0 | 0 | 33418.88 | 0 | 0 | 0 | 0 | 0 | 33418.88
2022120910 | 6 | 0.54231 | 43384.8 | 0.09342 | 3363.12 | 0.11243 | 1349.16 | 1 | 5000 | 3363.12 | 1349.16 | 0 | 0 | 0 | 0 | 33672.52 | 0 | 0 | 0 | 0 | 0 | 33672.52
2022120911 | 6 | 0.55543 | 44434.4 | 0.10486 | 3774.96 | 0.17284 | 2074.08 | 1 | 5000 | 3774.96 | 2074.08 | 0 | 0 | 0 | 0 | 33585.36 | 0 | 0 | 0 | 0 | 0 | 33585.36
2022120912 | 6 | 0.56566 | 45252.8 | 0.12082 | 4349.52 | 0.21385 | 2566.2 | 1 | 5000 | 4349.52 | 2566.2 | 0 | 0 | 0 | 0 | 33337.08 | 0 | 0 | 0 | 0 | 0 | 33337.08
2022120913 | 6 | 0.57751 | 46200.8 | 0.13343 | 4803.48 | 0.24929 | 2991.48 | 1 | 5000 | 4803.48 | 2991.48 | 0 | 0 | 0 | 0 | 33405.84 | 0 | 0 | 0 | 0 | 0 | 33405.84
2022120914 | 6 | 0.58726 | 46980.8 | 0.14923 | 5372.28 | 0.26436 | 3172.32 | 1 | 5000 | 5372.28 | 3172.32 | 0 | 0 | 0 | 0 | 33436.2 | 0 | 0 | 0 | 0 | 0 | 33436.2
2022120915 | 6 | 0.59479 | 47583.2 | 0.17367 | 6252.12 | 0.24823 | 2978.76 | 1 | 5000 | 6252.12 | 2978.76 | 0 | 0 | 0 | 0 | 33352.32 | 0 | 0 | 0 | 0 | 0 | 33352.32
2022120916 | 6 | 0.59491 | 47592.8 | 0.19516 | 7025.76 | 0.22072 | 2648.64 | 1 | 5000 | 7025.76 | 2648.64 | 0 | 0 | 0 | 0 | 32918.4 | 0 | 0 | 0 | 0 | 0 | 32918.4
2022120917 | 6 | 0.58986 | 47188.8 | 0.19647 | 7072.92 | 0.09624 | 1154.88 | 1 | 5000 | 7072.92 | 1154.88 | 0 | 0 | 0 | 0 | 33961 | 0 | 0 | 0 | 0 | 0 | 33961
2022120918 | 6 | 0.59217 | 47373.6 | 0.19594 | 7053.84 | 0.00697 | 83.64 | 1 | 5000 | 7053.84 | 83.64 | 0 | 0 | 0 | 0 | 35236.12 | 0 | 0 | 0 | 0 | 0 | 35236.12
2022120919 | 6 | 0.59168 | 47334.4 | 0.2057 | 7405.2 | 0 | 0 | 1 | 5000 | 7405.2 | 0 | 0 | 0 | 0 | 0 | 34929.2 | 0 | 0 | 0 | 0 | 0 | 34929.2
2022120920 | 6 | 0.57828 | 46262.4 | 0.21454 | 7723.44 | 0 | 0 | 1 | 5000 | 7723.44 | 0 | 0 | 0 | 0 | 0 | 33538.96 | 0 | 0 | 0 | 0 | 0 | 33538.96
2022120921 | 6 | 0.56387 | 45109.6 | 0.21982 | 7913.52 | 0 | 0 | 1 | 5000 | 7913.52 | 0 | 0 | 0 | 0 | 0 | 32196.08 | 0 | 0 | 0 | 0 | 0 | 32196.08
2022120922 | 6 | 0.55033 | 44026.4 | 0.2433 | 8758.8 | 0 | 0 | 1 | 5000 | 8758.8 | 0 | 0 | 0 | 0 | 0 | 30267.6 | 0 | 0 | 0 | 0 | 0 | 30267.6
2022120923 | 6 | 0.52875 | 42300 | 0.2953 | 10630.8 | 0 | 0 | 1 | 5000 | 10630.8 | 0 | 0 | 0 | 0 | 0 | 26669.2 | 0 | 0 | 0 | 0 | 0 | 26669.2
2022120924 | 6 | 0.49934 | 39947.2 | 0.29455 | 10603.8 | 0 | 0 | 1 | 5000 | 10603.8 | 0 | 0 | 0 | 0 | 0 | 24343.4 | 0 | 0 | 0 | 0 | 0 | 24343.4
2022121001 | 7 | 0.47478 | 37982.4 | 0.25821 | 9295.56 | 0 | 0 | 1 | 5000 | 9295.56 | 0 | 0 | 0 | 0 | 0 | 23686.84 | 0 | 0 | 0 | 0 | 0 | 23686.84
2022121002 | 7 | 0.45999 | 36799.2 | 0.24431 | 8795.16 | 0 | 0 | 1 | 5000 | 8795.16 | 0 | 0 | 0 | 0 | 0 | 23004.04 | 0 | 0 | 0 | 0 | 0 | 23004.04
2022121003 | 7 | 0.4508 | 36064 | 0.22665 | 8159.4 | 0 | 0 | 1 | 5000 | 8159.4 | 0 | 0 | 0 | 0 | 0 | 22904.6 | 0 | 0 | 0 | 0 | 0 | 22904.6
2022121004 | 7 | 0.44045 | 35236 | 0.19406 | 6986.16 | 0 | 0 | 1 | 5000 | 6986.16 | 0 | 0 | 0 | 0 | 0 | 23249.84 | 0 | 0 | 0 | 0 | 0 | 23249.84
2022121005 | 7 | 0.43891 | 35112.8 | 0.17337 | 6241.32 | 0 | 0 | 1 | 5000 | 6241.32 | 0 | 0 | 0 | 0 | 0 | 23871.48 | 0 | 0 | 0 | 0 | 0 | 23871.48
2022121006 | 7 | 0.44328 | 35462.4 | 0.16477 | 5931.72 | 0 | 0 | 1 | 5000 | 5931.72 | 0 | 0 | 0 | 0 | 0 | 24530.68 | 0 | 0 | 0 | 0 | 0 | 24530.68
2022121007 | 7 | 0.45702 | 36561.6 | 0.16002 | 5760.72 | 0 | 0 | 1 | 5000 | 5760.72 | 0 | 0 | 0 | 0 | 0 | 25800.88 | 0 | 0 | 0 | 0 | 0 | 25800.88
2022121008 | 7 | 0.47462 | 37969.6 | 0.14722 | 5299.92 | 0.00643 | 77.16 | 1 | 5000 | 5299.92 | 77.16 | 0 | 0 | 0 | 0 | 27592.52 | 0 | 0 | 0 | 0 | 0 | 27592.52
2022121009 | 7 | 0.49438 | 39550.4 | 0.13537 | 4873.32 | 0.06318 | 758.16 | 1 | 5000 | 4873.32 | 758.16 | 0 | 0 | 0 | 0 | 28918.92 | 0 | 0 | 0 | 0 | 0 | 28918.92
2022121010 | 7 | 0.5205 | 41640 | 0.13948 | 5021.28 | 0.1326 | 1591.2 | 1 | 5000 | 5021.28 | 1591.2 | 0 | 0 | 0 | 0 | 30027.52 | 0 | 0 | 0 | 0 | 0 | 30027.52
2022121011 | 7 | 0.54243 | 43394.4 | 0.18121 | 6523.56 | 0.16595 | 1991.4 | 1 | 5000 | 6523.56 | 1991.4 | 0 | 0 | 0 | 0 | 29879.44 | 0 | 0 | 0 | 0 | 0 | 29879.44
2022121012 | 7 | 0.55593 | 44474.4 | 0.22157 | 7976.52 | 0.18716 | 2245.92 | 1 | 5000 | 7976.52 | 2245.92 | 0 | 0 | 0 | 0 | 29251.96 | 0 | 0 | 0 | 0 | 0 | 29251.96
2022121013 | 7 | 0.56328 | 45062.4 | 0.23818 | 8574.48 | 0.19059 | 2287.08 | 1 | 5000 | 8574.48 | 2287.08 | 0 | 0 | 0 | 0 | 29200.84 | 0 | 0 | 0 | 0 | 0 | 29200.84
2022121014 | 7 | 0.56767 | 45413.6 | 0.2453 | 8830.8 | 0.19684 | 2362.08 | 1 | 5000 | 8830.8 | 2362.08 | 0 | 0 | 0 | 0 | 29220.72 | 0 | 0 | 0 | 0 | 0 | 29220.72
2022121015 | 7 | 0.56683 | 45346.4 | 0.22782 | 8201.52 | 0.19588 | 2350.56 | 1 | 5000 | 8201.52 | 2350.56 | 0 | 0 | 0 | 0 | 29794.32 | 0 | 0 | 0 | 0 | 0 | 29794.32
2022121016 | 7 | 0.56392 | 45113.6 | 0.22613 | 8140.68 | 0.13675 | 1641 | 1 | 5000 | 8140.68 | 1641 | 0 | 0 | 0 | 0 | 30331.92 | 0 | 0 | 0 | 0 | 0 | 30331.92
2022121017 | 7 | 0.56135 | 44908 | 0.22201 | 7992.36 | 0.09984 | 1198.08 | 1 | 5000 | 7992.36 | 1198.08 | 0 | 0 | 0 | 0 | 30717.56 | 0 | 0 | 0 | 0 | 0 | 30717.56
2022121018 | 7 | 0.56712 | 45369.6 | 0.22296 | 8026.56 | 0.01805 | 216.6 | 1 | 5000 | 8026.56 | 216.6 | 0 | 0 | 0 | 0 | 32126.44 | 0 | 0 | 0 | 0 | 0 | 32126.44
2022121019 | 7 | 0.56594 | 45275.2 | 0.24036 | 8652.96 | 0 | 0 | 1 | 5000 | 8652.96 | 0 | 0 | 0 | 0 | 0 | 31622.24 | 0 | 0 | 0 | 0 | 0 | 31622.24
2022121020 | 7 | 0.55724 | 44579.2 | 0.23677 | 8523.72 | 0 | 0 | 1 | 5000 | 8523.72 | 0 | 0 | 0 | 0 | 0 | 31055.48 | 0 | 0 | 0 | 0 | 0 | 31055.48
2022121021 | 7 | 0.54702 | 43761.6 | 0.20846 | 7504.56 | 0 | 0 | 1 | 5000 | 7504.56 | 0 | 0 | 0 | 0 | 0 | 31257.04 | 0 | 0 | 0 | 0 | 0 | 31257.04
2022121022 | 7 | 0.53586 | 42868.8 | 0.17285 | 6222.6 | 0 | 0 | 1 | 5000 | 6222.6 | 0 | 0 | 0 | 0 | 0 | 31646.2 | 0 | 0 | 0 | 0 | 0 | 31646.2
2022121023 | 7 | 0.51689 | 41351.2 | 0.1518 | 5464.8 | 0 | 0 | 1 | 5000 | 5464.8 | 0 | 0 | 0 | 0 | 0 | 30886.4 | 0 | 0 | 0 | 0 | 0 | 30886.4
2022121024 | 7 | 0.49689 | 39751.2 | 0.12503 | 4501.08 | 0 | 0 | 1 | 5000 | 4501.08 | 0 | 0 | 0 | 0 | 0 | 30250.12 | 0 | 0 | 0 | 0 | 0 | 30250.12
2022121101 | 1 | 0.47388 | 37910.4 | 0.10113 | 3640.68 | 0 | 0 | 1 | 5000 | 3640.68 | 0 | 0 | 0 | 0 | 0 | 29269.72 | 0 | 0 | 0 | 0 | 0 | 29269.72
2022121102 | 1 | 0.45607 | 36485.6 | 0.09094 | 3273.84 | 0 | 0 | 1 | 5000 | 3273.84 | 0 | 0 | 0 | 0 | 0 | 28211.76 | 0 | 0 | 0 | 0 | 0 | 28211.76
2022121103 | 1 | 0.44499 | 35599.2 | 0.08567 | 3084.12 | 0 | 0 | 1 | 5000 | 3084.12 | 0 | 0 | 0 | 0 | 0 | 27515.08 | 0 | 0 | 0 | 0 | 0 | 27515.08
2022121104 | 1 | 0.43801 | 35040.8 | 0.07731 | 2783.16 | 0 | 0 | 1 | 5000 | 2783.16 | 0 | 0 | 0 | 0 | 0 | 27257.64 | 0 | 0 | 0 | 0 | 0 | 27257.64
2022121105 | 1 | 0.43315 | 34652 | 0.07703 | 2773.08 | 0 | 0 | 1 | 5000 | 2773.08 | 0 | 0 | 0 | 0 | 0 | 26878.92 | 0 | 0 | 0 | 0 | 0 | 26878.92
2022121106 | 1 | 0.43481 | 34784.8 | 0.07175 | 2583 | 0 | 0 | 1 | 5000 | 2583 | 0 | 0 | 0 | 0 | 0 | 27201.8 | 0 | 0 | 0 | 0 | 0 | 27201.8
2022121107 | 1 | 0.44057 | 35245.6 | 0.06328 | 2278.08 | 0 | 0 | 1 | 5000 | 2278.08 | 0 | 0 | 0 | 0 | 0 | 27967.52 | 0 | 0 | 0 | 0 | 0 | 27967.52
2022121108 | 1 | 0.45444 | 36355.2 | 0.06016 | 2165.76 | 0.00153 | 18.36 | 1 | 5000 | 2165.76 | 18.36 | 0 | 0 | 0 | 0 | 29171.08 | 0 | 0 | 0 | 0 | 0 | 29171.08
2022121109 | 1 | 0.47296 | 37836.8 | 0.06557 | 2360.52 | 0.02602 | 312.24 | 1 | 5000 | 2360.52 | 312.24 | 0 | 0 | 0 | 0 | 30164.04 | 0 | 0 | 0 | 0 | 0 | 30164.04
2022121110 | 1 | 0.49397 | 39517.6 | 0.05565 | 2003.4 | 0.07778 | 933.36 | 1 | 5000 | 2003.4 | 933.36 | 0 | 0 | 0 | 0 | 31580.84 | 0 | 0 | 0 | 0 | 0 | 31580.84
2022121111 | 1 | 0.50924 | 40739.2 | 0.04684 | 1686.24 | 0.16738 | 2008.56 | 1 | 5000 | 1686.24 | 2008.56 | 0 | 0 | 0 | 0 | 32044.4 | 0 | 0 | 0 | 0 | 0 | 32044.4
2022121112 | 1 | 0.52405 | 41924 | 0.05669 | 2040.84 | 0.2378 | 2853.6 | 1 | 5000 | 2040.84 | 2853.6 | 0 | 0 | 0 | 0 | 32029.56 | 0 | 0 | 0 | 0 | 0 | 32029.56
2022121113 | 1 | 0.52994 | 42395.2 | 0.06137 | 2209.32 | 0.28918 | 3470.16 | 1 | 5000 | 2209.32 | 3470.16 | 0 | 0 | 0 | 0 | 31715.72 | 0 | 0 | 0 | 0 | 0 | 31715.72
2022121114 | 1 | 0.53236 | 42588.8 | 0.07339 | 2642.04 | 0.30228 | 3627.36 | 1 | 5000 | 2642.04 | 3627.36 | 0 | 0 | 0 | 0 | 31319.4 | 0 | 0 | 0 | 0 | 0 | 31319.4
2022121115 | 1 | 0.53139 | 42511.2 | 0.09163 | 3298.68 | 0.30974 | 3716.88 | 1 | 5000 | 3298.68 | 3716.88 | 0 | 0 | 0 | 0 | 30495.64 | 0 | 0 | 0 | 0 | 0 | 30495.64
2022121116 | 1 | 0.53125 | 42500 | 0.11655 | 4195.8 | 0.28693 | 3443.16 | 1 | 5000 | 4195.8 | 3443.16 | 0 | 0 | 0 | 0 | 29861.04 | 0 | 0 | 0 | 0 | 0 | 29861.04
2022121117 | 1 | 0.53589 | 42871.2 | 0.13457 | 4844.52 | 0.16412 | 1969.44 | 1 | 5000 | 4844.52 | 1969.44 | 0 | 0 | 0 | 0 | 31057.24 | 0 | 0 | 0 | 0 | 0 | 31057.24
2022121118 | 1 | 0.54851 | 43880.8 | 0.13679 | 4924.44 | 0.02025 | 243 | 1 | 5000 | 4924.44 | 243 | 0 | 0 | 0 | 0 | 33713.36 | 0 | 0 | 0 | 0 | 0 | 33713.36
2022121119 | 1 | 0.55974 | 44779.2 | 0.14921 | 5371.56 | 0 | 0 | 1 | 5000 | 5371.56 | 0 | 0 | 0 | 0 | 0 | 34407.64 | 0 | 0 | 0 | 0 | 0 | 34407.64
2022121120 | 1 | 0.55571 | 44456.8 | 0.17293 | 6225.48 | 0 | 0 | 1 | 5000 | 6225.48 | 0 | 0 | 0 | 0 | 0 | 33231.32 | 0 | 0 | 0 | 0 | 0 | 33231.32
2022121121 | 1 | 0.54938 | 43950.4 | 0.2096 | 7545.6 | 0 | 0 | 1 | 5000 | 7545.6 | 0 | 0 | 0 | 0 | 0 | 31404.8 | 0 | 0 | 0 | 0 | 0 | 31404.8
2022121122 | 1 | 0.53678 | 42942.4 | 0.24621 | 8863.56 | 0 | 0 | 1 | 5000 | 8863.56 | 0 | 0 | 0 | 0 | 0 | 29078.84 | 0 | 0 | 0 | 0 | 0 | 29078.84
2022121123 | 1 | 0.51161 | 40928.8 | 0.26896 | 9682.56 | 0 | 0 | 1 | 5000 | 9682.56 | 0 | 0 | 0 | 0 | 0 | 26246.24 | 0 | 0 | 0 | 0 | 0 | 26246.24
2022121124 | 1 | 0.48171 | 38536.8 | 0.30872 | 11113.92 | 0 | 0 | 1 | 5000 | 11113.92 | 0 | 0 | 0 | 0 | 0 | 22422.88 | 0 | 0 | 0 | 0 | 0 | 22422.88
2022121201 | 2 | 0.45844 | 36675.2 | 0.33612 | 12100.32 | 0 | 0 | 1 | 5000 | 12100.32 | 0 | 0 | 0 | 0 | 0 | 19574.88 | 0 | 0 | 0 | 0 | 0 | 19574.88
2022121202 | 2 | 0.44308 | 35446.4 | 0.34531 | 12431.16 | 0 | 0 | 1 | 5000 | 12431.16 | 0 | 0 | 0 | 0 | 0 | 18015.24 | 0 | 0 | 0 | 0 | 0 | 18015.24
2022121203 | 2 | 0.43578 | 34862.4 | 0.35303 | 12709.08 | 0 | 0 | 1 | 5000 | 12709.08 | 0 | 0 | 0 | 0 | 0 | 17153.32 | 0 | 0 | 0 | 0 | 0 | 17153.32
2022121204 | 2 | 0.43489 | 34791.2 | 0.35897 | 12922.92 | 0 | 0 | 1 | 5000 | 12922.92 | 0 | 0 | 0 | 0 | 0 | 16868.28 | 0 | 0 | 0 | 0 | 0 | 16868.28
2022121205 | 2 | 0.44464 | 35571.2 | 0.37716 | 13577.76 | 0 | 0 | 1 | 5000 | 13577.76 | 0 | 0 | 0 | 0 | 0 | 16993.44 | 0 | 0 | 0 | 0 | 0 | 16993.44
2022121206 | 2 | 0.46926 | 37540.8 | 0.40574 | 14606.64 | 0 | 0 | 1 | 5000 | 14606.64 | 0 | 0 | 0 | 0 | 0 | 17934.16 | 0 | 0 | 0 | 0 | 0 | 17934.16
2022121207 | 2 | 0.50877 | 40701.6 | 0.43357 | 15608.52 | 0 | 0 | 1 | 5000 | 15608.52 | 0 | 0 | 0 | 0 | 0 | 20093.08 | 0 | 0 | 0 | 0 | 0 | 20093.08
2022121208 | 2 | 0.52965 | 42372 | 0.45368 | 16332.48 | 0.00244 | 29.28 | 1 | 5000 | 16332.48 | 29.28 | 0 | 0 | 0 | 0 | 21010.24 | 0 | 0 | 0 | 0 | 0 | 21010.24
2022121209 | 2 | 0.53801 | 43040.8 | 0.45612 | 16420.32 | 0.06399 | 767.88 | 1 | 5000 | 16420.32 | 767.88 | 0 | 0 | 0 | 0 | 20852.6 | 0 | 0 | 0 | 0 | 0 | 20852.6
2022121210 | 2 | 0.55155 | 44124 | 0.46573 | 16766.28 | 0.17029 | 2043.48 | 1 | 5000 | 16766.28 | 2043.48 | 0 | 0 | 0 | 0 | 20314.24 | 0 | 0 | 0 | 0 | 0 | 20314.24
2022121211 | 2 | 0.55513 | 44410.4 | 0.49527 | 17829.72 | 0.20427 | 2451.24 | 1 | 5000 | 17829.72 | 2451.24 | 0 | 0 | 0 | 0 | 19129.44 | 0 | 0 | 0 | 0 | 0 | 19129.44
2022121212 | 2 | 0.56255 | 45004 | 0.53831 | 19379.16 | 0.19047 | 2285.64 | 1 | 5000 | 19379.16 | 2285.64 | 0 | 0 | 0 | 0 | 18339.2 | 0 | 0 | 0 | 0 | 0 | 18339.2
2022121213 | 2 | 0.56232 | 44985.6 | 0.5553 | 19990.8 | 0.14888 | 1786.56 | 1 | 5000 | 19990.8 | 1786.56 | 0 | 0 | 0 | 0 | 18208.24 | 0 | 0 | 0 | 0 | 0 | 18208.24
2022121214 | 2 | 0.56287 | 45029.6 | 0.5571 | 20055.6 | 0.12661 | 1519.32 | 1 | 5000 | 20055.6 | 1519.32 | 0 | 0 | 0 | 0 | 18454.68 | 0 | 0 | 0 | 0 | 0 | 18454.68
2022121215 | 2 | 0.56085 | 44868 | 0.58104 | 20917.44 | 0.1087 | 1304.4 | 1 | 5000 | 20917.44 | 1304.4 | 0 | 0 | 0 | 0 | 17646.16 | 0 | 0 | 0 | 0 | 0 | 17646.16
2022121216 | 2 | 0.56156 | 44924.8 | 0.60089 | 21632.04 | 0.08348 | 1001.76 | 1 | 5000 | 21632.04 | 1001.76 | 0 | 0 | 0 | 0 | 17291 | 0 | 0 | 0 | 0 | 0 | 17291
2022121217 | 2 | 0.56832 | 45465.6 | 0.60911 | 21927.96 | 0.04673 | 560.76 | 1 | 5000 | 21927.96 | 560.76 | 0 | 0 | 0 | 0 | 17976.88 | 0 | 0 | 0 | 0 | 0 | 17976.88
2022121218 | 2 | 0.58365 | 46692 | 0.61545 | 22156.2 | 0.01052 | 126.24 | 1 | 5000 | 22156.2 | 126.24 | 0 | 0 | 0 | 0 | 19409.56 | 0 | 0 | 0 | 0 | 0 | 19409.56
2022121219 | 2 | 0.59425 | 47540 | 0.63455 | 22843.8 | 0 | 0 | 1 | 5000 | 22843.8 | 0 | 0 | 0 | 0 | 0 | 19696.2 | 0 | 0 | 0 | 0 | 0 | 19696.2
2022121220 | 2 | 0.58562 | 46849.6 | 0.65847 | 23704.92 | 0 | 0 | 1 | 5000 | 23704.92 | 0 | 0 | 0 | 0 | 0 | 18144.68 | 0 | 0 | 0 | 0 | 0 | 18144.68
2022121221 | 2 | 0.57876 | 46300.8 | 0.6662 | 23983.2 | 0 | 0 | 1 | 5000 | 23983.2 | 0 | 0 | 0 | 0 | 0 | 17317.6 | 0 | 0 | 0 | 0 | 0 | 17317.6
2022121222 | 2 | 0.56306 | 45044.8 | 0.66618 | 23982.48 | 0 | 0 | 1 | 5000 | 23982.48 | 0 | 0 | 0 | 0 | 0 | 16062.32 | 0 | 0 | 0 | 0 | 0 | 16062.32
2022121223 | 2 | 0.53501 | 42800.8 | 0.65681 | 23645.16 | 0 | 0 | 1 | 5000 | 23645.16 | 0 | 0 | 0 | 0 | 0 | 14155.64 | 0 | 0 | 0 | 0 | 0 | 14155.64
2022121224 | 2 | 0.50582 | 40465.6 | 0.65083 | 23429.88 | 0 | 0 | 1 | 5000 | 23429.88 | 0 | 0 | 0 | 0 | 0 | 12035.72 | 0 | 0 | 0 | 0 | 0 | 12035.72
2022121301 | 3 | 0.48163 | 38530.4 | 0.63345 | 22804.2 | 0 | 0 | 1 | 5000 | 22804.2 | 0 | 0 | 0 | 0 | 0 | 10726.2 | 0 | 0 | 0 | 0 | 0 | 10726.2
2022121302 | 3 | 0.46573 | 37258.4 | 0.61456 | 22124.16 | 0 | 0 | 1 | 5000 | 22124.16 | 0 | 0 | 0 | 0 | 0 | 10134.24 | 0 | 0 | 0 | 0 | 0 | 10134.24
2022121303 | 3 | 0.45626 | 36500.8 | 0.60516 | 21785.76 | 0 | 0 | 1 | 5000 | 21785.76 | 0 | 0 | 0 | 0 | 0 | 9715.04 | 0 | 0 | 0 | 0 | 0 | 9715.04
2022121304 | 3 | 0.45294 | 36235.2 | 0.58155 | 20935.8 | 0 | 0 | 1 | 5000 | 20935.8 | 0 | 0 | 0 | 0 | 0 | 10299.4 | 0 | 0 | 0 | 0 | 0 | 10299.4
2022121305 | 3 | 0.45975 | 36780 | 0.54928 | 19774.08 | 0 | 0 | 1 | 5000 | 19774.08 | 0 | 0 | 0 | 0 | 0 | 12005.92 | 0 | 0 | 0 | 0 | 0 | 12005.92
2022121306 | 3 | 0.4798 | 38384 | 0.52738 | 18985.68 | 0 | 0 | 1 | 5000 | 18985.68 | 0 | 0 | 0 | 0 | 0 | 14398.32 | 0 | 0 | 0 | 0 | 0 | 14398.32
2022121307 | 3 | 0.51499 | 41199.2 | 0.50551 | 18198.36 | 0 | 0 | 1 | 5000 | 18198.36 | 0 | 0 | 0 | 0 | 0 | 18000.84 | 0 | 0 | 0 | 0 | 0 | 18000.84
2022121308 | 3 | 0.53502 | 42801.6 | 0.51683 | 18605.88 | 0.00645 | 77.4 | 1 | 5000 | 18605.88 | 77.4 | 0 | 0 | 0 | 0 | 19118.32 | 0 | 0 | 0 | 0 | 0 | 19118.32
2022121309 | 3 | 0.54592 | 43673.6 | 0.4786 | 17229.6 | 0.16099 | 1931.88 | 1 | 5000 | 17229.6 | 1931.88 | 0 | 0 | 0 | 0 | 19512.12 | 0 | 0 | 0 | 0 | 0 | 19512.12
2022121310 | 3 | 0.55623 | 44498.4 | 0.41266 | 14855.76 | 0.38024 | 4562.88 | 1 | 5000 | 14855.76 | 4562.88 | 0 | 0 | 0 | 0 | 20079.76 | 0 | 0 | 0 | 0 | 0 | 20079.76
2022121311 | 3 | 0.56553 | 45242.4 | 0.42409 | 15267.24 | 0.42192 | 5063.04 | 1 | 5000 | 15267.24 | 5063.04 | 0 | 0 | 0 | 0 | 19912.12 | 0 | 0 | 0 | 0 | 0 | 19912.12
2022121312 | 3 | 0.57355 | 45884 | 0.48463 | 17446.68 | 0.35305 | 4236.6 | 1 | 5000 | 17446.68 | 4236.6 | 0 | 0 | 0 | 0 | 19200.72 | 0 | 0 | 0 | 0 | 0 | 19200.72
2022121313 | 3 | 0.57809 | 46247.2 | 0.54285 | 19542.6 | 0.24222 | 2906.64 | 1 | 5000 | 19542.6 | 2906.64 | 0 | 0 | 0 | 0 | 18797.96 | 0 | 0 | 0 | 0 | 0 | 18797.96
2022121314 | 3 | 0.58521 | 46816.8 | 0.54058 | 19460.88 | 0.18692 | 2243.04 | 1 | 5000 | 19460.88 | 2243.04 | 0 | 0 | 0 | 0 | 20112.88 | 0 | 0 | 0 | 0 | 0 | 20112.88
2022121315 | 3 | 0.58414 | 46731.2 | 0.52774 | 18998.64 | 0.17828 | 2139.36 | 1 | 5000 | 18998.64 | 2139.36 | 0 | 0 | 0 | 0 | 20593.2 | 0 | 0 | 0 | 0 | 0 | 20593.2
2022121316 | 3 | 0.58228 | 46582.4 | 0.52937 | 19057.32 | 0.14008 | 1680.96 | 1 | 5000 | 19057.32 | 1680.96 | 0 | 0 | 0 | 0 | 20844.12 | 0 | 0 | 0 | 0 | 0 | 20844.12
2022121317 | 3 | 0.58417 | 46733.6 | 0.53953 | 19423.08 | 0.07522 | 902.64 | 1 | 5000 | 19423.08 | 902.64 | 0 | 0 | 0 | 0 | 21407.88 | 0 | 0 | 0 | 0 | 0 | 21407.88
2022121318 | 3 | 0.59156 | 47324.8 | 0.48914 | 17609.04 | 0.02369 | 284.28 | 1 | 5000 | 17609.04 | 284.28 | 0 | 0 | 0 | 0 | 24431.48 | 0 | 0 | 0 | 0 | 0 | 24431.48
2022121319 | 3 | 0.59982 | 47985.6 | 0.43226 | 15561.36 | 0 | 0 | 1 | 5000 | 15561.36 | 0 | 0 | 0 | 0 | 0 | 27424.24 | 0 | 0 | 0 | 0 | 0 | 27424.24
2022121320 | 3 | 0.58941 | 47152.8 | 0.39451 | 14202.36 | 0 | 0 | 1 | 5000 | 14202.36 | 0 | 0 | 0 | 0 | 0 | 27950.44 | 0 | 0 | 0 | 0 | 0 | 27950.44
2022121321 | 3 | 0.57609 | 46087.2 | 0.38104 | 13717.44 | 0 | 0 | 1 | 5000 | 13717.44 | 0 | 0 | 0 | 0 | 0 | 27369.76 | 0 | 0 | 0 | 0 | 0 | 27369.76
2022121322 | 3 | 0.5636 | 45088 | 0.39728 | 14302.08 | 0 | 0 | 1 | 5000 | 14302.08 | 0 | 0 | 0 | 0 | 0 | 25785.92 | 0 | 0 | 0 | 0 | 0 | 25785.92
2022121323 | 3 | 0.53353 | 42682.4 | 0.39441 | 14198.76 | 0 | 0 | 1 | 5000 | 14198.76 | 0 | 0 | 0 | 0 | 0 | 23483.64 | 0 | 0 | 0 | 0 | 0 | 23483.64
2022121324 | 3 | 0.50466 | 40372.8 | 0.39534 | 14232.24 | 0 | 0 | 1 | 5000 | 14232.24 | 0 | 0 | 0 | 0 | 0 | 21140.56 | 0 | 0 | 0 | 0 | 0 | 21140.56
2022121401 | 4 | 0.47872 | 38297.6 | 0.39635 | 14268.6 | 0 | 0 | 1 | 5000 | 14268.6 | 0 | 0 | 0 | 0 | 0 | 19029 | 0 | 0 | 0 | 0 | 0 | 19029
2022121402 | 4 | 0.46176 | 36940.8 | 0.37006 | 13322.16 | 0 | 0 | 1 | 5000 | 13322.16 | 0 | 0 | 0 | 0 | 0 | 18618.64 | 0 | 0 | 0 | 0 | 0 | 18618.64
2022121403 | 4 | 0.45124 | 36099.2 | 0.35283 | 12701.88 | 0 | 0 | 1 | 5000 | 12701.88 | 0 | 0 | 0 | 0 | 0 | 18397.32 | 0 | 0 | 0 | 0 | 0 | 18397.32
2022121404 | 4 | 0.44684 | 35747.2 | 0.3672 | 13219.2 | 0 | 0 | 1 | 5000 | 13219.2 | 0 | 0 | 0 | 0 | 0 | 17528 | 0 | 0 | 0 | 0 | 0 | 17528
2022121405 | 4 | 0.45352 | 36281.6 | 0.35511 | 12783.96 | 0 | 0 | 1 | 5000 | 12783.96 | 0 | 0 | 0 | 0 | 0 | 18497.64 | 0 | 0 | 0 | 0 | 0 | 18497.64
2022121406 | 4 | 0.4733 | 37864 | 0.33637 | 12109.32 | 0 | 0 | 1 | 5000 | 12109.32 | 0 | 0 | 0 | 0 | 0 | 20754.68 | 0 | 0 | 0 | 0 | 0 | 20754.68
2022121407 | 4 | 0.51233 | 40986.4 | 0.36633 | 13187.88 | 0 | 0 | 1 | 5000 | 13187.88 | 0 | 0 | 0 | 0 | 0 | 22798.52 | 0 | 0 | 0 | 0 | 0 | 22798.52
2022121408 | 4 | 0.53268 | 42614.4 | 0.40787 | 14683.32 | 0.00314 | 37.68 | 1 | 5000 | 14683.32 | 37.68 | 0 | 0 | 0 | 0 | 22893.4 | 0 | 0 | 0 | 0 | 0 | 22893.4
2022121409 | 4 | 0.53432 | 42745.6 | 0.40074 | 14426.64 | 0.1705 | 2046 | 1 | 5000 | 14426.64 | 2046 | 0 | 0 | 0 | 0 | 21272.96 | 0 | 0 | 0 | 0 | 0 | 21272.96
2022121410 | 4 | 0.53576 | 42860.8 | 0.3863 | 13906.8 | 0.33227 | 3987.24 | 1 | 5000 | 13906.8 | 3987.24 | 0 | 0 | 0 | 0 | 19966.76 | 0 | 0 | 0 | 0 | 0 | 19966.76
2022121411 | 4 | 0.53011 | 42408.8 | 0.44358 | 15968.88 | 0.26477 | 3177.24 | 1 | 5000 | 15968.88 | 3177.24 | 0 | 0 | 0 | 0 | 18262.68 | 0 | 0 | 0 | 0 | 0 | 18262.68
2022121412 | 4 | 0.52683 | 42146.4 | 0.45156 | 16256.16 | 0.25409 | 3049.08 | 1 | 5000 | 16256.16 | 3049.08 | 0 | 0 | 0 | 0 | 17841.16 | 0 | 0 | 0 | 0 | 0 | 17841.16
2022121413 | 4 | 0.52307 | 41845.6 | 0.44108 | 15878.88 | 0.28023 | 3362.76 | 1 | 5000 | 15878.88 | 3362.76 | 0 | 0 | 0 | 0 | 17603.96 | 0 | 0 | 0 | 0 | 0 | 17603.96
2022121414 | 4 | 0.52226 | 41780.8 | 0.41361 | 14889.96 | 0.34864 | 4183.68 | 1 | 5000 | 14889.96 | 4183.68 | 0 | 0 | 0 | 0 | 17707.16 | 0 | 0 | 0 | 0 | 0 | 17707.16
2022121415 | 4 | 0.52065 | 41652 | 0.37004 | 13321.44 | 0.42408 | 5088.96 | 1 | 5000 | 13321.44 | 5088.96 | 0 | 0 | 0 | 0 | 18241.6 | 0 | 0 | 0 | 0 | 0 | 18241.6
2022121416 | 4 | 0.52362 | 41889.6 | 0.30463 | 10966.68 | 0.51576 | 6189.12 | 1 | 5000 | 10966.68 | 6189.12 | 0 | 0 | 0 | 0 | 19733.8 | 0 | 0 | 0 | 0 | 0 | 19733.8
2022121417 | 4 | 0.53014 | 42411.2 | 0.23634 | 8508.24 | 0.35295 | 4235.4 | 1 | 5000 | 8508.24 | 4235.4 | 0 | 0 | 0 | 0 | 24667.56 | 0 | 0 | 0 | 0 | 0 | 24667.56
2022121418 | 4 | 0.55261 | 44208.8 | 0.14303 | 5149.08 | 0.03937 | 472.44 | 1 | 5000 | 5149.08 | 472.44 | 0 | 0 | 0 | 0 | 33587.28 | 0 | 0 | 0 | 0 | 0 | 33587.28
2022121419 | 4 | 0.5725 | 45800 | 0.12339 | 4442.04 | 0 | 0 | 1 | 5000 | 4442.04 | 0 | 0 | 0 | 0 | 0 | 36357.96 | 0 | 0 | 0 | 0 | 0 | 36357.96
2022121420 | 4 | 0.57139 | 45711.2 | 0.13189 | 4748.04 | 0 | 0 | 1 | 5000 | 4748.04 | 0 | 0 | 0 | 0 | 0 | 35963.16 | 0 | 0 | 0 | 0 | 0 | 35963.16
2022121421 | 4 | 0.57032 | 45625.6 | 0.13726 | 4941.36 | 0 | 0 | 1 | 5000 | 4941.36 | 0 | 0 | 0 | 0 | 0 | 35684.24 | 0 | 0 | 0 | 0 | 0 | 35684.24
2022121422 | 4 | 0.55919 | 44735.2 | 0.16342 | 5883.12 | 0 | 0 | 1 | 5000 | 5883.12 | 0 | 0 | 0 | 0 | 0 | 33852.08 | 0 | 0 | 0 | 0 | 0 | 33852.08
2022121423 | 4 | 0.53982 | 43185.6 | 0.18704 | 6733.44 | 0 | 0 | 1 | 5000 | 6733.44 | 0 | 0 | 0 | 0 | 0 | 31452.16 | 0 | 0 | 0 | 0 | 0 | 31452.16
2022121424 | 4 | 0.51647 | 41317.6 | 0.19182 | 6905.52 | 0 | 0 | 1 | 5000 | 6905.52 | 0 | 0 | 0 | 0 | 0 | 29412.08 | 0 | 0 | 0 | 0 | 0 | 29412.08
2022121501 | 5 | 0.4999 | 39992 | 0.18584 | 6690.24 | 0 | 0 | 1 | 5000 | 6690.24 | 0 | 0 | 0 | 0 | 0 | 28301.76 | 0 | 0 | 0 | 0 | 0 | 28301.76
2022121502 | 5 | 0.49241 | 39392.8 | 0.17975 | 6471 | 0 | 0 | 1 | 5000 | 6471 | 0 | 0 | 0 | 0 | 0 | 27921.8 | 0 | 0 | 0 | 0 | 0 | 27921.8
2022121503 | 5 | 0.49004 | 39203.2 | 0.17657 | 6356.52 | 0 | 0 | 1 | 5000 | 6356.52 | 0 | 0 | 0 | 0 | 0 | 27846.68 | 0 | 0 | 0 | 0 | 0 | 27846.68
2022121504 | 5 | 0.496 | 39680 | 0.16605 | 5977.8 | 0 | 0 | 1 | 5000 | 5977.8 | 0 | 0 | 0 | 0 | 0 | 28702.2 | 0 | 0 | 0 | 0 | 0 | 28702.2
2022121505 | 5 | 0.51462 | 41169.6 | 0.16013 | 5764.68 | 0 | 0 | 1 | 5000 | 5764.68 | 0 | 0 | 0 | 0 | 0 | 30404.92 | 0 | 0 | 0 | 0 | 0 | 30404.92
2022121506 | 5 | 0.54994 | 43995.2 | 0.1572 | 5659.2 | 0 | 0 | 1 | 5000 | 5659.2 | 0 | 0 | 0 | 0 | 0 | 33336 | 0 | 0 | 0 | 0 | 0 | 33336
2022121507 | 5 | 0.60495 | 48396 | 0.15133 | 5447.88 | 0 | 0 | 1 | 5000 | 5447.88 | 0 | 0 | 0 | 0 | 0 | 37948.12 | 0 | 0 | 0 | 0 | 0 | 37948.12
2022121508 | 5 | 0.62996 | 50396.8 | 0.14374 | 5174.64 | 0.01952 | 234.24 | 1 | 5000 | 5174.64 | 234.24 | 0 | 0 | 0 | 0 | 39987.92 | 0 | 0 | 0 | 0 | 0 | 39987.92
2022121509 | 5 | 0.61899 | 49519.2 | 0.13218 | 4758.48 | 0.3172 | 3806.4 | 1 | 5000 | 4758.48 | 3806.4 | 0 | 0 | 0 | 0 | 35954.32 | 0 | 0 | 0 | 0 | 0 | 35954.32
2022121510 | 5 | 0.59571 | 47656.8 | 0.08034 | 2892.24 | 0.61581 | 7389.72 | 1 | 5000 | 2892.24 | 7389.72 | 0 | 0 | 0 | 0 | 32374.84 | 0 | 0 | 0 | 0 | 0 | 32374.84
2022121511 | 5 | 0.56961 | 45568.8 | 0.10111 | 3639.96 | 0.63439 | 7612.68 | 1 | 5000 | 3639.96 | 7612.68 | 0 | 0 | 0 | 0 | 29316.16 | 0 | 0 | 0 | 0 | 0 | 29316.16
2022121512 | 5 | 0.5469 | 43752 | 0.12214 | 4397.04 | 0.60984 | 7318.08 | 1 | 5000 | 4397.04 | 7318.08 | 0 | 0 | 0 | 0 | 27036.88 | 0 | 0 | 0 | 0 | 0 | 27036.88
2022121513 | 5 | 0.53167 | 42533.6 | 0.10201 | 3672.36 | 0.59541 | 7144.92 | 1 | 5000 | 3672.36 | 7144.92 | 0 | 0 | 0 | 0 | 26716.32 | 0 | 0 | 0 | 0 | 0 | 26716.32
2022121514 | 5 | 0.52734 | 42187.2 | 0.08258 | 2972.88 | 0.60633 | 7275.96 | 1 | 5000 | 2972.88 | 7275.96 | 0 | 0 | 0 | 0 | 26938.36 | 0 | 0 | 0 | 0 | 0 | 26938.36
2022121515 | 5 | 0.52307 | 41845.6 | 0.07341 | 2642.76 | 0.63201 | 7584.12 | 1 | 5000 | 2642.76 | 7584.12 | 0 | 0 | 0 | 0 | 26618.72 | 0 | 0 | 0 | 0 | 0 | 26618.72
2022121516 | 5 | 0.52269 | 41815.2 | 0.07752 | 2790.72 | 0.60811 | 7297.32 | 1 | 5000 | 2790.72 | 7297.32 | 0 | 0 | 0 | 0 | 26727.16 | 0 | 0 | 0 | 0 | 0 | 26727.16
2022121517 | 5 | 0.53095 | 42476 | 0.07997 | 2878.92 | 0.3689 | 4426.8 | 1 | 5000 | 2878.92 | 4426.8 | 0 | 0 | 0 | 0 | 30170.28 | 0 | 0 | 0 | 0 | 0 | 30170.28
2022121518 | 5 | 0.55252 | 44201.6 | 0.07565 | 2723.4 | 0.03768 | 452.16 | 1 | 5000 | 2723.4 | 452.16 | 0 | 0 | 0 | 0 | 36026.04 | 0 | 0 | 0 | 0 | 0 | 36026.04
2022121519 | 5 | 0.57613 | 46090.4 | 0.11671 | 4201.56 | 0 | 0 | 1 | 5000 | 4201.56 | 0 | 0 | 0 | 0 | 0 | 36888.84 | 0 | 0 | 0 | 0 | 0 | 36888.84
2022121520 | 5 | 0.58011 | 46408.8 | 0.17252 | 6210.72 | 0 | 0 | 1 | 5000 | 6210.72 | 0 | 0 | 0 | 0 | 0 | 35198.08 | 0 | 0 | 0 | 0 | 0 | 35198.08
2022121521 | 5 | 0.58151 | 46520.8 | 0.20622 | 7423.92 | 0 | 0 | 1 | 5000 | 7423.92 | 0 | 0 | 0 | 0 | 0 | 34096.88 | 0 | 0 | 0 | 0 | 0 | 34096.88
2022121522 | 5 | 0.57715 | 46172 | 0.2312 | 8323.2 | 0 | 0 | 1 | 5000 | 8323.2 | 0 | 0 | 0 | 0 | 0 | 32848.8 | 0 | 0 | 0 | 0 | 0 | 32848.8
2022121523 | 5 | 0.55881 | 44704.8 | 0.25223 | 9080.28 | 0 | 0 | 1 | 5000 | 9080.28 | 0 | 0 | 0 | 0 | 0 | 30624.52 | 0 | 0 | 0 | 0 | 0 | 30624.52
2022121524 | 5 | 0.53914 | 43131.2 | 0.26583 | 9569.88 | 0 | 0 | 1 | 5000 | 9569.88 | 0 | 0 | 0 | 0 | 0 | 28561.32 | 0 | 0 | 0 | 0 | 0 | 28561.32
2022121601 | 6 | 0.52484 | 41987.2 | 0.25993 | 9357.48 | 0 | 0 | 1 | 5000 | 9357.48 | 0 | 0 | 0 | 0 | 0 | 27629.72 | 0 | 0 | 0 | 0 | 0 | 27629.72
2022121602 | 6 | 0.51933 | 41546.4 | 0.26015 | 9365.4 | 0 | 0 | 1 | 5000 | 9365.4 | 0 | 0 | 0 | 0 | 0 | 27181 | 0 | 0 | 0 | 0 | 0 | 27181
2022121603 | 6 | 0.51577 | 41261.6 | 0.25722 | 9259.92 | 0 | 0 | 1 | 5000 | 9259.92 | 0 | 0 | 0 | 0 | 0 | 27001.68 | 0 | 0 | 0 | 0 | 0 | 27001.68
2022121604 | 6 | 0.51696 | 41356.8 | 0.26602 | 9576.72 | 0 | 0 | 1 | 5000 | 9576.72 | 0 | 0 | 0 | 0 | 0 | 26780.08 | 0 | 0 | 0 | 0 | 0 | 26780.08
2022121605 | 6 | 0.53007 | 42405.6 | 0.28973 | 10430.28 | 0 | 0 | 1 | 5000 | 10430.28 | 0 | 0 | 0 | 0 | 0 | 26975.32 | 0 | 0 | 0 | 0 | 0 | 26975.32
2022121606 | 6 | 0.55949 | 44759.2 | 0.27492 | 9897.12 | 0 | 0 | 1 | 5000 | 9897.12 | 0 | 0 | 0 | 0 | 0 | 29862.08 | 0 | 0 | 0 | 0 | 0 | 29862.08
2022121607 | 6 | 0.60656 | 48524.8 | 0.27607 | 9938.52 | 0 | 0 | 1 | 5000 | 9938.52 | 0 | 0 | 0 | 0 | 0 | 33586.28 | 0 | 0 | 0 | 0 | 0 | 33586.28
2022121608 | 6 | 0.62431 | 49944.8 | 0.30037 | 10813.32 | 0.01073 | 128.76 | 1 | 5000 | 10813.32 | 128.76 | 0 | 0 | 0 | 0 | 34002.72 | 0 | 0 | 0 | 0 | 0 | 34002.72
2022121609 | 6 | 0.61622 | 49297.6 | 0.2813 | 10126.8 | 0.18335 | 2200.2 | 1 | 5000 | 10126.8 | 2200.2 | 0 | 0 | 0 | 0 | 31970.6 | 0 | 0 | 0 | 0 | 0 | 31970.6
2022121610 | 6 | 0.6061 | 48488 | 0.23967 | 8628.12 | 0.42564 | 5107.68 | 1 | 5000 | 8628.12 | 5107.68 | 0 | 0 | 0 | 0 | 29752.2 | 0 | 0 | 0 | 0 | 0 | 29752.2
2022121611 | 6 | 0.60157 | 48125.6 | 0.26586 | 9570.96 | 0.49585 | 5950.2 | 1 | 5000 | 9570.96 | 5950.2 | 0 | 0 | 0 | 0 | 27604.44 | 0 | 0 | 0 | 0 | 0 | 27604.44
2022121612 | 6 | 0.5908 | 47264 | 0.23068 | 8304.48 | 0.45045 | 5405.4 | 1 | 5000 | 8304.48 | 5405.4 | 0 | 0 | 0 | 0 | 28554.12 | 0 | 0 | 0 | 0 | 0 | 28554.12
2022121613 | 6 | 0.57837 | 46269.6 | 0.17568 | 6324.48 | 0.40927 | 4911.24 | 1 | 5000 | 6324.48 | 4911.24 | 0 | 0 | 0 | 0 | 30033.88 | 0 | 0 | 0 | 0 | 0 | 30033.88
2022121614 | 6 | 0.57115 | 45692 | 0.13182 | 4745.52 | 0.38405 | 4608.6 | 1 | 5000 | 4745.52 | 4608.6 | 0 | 0 | 0 | 0 | 31337.88 | 0 | 0 | 0 | 0 | 0 | 31337.88
2022121615 | 6 | 0.56623 | 45298.4 | 0.1046 | 3765.6 | 0.36256 | 4350.72 | 1 | 5000 | 3765.6 | 4350.72 | 0 | 0 | 0 | 0 | 32182.08 | 0 | 0 | 0 | 0 | 0 | 32182.08
2022121616 | 6 | 0.56869 | 45495.2 | 0.10247 | 3688.92 | 0.29358 | 3522.96 | 1 | 5000 | 3688.92 | 3522.96 | 0 | 0 | 0 | 0 | 33283.32 | 0 | 0 | 0 | 0 | 0 | 33283.32
2022121617 | 6 | 0.57487 | 45989.6 | 0.09966 | 3587.76 | 0.1512 | 1814.4 | 1 | 5000 | 3587.76 | 1814.4 | 0 | 0 | 0 | 0 | 35587.44 | 0 | 0 | 0 | 0 | 0 | 35587.44
2022121618 | 6 | 0.59638 | 47710.4 | 0.08444 | 3039.84 | 0.01636 | 196.32 | 1 | 5000 | 3039.84 | 196.32 | 0 | 0 | 0 | 0 | 39474.24 | 0 | 0 | 0 | 0 | 0 | 39474.24
2022121619 | 6 | 0.61153 | 48922.4 | 0.10081 | 3629.16 | 0 | 0 | 1 | 5000 | 3629.16 | 0 | 0 | 0 | 0 | 0 | 40293.24 | 0 | 0 | 0 | 0 | 0 | 40293.24
2022121620 | 6 | 0.60922 | 48737.6 | 0.13771 | 4957.56 | 0 | 0 | 1 | 5000 | 4957.56 | 0 | 0 | 0 | 0 | 0 | 38780.04 | 0 | 0 | 0 | 0 | 0 | 38780.04
2022121621 | 6 | 0.60375 | 48300 | 0.17516 | 6305.76 | 0 | 0 | 1 | 5000 | 6305.76 | 0 | 0 | 0 | 0 | 0 | 36994.24 | 0 | 0 | 0 | 0 | 0 | 36994.24
2022121622 | 6 | 0.5942 | 47536 | 0.19983 | 7193.88 | 0 | 0 | 1 | 5000 | 7193.88 | 0 | 0 | 0 | 0 | 0 | 35342.12 | 0 | 0 | 0 | 0 | 0 | 35342.12
2022121623 | 6 | 0.57975 | 46380 | 0.2284 | 8222.4 | 0 | 0 | 1 | 5000 | 8222.4 | 0 | 0 | 0 | 0 | 0 | 33157.6 | 0 | 0 | 0 | 0 | 0 | 33157.6
2022121624 | 6 | 0.55779 | 44623.2 | 0.23599 | 8495.64 | 0 | 0 | 1 | 5000 | 8495.64 | 0 | 0 | 0 | 0 | 0 | 31127.56 | 0 | 0 | 0 | 0 | 0 | 31127.56
2022121701 | 7 | 0.54152 | 43321.6 | 0.24163 | 8698.68 | 0 | 0 | 1 | 5000 | 8698.68 | 0 | 0 | 0 | 0 | 0 | 29622.92 | 0 | 0 | 0 | 0 | 0 | 29622.92
2022121702 | 7 | 0.53035 | 42428 | 0.24074 | 8666.64 | 0 | 0 | 1 | 5000 | 8666.64 | 0 | 0 | 0 | 0 | 0 | 28761.36 | 0 | 0 | 0 | 0 | 0 | 28761.36
2022121703 | 7 | 0.52636 | 42108.8 | 0.23056 | 8300.16 | 0 | 0 | 1 | 5000 | 8300.16 | 0 | 0 | 0 | 0 | 0 | 28808.64 | 0 | 0 | 0 | 0 | 0 | 28808.64
2022121704 | 7 | 0.52691 | 42152.8 | 0.21489 | 7736.04 | 0 | 0 | 1 | 5000 | 7736.04 | 0 | 0 | 0 | 0 | 0 | 29416.76 | 0 | 0 | 0 | 0 | 0 | 29416.76
2022121705 | 7 | 0.53677 | 42941.6 | 0.21438 | 7717.68 | 0 | 0 | 1 | 5000 | 7717.68 | 0 | 0 | 0 | 0 | 0 | 30223.92 | 0 | 0 | 0 | 0 | 0 | 30223.92
2022121706 | 7 | 0.55353 | 44282.4 | 0.21896 | 7882.56 | 0 | 0 | 1 | 5000 | 7882.56 | 0 | 0 | 0 | 0 | 0 | 31399.84 | 0 | 0 | 0 | 0 | 0 | 31399.84
2022121707 | 7 | 0.57825 | 46260 | 0.21031 | 7571.16 | 0 | 0 | 1 | 5000 | 7571.16 | 0 | 0 | 0 | 0 | 0 | 33688.84 | 0 | 0 | 0 | 0 | 0 | 33688.84
2022121708 | 7 | 0.59769 | 47815.2 | 0.17894 | 6441.84 | 0.00639 | 76.68 | 1 | 5000 | 6441.84 | 76.68 | 0 | 0 | 0 | 0 | 36296.68 | 0 | 0 | 0 | 0 | 0 | 36296.68
2022121709 | 7 | 0.61697 | 49357.6 | 0.16225 | 5841 | 0.22408 | 2688.96 | 1 | 5000 | 5841 | 2688.96 | 0 | 0 | 0 | 0 | 35827.64 | 0 | 0 | 0 | 0 | 0 | 35827.64
2022121710 | 7 | 0.61656 | 49324.8 | 0.1271 | 4575.6 | 0.50277 | 6033.24 | 1 | 5000 | 4575.6 | 6033.24 | 0 | 0 | 0 | 0 | 33715.96 | 0 | 0 | 0 | 0 | 0 | 33715.96
2022121711 | 7 | 0.60121 | 48096.8 | 0.12536 | 4512.96 | 0.55084 | 6610.08 | 1 | 5000 | 4512.96 | 6610.08 | 0 | 0 | 0 | 0 | 31973.76 | 0 | 0 | 0 | 0 | 0 | 31973.76
2022121712 | 7 | 0.58211 | 46568.8 | 0.12813 | 4612.68 | 0.55769 | 6692.28 | 1 | 5000 | 4612.68 | 6692.28 | 0 | 0 | 0 | 0 | 30263.84 | 0 | 0 | 0 | 0 | 0 | 30263.84
2022121713 | 7 | 0.55791 | 44632.8 | 0.13283 | 4781.88 | 0.55735 | 6688.2 | 1 | 5000 | 4781.88 | 6688.2 | 0 | 0 | 0 | 0 | 28162.72 | 0 | 0 | 0 | 0 | 0 | 28162.72
2022121714 | 7 | 0.53885 | 43108 | 0.12877 | 4635.72 | 0.56437 | 6772.44 | 1 | 5000 | 4635.72 | 6772.44 | 0 | 0 | 0 | 0 | 26699.84 | 0 | 0 | 0 | 0 | 0 | 26699.84
2022121715 | 7 | 0.52387 | 41909.6 | 0.11934 | 4296.24 | 0.58479 | 7017.48 | 1 | 5000 | 4296.24 | 7017.48 | 0 | 0 | 0 | 0 | 25595.88 | 0 | 0 | 0 | 0 | 0 | 25595.88
2022121716 | 7 | 0.51631 | 41304.8 | 0.10345 | 3724.2 | 0.58598 | 7031.76 | 1 | 5000 | 3724.2 | 7031.76 | 0 | 0 | 0 | 0 | 25548.84 | 0 | 0 | 0 | 0 | 0 | 25548.84
2022121717 | 7 | 0.52356 | 41884.8 | 0.09143 | 3291.48 | 0.35884 | 4306.08 | 1 | 5000 | 3291.48 | 4306.08 | 0 | 0 | 0 | 0 | 29287.24 | 0 | 0 | 0 | 0 | 0 | 29287.24
2022121718 | 7 | 0.54924 | 43939.2 | 0.08404 | 3025.44 | 0.03928 | 471.36 | 1 | 5000 | 3025.44 | 471.36 | 0 | 0 | 0 | 0 | 35442.4 | 0 | 0 | 0 | 0 | 0 | 35442.4
2022121719 | 7 | 0.57456 | 45964.8 | 0.11508 | 4142.88 | 0 | 0 | 1 | 5000 | 4142.88 | 0 | 0 | 0 | 0 | 0 | 36821.92 | 0 | 0 | 0 | 0 | 0 | 36821.92
2022121720 | 7 | 0.58345 | 46676 | 0.15719 | 5658.84 | 4e-05 | 0.48 | 1 | 5000 | 5658.84 | 0.48 | 0 | 0 | 0 | 0 | 36016.68 | 0 | 0 | 0 | 0 | 0 | 36016.68
2022121721 | 7 | 0.59442 | 47553.6 | 0.19599 | 7055.64 | 0 | 0 | 1 | 5000 | 7055.64 | 0 | 0 | 0 | 0 | 0 | 35497.96 | 0 | 0 | 0 | 0 | 0 | 35497.96
2022121722 | 7 | 0.59932 | 47945.6 | 0.23122 | 8323.92 | 0 | 0 | 1 | 5000 | 8323.92 | 0 | 0 | 0 | 0 | 0 | 34621.68 | 0 | 0 | 0 | 0 | 0 | 34621.68
2022121723 | 7 | 0.59742 | 47793.6 | 0.28824 | 10376.64 | 0 | 0 | 1 | 5000 | 10376.64 | 0 | 0 | 0 | 0 | 0 | 32416.96 | 0 | 0 | 0 | 0 | 0 | 32416.96
2022121724 | 7 | 0.58923 | 47138.4 | 0.34321 | 12355.56 | 0 | 0 | 1 | 5000 | 12355.56 | 0 | 0 | 0 | 0 | 0 | 29782.84 | 0 | 0 | 0 | 0 | 0 | 29782.84
2022121801 | 1 | 0.57975 | 46380 | 0.38233 | 13763.88 | 0 | 0 | 1 | 5000 | 13763.88 | 0 | 0 | 0 | 0 | 0 | 27616.12 | 0 | 0 | 0 | 0 | 0 | 27616.12
2022121802 | 1 | 0.57464 | 45971.2 | 0.41094 | 14793.84 | 0 | 0 | 1 | 5000 | 14793.84 | 0 | 0 | 0 | 0 | 0 | 26177.36 | 0 | 0 | 0 | 0 | 0 | 26177.36
2022121803 | 1 | 0.57566 | 46052.8 | 0.42652 | 15354.72 | 0 | 0 | 1 | 5000 | 15354.72 | 0 | 0 | 0 | 0 | 0 | 25698.08 | 0 | 0 | 0 | 0 | 0 | 25698.08
2022121804 | 1 | 0.57947 | 46357.6 | 0.44649 | 16073.64 | 0 | 0 | 1 | 5000 | 16073.64 | 0 | 0 | 0 | 0 | 0 | 25283.96 | 0 | 0 | 0 | 0 | 0 | 25283.96
2022121805 | 1 | 0.58908 | 47126.4 | 0.47093 | 16953.48 | 0 | 0 | 1 | 5000 | 16953.48 | 0 | 0 | 0 | 0 | 0 | 25172.92 | 0 | 0 | 0 | 0 | 0 | 25172.92
2022121806 | 1 | 0.60368 | 48294.4 | 0.48951 | 17622.36 | 0 | 0 | 1 | 5000 | 17622.36 | 0 | 0 | 0 | 0 | 0 | 25672.04 | 0 | 0 | 0 | 0 | 0 | 25672.04
2022121807 | 1 | 0.62338 | 49870.4 | 0.49088 | 17671.68 | 0 | 0 | 1 | 5000 | 17671.68 | 0 | 0 | 0 | 0 | 0 | 27198.72 | 0 | 0 | 0 | 0 | 0 | 27198.72
2022121808 | 1 | 0.64156 | 51324.8 | 0.49051 | 17658.36 | 0.0145 | 174 | 1 | 5000 | 17658.36 | 174 | 0 | 0 | 0 | 0 | 28492.44 | 0 | 0 | 0 | 0 | 0 | 28492.44
2022121809 | 1 | 0.64469 | 51575.2 | 0.47872 | 17233.92 | 0.21564 | 2587.68 | 1 | 5000 | 17233.92 | 2587.68 | 0 | 0 | 0 | 0 | 26753.6 | 0 | 0 | 0 | 0 | 0 | 26753.6
2022121810 | 1 | 0.62584 | 50067.2 | 0.41204 | 14833.44 | 0.39774 | 4772.88 | 1 | 5000 | 14833.44 | 4772.88 | 0 | 0 | 0 | 0 | 25460.88 | 0 | 0 | 0 | 0 | 0 | 25460.88
2022121811 | 1 | 0.60226 | 48180.8 | 0.41321 | 14875.56 | 0.42863 | 5143.56 | 1 | 5000 | 14875.56 | 5143.56 | 0 | 0 | 0 | 0 | 23161.68 | 0 | 0 | 0 | 0 | 0 | 23161.68
2022121812 | 1 | 0.57758 | 46206.4 | 0.45641 | 16430.76 | 0.41597 | 4991.64 | 1 | 5000 | 16430.76 | 4991.64 | 0 | 0 | 0 | 0 | 19784 | 0 | 0 | 0 | 0 | 0 | 19784
2022121813 | 1 | 0.56162 | 44929.6 | 0.48521 | 17467.56 | 0.33959 | 4075.08 | 1 | 5000 | 17467.56 | 4075.08 | 0 | 0 | 0 | 0 | 18386.96 | 0 | 0 | 0 | 0 | 0 | 18386.96
2022121814 | 1 | 0.54805 | 43844 | 0.49028 | 17650.08 | 0.26034 | 3124.08 | 1 | 5000 | 17650.08 | 3124.08 | 0 | 0 | 0 | 0 | 18069.84 | 0 | 0 | 0 | 0 | 0 | 18069.84
2022121815 | 1 | 0.54022 | 43217.6 | 0.50243 | 18087.48 | 0.2185 | 2622 | 1 | 5000 | 18087.48 | 2622 | 0 | 0 | 0 | 0 | 17508.12 | 0 | 0 | 0 | 0 | 0 | 17508.12
2022121816 | 1 | 0.5397 | 43176 | 0.52562 | 18922.32 | 0.14179 | 1701.48 | 1 | 5000 | 18922.32 | 1701.48 | 0 | 0 | 0 | 0 | 17552.2 | 0 | 0 | 0 | 0 | 0 | 17552.2
2022121817 | 1 | 0.55048 | 44038.4 | 0.53531 | 19271.16 | 0.08797 | 1055.64 | 1 | 5000 | 19271.16 | 1055.64 | 0 | 0 | 0 | 0 | 18711.6 | 0 | 0 | 0 | 0 | 0 | 18711.6
2022121818 | 1 | 0.58046 | 46436.8 | 0.53681 | 19325.16 | 0.01275 | 153 | 1 | 5000 | 19325.16 | 153 | 0 | 0 | 0 | 0 | 21958.64 | 0 | 0 | 0 | 0 | 0 | 21958.64
2022121819 | 1 | 0.59982 | 47985.6 | 0.55356 | 19928.16 | 0 | 0 | 1 | 5000 | 19928.16 | 0 | 0 | 0 | 0 | 0 | 23057.44 | 0 | 0 | 0 | 0 | 0 | 23057.44
2022121820 | 1 | 0.5992 | 47936 | 0.57474 | 20690.64 | 0 | 0 | 1 | 5000 | 20690.64 | 0 | 0 | 0 | 0 | 0 | 22245.36 | 0 | 0 | 0 | 0 | 0 | 22245.36
2022121821 | 1 | 0.59411 | 47528.8 | 0.57463 | 20686.68 | 0 | 0 | 1 | 5000 | 20686.68 | 0 | 0 | 0 | 0 | 0 | 21842.12 | 0 | 0 | 0 | 0 | 0 | 21842.12
2022121822 | 1 | 0.58228 | 46582.4 | 0.56458 | 20324.88 | 0 | 0 | 1 | 5000 | 20324.88 | 0 | 0 | 0 | 0 | 0 | 21257.52 | 0 | 0 | 0 | 0 | 0 | 21257.52
2022121823 | 1 | 0.55994 | 44795.2 | 0.55801 | 20088.36 | 0 | 0 | 1 | 5000 | 20088.36 | 0 | 0 | 0 | 0 | 0 | 19706.84 | 0 | 0 | 0 | 0 | 0 | 19706.84
2022121824 | 1 | 0.536 | 42880 | 0.54518 | 19626.48 | 0 | 0 | 1 | 5000 | 19626.48 | 0 | 0 | 0 | 0 | 0 | 18253.52 | 0 | 0 | 0 | 0 | 0 | 18253.52
2022121901 | 2 | 0.51766 | 41412.8 | 0.54321 | 19555.56 | 0 | 0 | 1 | 5000 | 19555.56 | 0 | 0 | 0 | 0 | 0 | 16857.24 | 0 | 0 | 0 | 0 | 0 | 16857.24
2022121902 | 2 | 0.50731 | 40584.8 | 0.54575 | 19647 | 0 | 0 | 1 | 5000 | 19647 | 0 | 0 | 0 | 0 | 0 | 15937.8 | 0 | 0 | 0 | 0 | 0 | 15937.8
2022121903 | 2 | 0.50233 | 40186.4 | 0.54075 | 19467 | 0 | 0 | 1 | 5000 | 19467 | 0 | 0 | 0 | 0 | 0 | 15719.4 | 0 | 0 | 0 | 0 | 0 | 15719.4
2022121904 | 2 | 0.50399 | 40319.2 | 0.52926 | 19053.36 | 0 | 0 | 1 | 5000 | 19053.36 | 0 | 0 | 0 | 0 | 0 | 16265.84 | 0 | 0 | 0 | 0 | 0 | 16265.84
2022121905 | 2 | 0.51675 | 41340 | 0.52043 | 18735.48 | 0 | 0 | 1 | 5000 | 18735.48 | 0 | 0 | 0 | 0 | 0 | 17604.52 | 0 | 0 | 0 | 0 | 0 | 17604.52
2022121906 | 2 | 0.54106 | 43284.8 | 0.50485 | 18174.6 | 0 | 0 | 1 | 5000 | 18174.6 | 0 | 0 | 0 | 0 | 0 | 20110.2 | 0 | 0 | 0 | 0 | 0 | 20110.2
2022121907 | 2 | 0.57502 | 46001.6 | 0.47576 | 17127.36 | 0 | 0 | 1 | 5000 | 17127.36 | 0 | 0 | 0 | 0 | 0 | 23874.24 | 0 | 0 | 0 | 0 | 0 | 23874.24
2022121908 | 2 | 0.60103 | 48082.4 | 0.42953 | 15463.08 | 0.00113 | 13.56 | 1 | 5000 | 15463.08 | 13.56 | 0 | 0 | 0 | 0 | 27605.76 | 0 | 0 | 0 | 0 | 0 | 27605.76
2022121909 | 2 | 0.61557 | 49245.6 | 0.38544 | 13875.84 | 0.11788 | 1414.56 | 1 | 5000 | 13875.84 | 1414.56 | 0 | 0 | 0 | 0 | 28955.2 | 0 | 0 | 0 | 0 | 0 | 28955.2
2022121910 | 2 | 0.62811 | 50248.8 | 0.3414 | 12290.4 | 0.3327 | 3992.4 | 1 | 5000 | 12290.4 | 3992.4 | 0 | 0 | 0 | 0 | 28966 | 0 | 0 | 0 | 0 | 0 | 28966
2022121911 | 2 | 0.63268 | 50614.4 | 0.3274 | 11786.4 | 0.38501 | 4620.12 | 1 | 5000 | 11786.4 | 4620.12 | 0 | 0 | 0 | 0 | 29207.88 | 0 | 0 | 0 | 0 | 0 | 29207.88
2022121912 | 2 | 0.63086 | 50468.8 | 0.29591 | 10652.76 | 0.38674 | 4640.88 | 1 | 5000 | 10652.76 | 4640.88 | 0 | 0 | 0 | 0 | 30175.16 | 0 | 0 | 0 | 0 | 0 | 30175.16
2022121913 | 2 | 0.62462 | 49969.6 | 0.27535 | 9912.6 | 0.3902 | 4682.4 | 1 | 5000 | 9912.6 | 4682.4 | 0 | 0 | 0 | 0 | 30374.6 | 0 | 0 | 0 | 0 | 0 | 30374.6
2022121914 | 2 | 0.61818 | 49454.4 | 0.26503 | 9541.08 | 0.40701 | 4884.12 | 1 | 5000 | 9541.08 | 4884.12 | 0 | 0 | 0 | 0 | 30029.2 | 0 | 0 | 0 | 0 | 0 | 30029.2
2022121915 | 2 | 0.61231 | 48984.8 | 0.24973 | 8990.28 | 0.4162 | 4994.4 | 1 | 5000 | 8990.28 | 4994.4 | 0 | 0 | 0 | 0 | 30000.12 | 0 | 0 | 0 | 0 | 0 | 30000.12
2022121916 | 2 | 0.61132 | 48905.6 | 0.24523 | 8828.28 | 0.40303 | 4836.36 | 1 | 5000 | 8828.28 | 4836.36 | 0 | 0 | 0 | 0 | 30240.96 | 0 | 0 | 0 | 0 | 0 | 30240.96
2022121917 | 2 | 0.61476 | 49180.8 | 0.23114 | 8321.04 | 0.2703 | 3243.6 | 1 | 5000 | 8321.04 | 3243.6 | 0 | 0 | 0 | 0 | 32616.16 | 0 | 0 | 0 | 0 | 0 | 32616.16
2022121918 | 2 | 0.63132 | 50505.6 | 0.20711 | 7455.96 | 0.03419 | 410.28 | 1 | 5000 | 7455.96 | 410.28 | 0 | 0 | 0 | 0 | 37639.36 | 0 | 0 | 0 | 0 | 0 | 37639.36
2022121919 | 2 | 0.64309 | 51447.2 | 0.24622 | 8863.92 | 0 | 0 | 1 | 5000 | 8863.92 | 0 | 0 | 0 | 0 | 0 | 37583.28 | 0 | 0 | 0 | 0 | 0 | 37583.28
2022121920 | 2 | 0.63685 | 50948 | 0.26629 | 9586.44 | 0 | 0 | 1 | 5000 | 9586.44 | 0 | 0 | 0 | 0 | 0 | 36361.56 | 0 | 0 | 0 | 0 | 0 | 36361.56
2022121921 | 2 | 0.62651 | 50120.8 | 0.26689 | 9608.04 | 0 | 0 | 1 | 5000 | 9608.04 | 0 | 0 | 0 | 0 | 0 | 35512.76 | 0 | 0 | 0 | 0 | 0 | 35512.76
2022121922 | 2 | 0.6088 | 48704 | 0.26244 | 9447.84 | 0 | 0 | 1 | 5000 | 9447.84 | 0 | 0 | 0 | 0 | 0 | 34256.16 | 0 | 0 | 0 | 0 | 0 | 34256.16
2022121923 | 2 | 0.5811 | 46488 | 0.27812 | 10012.32 | 0 | 0 | 1 | 5000 | 10012.32 | 0 | 0 | 0 | 0 | 0 | 31475.68 | 0 | 0 | 0 | 0 | 0 | 31475.68
2022121924 | 2 | 0.55602 | 44481.6 | 0.29123 | 10484.28 | 0 | 0 | 1 | 5000 | 10484.28 | 0 | 0 | 0 | 0 | 0 | 28997.32 | 0 | 0 | 0 | 0 | 0 | 28997.32
2022122001 | 3 | 0.53509 | 42807.2 | 0.31765 | 11435.4 | 0 | 0 | 1 | 5000 | 11435.4 | 0 | 0 | 0 | 0 | 0 | 26371.8 | 0 | 0 | 0 | 0 | 0 | 26371.8
2022122002 | 3 | 0.52437 | 41949.6 | 0.32214 | 11597.04 | 0 | 0 | 1 | 5000 | 11597.04 | 0 | 0 | 0 | 0 | 0 | 25352.56 | 0 | 0 | 0 | 0 | 0 | 25352.56
2022122003 | 3 | 0.51745 | 41396 | 0.33168 | 11940.48 | 0 | 0 | 1 | 5000 | 11940.48 | 0 | 0 | 0 | 0 | 0 | 24455.52 | 0 | 0 | 0 | 0 | 0 | 24455.52
2022122004 | 3 | 0.51475 | 41180 | 0.35795 | 12886.2 | 0 | 0 | 1 | 5000 | 12886.2 | 0 | 0 | 0 | 0 | 0 | 23293.8 | 0 | 0 | 0 | 0 | 0 | 23293.8
2022122005 | 3 | 0.52778 | 42222.4 | 0.3776 | 13593.6 | 0 | 0 | 1 | 5000 | 13593.6 | 0 | 0 | 0 | 0 | 0 | 23628.8 | 0 | 0 | 0 | 0 | 0 | 23628.8
2022122006 | 3 | 0.5548 | 44384 | 0.3834 | 13802.4 | 0 | 0 | 1 | 5000 | 13802.4 | 0 | 0 | 0 | 0 | 0 | 25581.6 | 0 | 0 | 0 | 0 | 0 | 25581.6
2022122007 | 3 | 0.58936 | 47148.8 | 0.37364 | 13451.04 | 0 | 0 | 1 | 5000 | 13451.04 | 0 | 0 | 0 | 0 | 0 | 28697.76 | 0 | 0 | 0 | 0 | 0 | 28697.76
2022122008 | 3 | 0.61198 | 48958.4 | 0.34558 | 12440.88 | 0.00204 | 24.48 | 1 | 5000 | 12440.88 | 24.48 | 0 | 0 | 0 | 0 | 31493.04 | 0 | 0 | 0 | 0 | 0 | 31493.04
2022122009 | 3 | 0.62079 | 49663.2 | 0.29276 | 10539.36 | 0.13419 | 1610.28 | 1 | 5000 | 10539.36 | 1610.28 | 0 | 0 | 0 | 0 | 32513.56 | 0 | 0 | 0 | 0 | 0 | 32513.56
2022122010 | 3 | 0.62172 | 49737.6 | 0.22784 | 8202.24 | 0.34666 | 4159.92 | 1 | 5000 | 8202.24 | 4159.92 | 0 | 0 | 0 | 0 | 32375.44 | 0 | 0 | 0 | 0 | 0 | 32375.44
2022122011 | 3 | 0.61241 | 48992.8 | 0.17935 | 6456.6 | 0.39859 | 4783.08 | 1 | 5000 | 6456.6 | 4783.08 | 0 | 0 | 0 | 0 | 32753.12 | 0 | 0 | 0 | 0 | 0 | 32753.12
2022122012 | 3 | 0.60178 | 48142.4 | 0.14556 | 5240.16 | 0.41916 | 5029.92 | 1 | 5000 | 5240.16 | 5029.92 | 0 | 0 | 0 | 0 | 32872.32 | 0 | 0 | 0 | 0 | 0 | 32872.32
2022122013 | 3 | 0.58799 | 47039.2 | 0.1293 | 4654.8 | 0.42448 | 5093.76 | 1 | 5000 | 4654.8 | 5093.76 | 0 | 0 | 0 | 0 | 32290.64 | 0 | 0 | 0 | 0 | 0 | 32290.64
2022122014 | 3 | 0.57865 | 46292 | 0.12221 | 4399.56 | 0.42983 | 5157.96 | 1 | 5000 | 4399.56 | 5157.96 | 0 | 0 | 0 | 0 | 31734.48 | 0 | 0 | 0 | 0 | 0 | 31734.48
2022122015 | 3 | 0.57168 | 45734.4 | 0.11779 | 4240.44 | 0.43104 | 5172.48 | 1 | 5000 | 4240.44 | 5172.48 | 0 | 0 | 0 | 0 | 31321.48 | 0 | 0 | 0 | 0 | 0 | 31321.48
2022122016 | 3 | 0.56818 | 45454.4 | 0.11535 | 4152.6 | 0.37956 | 4554.72 | 1 | 5000 | 4152.6 | 4554.72 | 0 | 0 | 0 | 0 | 31747.08 | 0 | 0 | 0 | 0 | 0 | 31747.08
2022122017 | 3 | 0.57425 | 45940 | 0.11675 | 4203 | 0.19514 | 2341.68 | 1 | 5000 | 4203 | 2341.68 | 0 | 0 | 0 | 0 | 34395.32 | 0 | 0 | 0 | 0 | 0 | 34395.32
2022122018 | 3 | 0.59985 | 47988 | 0.12429 | 4474.44 | 0.01917 | 230.04 | 1 | 5000 | 4474.44 | 230.04 | 0 | 0 | 0 | 0 | 38283.52 | 0 | 0 | 0 | 0 | 0 | 38283.52
2022122019 | 3 | 0.62329 | 49863.2 | 0.15418 | 5550.48 | 0 | 0 | 1 | 5000 | 5550.48 | 0 | 0 | 0 | 0 | 0 | 39312.72 | 0 | 0 | 0 | 0 | 0 | 39312.72
2022122020 | 3 | 0.62786 | 50228.8 | 0.16361 | 5889.96 | 0 | 0 | 1 | 5000 | 5889.96 | 0 | 0 | 0 | 0 | 0 | 39338.84 | 0 | 0 | 0 | 0 | 0 | 39338.84
2022122021 | 3 | 0.62415 | 49932 | 0.15861 | 5709.96 | 0 | 0 | 1 | 5000 | 5709.96 | 0 | 0 | 0 | 0 | 0 | 39222.04 | 0 | 0 | 0 | 0 | 0 | 39222.04
2022122022 | 3 | 0.61689 | 49351.2 | 0.15641 | 5630.76 | 0 | 0 | 1 | 5000 | 5630.76 | 0 | 0 | 0 | 0 | 0 | 38720.44 | 0 | 0 | 0 | 0 | 0 | 38720.44
2022122023 | 3 | 0.5985 | 47880 | 0.14774 | 5318.64 | 0 | 0 | 1 | 5000 | 5318.64 | 0 | 0 | 0 | 0 | 0 | 37561.36 | 0 | 0 | 0 | 0 | 0 | 37561.36
2022122024 | 3 | 0.57937 | 46349.6 | 0.14766 | 5315.76 | 0 | 0 | 1 | 5000 | 5315.76 | 0 | 0 | 0 | 0 | 0 | 36033.84 | 0 | 0 | 0 | 0 | 0 | 36033.84
2022122101 | 4 | 0.56491 | 45192.8 | 0.15554 | 5599.44 | 0 | 0 | 1 | 5000 | 5599.44 | 0 | 0 | 0 | 0 | 0 | 34593.36 | 0 | 0 | 0 | 0 | 0 | 34593.36
2022122102 | 4 | 0.56024 | 44819.2 | 0.16911 | 6087.96 | 0 | 0 | 1 | 5000 | 6087.96 | 0 | 0 | 0 | 0 | 0 | 33731.24 | 0 | 0 | 0 | 0 | 0 | 33731.24
2022122103 | 4 | 0.56017 | 44813.6 | 0.17738 | 6385.68 | 0 | 0 | 1 | 5000 | 6385.68 | 0 | 0 | 0 | 0 | 0 | 33427.92 | 0 | 0 | 0 | 0 | 0 | 33427.92
2022122104 | 4 | 0.56771 | 45416.8 | 0.17937 | 6457.32 | 0 | 0 | 1 | 5000 | 6457.32 | 0 | 0 | 0 | 0 | 0 | 33959.48 | 0 | 0 | 0 | 0 | 0 | 33959.48
2022122105 | 4 | 0.58597 | 46877.6 | 0.17653 | 6355.08 | 0 | 0 | 1 | 5000 | 6355.08 | 0 | 0 | 0 | 0 | 0 | 35522.52 | 0 | 0 | 0 | 0 | 0 | 35522.52
2022122106 | 4 | 0.6158 | 49264 | 0.19613 | 7060.68 | 0 | 0 | 1 | 5000 | 7060.68 | 0 | 0 | 0 | 0 | 0 | 37203.32 | 0 | 0 | 0 | 0 | 0 | 37203.32
2022122107 | 4 | 0.6566 | 52528 | 0.20887 | 7519.32 | 0 | 0 | 1 | 5000 | 7519.32 | 0 | 0 | 0 | 0 | 0 | 40008.68 | 0 | 0 | 0 | 0 | 0 | 40008.68
2022122108 | 4 | 0.67705 | 54164 | 0.21953 | 7903.08 | 0.00594 | 71.28 | 1 | 5000 | 7903.08 | 71.28 | 0 | 0 | 0 | 0 | 41189.64 | 0 | 0 | 0 | 0 | 0 | 41189.64
2022122109 | 4 | 0.6781 | 54248 | 0.23207 | 8354.52 | 0.06727 | 807.24 | 1 | 5000 | 8354.52 | 807.24 | 0 | 0 | 0 | 0 | 40086.24 | 0 | 0 | 0 | 0 | 0 | 40086.24
2022122110 | 4 | 0.67245 | 53796 | 0.26876 | 9675.36 | 0.14769 | 1772.28 | 1 | 5000 | 9675.36 | 1772.28 | 0 | 0 | 0 | 0 | 37348.36 | 0 | 0 | 0 | 0 | 0 | 37348.36
2022122111 | 4 | 0.65223 | 52178.4 | 0.28468 | 10248.48 | 0.25266 | 3031.92 | 1 | 5000 | 10248.48 | 3031.92 | 0 | 0 | 0 | 0 | 33898 | 0 | 0 | 0 | 0 | 0 | 33898
2022122112 | 4 | 0.62993 | 50394.4 | 0.30905 | 11125.8 | 0.36486 | 4378.32 | 1 | 5000 | 11125.8 | 4378.32 | 0 | 0 | 0 | 0 | 29890.28 | 0 | 0 | 0 | 0 | 0 | 29890.28
2022122113 | 4 | 0.61215 | 48972 | 0.36402 | 13104.72 | 0.39806 | 4776.72 | 1 | 5000 | 13104.72 | 4776.72 | 0 | 0 | 0 | 0 | 26090.56 | 0 | 0 | 0 | 0 | 0 | 26090.56
2022122114 | 4 | 0.59742 | 47793.6 | 0.37587 | 13531.32 | 0.41798 | 5015.76 | 1 | 5000 | 13531.32 | 5015.76 | 0 | 0 | 0 | 0 | 24246.52 | 0 | 0 | 0 | 0 | 0 | 24246.52
2022122115 | 4 | 0.58498 | 46798.4 | 0.36906 | 13286.16 | 0.44065 | 5287.8 | 1 | 5000 | 13286.16 | 5287.8 | 0 | 0 | 0 | 0 | 23224.44 | 0 | 0 | 0 | 0 | 0 | 23224.44
2022122116 | 4 | 0.58202 | 46561.6 | 0.36491 | 13136.76 | 0.44976 | 5397.12 | 1 | 5000 | 13136.76 | 5397.12 | 0 | 0 | 0 | 0 | 23027.72 | 0 | 0 | 0 | 0 | 0 | 23027.72
2022122117 | 4 | 0.5874 | 46992 | 0.35355 | 12727.8 | 0.29597 | 3551.64 | 1 | 5000 | 12727.8 | 3551.64 | 0 | 0 | 0 | 0 | 25712.56 | 0 | 0 | 0 | 0 | 0 | 25712.56
2022122118 | 4 | 0.61272 | 49017.6 | 0.34582 | 12449.52 | 0.04233 | 507.96 | 1 | 5000 | 12449.52 | 507.96 | 0 | 0 | 0 | 0 | 31060.12 | 0 | 0 | 0 | 0 | 0 | 31060.12
2022122119 | 4 | 0.63943 | 51154.4 | 0.41473 | 14930.28 | 0 | 0 | 1 | 5000 | 14930.28 | 0 | 0 | 0 | 0 | 0 | 31224.12 | 0 | 0 | 0 | 0 | 0 | 31224.12
2022122120 | 4 | 0.64257 | 51405.6 | 0.49356 | 17768.16 | 0 | 0 | 1 | 5000 | 17768.16 | 0 | 0 | 0 | 0 | 0 | 28637.44 | 0 | 0 | 0 | 0 | 0 | 28637.44
2022122121 | 4 | 0.64628 | 51702.4 | 0.54658 | 19676.88 | 0 | 0 | 1 | 5000 | 19676.88 | 0 | 0 | 0 | 0 | 0 | 27025.52 | 0 | 0 | 0 | 0 | 0 | 27025.52
2022122122 | 4 | 0.63963 | 51170.4 | 0.56196 | 20230.56 | 0 | 0 | 1 | 5000 | 20230.56 | 0 | 0 | 0 | 0 | 0 | 25939.84 | 0 | 0 | 0 | 0 | 0 | 25939.84
2022122123 | 4 | 0.62334 | 49867.2 | 0.56043 | 20175.48 | 0 | 0 | 1 | 5000 | 20175.48 | 0 | 0 | 0 | 0 | 0 | 24691.72 | 0 | 0 | 0 | 0 | 0 | 24691.72
2022122124 | 4 | 0.60168 | 48134.4 | 0.55978 | 20152.08 | 0 | 0 | 1 | 5000 | 20152.08 | 0 | 0 | 0 | 0 | 0 | 22982.32 | 0 | 0 | 0 | 0 | 0 | 22982.32
2022122201 | 5 | 0.58339 | 46671.2 | 0.55202 | 19872.72 | 0 | 0 | 1 | 5000 | 19872.72 | 0 | 0 | 0 | 0 | 0 | 21798.48 | 0 | 0 | 0 | 0 | 0 | 21798.48
2022122202 | 5 | 0.57197 | 45757.6 | 0.54293 | 19545.48 | 0 | 0 | 1 | 5000 | 19545.48 | 0 | 0 | 0 | 0 | 0 | 21212.12 | 0 | 0 | 0 | 0 | 0 | 21212.12
2022122203 | 5 | 0.56247 | 44997.6 | 0.52857 | 19028.52 | 0 | 0 | 1 | 5000 | 19028.52 | 0 | 0 | 0 | 0 | 0 | 20969.08 | 0 | 0 | 0 | 0 | 0 | 20969.08
2022122204 | 5 | 0.55786 | 44628.8 | 0.52237 | 18805.32 | 0 | 0 | 1 | 5000 | 18805.32 | 0 | 0 | 0 | 0 | 0 | 20823.48 | 0 | 0 | 0 | 0 | 0 | 20823.48
2022122205 | 5 | 0.56382 | 45105.6 | 0.52367 | 18852.12 | 0 | 0 | 1 | 5000 | 18852.12 | 0 | 0 | 0 | 0 | 0 | 21253.48 | 0 | 0 | 0 | 0 | 0 | 21253.48
2022122206 | 5 | 0.58285 | 46628 | 0.50851 | 18306.36 | 0 | 0 | 1 | 5000 | 18306.36 | 0 | 0 | 0 | 0 | 0 | 23321.64 | 0 | 0 | 0 | 0 | 0 | 23321.64
2022122207 | 5 | 0.61057 | 48845.6 | 0.52079 | 18748.44 | 0 | 0 | 1 | 5000 | 18748.44 | 0 | 0 | 0 | 0 | 0 | 25097.16 | 0 | 0 | 0 | 0 | 0 | 25097.16
2022122208 | 5 | 0.6322 | 50576 | 0.53565 | 19283.4 | 0.00322 | 38.64 | 1 | 5000 | 19283.4 | 38.64 | 0 | 0 | 0 | 0 | 26253.96 | 0 | 0 | 0 | 0 | 0 | 26253.96
2022122209 | 5 | 0.65211 | 52168.8 | 0.52153 | 18775.08 | 0.10539 | 1264.68 | 1 | 5000 | 18775.08 | 1264.68 | 0 | 0 | 0 | 0 | 27129.04 | 0 | 0 | 0 | 0 | 0 | 27129.04
2022122210 | 5 | 0.67689 | 54151.2 | 0.54518 | 19626.48 | 0.14201 | 1704.12 | 1 | 5000 | 19626.48 | 1704.12 | 0 | 0 | 0 | 0 | 27820.6 | 0 | 0 | 0 | 0 | 0 | 27820.6
2022122211 | 5 | 0.69448 | 55558.4 | 0.56366 | 20291.76 | 0.16812 | 2017.44 | 1 | 5000 | 20291.76 | 2017.44 | 0 | 0 | 0 | 0 | 28249.2 | 0 | 0 | 0 | 0 | 0 | 28249.2
2022122212 | 5 | 0.70736 | 56588.8 | 0.55318 | 19914.48 | 0.22327 | 2679.24 | 1 | 5000 | 19914.48 | 2679.24 | 0 | 0 | 0 | 0 | 28995.08 | 0 | 0 | 0 | 0 | 0 | 28995.08
2022122213 | 5 | 0.71702 | 57361.6 | 0.54778 | 19720.08 | 0.21909 | 2629.08 | 1 | 5000 | 19720.08 | 2629.08 | 0 | 0 | 0 | 0 | 30012.44 | 0 | 0 | 0 | 0 | 0 | 30012.44
2022122214 | 5 | 0.73091 | 58472.8 | 0.55235 | 19884.6 | 0.19436 | 2332.32 | 1 | 5000 | 19884.6 | 2332.32 | 0 | 0 | 0 | 0 | 31255.88 | 0 | 0 | 0 | 0 | 0 | 31255.88
2022122215 | 5 | 0.74345 | 59476 | 0.55021 | 19807.56 | 0.19359 | 2323.08 | 1 | 5000 | 19807.56 | 2323.08 | 0 | 0 | 0 | 0 | 32345.36 | 0 | 0 | 0 | 0 | 0 | 32345.36
2022122216 | 5 | 0.76065 | 60852 | 0.56093 | 20193.48 | 0.18755 | 2250.6 | 1 | 5000 | 20193.48 | 2250.6 | 0 | 0 | 0 | 0 | 33407.92 | 0 | 0 | 0 | 0 | 0 | 33407.92
2022122217 | 5 | 0.78548 | 62838.4 | 0.60024 | 21608.64 | 0.12524 | 1502.88 | 1 | 5000 | 21608.64 | 1502.88 | 0 | 0 | 0 | 0 | 34726.88 | 0 | 0 | 0 | 0 | 0 | 34726.88
2022122218 | 5 | 0.83785 | 67028 | 0.6532 | 23515.2 | 0.01821 | 218.52 | 1 | 5000 | 23515.2 | 218.52 | 0 | 0 | 0 | 0 | 38294.28 | 0 | 0 | 0 | 0 | 0 | 38294.28
2022122219 | 5 | 0.88285 | 70628 | 0.66483 | 23933.88 | 0 | 0 | 1 | 5000 | 23933.88 | 0 | 0 | 0 | 0 | 0 | 41694.12 | 0 | 0 | 0 | 0 | 0 | 41694.12
2022122220 | 5 | 0.90326 | 72260.8 | 0.65158 | 23456.88 | 0 | 0 | 1 | 5000 | 23456.88 | 0 | 0 | 0 | 0 | 0 | 43803.92 | 0 | 0 | 0 | 0 | 0 | 43803.92
2022122221 | 5 | 0.91795 | 73436 | 0.64341 | 23162.76 | 0 | 0 | 1 | 5000 | 23162.76 | 0 | 0 | 0 | 0 | 0 | 45273.24 | 0 | 0 | 0 | 0 | 0 | 45273.24
2022122222 | 5 | 0.92266 | 73812.8 | 0.63087 | 22711.32 | 0 | 0 | 1 | 5000 | 22711.32 | 0 | 0 | 0 | 0 | 0 | 46101.48 | 0 | 0 | 0 | 0 | 0 | 46101.48
2022122223 | 5 | 0.91159 | 72927.2 | 0.61135 | 22008.6 | 0 | 0 | 1 | 5000 | 22008.6 | 0 | 0 | 0 | 0 | 0 | 45918.6 | 0 | 0 | 0 | 0 | 0 | 45918.6
2022122224 | 5 | 0.89802 | 71841.6 | 0.58189 | 20948.04 | 0 | 0 | 1 | 5000 | 20948.04 | 0 | 0 | 0 | 0 | 0 | 45893.56 | 0 | 0 | 0 | 0 | 0 | 45893.56
2022122301 | 6 | 0.889 | 71120 | 0.53966 | 19427.76 | 0 | 0 | 1 | 5000 | 19427.76 | 0 | 0 | 0 | 0 | 0 | 46692.24 | 0 | 0 | 0 | 0 | 0 | 46692.24
2022122302 | 6 | 0.88335 | 70668 | 0.4872 | 17539.2 | 0 | 0 | 1 | 5000 | 17539.2 | 0 | 0 | 0 | 0 | 0 | 48128.8 | 0 | 0 | 0 | 0 | 0 | 48128.8
2022122303 | 6 | 0.87904 | 70323.2 | 0.44825 | 16137 | 0 | 0 | 1 | 5000 | 16137 | 0 | 0 | 0 | 0 | 0 | 49186.2 | 0 | 0 | 0 | 0 | 0 | 49186.2
2022122304 | 6 | 0.88116 | 70492.8 | 0.41718 | 15018.48 | 0 | 0 | 1 | 5000 | 15018.48 | 0 | 0 | 0 | 0 | 0 | 50474.32 | 0 | 0 | 0 | 0 | 0 | 50474.32
2022122305 | 6 | 0.88786 | 71028.8 | 0.40525 | 14589 | 0 | 0 | 1 | 5000 | 14589 | 0 | 0 | 0 | 0 | 0 | 51439.8 | 0 | 0 | 0 | 0 | 0 | 51439.8
2022122306 | 6 | 0.89945 | 71956 | 0.38485 | 13854.6 | 0 | 0 | 1 | 5000 | 13854.6 | 0 | 0 | 0 | 0 | 0 | 53101.4 | 0 | 0 | 0 | 0 | 0 | 53101.4
2022122307 | 6 | 0.91481 | 73184.8 | 0.36202 | 13032.72 | 0 | 0 | 1 | 5000 | 13032.72 | 0 | 0 | 0 | 0 | 0 | 55152.08 | 0 | 0 | 0 | 0 | 0 | 55152.08
2022122308 | 6 | 0.92667 | 74133.6 | 0.32533 | 11711.88 | 0.01136 | 136.32 | 1 | 5000 | 11711.88 | 136.32 | 0 | 0 | 0 | 0 | 57285.4 | 0 | 0 | 0 | 0 | 0 | 57285.4
2022122309 | 6 | 0.92578 | 74062.4 | 0.27958 | 10064.88 | 0.16697 | 2003.64 | 1 | 5000 | 10064.88 | 2003.64 | 0 | 0 | 0 | 0 | 56993.88 | 0 | 0 | 0 | 0 | 0 | 56993.88
2022122310 | 6 | 0.92283 | 73826.4 | 0.28332 | 10199.52 | 0.4456 | 5347.2 | 1 | 5000 | 10199.52 | 5347.2 | 0 | 0 | 0 | 0 | 53279.68 | 0 | 0 | 0 | 0 | 0 | 53279.68
2022122311 | 6 | 0.90423 | 72338.4 | 0.27317 | 9834.12 | 0.52716 | 6325.92 | 1 | 5000 | 9834.12 | 6325.92 | 0 | 0 | 0 | 0 | 51178.36 | 0 | 0 | 0 | 0 | 0 | 51178.36
2022122312 | 6 | 0.87661 | 70128.8 | 0.25638 | 9229.68 | 0.52841 | 6340.92 | 1 | 5000 | 9229.68 | 6340.92 | 0 | 0 | 0 | 0 | 49558.2 | 0 | 0 | 0 | 0 | 0 | 49558.2
2022122313 | 6 | 0.84466 | 67572.8 | 0.23875 | 8595 | 0.53703 | 6444.36 | 1 | 5000 | 8595 | 6444.36 | 0 | 0 | 0 | 0 | 47533.44 | 0 | 0 | 0 | 0 | 0 | 47533.44
2022122314 | 6 | 0.82039 | 65631.2 | 0.22862 | 8230.32 | 0.53791 | 6454.92 | 1 | 5000 | 8230.32 | 6454.92 | 0 | 0 | 0 | 0 | 45945.96 | 0 | 0 | 0 | 0 | 0 | 45945.96
2022122315 | 6 | 0.79951 | 63960.8 | 0.19959 | 7185.24 | 0.51877 | 6225.24 | 1 | 5000 | 7185.24 | 6225.24 | 0 | 0 | 0 | 0 | 45550.32 | 0 | 0 | 0 | 0 | 0 | 45550.32
2022122316 | 6 | 0.79419 | 63535.2 | 0.17766 | 6395.76 | 0.50683 | 6081.96 | 1 | 5000 | 6395.76 | 6081.96 | 0 | 0 | 0 | 0 | 46057.48 | 0 | 0 | 0 | 0 | 0 | 46057.48
2022122317 | 6 | 0.80538 | 64430.4 | 0.1592 | 5731.2 | 0.27447 | 3293.64 | 1 | 5000 | 5731.2 | 3293.64 | 0 | 0 | 0 | 0 | 50405.56 | 0 | 0 | 0 | 0 | 0 | 50405.56
2022122318 | 6 | 0.83408 | 66726.4 | 0.12615 | 4541.4 | 0.03244 | 389.28 | 1 | 5000 | 4541.4 | 389.28 | 0 | 0 | 0 | 0 | 56795.72 | 0 | 0 | 0 | 0 | 0 | 56795.72
2022122319 | 6 | 0.85116 | 68092.8 | 0.09739 | 3506.04 | 0 | 0 | 1 | 5000 | 3506.04 | 0 | 0 | 0 | 0 | 0 | 59586.76 | 0 | 0 | 0 | 0 | 0 | 59586.76
2022122320 | 6 | 0.85155 | 68124 | 0.08366 | 3011.76 | 0 | 0 | 1 | 5000 | 3011.76 | 0 | 0 | 0 | 0 | 0 | 60112.24 | 0 | 0 | 0 | 0 | 0 | 60112.24
2022122321 | 6 | 0.8499 | 67992 | 0.07454 | 2683.44 | 0 | 0 | 1 | 5000 | 2683.44 | 0 | 0 | 0 | 0 | 0 | 60308.56 | 0 | 0 | 0 | 0 | 0 | 60308.56
2022122322 | 6 | 0.8434 | 67472 | 0.07309 | 2631.24 | 0 | 0 | 1 | 5000 | 2631.24 | 0 | 0 | 0 | 0 | 0 | 59840.76 | 0 | 0 | 0 | 0 | 0 | 59840.76
2022122323 | 6 | 0.83046 | 66436.8 | 0.07103 | 2557.08 | 0 | 0 | 1 | 5000 | 2557.08 | 0 | 0 | 0 | 0 | 0 | 58879.72 | 0 | 0 | 0 | 0 | 0 | 58879.72
2022122324 | 6 | 0.81157 | 64925.6 | 0.07502 | 2700.72 | 0 | 0 | 1 | 5000 | 2700.72 | 0 | 0 | 0 | 0 | 0 | 57224.88 | 0 | 0 | 0 | 0 | 0 | 57224.88
2022122401 | 7 | 0.79473 | 63578.4 | 0.09238 | 3325.68 | 0 | 0 | 1 | 5000 | 3325.68 | 0 | 0 | 0 | 0 | 0 | 55252.72 | 0 | 0 | 0 | 0 | 0 | 55252.72
2022122402 | 7 | 0.78702 | 62961.6 | 0.11314 | 4073.04 | 0 | 0 | 1 | 5000 | 4073.04 | 0 | 0 | 0 | 0 | 0 | 53888.56 | 0 | 0 | 0 | 0 | 0 | 53888.56
2022122403 | 7 | 0.78413 | 62730.4 | 0.11989 | 4316.04 | 0 | 0 | 1 | 5000 | 4316.04 | 0 | 0 | 0 | 0 | 0 | 53414.36 | 0 | 0 | 0 | 0 | 0 | 53414.36
2022122404 | 7 | 0.78507 | 62805.6 | 0.12419 | 4470.84 | 0 | 0 | 1 | 5000 | 4470.84 | 0 | 0 | 0 | 0 | 0 | 53334.76 | 0 | 0 | 0 | 0 | 0 | 53334.76
2022122405 | 7 | 0.78874 | 63099.2 | 0.12949 | 4661.64 | 0 | 0 | 1 | 5000 | 4661.64 | 0 | 0 | 0 | 0 | 0 | 53437.56 | 0 | 0 | 0 | 0 | 0 | 53437.56
2022122406 | 7 | 0.79598 | 63678.4 | 0.12653 | 4555.08 | 0 | 0 | 1 | 5000 | 4555.08 | 0 | 0 | 0 | 0 | 0 | 54123.32 | 0 | 0 | 0 | 0 | 0 | 54123.32
2022122407 | 7 | 0.80939 | 64751.2 | 0.13007 | 4682.52 | 0 | 0 | 1 | 5000 | 4682.52 | 0 | 0 | 0 | 0 | 0 | 55068.68 | 0 | 0 | 0 | 0 | 0 | 55068.68
2022122408 | 7 | 0.82158 | 65726.4 | 0.13397 | 4822.92 | 0.00893 | 107.16 | 1 | 5000 | 4822.92 | 107.16 | 0 | 0 | 0 | 0 | 55796.32 | 0 | 0 | 0 | 0 | 0 | 55796.32
2022122409 | 7 | 0.81711 | 65368.8 | 0.13293 | 4785.48 | 0.22532 | 2703.84 | 1 | 5000 | 4785.48 | 2703.84 | 0 | 0 | 0 | 0 | 52879.48 | 0 | 0 | 0 | 0 | 0 | 52879.48
2022122410 | 7 | 0.80075 | 64060 | 0.12139 | 4370.04 | 0.53049 | 6365.88 | 1 | 5000 | 4370.04 | 6365.88 | 0 | 0 | 0 | 0 | 48324.08 | 0 | 0 | 0 | 0 | 0 | 48324.08
2022122411 | 7 | 0.76943 | 61554.4 | 0.13085 | 4710.6 | 0.60453 | 7254.36 | 1 | 5000 | 4710.6 | 7254.36 | 0 | 0 | 0 | 0 | 44589.44 | 0 | 0 | 0 | 0 | 0 | 44589.44
2022122412 | 7 | 0.73272 | 58617.6 | 0.12916 | 4649.76 | 0.59563 | 7147.56 | 1 | 5000 | 4649.76 | 7147.56 | 0 | 0 | 0 | 0 | 41820.28 | 0 | 0 | 0 | 0 | 0 | 41820.28
2022122413 | 7 | 0.69445 | 55556 | 0.12176 | 4383.36 | 0.58432 | 7011.84 | 1 | 5000 | 4383.36 | 7011.84 | 0 | 0 | 0 | 0 | 39160.8 | 0 | 0 | 0 | 0 | 0 | 39160.8
2022122414 | 7 | 0.6602 | 52816 | 0.09947 | 3580.92 | 0.59876 | 7185.12 | 1 | 5000 | 3580.92 | 7185.12 | 0 | 0 | 0 | 0 | 37049.96 | 0 | 0 | 0 | 0 | 0 | 37049.96
2022122415 | 7 | 0.6344 | 50752 | 0.08019 | 2886.84 | 0.62168 | 7460.16 | 1 | 5000 | 2886.84 | 7460.16 | 0 | 0 | 0 | 0 | 35405 | 0 | 0 | 0 | 0 | 0 | 35405
2022122416 | 7 | 0.62321 | 49856.8 | 0.06755 | 2431.8 | 0.60823 | 7298.76 | 1 | 5000 | 2431.8 | 7298.76 | 0 | 0 | 0 | 0 | 35126.24 | 0 | 0 | 0 | 0 | 0 | 35126.24
2022122417 | 7 | 0.62772 | 50217.6 | 0.05009 | 1803.24 | 0.39954 | 4794.48 | 1 | 5000 | 1803.24 | 4794.48 | 0 | 0 | 0 | 0 | 38619.88 | 0 | 0 | 0 | 0 | 0 | 38619.88
2022122418 | 7 | 0.66501 | 53200.8 | 0.04449 | 1601.64 | 0.04994 | 599.28 | 1 | 5000 | 1601.64 | 599.28 | 0 | 0 | 0 | 0 | 45999.88 | 0 | 0 | 0 | 0 | 0 | 45999.88
2022122419 | 7 | 0.70159 | 56127.2 | 0.04445 | 1600.2 | 0 | 0 | 1 | 5000 | 1600.2 | 0 | 0 | 0 | 0 | 0 | 49527 | 0 | 0 | 0 | 0 | 0 | 49527
2022122420 | 7 | 0.71426 | 57140.8 | 0.05803 | 2089.08 | 0 | 0 | 1 | 5000 | 2089.08 | 0 | 0 | 0 | 0 | 0 | 50051.72 | 0 | 0 | 0 | 0 | 0 | 50051.72
2022122421 | 7 | 0.72224 | 57779.2 | 0.07204 | 2593.44 | 0 | 0 | 1 | 5000 | 2593.44 | 0 | 0 | 0 | 0 | 0 | 50185.76 | 0 | 0 | 0 | 0 | 0 | 50185.76
2022122422 | 7 | 0.72634 | 58107.2 | 0.10042 | 3615.12 | 0 | 0 | 1 | 5000 | 3615.12 | 0 | 0 | 0 | 0 | 0 | 49492.08 | 0 | 0 | 0 | 0 | 0 | 49492.08
2022122423 | 7 | 0.72283 | 57826.4 | 0.14502 | 5220.72 | 0 | 0 | 1 | 5000 | 5220.72 | 0 | 0 | 0 | 0 | 0 | 47605.68 | 0 | 0 | 0 | 0 | 0 | 47605.68
2022122424 | 7 | 0.71896 | 57516.8 | 0.17363 | 6250.68 | 0 | 0 | 1 | 5000 | 6250.68 | 0 | 0 | 0 | 0 | 0 | 46266.12 | 0 | 0 | 0 | 0 | 0 | 46266.12
2022122501 | 1 | 0.71661 | 57328.8 | 0.19704 | 7093.44 | 0 | 0 | 1 | 5000 | 7093.44 | 0 | 0 | 0 | 0 | 0 | 45235.36 | 0 | 0 | 0 | 0 | 0 | 45235.36
2022122502 | 1 | 0.71666 | 57332.8 | 0.21475 | 7731 | 0 | 0 | 1 | 5000 | 7731 | 0 | 0 | 0 | 0 | 0 | 44601.8 | 0 | 0 | 0 | 0 | 0 | 44601.8
2022122503 | 1 | 0.71963 | 57570.4 | 0.21846 | 7864.56 | 0 | 0 | 1 | 5000 | 7864.56 | 0 | 0 | 0 | 0 | 0 | 44705.84 | 0 | 0 | 0 | 0 | 0 | 44705.84
2022122504 | 1 | 0.72158 | 57726.4 | 0.22017 | 7926.12 | 0 | 0 | 1 | 5000 | 7926.12 | 0 | 0 | 0 | 0 | 0 | 44800.28 | 0 | 0 | 0 | 0 | 0 | 44800.28
2022122505 | 1 | 0.7251 | 58008 | 0.21493 | 7737.48 | 0 | 0 | 1 | 5000 | 7737.48 | 0 | 0 | 0 | 0 | 0 | 45270.52 | 0 | 0 | 0 | 0 | 0 | 45270.52
2022122506 | 1 | 0.73636 | 58908.8 | 0.19702 | 7092.72 | 0 | 0 | 1 | 5000 | 7092.72 | 0 | 0 | 0 | 0 | 0 | 46816.08 | 0 | 0 | 0 | 0 | 0 | 46816.08
2022122507 | 1 | 0.74997 | 59997.6 | 0.17577 | 6327.72 | 0 | 0 | 1 | 5000 | 6327.72 | 0 | 0 | 0 | 0 | 0 | 48669.88 | 0 | 0 | 0 | 0 | 0 | 48669.88
2022122508 | 1 | 0.76264 | 61011.2 | 0.1583 | 5698.8 | 0.01219 | 146.28 | 1 | 5000 | 5698.8 | 146.28 | 0 | 0 | 0 | 0 | 50166.12 | 0 | 0 | 0 | 0 | 0 | 50166.12
2022122509 | 1 | 0.74809 | 59847.2 | 0.14151 | 5094.36 | 0.24509 | 2941.08 | 1 | 5000 | 5094.36 | 2941.08 | 0 | 0 | 0 | 0 | 46811.76 | 0 | 0 | 0 | 0 | 0 | 46811.76
2022122510 | 1 | 0.7063 | 56504 | 0.08383 | 3017.88 | 0.57947 | 6953.64 | 1 | 5000 | 3017.88 | 6953.64 | 0 | 0 | 0 | 0 | 41532.48 | 0 | 0 | 0 | 0 | 0 | 41532.48
2022122511 | 1 | 0.65628 | 52502.4 | 0.05586 | 2010.96 | 0.61268 | 7352.16 | 1 | 5000 | 2010.96 | 7352.16 | 0 | 0 | 0 | 0 | 38139.28 | 0 | 0 | 0 | 0 | 0 | 38139.28
2022122512 | 1 | 0.61109 | 48887.2 | 0.0785 | 2826 | 0.58818 | 7058.16 | 1 | 5000 | 2826 | 7058.16 | 0 | 0 | 0 | 0 | 34003.04 | 0 | 0 | 0 | 0 | 0 | 34003.04
2022122513 | 1 | 0.57211 | 45768.8 | 0.13373 | 4814.28 | 0.49956 | 5994.72 | 1 | 5000 | 4814.28 | 5994.72 | 0 | 0 | 0 | 0 | 29959.8 | 0 | 0 | 0 | 0 | 0 | 29959.8
2022122514 | 1 | 0.53872 | 43097.6 | 0.17148 | 6173.28 | 0.32757 | 3930.84 | 1 | 5000 | 6173.28 | 3930.84 | 0 | 0 | 0 | 0 | 27993.48 | 0 | 0 | 0 | 0 | 0 | 27993.48
2022122515 | 1 | 0.51645 | 41316 | 0.18149 | 6533.64 | 0.21926 | 2631.12 | 1 | 5000 | 6533.64 | 2631.12 | 0 | 0 | 0 | 0 | 27151.24 | 0 | 0 | 0 | 0 | 0 | 27151.24
2022122516 | 1 | 0.50633 | 40506.4 | 0.19121 | 6883.56 | 0.14571 | 1748.52 | 1 | 5000 | 6883.56 | 1748.52 | 0 | 0 | 0 | 0 | 26874.32 | 0 | 0 | 0 | 0 | 0 | 26874.32
2022122517 | 1 | 0.51181 | 40944.8 | 0.21092 | 7593.12 | 0.12992 | 1559.04 | 1 | 5000 | 7593.12 | 1559.04 | 0 | 0 | 0 | 0 | 26792.64 | 0 | 0 | 0 | 0 | 0 | 26792.64
2022122518 | 1 | 0.54729 | 43783.2 | 0.25348 | 9125.28 | 0.0327 | 392.4 | 1 | 5000 | 9125.28 | 392.4 | 0 | 0 | 0 | 0 | 29265.52 | 0 | 0 | 0 | 0 | 0 | 29265.52
2022122519 | 1 | 0.58773 | 47018.4 | 0.37184 | 13386.24 | 0 | 0 | 1 | 5000 | 13386.24 | 0 | 0 | 0 | 0 | 0 | 28632.16 | 0 | 0 | 0 | 0 | 0 | 28632.16
2022122520 | 1 | 0.60696 | 48556.8 | 0.4367 | 15721.2 | 0 | 0 | 1 | 5000 | 15721.2 | 0 | 0 | 0 | 0 | 0 | 27835.6 | 0 | 0 | 0 | 0 | 0 | 27835.6
2022122521 | 1 | 0.62133 | 49706.4 | 0.46086 | 16590.96 | 0 | 0 | 1 | 5000 | 16590.96 | 0 | 0 | 0 | 0 | 0 | 28115.44 | 0 | 0 | 0 | 0 | 0 | 28115.44
2022122522 | 1 | 0.62794 | 50235.2 | 0.46667 | 16800.12 | 0 | 0 | 1 | 5000 | 16800.12 | 0 | 0 | 0 | 0 | 0 | 28435.08 | 0 | 0 | 0 | 0 | 0 | 28435.08
2022122523 | 1 | 0.62615 | 50092 | 0.48988 | 17635.68 | 0 | 0 | 1 | 5000 | 17635.68 | 0 | 0 | 0 | 0 | 0 | 27456.32 | 0 | 0 | 0 | 0 | 0 | 27456.32
2022122524 | 1 | 0.622 | 49760 | 0.50961 | 18345.96 | 0 | 0 | 1 | 5000 | 18345.96 | 0 | 0 | 0 | 0 | 0 | 26414.04 | 0 | 0 | 0 | 0 | 0 | 26414.04
2022122601 | 2 | 0.61415 | 49132 | 0.4975 | 17910 | 0 | 0 | 1 | 5000 | 17910 | 0 | 0 | 0 | 0 | 0 | 26222 | 0 | 0 | 0 | 0 | 0 | 26222
2022122602 | 2 | 0.61271 | 49016.8 | 0.47732 | 17183.52 | 0 | 0 | 1 | 5000 | 17183.52 | 0 | 0 | 0 | 0 | 0 | 26833.28 | 0 | 0 | 0 | 0 | 0 | 26833.28
2022122603 | 2 | 0.6137 | 49096 | 0.42098 | 15155.28 | 0 | 0 | 1 | 5000 | 15155.28 | 0 | 0 | 0 | 0 | 0 | 28940.72 | 0 | 0 | 0 | 0 | 0 | 28940.72
2022122604 | 2 | 0.62021 | 49616.8 | 0.36274 | 13058.64 | 0 | 0 | 1 | 5000 | 13058.64 | 0 | 0 | 0 | 0 | 0 | 31558.16 | 0 | 0 | 0 | 0 | 0 | 31558.16
2022122605 | 2 | 0.63246 | 50596.8 | 0.33405 | 12025.8 | 0 | 0 | 1 | 5000 | 12025.8 | 0 | 0 | 0 | 0 | 0 | 33571 | 0 | 0 | 0 | 0 | 0 | 33571
2022122606 | 2 | 0.65085 | 52068 | 0.29372 | 10573.92 | 0 | 0 | 1 | 5000 | 10573.92 | 0 | 0 | 0 | 0 | 0 | 36494.08 | 0 | 0 | 0 | 0 | 0 | 36494.08
2022122607 | 2 | 0.67078 | 53662.4 | 0.29032 | 10451.52 | 0 | 0 | 1 | 5000 | 10451.52 | 0 | 0 | 0 | 0 | 0 | 38210.88 | 0 | 0 | 0 | 0 | 0 | 38210.88
2022122608 | 2 | 0.68308 | 54646.4 | 0.33613 | 12100.68 | 0.00953 | 114.36 | 1 | 5000 | 12100.68 | 114.36 | 0 | 0 | 0 | 0 | 37431.36 | 0 | 0 | 0 | 0 | 0 | 37431.36
2022122609 | 2 | 0.67528 | 54022.4 | 0.37907 | 13646.52 | 0.22424 | 2690.88 | 1 | 5000 | 13646.52 | 2690.88 | 0 | 0 | 0 | 0 | 32685 | 0 | 0 | 0 | 0 | 0 | 32685
2022122610 | 2 | 0.65415 | 52332 | 0.34839 | 12542.04 | 0.51415 | 6169.8 | 1 | 5000 | 12542.04 | 6169.8 | 0 | 0 | 0 | 0 | 28620.16 | 0 | 0 | 0 | 0 | 0 | 28620.16
2022122611 | 2 | 0.6295 | 50360 | 0.37585 | 13530.6 | 0.4758 | 5709.6 | 1 | 5000 | 13530.6 | 5709.6 | 0 | 0 | 0 | 0 | 26119.8 | 0 | 0 | 0 | 0 | 0 | 26119.8
2022122612 | 2 | 0.60113 | 48090.4 | 0.42757 | 15392.52 | 0.25099 | 3011.88 | 1 | 5000 | 15392.52 | 3011.88 | 0 | 0 | 0 | 0 | 24686 | 0 | 0 | 0 | 0 | 0 | 24686
2022122613 | 2 | 0.57164 | 45731.2 | 0.41481 | 14933.16 | 0.13467 | 1616.04 | 1 | 5000 | 14933.16 | 1616.04 | 0 | 0 | 0 | 0 | 24182 | 0 | 0 | 0 | 0 | 0 | 24182
2022122614 | 2 | 0.54185 | 43348 | 0.37577 | 13527.72 | 0.09111 | 1093.32 | 1 | 5000 | 13527.72 | 1093.32 | 0 | 0 | 0 | 0 | 23726.96 | 0 | 0 | 0 | 0 | 0 | 23726.96
2022122615 | 2 | 0.51862 | 41489.6 | 0.33194 | 11949.84 | 0.08906 | 1068.72 | 1 | 5000 | 11949.84 | 1068.72 | 0 | 0 | 0 | 0 | 23471.04 | 0 | 0 | 0 | 0 | 0 | 23471.04
2022122616 | 2 | 0.50925 | 40740 | 0.27448 | 9881.28 | 0.18338 | 2200.56 | 1 | 5000 | 9881.28 | 2200.56 | 0 | 0 | 0 | 0 | 23658.16 | 0 | 0 | 0 | 0 | 0 | 23658.16
2022122617 | 2 | 0.51255 | 41004 | 0.22329 | 8038.44 | 0.25622 | 3074.64 | 1 | 5000 | 8038.44 | 3074.64 | 0 | 0 | 0 | 0 | 24890.92 | 0 | 0 | 0 | 0 | 0 | 24890.92
2022122618 | 2 | 0.54261 | 43408.8 | 0.16899 | 6083.64 | 0.04933 | 591.96 | 1 | 5000 | 6083.64 | 591.96 | 0 | 0 | 0 | 0 | 31733.2 | 0 | 0 | 0 | 0 | 0 | 31733.2
2022122619 | 2 | 0.57673 | 46138.4 | 0.15986 | 5754.96 | 0 | 0 | 1 | 5000 | 5754.96 | 0 | 0 | 0 | 0 | 0 | 35383.44 | 0 | 0 | 0 | 0 | 0 | 35383.44
2022122620 | 2 | 0.58622 | 46897.6 | 0.16113 | 5800.68 | 0 | 0 | 1 | 5000 | 5800.68 | 0 | 0 | 0 | 0 | 0 | 36096.92 | 0 | 0 | 0 | 0 | 0 | 36096.92
2022122621 | 2 | 0.59547 | 47637.6 | 0.15913 | 5728.68 | 0 | 0 | 1 | 5000 | 5728.68 | 0 | 0 | 0 | 0 | 0 | 36908.92 | 0 | 0 | 0 | 0 | 0 | 36908.92
2022122622 | 2 | 0.60113 | 48090.4 | 0.1491 | 5367.6 | 0 | 0 | 1 | 5000 | 5367.6 | 0 | 0 | 0 | 0 | 0 | 37722.8 | 0 | 0 | 0 | 0 | 0 | 37722.8
2022122623 | 2 | 0.60067 | 48053.6 | 0.14339 | 5162.04 | 0 | 0 | 1 | 5000 | 5162.04 | 0 | 0 | 0 | 0 | 0 | 37891.56 | 0 | 0 | 0 | 0 | 0 | 37891.56
2022122624 | 2 | 0.59401 | 47520.8 | 0.14476 | 5211.36 | 0 | 0 | 1 | 5000 | 5211.36 | 0 | 0 | 0 | 0 | 0 | 37309.44 | 0 | 0 | 0 | 0 | 0 | 37309.44
2022122701 | 3 | 0.58235 | 46588 | 0.14809 | 5331.24 | 0 | 0 | 1 | 5000 | 5331.24 | 0 | 0 | 0 | 0 | 0 | 36256.76 | 0 | 0 | 0 | 0 | 0 | 36256.76
2022122702 | 3 | 0.58459 | 46767.2 | 0.16888 | 6079.68 | 0 | 0 | 1 | 5000 | 6079.68 | 0 | 0 | 0 | 0 | 0 | 35687.52 | 0 | 0 | 0 | 0 | 0 | 35687.52
2022122703 | 3 | 0.59513 | 47610.4 | 0.19807 | 7130.52 | 0 | 0 | 1 | 5000 | 7130.52 | 0 | 0 | 0 | 0 | 0 | 35479.88 | 0 | 0 | 0 | 0 | 0 | 35479.88
2022122704 | 3 | 0.60643 | 48514.4 | 0.24303 | 8749.08 | 0 | 0 | 1 | 5000 | 8749.08 | 0 | 0 | 0 | 0 | 0 | 34765.32 | 0 | 0 | 0 | 0 | 0 | 34765.32
2022122705 | 3 | 0.62743 | 50194.4 | 0.30364 | 10931.04 | 0 | 0 | 1 | 5000 | 10931.04 | 0 | 0 | 0 | 0 | 0 | 34263.36 | 0 | 0 | 0 | 0 | 0 | 34263.36
2022122706 | 3 | 0.65978 | 52782.4 | 0.36751 | 13230.36 | 0 | 0 | 1 | 5000 | 13230.36 | 0 | 0 | 0 | 0 | 0 | 34552.04 | 0 | 0 | 0 | 0 | 0 | 34552.04
2022122707 | 3 | 0.69903 | 55922.4 | 0.43925 | 15813 | 0 | 0 | 1 | 5000 | 15813 | 0 | 0 | 0 | 0 | 0 | 35109.4 | 0 | 0 | 0 | 0 | 0 | 35109.4
2022122708 | 3 | 0.72547 | 58037.6 | 0.51044 | 18375.84 | 0.01077 | 129.24 | 1 | 5000 | 18375.84 | 129.24 | 0 | 0 | 0 | 0 | 34532.52 | 0 | 0 | 0 | 0 | 0 | 34532.52
2022122709 | 3 | 0.72046 | 57636.8 | 0.51907 | 18686.52 | 0.22684 | 2722.08 | 1 | 5000 | 18686.52 | 2722.08 | 0 | 0 | 0 | 0 | 31228.2 | 0 | 0 | 0 | 0 | 0 | 31228.2
2022122710 | 3 | 0.69281 | 55424.8 | 0.45336 | 16320.96 | 0.44718 | 5366.16 | 1 | 5000 | 16320.96 | 5366.16 | 0 | 0 | 0 | 0 | 28737.68 | 0 | 0 | 0 | 0 | 0 | 28737.68
2022122711 | 3 | 0.65768 | 52614.4 | 0.44404 | 15985.44 | 0.45677 | 5481.24 | 1 | 5000 | 15985.44 | 5481.24 | 0 | 0 | 0 | 0 | 26147.72 | 0 | 0 | 0 | 0 | 0 | 26147.72
2022122712 | 3 | 0.6246 | 49968 | 0.46891 | 16880.76 | 0.40411 | 4849.32 | 1 | 5000 | 16880.76 | 4849.32 | 0 | 0 | 0 | 0 | 23237.92 | 0 | 0 | 0 | 0 | 0 | 23237.92
2022122713 | 3 | 0.59374 | 47499.2 | 0.49605 | 17857.8 | 0.34293 | 4115.16 | 1 | 5000 | 17857.8 | 4115.16 | 0 | 0 | 0 | 0 | 20526.24 | 0 | 0 | 0 | 0 | 0 | 20526.24
2022122714 | 3 | 0.56963 | 45570.4 | 0.50033 | 18011.88 | 0.30586 | 3670.32 | 1 | 5000 | 18011.88 | 3670.32 | 0 | 0 | 0 | 0 | 18888.2 | 0 | 0 | 0 | 0 | 0 | 18888.2
2022122715 | 3 | 0.55419 | 44335.2 | 0.50629 | 18226.44 | 0.21341 | 2560.92 | 1 | 5000 | 18226.44 | 2560.92 | 0 | 0 | 0 | 0 | 18547.84 | 0 | 0 | 0 | 0 | 0 | 18547.84
2022122716 | 3 | 0.54657 | 43725.6 | 0.50837 | 18301.32 | 0.17365 | 2083.8 | 1 | 5000 | 18301.32 | 2083.8 | 0 | 0 | 0 | 0 | 18340.48 | 0 | 0 | 0 | 0 | 0 | 18340.48
2022122717 | 3 | 0.55411 | 44328.8 | 0.53463 | 19246.68 | 0.12325 | 1479 | 1 | 5000 | 19246.68 | 1479 | 0 | 0 | 0 | 0 | 18603.12 | 0 | 0 | 0 | 0 | 0 | 18603.12
2022122718 | 3 | 0.58629 | 46903.2 | 0.57147 | 20572.92 | 0.01604 | 192.48 | 1 | 5000 | 20572.92 | 192.48 | 0 | 0 | 0 | 0 | 21137.8 | 0 | 0 | 0 | 0 | 0 | 21137.8
2022122719 | 3 | 0.61845 | 49476 | 0.59988 | 21595.68 | 0 | 0 | 1 | 5000 | 21595.68 | 0 | 0 | 0 | 0 | 0 | 22880.32 | 0 | 0 | 0 | 0 | 0 | 22880.32
2022122720 | 3 | 0.62479 | 49983.2 | 0.62117 | 22362.12 | 0 | 0 | 1 | 5000 | 22362.12 | 0 | 0 | 0 | 0 | 0 | 22621.08 | 0 | 0 | 0 | 0 | 0 | 22621.08
2022122721 | 3 | 0.62616 | 50092.8 | 0.62489 | 22496.04 | 0 | 0 | 1 | 5000 | 22496.04 | 0 | 0 | 0 | 0 | 0 | 22596.76 | 0 | 0 | 0 | 0 | 0 | 22596.76
2022122722 | 3 | 0.61931 | 49544.8 | 0.62971 | 22669.56 | 0 | 0 | 1 | 5000 | 22669.56 | 0 | 0 | 0 | 0 | 0 | 21875.24 | 0 | 0 | 0 | 0 | 0 | 21875.24
2022122723 | 3 | 0.6003 | 48024 | 0.63582 | 22889.52 | 0 | 0 | 1 | 5000 | 22889.52 | 0 | 0 | 0 | 0 | 0 | 20134.48 | 0 | 0 | 0 | 0 | 0 | 20134.48
2022122724 | 3 | 0.58212 | 46569.6 | 0.65574 | 23606.64 | 0 | 0 | 1 | 5000 | 23606.64 | 0 | 0 | 0 | 0 | 0 | 17962.96 | 0 | 0 | 0 | 0 | 0 | 17962.96
2022122801 | 4 | 0.56754 | 45403.2 | 0.67087 | 24151.32 | 0 | 0 | 1 | 5000 | 24151.32 | 0 | 0 | 0 | 0 | 0 | 16251.88 | 0 | 0 | 0 | 0 | 0 | 16251.88
2022122802 | 4 | 0.56208 | 44966.4 | 0.68269 | 24576.84 | 0 | 0 | 1 | 5000 | 24576.84 | 0 | 0 | 0 | 0 | 0 | 15389.56 | 0 | 0 | 0 | 0 | 0 | 15389.56
2022122803 | 4 | 0.56028 | 44822.4 | 0.68631 | 24707.16 | 0 | 0 | 1 | 5000 | 24707.16 | 0 | 0 | 0 | 0 | 0 | 15115.24 | 0 | 0 | 0 | 0 | 0 | 15115.24
2022122804 | 4 | 0.56414 | 45131.2 | 0.68569 | 24684.84 | 0 | 0 | 1 | 5000 | 24684.84 | 0 | 0 | 0 | 0 | 0 | 15446.36 | 0 | 0 | 0 | 0 | 0 | 15446.36
2022122805 | 4 | 0.57498 | 45998.4 | 0.68688 | 24727.68 | 0 | 0 | 1 | 5000 | 24727.68 | 0 | 0 | 0 | 0 | 0 | 16270.72 | 0 | 0 | 0 | 0 | 0 | 16270.72
2022122806 | 4 | 0.59636 | 47708.8 | 0.68775 | 24759 | 0 | 0 | 1 | 5000 | 24759 | 0 | 0 | 0 | 0 | 0 | 17949.8 | 0 | 0 | 0 | 0 | 0 | 17949.8
2022122807 | 4 | 0.62158 | 49726.4 | 0.68861 | 24789.96 | 0 | 0 | 1 | 5000 | 24789.96 | 0 | 0 | 0 | 0 | 0 | 19936.44 | 0 | 0 | 0 | 0 | 0 | 19936.44
2022122808 | 4 | 0.63483 | 50786.4 | 0.69028 | 24850.08 | 0.00829 | 99.48 | 1 | 5000 | 24850.08 | 99.48 | 0 | 0 | 0 | 0 | 20836.84 | 0 | 0 | 0 | 0 | 0 | 20836.84
2022122809 | 4 | 0.62605 | 50084 | 0.67463 | 24286.68 | 0.14285 | 1714.2 | 1 | 5000 | 24286.68 | 1714.2 | 0 | 0 | 0 | 0 | 19083.12 | 0 | 0 | 0 | 0 | 0 | 19083.12
2022122810 | 4 | 0.59755 | 47804 | 0.64161 | 23097.96 | 0.27183 | 3261.96 | 1 | 5000 | 23097.96 | 3261.96 | 0 | 0 | 0 | 0 | 16444.08 | 0 | 0 | 0 | 0 | 0 | 16444.08
2022122811 | 4 | 0.56718 | 45374.4 | 0.64042 | 23055.12 | 0.27621 | 3314.52 | 1 | 5000 | 23055.12 | 3314.52 | 0 | 0 | 0 | 0 | 14004.76 | 0 | 0 | 0 | 0 | 0 | 14004.76
2022122812 | 4 | 0.54244 | 43395.2 | 0.64063 | 23062.68 | 0.2111 | 2533.2 | 1 | 5000 | 23062.68 | 2533.2 | 0 | 0 | 0 | 0 | 12799.32 | 0 | 0 | 0 | 0 | 0 | 12799.32
2022122813 | 4 | 0.52387 | 41909.6 | 0.61829 | 22258.44 | 0.2074 | 2488.8 | 1 | 5000 | 22258.44 | 2488.8 | 0 | 0 | 0 | 0 | 12162.36 | 0 | 0 | 0 | 0 | 0 | 12162.36
2022122814 | 4 | 0.51403 | 41122.4 | 0.59896 | 21562.56 | 0.22198 | 2663.76 | 1 | 5000 | 21562.56 | 2663.76 | 0 | 0 | 0 | 0 | 11896.08 | 0 | 0 | 0 | 0 | 0 | 11896.08
2022122815 | 4 | 0.50873 | 40698.4 | 0.57629 | 20746.44 | 0.24166 | 2899.92 | 1 | 5000 | 20746.44 | 2899.92 | 0 | 0 | 0 | 0 | 12052.04 | 0 | 0 | 0 | 0 | 0 | 12052.04
2022122816 | 4 | 0.50772 | 40617.6 | 0.56081 | 20189.16 | 0.25987 | 3118.44 | 1 | 5000 | 20189.16 | 3118.44 | 0 | 0 | 0 | 0 | 12310 | 0 | 0 | 0 | 0 | 0 | 12310
2022122817 | 4 | 0.51109 | 40887.2 | 0.56062 | 20182.32 | 0.1438 | 1725.6 | 1 | 5000 | 20182.32 | 1725.6 | 0 | 0 | 0 | 0 | 13979.28 | 0 | 0 | 0 | 0 | 0 | 13979.28
2022122818 | 4 | 0.52369 | 41895.2 | 0.58227 | 20961.72 | 0.01275 | 153 | 1 | 5000 | 20961.72 | 153 | 0 | 0 | 0 | 0 | 15780.48 | 0 | 0 | 0 | 0 | 0 | 15780.48
2022122819 | 4 | 0.5415 | 43320 | 0.65646 | 23632.56 | 0 | 0 | 1 | 5000 | 23632.56 | 0 | 0 | 0 | 0 | 0 | 14687.44 | 0 | 0 | 0 | 0 | 0 | 14687.44
2022122820 | 4 | 0.53988 | 43190.4 | 0.69236 | 24924.96 | 4e-05 | 0.48 | 1 | 5000 | 24924.96 | 0.48 | 0 | 0 | 0 | 0 | 13264.96 | 0 | 0 | 0 | 0 | 0 | 13264.96
2022122821 | 4 | 0.53231 | 42584.8 | 0.68431 | 24635.16 | 4e-05 | 0.48 | 1 | 5000 | 24635.16 | 0.48 | 0 | 0 | 0 | 0 | 12949.16 | 0 | 0 | 0 | 0 | 0 | 12949.16
2022122822 | 4 | 0.52165 | 41732 | 0.67583 | 24329.88 | 0 | 0 | 1 | 5000 | 24329.88 | 0 | 0 | 0 | 0 | 0 | 12402.12 | 0 | 0 | 0 | 0 | 0 | 12402.12
2022122823 | 4 | 0.50272 | 40217.6 | 0.64391 | 23180.76 | 0 | 0 | 1 | 5000 | 23180.76 | 0 | 0 | 0 | 0 | 0 | 12036.84 | 0 | 0 | 0 | 0 | 0 | 12036.84
2022122824 | 4 | 0.4759 | 38072 | 0.5905 | 21258 | 0 | 0 | 1 | 5000 | 21258 | 0 | 0 | 0 | 0 | 0 | 11814 | 0 | 0 | 0 | 0 | 0 | 11814
2022122901 | 5 | 0.4539 | 36312 | 0.55886 | 20118.96 | 0 | 0 | 1 | 5000 | 20118.96 | 0 | 0 | 0 | 0 | 0 | 11193.04 | 0 | 0 | 0 | 0 | 0 | 11193.04
2022122902 | 5 | 0.43753 | 35002.4 | 0.52334 | 18840.24 | 0 | 0 | 1 | 5000 | 18840.24 | 0 | 0 | 0 | 0 | 0 | 11162.16 | 0 | 0 | 0 | 0 | 0 | 11162.16
2022122903 | 5 | 0.42545 | 34036 | 0.4967 | 17881.2 | 0 | 0 | 1 | 5000 | 17881.2 | 0 | 0 | 0 | 0 | 0 | 11154.8 | 0 | 0 | 0 | 0 | 0 | 11154.8
2022122904 | 5 | 0.42077 | 33661.6 | 0.47907 | 17246.52 | 4e-05 | 0.48 | 1 | 5000 | 17246.52 | 0.48 | 0 | 0 | 0 | 0 | 11414.6 | 0 | 0 | 0 | 0 | 0 | 11414.6
2022122905 | 5 | 0.42311 | 33848.8 | 0.47598 | 17135.28 | 4e-05 | 0.48 | 1 | 5000 | 17135.28 | 0.48 | 0 | 0 | 0 | 0 | 11713.04 | 0 | 0 | 0 | 0 | 0 | 11713.04
2022122906 | 5 | 0.4379 | 35032 | 0.47402 | 17064.72 | 4e-05 | 0.48 | 1 | 5000 | 17064.72 | 0.48 | 0 | 0 | 0 | 0 | 12966.8 | 0 | 0 | 0 | 0 | 0 | 12966.8
2022122907 | 5 | 0.45898 | 36718.4 | 0.45623 | 16424.28 | 4e-05 | 0.48 | 1 | 5000 | 16424.28 | 0.48 | 0 | 0 | 0 | 0 | 15293.64 | 0 | 0 | 0 | 0 | 0 | 15293.64
2022122908 | 5 | 0.47657 | 38125.6 | 0.46778 | 16840.08 | 0.00416 | 49.92 | 1 | 5000 | 16840.08 | 49.92 | 0 | 0 | 0 | 0 | 16235.6 | 0 | 0 | 0 | 0 | 0 | 16235.6
2022122909 | 5 | 0.48973 | 39178.4 | 0.45517 | 16386.12 | 0.08377 | 1005.24 | 1 | 5000 | 16386.12 | 1005.24 | 0 | 0 | 0 | 0 | 16787.04 | 0 | 0 | 0 | 0 | 0 | 16787.04
2022122910 | 5 | 0.50514 | 40411.2 | 0.4126 | 14853.6 | 0.22403 | 2688.36 | 1 | 5000 | 14853.6 | 2688.36 | 0 | 0 | 0 | 0 | 17869.24 | 0 | 0 | 0 | 0 | 0 | 17869.24
2022122911 | 5 | 0.50906 | 40724.8 | 0.35633 | 12827.88 | 0.28226 | 3387.12 | 1 | 5000 | 12827.88 | 3387.12 | 0 | 0 | 0 | 0 | 19509.8 | 0 | 0 | 0 | 0 | 0 | 19509.8
2022122912 | 5 | 0.5136 | 41088 | 0.3436 | 12369.6 | 0.33301 | 3996.12 | 1 | 5000 | 12369.6 | 3996.12 | 0 | 0 | 0 | 0 | 19722.28 | 0 | 0 | 0 | 0 | 0 | 19722.28
2022122913 | 5 | 0.51599 | 41279.2 | 0.32494 | 11697.84 | 0.32707 | 3924.84 | 1 | 5000 | 11697.84 | 3924.84 | 0 | 0 | 0 | 0 | 20656.52 | 0 | 0 | 0 | 0 | 0 | 20656.52
2022122914 | 5 | 0.51798 | 41438.4 | 0.29158 | 10496.88 | 0.29256 | 3510.72 | 1 | 5000 | 10496.88 | 3510.72 | 0 | 0 | 0 | 0 | 22430.8 | 0 | 0 | 0 | 0 | 0 | 22430.8
2022122915 | 5 | 0.51642 | 41313.6 | 0.2544 | 9158.4 | 0.26865 | 3223.8 | 1 | 5000 | 9158.4 | 3223.8 | 0 | 0 | 0 | 0 | 23931.4 | 0 | 0 | 0 | 0 | 0 | 23931.4
2022122916 | 5 | 0.51258 | 41006.4 | 0.22711 | 8175.96 | 0.18409 | 2209.08 | 1 | 5000 | 8175.96 | 2209.08 | 0 | 0 | 0 | 0 | 25621.36 | 0 | 0 | 0 | 0 | 0 | 25621.36
2022122917 | 5 | 0.51142 | 40913.6 | 0.20087 | 7231.32 | 0.09485 | 1138.2 | 1 | 5000 | 7231.32 | 1138.2 | 0 | 0 | 0 | 0 | 27544.08 | 0 | 0 | 0 | 0 | 0 | 27544.08
2022122918 | 5 | 0.525 | 42000 | 0.18108 | 6518.88 | 0.02289 | 274.68 | 1 | 5000 | 6518.88 | 274.68 | 0 | 0 | 0 | 0 | 30206.44 | 0 | 0 | 0 | 0 | 0 | 30206.44
2022122919 | 5 | 0.53604 | 42883.2 | 0.16612 | 5980.32 | 0 | 0 | 1 | 5000 | 5980.32 | 0 | 0 | 0 | 0 | 0 | 31902.88 | 0 | 0 | 0 | 0 | 0 | 31902.88
2022122920 | 5 | 0.52819 | 42255.2 | 0.15696 | 5650.56 | 0 | 0 | 1 | 5000 | 5650.56 | 0 | 0 | 0 | 0 | 0 | 31604.64 | 0 | 0 | 0 | 0 | 0 | 31604.64
2022122921 | 5 | 0.51856 | 41484.8 | 0.17555 | 6319.8 | 0 | 0 | 1 | 5000 | 6319.8 | 0 | 0 | 0 | 0 | 0 | 30165 | 0 | 0 | 0 | 0 | 0 | 30165
2022122922 | 5 | 0.50618 | 40494.4 | 0.19383 | 6977.88 | 0 | 0 | 1 | 5000 | 6977.88 | 0 | 0 | 0 | 0 | 0 | 28516.52 | 0 | 0 | 0 | 0 | 0 | 28516.52
2022122923 | 5 | 0.487 | 38960 | 0.17176 | 6183.36 | 0 | 0 | 1 | 5000 | 6183.36 | 0 | 0 | 0 | 0 | 0 | 27776.64 | 0 | 0 | 0 | 0 | 0 | 27776.64
2022122924 | 5 | 0.46456 | 37164.8 | 0.14892 | 5361.12 | 0 | 0 | 1 | 5000 | 5361.12 | 0 | 0 | 0 | 0 | 0 | 26803.68 | 0 | 0 | 0 | 0 | 0 | 26803.68
2022123001 | 6 | 0.44471 | 35576.8 | 0.11791 | 4244.76 | 0 | 0 | 1 | 5000 | 4244.76 | 0 | 0 | 0 | 0 | 0 | 26332.04 | 0 | 0 | 0 | 0 | 0 | 26332.04
2022123002 | 6 | 0.43122 | 34497.6 | 0.0997 | 3589.2 | 0 | 0 | 1 | 5000 | 3589.2 | 0 | 0 | 0 | 0 | 0 | 25908.4 | 0 | 0 | 0 | 0 | 0 | 25908.4
2022123003 | 6 | 0.42498 | 33998.4 | 0.08715 | 3137.4 | 0 | 0 | 1 | 5000 | 3137.4 | 0 | 0 | 0 | 0 | 0 | 25861 | 0 | 0 | 0 | 0 | 0 | 25861
2022123004 | 6 | 0.42517 | 34013.6 | 0.06878 | 2476.08 | 0 | 0 | 1 | 5000 | 2476.08 | 0 | 0 | 0 | 0 | 0 | 26537.52 | 0 | 0 | 0 | 0 | 0 | 26537.52
2022123005 | 6 | 0.43065 | 34452 | 0.0792 | 2851.2 | 0 | 0 | 1 | 5000 | 2851.2 | 0 | 0 | 0 | 0 | 0 | 26600.8 | 0 | 0 | 0 | 0 | 0 | 26600.8
2022123006 | 6 | 0.44647 | 35717.6 | 0.10314 | 3713.04 | 0 | 0 | 1 | 5000 | 3713.04 | 0 | 0 | 0 | 0 | 0 | 27004.56 | 0 | 0 | 0 | 0 | 0 | 27004.56
2022123007 | 6 | 0.47115 | 37692 | 0.12335 | 4440.6 | 0 | 0 | 1 | 5000 | 4440.6 | 0 | 0 | 0 | 0 | 0 | 28251.4 | 0 | 0 | 0 | 0 | 0 | 28251.4
2022123008 | 6 | 0.49302 | 39441.6 | 0.12489 | 4496.04 | 0.00205 | 24.6 | 1 | 5000 | 4496.04 | 24.6 | 0 | 0 | 0 | 0 | 29920.96 | 0 | 0 | 0 | 0 | 0 | 29920.96
2022123009 | 6 | 0.50692 | 40553.6 | 0.11155 | 4015.8 | 0.06046 | 725.52 | 1 | 5000 | 4015.8 | 725.52 | 0 | 0 | 0 | 0 | 30812.28 | 0 | 0 | 0 | 0 | 0 | 30812.28
2022123010 | 6 | 0.51583 | 41266.4 | 0.08416 | 3029.76 | 0.14116 | 1693.92 | 1 | 5000 | 3029.76 | 1693.92 | 0 | 0 | 0 | 0 | 31542.72 | 0 | 0 | 0 | 0 | 0 | 31542.72
2022123011 | 6 | 0.51471 | 41176.8 | 0.06793 | 2445.48 | 0.22102 | 2652.24 | 1 | 5000 | 2445.48 | 2652.24 | 0 | 0 | 0 | 0 | 31079.08 | 0 | 0 | 0 | 0 | 0 | 31079.08
2022123012 | 6 | 0.50983 | 40786.4 | 0.07165 | 2579.4 | 0.23554 | 2826.48 | 1 | 5000 | 2579.4 | 2826.48 | 0 | 0 | 0 | 0 | 30380.52 | 0 | 0 | 0 | 0 | 0 | 30380.52
2022123013 | 6 | 0.5088 | 40704 | 0.0942 | 3391.2 | 0.27118 | 3254.16 | 1 | 5000 | 3391.2 | 3254.16 | 0 | 0 | 0 | 0 | 29058.64 | 0 | 0 | 0 | 0 | 0 | 29058.64
2022123014 | 6 | 0.5056 | 40448 | 0.13373 | 4814.28 | 0.24954 | 2994.48 | 1 | 5000 | 4814.28 | 2994.48 | 0 | 0 | 0 | 0 | 27639.24 | 0 | 0 | 0 | 0 | 0 | 27639.24
2022123015 | 6 | 0.49922 | 39937.6 | 0.15173 | 5462.28 | 0.27515 | 3301.8 | 1 | 5000 | 5462.28 | 3301.8 | 0 | 0 | 0 | 0 | 26173.52 | 0 | 0 | 0 | 0 | 0 | 26173.52
2022123016 | 6 | 0.50216 | 40172.8 | 0.15546 | 5596.56 | 0.28443 | 3413.16 | 1 | 5000 | 5596.56 | 3413.16 | 0 | 0 | 0 | 0 | 26163.08 | 0 | 0 | 0 | 0 | 0 | 26163.08
2022123017 | 6 | 0.50286 | 40228.8 | 0.16068 | 5784.48 | 0.21777 | 2613.24 | 1 | 5000 | 5784.48 | 2613.24 | 0 | 0 | 0 | 0 | 26831.08 | 0 | 0 | 0 | 0 | 0 | 26831.08
2022123018 | 6 | 0.51408 | 41126.4 | 0.17923 | 6452.28 | 0.03258 | 390.96 | 1 | 5000 | 6452.28 | 390.96 | 0 | 0 | 0 | 0 | 29283.16 | 0 | 0 | 0 | 0 | 0 | 29283.16
2022123019 | 6 | 0.53086 | 42468.8 | 0.23595 | 8494.2 | 0 | 0 | 1 | 5000 | 8494.2 | 0 | 0 | 0 | 0 | 0 | 28974.6 | 0 | 0 | 0 | 0 | 0 | 28974.6
2022123020 | 6 | 0.52872 | 42297.6 | 0.27178 | 9784.08 | 0 | 0 | 1 | 5000 | 9784.08 | 0 | 0 | 0 | 0 | 0 | 27513.52 | 0 | 0 | 0 | 0 | 0 | 27513.52
2022123021 | 6 | 0.52187 | 41749.6 | 0.29488 | 10615.68 | 0 | 0 | 1 | 5000 | 10615.68 | 0 | 0 | 0 | 0 | 0 | 26133.92 | 0 | 0 | 0 | 0 | 0 | 26133.92
2022123022 | 6 | 0.51515 | 41212 | 0.32816 | 11813.76 | 0 | 0 | 1 | 5000 | 11813.76 | 0 | 0 | 0 | 0 | 0 | 24398.24 | 0 | 0 | 0 | 0 | 0 | 24398.24
2022123023 | 6 | 0.50102 | 40081.6 | 0.37562 | 13522.32 | 0 | 0 | 1 | 5000 | 13522.32 | 0 | 0 | 0 | 0 | 0 | 21559.28 | 0 | 0 | 0 | 0 | 0 | 21559.28
2022123024 | 6 | 0.48502 | 38801.6 | 0.41847 | 15064.92 | 0 | 0 | 1 | 5000 | 15064.92 | 0 | 0 | 0 | 0 | 0 | 18736.68 | 0 | 0 | 0 | 0 | 0 | 18736.68
2022123101 | 7 | 0.46837 | 37469.6 | 0.43556 | 15680.16 | 0 | 0 | 1 | 5000 | 15680.16 | 0 | 0 | 0 | 0 | 0 | 16789.44 | 0 | 0 | 0 | 0 | 0 | 16789.44
2022123102 | 7 | 0.45691 | 36552.8 | 0.43971 | 15829.56 | 0 | 0 | 1 | 5000 | 15829.56 | 0 | 0 | 0 | 0 | 0 | 15723.24 | 0 | 0 | 0 | 0 | 0 | 15723.24
2022123103 | 7 | 0.45079 | 36063.2 | 0.44593 | 16053.48 | 0 | 0 | 1 | 5000 | 16053.48 | 0 | 0 | 0 | 0 | 0 | 15009.72 | 0 | 0 | 0 | 0 | 0 | 15009.72
2022123104 | 7 | 0.44952 | 35961.6 | 0.45638 | 16429.68 | 0 | 0 | 1 | 5000 | 16429.68 | 0 | 0 | 0 | 0 | 0 | 14531.92 | 0 | 0 | 0 | 0 | 0 | 14531.92
2022123105 | 7 | 0.45592 | 36473.6 | 0.47974 | 17270.64 | 0 | 0 | 1 | 5000 | 17270.64 | 0 | 0 | 0 | 0 | 0 | 14202.96 | 0 | 0 | 0 | 0 | 0 | 14202.96
2022123106 | 7 | 0.46622 | 37297.6 | 0.50384 | 18138.24 | 0 | 0 | 1 | 5000 | 18138.24 | 0 | 0 | 0 | 0 | 0 | 14159.36 | 0 | 0 | 0 | 0 | 0 | 14159.36
2022123107 | 7 | 0.4828 | 38624 | 0.52958 | 19064.88 | 0 | 0 | 1 | 5000 | 19064.88 | 0 | 0 | 0 | 0 | 0 | 14559.12 | 0 | 0 | 0 | 0 | 0 | 14559.12
2022123108 | 7 | 0.49744 | 39795.2 | 0.56093 | 20193.48 | 0.00418 | 50.16 | 1 | 5000 | 20193.48 | 50.16 | 0 | 0 | 0 | 0 | 14551.56 | 0 | 0 | 0 | 0 | 0 | 14551.56
2022123109 | 7 | 0.50467 | 40373.6 | 0.5546 | 19965.6 | 0.11751 | 1410.12 | 1 | 5000 | 19965.6 | 1410.12 | 0 | 0 | 0 | 0 | 13997.88 | 0 | 0 | 0 | 0 | 0 | 13997.88
2022123110 | 7 | 0.50418 | 40334.4 | 0.50764 | 18275.04 | 0.27875 | 3345 | 1 | 5000 | 18275.04 | 3345 | 0 | 0 | 0 | 0 | 13714.36 | 0 | 0 | 0 | 0 | 0 | 13714.36
2022123111 | 7 | 0.49987 | 39989.6 | 0.48376 | 17415.36 | 0.33331 | 3999.72 | 1 | 5000 | 17415.36 | 3999.72 | 0 | 0 | 0 | 0 | 13574.52 | 0 | 0 | 0 | 0 | 0 | 13574.52
2022123112 | 7 | 0.49543 | 39634.4 | 0.50258 | 18092.88 | 0.27203 | 3264.36 | 1 | 5000 | 18092.88 | 3264.36 | 0 | 0 | 0 | 0 | 13277.16 | 0 | 0 | 0 | 0 | 0 | 13277.16
2022123113 | 7 | 0.49251 | 39400.8 | 0.51625 | 18585 | 0.2265 | 2718 | 1 | 5000 | 18585 | 2718 | 0 | 0 | 0 | 0 | 13097.8 | 0 | 0 | 0 | 0 | 0 | 13097.8
2022123114 | 7 | 0.49348 | 39478.4 | 0.51415 | 18509.4 | 0.24063 | 2887.56 | 1 | 5000 | 18509.4 | 2887.56 | 0 | 0 | 0 | 0 | 13081.44 | 0 | 0 | 0 | 0 | 0 | 13081.44
2022123115 | 7 | 0.49615 | 39692 | 0.48941 | 17618.76 | 0.33032 | 3963.84 | 1 | 5000 | 17618.76 | 3963.84 | 0 | 0 | 0 | 0 | 13109.4 | 0 | 0 | 0 | 0 | 0 | 13109.4
2022123116 | 7 | 0.50041 | 40032.8 | 0.47015 | 16925.4 | 0.39045 | 4685.4 | 1 | 5000 | 16925.4 | 4685.4 | 0 | 0 | 0 | 0 | 13422 | 0 | 0 | 0 | 0 | 0 | 13422
2022123117 | 7 | 0.50569 | 40455.2 | 0.44868 | 16152.48 | 0.25989 | 3118.68 | 1 | 5000 | 16152.48 | 3118.68 | 0 | 0 | 0 | 0 | 16184.04 | 0 | 0 | 0 | 0 | 0 | 16184.04
2022123118 | 7 | 0.51101 | 40880.8 | 0.40532 | 14591.52 | 0.03042 | 365.04 | 1 | 5000 | 14591.52 | 365.04 | 0 | 0 | 0 | 0 | 20924.24 | 0 | 0 | 0 | 0 | 0 | 20924.24
2022123119 | 7 | 0.52427 | 41941.6 | 0.4822 | 17359.2 | 0 | 0 | 1 | 5000 | 17359.2 | 0 | 0 | 0 | 0 | 0 | 19582.4 | 0 | 0 | 0 | 0 | 0 | 19582.4
2022123120 | 7 | 0.51503 | 41202.4 | 0.56302 | 20268.72 | 0 | 0 | 1 | 5000 | 20268.72 | 0 | 0 | 0 | 0 | 0 | 15933.68 | 0 | 0 | 0 | 0 | 0 | 15933.68
2022123121 | 7 | 0.49985 | 39988 | 0.58325 | 20997 | 0 | 0 | 1 | 5000 | 20997 | 0 | 0 | 0 | 0 | 0 | 13991 | 0 | 0 | 0 | 0 | 0 | 13991
2022123122 | 7 | 0.4872 | 38976 | 0.60108 | 21638.88 | 0 | 0 | 1 | 5000 | 21638.88 | 0 | 0 | 0 | 0 | 0 | 12337.12 | 0 | 0 | 0 | 0 | 0 | 12337.12
2022123123 | 7 | 0.47265 | 37812 | 0.60861 | 21909.96 | 0 | 0 | 1 | 5000 | 21909.96 | 0 | 0 | 0 | 0 | 0 | 10902.04 | 0 | 0 | 0 | 0 | 0 | 10902.04
2022123124 | 7 | 0.45911 | 36728.8 | 0.59735 | 21504.6 | 0 | 0 | 1 | 5000 | 21504.6 | 0 | 0 | 0 | 0 | 0 | 10224.2 | 0 | 0 | 0 | 0 | 0 | 10224.2
Note on AE4: ERCOT 2022 hourly demand wind and solar.
Note on C17: Base loaded nuclear net maximum power output in MW, i.e. the total nameplate MWs.
Note on D18: New annual peak demand forecast.
Note on F18: Installed nameplate MW generation capacity of onshore wind.
Note on H18: Installed nameplate MW generation capacity of solar.
Note on A19: This integer format of year month day hour allows for easy sorting of the date time stamp in text editors.
Note on B19: D is the day of the week Sunday is day 1
Note on C19: The historical test year 2022 hourly loads profile is in per unit with the annual peak having 1 per unit. See reference 1.
Note on D19: The per unit loads to the left are multiplied times the annual peak forecast for this simulation which is simply scaling up the historical data to the new load forecast.
Note on E19: On shore wind per unit hourly profile for the historical 2022 year from actual data posted by ERCOT. See reference 1.
Note on F19: The per unit on shore wind values to the left are multiplied times the on shore wind capacity.
Note on G19: Solar per unit hourly profile for the historical 2022 year from actual data posted by ERCOT. See reference 1.
Note on H19: The per unit solar values to the left are multiplied times the solar MW capacity.
Note on K19: If (Demand > Nucl Pmax, then Nucl Pmax, otherwise Demand).
Note on L19: If (Demand - Nucl > Wind, then Wind, otherwise Demand - Nuclear).
Note on M19: If (Demand - Nucl - Wind> Solar, then Solar, otherwise Demand - Nucl - Wind).
Note on S19: The MWHs electrical energy storage that can serve load. Losses are applied to charging. See reference 3.
Note on U19: Uses excess nuclear.
Note on V19: Uses excess wind.
Note on W19: Uses excess solar.
Note on AA48: May - Sept summer peak is not low enough compared to the winter peak to allow peak shaving credit from battery storage.
Note on AC48: Jan - Feb
Note on AE48: Nov - Dec

## Graphs
Case | Load | Nuclear | Wind | Solar | Battery | Fossil | CO2 | Nuclear | Wind | Solar | Average | Wind Solar | Nuclear | Total | Nuclear | Wind | Solar
ERCOT22 | GW | GW | GW | GW | GWh | GW | % | % | % | % | c/kWh | $Bn/yr | $Bn/yr | $Bn/yr | %unused | %unused | %unused
A | 80 | 5 | 36 | 12 | 0 | 61 | 59 | 10 | 25 | 6 | 7.3 | 7.683 | 3.549 | 11.232 | 0 | 0 | 0
A1 | 90 | 5 | 40 | 50 | 100 | 69 | 45 | 9 | 25 | 21 | 8.9 | 19.239 | 3.549 | 22.788 | 0 | 0 | 0.09
A2 | 100 | 5 | 52 | 89 | 200 | 76 | 30 | 8 | 29 | 33 | 9.6 | 31.287 | 3.549 | 34.836 | 0 | 0 | 0.85
A3 | 110 | 5 | 109 | 111 | 600 | 80 | 10 | 7 | 53 | 29 | 12.6 | 59.091 | 3.549 | 62.64 | 0 | 1.62 | 5.42
A4 | 120 | 5 | 139 | 141 | 950 | 87 | 5 | 7 | 59 | 29 | 15 | 83.129 | 3.549 | 86.678 | 0 | 3.11 | 8.24
Case | Load | Nuclear | Wind | Solar | Battery | Fossil | CO2 | Nuclear | Wind | Solar | Average | Wind Solar | Nuclear | Total | Nuclear | Wind | Solar
ERCOT22 | GW | GW | GW | GW | GWh | GW | % | % | % | % | c/kWh | $Bn/yr | $Bn/yr | $Bn/yr | %unused | %unused | %unused
A | 80 | 5 | 36 | 12 | 0 | 61 | 59 | 10 | 25 | 6 | 7.3 | 7.683 | 3.549 | 11.232 | 0 | 0 | 0
N1 | 90 | 5 | 40 | 50 | 100 | 69 | 45 | 9 | 25 | 21 | 8.9 | 19.239 | 3.549 | 22.788 | 0 | 0 | 0.09
N2 | 100 | 18 | 40 | 50 | 100 | 64 | 30 | 29 | 22 | 19 | 8.8 | 19.324 | 12.776 | 32.1 | 0 | 0 | 0.41
N3 | 110 | 39 | 40 | 50 | 100 | 52 | 10 | 56 | 20 | 15 | 9.4 | 19.014 | 27.681 | 46.695 | 4.64 | 1.24 | 3.43
N4 | 120 | 52 | 40 | 50 | 100 | 47 | 5 | 67 | 16 | 11 | 9.7 | 19.014 | 36.904 | 55.918 | 4.66 | 4.32 | 6.64
| These are pictures of the acutal graphs which are below. | [5 empty] | This is necessary to overcome a glitch in excel.
ERCOT is forced to add new gas peakers (fossil) generation for reliability in the interim period while preparing to switch over to adding nuclear power, which will take a while.
Nuclear plants are installed after ERCOT reaches a 90 GW peak and wind and solar have already grown to 40 and 50 GW respectively. Fossil generation has grown to 70 GW for reliability.
As more nuclear is added it's possible to lower the gas peaking energy used which reduces ERCOTs dependency on gas and improves grid reliability, especially in cold weather periods.
Planning new transmission for 52 GW of nuclear will be easier than planning for 280 GW of wind and solar, especially if the nuclear can be sited near load centers at old fossil plant sites.
All resources are dispatched to load in the order of nuclear, wind, solar, and fossil peaking. Excess is sent to storage as fast as possible and used as fast as possible to reduce fossil fuels.
Adding battery storage can improve the usefulness of a resource such as solar but at a high capital cost. The spreadsheet keeps careful track of the excess battery energy charging sources.
| Its important that all the resources be utilized as much as possible. If a resource is | [8 empty] | In order for wind and solar to be effective reducers of fossil energy quite a large amount
| lightly used then decrease it's capacity to decrease the % unused capacity. Adding | [8 empty] | of battery storage is needed which increases the cost of the non nuclear plan.
storage can lower the amount of lost or unused energy. If solar has a maximum of
25% capacity factor and 5% is unused, this means the capacity factor is now 20%.
These are the actual graphs created in a 2010 version of excel workbook.