## 2022
ERCOT 2022 with 5% CO2 emissions from case 22A with 40 GW nucl, 35 GW wind, 14 GW solar, no storage, and 25.4 GW gas peaking (calculated). Average energy cost is 9.2 c/kWh.
[22 empty] | Input | Calculated | Yellow per unit (pu) header means the column is input data.
References:
[21 empty] | 1 | https://www.ercot.com/mp/data-products/data-product-details?id=PG7-126-M
[21 empty] | 2 | https://www.futureofenergyinitiative.org/Pubs/46_CostInputsForToyModels.pdf
[21 empty] | 3 | https://egpreston.com/ExcelStorage.pdf |  |  |  | has more info on programming storage.
[22 empty] | Total Energy = |  | 431527.2016 | GWh
[22 empty] | Fossil Energy = |  | 21420.087 | GWh | 4.9638 | %
[22 empty] | Non CO2 Energy = |  | 410107.1146 | Gwh | 95.0362 | %
A winter peak occurred 12/22 hour 21 with peak 91.8% of the summer peak.
Gas Peak of 25,309 MW occurred on 12/23/21 or Dec 23, 2022 at 9 pm.
Demand was 85% of summer peak, wind was 7.5% of Pmax, and solar was 0.
[22 empty] | System Energy Cost= |  | 9.1683 | cent/kWh | 25383.1 | MW Gas
|  | Hourly Demand and Variable Resources Input | [7 empty] | Hourly Dispatching of All Resources, Seasonal Thermal Storage, and Battery Peak Shaving Storage | [11 empty] | Costs and Performance of Individual Sources
Base Nucl MW = |  | 40000 | Pmax, which is the installed nameplate MW of each resource.
|  | PeakMW= | 80000 | Hydro= | 0 | WinPmx= | 35000 | SolPmax= | 14000 | Nuclear | Excess | Wind | Excess | Solar | Excess | All Excess | Peaking | Battery MWh | Battery | Fossil |  | Hourly Load Stats
YYYYMMDDHH | D | load pu | loadMW | hydro pu | hydro MW | wind pu | windMW | solar pu | solarMW | MW | MW | MW | MW | MW | MW | MW | MW | 0 | MW out | MW |  | 80000 | MW Peak | 49.2611 | GW Avg | 31.7289 | %Reserve
2022010101 | 7 | 0.47757 | 38205.6 | 0 | 0 | 0.35313 | 12359.55 | 0 | 0 | 38205.6 | 1794.4 | 0 | 12359.55 | 0 | 0 | 14153.95 | 0 | 0 | 0 | 0 |  | 32017.6 | MW Min | 431527.2016 | GWh | 61.5764 | %CF
2022010102 | 7 | 0.46503 | 37202.4 | 0 | 0 | 0.37703 | 13196.05 | 0 | 0 | 37202.4 | 2797.6 | 0 | 13196.05 | 0 | 0 | 15993.65 | 0 | 0 | 0 | 0
2022010103 | 7 | 0.45017 | 36013.6 | 0 | 0 | 0.42041 | 14714.35 | 0 | 0 | 36013.6 | 3986.4 | 0 | 14714.35 | 0 | 0 | 18700.75 | 0 | 0 | 0 | 0 |  | Lithium Ion Battery |  |  | CAPEX B$ |  | loss/day: | 0.5 | %
2022010104 | 7 | 0.44009 | 35207.2 | 0 | 0 | 0.48177 | 16861.95 | 0 | 0 | 35207.2 | 4792.8 | 0 | 16861.95 | 0 | 0 | 21654.75 | 0 | 0 | 0 | 0 |  | power | $/kW | 249 | 0 | 0 | MW max | 0 | MWh/hr
2022010105 | 7 | 0.43346 | 34676.8 | 0 | 0 | 0.53661 | 18781.35 | 0 | 0 | 34676.8 | 5323.2 | 0 | 18781.35 | 0 | 0 | 24104.55 | 0 | 0 | 0 | 0 |  | energy | $/kWh | 369 | 0 | 0 | Hrs | 0.85 | efficiency
2022010106 | 7 | 0.43155 | 34524 | 0 | 0 | 0.53149 | 18602.15 | 0 | 0 | 34524 | 5476 | 0 | 18602.15 | 0 | 0 | 24078.15 | 0 | 0 | 0 | 0
2022010107 | 7 | 0.43306 | 34644.8 | 0 | 0 | 0.54249 | 18987.15 | 0 | 0 | 34644.8 | 5355.2 | 0 | 18987.15 | 0 | 0 | 24342.35 | 0 | 0 | 0 | 0 |  | Annual Costs |  |  |  | per year | annual | uplifted
2022010108 | 7 | 0.43386 | 34708.8 | 0 | 0 | 0.53572 | 18750.2 | 0.0008 | 11.2 | 34708.8 | 5291.2 | 0 | 18750.2 | 0 | 11.2 | 24052.6 | 0 | 0 | 0 | 0 |  | Hydro | No Hydro |  |  | capt cost | cost M$ | cent/kWh
2022010109 | 7 | 0.446 | 35680 | 0 | 0 | 0.50624 | 17718.4 | 0.14415 | 2018.1 | 35680 | 4320 | 0 | 17718.4 | 0 | 2018.1 | 24056.5 | 0 | 0 | 0 | 0 |  | 0 | hydroMW | 0 | $/kW | 0 | 0 | 0
2022010110 | 7 | 0.47494 | 37995.2 | 0 | 0 | 0.49502 | 17325.7 | 0.37098 | 5193.72 | 37995.2 | 2004.8 | 0 | 17325.7 | 0 | 5193.72 | 24524.22 | 0 | 0 | 0 | 0 |  |  | O&M | 0 | $/kW/yr |  | 0 | 0
2022010111 | 7 | 0.5009 | 40072 | 0 | 0 | 0.51769 | 18119.15 | 0.34787 | 4870.18 | 40000 | 0 | 72 | 18047.15 | 0 | 4870.18 | 22917.33 | 0 | 0 | 0 | 0 |  | Base Loaded Nuclear
2022010112 | 7 | 0.52403 | 41922.4 | 0 | 0 | 0.52035 | 18212.25 | 0.28867 | 4041.38 | 40000 | 0 | 1922.4 | 16289.85 | 0 | 4041.38 | 20331.23 | 0 | 0 | 0 | 0 |  | 40000 | MW nucl | 7440 | $/kW | 0.064 | 19046.4 | 4.4137
2022010113 | 7 | 0.54068 | 43254.4 | 0 | 0 | 0.47815 | 16735.25 | 0.38506 | 5390.84 | 40000 | 0 | 3254.4 | 13480.85 | 0 | 5390.84 | 18871.69 | 0 | 0 | 0 | 0 |  |  | Nucl O&M | 146 | $/kW/yr |  | 5840 | 1.3533
2022010114 | 7 | 0.55124 | 44099.2 | 0 | 0 | 0.4348 | 15218 | 0.50861 | 7120.54 | 40000 | 0 | 4099.2 | 11118.8 | 0 | 7120.54 | 18239.34 | 0 | 0 | 0 | 0 |  |  | Vari O&M | 10 | $/MWh/yr |  | 3460.0508 | 0.80182
2022010115 | 7 | 0.55428 | 44342.4 | 0 | 0 | 0.41077 | 14376.95 | 0.54386 | 7614.04 | 40000 | 0 | 4342.4 | 10034.55 | 0 | 7614.04 | 17648.59 | 0 | 0 | 0 | 0 |  | On Shore Wind
2022010116 | 7 | 0.55378 | 44302.4 | 0 | 0 | 0.41978 | 14692.3 | 0.49681 | 6955.34 | 40000 | 0 | 4302.4 | 10389.9 | 0 | 6955.34 | 17345.24 | 0 | 0 | 0 | 0 |  | 35000 | MW wind | 1460 | $/kW | 0.089 | 4547.9 | 1.0539
2022010117 | 7 | 0.55539 | 44431.2 | 0 | 0 | 0.49428 | 17299.8 | 0.21587 | 3022.18 | 40000 | 0 | 4431.2 | 12868.6 | 0 | 3022.18 | 15890.78 | 0 | 0 | 0 | 0 |  |  | WndO&M | 43 | $/kW/yr |  | 1505 | 0.34876
2022010118 | 7 | 0.56347 | 45077.6 | 0 | 0 | 0.54996 | 19248.6 | 0.02487 | 348.18 | 40000 | 0 | 5077.6 | 14171 | 0 | 348.18 | 14519.18 | 0 | 0 | 0 | 0 |  | Solar
2022010119 | 7 | 0.57757 | 46205.6 | 0 | 0 | 0.58111 | 20338.85 | 0 | 0 | 40000 | 0 | 6205.6 | 14133.25 | 0 | 0 | 14133.25 | 0 | 0 | 0 | 0 |  | 14000 | MW solar | 1330 | $/kW | 0.074 | 1377.88 | 0.3193
2022010120 | 7 | 0.57553 | 46042.4 | 0 | 0 | 0.59821 | 20937.35 | 0 | 0 | 40000 | 0 | 6042.4 | 14894.95 | 0 | 0 | 14894.95 | 0 | 0 | 0 | 0 |  |  | solarO&M | 23 | $/kW/yr |  | 322 | 0.074619
2022010121 | 7 | 0.5732 | 45856 | 0 | 0 | 0.6104 | 21364 | 0 | 0 | 40000 | 0 | 5856 | 15508 | 0 | 0 | 15508 | 0 | 0 | 0 | 0 |  | Lithium Ion Battery
2022010122 | 7 | 0.5702 | 45616 | 0 | 0 | 0.62561 | 21896.35 | 0 | 0 | 40000 | 0 | 5616 | 16280.35 | 0 | 0 | 16280.35 | 0 | 0 | 0 | 0 |  | 0 | MW Batt | 249 | $/kW | 0.104 | 0 | 0
2022010123 | 7 | 0.56127 | 44901.6 | 0 | 0 | 0.63679 | 22287.65 | 0 | 0 | 40000 | 0 | 4901.6 | 17386.05 | 0 | 0 | 17386.05 | 0 | 0 | 0 | 0 |  | 0 | GWh Batt | 369 | B$ capex |  | 0 | 0
2022010124 | 7 | 0.54944 | 43955.2 | 0 | 0 | 0.63059 | 22070.65 | 0 | 0 | 40000 | 0 | 3955.2 | 18115.45 | 0 | 0 | 18115.45 | 0 | 0 | 0 | 0 |  |  | Batt O&M | 43 | $/kW/yr |  | 0 | 0
2022010201 | 1 | 0.53715 | 42972 | 0 | 0 | 0.6054 | 21189 | 0 | 0 | 40000 | 0 | 2972 | 18217 | 0 | 0 | 18217 | 0 | 0 | 0 | 0 |  | Gas Peaking
2022010202 | 1 | 0.52822 | 42257.6 | 0 | 0 | 0.58365 | 20427.75 | 0 | 0 | 40000 | 0 | 2257.6 | 18170.15 | 0 | 0 | 18170.15 | 0 | 0 | 0 | 0 |  | 25383.1 | MW Gas | 922 | $/kW | 0.074 | 1731.8381 | 0.40133
2022010203 | 1 | 0.52689 | 42151.2 | 0 | 0 | 0.58429 | 20450.15 | 0 | 0 | 40000 | 0 | 2151.2 | 18298.95 | 0 | 0 | 18298.95 | 0 | 0 | 0 | 0 |  |  | Gas O&M | 21 | $/kW/yr |  | 533.0451 | 0.12353
2022010204 | 1 | 0.53254 | 42603.2 | 0 | 0 | 0.59276 | 20746.6 | 0 | 0 | 40000 | 0 | 2603.2 | 18143.4 | 0 | 0 | 18143.4 | 0 | 0 | 0 | 0 |  |  | Vari O&M | 16 | $/MWh/yr |  | 342.7214 | 0.079421
2022010205 | 1 | 0.54448 | 43558.4 | 0 | 0 | 0.60709 | 21248.15 | 0 | 0 | 40000 | 0 | 3558.4 | 17689.75 | 0 | 0 | 17689.75 | 0 | 0 | 0 | 0 |  | 2445.2154 | AvgGasMW | 40 | $/MWh fuel cost |  | 856.8035 | 0.19855
2022010206 | 1 | 0.56207 | 44965.6 | 0 | 0 | 0.594 | 20790 | 0 | 0 | 40000 | 0 | 4965.6 | 15824.4 | 0 | 0 | 15824.4 | 0 | 0 | 0 | 0 | [5 empty] | total | 39563.6389 | 9.1683
2022010207 | 1 | 0.58685 | 46948 | 0 | 0 | 0.58346 | 20421.1 | 0 | 0 | 40000 | 0 | 6948 | 13473.1 | 0 | 0 | 13473.1 | 0 | 0 | 0 | 0
2022010208 | 1 | 0.6176 | 49408 | 0 | 0 | 0.56658 | 19830.3 | 0.00178 | 24.92 | 40000 | 0 | 9408 | 10422.3 | 0 | 24.92 | 10447.22 | 0 | 0 | 0 | 0 |  | Annual Costs |  |  |  |  | annual | source
2022010209 | 1 | 0.64339 | 51471.2 | 0 | 0 | 0.52563 | 18397.05 | 0.19981 | 2797.34 | 40000 | 0 | 11471.2 | 6925.85 | 0 | 2797.34 | 9723.19 | 0 | 0 | 0 | 0 |  |  | max % CF | load %CF | batt %CF | unused% | cost M$ | cent/kWh
2022010210 | 1 | 0.65706 | 52564.8 | 0 | 0 | 0.46166 | 16158.1 | 0.58937 | 8251.18 | 40000 | 0 | 12564.8 | 3593.3 | 0 | 8251.18 | 11844.48 | 0 | 0 | 0 | 0 |  | Hydro | 0 | 0 | not allowed | 0 | 0 | 0
2022010211 | 1 | 0.65519 | 52415.2 | 0 | 0 | 0.38041 | 13314.35 | 0.6689 | 9364.6 | 40000 | 0 | 12415.2 | 899.15 | 0 | 9364.6 | 10263.75 | 0 | 0 | 0 | 0 |  | Nuclear | 100 | 98.7457 | 0.0868 | 1.1675 | 28346.4508 | 8.1853
2022010212 | 1 | 0.64415 | 51532 | 0 | 0 | 0.31874 | 11155.9 | 0.64915 | 9088.1 | 40000 | 0 | 11155.9 | 0 | 376.1 | 8712 | 8712 | 0 | 0 | 0 | 0 |  | Wind | 34.4573 | 16.2755 | 15.9631 | 2.2188 | 6052.9 | 6.1244
2022010213 | 1 | 0.62951 | 50360.8 | 0 | 0 | 0.30735 | 10757.25 | 0.66737 | 9343.18 | 40000 | 0 | 10360.8 | 396.45 | 0 | 9343.18 | 9739.63 | 0 | 0 | 0 | 0 |  | Solar | 23.4628 | 11.5844 | 2.7248 | 9.1536 | 1699.88 | 9.6866
2022010214 | 1 | 0.60784 | 48627.2 | 0 | 0 | 0.28154 | 9853.9 | 0.69465 | 9725.1 | 40000 | 0 | 8627.2 | 1226.7 | 0 | 9725.1 | 10951.8 | 0 | 0 | 0 | 0 |  | Battery |  |  |  |  | 0 | 0
2022010215 | 1 | 0.58894 | 47115.2 | 0 | 0 | 0.25397 | 8888.95 | 0.72893 | 10205.02 | 40000 | 0 | 7115.2 | 1773.75 | 0 | 10205.02 | 11978.77 | 0 | 0 | 0 | 0 |  | GasPeak | 100 | 9.6332 |  | 90.3668 | 3464.4081 | 16.1736
2022010216 | 1 | 0.57791 | 46232.8 | 0 | 0 | 0.22273 | 7795.55 | 0.73272 | 10258.08 | 40000 | 0 | 6232.8 | 1562.75 | 0 | 10258.08 | 11820.83 | 0 | 0 | 0 | 0 | [5 empty] | total | 39563.6389
2022010217 | 1 | 0.57907 | 46325.6 | 0 | 0 | 0.1807 | 6324.5 | 0.5544 | 7761.6 | 40000 | 0 | 6324.5 | 0 | 1.1 | 7760.5 | 7760.5 | 0 | 0 | 0 | 0
2022010218 | 1 | 0.6104 | 48832 | 0 | 0 | 0.14866 | 5203.1 | 0.10251 | 1435.14 | 40000 | 0 | 5203.1 | 0 | 1435.14 | 0 | 0 | 2193.76 | 0 | 0 | 2193.76
2022010219 | 1 | 0.64731 | 51784.8 | 0 | 0 | 0.14265 | 4992.75 | 0 | 0 | 40000 | 0 | 4992.75 | 0 | 0 | 0 | 0 | 6792.05 | 0 | 0 | 6792.05
2022010220 | 1 | 0.6561 | 52488 | 0 | 0 | 0.14091 | 4931.85 | 0 | 0 | 40000 | 0 | 4931.85 | 0 | 0 | 0 | 0 | 7556.15 | 0 | 0 | 7556.15
2022010221 | 1 | 0.65547 | 52437.6 | 0 | 0 | 0.14422 | 5047.7 | 0 | 0 | 40000 | 0 | 5047.7 | 0 | 0 | 0 | 0 | 7389.9 | 0 | 0 | 7389.9
2022010222 | 1 | 0.65153 | 52122.4 | 0 | 0 | 0.14561 | 5096.35 | 0 | 0 | 40000 | 0 | 5096.35 | 0 | 0 | 0 | 0 | 7026.05 | 0 | 0 | 7026.05
2022010223 | 1 | 0.63521 | 50816.8 | 0 | 0 | 0.14364 | 5027.4 | 0 | 0 | 40000 | 0 | 5027.4 | 0 | 0 | 0 | 0 | 5789.4 | 0 | 0 | 5789.4
2022010224 | 1 | 0.61937 | 49549.6 | 0 | 0 | 0.14195 | 4968.25 | 0 | 0 | 40000 | 0 | 4968.25 | 0 | 0 | 0 | 0 | 4581.35 | 0 | 0 | 4581.35
2022010301 | 2 | 0.60764 | 48611.2 | 0 | 0 | 0.1436 | 5026 | 0 | 0 | 40000 | 0 | 5026 | 0 | 0 | 0 | 0 | 3585.2 | 0 | 0 | 3585.2
2022010302 | 2 | 0.60463 | 48370.4 | 0 | 0 | 0.14657 | 5129.95 | 0 | 0 | 40000 | 0 | 5129.95 | 0 | 0 | 0 | 0 | 3240.45 | 0 | 0 | 3240.45
2022010303 | 2 | 0.60608 | 48486.4 | 0 | 0 | 0.15007 | 5252.45 | 0 | 0 | 40000 | 0 | 5252.45 | 0 | 0 | 0 | 0 | 3233.95 | 0 | 0 | 3233.95
2022010304 | 2 | 0.61457 | 49165.6 | 0 | 0 | 0.15489 | 5421.15 | 0 | 0 | 40000 | 0 | 5421.15 | 0 | 0 | 0 | 0 | 3744.45 | 0 | 0 | 3744.45
2022010305 | 2 | 0.63087 | 50469.6 | 0 | 0 | 0.16599 | 5809.65 | 0 | 0 | 40000 | 0 | 5809.65 | 0 | 0 | 0 | 0 | 4659.95 | 0 | 0 | 4659.95
2022010306 | 2 | 0.6592 | 52736 | 0 | 0 | 0.18519 | 6481.65 | 0 | 0 | 40000 | 0 | 6481.65 | 0 | 0 | 0 | 0 | 6254.35 | 0 | 0 | 6254.35
2022010307 | 2 | 0.69698 | 55758.4 | 0 | 0 | 0.19196 | 6718.6 | 0 | 0 | 40000 | 0 | 6718.6 | 0 | 0 | 0 | 0 | 9039.8 | 0 | 0 | 9039.8
2022010308 | 2 | 0.72183 | 57746.4 | 0 | 0 | 0.2057 | 7199.5 | 0.00691 | 96.74 | 40000 | 0 | 7199.5 | 0 | 96.74 | 0 | 0 | 10450.16 | 0 | 0 | 10450.16
2022010309 | 2 | 0.7143 | 57144 | 0 | 0 | 0.22354 | 7823.9 | 0.27564 | 3858.96 | 40000 | 0 | 7823.9 | 0 | 3858.96 | 0 | 0 | 5461.14 | 0 | 0 | 5461.14
2022010310 | 2 | 0.68042 | 54433.6 | 0 | 0 | 0.16827 | 5889.45 | 0.71326 | 9985.64 | 40000 | 0 | 5889.45 | 0 | 8544.15 | 1441.49 | 1441.49 | 0 | 0 | 0 | 0
2022010311 | 2 | 0.645 | 51600 | 0 | 0 | 0.12364 | 4327.4 | 0.75983 | 10637.62 | 40000 | 0 | 4327.4 | 0 | 7272.6 | 3365.02 | 3365.02 | 0 | 0 | 0 | 0
2022010312 | 2 | 0.60996 | 48796.8 | 0 | 0 | 0.15141 | 5299.35 | 0.72612 | 10165.68 | 40000 | 0 | 5299.35 | 0 | 3497.45 | 6668.23 | 6668.23 | 0 | 0 | 0 | 0
2022010313 | 2 | 0.58021 | 46416.8 | 0 | 0 | 0.19036 | 6662.6 | 0.70442 | 9861.88 | 40000 | 0 | 6416.8 | 245.8 | 0 | 9861.88 | 10107.68 | 0 | 0 | 0 | 0
2022010314 | 2 | 0.55632 | 44505.6 | 0 | 0 | 0.21292 | 7452.2 | 0.71519 | 10012.66 | 40000 | 0 | 4505.6 | 2946.6 | 0 | 10012.66 | 12959.26 | 0 | 0 | 0 | 0
2022010315 | 2 | 0.53846 | 43076.8 | 0 | 0 | 0.23557 | 8244.95 | 0.74852 | 10479.28 | 40000 | 0 | 3076.8 | 5168.15 | 0 | 10479.28 | 15647.43 | 0 | 0 | 0 | 0
2022010316 | 2 | 0.53059 | 42447.2 | 0 | 0 | 0.2686 | 9401 | 0.71808 | 10053.12 | 40000 | 0 | 2447.2 | 6953.8 | 0 | 10053.12 | 17006.92 | 0 | 0 | 0 | 0
2022010317 | 2 | 0.53341 | 42672.8 | 0 | 0 | 0.28035 | 9812.25 | 0.44425 | 6219.5 | 40000 | 0 | 2672.8 | 7139.45 | 0 | 6219.5 | 13358.95 | 0 | 0 | 0 | 0
2022010318 | 2 | 0.56288 | 45030.4 | 0 | 0 | 0.28179 | 9862.65 | 0.06108 | 855.12 | 40000 | 0 | 5030.4 | 4832.25 | 0 | 855.12 | 5687.37 | 0 | 0 | 0 | 0
2022010319 | 2 | 0.6025 | 48200 | 0 | 0 | 0.38975 | 13641.25 | 0 | 0 | 40000 | 0 | 8200 | 5441.25 | 0 | 0 | 5441.25 | 0 | 0 | 0 | 0
2022010320 | 2 | 0.61435 | 49148 | 0 | 0 | 0.51913 | 18169.55 | 0 | 0 | 40000 | 0 | 9148 | 9021.55 | 0 | 0 | 9021.55 | 0 | 0 | 0 | 0
2022010321 | 2 | 0.61832 | 49465.6 | 0 | 0 | 0.6015 | 21052.5 | 0 | 0 | 40000 | 0 | 9465.6 | 11586.9 | 0 | 0 | 11586.9 | 0 | 0 | 0 | 0
2022010322 | 2 | 0.61047 | 48837.6 | 0 | 0 | 0.60641 | 21224.35 | 0 | 0 | 40000 | 0 | 8837.6 | 12386.75 | 0 | 0 | 12386.75 | 0 | 0 | 0 | 0
2022010323 | 2 | 0.59106 | 47284.8 | 0 | 0 | 0.60471 | 21164.85 | 0 | 0 | 40000 | 0 | 7284.8 | 13880.05 | 0 | 0 | 13880.05 | 0 | 0 | 0 | 0
2022010324 | 2 | 0.57014 | 45611.2 | 0 | 0 | 0.60316 | 21110.6 | 0 | 0 | 40000 | 0 | 5611.2 | 15499.4 | 0 | 0 | 15499.4 | 0 | 0 | 0 | 0
2022010401 | 3 | 0.55636 | 44508.8 | 0 | 0 | 0.59894 | 20962.9 | 0 | 0 | 40000 | 0 | 4508.8 | 16454.1 | 0 | 0 | 16454.1 | 0 | 0 | 0 | 0
2022010402 | 3 | 0.55052 | 44041.6 | 0 | 0 | 0.59187 | 20715.45 | 0 | 0 | 40000 | 0 | 4041.6 | 16673.85 | 0 | 0 | 16673.85 | 0 | 0 | 0 | 0
2022010403 | 3 | 0.55048 | 44038.4 | 0 | 0 | 0.57574 | 20150.9 | 0 | 0 | 40000 | 0 | 4038.4 | 16112.5 | 0 | 0 | 16112.5 | 0 | 0 | 0 | 0
2022010404 | 3 | 0.55703 | 44562.4 | 0 | 0 | 0.56376 | 19731.6 | 0 | 0 | 40000 | 0 | 4562.4 | 15169.2 | 0 | 0 | 15169.2 | 0 | 0 | 0 | 0
2022010405 | 3 | 0.57318 | 45854.4 | 0 | 0 | 0.56625 | 19818.75 | 0 | 0 | 40000 | 0 | 5854.4 | 13964.35 | 0 | 0 | 13964.35 | 0 | 0 | 0 | 0
2022010406 | 3 | 0.60514 | 48411.2 | 0 | 0 | 0.58296 | 20403.6 | 0 | 0 | 40000 | 0 | 8411.2 | 11992.4 | 0 | 0 | 11992.4 | 0 | 0 | 0 | 0
2022010407 | 3 | 0.64916 | 51932.8 | 0 | 0 | 0.57942 | 20279.7 | 0 | 0 | 40000 | 0 | 11932.8 | 8346.9 | 0 | 0 | 8346.9 | 0 | 0 | 0 | 0
2022010408 | 3 | 0.67235 | 53788 | 0 | 0 | 0.57188 | 20015.8 | 0.0054 | 75.6 | 40000 | 0 | 13788 | 6227.8 | 0 | 75.6 | 6303.4 | 0 | 0 | 0 | 0
2022010409 | 3 | 0.65968 | 52774.4 | 0 | 0 | 0.54659 | 19130.65 | 0.1368 | 1915.2 | 40000 | 0 | 12774.4 | 6356.25 | 0 | 1915.2 | 8271.45 | 0 | 0 | 0 | 0
2022010410 | 3 | 0.62828 | 50262.4 | 0 | 0 | 0.50122 | 17542.7 | 0.34842 | 4877.88 | 40000 | 0 | 10262.4 | 7280.3 | 0 | 4877.88 | 12158.18 | 0 | 0 | 0 | 0
2022010411 | 3 | 0.60042 | 48033.6 | 0 | 0 | 0.49452 | 17308.2 | 0.42653 | 5971.42 | 40000 | 0 | 8033.6 | 9274.6 | 0 | 5971.42 | 15246.02 | 0 | 0 | 0 | 0
2022010412 | 3 | 0.57371 | 45896.8 | 0 | 0 | 0.52668 | 18433.8 | 0.41488 | 5808.32 | 40000 | 0 | 5896.8 | 12537 | 0 | 5808.32 | 18345.32 | 0 | 0 | 0 | 0
2022010413 | 3 | 0.55268 | 44214.4 | 0 | 0 | 0.53609 | 18763.15 | 0.40206 | 5628.84 | 40000 | 0 | 4214.4 | 14548.75 | 0 | 5628.84 | 20177.59 | 0 | 0 | 0 | 0
2022010414 | 3 | 0.53596 | 42876.8 | 0 | 0 | 0.52981 | 18543.35 | 0.41692 | 5836.88 | 40000 | 0 | 2876.8 | 15666.55 | 0 | 5836.88 | 21503.43 | 0 | 0 | 0 | 0
2022010415 | 3 | 0.52256 | 41804.8 | 0 | 0 | 0.51598 | 18059.3 | 0.43 | 6020 | 40000 | 0 | 1804.8 | 16254.5 | 0 | 6020 | 22274.5 | 0 | 0 | 0 | 0
2022010416 | 3 | 0.51647 | 41317.6 | 0 | 0 | 0.49874 | 17455.9 | 0.46933 | 6570.62 | 40000 | 0 | 1317.6 | 16138.3 | 0 | 6570.62 | 22708.92 | 0 | 0 | 0 | 0
2022010417 | 3 | 0.51813 | 41450.4 | 0 | 0 | 0.4542 | 15897 | 0.48399 | 6775.86 | 40000 | 0 | 1450.4 | 14446.6 | 0 | 6775.86 | 21222.46 | 0 | 0 | 0 | 0
2022010418 | 3 | 0.53249 | 42599.2 | 0 | 0 | 0.40924 | 14323.4 | 0.10021 | 1402.94 | 40000 | 0 | 2599.2 | 11724.2 | 0 | 1402.94 | 13127.14 | 0 | 0 | 0 | 0
2022010419 | 3 | 0.55817 | 44653.6 | 0 | 0 | 0.43165 | 15107.75 | 0 | 0 | 40000 | 0 | 4653.6 | 10454.15 | 0 | 0 | 10454.15 | 0 | 0 | 0 | 0
2022010420 | 3 | 0.55639 | 44511.2 | 0 | 0 | 0.50108 | 17537.8 | 0 | 0 | 40000 | 0 | 4511.2 | 13026.6 | 0 | 0 | 13026.6 | 0 | 0 | 0 | 0
2022010421 | 3 | 0.55069 | 44055.2 | 0 | 0 | 0.52326 | 18314.1 | 0 | 0 | 40000 | 0 | 4055.2 | 14258.9 | 0 | 0 | 14258.9 | 0 | 0 | 0 | 0
2022010422 | 3 | 0.53491 | 42792.8 | 0 | 0 | 0.5209 | 18231.5 | 0 | 0 | 40000 | 0 | 2792.8 | 15438.7 | 0 | 0 | 15438.7 | 0 | 0 | 0 | 0
2022010423 | 3 | 0.51076 | 40860.8 | 0 | 0 | 0.51082 | 17878.7 | 0 | 0 | 40000 | 0 | 860.8 | 17017.9 | 0 | 0 | 17017.9 | 0 | 0 | 0 | 0
2022010424 | 3 | 0.48777 | 39021.6 | 0 | 0 | 0.47088 | 16480.8 | 0 | 0 | 39021.6 | 978.4 | 0 | 16480.8 | 0 | 0 | 17459.2 | 0 | 0 | 0 | 0
2022010501 | 4 | 0.47259 | 37807.2 | 0 | 0 | 0.4446 | 15561 | 0 | 0 | 37807.2 | 2192.8 | 0 | 15561 | 0 | 0 | 17753.8 | 0 | 0 | 0 | 0
2022010502 | 4 | 0.46655 | 37324 | 0 | 0 | 0.43209 | 15123.15 | 0 | 0 | 37324 | 2676 | 0 | 15123.15 | 0 | 0 | 17799.15 | 0 | 0 | 0 | 0
2022010503 | 4 | 0.46688 | 37350.4 | 0 | 0 | 0.42818 | 14986.3 | 0 | 0 | 37350.4 | 2649.6 | 0 | 14986.3 | 0 | 0 | 17635.9 | 0 | 0 | 0 | 0
2022010504 | 4 | 0.47322 | 37857.6 | 0 | 0 | 0.47859 | 16750.65 | 0 | 0 | 37857.6 | 2142.4 | 0 | 16750.65 | 0 | 0 | 18893.05 | 0 | 0 | 0 | 0
2022010505 | 4 | 0.48888 | 39110.4 | 0 | 0 | 0.50781 | 17773.35 | 0 | 0 | 39110.4 | 889.6 | 0 | 17773.35 | 0 | 0 | 18662.95 | 0 | 0 | 0 | 0
2022010506 | 4 | 0.51974 | 41579.2 | 0 | 0 | 0.5221 | 18273.5 | 0 | 0 | 40000 | 0 | 1579.2 | 16694.3 | 0 | 0 | 16694.3 | 0 | 0 | 0 | 0
2022010507 | 4 | 0.56468 | 45174.4 | 0 | 0 | 0.53246 | 18636.1 | 0 | 0 | 40000 | 0 | 5174.4 | 13461.7 | 0 | 0 | 13461.7 | 0 | 0 | 0 | 0
2022010508 | 4 | 0.58747 | 46997.6 | 0 | 0 | 0.53666 | 18783.1 | 0.00388 | 54.32 | 40000 | 0 | 6997.6 | 11785.5 | 0 | 54.32 | 11839.82 | 0 | 0 | 0 | 0
2022010509 | 4 | 0.57663 | 46130.4 | 0 | 0 | 0.48474 | 16965.9 | 0.23604 | 3304.56 | 40000 | 0 | 6130.4 | 10835.5 | 0 | 3304.56 | 14140.06 | 0 | 0 | 0 | 0
2022010510 | 4 | 0.55902 | 44721.6 | 0 | 0 | 0.39487 | 13820.45 | 0.65407 | 9156.98 | 40000 | 0 | 4721.6 | 9098.85 | 0 | 9156.98 | 18255.83 | 0 | 0 | 0 | 0
2022010511 | 4 | 0.54359 | 43487.2 | 0 | 0 | 0.32134 | 11246.9 | 0.71174 | 9964.36 | 40000 | 0 | 3487.2 | 7759.7 | 0 | 9964.36 | 17724.06 | 0 | 0 | 0 | 0
2022010512 | 4 | 0.52678 | 42142.4 | 0 | 0 | 0.22283 | 7799.05 | 0.69885 | 9783.9 | 40000 | 0 | 2142.4 | 5656.65 | 0 | 9783.9 | 15440.55 | 0 | 0 | 0 | 0
2022010513 | 4 | 0.51545 | 41236 | 0 | 0 | 0.14339 | 5018.65 | 0.68534 | 9594.76 | 40000 | 0 | 1236 | 3782.65 | 0 | 9594.76 | 13377.41 | 0 | 0 | 0 | 0
2022010514 | 4 | 0.50948 | 40758.4 | 0 | 0 | 0.09841 | 3444.35 | 0.69353 | 9709.42 | 40000 | 0 | 758.4 | 2685.95 | 0 | 9709.42 | 12395.37 | 0 | 0 | 0 | 0
2022010515 | 4 | 0.50818 | 40654.4 | 0 | 0 | 0.09058 | 3170.3 | 0.72225 | 10111.5 | 40000 | 0 | 654.4 | 2515.9 | 0 | 10111.5 | 12627.4 | 0 | 0 | 0 | 0
2022010516 | 4 | 0.50828 | 40662.4 | 0 | 0 | 0.09594 | 3357.9 | 0.72334 | 10126.76 | 40000 | 0 | 662.4 | 2695.5 | 0 | 10126.76 | 12822.26 | 0 | 0 | 0 | 0
2022010517 | 4 | 0.51143 | 40914.4 | 0 | 0 | 0.12188 | 4265.8 | 0.55665 | 7793.1 | 40000 | 0 | 914.4 | 3351.4 | 0 | 7793.1 | 11144.5 | 0 | 0 | 0 | 0
2022010518 | 4 | 0.52645 | 42116 | 0 | 0 | 0.133 | 4655 | 0.1105 | 1547 | 40000 | 0 | 2116 | 2539 | 0 | 1547 | 4086 | 0 | 0 | 0 | 0
2022010519 | 4 | 0.54817 | 43853.6 | 0 | 0 | 0.16463 | 5762.05 | 0 | 0 | 40000 | 0 | 3853.6 | 1908.45 | 0 | 0 | 1908.45 | 0 | 0 | 0 | 0
2022010520 | 4 | 0.54569 | 43655.2 | 0 | 0 | 0.19062 | 6671.7 | 0 | 0 | 40000 | 0 | 3655.2 | 3016.5 | 0 | 0 | 3016.5 | 0 | 0 | 0 | 0
2022010521 | 4 | 0.53979 | 43183.2 | 0 | 0 | 0.23184 | 8114.4 | 0 | 0 | 40000 | 0 | 3183.2 | 4931.2 | 0 | 0 | 4931.2 | 0 | 0 | 0 | 0
2022010522 | 4 | 0.52665 | 42132 | 0 | 0 | 0.28004 | 9801.4 | 0 | 0 | 40000 | 0 | 2132 | 7669.4 | 0 | 0 | 7669.4 | 0 | 0 | 0 | 0
2022010523 | 4 | 0.50467 | 40373.6 | 0 | 0 | 0.34716 | 12150.6 | 0 | 0 | 40000 | 0 | 373.6 | 11777 | 0 | 0 | 11777 | 0 | 0 | 0 | 0
2022010524 | 4 | 0.48256 | 38604.8 | 0 | 0 | 0.41695 | 14593.25 | 0 | 0 | 38604.8 | 1395.2 | 0 | 14593.25 | 0 | 0 | 15988.45 | 0 | 0 | 0 | 0
2022010601 | 5 | 0.46938 | 37550.4 | 0 | 0 | 0.43334 | 15166.9 | 0 | 0 | 37550.4 | 2449.6 | 0 | 15166.9 | 0 | 0 | 17616.5 | 0 | 0 | 0 | 0
2022010602 | 5 | 0.46467 | 37173.6 | 0 | 0 | 0.44907 | 15717.45 | 0 | 0 | 37173.6 | 2826.4 | 0 | 15717.45 | 0 | 0 | 18543.85 | 0 | 0 | 0 | 0
2022010603 | 5 | 0.46721 | 37376.8 | 0 | 0 | 0.46328 | 16214.8 | 0 | 0 | 37376.8 | 2623.2 | 0 | 16214.8 | 0 | 0 | 18838 | 0 | 0 | 0 | 0
2022010604 | 5 | 0.47419 | 37935.2 | 0 | 0 | 0.43692 | 15292.2 | 0 | 0 | 37935.2 | 2064.8 | 0 | 15292.2 | 0 | 0 | 17357 | 0 | 0 | 0 | 0
2022010605 | 5 | 0.49017 | 39213.6 | 0 | 0 | 0.48463 | 16962.05 | 0 | 0 | 39213.6 | 786.4 | 0 | 16962.05 | 0 | 0 | 17748.45 | 0 | 0 | 0 | 0
2022010606 | 5 | 0.52636 | 42108.8 | 0 | 0 | 0.53376 | 18681.6 | 0 | 0 | 40000 | 0 | 2108.8 | 16572.8 | 0 | 0 | 16572.8 | 0 | 0 | 0 | 0
2022010607 | 5 | 0.57531 | 46024.8 | 0 | 0 | 0.57179 | 20012.65 | 0 | 0 | 40000 | 0 | 6024.8 | 13987.85 | 0 | 0 | 13987.85 | 0 | 0 | 0 | 0
2022010608 | 5 | 0.6048 | 48384 | 0 | 0 | 0.59376 | 20781.6 | 0.00374 | 52.36 | 40000 | 0 | 8384 | 12397.6 | 0 | 52.36 | 12449.96 | 0 | 0 | 0 | 0
2022010609 | 5 | 0.60699 | 48559.2 | 0 | 0 | 0.57294 | 20052.9 | 0.14311 | 2003.54 | 40000 | 0 | 8559.2 | 11493.7 | 0 | 2003.54 | 13497.24 | 0 | 0 | 0 | 0
2022010610 | 5 | 0.60339 | 48271.2 | 0 | 0 | 0.53261 | 18641.35 | 0.32911 | 4607.54 | 40000 | 0 | 8271.2 | 10370.15 | 0 | 4607.54 | 14977.69 | 0 | 0 | 0 | 0
2022010611 | 5 | 0.59792 | 47833.6 | 0 | 0 | 0.50041 | 17514.35 | 0.45868 | 6421.52 | 40000 | 0 | 7833.6 | 9680.75 | 0 | 6421.52 | 16102.27 | 0 | 0 | 0 | 0
2022010612 | 5 | 0.59083 | 47266.4 | 0 | 0 | 0.45285 | 15849.75 | 0.60042 | 8405.88 | 40000 | 0 | 7266.4 | 8583.35 | 0 | 8405.88 | 16989.23 | 0 | 0 | 0 | 0
2022010613 | 5 | 0.58181 | 46544.8 | 0 | 0 | 0.4081 | 14283.5 | 0.6901 | 9661.4 | 40000 | 0 | 6544.8 | 7738.7 | 0 | 9661.4 | 17400.1 | 0 | 0 | 0 | 0
2022010614 | 5 | 0.57344 | 45875.2 | 0 | 0 | 0.31856 | 11149.6 | 0.71467 | 10005.38 | 40000 | 0 | 5875.2 | 5274.4 | 0 | 10005.38 | 15279.78 | 0 | 0 | 0 | 0
2022010615 | 5 | 0.56747 | 45397.6 | 0 | 0 | 0.23731 | 8305.85 | 0.74839 | 10477.46 | 40000 | 0 | 5397.6 | 2908.25 | 0 | 10477.46 | 13385.71 | 0 | 0 | 0 | 0
2022010616 | 5 | 0.56517 | 45213.6 | 0 | 0 | 0.2006 | 7021 | 0.73887 | 10344.18 | 40000 | 0 | 5213.6 | 1807.4 | 0 | 10344.18 | 12151.58 | 0 | 0 | 0 | 0
2022010617 | 5 | 0.57441 | 45952.8 | 0 | 0 | 0.17672 | 6185.2 | 0.55097 | 7713.58 | 40000 | 0 | 5952.8 | 232.4 | 0 | 7713.58 | 7945.98 | 0 | 0 | 0 | 0
2022010618 | 5 | 0.60116 | 48092.8 | 0 | 0 | 0.17775 | 6221.25 | 0.11669 | 1633.66 | 40000 | 0 | 6221.25 | 0 | 1633.66 | 0 | 0 | 237.89 | 0 | 0 | 237.89
2022010619 | 5 | 0.63522 | 50817.6 | 0 | 0 | 0.21454 | 7508.9 | 7e-05 | 0.98 | 40000 | 0 | 7508.9 | 0 | 0.98 | 0 | 0 | 3307.72 | 0 | 0 | 3307.72
2022010620 | 5 | 0.64013 | 51210.4 | 0 | 0 | 0.25706 | 8997.1 | 0 | 0 | 40000 | 0 | 8997.1 | 0 | 0 | 0 | 0 | 2213.3 | 0 | 0 | 2213.3
2022010621 | 5 | 0.63978 | 51182.4 | 0 | 0 | 0.27986 | 9795.1 | 0 | 0 | 40000 | 0 | 9795.1 | 0 | 0 | 0 | 0 | 1387.3 | 0 | 0 | 1387.3
2022010622 | 5 | 0.63114 | 50491.2 | 0 | 0 | 0.29415 | 10295.25 | 0 | 0 | 40000 | 0 | 10295.25 | 0 | 0 | 0 | 0 | 195.95 | 0 | 0 | 195.95
2022010623 | 5 | 0.61124 | 48899.2 | 0 | 0 | 0.28612 | 10014.2 | 0 | 0 | 40000 | 0 | 8899.2 | 1115 | 0 | 0 | 1115 | 0 | 0 | 0 | 0
2022010624 | 5 | 0.59533 | 47626.4 | 0 | 0 | 0.27991 | 9796.85 | 0 | 0 | 40000 | 0 | 7626.4 | 2170.45 | 0 | 0 | 2170.45 | 0 | 0 | 0 | 0
2022010701 | 6 | 0.58485 | 46788 | 0 | 0 | 0.2689 | 9411.5 | 0 | 0 | 40000 | 0 | 6788 | 2623.5 | 0 | 0 | 2623.5 | 0 | 0 | 0 | 0
2022010702 | 6 | 0.58259 | 46607.2 | 0 | 0 | 0.26463 | 9262.05 | 0 | 0 | 40000 | 0 | 6607.2 | 2654.85 | 0 | 0 | 2654.85 | 0 | 0 | 0 | 0
2022010703 | 6 | 0.58472 | 46777.6 | 0 | 0 | 0.26121 | 9142.35 | 0 | 0 | 40000 | 0 | 6777.6 | 2364.75 | 0 | 0 | 2364.75 | 0 | 0 | 0 | 0
2022010704 | 6 | 0.59424 | 47539.2 | 0 | 0 | 0.25053 | 8768.55 | 0 | 0 | 40000 | 0 | 7539.2 | 1229.35 | 0 | 0 | 1229.35 | 0 | 0 | 0 | 0
2022010705 | 6 | 0.61062 | 48849.6 | 0 | 0 | 0.25205 | 8821.75 | 0 | 0 | 40000 | 0 | 8821.75 | 0 | 0 | 0 | 0 | 27.85 | 0 | 0 | 27.85
2022010706 | 6 | 0.6437 | 51496 | 0 | 0 | 0.26041 | 9114.35 | 0 | 0 | 40000 | 0 | 9114.35 | 0 | 0 | 0 | 0 | 2381.65 | 0 | 0 | 2381.65
2022010707 | 6 | 0.68858 | 55086.4 | 0 | 0 | 0.25838 | 9043.3 | 0 | 0 | 40000 | 0 | 9043.3 | 0 | 0 | 0 | 0 | 6043.1 | 0 | 0 | 6043.1
2022010708 | 6 | 0.71202 | 56961.6 | 0 | 0 | 0.2584 | 9044 | 0.0029 | 40.6 | 40000 | 0 | 9044 | 0 | 40.6 | 0 | 0 | 7877 | 0 | 0 | 7877
2022010709 | 6 | 0.70991 | 56792.8 | 0 | 0 | 0.23175 | 8111.25 | 0.20939 | 2931.46 | 40000 | 0 | 8111.25 | 0 | 2931.46 | 0 | 0 | 5750.09 | 0 | 0 | 5750.09
2022010710 | 6 | 0.69669 | 55735.2 | 0 | 0 | 0.18403 | 6441.05 | 0.60885 | 8523.9 | 40000 | 0 | 6441.05 | 0 | 8523.9 | 0 | 0 | 770.25 | 0 | 0 | 770.25
2022010711 | 6 | 0.67827 | 54261.6 | 0 | 0 | 0.18092 | 6332.2 | 0.66993 | 9379.02 | 40000 | 0 | 6332.2 | 0 | 7929.4 | 1449.62 | 1449.62 | 0 | 0 | 0 | 0
2022010712 | 6 | 0.65522 | 52417.6 | 0 | 0 | 0.20451 | 7157.85 | 0.64978 | 9096.92 | 40000 | 0 | 7157.85 | 0 | 5259.75 | 3837.17 | 3837.17 | 0 | 0 | 0 | 0
2022010713 | 6 | 0.63208 | 50566.4 | 0 | 0 | 0.24803 | 8681.05 | 0.63638 | 8909.32 | 40000 | 0 | 8681.05 | 0 | 1885.35 | 7023.97 | 7023.97 | 0 | 0 | 0 | 0
2022010714 | 6 | 0.616 | 49280 | 0 | 0 | 0.29461 | 10311.35 | 0.62728 | 8781.92 | 40000 | 0 | 9280 | 1031.35 | 0 | 8781.92 | 9813.27 | 0 | 0 | 0 | 0
2022010715 | 6 | 0.60507 | 48405.6 | 0 | 0 | 0.32405 | 11341.75 | 0.63264 | 8856.96 | 40000 | 0 | 8405.6 | 2936.15 | 0 | 8856.96 | 11793.11 | 0 | 0 | 0 | 0
2022010716 | 6 | 0.60758 | 48606.4 | 0 | 0 | 0.35278 | 12347.3 | 0.62321 | 8724.94 | 40000 | 0 | 8606.4 | 3740.9 | 0 | 8724.94 | 12465.84 | 0 | 0 | 0 | 0
2022010717 | 6 | 0.61528 | 49222.4 | 0 | 0 | 0.38388 | 13435.8 | 0.48484 | 6787.76 | 40000 | 0 | 9222.4 | 4213.4 | 0 | 6787.76 | 11001.16 | 0 | 0 | 0 | 0
2022010718 | 6 | 0.62665 | 50132 | 0 | 0 | 0.40896 | 14313.6 | 0.11119 | 1556.66 | 40000 | 0 | 10132 | 4181.6 | 0 | 1556.66 | 5738.26 | 0 | 0 | 0 | 0
2022010719 | 6 | 0.64017 | 51213.6 | 0 | 0 | 0.50167 | 17558.45 | 9e-05 | 1.26 | 40000 | 0 | 11213.6 | 6344.85 | 0 | 1.26 | 6346.11 | 0 | 0 | 0 | 0
2022010720 | 6 | 0.6328 | 50624 | 0 | 0 | 0.57189 | 20016.15 | 0 | 0 | 40000 | 0 | 10624 | 9392.15 | 0 | 0 | 9392.15 | 0 | 0 | 0 | 0
2022010721 | 6 | 0.61957 | 49565.6 | 0 | 0 | 0.56964 | 19937.4 | 0 | 0 | 40000 | 0 | 9565.6 | 10371.8 | 0 | 0 | 10371.8 | 0 | 0 | 0 | 0
2022010722 | 6 | 0.60063 | 48050.4 | 0 | 0 | 0.57402 | 20090.7 | 0 | 0 | 40000 | 0 | 8050.4 | 12040.3 | 0 | 0 | 12040.3 | 0 | 0 | 0 | 0
2022010723 | 6 | 0.57512 | 46009.6 | 0 | 0 | 0.57121 | 19992.35 | 0 | 0 | 40000 | 0 | 6009.6 | 13982.75 | 0 | 0 | 13982.75 | 0 | 0 | 0 | 0
2022010724 | 6 | 0.55 | 44000 | 0 | 0 | 0.56851 | 19897.85 | 0 | 0 | 40000 | 0 | 4000 | 15897.85 | 0 | 0 | 15897.85 | 0 | 0 | 0 | 0
2022010801 | 7 | 0.52779 | 42223.2 | 0 | 0 | 0.56389 | 19736.15 | 0 | 0 | 40000 | 0 | 2223.2 | 17512.95 | 0 | 0 | 17512.95 | 0 | 0 | 0 | 0
2022010802 | 7 | 0.51423 | 41138.4 | 0 | 0 | 0.55874 | 19555.9 | 0 | 0 | 40000 | 0 | 1138.4 | 18417.5 | 0 | 0 | 18417.5 | 0 | 0 | 0 | 0
2022010803 | 7 | 0.50499 | 40399.2 | 0 | 0 | 0.55732 | 19506.2 | 0 | 0 | 40000 | 0 | 399.2 | 19107 | 0 | 0 | 19107 | 0 | 0 | 0 | 0
2022010804 | 7 | 0.50118 | 40094.4 | 0 | 0 | 0.55606 | 19462.1 | 0 | 0 | 40000 | 0 | 94.4 | 19367.7 | 0 | 0 | 19367.7 | 0 | 0 | 0 | 0
2022010805 | 7 | 0.50042 | 40033.6 | 0 | 0 | 0.5556 | 19446 | 0 | 0 | 40000 | 0 | 33.6 | 19412.4 | 0 | 0 | 19412.4 | 0 | 0 | 0 | 0
2022010806 | 7 | 0.50747 | 40597.6 | 0 | 0 | 0.54638 | 19123.3 | 0 | 0 | 40000 | 0 | 597.6 | 18525.7 | 0 | 0 | 18525.7 | 0 | 0 | 0 | 0
2022010807 | 7 | 0.51935 | 41548 | 0 | 0 | 0.52416 | 18345.6 | 0 | 0 | 40000 | 0 | 1548 | 16797.6 | 0 | 0 | 16797.6 | 0 | 0 | 0 | 0
2022010808 | 7 | 0.53227 | 42581.6 | 0 | 0 | 0.51296 | 17953.6 | 0.00058 | 8.12 | 40000 | 0 | 2581.6 | 15372 | 0 | 8.12 | 15380.12 | 0 | 0 | 0 | 0
2022010809 | 7 | 0.54664 | 43731.2 | 0 | 0 | 0.51136 | 17897.6 | 0.13418 | 1878.52 | 40000 | 0 | 3731.2 | 14166.4 | 0 | 1878.52 | 16044.92 | 0 | 0 | 0 | 0
2022010810 | 7 | 0.55593 | 44474.4 | 0 | 0 | 0.45729 | 16005.15 | 0.33434 | 4680.76 | 40000 | 0 | 4474.4 | 11530.75 | 0 | 4680.76 | 16211.51 | 0 | 0 | 0 | 0
2022010811 | 7 | 0.56022 | 44817.6 | 0 | 0 | 0.42901 | 15015.35 | 0.46122 | 6457.08 | 40000 | 0 | 4817.6 | 10197.75 | 0 | 6457.08 | 16654.83 | 0 | 0 | 0 | 0
2022010812 | 7 | 0.55682 | 44545.6 | 0 | 0 | 0.41683 | 14589.05 | 0.51149 | 7160.86 | 40000 | 0 | 4545.6 | 10043.45 | 0 | 7160.86 | 17204.31 | 0 | 0 | 0 | 0
2022010813 | 7 | 0.5501 | 44008 | 0 | 0 | 0.41724 | 14603.4 | 0.51636 | 7229.04 | 40000 | 0 | 4008 | 10595.4 | 0 | 7229.04 | 17824.44 | 0 | 0 | 0 | 0
2022010814 | 7 | 0.54064 | 43251.2 | 0 | 0 | 0.41573 | 14550.55 | 0.49328 | 6905.92 | 40000 | 0 | 3251.2 | 11299.35 | 0 | 6905.92 | 18205.27 | 0 | 0 | 0 | 0
2022010815 | 7 | 0.53087 | 42469.6 | 0 | 0 | 0.40179 | 14062.65 | 0.53532 | 7494.48 | 40000 | 0 | 2469.6 | 11593.05 | 0 | 7494.48 | 19087.53 | 0 | 0 | 0 | 0
2022010816 | 7 | 0.52363 | 41890.4 | 0 | 0 | 0.39404 | 13791.4 | 0.56412 | 7897.68 | 40000 | 0 | 1890.4 | 11901 | 0 | 7897.68 | 19798.68 | 0 | 0 | 0 | 0
2022010817 | 7 | 0.52128 | 41702.4 | 0 | 0 | 0.4025 | 14087.5 | 0.46423 | 6499.22 | 40000 | 0 | 1702.4 | 12385.1 | 0 | 6499.22 | 18884.32 | 0 | 0 | 0 | 0
2022010818 | 7 | 0.52614 | 42091.2 | 0 | 0 | 0.36453 | 12758.55 | 0.12758 | 1786.12 | 40000 | 0 | 2091.2 | 10667.35 | 0 | 1786.12 | 12453.47 | 0 | 0 | 0 | 0
2022010819 | 7 | 0.53425 | 42740 | 0 | 0 | 0.35636 | 12472.6 | 0.02108 | 295.12 | 40000 | 0 | 2740 | 9732.6 | 0 | 295.12 | 10027.72 | 0 | 0 | 0 | 0
2022010820 | 7 | 0.52696 | 42156.8 | 0 | 0 | 0.39954 | 13983.9 | 0.00608 | 85.12 | 40000 | 0 | 2156.8 | 11827.1 | 0 | 85.12 | 11912.22 | 0 | 0 | 0 | 0
2022010821 | 7 | 0.51602 | 41281.6 | 0 | 0 | 0.45898 | 16064.3 | 0 | 0 | 40000 | 0 | 1281.6 | 14782.7 | 0 | 0 | 14782.7 | 0 | 0 | 0 | 0
2022010822 | 7 | 0.50474 | 40379.2 | 0 | 0 | 0.50275 | 17596.25 | 0 | 0 | 40000 | 0 | 379.2 | 17217.05 | 0 | 0 | 17217.05 | 0 | 0 | 0 | 0
2022010823 | 7 | 0.48837 | 39069.6 | 0 | 0 | 0.53517 | 18730.95 | 0 | 0 | 39069.6 | 930.4 | 0 | 18730.95 | 0 | 0 | 19661.35 | 0 | 0 | 0 | 0
2022010824 | 7 | 0.46887 | 37509.6 | 0 | 0 | 0.51555 | 18044.25 | 0 | 0 | 37509.6 | 2490.4 | 0 | 18044.25 | 0 | 0 | 20534.65 | 0 | 0 | 0 | 0
2022010901 | 1 | 0.45116 | 36092.8 | 0 | 0 | 0.49398 | 17289.3 | 0 | 0 | 36092.8 | 3907.2 | 0 | 17289.3 | 0 | 0 | 21196.5 | 0 | 0 | 0 | 0
2022010902 | 1 | 0.43923 | 35138.4 | 0 | 0 | 0.50027 | 17509.45 | 0 | 0 | 35138.4 | 4861.6 | 0 | 17509.45 | 0 | 0 | 22371.05 | 0 | 0 | 0 | 0
2022010903 | 1 | 0.4333 | 34664 | 0 | 0 | 0.52784 | 18474.4 | 0 | 0 | 34664 | 5336 | 0 | 18474.4 | 0 | 0 | 23810.4 | 0 | 0 | 0 | 0
2022010904 | 1 | 0.43208 | 34566.4 | 0 | 0 | 0.55528 | 19434.8 | 0 | 0 | 34566.4 | 5433.6 | 0 | 19434.8 | 0 | 0 | 24868.4 | 0 | 0 | 0 | 0
2022010905 | 1 | 0.43289 | 34631.2 | 0 | 0 | 0.5665 | 19827.5 | 0 | 0 | 34631.2 | 5368.8 | 0 | 19827.5 | 0 | 0 | 25196.3 | 0 | 0 | 0 | 0
2022010906 | 1 | 0.4399 | 35192 | 0 | 0 | 0.58852 | 20598.2 | 0 | 0 | 35192 | 4808 | 0 | 20598.2 | 0 | 0 | 25406.2 | 0 | 0 | 0 | 0
2022010907 | 1 | 0.45152 | 36121.6 | 0 | 0 | 0.59525 | 20833.75 | 0 | 0 | 36121.6 | 3878.4 | 0 | 20833.75 | 0 | 0 | 24712.15 | 0 | 0 | 0 | 0
2022010908 | 1 | 0.46606 | 37284.8 | 0 | 0 | 0.59738 | 20908.3 | 0.00135 | 18.9 | 37284.8 | 2715.2 | 0 | 20908.3 | 0 | 18.9 | 23642.4 | 0 | 0 | 0 | 0
2022010909 | 1 | 0.48308 | 38646.4 | 0 | 0 | 0.58704 | 20546.4 | 0.05031 | 704.34 | 38646.4 | 1353.6 | 0 | 20546.4 | 0 | 704.34 | 22604.34 | 0 | 0 | 0 | 0
2022010910 | 1 | 0.50299 | 40239.2 | 0 | 0 | 0.56178 | 19662.3 | 0.11767 | 1647.38 | 40000 | 0 | 239.2 | 19423.1 | 0 | 1647.38 | 21070.48 | 0 | 0 | 0 | 0
2022010911 | 1 | 0.51795 | 41436 | 0 | 0 | 0.5616 | 19656 | 0.16042 | 2245.88 | 40000 | 0 | 1436 | 18220 | 0 | 2245.88 | 20465.88 | 0 | 0 | 0 | 0
2022010912 | 1 | 0.52877 | 42301.6 | 0 | 0 | 0.55322 | 19362.7 | 0.24336 | 3407.04 | 40000 | 0 | 2301.6 | 17061.1 | 0 | 3407.04 | 20468.14 | 0 | 0 | 0 | 0
2022010913 | 1 | 0.5316 | 42528 | 0 | 0 | 0.51374 | 17980.9 | 0.35837 | 5017.18 | 40000 | 0 | 2528 | 15452.9 | 0 | 5017.18 | 20470.08 | 0 | 0 | 0 | 0
2022010914 | 1 | 0.53366 | 42692.8 | 0 | 0 | 0.50723 | 17753.05 | 0.42775 | 5988.5 | 40000 | 0 | 2692.8 | 15060.25 | 0 | 5988.5 | 21048.75 | 0 | 0 | 0 | 0
2022010915 | 1 | 0.53116 | 42492.8 | 0 | 0 | 0.49061 | 17171.35 | 0.43372 | 6072.08 | 40000 | 0 | 2492.8 | 14678.55 | 0 | 6072.08 | 20750.63 | 0 | 0 | 0 | 0
2022010916 | 1 | 0.52676 | 42140.8 | 0 | 0 | 0.49973 | 17490.55 | 0.36632 | 5128.48 | 40000 | 0 | 2140.8 | 15349.75 | 0 | 5128.48 | 20478.23 | 0 | 0 | 0 | 0
2022010917 | 1 | 0.52776 | 42220.8 | 0 | 0 | 0.4939 | 17286.5 | 0.23419 | 3278.66 | 40000 | 0 | 2220.8 | 15065.7 | 0 | 3278.66 | 18344.36 | 0 | 0 | 0 | 0
2022010918 | 1 | 0.54314 | 43451.2 | 0 | 0 | 0.47054 | 16468.9 | 0.04226 | 591.64 | 40000 | 0 | 3451.2 | 13017.7 | 0 | 591.64 | 13609.34 | 0 | 0 | 0 | 0
2022010919 | 1 | 0.56608 | 45286.4 | 0 | 0 | 0.4538 | 15883 | 0 | 0 | 40000 | 0 | 5286.4 | 10596.6 | 0 | 0 | 10596.6 | 0 | 0 | 0 | 0
2022010920 | 1 | 0.56886 | 45508.8 | 0 | 0 | 0.47963 | 16787.05 | 0 | 0 | 40000 | 0 | 5508.8 | 11278.25 | 0 | 0 | 11278.25 | 0 | 0 | 0 | 0
2022010921 | 1 | 0.56273 | 45018.4 | 0 | 0 | 0.48162 | 16856.7 | 0 | 0 | 40000 | 0 | 5018.4 | 11838.3 | 0 | 0 | 11838.3 | 0 | 0 | 0 | 0
2022010922 | 1 | 0.55094 | 44075.2 | 0 | 0 | 0.50316 | 17610.6 | 0 | 0 | 40000 | 0 | 4075.2 | 13535.4 | 0 | 0 | 13535.4 | 0 | 0 | 0 | 0
2022010923 | 1 | 0.52934 | 42347.2 | 0 | 0 | 0.47255 | 16539.25 | 0 | 0 | 40000 | 0 | 2347.2 | 14192.05 | 0 | 0 | 14192.05 | 0 | 0 | 0 | 0
2022010924 | 1 | 0.50858 | 40686.4 | 0 | 0 | 0.44659 | 15630.65 | 0 | 0 | 40000 | 0 | 686.4 | 14944.25 | 0 | 0 | 14944.25 | 0 | 0 | 0 | 0
2022011001 | 2 | 0.49479 | 39583.2 | 0 | 0 | 0.42945 | 15030.75 | 0 | 0 | 39583.2 | 416.8 | 0 | 15030.75 | 0 | 0 | 15447.55 | 0 | 0 | 0 | 0
2022011002 | 2 | 0.49103 | 39282.4 | 0 | 0 | 0.41829 | 14640.15 | 0 | 0 | 39282.4 | 717.6 | 0 | 14640.15 | 0 | 0 | 15357.75 | 0 | 0 | 0 | 0
2022011003 | 2 | 0.49345 | 39476 | 0 | 0 | 0.40851 | 14297.85 | 0 | 0 | 39476 | 524 | 0 | 14297.85 | 0 | 0 | 14821.85 | 0 | 0 | 0 | 0
2022011004 | 2 | 0.50022 | 40017.6 | 0 | 0 | 0.40016 | 14005.6 | 0 | 0 | 40000 | 0 | 17.6 | 13988 | 0 | 0 | 13988 | 0 | 0 | 0 | 0
2022011005 | 2 | 0.51712 | 41369.6 | 0 | 0 | 0.34294 | 12002.9 | 0 | 0 | 40000 | 0 | 1369.6 | 10633.3 | 0 | 0 | 10633.3 | 0 | 0 | 0 | 0
2022011006 | 2 | 0.55359 | 44287.2 | 0 | 0 | 0.32968 | 11538.8 | 0 | 0 | 40000 | 0 | 4287.2 | 7251.6 | 0 | 0 | 7251.6 | 0 | 0 | 0 | 0
2022011007 | 2 | 0.60716 | 48572.8 | 0 | 0 | 0.32267 | 11293.45 | 0 | 0 | 40000 | 0 | 8572.8 | 2720.65 | 0 | 0 | 2720.65 | 0 | 0 | 0 | 0
2022011008 | 2 | 0.63906 | 51124.8 | 0 | 0 | 0.27499 | 9624.65 | 0.00343 | 48.02 | 40000 | 0 | 9624.65 | 0 | 48.02 | 0 | 0 | 1452.13 | 0 | 0 | 1452.13
2022011009 | 2 | 0.64012 | 51209.6 | 0 | 0 | 0.23003 | 8051.05 | 0.11373 | 1592.22 | 40000 | 0 | 8051.05 | 0 | 1592.22 | 0 | 0 | 1566.33 | 0 | 0 | 1566.33
2022011010 | 2 | 0.62526 | 50020.8 | 0 | 0 | 0.18591 | 6506.85 | 0.3229 | 4520.6 | 40000 | 0 | 6506.85 | 0 | 3513.95 | 1006.65 | 1006.65 | 0 | 0 | 0 | 0
2022011011 | 2 | 0.60658 | 48526.4 | 0 | 0 | 0.15808 | 5532.8 | 0.40032 | 5604.48 | 40000 | 0 | 5532.8 | 0 | 2993.6 | 2610.88 | 2610.88 | 0 | 0 | 0 | 0
2022011012 | 2 | 0.58501 | 46800.8 | 0 | 0 | 0.14008 | 4902.8 | 0.49136 | 6879.04 | 40000 | 0 | 4902.8 | 0 | 1898 | 4981.04 | 4981.04 | 0 | 0 | 0 | 0
2022011013 | 2 | 0.56504 | 45203.2 | 0 | 0 | 0.11889 | 4161.15 | 0.49715 | 6960.1 | 40000 | 0 | 4161.15 | 0 | 1042.05 | 5918.05 | 5918.05 | 0 | 0 | 0 | 0
2022011014 | 2 | 0.54923 | 43938.4 | 0 | 0 | 0.11353 | 3973.55 | 0.50225 | 7031.5 | 40000 | 0 | 3938.4 | 35.15 | 0 | 7031.5 | 7066.65 | 0 | 0 | 0 | 0
2022011015 | 2 | 0.534 | 42720 | 0 | 0 | 0.1129 | 3951.5 | 0.51852 | 7259.28 | 40000 | 0 | 2720 | 1231.5 | 0 | 7259.28 | 8490.78 | 0 | 0 | 0 | 0
2022011016 | 2 | 0.52596 | 42076.8 | 0 | 0 | 0.10656 | 3729.6 | 0.41455 | 5803.7 | 40000 | 0 | 2076.8 | 1652.8 | 0 | 5803.7 | 7456.5 | 0 | 0 | 0 | 0
2022011017 | 2 | 0.53356 | 42684.8 | 0 | 0 | 0.09115 | 3190.25 | 0.28413 | 3977.82 | 40000 | 0 | 2684.8 | 505.45 | 0 | 3977.82 | 4483.27 | 0 | 0 | 0 | 0
2022011018 | 2 | 0.56093 | 44874.4 | 0 | 0 | 0.08063 | 2822.05 | 0.04311 | 603.54 | 40000 | 0 | 2822.05 | 0 | 603.54 | 0 | 0 | 1448.81 | 0 | 0 | 1448.81
2022011019 | 2 | 0.59521 | 47616.8 | 0 | 0 | 0.09564 | 3347.4 | 0 | 0 | 40000 | 0 | 3347.4 | 0 | 0 | 0 | 0 | 4269.4 | 0 | 0 | 4269.4
2022011020 | 2 | 0.59962 | 47969.6 | 0 | 0 | 0.13359 | 4675.65 | 0 | 0 | 40000 | 0 | 4675.65 | 0 | 0 | 0 | 0 | 3293.95 | 0 | 0 | 3293.95
2022011021 | 2 | 0.59874 | 47899.2 | 0 | 0 | 0.15336 | 5367.6 | 0 | 0 | 40000 | 0 | 5367.6 | 0 | 0 | 0 | 0 | 2531.6 | 0 | 0 | 2531.6
2022011022 | 2 | 0.58797 | 47037.6 | 0 | 0 | 0.17149 | 6002.15 | 0 | 0 | 40000 | 0 | 6002.15 | 0 | 0 | 0 | 0 | 1035.45 | 0 | 0 | 1035.45
2022011023 | 2 | 0.56541 | 45232.8 | 0 | 0 | 0.18238 | 6383.3 | 0 | 0 | 40000 | 0 | 5232.8 | 1150.5 | 0 | 0 | 1150.5 | 0 | 0 | 0 | 0
2022011024 | 2 | 0.54649 | 43719.2 | 0 | 0 | 0.20122 | 7042.7 | 0 | 0 | 40000 | 0 | 3719.2 | 3323.5 | 0 | 0 | 3323.5 | 0 | 0 | 0 | 0
2022011101 | 3 | 0.53341 | 42672.8 | 0 | 0 | 0.21655 | 7579.25 | 0 | 0 | 40000 | 0 | 2672.8 | 4906.45 | 0 | 0 | 4906.45 | 0 | 0 | 0 | 0
2022011102 | 3 | 0.53186 | 42548.8 | 0 | 0 | 0.26195 | 9168.25 | 0 | 0 | 40000 | 0 | 2548.8 | 6619.45 | 0 | 0 | 6619.45 | 0 | 0 | 0 | 0
2022011103 | 3 | 0.53393 | 42714.4 | 0 | 0 | 0.28614 | 10014.9 | 0 | 0 | 40000 | 0 | 2714.4 | 7300.5 | 0 | 0 | 7300.5 | 0 | 0 | 0 | 0
2022011104 | 3 | 0.54224 | 43379.2 | 0 | 0 | 0.30118 | 10541.3 | 0 | 0 | 40000 | 0 | 3379.2 | 7162.1 | 0 | 0 | 7162.1 | 0 | 0 | 0 | 0
2022011105 | 3 | 0.55631 | 44504.8 | 0 | 0 | 0.28956 | 10134.6 | 0 | 0 | 40000 | 0 | 4504.8 | 5629.8 | 0 | 0 | 5629.8 | 0 | 0 | 0 | 0
2022011106 | 3 | 0.59234 | 47387.2 | 0 | 0 | 0.28439 | 9953.65 | 0 | 0 | 40000 | 0 | 7387.2 | 2566.45 | 0 | 0 | 2566.45 | 0 | 0 | 0 | 0
2022011107 | 3 | 0.64194 | 51355.2 | 0 | 0 | 0.2951 | 10328.5 | 0 | 0 | 40000 | 0 | 10328.5 | 0 | 0 | 0 | 0 | 1026.7 | 0 | 0 | 1026.7
2022011108 | 3 | 0.66541 | 53232.8 | 0 | 0 | 0.30919 | 10821.65 | 0.00463 | 64.82 | 40000 | 0 | 10821.65 | 0 | 64.82 | 0 | 0 | 2346.33 | 0 | 0 | 2346.33
2022011109 | 3 | 0.65497 | 52397.6 | 0 | 0 | 0.28956 | 10134.6 | 0.10511 | 1471.54 | 40000 | 0 | 10134.6 | 0 | 1471.54 | 0 | 0 | 791.46 | 0 | 0 | 791.46
2022011110 | 3 | 0.63188 | 50550.4 | 0 | 0 | 0.24622 | 8617.7 | 0.32642 | 4569.88 | 40000 | 0 | 8617.7 | 0 | 1932.7 | 2637.18 | 2637.18 | 0 | 0 | 0 | 0
2022011111 | 3 | 0.6094 | 48752 | 0 | 0 | 0.25071 | 8774.85 | 0.41488 | 5808.32 | 40000 | 0 | 8752 | 22.85 | 0 | 5808.32 | 5831.17 | 0 | 0 | 0 | 0
2022011112 | 3 | 0.59371 | 47496.8 | 0 | 0 | 0.29531 | 10335.85 | 0.51618 | 7226.52 | 40000 | 0 | 7496.8 | 2839.05 | 0 | 7226.52 | 10065.57 | 0 | 0 | 0 | 0
2022011113 | 3 | 0.57866 | 46292.8 | 0 | 0 | 0.29648 | 10376.8 | 0.53312 | 7463.68 | 40000 | 0 | 6292.8 | 4084 | 0 | 7463.68 | 11547.68 | 0 | 0 | 0 | 0
2022011114 | 3 | 0.56651 | 45320.8 | 0 | 0 | 0.31478 | 11017.3 | 0.53103 | 7434.42 | 40000 | 0 | 5320.8 | 5696.5 | 0 | 7434.42 | 13130.92 | 0 | 0 | 0 | 0
2022011115 | 3 | 0.5573 | 44584 | 0 | 0 | 0.32964 | 11537.4 | 0.57562 | 8058.68 | 40000 | 0 | 4584 | 6953.4 | 0 | 8058.68 | 15012.08 | 0 | 0 | 0 | 0
2022011116 | 3 | 0.55656 | 44524.8 | 0 | 0 | 0.30524 | 10683.4 | 0.5475 | 7665 | 40000 | 0 | 4524.8 | 6158.6 | 0 | 7665 | 13823.6 | 0 | 0 | 0 | 0
2022011117 | 3 | 0.56657 | 45325.6 | 0 | 0 | 0.25514 | 8929.9 | 0.33952 | 4753.28 | 40000 | 0 | 5325.6 | 3604.3 | 0 | 4753.28 | 8357.58 | 0 | 0 | 0 | 0
2022011118 | 3 | 0.58724 | 46979.2 | 0 | 0 | 0.21008 | 7352.8 | 0.07152 | 1001.28 | 40000 | 0 | 6979.2 | 373.6 | 0 | 1001.28 | 1374.88 | 0 | 0 | 0 | 0
2022011119 | 3 | 0.60572 | 48457.6 | 0 | 0 | 0.25595 | 8958.25 | 0.00026 | 3.64 | 40000 | 0 | 8457.6 | 500.65 | 0 | 3.64 | 504.29 | 0 | 0 | 0 | 0
2022011120 | 3 | 0.60356 | 48284.8 | 0 | 0 | 0.33679 | 11787.65 | 0 | 0 | 40000 | 0 | 8284.8 | 3502.85 | 0 | 0 | 3502.85 | 0 | 0 | 0 | 0
2022011121 | 3 | 0.59739 | 47791.2 | 0 | 0 | 0.39771 | 13919.85 | 0 | 0 | 40000 | 0 | 7791.2 | 6128.65 | 0 | 0 | 6128.65 | 0 | 0 | 0 | 0
2022011122 | 3 | 0.57923 | 46338.4 | 0 | 0 | 0.41142 | 14399.7 | 0 | 0 | 40000 | 0 | 6338.4 | 8061.3 | 0 | 0 | 8061.3 | 0 | 0 | 0 | 0
2022011123 | 3 | 0.54956 | 43964.8 | 0 | 0 | 0.4088 | 14308 | 0 | 0 | 40000 | 0 | 3964.8 | 10343.2 | 0 | 0 | 10343.2 | 0 | 0 | 0 | 0
2022011124 | 3 | 0.52311 | 41848.8 | 0 | 0 | 0.40946 | 14331.1 | 0 | 0 | 40000 | 0 | 1848.8 | 12482.3 | 0 | 0 | 12482.3 | 0 | 0 | 0 | 0
2022011201 | 4 | 0.50715 | 40572 | 0 | 0 | 0.39785 | 13924.75 | 0 | 0 | 40000 | 0 | 572 | 13352.75 | 0 | 0 | 13352.75 | 0 | 0 | 0 | 0
2022011202 | 4 | 0.49972 | 39977.6 | 0 | 0 | 0.37416 | 13095.6 | 0 | 0 | 39977.6 | 22.4 | 0 | 13095.6 | 0 | 0 | 13118 | 0 | 0 | 0 | 0
2022011203 | 4 | 0.49596 | 39676.8 | 0 | 0 | 0.35619 | 12466.65 | 0 | 0 | 39676.8 | 323.2 | 0 | 12466.65 | 0 | 0 | 12789.85 | 0 | 0 | 0 | 0
2022011204 | 4 | 0.50032 | 40025.6 | 0 | 0 | 0.33063 | 11572.05 | 0 | 0 | 40000 | 0 | 25.6 | 11546.45 | 0 | 0 | 11546.45 | 0 | 0 | 0 | 0
2022011205 | 4 | 0.51409 | 41127.2 | 0 | 0 | 0.2951 | 10328.5 | 0 | 0 | 40000 | 0 | 1127.2 | 9201.3 | 0 | 0 | 9201.3 | 0 | 0 | 0 | 0
2022011206 | 4 | 0.54515 | 43612 | 0 | 0 | 0.25562 | 8946.7 | 0 | 0 | 40000 | 0 | 3612 | 5334.7 | 0 | 0 | 5334.7 | 0 | 0 | 0 | 0
2022011207 | 4 | 0.58954 | 47163.2 | 0 | 0 | 0.23353 | 8173.55 | 0 | 0 | 40000 | 0 | 7163.2 | 1010.35 | 0 | 0 | 1010.35 | 0 | 0 | 0 | 0
2022011208 | 4 | 0.61428 | 49142.4 | 0 | 0 | 0.19859 | 6950.65 | 0.00136 | 19.04 | 40000 | 0 | 6950.65 | 0 | 19.04 | 0 | 0 | 2172.71 | 0 | 0 | 2172.71
2022011209 | 4 | 0.60955 | 48764 | 0 | 0 | 0.17275 | 6046.25 | 0.20424 | 2859.36 | 40000 | 0 | 6046.25 | 0 | 2717.75 | 141.61 | 141.61 | 0 | 0 | 0 | 0
2022011210 | 4 | 0.59382 | 47505.6 | 0 | 0 | 0.10943 | 3830.05 | 0.6113 | 8558.2 | 40000 | 0 | 3830.05 | 0 | 3675.55 | 4882.65 | 4882.65 | 0 | 0 | 0 | 0
2022011211 | 4 | 0.57731 | 46184.8 | 0 | 0 | 0.07156 | 2504.6 | 0.67101 | 9394.14 | 40000 | 0 | 2504.6 | 0 | 3680.2 | 5713.94 | 5713.94 | 0 | 0 | 0 | 0
2022011212 | 4 | 0.5579 | 44632 | 0 | 0 | 0.05723 | 2003.05 | 0.67133 | 9398.62 | 40000 | 0 | 2003.05 | 0 | 2628.95 | 6769.67 | 6769.67 | 0 | 0 | 0 | 0
2022011213 | 4 | 0.53874 | 43099.2 | 0 | 0 | 0.05782 | 2023.7 | 0.65504 | 9170.56 | 40000 | 0 | 2023.7 | 0 | 1075.5 | 8095.06 | 8095.06 | 0 | 0 | 0 | 0
2022011214 | 4 | 0.52102 | 41681.6 | 0 | 0 | 0.06738 | 2358.3 | 0.6748 | 9447.2 | 40000 | 0 | 1681.6 | 676.7 | 0 | 9447.2 | 10123.9 | 0 | 0 | 0 | 0
2022011215 | 4 | 0.50862 | 40689.6 | 0 | 0 | 0.0532 | 1862 | 0.69551 | 9737.14 | 40000 | 0 | 689.6 | 1172.4 | 0 | 9737.14 | 10909.54 | 0 | 0 | 0 | 0
2022011216 | 4 | 0.50379 | 40303.2 | 0 | 0 | 0.03379 | 1182.65 | 0.72545 | 10156.3 | 40000 | 0 | 303.2 | 879.45 | 0 | 10156.3 | 11035.75 | 0 | 0 | 0 | 0
2022011217 | 4 | 0.50796 | 40636.8 | 0 | 0 | 0.02284 | 799.4 | 0.58879 | 8243.06 | 40000 | 0 | 636.8 | 162.6 | 0 | 8243.06 | 8405.66 | 0 | 0 | 0 | 0
2022011218 | 4 | 0.52654 | 42123.2 | 0 | 0 | 0.02504 | 876.4 | 0.1457 | 2039.8 | 40000 | 0 | 876.4 | 0 | 1246.8 | 793 | 793 | 0 | 0 | 0 | 0
2022011219 | 4 | 0.55246 | 44196.8 | 0 | 0 | 0.02487 | 870.45 | 0 | 0 | 40000 | 0 | 870.45 | 0 | 0 | 0 | 0 | 3326.35 | 0 | 0 | 3326.35
2022011220 | 4 | 0.55401 | 44320.8 | 0 | 0 | 0.03045 | 1065.75 | 0 | 0 | 40000 | 0 | 1065.75 | 0 | 0 | 0 | 0 | 3255.05 | 0 | 0 | 3255.05
2022011221 | 4 | 0.55109 | 44087.2 | 0 | 0 | 0.03511 | 1228.85 | 0 | 0 | 40000 | 0 | 1228.85 | 0 | 0 | 0 | 0 | 2858.35 | 0 | 0 | 2858.35
2022011222 | 4 | 0.53998 | 43198.4 | 0 | 0 | 0.03511 | 1228.85 | 0 | 0 | 40000 | 0 | 1228.85 | 0 | 0 | 0 | 0 | 1969.55 | 0 | 0 | 1969.55
2022011223 | 4 | 0.51868 | 41494.4 | 0 | 0 | 0.03755 | 1314.25 | 0 | 0 | 40000 | 0 | 1314.25 | 0 | 0 | 0 | 0 | 180.15 | 0 | 0 | 180.15
2022011224 | 4 | 0.49963 | 39970.4 | 0 | 0 | 0.05239 | 1833.65 | 0 | 0 | 39970.4 | 29.6 | 0 | 1833.65 | 0 | 0 | 1863.25 | 0 | 0 | 0 | 0
2022011301 | 5 | 0.48912 | 39129.6 | 0 | 0 | 0.06838 | 2393.3 | 0 | 0 | 39129.6 | 870.4 | 0 | 2393.3 | 0 | 0 | 3263.7 | 0 | 0 | 0 | 0
2022011302 | 5 | 0.48515 | 38812 | 0 | 0 | 0.08516 | 2980.6 | 0 | 0 | 38812 | 1188 | 0 | 2980.6 | 0 | 0 | 4168.6 | 0 | 0 | 0 | 0
2022011303 | 5 | 0.48889 | 39111.2 | 0 | 0 | 0.08507 | 2977.45 | 0 | 0 | 39111.2 | 888.8 | 0 | 2977.45 | 0 | 0 | 3866.25 | 0 | 0 | 0 | 0
2022011304 | 5 | 0.49706 | 39764.8 | 0 | 0 | 0.08799 | 3079.65 | 0 | 0 | 39764.8 | 235.2 | 0 | 3079.65 | 0 | 0 | 3314.85 | 0 | 0 | 0 | 0
2022011305 | 5 | 0.51443 | 41154.4 | 0 | 0 | 0.09972 | 3490.2 | 0 | 0 | 40000 | 0 | 1154.4 | 2335.8 | 0 | 0 | 2335.8 | 0 | 0 | 0 | 0
2022011306 | 5 | 0.54853 | 43882.4 | 0 | 0 | 0.13188 | 4615.8 | 0 | 0 | 40000 | 0 | 3882.4 | 733.4 | 0 | 0 | 733.4 | 0 | 0 | 0 | 0
2022011307 | 5 | 0.59752 | 47801.6 | 0 | 0 | 0.15113 | 5289.55 | 0 | 0 | 40000 | 0 | 5289.55 | 0 | 0 | 0 | 0 | 2512.05 | 0 | 0 | 2512.05
2022011308 | 5 | 0.62121 | 49696.8 | 0 | 0 | 0.15223 | 5328.05 | 0.0061 | 85.4 | 40000 | 0 | 5328.05 | 0 | 85.4 | 0 | 0 | 4283.35 | 0 | 0 | 4283.35
2022011309 | 5 | 0.60527 | 48421.6 | 0 | 0 | 0.13874 | 4855.9 | 0.27477 | 3846.78 | 40000 | 0 | 4855.9 | 0 | 3565.7 | 281.08 | 281.08 | 0 | 0 | 0 | 0
2022011310 | 5 | 0.57416 | 45932.8 | 0 | 0 | 0.07623 | 2668.05 | 0.69948 | 9792.72 | 40000 | 0 | 2668.05 | 0 | 3264.75 | 6527.97 | 6527.97 | 0 | 0 | 0 | 0
2022011311 | 5 | 0.5467 | 43736 | 0 | 0 | 0.02029 | 710.15 | 0.74219 | 10390.66 | 40000 | 0 | 710.15 | 0 | 3025.85 | 7364.81 | 7364.81 | 0 | 0 | 0 | 0
2022011312 | 5 | 0.52471 | 41976.8 | 0 | 0 | 0.01158 | 405.3 | 0.71187 | 9966.18 | 40000 | 0 | 405.3 | 0 | 1571.5 | 8394.68 | 8394.68 | 0 | 0 | 0 | 0
2022011313 | 5 | 0.5098 | 40784 | 0 | 0 | 0.01056 | 369.6 | 0.6863 | 9608.2 | 40000 | 0 | 369.6 | 0 | 414.4 | 9193.8 | 9193.8 | 0 | 0 | 0 | 0
2022011314 | 5 | 0.50274 | 40219.2 | 0 | 0 | 0.00909 | 318.15 | 0.69265 | 9697.1 | 40000 | 0 | 219.2 | 98.95 | 0 | 9697.1 | 9796.05 | 0 | 0 | 0 | 0
2022011315 | 5 | 0.4987 | 39896 | 0 | 0 | 0.01321 | 462.35 | 0.71443 | 10002.02 | 39896 | 104 | 0 | 462.35 | 0 | 10002.02 | 10568.37 | 0 | 0 | 0 | 0
2022011316 | 5 | 0.4984 | 39872 | 0 | 0 | 0.01123 | 393.05 | 0.72941 | 10211.74 | 39872 | 128 | 0 | 393.05 | 0 | 10211.74 | 10732.79 | 0 | 0 | 0 | 0
2022011317 | 5 | 0.50162 | 40129.6 | 0 | 0 | 0.00892 | 312.2 | 0.60235 | 8432.9 | 40000 | 0 | 129.6 | 182.6 | 0 | 8432.9 | 8615.5 | 0 | 0 | 0 | 0
2022011318 | 5 | 0.50913 | 40730.4 | 0 | 0 | 0.01268 | 443.8 | 0.15314 | 2143.96 | 40000 | 0 | 443.8 | 0 | 286.6 | 1857.36 | 1857.36 | 0 | 0 | 0 | 0
2022011319 | 5 | 0.52656 | 42124.8 | 0 | 0 | 0.02282 | 798.7 | 0.00036 | 5.04 | 40000 | 0 | 798.7 | 0 | 5.04 | 0 | 0 | 1321.06 | 0 | 0 | 1321.06
2022011320 | 5 | 0.52381 | 41904.8 | 0 | 0 | 0.03655 | 1279.25 | 0 | 0 | 40000 | 0 | 1279.25 | 0 | 0 | 0 | 0 | 625.55 | 0 | 0 | 625.55
2022011321 | 5 | 0.51649 | 41319.2 | 0 | 0 | 0.06431 | 2250.85 | 0 | 0 | 40000 | 0 | 1319.2 | 931.65 | 0 | 0 | 931.65 | 0 | 0 | 0 | 0
2022011322 | 5 | 0.50451 | 40360.8 | 0 | 0 | 0.11398 | 3989.3 | 0 | 0 | 40000 | 0 | 360.8 | 3628.5 | 0 | 0 | 3628.5 | 0 | 0 | 0 | 0
2022011323 | 5 | 0.48369 | 38695.2 | 0 | 0 | 0.18052 | 6318.2 | 0 | 0 | 38695.2 | 1304.8 | 0 | 6318.2 | 0 | 0 | 7623 | 0 | 0 | 0 | 0
2022011324 | 5 | 0.46249 | 36999.2 | 0 | 0 | 0.23399 | 8189.65 | 0 | 0 | 36999.2 | 3000.8 | 0 | 8189.65 | 0 | 0 | 11190.45 | 0 | 0 | 0 | 0
2022011401 | 6 | 0.45162 | 36129.6 | 0 | 0 | 0.29469 | 10314.15 | 0 | 0 | 36129.6 | 3870.4 | 0 | 10314.15 | 0 | 0 | 14184.55 | 0 | 0 | 0 | 0
2022011402 | 6 | 0.44982 | 35985.6 | 0 | 0 | 0.36609 | 12813.15 | 0 | 0 | 35985.6 | 4014.4 | 0 | 12813.15 | 0 | 0 | 16827.55 | 0 | 0 | 0 | 0
2022011403 | 6 | 0.45294 | 36235.2 | 0 | 0 | 0.39642 | 13874.7 | 0 | 0 | 36235.2 | 3764.8 | 0 | 13874.7 | 0 | 0 | 17639.5 | 0 | 0 | 0 | 0
2022011404 | 6 | 0.46142 | 36913.6 | 0 | 0 | 0.39913 | 13969.55 | 0 | 0 | 36913.6 | 3086.4 | 0 | 13969.55 | 0 | 0 | 17055.95 | 0 | 0 | 0 | 0
2022011405 | 6 | 0.47793 | 38234.4 | 0 | 0 | 0.4282 | 14987 | 0 | 0 | 38234.4 | 1765.6 | 0 | 14987 | 0 | 0 | 16752.6 | 0 | 0 | 0 | 0
2022011406 | 6 | 0.51261 | 41008.8 | 0 | 0 | 0.46941 | 16429.35 | 0 | 0 | 40000 | 0 | 1008.8 | 15420.55 | 0 | 0 | 15420.55 | 0 | 0 | 0 | 0
2022011407 | 6 | 0.56183 | 44946.4 | 0 | 0 | 0.49301 | 17255.35 | 0 | 0 | 40000 | 0 | 4946.4 | 12308.95 | 0 | 0 | 12308.95 | 0 | 0 | 0 | 0
2022011408 | 6 | 0.59042 | 47233.6 | 0 | 0 | 0.52862 | 18501.7 | 0.00505 | 70.7 | 40000 | 0 | 7233.6 | 11268.1 | 0 | 70.7 | 11338.8 | 0 | 0 | 0 | 0
2022011409 | 6 | 0.58554 | 46843.2 | 0 | 0 | 0.52786 | 18475.1 | 0.21295 | 2981.3 | 40000 | 0 | 6843.2 | 11631.9 | 0 | 2981.3 | 14613.2 | 0 | 0 | 0 | 0
2022011410 | 6 | 0.56289 | 45031.2 | 0 | 0 | 0.44345 | 15520.75 | 0.50933 | 7130.62 | 40000 | 0 | 5031.2 | 10489.55 | 0 | 7130.62 | 17620.17 | 0 | 0 | 0 | 0
2022011411 | 6 | 0.54203 | 43362.4 | 0 | 0 | 0.40089 | 14031.15 | 0.61597 | 8623.58 | 40000 | 0 | 3362.4 | 10668.75 | 0 | 8623.58 | 19292.33 | 0 | 0 | 0 | 0
2022011412 | 6 | 0.52667 | 42133.6 | 0 | 0 | 0.43914 | 15369.9 | 0.58194 | 8147.16 | 40000 | 0 | 2133.6 | 13236.3 | 0 | 8147.16 | 21383.46 | 0 | 0 | 0 | 0
2022011413 | 6 | 0.51857 | 41485.6 | 0 | 0 | 0.50876 | 17806.6 | 0.41766 | 5847.24 | 40000 | 0 | 1485.6 | 16321 | 0 | 5847.24 | 22168.24 | 0 | 0 | 0 | 0
2022011414 | 6 | 0.51483 | 41186.4 | 0 | 0 | 0.51341 | 17969.35 | 0.45386 | 6354.04 | 40000 | 0 | 1186.4 | 16782.95 | 0 | 6354.04 | 23136.99 | 0 | 0 | 0 | 0
2022011415 | 6 | 0.51232 | 40985.6 | 0 | 0 | 0.48509 | 16978.15 | 0.55262 | 7736.68 | 40000 | 0 | 985.6 | 15992.55 | 0 | 7736.68 | 23729.23 | 0 | 0 | 0 | 0
2022011416 | 6 | 0.50928 | 40742.4 | 0 | 0 | 0.46265 | 16192.75 | 0.5321 | 7449.4 | 40000 | 0 | 742.4 | 15450.35 | 0 | 7449.4 | 22899.75 | 0 | 0 | 0 | 0
2022011417 | 6 | 0.51039 | 40831.2 | 0 | 0 | 0.47653 | 16678.55 | 0.4081 | 5713.4 | 40000 | 0 | 831.2 | 15847.35 | 0 | 5713.4 | 21560.75 | 0 | 0 | 0 | 0
2022011418 | 6 | 0.5138 | 41104 | 0 | 0 | 0.50045 | 17515.75 | 0.09704 | 1358.56 | 40000 | 0 | 1104 | 16411.75 | 0 | 1358.56 | 17770.31 | 0 | 0 | 0 | 0
2022011419 | 6 | 0.52638 | 42110.4 | 0 | 0 | 0.58521 | 20482.35 | 0.00025 | 3.5 | 40000 | 0 | 2110.4 | 18371.95 | 0 | 3.5 | 18375.45 | 0 | 0 | 0 | 0
2022011420 | 6 | 0.51979 | 41583.2 | 0 | 0 | 0.65356 | 22874.6 | 0 | 0 | 40000 | 0 | 1583.2 | 21291.4 | 0 | 0 | 21291.4 | 0 | 0 | 0 | 0
2022011421 | 6 | 0.51132 | 40905.6 | 0 | 0 | 0.66848 | 23396.8 | 0 | 0 | 40000 | 0 | 905.6 | 22491.2 | 0 | 0 | 22491.2 | 0 | 0 | 0 | 0
2022011422 | 6 | 0.49808 | 39846.4 | 0 | 0 | 0.66491 | 23271.85 | 0 | 0 | 39846.4 | 153.6 | 0 | 23271.85 | 0 | 0 | 23425.45 | 0 | 0 | 0 | 0
2022011423 | 6 | 0.48123 | 38498.4 | 0 | 0 | 0.666 | 23310 | 0 | 0 | 38498.4 | 1501.6 | 0 | 23310 | 0 | 0 | 24811.6 | 0 | 0 | 0 | 0
2022011424 | 6 | 0.46582 | 37265.6 | 0 | 0 | 0.65456 | 22909.6 | 0 | 0 | 37265.6 | 2734.4 | 0 | 22909.6 | 0 | 0 | 25644 | 0 | 0 | 0 | 0
2022011501 | 7 | 0.45227 | 36181.6 | 0 | 0 | 0.6313 | 22095.5 | 0 | 0 | 36181.6 | 3818.4 | 0 | 22095.5 | 0 | 0 | 25913.9 | 0 | 0 | 0 | 0
2022011502 | 7 | 0.44708 | 35766.4 | 0 | 0 | 0.63586 | 22255.1 | 0 | 0 | 35766.4 | 4233.6 | 0 | 22255.1 | 0 | 0 | 26488.7 | 0 | 0 | 0 | 0
2022011503 | 7 | 0.44851 | 35880.8 | 0 | 0 | 0.64358 | 22525.3 | 0 | 0 | 35880.8 | 4119.2 | 0 | 22525.3 | 0 | 0 | 26644.5 | 0 | 0 | 0 | 0
2022011504 | 7 | 0.45577 | 36461.6 | 0 | 0 | 0.64279 | 22497.65 | 0 | 0 | 36461.6 | 3538.4 | 0 | 22497.65 | 0 | 0 | 26036.05 | 0 | 0 | 0 | 0
2022011505 | 7 | 0.46819 | 37455.2 | 0 | 0 | 0.66935 | 23427.25 | 0 | 0 | 37455.2 | 2544.8 | 0 | 23427.25 | 0 | 0 | 25972.05 | 0 | 0 | 0 | 0
2022011506 | 7 | 0.49018 | 39214.4 | 0 | 0 | 0.68071 | 23824.85 | 0 | 0 | 39214.4 | 785.6 | 0 | 23824.85 | 0 | 0 | 24610.45 | 0 | 0 | 0 | 0
2022011507 | 7 | 0.52037 | 41629.6 | 0 | 0 | 0.69134 | 24196.9 | 0 | 0 | 40000 | 0 | 1629.6 | 22567.3 | 0 | 0 | 22567.3 | 0 | 0 | 0 | 0
2022011508 | 7 | 0.55448 | 44358.4 | 0 | 0 | 0.69662 | 24381.7 | 0.00145 | 20.3 | 40000 | 0 | 4358.4 | 20023.3 | 0 | 20.3 | 20043.6 | 0 | 0 | 0 | 0
2022011509 | 7 | 0.58333 | 46666.4 | 0 | 0 | 0.68634 | 24021.9 | 0.08771 | 1227.94 | 40000 | 0 | 6666.4 | 17355.5 | 0 | 1227.94 | 18583.44 | 0 | 0 | 0 | 0
2022011510 | 7 | 0.60596 | 48476.8 | 0 | 0 | 0.66207 | 23172.45 | 0.22537 | 3155.18 | 40000 | 0 | 8476.8 | 14695.65 | 0 | 3155.18 | 17850.83 | 0 | 0 | 0 | 0
2022011511 | 7 | 0.61569 | 49255.2 | 0 | 0 | 0.66117 | 23140.95 | 0.26315 | 3684.1 | 40000 | 0 | 9255.2 | 13885.75 | 0 | 3684.1 | 17569.85 | 0 | 0 | 0 | 0
2022011512 | 7 | 0.6178 | 49424 | 0 | 0 | 0.6637 | 23229.5 | 0.286 | 4004 | 40000 | 0 | 9424 | 13805.5 | 0 | 4004 | 17809.5 | 0 | 0 | 0 | 0
2022011513 | 7 | 0.61481 | 49184.8 | 0 | 0 | 0.66801 | 23380.35 | 0.2876 | 4026.4 | 40000 | 0 | 9184.8 | 14195.55 | 0 | 4026.4 | 18221.95 | 0 | 0 | 0 | 0
2022011514 | 7 | 0.61093 | 48874.4 | 0 | 0 | 0.66551 | 23292.85 | 0.29747 | 4164.58 | 40000 | 0 | 8874.4 | 14418.45 | 0 | 4164.58 | 18583.03 | 0 | 0 | 0 | 0
2022011515 | 7 | 0.60779 | 48623.2 | 0 | 0 | 0.66338 | 23218.3 | 0.28455 | 3983.7 | 40000 | 0 | 8623.2 | 14595.1 | 0 | 3983.7 | 18578.8 | 0 | 0 | 0 | 0
2022011516 | 7 | 0.60869 | 48695.2 | 0 | 0 | 0.65749 | 23012.15 | 0.25604 | 3584.56 | 40000 | 0 | 8695.2 | 14316.95 | 0 | 3584.56 | 17901.51 | 0 | 0 | 0 | 0
2022011517 | 7 | 0.61725 | 49380 | 0 | 0 | 0.65626 | 22969.1 | 0.22978 | 3216.92 | 40000 | 0 | 9380 | 13589.1 | 0 | 3216.92 | 16806.02 | 0 | 0 | 0 | 0
2022011518 | 7 | 0.63901 | 51120.8 | 0 | 0 | 0.6593 | 23075.5 | 0.07749 | 1084.86 | 40000 | 0 | 11120.8 | 11954.7 | 0 | 1084.86 | 13039.56 | 0 | 0 | 0 | 0
2022011519 | 7 | 0.66386 | 53108.8 | 0 | 0 | 0.59569 | 20849.15 | 0.00016 | 2.24 | 40000 | 0 | 13108.8 | 7740.35 | 0 | 2.24 | 7742.59 | 0 | 0 | 0 | 0
2022011520 | 7 | 0.66565 | 53252 | 0 | 0 | 0.52662 | 18431.7 | 0 | 0 | 40000 | 0 | 13252 | 5179.7 | 0 | 0 | 5179.7 | 0 | 0 | 0 | 0
2022011521 | 7 | 0.66202 | 52961.6 | 0 | 0 | 0.49602 | 17360.7 | 0 | 0 | 40000 | 0 | 12961.6 | 4399.1 | 0 | 0 | 4399.1 | 0 | 0 | 0 | 0
2022011522 | 7 | 0.65286 | 52228.8 | 0 | 0 | 0.44715 | 15650.25 | 0 | 0 | 40000 | 0 | 12228.8 | 3421.45 | 0 | 0 | 3421.45 | 0 | 0 | 0 | 0
2022011523 | 7 | 0.63666 | 50932.8 | 0 | 0 | 0.39348 | 13771.8 | 0 | 0 | 40000 | 0 | 10932.8 | 2839 | 0 | 0 | 2839 | 0 | 0 | 0 | 0
2022011524 | 7 | 0.62087 | 49669.6 | 0 | 0 | 0.34366 | 12028.1 | 0 | 0 | 40000 | 0 | 9669.6 | 2358.5 | 0 | 0 | 2358.5 | 0 | 0 | 0 | 0
2022011601 | 1 | 0.60801 | 48640.8 | 0 | 0 | 0.30827 | 10789.45 | 0 | 0 | 40000 | 0 | 8640.8 | 2148.65 | 0 | 0 | 2148.65 | 0 | 0 | 0 | 0
2022011602 | 1 | 0.60182 | 48145.6 | 0 | 0 | 0.28555 | 9994.25 | 0 | 0 | 40000 | 0 | 8145.6 | 1848.65 | 0 | 0 | 1848.65 | 0 | 0 | 0 | 0
2022011603 | 1 | 0.59991 | 47992.8 | 0 | 0 | 0.26935 | 9427.25 | 0 | 0 | 40000 | 0 | 7992.8 | 1434.45 | 0 | 0 | 1434.45 | 0 | 0 | 0 | 0
2022011604 | 1 | 0.60385 | 48308 | 0 | 0 | 0.27203 | 9521.05 | 0 | 0 | 40000 | 0 | 8308 | 1213.05 | 0 | 0 | 1213.05 | 0 | 0 | 0 | 0
2022011605 | 1 | 0.61163 | 48930.4 | 0 | 0 | 0.27794 | 9727.9 | 0 | 0 | 40000 | 0 | 8930.4 | 797.5 | 0 | 0 | 797.5 | 0 | 0 | 0 | 0
2022011606 | 1 | 0.62513 | 50010.4 | 0 | 0 | 0.28523 | 9983.05 | 0 | 0 | 40000 | 0 | 9983.05 | 0 | 0 | 0 | 0 | 27.35 | 0 | 0 | 27.35
2022011607 | 1 | 0.64278 | 51422.4 | 0 | 0 | 0.26926 | 9424.1 | 0 | 0 | 40000 | 0 | 9424.1 | 0 | 0 | 0 | 0 | 1998.3 | 0 | 0 | 1998.3
2022011608 | 1 | 0.66183 | 52946.4 | 0 | 0 | 0.28886 | 10110.1 | 0.00644 | 90.16 | 40000 | 0 | 10110.1 | 0 | 90.16 | 0 | 0 | 2746.14 | 0 | 0 | 2746.14
2022011609 | 1 | 0.66397 | 53117.6 | 0 | 0 | 0.28989 | 10146.15 | 0.2813 | 3938.2 | 40000 | 0 | 10146.15 | 0 | 2971.45 | 966.75 | 966.75 | 0 | 0 | 0 | 0
2022011610 | 1 | 0.64599 | 51679.2 | 0 | 0 | 0.22942 | 8029.7 | 0.72548 | 10156.72 | 40000 | 0 | 8029.7 | 0 | 3649.5 | 6507.22 | 6507.22 | 0 | 0 | 0 | 0
2022011611 | 1 | 0.61513 | 49210.4 | 0 | 0 | 0.15705 | 5496.75 | 0.77287 | 10820.18 | 40000 | 0 | 5496.75 | 0 | 3713.65 | 7106.53 | 7106.53 | 0 | 0 | 0 | 0
2022011612 | 1 | 0.5828 | 46624 | 0 | 0 | 0.12321 | 4312.35 | 0.74401 | 10416.14 | 40000 | 0 | 4312.35 | 0 | 2311.65 | 8104.49 | 8104.49 | 0 | 0 | 0 | 0
2022011613 | 1 | 0.5519 | 44152 | 0 | 0 | 0.12182 | 4263.7 | 0.719 | 10066 | 40000 | 0 | 4152 | 111.7 | 0 | 10066 | 10177.7 | 0 | 0 | 0 | 0
2022011614 | 1 | 0.52626 | 42100.8 | 0 | 0 | 0.14343 | 5020.05 | 0.71902 | 10066.28 | 40000 | 0 | 2100.8 | 2919.25 | 0 | 10066.28 | 12985.53 | 0 | 0 | 0 | 0
2022011615 | 1 | 0.50762 | 40609.6 | 0 | 0 | 0.13834 | 4841.9 | 0.74722 | 10461.08 | 40000 | 0 | 609.6 | 4232.3 | 0 | 10461.08 | 14693.38 | 0 | 0 | 0 | 0
2022011616 | 1 | 0.49729 | 39783.2 | 0 | 0 | 0.11237 | 3932.95 | 0.76119 | 10656.66 | 39783.2 | 216.8 | 0 | 3932.95 | 0 | 10656.66 | 14806.41 | 0 | 0 | 0 | 0
2022011617 | 1 | 0.49505 | 39604 | 0 | 0 | 0.08808 | 3082.8 | 0.63101 | 8834.14 | 39604 | 396 | 0 | 3082.8 | 0 | 8834.14 | 12312.94 | 0 | 0 | 0 | 0
2022011618 | 1 | 0.51363 | 41090.4 | 0 | 0 | 0.05384 | 1884.4 | 0.16338 | 2287.32 | 40000 | 0 | 1090.4 | 794 | 0 | 2287.32 | 3081.32 | 0 | 0 | 0 | 0
2022011619 | 1 | 0.54504 | 43603.2 | 0 | 0 | 0.05646 | 1976.1 | 0.00024 | 3.36 | 40000 | 0 | 1976.1 | 0 | 3.36 | 0 | 0 | 1623.74 | 0 | 0 | 1623.74
2022011620 | 1 | 0.56094 | 44875.2 | 0 | 0 | 0.0768 | 2688 | 0 | 0 | 40000 | 0 | 2688 | 0 | 0 | 0 | 0 | 2187.2 | 0 | 0 | 2187.2
2022011621 | 1 | 0.56499 | 45199.2 | 0 | 0 | 0.09613 | 3364.55 | 0 | 0 | 40000 | 0 | 3364.55 | 0 | 0 | 0 | 0 | 1834.65 | 0 | 0 | 1834.65
2022011622 | 1 | 0.56436 | 45148.8 | 0 | 0 | 0.12157 | 4254.95 | 0 | 0 | 40000 | 0 | 4254.95 | 0 | 0 | 0 | 0 | 893.85 | 0 | 0 | 893.85
2022011623 | 1 | 0.5547 | 44376 | 0 | 0 | 0.1516 | 5306 | 0 | 0 | 40000 | 0 | 4376 | 930 | 0 | 0 | 930 | 0 | 0 | 0 | 0
2022011624 | 1 | 0.54487 | 43589.6 | 0 | 0 | 0.16976 | 5941.6 | 0 | 0 | 40000 | 0 | 3589.6 | 2352 | 0 | 0 | 2352 | 0 | 0 | 0 | 0
2022011701 | 2 | 0.54086 | 43268.8 | 0 | 0 | 0.15483 | 5419.05 | 0 | 0 | 40000 | 0 | 3268.8 | 2150.25 | 0 | 0 | 2150.25 | 0 | 0 | 0 | 0
2022011702 | 2 | 0.54101 | 43280.8 | 0 | 0 | 0.15955 | 5584.25 | 0 | 0 | 40000 | 0 | 3280.8 | 2303.45 | 0 | 0 | 2303.45 | 0 | 0 | 0 | 0
2022011703 | 2 | 0.54662 | 43729.6 | 0 | 0 | 0.16056 | 5619.6 | 0 | 0 | 40000 | 0 | 3729.6 | 1890 | 0 | 0 | 1890 | 0 | 0 | 0 | 0
2022011704 | 2 | 0.55836 | 44668.8 | 0 | 0 | 0.16785 | 5874.75 | 0 | 0 | 40000 | 0 | 4668.8 | 1205.95 | 0 | 0 | 1205.95 | 0 | 0 | 0 | 0
2022011705 | 2 | 0.57624 | 46099.2 | 0 | 0 | 0.16405 | 5741.75 | 0 | 0 | 40000 | 0 | 5741.75 | 0 | 0 | 0 | 0 | 357.45 | 0 | 0 | 357.45
2022011706 | 2 | 0.60777 | 48621.6 | 0 | 0 | 0.15527 | 5434.45 | 0 | 0 | 40000 | 0 | 5434.45 | 0 | 0 | 0 | 0 | 3187.15 | 0 | 0 | 3187.15
2022011707 | 2 | 0.64506 | 51604.8 | 0 | 0 | 0.14645 | 5125.75 | 0 | 0 | 40000 | 0 | 5125.75 | 0 | 0 | 0 | 0 | 6479.05 | 0 | 0 | 6479.05
2022011708 | 2 | 0.6713 | 53704 | 0 | 0 | 0.14444 | 5055.4 | 0.00731 | 102.34 | 40000 | 0 | 5055.4 | 0 | 102.34 | 0 | 0 | 8546.26 | 0 | 0 | 8546.26
2022011709 | 2 | 0.66246 | 52996.8 | 0 | 0 | 0.15279 | 5347.65 | 0.27272 | 3818.08 | 40000 | 0 | 5347.65 | 0 | 3818.08 | 0 | 0 | 3831.07 | 0 | 0 | 3831.07
2022011710 | 2 | 0.62885 | 50308 | 0 | 0 | 0.11573 | 4050.55 | 0.68042 | 9525.88 | 40000 | 0 | 4050.55 | 0 | 6257.45 | 3268.43 | 3268.43 | 0 | 0 | 0 | 0
2022011711 | 2 | 0.59322 | 47457.6 | 0 | 0 | 0.13433 | 4701.55 | 0.72329 | 10126.06 | 40000 | 0 | 4701.55 | 0 | 2756.05 | 7370.01 | 7370.01 | 0 | 0 | 0 | 0
2022011712 | 2 | 0.56374 | 45099.2 | 0 | 0 | 0.17346 | 6071.1 | 0.69438 | 9721.32 | 40000 | 0 | 5099.2 | 971.9 | 0 | 9721.32 | 10693.22 | 0 | 0 | 0 | 0
2022011713 | 2 | 0.54002 | 43201.6 | 0 | 0 | 0.18829 | 6590.15 | 0.67013 | 9381.82 | 40000 | 0 | 3201.6 | 3388.55 | 0 | 9381.82 | 12770.37 | 0 | 0 | 0 | 0
2022011714 | 2 | 0.52154 | 41723.2 | 0 | 0 | 0.22976 | 8041.6 | 0.66172 | 9264.08 | 40000 | 0 | 1723.2 | 6318.4 | 0 | 9264.08 | 15582.48 | 0 | 0 | 0 | 0
2022011715 | 2 | 0.51025 | 40820 | 0 | 0 | 0.27878 | 9757.3 | 0.66342 | 9287.88 | 40000 | 0 | 820 | 8937.3 | 0 | 9287.88 | 18225.18 | 0 | 0 | 0 | 0
2022011716 | 2 | 0.5053 | 40424 | 0 | 0 | 0.33107 | 11587.45 | 0.57477 | 8046.78 | 40000 | 0 | 424 | 11163.45 | 0 | 8046.78 | 19210.23 | 0 | 0 | 0 | 0
2022011717 | 2 | 0.50704 | 40563.2 | 0 | 0 | 0.36758 | 12865.3 | 0.4047 | 5665.8 | 40000 | 0 | 563.2 | 12302.1 | 0 | 5665.8 | 17967.9 | 0 | 0 | 0 | 0
2022011718 | 2 | 0.5189 | 41512 | 0 | 0 | 0.37775 | 13221.25 | 0.1353 | 1894.2 | 40000 | 0 | 1512 | 11709.25 | 0 | 1894.2 | 13603.45 | 0 | 0 | 0 | 0
2022011719 | 2 | 0.54779 | 43823.2 | 0 | 0 | 0.47235 | 16532.25 | 0.00123 | 17.22 | 40000 | 0 | 3823.2 | 12709.05 | 0 | 17.22 | 12726.27 | 0 | 0 | 0 | 0
2022011720 | 2 | 0.55398 | 44318.4 | 0 | 0 | 0.53992 | 18897.2 | 0 | 0 | 40000 | 0 | 4318.4 | 14578.8 | 0 | 0 | 14578.8 | 0 | 0 | 0 | 0
2022011721 | 2 | 0.55066 | 44052.8 | 0 | 0 | 0.55733 | 19506.55 | 0 | 0 | 40000 | 0 | 4052.8 | 15453.75 | 0 | 0 | 15453.75 | 0 | 0 | 0 | 0
2022011722 | 2 | 0.53986 | 43188.8 | 0 | 0 | 0.57432 | 20101.2 | 0 | 0 | 40000 | 0 | 3188.8 | 16912.4 | 0 | 0 | 16912.4 | 0 | 0 | 0 | 0
2022011723 | 2 | 0.51971 | 41576.8 | 0 | 0 | 0.57849 | 20247.15 | 0 | 0 | 40000 | 0 | 1576.8 | 18670.35 | 0 | 0 | 18670.35 | 0 | 0 | 0 | 0
2022011724 | 2 | 0.49876 | 39900.8 | 0 | 0 | 0.58271 | 20394.85 | 0 | 0 | 39900.8 | 99.2 | 0 | 20394.85 | 0 | 0 | 20494.05 | 0 | 0 | 0 | 0
2022011801 | 3 | 0.48684 | 38947.2 | 0 | 0 | 0.58259 | 20390.65 | 0 | 0 | 38947.2 | 1052.8 | 0 | 20390.65 | 0 | 0 | 21443.45 | 0 | 0 | 0 | 0
2022011802 | 3 | 0.48165 | 38532 | 0 | 0 | 0.581 | 20335 | 0 | 0 | 38532 | 1468 | 0 | 20335 | 0 | 0 | 21803 | 0 | 0 | 0 | 0
2022011803 | 3 | 0.48248 | 38598.4 | 0 | 0 | 0.58294 | 20402.9 | 0 | 0 | 38598.4 | 1401.6 | 0 | 20402.9 | 0 | 0 | 21804.5 | 0 | 0 | 0 | 0
2022011804 | 3 | 0.4887 | 39096 | 0 | 0 | 0.58228 | 20379.8 | 0 | 0 | 39096 | 904 | 0 | 20379.8 | 0 | 0 | 21283.8 | 0 | 0 | 0 | 0
2022011805 | 3 | 0.5028 | 40224 | 0 | 0 | 0.58669 | 20534.15 | 0 | 0 | 40000 | 0 | 224 | 20310.15 | 0 | 0 | 20310.15 | 0 | 0 | 0 | 0
2022011806 | 3 | 0.5345 | 42760 | 0 | 0 | 0.60275 | 21096.25 | 0 | 0 | 40000 | 0 | 2760 | 18336.25 | 0 | 0 | 18336.25 | 0 | 0 | 0 | 0
2022011807 | 3 | 0.58194 | 46555.2 | 0 | 0 | 0.6403 | 22410.5 | 0 | 0 | 40000 | 0 | 6555.2 | 15855.3 | 0 | 0 | 15855.3 | 0 | 0 | 0 | 0
2022011808 | 3 | 0.60087 | 48069.6 | 0 | 0 | 0.64226 | 22479.1 | 0.00397 | 55.58 | 40000 | 0 | 8069.6 | 14409.5 | 0 | 55.58 | 14465.08 | 0 | 0 | 0 | 0
2022011809 | 3 | 0.58729 | 46983.2 | 0 | 0 | 0.5906 | 20671 | 0.20348 | 2848.72 | 40000 | 0 | 6983.2 | 13687.8 | 0 | 2848.72 | 16536.52 | 0 | 0 | 0 | 0
2022011810 | 3 | 0.56531 | 45224.8 | 0 | 0 | 0.48489 | 16971.15 | 0.48452 | 6783.28 | 40000 | 0 | 5224.8 | 11746.35 | 0 | 6783.28 | 18529.63 | 0 | 0 | 0 | 0
2022011811 | 3 | 0.54478 | 43582.4 | 0 | 0 | 0.50517 | 17680.95 | 0.58099 | 8133.86 | 40000 | 0 | 3582.4 | 14098.55 | 0 | 8133.86 | 22232.41 | 0 | 0 | 0 | 0
2022011812 | 3 | 0.52944 | 42355.2 | 0 | 0 | 0.54199 | 18969.65 | 0.52613 | 7365.82 | 40000 | 0 | 2355.2 | 16614.45 | 0 | 7365.82 | 23980.27 | 0 | 0 | 0 | 0
2022011813 | 3 | 0.51711 | 41368.8 | 0 | 0 | 0.57573 | 20150.55 | 0.3764 | 5269.6 | 40000 | 0 | 1368.8 | 18781.75 | 0 | 5269.6 | 24051.35 | 0 | 0 | 0 | 0
2022011814 | 3 | 0.51117 | 40893.6 | 0 | 0 | 0.57271 | 20044.85 | 0.35366 | 4951.24 | 40000 | 0 | 893.6 | 19151.25 | 0 | 4951.24 | 24102.49 | 0 | 0 | 0 | 0
2022011815 | 3 | 0.50862 | 40689.6 | 0 | 0 | 0.57083 | 19979.05 | 0.34997 | 4899.58 | 40000 | 0 | 689.6 | 19289.45 | 0 | 4899.58 | 24189.03 | 0 | 0 | 0 | 0
2022011816 | 3 | 0.50891 | 40712.8 | 0 | 0 | 0.56602 | 19810.7 | 0.36161 | 5062.54 | 40000 | 0 | 712.8 | 19097.9 | 0 | 5062.54 | 24160.44 | 0 | 0 | 0 | 0
2022011817 | 3 | 0.51173 | 40938.4 | 0 | 0 | 0.55404 | 19391.4 | 0.32793 | 4591.02 | 40000 | 0 | 938.4 | 18453 | 0 | 4591.02 | 23044.02 | 0 | 0 | 0 | 0
2022011818 | 3 | 0.51759 | 41407.2 | 0 | 0 | 0.50049 | 17517.15 | 0.09998 | 1399.72 | 40000 | 0 | 1407.2 | 16109.95 | 0 | 1399.72 | 17509.67 | 0 | 0 | 0 | 0
2022011819 | 3 | 0.53535 | 42828 | 0 | 0 | 0.43664 | 15282.4 | 0.00059 | 8.26 | 40000 | 0 | 2828 | 12454.4 | 0 | 8.26 | 12462.66 | 0 | 0 | 0 | 0
2022011820 | 3 | 0.53178 | 42542.4 | 0 | 0 | 0.46342 | 16219.7 | 0 | 0 | 40000 | 0 | 2542.4 | 13677.3 | 0 | 0 | 13677.3 | 0 | 0 | 0 | 0
2022011821 | 3 | 0.52148 | 41718.4 | 0 | 0 | 0.51393 | 17987.55 | 0 | 0 | 40000 | 0 | 1718.4 | 16269.15 | 0 | 0 | 16269.15 | 0 | 0 | 0 | 0
2022011822 | 3 | 0.5031 | 40248 | 0 | 0 | 0.5456 | 19096 | 0 | 0 | 40000 | 0 | 248 | 18848 | 0 | 0 | 18848 | 0 | 0 | 0 | 0
2022011823 | 3 | 0.47725 | 38180 | 0 | 0 | 0.52811 | 18483.85 | 0 | 0 | 38180 | 1820 | 0 | 18483.85 | 0 | 0 | 20303.85 | 0 | 0 | 0 | 0
2022011824 | 3 | 0.45037 | 36029.6 | 0 | 0 | 0.52929 | 18525.15 | 0 | 0 | 36029.6 | 3970.4 | 0 | 18525.15 | 0 | 0 | 22495.55 | 0 | 0 | 0 | 0
2022011901 | 4 | 0.43155 | 34524 | 0 | 0 | 0.49645 | 17375.75 | 0 | 0 | 34524 | 5476 | 0 | 17375.75 | 0 | 0 | 22851.75 | 0 | 0 | 0 | 0
2022011902 | 4 | 0.41947 | 33557.6 | 0 | 0 | 0.47911 | 16768.85 | 0 | 0 | 33557.6 | 6442.4 | 0 | 16768.85 | 0 | 0 | 23211.25 | 0 | 0 | 0 | 0
2022011903 | 4 | 0.4152 | 33216 | 0 | 0 | 0.46147 | 16151.45 | 0 | 0 | 33216 | 6784 | 0 | 16151.45 | 0 | 0 | 22935.45 | 0 | 0 | 0 | 0
2022011904 | 4 | 0.41719 | 33375.2 | 0 | 0 | 0.49055 | 17169.25 | 0 | 0 | 33375.2 | 6624.8 | 0 | 17169.25 | 0 | 0 | 23794.05 | 0 | 0 | 0 | 0
2022011905 | 4 | 0.42441 | 33952.8 | 0 | 0 | 0.48976 | 17141.6 | 0 | 0 | 33952.8 | 6047.2 | 0 | 17141.6 | 0 | 0 | 23188.8 | 0 | 0 | 0 | 0
2022011906 | 4 | 0.44773 | 35818.4 | 0 | 0 | 0.47412 | 16594.2 | 0 | 0 | 35818.4 | 4181.6 | 0 | 16594.2 | 0 | 0 | 20775.8 | 0 | 0 | 0 | 0
2022011907 | 4 | 0.48755 | 39004 | 0 | 0 | 0.49804 | 17431.4 | 0 | 0 | 39004 | 996 | 0 | 17431.4 | 0 | 0 | 18427.4 | 0 | 0 | 0 | 0
2022011908 | 4 | 0.50798 | 40638.4 | 0 | 0 | 0.53184 | 18614.4 | 0.00289 | 40.46 | 40000 | 0 | 638.4 | 17976 | 0 | 40.46 | 18016.46 | 0 | 0 | 0 | 0
2022011909 | 4 | 0.51177 | 40941.6 | 0 | 0 | 0.51355 | 17974.25 | 0.1946 | 2724.4 | 40000 | 0 | 941.6 | 17032.65 | 0 | 2724.4 | 19757.05 | 0 | 0 | 0 | 0
2022011910 | 4 | 0.51865 | 41492 | 0 | 0 | 0.46897 | 16413.95 | 0.56233 | 7872.62 | 40000 | 0 | 1492 | 14921.95 | 0 | 7872.62 | 22794.57 | 0 | 0 | 0 | 0
2022011911 | 4 | 0.52397 | 41917.6 | 0 | 0 | 0.51289 | 17951.15 | 0.45916 | 6428.24 | 40000 | 0 | 1917.6 | 16033.55 | 0 | 6428.24 | 22461.79 | 0 | 0 | 0 | 0
2022011912 | 4 | 0.52538 | 42030.4 | 0 | 0 | 0.54383 | 19034.05 | 0.34034 | 4764.76 | 40000 | 0 | 2030.4 | 17003.65 | 0 | 4764.76 | 21768.41 | 0 | 0 | 0 | 0
2022011913 | 4 | 0.52843 | 42274.4 | 0 | 0 | 0.52318 | 18311.3 | 0.31487 | 4408.18 | 40000 | 0 | 2274.4 | 16036.9 | 0 | 4408.18 | 20445.08 | 0 | 0 | 0 | 0
2022011914 | 4 | 0.53371 | 42696.8 | 0 | 0 | 0.53549 | 18742.15 | 0.29605 | 4144.7 | 40000 | 0 | 2696.8 | 16045.35 | 0 | 4144.7 | 20190.05 | 0 | 0 | 0 | 0
2022011915 | 4 | 0.53707 | 42965.6 | 0 | 0 | 0.54347 | 19021.45 | 0.27231 | 3812.34 | 40000 | 0 | 2965.6 | 16055.85 | 0 | 3812.34 | 19868.19 | 0 | 0 | 0 | 0
2022011916 | 4 | 0.53987 | 43189.6 | 0 | 0 | 0.58186 | 20365.1 | 0.18862 | 2640.68 | 40000 | 0 | 3189.6 | 17175.5 | 0 | 2640.68 | 19816.18 | 0 | 0 | 0 | 0
2022011917 | 4 | 0.54565 | 43652 | 0 | 0 | 0.60894 | 21312.9 | 0.0961 | 1345.4 | 40000 | 0 | 3652 | 17660.9 | 0 | 1345.4 | 19006.3 | 0 | 0 | 0 | 0
2022011918 | 4 | 0.56254 | 45003.2 | 0 | 0 | 0.61587 | 21555.45 | 0.04195 | 587.3 | 40000 | 0 | 5003.2 | 16552.25 | 0 | 587.3 | 17139.55 | 0 | 0 | 0 | 0
2022011919 | 4 | 0.58351 | 46680.8 | 0 | 0 | 0.64454 | 22558.9 | 0.00025 | 3.5 | 40000 | 0 | 6680.8 | 15878.1 | 0 | 3.5 | 15881.6 | 0 | 0 | 0 | 0
2022011920 | 4 | 0.58669 | 46935.2 | 0 | 0 | 0.64773 | 22670.55 | 0 | 0 | 40000 | 0 | 6935.2 | 15735.35 | 0 | 0 | 15735.35 | 0 | 0 | 0 | 0
2022011921 | 4 | 0.584 | 46720 | 0 | 0 | 0.62892 | 22012.2 | 0 | 0 | 40000 | 0 | 6720 | 15292.2 | 0 | 0 | 15292.2 | 0 | 0 | 0 | 0
2022011922 | 4 | 0.57477 | 45981.6 | 0 | 0 | 0.6044 | 21154 | 0 | 0 | 40000 | 0 | 5981.6 | 15172.4 | 0 | 0 | 15172.4 | 0 | 0 | 0 | 0
2022011923 | 4 | 0.55323 | 44258.4 | 0 | 0 | 0.58661 | 20531.35 | 0 | 0 | 40000 | 0 | 4258.4 | 16272.95 | 0 | 0 | 16272.95 | 0 | 0 | 0 | 0
2022011924 | 4 | 0.53553 | 42842.4 | 0 | 0 | 0.58893 | 20612.55 | 0 | 0 | 40000 | 0 | 2842.4 | 17770.15 | 0 | 0 | 17770.15 | 0 | 0 | 0 | 0
2022012001 | 5 | 0.52786 | 42228.8 | 0 | 0 | 0.6052 | 21182 | 0 | 0 | 40000 | 0 | 2228.8 | 18953.2 | 0 | 0 | 18953.2 | 0 | 0 | 0 | 0
2022012002 | 5 | 0.52793 | 42234.4 | 0 | 0 | 0.6044 | 21154 | 0 | 0 | 40000 | 0 | 2234.4 | 18919.6 | 0 | 0 | 18919.6 | 0 | 0 | 0 | 0
2022012003 | 5 | 0.53472 | 42777.6 | 0 | 0 | 0.61468 | 21513.8 | 0 | 0 | 40000 | 0 | 2777.6 | 18736.2 | 0 | 0 | 18736.2 | 0 | 0 | 0 | 0
2022012004 | 5 | 0.55034 | 44027.2 | 0 | 0 | 0.62988 | 22045.8 | 0 | 0 | 40000 | 0 | 4027.2 | 18018.6 | 0 | 0 | 18018.6 | 0 | 0 | 0 | 0
2022012005 | 5 | 0.57247 | 45797.6 | 0 | 0 | 0.64419 | 22546.65 | 0 | 0 | 40000 | 0 | 5797.6 | 16749.05 | 0 | 0 | 16749.05 | 0 | 0 | 0 | 0
2022012006 | 5 | 0.61214 | 48971.2 | 0 | 0 | 0.64809 | 22683.15 | 0 | 0 | 40000 | 0 | 8971.2 | 13711.95 | 0 | 0 | 13711.95 | 0 | 0 | 0 | 0
2022012007 | 5 | 0.66987 | 53589.6 | 0 | 0 | 0.63835 | 22342.25 | 0 | 0 | 40000 | 0 | 13589.6 | 8752.65 | 0 | 0 | 8752.65 | 0 | 0 | 0 | 0
2022012008 | 5 | 0.70905 | 56724 | 0 | 0 | 0.63118 | 22091.3 | 0.00078 | 10.92 | 40000 | 0 | 16724 | 5367.3 | 0 | 10.92 | 5378.22 | 0 | 0 | 0 | 0
2022012009 | 5 | 0.72637 | 58109.6 | 0 | 0 | 0.6092 | 21322 | 0.03403 | 476.42 | 40000 | 0 | 18109.6 | 3212.4 | 0 | 476.42 | 3688.82 | 0 | 0 | 0 | 0
2022012010 | 5 | 0.74046 | 59236.8 | 0 | 0 | 0.57289 | 20051.15 | 0.11448 | 1602.72 | 40000 | 0 | 19236.8 | 814.35 | 0 | 1602.72 | 2417.07 | 0 | 0 | 0 | 0
2022012011 | 5 | 0.74597 | 59677.6 | 0 | 0 | 0.54664 | 19132.4 | 0.1804 | 2525.6 | 40000 | 0 | 19132.4 | 0 | 545.2 | 1980.4 | 1980.4 | 0 | 0 | 0 | 0
2022012012 | 5 | 0.74371 | 59496.8 | 0 | 0 | 0.52692 | 18442.2 | 0.25905 | 3626.7 | 40000 | 0 | 18442.2 | 0 | 1054.6 | 2572.1 | 2572.1 | 0 | 0 | 0 | 0
2022012013 | 5 | 0.73312 | 58649.6 | 0 | 0 | 0.50478 | 17667.3 | 0.29979 | 4197.06 | 40000 | 0 | 17667.3 | 0 | 982.3 | 3214.76 | 3214.76 | 0 | 0 | 0 | 0
2022012014 | 5 | 0.72292 | 57833.6 | 0 | 0 | 0.47083 | 16479.05 | 0.33787 | 4730.18 | 40000 | 0 | 16479.05 | 0 | 1354.55 | 3375.63 | 3375.63 | 0 | 0 | 0 | 0
2022012015 | 5 | 0.7122 | 56976 | 0 | 0 | 0.43848 | 15346.8 | 0.34922 | 4889.08 | 40000 | 0 | 15346.8 | 0 | 1629.2 | 3259.88 | 3259.88 | 0 | 0 | 0 | 0
2022012016 | 5 | 0.71289 | 57031.2 | 0 | 0 | 0.42528 | 14884.8 | 0.27388 | 3834.32 | 40000 | 0 | 14884.8 | 0 | 2146.4 | 1687.92 | 1687.92 | 0 | 0 | 0 | 0
2022012017 | 5 | 0.7279 | 58232 | 0 | 0 | 0.39201 | 13720.35 | 0.17055 | 2387.7 | 40000 | 0 | 13720.35 | 0 | 2387.7 | 0 | 0 | 2123.95 | 0 | 0 | 2123.95
2022012018 | 5 | 0.75263 | 60210.4 | 0 | 0 | 0.33387 | 11685.45 | 0.05029 | 704.06 | 40000 | 0 | 11685.45 | 0 | 704.06 | 0 | 0 | 7820.89 | 0 | 0 | 7820.89
2022012019 | 5 | 0.77695 | 62156 | 0 | 0 | 0.2811 | 9838.5 | 0.00049 | 6.86 | 40000 | 0 | 9838.5 | 0 | 6.86 | 0 | 0 | 12310.64 | 0 | 0 | 12310.64
2022012020 | 5 | 0.77522 | 62017.6 | 0 | 0 | 0.26939 | 9428.65 | 0 | 0 | 40000 | 0 | 9428.65 | 0 | 0 | 0 | 0 | 12588.95 | 0 | 0 | 12588.95
2022012021 | 5 | 0.76644 | 61315.2 | 0 | 0 | 0.24251 | 8487.85 | 0 | 0 | 40000 | 0 | 8487.85 | 0 | 0 | 0 | 0 | 12827.35 | 0 | 0 | 12827.35
2022012022 | 5 | 0.74711 | 59768.8 | 0 | 0 | 0.21329 | 7465.15 | 0 | 0 | 40000 | 0 | 7465.15 | 0 | 0 | 0 | 0 | 12303.65 | 0 | 0 | 12303.65
2022012023 | 5 | 0.71737 | 57389.6 | 0 | 0 | 0.19792 | 6927.2 | 0 | 0 | 40000 | 0 | 6927.2 | 0 | 0 | 0 | 0 | 10462.4 | 0 | 0 | 10462.4
2022012024 | 5 | 0.69313 | 55450.4 | 0 | 0 | 0.19836 | 6942.6 | 0 | 0 | 40000 | 0 | 6942.6 | 0 | 0 | 0 | 0 | 8507.8 | 0 | 0 | 8507.8
2022012101 | 6 | 0.67865 | 54292 | 0 | 0 | 0.20034 | 7011.9 | 0 | 0 | 40000 | 0 | 7011.9 | 0 | 0 | 0 | 0 | 7280.1 | 0 | 0 | 7280.1
2022012102 | 6 | 0.67184 | 53747.2 | 0 | 0 | 0.20902 | 7315.7 | 0 | 0 | 40000 | 0 | 7315.7 | 0 | 0 | 0 | 0 | 6431.5 | 0 | 0 | 6431.5
2022012103 | 6 | 0.67074 | 53659.2 | 0 | 0 | 0.19977 | 6991.95 | 0 | 0 | 40000 | 0 | 6991.95 | 0 | 0 | 0 | 0 | 6667.25 | 0 | 0 | 6667.25
2022012104 | 6 | 0.67867 | 54293.6 | 0 | 0 | 0.17616 | 6165.6 | 0 | 0 | 40000 | 0 | 6165.6 | 0 | 0 | 0 | 0 | 8128 | 0 | 0 | 8128
2022012105 | 6 | 0.69337 | 55469.6 | 0 | 0 | 0.16332 | 5716.2 | 0 | 0 | 40000 | 0 | 5716.2 | 0 | 0 | 0 | 0 | 9753.4 | 0 | 0 | 9753.4
2022012106 | 6 | 0.72506 | 58004.8 | 0 | 0 | 0.16275 | 5696.25 | 0 | 0 | 40000 | 0 | 5696.25 | 0 | 0 | 0 | 0 | 12308.55 | 0 | 0 | 12308.55
2022012107 | 6 | 0.77053 | 61642.4 | 0 | 0 | 0.16199 | 5669.65 | 0 | 0 | 40000 | 0 | 5669.65 | 0 | 0 | 0 | 0 | 15972.75 | 0 | 0 | 15972.75
2022012108 | 6 | 0.79549 | 63639.2 | 0 | 0 | 0.16647 | 5826.45 | 0.00345 | 48.3 | 40000 | 0 | 5826.45 | 0 | 48.3 | 0 | 0 | 17764.45 | 0 | 0 | 17764.45
2022012109 | 6 | 0.78776 | 63020.8 | 0 | 0 | 0.16977 | 5941.95 | 0.2218 | 3105.2 | 40000 | 0 | 5941.95 | 0 | 3105.2 | 0 | 0 | 13973.65 | 0 | 0 | 13973.65
2022012110 | 6 | 0.76802 | 61441.6 | 0 | 0 | 0.13229 | 4630.15 | 0.61192 | 8566.88 | 40000 | 0 | 4630.15 | 0 | 8566.88 | 0 | 0 | 8244.57 | 0 | 0 | 8244.57
2022012111 | 6 | 0.74251 | 59400.8 | 0 | 0 | 0.13495 | 4723.25 | 0.67915 | 9508.1 | 40000 | 0 | 4723.25 | 0 | 9508.1 | 0 | 0 | 5169.45 | 0 | 0 | 5169.45
2022012112 | 6 | 0.7078 | 56624 | 0 | 0 | 0.14693 | 5142.55 | 0.68082 | 9531.48 | 40000 | 0 | 5142.55 | 0 | 9531.48 | 0 | 0 | 1949.97 | 0 | 0 | 1949.97
2022012113 | 6 | 0.67036 | 53628.8 | 0 | 0 | 0.17372 | 6080.2 | 0.6858 | 9601.2 | 40000 | 0 | 6080.2 | 0 | 7548.6 | 2052.6 | 2052.6 | 0 | 0 | 0 | 0
2022012114 | 6 | 0.63964 | 51171.2 | 0 | 0 | 0.17671 | 6184.85 | 0.69455 | 9723.7 | 40000 | 0 | 6184.85 | 0 | 4986.35 | 4737.35 | 4737.35 | 0 | 0 | 0 | 0
2022012115 | 6 | 0.61137 | 48909.6 | 0 | 0 | 0.19448 | 6806.8 | 0.7099 | 9938.6 | 40000 | 0 | 6806.8 | 0 | 2102.8 | 7835.8 | 7835.8 | 0 | 0 | 0 | 0
2022012116 | 6 | 0.59624 | 47699.2 | 0 | 0 | 0.20807 | 7282.45 | 0.74246 | 10394.44 | 40000 | 0 | 7282.45 | 0 | 416.75 | 9977.69 | 9977.69 | 0 | 0 | 0 | 0
2022012117 | 6 | 0.59546 | 47636.8 | 0 | 0 | 0.21087 | 7380.45 | 0.62751 | 8785.14 | 40000 | 0 | 7380.45 | 0 | 256.35 | 8528.79 | 8528.79 | 0 | 0 | 0 | 0
2022012118 | 6 | 0.61543 | 49234.4 | 0 | 0 | 0.20779 | 7272.65 | 0.19106 | 2674.84 | 40000 | 0 | 7272.65 | 0 | 1961.75 | 713.09 | 713.09 | 0 | 0 | 0 | 0
2022012119 | 6 | 0.65445 | 52356 | 0 | 0 | 0.25192 | 8817.2 | 0.00187 | 26.18 | 40000 | 0 | 8817.2 | 0 | 26.18 | 0 | 0 | 3512.62 | 0 | 0 | 3512.62
2022012120 | 6 | 0.66781 | 53424.8 | 0 | 0 | 0.34073 | 11925.55 | 0 | 0 | 40000 | 0 | 11925.55 | 0 | 0 | 0 | 0 | 1499.25 | 0 | 0 | 1499.25
2022012121 | 6 | 0.67447 | 53957.6 | 0 | 0 | 0.40536 | 14187.6 | 0 | 0 | 40000 | 0 | 13957.6 | 230 | 0 | 0 | 230 | 0 | 0 | 0 | 0
2022012122 | 6 | 0.67336 | 53868.8 | 0 | 0 | 0.44387 | 15535.45 | 0 | 0 | 40000 | 0 | 13868.8 | 1666.65 | 0 | 0 | 1666.65 | 0 | 0 | 0 | 0
2022012123 | 6 | 0.66206 | 52964.8 | 0 | 0 | 0.43229 | 15130.15 | 0 | 0 | 40000 | 0 | 12964.8 | 2165.35 | 0 | 0 | 2165.35 | 0 | 0 | 0 | 0
2022012124 | 6 | 0.64688 | 51750.4 | 0 | 0 | 0.41327 | 14464.45 | 0 | 0 | 40000 | 0 | 11750.4 | 2714.05 | 0 | 0 | 2714.05 | 0 | 0 | 0 | 0
2022012201 | 7 | 0.63693 | 50954.4 | 0 | 0 | 0.3754 | 13139 | 0 | 0 | 40000 | 0 | 10954.4 | 2184.6 | 0 | 0 | 2184.6 | 0 | 0 | 0 | 0
2022012202 | 7 | 0.6348 | 50784 | 0 | 0 | 0.32936 | 11527.6 | 0 | 0 | 40000 | 0 | 10784 | 743.6 | 0 | 0 | 743.6 | 0 | 0 | 0 | 0
2022012203 | 7 | 0.6371 | 50968 | 0 | 0 | 0.27891 | 9761.85 | 0 | 0 | 40000 | 0 | 9761.85 | 0 | 0 | 0 | 0 | 1206.15 | 0 | 0 | 1206.15
2022012204 | 7 | 0.64572 | 51657.6 | 0 | 0 | 0.23631 | 8270.85 | 0 | 0 | 40000 | 0 | 8270.85 | 0 | 0 | 0 | 0 | 3386.75 | 0 | 0 | 3386.75
2022012205 | 7 | 0.65817 | 52653.6 | 0 | 0 | 0.20841 | 7294.35 | 0 | 0 | 40000 | 0 | 7294.35 | 0 | 0 | 0 | 0 | 5359.25 | 0 | 0 | 5359.25
2022012206 | 7 | 0.6786 | 54288 | 0 | 0 | 0.1839 | 6436.5 | 0 | 0 | 40000 | 0 | 6436.5 | 0 | 0 | 0 | 0 | 7851.5 | 0 | 0 | 7851.5
2022012207 | 7 | 0.70499 | 56399.2 | 0 | 0 | 0.18632 | 6521.2 | 0 | 0 | 40000 | 0 | 6521.2 | 0 | 0 | 0 | 0 | 9878 | 0 | 0 | 9878
2022012208 | 7 | 0.72647 | 58117.6 | 0 | 0 | 0.1802 | 6307 | 0.00691 | 96.74 | 40000 | 0 | 6307 | 0 | 96.74 | 0 | 0 | 11713.86 | 0 | 0 | 11713.86
2022012209 | 7 | 0.72418 | 57934.4 | 0 | 0 | 0.13532 | 4736.2 | 0.2321 | 3249.4 | 40000 | 0 | 4736.2 | 0 | 3249.4 | 0 | 0 | 9948.8 | 0 | 0 | 9948.8
2022012210 | 7 | 0.6992 | 55936 | 0 | 0 | 0.08976 | 3141.6 | 0.49476 | 6926.64 | 40000 | 0 | 3141.6 | 0 | 6926.64 | 0 | 0 | 5867.76 | 0 | 0 | 5867.76
2022012211 | 7 | 0.66893 | 53514.4 | 0 | 0 | 0.06581 | 2303.35 | 0.45158 | 6322.12 | 40000 | 0 | 2303.35 | 0 | 6322.12 | 0 | 0 | 4888.93 | 0 | 0 | 4888.93
2022012212 | 7 | 0.63904 | 51123.2 | 0 | 0 | 0.05506 | 1927.1 | 0.42541 | 5955.74 | 40000 | 0 | 1927.1 | 0 | 5955.74 | 0 | 0 | 3240.36 | 0 | 0 | 3240.36
2022012213 | 7 | 0.60626 | 48500.8 | 0 | 0 | 0.05536 | 1937.6 | 0.42846 | 5998.44 | 40000 | 0 | 1937.6 | 0 | 5998.44 | 0 | 0 | 564.76 | 0 | 0 | 564.76
2022012214 | 7 | 0.57618 | 46094.4 | 0 | 0 | 0.0498 | 1743 | 0.41087 | 5752.18 | 40000 | 0 | 1743 | 0 | 4351.4 | 1400.78 | 1400.78 | 0 | 0 | 0 | 0
2022012215 | 7 | 0.55407 | 44325.6 | 0 | 0 | 0.04792 | 1677.2 | 0.4053 | 5674.2 | 40000 | 0 | 1677.2 | 0 | 2648.4 | 3025.8 | 3025.8 | 0 | 0 | 0 | 0
2022012216 | 7 | 0.54363 | 43490.4 | 0 | 0 | 0.05459 | 1910.65 | 0.34249 | 4794.86 | 40000 | 0 | 1910.65 | 0 | 1579.75 | 3215.11 | 3215.11 | 0 | 0 | 0 | 0
2022012217 | 7 | 0.5447 | 43576 | 0 | 0 | 0.064 | 2240 | 0.24648 | 3450.72 | 40000 | 0 | 2240 | 0 | 1336 | 2114.72 | 2114.72 | 0 | 0 | 0 | 0
2022012218 | 7 | 0.56372 | 45097.6 | 0 | 0 | 0.06817 | 2385.95 | 0.06379 | 893.06 | 40000 | 0 | 2385.95 | 0 | 893.06 | 0 | 0 | 1818.59 | 0 | 0 | 1818.59
2022012219 | 7 | 0.59815 | 47852 | 0 | 0 | 0.06982 | 2443.7 | 0.00059 | 8.26 | 40000 | 0 | 2443.7 | 0 | 8.26 | 0 | 0 | 5400.04 | 0 | 0 | 5400.04
2022012220 | 7 | 0.60868 | 48694.4 | 0 | 0 | 0.08009 | 2803.15 | 0 | 0 | 40000 | 0 | 2803.15 | 0 | 0 | 0 | 0 | 5891.25 | 0 | 0 | 5891.25
2022012221 | 7 | 0.61139 | 48911.2 | 0 | 0 | 0.09634 | 3371.9 | 0 | 0 | 40000 | 0 | 3371.9 | 0 | 0 | 0 | 0 | 5539.3 | 0 | 0 | 5539.3
2022012222 | 7 | 0.60779 | 48623.2 | 0 | 0 | 0.12314 | 4309.9 | 0 | 0 | 40000 | 0 | 4309.9 | 0 | 0 | 0 | 0 | 4313.3 | 0 | 0 | 4313.3
2022012223 | 7 | 0.59752 | 47801.6 | 0 | 0 | 0.1702 | 5957 | 0 | 0 | 40000 | 0 | 5957 | 0 | 0 | 0 | 0 | 1844.6 | 0 | 0 | 1844.6
2022012224 | 7 | 0.58465 | 46772 | 0 | 0 | 0.19926 | 6974.1 | 0 | 0 | 40000 | 0 | 6772 | 202.1 | 0 | 0 | 202.1 | 0 | 0 | 0 | 0
2022012301 | 1 | 0.57474 | 45979.2 | 0 | 0 | 0.20277 | 7096.95 | 0 | 0 | 40000 | 0 | 5979.2 | 1117.75 | 0 | 0 | 1117.75 | 0 | 0 | 0 | 0
2022012302 | 1 | 0.56784 | 45427.2 | 0 | 0 | 0.19948 | 6981.8 | 0 | 0 | 40000 | 0 | 5427.2 | 1554.6 | 0 | 0 | 1554.6 | 0 | 0 | 0 | 0
2022012303 | 1 | 0.56521 | 45216.8 | 0 | 0 | 0.20655 | 7229.25 | 0 | 0 | 40000 | 0 | 5216.8 | 2012.45 | 0 | 0 | 2012.45 | 0 | 0 | 0 | 0
2022012304 | 1 | 0.56625 | 45300 | 0 | 0 | 0.21686 | 7590.1 | 0 | 0 | 40000 | 0 | 5300 | 2290.1 | 0 | 0 | 2290.1 | 0 | 0 | 0 | 0
2022012305 | 1 | 0.56979 | 45583.2 | 0 | 0 | 0.2197 | 7689.5 | 0 | 0 | 40000 | 0 | 5583.2 | 2106.3 | 0 | 0 | 2106.3 | 0 | 0 | 0 | 0
2022012306 | 1 | 0.57978 | 46382.4 | 0 | 0 | 0.21246 | 7436.1 | 0 | 0 | 40000 | 0 | 6382.4 | 1053.7 | 0 | 0 | 1053.7 | 0 | 0 | 0 | 0
2022012307 | 1 | 0.59432 | 47545.6 | 0 | 0 | 0.20199 | 7069.65 | 0 | 0 | 40000 | 0 | 7069.65 | 0 | 0 | 0 | 0 | 475.95 | 0 | 0 | 475.95
2022012308 | 1 | 0.60887 | 48709.6 | 0 | 0 | 0.18307 | 6407.45 | 0.004 | 56 | 40000 | 0 | 6407.45 | 0 | 56 | 0 | 0 | 2246.15 | 0 | 0 | 2246.15
2022012309 | 1 | 0.61424 | 49139.2 | 0 | 0 | 0.16843 | 5895.05 | 0.11774 | 1648.36 | 40000 | 0 | 5895.05 | 0 | 1648.36 | 0 | 0 | 1595.79 | 0 | 0 | 1595.79
2022012310 | 1 | 0.60169 | 48135.2 | 0 | 0 | 0.11024 | 3858.4 | 0.31666 | 4433.24 | 40000 | 0 | 3858.4 | 0 | 4276.8 | 156.44 | 156.44 | 0 | 0 | 0 | 0
2022012311 | 1 | 0.57924 | 46339.2 | 0 | 0 | 0.06841 | 2394.35 | 0.40515 | 5672.1 | 40000 | 0 | 2394.35 | 0 | 3944.85 | 1727.25 | 1727.25 | 0 | 0 | 0 | 0
2022012312 | 1 | 0.55176 | 44140.8 | 0 | 0 | 0.04901 | 1715.35 | 0.46127 | 6457.78 | 40000 | 0 | 1715.35 | 0 | 2425.45 | 4032.33 | 4032.33 | 0 | 0 | 0 | 0
2022012313 | 1 | 0.53218 | 42574.4 | 0 | 0 | 0.04595 | 1608.25 | 0.49051 | 6867.14 | 40000 | 0 | 1608.25 | 0 | 966.15 | 5900.99 | 5900.99 | 0 | 0 | 0 | 0
2022012314 | 1 | 0.51421 | 41136.8 | 0 | 0 | 0.04882 | 1708.7 | 0.52202 | 7308.28 | 40000 | 0 | 1136.8 | 571.9 | 0 | 7308.28 | 7880.18 | 0 | 0 | 0 | 0
2022012315 | 1 | 0.49983 | 39986.4 | 0 | 0 | 0.04551 | 1592.85 | 0.50216 | 7030.24 | 39986.4 | 13.6 | 0 | 1592.85 | 0 | 7030.24 | 8636.69 | 0 | 0 | 0 | 0
2022012316 | 1 | 0.4948 | 39584 | 0 | 0 | 0.03998 | 1399.3 | 0.49912 | 6987.68 | 39584 | 416 | 0 | 1399.3 | 0 | 6987.68 | 8802.98 | 0 | 0 | 0 | 0
2022012317 | 1 | 0.49884 | 39907.2 | 0 | 0 | 0.04517 | 1580.95 | 0.38687 | 5416.18 | 39907.2 | 92.8 | 0 | 1580.95 | 0 | 5416.18 | 7089.93 | 0 | 0 | 0 | 0
2022012318 | 1 | 0.51706 | 41364.8 | 0 | 0 | 0.05342 | 1869.7 | 0.10733 | 1502.62 | 40000 | 0 | 1364.8 | 504.9 | 0 | 1502.62 | 2007.52 | 0 | 0 | 0 | 0
2022012319 | 1 | 0.54751 | 43800.8 | 0 | 0 | 0.07855 | 2749.25 | 0.00097 | 13.58 | 40000 | 0 | 2749.25 | 0 | 13.58 | 0 | 0 | 1037.97 | 0 | 0 | 1037.97
2022012320 | 1 | 0.55244 | 44195.2 | 0 | 0 | 0.12184 | 4264.4 | 0 | 0 | 40000 | 0 | 4195.2 | 69.2 | 0 | 0 | 69.2 | 0 | 0 | 0 | 0
2022012321 | 1 | 0.54557 | 43645.6 | 0 | 0 | 0.15092 | 5282.2 | 0 | 0 | 40000 | 0 | 3645.6 | 1636.6 | 0 | 0 | 1636.6 | 0 | 0 | 0 | 0
2022012322 | 1 | 0.53713 | 42970.4 | 0 | 0 | 0.17971 | 6289.85 | 0 | 0 | 40000 | 0 | 2970.4 | 3319.45 | 0 | 0 | 3319.45 | 0 | 0 | 0 | 0
2022012323 | 1 | 0.51407 | 41125.6 | 0 | 0 | 0.23073 | 8075.55 | 0 | 0 | 40000 | 0 | 1125.6 | 6949.95 | 0 | 0 | 6949.95 | 0 | 0 | 0 | 0
2022012324 | 1 | 0.49236 | 39388.8 | 0 | 0 | 0.27756 | 9714.6 | 0 | 0 | 39388.8 | 611.2 | 0 | 9714.6 | 0 | 0 | 10325.8 | 0 | 0 | 0 | 0
2022012401 | 2 | 0.47897 | 38317.6 | 0 | 0 | 0.31528 | 11034.8 | 0 | 0 | 38317.6 | 1682.4 | 0 | 11034.8 | 0 | 0 | 12717.2 | 0 | 0 | 0 | 0
2022012402 | 2 | 0.47258 | 37806.4 | 0 | 0 | 0.35012 | 12254.2 | 0 | 0 | 37806.4 | 2193.6 | 0 | 12254.2 | 0 | 0 | 14447.8 | 0 | 0 | 0 | 0
2022012403 | 2 | 0.47155 | 37724 | 0 | 0 | 0.36034 | 12611.9 | 0 | 0 | 37724 | 2276 | 0 | 12611.9 | 0 | 0 | 14887.9 | 0 | 0 | 0 | 0
2022012404 | 2 | 0.47727 | 38181.6 | 0 | 0 | 0.35742 | 12509.7 | 0 | 0 | 38181.6 | 1818.4 | 0 | 12509.7 | 0 | 0 | 14328.1 | 0 | 0 | 0 | 0
2022012405 | 2 | 0.4901 | 39208 | 0 | 0 | 0.34324 | 12013.4 | 0 | 0 | 39208 | 792 | 0 | 12013.4 | 0 | 0 | 12805.4 | 0 | 0 | 0 | 0
2022012406 | 2 | 0.51779 | 41423.2 | 0 | 0 | 0.32435 | 11352.25 | 0 | 0 | 40000 | 0 | 1423.2 | 9929.05 | 0 | 0 | 9929.05 | 0 | 0 | 0 | 0
2022012407 | 2 | 0.56115 | 44892 | 0 | 0 | 0.28319 | 9911.65 | 0 | 0 | 40000 | 0 | 4892 | 5019.65 | 0 | 0 | 5019.65 | 0 | 0 | 0 | 0
2022012408 | 2 | 0.58516 | 46812.8 | 0 | 0 | 0.26643 | 9325.05 | 0.00065 | 9.1 | 40000 | 0 | 6812.8 | 2512.25 | 0 | 9.1 | 2521.35 | 0 | 0 | 0 | 0
2022012409 | 2 | 0.58598 | 46878.4 | 0 | 0 | 0.23479 | 8217.65 | 0.13321 | 1864.94 | 40000 | 0 | 6878.4 | 1339.25 | 0 | 1864.94 | 3204.19 | 0 | 0 | 0 | 0
2022012410 | 2 | 0.58671 | 46936.8 | 0 | 0 | 0.16508 | 5777.8 | 0.45399 | 6355.86 | 40000 | 0 | 5777.8 | 0 | 1159 | 5196.86 | 5196.86 | 0 | 0 | 0 | 0
2022012411 | 2 | 0.58819 | 47055.2 | 0 | 0 | 0.12305 | 4306.75 | 0.55256 | 7735.84 | 40000 | 0 | 4306.75 | 0 | 2748.45 | 4987.39 | 4987.39 | 0 | 0 | 0 | 0
2022012412 | 2 | 0.58634 | 46907.2 | 0 | 0 | 0.13771 | 4819.85 | 0.55393 | 7755.02 | 40000 | 0 | 4819.85 | 0 | 2087.35 | 5667.67 | 5667.67 | 0 | 0 | 0 | 0
2022012413 | 2 | 0.58054 | 46443.2 | 0 | 0 | 0.14263 | 4992.05 | 0.54414 | 7617.96 | 40000 | 0 | 4992.05 | 0 | 1451.15 | 6166.81 | 6166.81 | 0 | 0 | 0 | 0
2022012414 | 2 | 0.57473 | 45978.4 | 0 | 0 | 0.13477 | 4716.95 | 0.56525 | 7913.5 | 40000 | 0 | 4716.95 | 0 | 1261.45 | 6652.05 | 6652.05 | 0 | 0 | 0 | 0
2022012415 | 2 | 0.56827 | 45461.6 | 0 | 0 | 0.14363 | 5027.05 | 0.58313 | 8163.82 | 40000 | 0 | 5027.05 | 0 | 434.55 | 7729.27 | 7729.27 | 0 | 0 | 0 | 0
2022012416 | 2 | 0.56264 | 45011.2 | 0 | 0 | 0.15467 | 5413.45 | 0.57504 | 8050.56 | 40000 | 0 | 5011.2 | 402.25 | 0 | 8050.56 | 8452.81 | 0 | 0 | 0 | 0
2022012417 | 2 | 0.56781 | 45424.8 | 0 | 0 | 0.12664 | 4432.4 | 0.52852 | 7399.28 | 40000 | 0 | 4432.4 | 0 | 992.4 | 6406.88 | 6406.88 | 0 | 0 | 0 | 0
2022012418 | 2 | 0.58375 | 46700 | 0 | 0 | 0.10493 | 3672.55 | 0.19403 | 2716.42 | 40000 | 0 | 3672.55 | 0 | 2716.42 | 0 | 0 | 311.03 | 0 | 0 | 311.03
2022012419 | 2 | 0.60369 | 48295.2 | 0 | 0 | 0.08583 | 3004.05 | 0.00241 | 33.74 | 40000 | 0 | 3004.05 | 0 | 33.74 | 0 | 0 | 5257.41 | 0 | 0 | 5257.41
2022012420 | 2 | 0.59913 | 47930.4 | 0 | 0 | 0.09318 | 3261.3 | 0 | 0 | 40000 | 0 | 3261.3 | 0 | 0 | 0 | 0 | 4669.1 | 0 | 0 | 4669.1
2022012421 | 2 | 0.58885 | 47108 | 0 | 0 | 0.1029 | 3601.5 | 0 | 0 | 40000 | 0 | 3601.5 | 0 | 0 | 0 | 0 | 3506.5 | 0 | 0 | 3506.5
2022012422 | 2 | 0.57086 | 45668.8 | 0 | 0 | 0.11657 | 4079.95 | 0 | 0 | 40000 | 0 | 4079.95 | 0 | 0 | 0 | 0 | 1588.85 | 0 | 0 | 1588.85
2022012423 | 2 | 0.54318 | 43454.4 | 0 | 0 | 0.1073 | 3755.5 | 0 | 0 | 40000 | 0 | 3454.4 | 301.1 | 0 | 0 | 301.1 | 0 | 0 | 0 | 0
2022012424 | 2 | 0.51848 | 41478.4 | 0 | 0 | 0.11275 | 3946.25 | 0 | 0 | 40000 | 0 | 1478.4 | 2467.85 | 0 | 0 | 2467.85 | 0 | 0 | 0 | 0
2022012501 | 3 | 0.50184 | 40147.2 | 0 | 0 | 0.13397 | 4688.95 | 0 | 0 | 40000 | 0 | 147.2 | 4541.75 | 0 | 0 | 4541.75 | 0 | 0 | 0 | 0
2022012502 | 3 | 0.49349 | 39479.2 | 0 | 0 | 0.17251 | 6037.85 | 0 | 0 | 39479.2 | 520.8 | 0 | 6037.85 | 0 | 0 | 6558.65 | 0 | 0 | 0 | 0
2022012503 | 3 | 0.48977 | 39181.6 | 0 | 0 | 0.2234 | 7819 | 0 | 0 | 39181.6 | 818.4 | 0 | 7819 | 0 | 0 | 8637.4 | 0 | 0 | 0 | 0
2022012504 | 3 | 0.49388 | 39510.4 | 0 | 0 | 0.27121 | 9492.35 | 0 | 0 | 39510.4 | 489.6 | 0 | 9492.35 | 0 | 0 | 9981.95 | 0 | 0 | 0 | 0
2022012505 | 3 | 0.5072 | 40576 | 0 | 0 | 0.3075 | 10762.5 | 0 | 0 | 40000 | 0 | 576 | 10186.5 | 0 | 0 | 10186.5 | 0 | 0 | 0 | 0
2022012506 | 3 | 0.53937 | 43149.6 | 0 | 0 | 0.3374 | 11809 | 0 | 0 | 40000 | 0 | 3149.6 | 8659.4 | 0 | 0 | 8659.4 | 0 | 0 | 0 | 0
2022012507 | 3 | 0.58989 | 47191.2 | 0 | 0 | 0.37823 | 13238.05 | 0 | 0 | 40000 | 0 | 7191.2 | 6046.85 | 0 | 0 | 6046.85 | 0 | 0 | 0 | 0
2022012508 | 3 | 0.61386 | 49108.8 | 0 | 0 | 0.38441 | 13454.35 | 0.00402 | 56.28 | 40000 | 0 | 9108.8 | 4345.55 | 0 | 56.28 | 4401.83 | 0 | 0 | 0 | 0
2022012509 | 3 | 0.607 | 48560 | 0 | 0 | 0.34303 | 12006.05 | 0.23873 | 3342.22 | 40000 | 0 | 8560 | 3446.05 | 0 | 3342.22 | 6788.27 | 0 | 0 | 0 | 0
2022012510 | 3 | 0.59526 | 47620.8 | 0 | 0 | 0.29668 | 10383.8 | 0.61942 | 8671.88 | 40000 | 0 | 7620.8 | 2763 | 0 | 8671.88 | 11434.88 | 0 | 0 | 0 | 0
2022012511 | 3 | 0.58005 | 46404 | 0 | 0 | 0.29755 | 10414.25 | 0.67625 | 9467.5 | 40000 | 0 | 6404 | 4010.25 | 0 | 9467.5 | 13477.75 | 0 | 0 | 0 | 0
2022012512 | 3 | 0.56424 | 45139.2 | 0 | 0 | 0.26515 | 9280.25 | 0.66686 | 9336.04 | 40000 | 0 | 5139.2 | 4141.05 | 0 | 9336.04 | 13477.09 | 0 | 0 | 0 | 0
2022012513 | 3 | 0.54681 | 43744.8 | 0 | 0 | 0.23796 | 8328.6 | 0.65315 | 9144.1 | 40000 | 0 | 3744.8 | 4583.8 | 0 | 9144.1 | 13727.9 | 0 | 0 | 0 | 0
2022012514 | 3 | 0.53387 | 42709.6 | 0 | 0 | 0.21327 | 7464.45 | 0.65934 | 9230.76 | 40000 | 0 | 2709.6 | 4754.85 | 0 | 9230.76 | 13985.61 | 0 | 0 | 0 | 0
2022012515 | 3 | 0.52655 | 42124 | 0 | 0 | 0.20837 | 7292.95 | 0.68237 | 9553.18 | 40000 | 0 | 2124 | 5168.95 | 0 | 9553.18 | 14722.13 | 0 | 0 | 0 | 0
2022012516 | 3 | 0.52261 | 41808.8 | 0 | 0 | 0.22429 | 7850.15 | 0.69485 | 9727.9 | 40000 | 0 | 1808.8 | 6041.35 | 0 | 9727.9 | 15769.25 | 0 | 0 | 0 | 0
2022012517 | 3 | 0.52776 | 42220.8 | 0 | 0 | 0.26572 | 9300.2 | 0.60819 | 8514.66 | 40000 | 0 | 2220.8 | 7079.4 | 0 | 8514.66 | 15594.06 | 0 | 0 | 0 | 0
2022012518 | 3 | 0.54673 | 43738.4 | 0 | 0 | 0.34644 | 12125.4 | 0.21865 | 3061.1 | 40000 | 0 | 3738.4 | 8387 | 0 | 3061.1 | 11448.1 | 0 | 0 | 0 | 0
2022012519 | 3 | 0.57486 | 45988.8 | 0 | 0 | 0.4419 | 15466.5 | 0.00768 | 107.52 | 40000 | 0 | 5988.8 | 9477.7 | 0 | 107.52 | 9585.22 | 0 | 0 | 0 | 0
2022012520 | 3 | 0.58065 | 46452 | 0 | 0 | 0.51647 | 18076.45 | 0.00485 | 67.9 | 40000 | 0 | 6452 | 11624.45 | 0 | 67.9 | 11692.35 | 0 | 0 | 0 | 0
2022012521 | 3 | 0.5783 | 46264 | 0 | 0 | 0.54269 | 18994.15 | 0.00485 | 67.9 | 40000 | 0 | 6264 | 12730.15 | 0 | 67.9 | 12798.05 | 0 | 0 | 0 | 0
2022012522 | 3 | 0.56854 | 45483.2 | 0 | 0 | 0.55402 | 19390.7 | 0.00485 | 67.9 | 40000 | 0 | 5483.2 | 13907.5 | 0 | 67.9 | 13975.4 | 0 | 0 | 0 | 0
2022012523 | 3 | 0.54736 | 43788.8 | 0 | 0 | 0.56045 | 19615.75 | 0.00485 | 67.9 | 40000 | 0 | 3788.8 | 15826.95 | 0 | 67.9 | 15894.85 | 0 | 0 | 0 | 0
2022012524 | 3 | 0.52793 | 42234.4 | 0 | 0 | 0.55884 | 19559.4 | 0.00486 | 68.04 | 40000 | 0 | 2234.4 | 17325 | 0 | 68.04 | 17393.04 | 0 | 0 | 0 | 0
2022012601 | 4 | 0.51655 | 41324 | 0 | 0 | 0.50629 | 17720.15 | 0.00485 | 67.9 | 40000 | 0 | 1324 | 16396.15 | 0 | 67.9 | 16464.05 | 0 | 0 | 0 | 0
2022012602 | 4 | 0.51545 | 41236 | 0 | 0 | 0.47225 | 16528.75 | 0.00485 | 67.9 | 40000 | 0 | 1236 | 15292.75 | 0 | 67.9 | 15360.65 | 0 | 0 | 0 | 0
2022012603 | 4 | 0.52091 | 41672.8 | 0 | 0 | 0.44277 | 15496.95 | 0.00485 | 67.9 | 40000 | 0 | 1672.8 | 13824.15 | 0 | 67.9 | 13892.05 | 0 | 0 | 0 | 0
2022012604 | 4 | 0.53224 | 42579.2 | 0 | 0 | 0.40026 | 14009.1 | 0.00485 | 67.9 | 40000 | 0 | 2579.2 | 11429.9 | 0 | 67.9 | 11497.8 | 0 | 0 | 0 | 0
2022012605 | 4 | 0.55371 | 44296.8 | 0 | 0 | 0.38252 | 13388.2 | 0.00485 | 67.9 | 40000 | 0 | 4296.8 | 9091.4 | 0 | 67.9 | 9159.3 | 0 | 0 | 0 | 0
2022012606 | 4 | 0.59247 | 47397.6 | 0 | 0 | 0.35448 | 12406.8 | 0.00485 | 67.9 | 40000 | 0 | 7397.6 | 5009.2 | 0 | 67.9 | 5077.1 | 0 | 0 | 0 | 0
2022012607 | 4 | 0.64753 | 51802.4 | 0 | 0 | 0.3312 | 11592 | 0.00368 | 51.52 | 40000 | 0 | 11592 | 0 | 51.52 | 0 | 0 | 158.88 | 0 | 0 | 158.88
2022012608 | 4 | 0.6741 | 53928 | 0 | 0 | 0.2854 | 9989 | 0.00425 | 59.5 | 40000 | 0 | 9989 | 0 | 59.5 | 0 | 0 | 3879.5 | 0 | 0 | 3879.5
2022012609 | 4 | 0.6676 | 53408 | 0 | 0 | 0.21147 | 7401.45 | 0.06936 | 971.04 | 40000 | 0 | 7401.45 | 0 | 971.04 | 0 | 0 | 5035.51 | 0 | 0 | 5035.51
2022012610 | 4 | 0.65127 | 52101.6 | 0 | 0 | 0.16046 | 5616.1 | 0.14809 | 2073.26 | 40000 | 0 | 5616.1 | 0 | 2073.26 | 0 | 0 | 4412.24 | 0 | 0 | 4412.24
2022012611 | 4 | 0.63253 | 50602.4 | 0 | 0 | 0.1311 | 4588.5 | 0.19458 | 2724.12 | 40000 | 0 | 4588.5 | 0 | 2724.12 | 0 | 0 | 3289.78 | 0 | 0 | 3289.78
2022012612 | 4 | 0.61049 | 48839.2 | 0 | 0 | 0.11133 | 3896.55 | 0.23941 | 3351.74 | 40000 | 0 | 3896.55 | 0 | 3351.74 | 0 | 0 | 1590.91 | 0 | 0 | 1590.91
2022012613 | 4 | 0.58706 | 46964.8 | 0 | 0 | 0.09593 | 3357.55 | 0.27798 | 3891.72 | 40000 | 0 | 3357.55 | 0 | 3607.25 | 284.47 | 284.47 | 0 | 0 | 0 | 0
2022012614 | 4 | 0.56791 | 45432.8 | 0 | 0 | 0.09119 | 3191.65 | 0.30596 | 4283.44 | 40000 | 0 | 3191.65 | 0 | 2241.15 | 2042.29 | 2042.29 | 0 | 0 | 0 | 0
2022012615 | 4 | 0.55322 | 44257.6 | 0 | 0 | 0.0958 | 3353 | 0.28551 | 3997.14 | 40000 | 0 | 3353 | 0 | 904.6 | 3092.54 | 3092.54 | 0 | 0 | 0 | 0
2022012616 | 4 | 0.54547 | 43637.6 | 0 | 0 | 0.10038 | 3513.3 | 0.25214 | 3529.96 | 40000 | 0 | 3513.3 | 0 | 124.3 | 3405.66 | 3405.66 | 0 | 0 | 0 | 0
2022012617 | 4 | 0.55232 | 44185.6 | 0 | 0 | 0.10324 | 3613.4 | 0.18419 | 2578.66 | 40000 | 0 | 3613.4 | 0 | 572.2 | 2006.46 | 2006.46 | 0 | 0 | 0 | 0
2022012618 | 4 | 0.57567 | 46053.6 | 0 | 0 | 0.09738 | 3408.3 | 0.06177 | 864.78 | 40000 | 0 | 3408.3 | 0 | 864.78 | 0 | 0 | 1780.52 | 0 | 0 | 1780.52
2022012619 | 4 | 0.60919 | 48735.2 | 0 | 0 | 0.11001 | 3850.35 | 0.00626 | 87.64 | 40000 | 0 | 3850.35 | 0 | 87.64 | 0 | 0 | 4797.21 | 0 | 0 | 4797.21
2022012620 | 4 | 0.61434 | 49147.2 | 0 | 0 | 0.11884 | 4159.4 | 0.00536 | 75.04 | 40000 | 0 | 4159.4 | 0 | 75.04 | 0 | 0 | 4912.76 | 0 | 0 | 4912.76
2022012621 | 4 | 0.60999 | 48799.2 | 0 | 0 | 0.10924 | 3823.4 | 0.00537 | 75.18 | 40000 | 0 | 3823.4 | 0 | 75.18 | 0 | 0 | 4900.62 | 0 | 0 | 4900.62
2022012622 | 4 | 0.59367 | 47493.6 | 0 | 0 | 0.1049 | 3671.5 | 0.00537 | 75.18 | 40000 | 0 | 3671.5 | 0 | 75.18 | 0 | 0 | 3746.92 | 0 | 0 | 3746.92
2022012623 | 4 | 0.56513 | 45210.4 | 0 | 0 | 0.11149 | 3902.15 | 0.00537 | 75.18 | 40000 | 0 | 3902.15 | 0 | 75.18 | 0 | 0 | 1233.07 | 0 | 0 | 1233.07
2022012624 | 4 | 0.53936 | 43148.8 | 0 | 0 | 0.12268 | 4293.8 | 0.00537 | 75.18 | 40000 | 0 | 3148.8 | 1145 | 0 | 75.18 | 1220.18 | 0 | 0 | 0 | 0
2022012701 | 5 | 0.52374 | 41899.2 | 0 | 0 | 0.14061 | 4921.35 | 0.00537 | 75.18 | 40000 | 0 | 1899.2 | 3022.15 | 0 | 75.18 | 3097.33 | 0 | 0 | 0 | 0
2022012702 | 5 | 0.51593 | 41274.4 | 0 | 0 | 0.14118 | 4941.3 | 0.00537 | 75.18 | 40000 | 0 | 1274.4 | 3666.9 | 0 | 75.18 | 3742.08 | 0 | 0 | 0 | 0
2022012703 | 5 | 0.514 | 41120 | 0 | 0 | 0.14299 | 5004.65 | 0.00537 | 75.18 | 40000 | 0 | 1120 | 3884.65 | 0 | 75.18 | 3959.83 | 0 | 0 | 0 | 0
2022012704 | 5 | 0.51813 | 41450.4 | 0 | 0 | 0.14484 | 5069.4 | 0.00537 | 75.18 | 40000 | 0 | 1450.4 | 3619 | 0 | 75.18 | 3694.18 | 0 | 0 | 0 | 0
2022012705 | 5 | 0.53219 | 42575.2 | 0 | 0 | 0.14615 | 5115.25 | 0.00193 | 27.02 | 40000 | 0 | 2575.2 | 2540.05 | 0 | 27.02 | 2567.07 | 0 | 0 | 0 | 0
2022012706 | 5 | 0.56516 | 45212.8 | 0 | 0 | 0.14281 | 4998.35 | 0 | 0 | 40000 | 0 | 4998.35 | 0 | 0 | 0 | 0 | 214.45 | 0 | 0 | 214.45
2022012707 | 5 | 0.61342 | 49073.6 | 0 | 0 | 0.13334 | 4666.9 | 0 | 0 | 40000 | 0 | 4666.9 | 0 | 0 | 0 | 0 | 4406.7 | 0 | 0 | 4406.7
2022012708 | 5 | 0.63683 | 50946.4 | 0 | 0 | 0.13353 | 4673.55 | 0.00397 | 55.58 | 40000 | 0 | 4673.55 | 0 | 55.58 | 0 | 0 | 6217.27 | 0 | 0 | 6217.27
2022012709 | 5 | 0.62713 | 50170.4 | 0 | 0 | 0.10674 | 3735.9 | 0.07574 | 1060.36 | 40000 | 0 | 3735.9 | 0 | 1060.36 | 0 | 0 | 5374.14 | 0 | 0 | 5374.14
2022012710 | 5 | 0.6084 | 48672 | 0 | 0 | 0.0885 | 3097.5 | 0.20662 | 2892.68 | 40000 | 0 | 3097.5 | 0 | 2892.68 | 0 | 0 | 2681.82 | 0 | 0 | 2681.82
2022012711 | 5 | 0.59156 | 47324.8 | 0 | 0 | 0.0668 | 2338 | 0.29407 | 4116.98 | 40000 | 0 | 2338 | 0 | 4116.98 | 0 | 0 | 869.82 | 0 | 0 | 869.82
2022012712 | 5 | 0.57327 | 45861.6 | 0 | 0 | 0.05435 | 1902.25 | 0.40788 | 5710.32 | 40000 | 0 | 1902.25 | 0 | 3959.35 | 1750.97 | 1750.97 | 0 | 0 | 0 | 0
2022012713 | 5 | 0.55459 | 44367.2 | 0 | 0 | 0.06124 | 2143.4 | 0.44474 | 6226.36 | 40000 | 0 | 2143.4 | 0 | 2223.8 | 4002.56 | 4002.56 | 0 | 0 | 0 | 0
2022012714 | 5 | 0.5413 | 43304 | 0 | 0 | 0.08207 | 2872.45 | 0.48654 | 6811.56 | 40000 | 0 | 2872.45 | 0 | 431.55 | 6380.01 | 6380.01 | 0 | 0 | 0 | 0
2022012715 | 5 | 0.52975 | 42380 | 0 | 0 | 0.11043 | 3865.05 | 0.51649 | 7230.86 | 40000 | 0 | 2380 | 1485.05 | 0 | 7230.86 | 8715.91 | 0 | 0 | 0 | 0
2022012716 | 5 | 0.52238 | 41790.4 | 0 | 0 | 0.14103 | 4936.05 | 0.53347 | 7468.58 | 40000 | 0 | 1790.4 | 3145.65 | 0 | 7468.58 | 10614.23 | 0 | 0 | 0 | 0
2022012717 | 5 | 0.52586 | 42068.8 | 0 | 0 | 0.16365 | 5727.75 | 0.45844 | 6418.16 | 40000 | 0 | 2068.8 | 3658.95 | 0 | 6418.16 | 10077.11 | 0 | 0 | 0 | 0
2022012718 | 5 | 0.54295 | 43436 | 0 | 0 | 0.19854 | 6948.9 | 0.17354 | 2429.56 | 40000 | 0 | 3436 | 3512.9 | 0 | 2429.56 | 5942.46 | 0 | 0 | 0 | 0
2022012719 | 5 | 0.571 | 45680 | 0 | 0 | 0.26646 | 9326.1 | 0.00326 | 45.64 | 40000 | 0 | 5680 | 3646.1 | 0 | 45.64 | 3691.74 | 0 | 0 | 0 | 0
2022012720 | 5 | 0.57709 | 46167.2 | 0 | 0 | 0.34055 | 11919.25 | 7e-05 | 0.98 | 40000 | 0 | 6167.2 | 5752.05 | 0 | 0.98 | 5753.03 | 0 | 0 | 0 | 0
2022012721 | 5 | 0.57603 | 46082.4 | 0 | 0 | 0.41797 | 14628.95 | 0 | 0 | 40000 | 0 | 6082.4 | 8546.55 | 0 | 0 | 8546.55 | 0 | 0 | 0 | 0
2022012722 | 5 | 0.5641 | 45128 | 0 | 0 | 0.47491 | 16621.85 | 0 | 0 | 40000 | 0 | 5128 | 11493.85 | 0 | 0 | 11493.85 | 0 | 0 | 0 | 0
2022012723 | 5 | 0.54209 | 43367.2 | 0 | 0 | 0.4808 | 16828 | 0 | 0 | 40000 | 0 | 3367.2 | 13460.8 | 0 | 0 | 13460.8 | 0 | 0 | 0 | 0
2022012724 | 5 | 0.52095 | 41676 | 0 | 0 | 0.47536 | 16637.6 | 0 | 0 | 40000 | 0 | 1676 | 14961.6 | 0 | 0 | 14961.6 | 0 | 0 | 0 | 0
2022012801 | 6 | 0.50937 | 40749.6 | 0 | 0 | 0.47781 | 16723.35 | 0 | 0 | 40000 | 0 | 749.6 | 15973.75 | 0 | 0 | 15973.75 | 0 | 0 | 0 | 0
2022012802 | 6 | 0.5047 | 40376 | 0 | 0 | 0.48053 | 16818.55 | 0 | 0 | 40000 | 0 | 376 | 16442.55 | 0 | 0 | 16442.55 | 0 | 0 | 0 | 0
2022012803 | 6 | 0.50906 | 40724.8 | 0 | 0 | 0.4605 | 16117.5 | 0 | 0 | 40000 | 0 | 724.8 | 15392.7 | 0 | 0 | 15392.7 | 0 | 0 | 0 | 0
2022012804 | 6 | 0.52097 | 41677.6 | 0 | 0 | 0.46389 | 16236.15 | 0 | 0 | 40000 | 0 | 1677.6 | 14558.55 | 0 | 0 | 14558.55 | 0 | 0 | 0 | 0
2022012805 | 6 | 0.54068 | 43254.4 | 0 | 0 | 0.47415 | 16595.25 | 0 | 0 | 40000 | 0 | 3254.4 | 13340.85 | 0 | 0 | 13340.85 | 0 | 0 | 0 | 0
2022012806 | 6 | 0.57894 | 46315.2 | 0 | 0 | 0.46044 | 16115.4 | 0 | 0 | 40000 | 0 | 6315.2 | 9800.2 | 0 | 0 | 9800.2 | 0 | 0 | 0 | 0
2022012807 | 6 | 0.63236 | 50588.8 | 0 | 0 | 0.43625 | 15268.75 | 0 | 0 | 40000 | 0 | 10588.8 | 4679.95 | 0 | 0 | 4679.95 | 0 | 0 | 0 | 0
2022012808 | 6 | 0.66271 | 53016.8 | 0 | 0 | 0.4077 | 14269.5 | 0.00656 | 91.84 | 40000 | 0 | 13016.8 | 1252.7 | 0 | 91.84 | 1344.54 | 0 | 0 | 0 | 0
2022012809 | 6 | 0.65782 | 52625.6 | 0 | 0 | 0.34848 | 12196.8 | 0.27776 | 3888.64 | 40000 | 0 | 12196.8 | 0 | 428.8 | 3459.84 | 3459.84 | 0 | 0 | 0 | 0
2022012810 | 6 | 0.63861 | 51088.8 | 0 | 0 | 0.2538 | 8883 | 0.69755 | 9765.7 | 40000 | 0 | 8883 | 0 | 2205.8 | 7559.9 | 7559.9 | 0 | 0 | 0 | 0
2022012811 | 6 | 0.61601 | 49280.8 | 0 | 0 | 0.21892 | 7662.2 | 0.75283 | 10539.62 | 40000 | 0 | 7662.2 | 0 | 1618.6 | 8921.02 | 8921.02 | 0 | 0 | 0 | 0
2022012812 | 6 | 0.59186 | 47348.8 | 0 | 0 | 0.25073 | 8775.55 | 0.75461 | 10564.54 | 40000 | 0 | 7348.8 | 1426.75 | 0 | 10564.54 | 11991.29 | 0 | 0 | 0 | 0
2022012813 | 6 | 0.57002 | 45601.6 | 0 | 0 | 0.27811 | 9733.85 | 0.75423 | 10559.22 | 40000 | 0 | 5601.6 | 4132.25 | 0 | 10559.22 | 14691.47 | 0 | 0 | 0 | 0
2022012814 | 6 | 0.55334 | 44267.2 | 0 | 0 | 0.28099 | 9834.65 | 0.76784 | 10749.76 | 40000 | 0 | 4267.2 | 5567.45 | 0 | 10749.76 | 16317.21 | 0 | 0 | 0 | 0
2022012815 | 6 | 0.53842 | 43073.6 | 0 | 0 | 0.2646 | 9261 | 0.78991 | 11058.74 | 40000 | 0 | 3073.6 | 6187.4 | 0 | 11058.74 | 17246.14 | 0 | 0 | 0 | 0
2022012816 | 6 | 0.52913 | 42330.4 | 0 | 0 | 0.24253 | 8488.55 | 0.81275 | 11378.5 | 40000 | 0 | 2330.4 | 6158.15 | 0 | 11378.5 | 17536.65 | 0 | 0 | 0 | 0
2022012817 | 6 | 0.52831 | 42264.8 | 0 | 0 | 0.20351 | 7122.85 | 0.71996 | 10079.44 | 40000 | 0 | 2264.8 | 4858.05 | 0 | 10079.44 | 14937.49 | 0 | 0 | 0 | 0
2022012818 | 6 | 0.54278 | 43422.4 | 0 | 0 | 0.12921 | 4522.35 | 0.26314 | 3683.96 | 40000 | 0 | 3422.4 | 1099.95 | 0 | 3683.96 | 4783.91 | 0 | 0 | 0 | 0
2022012819 | 6 | 0.57587 | 46069.6 | 0 | 0 | 0.07706 | 2697.1 | 0.00488 | 68.32 | 40000 | 0 | 2697.1 | 0 | 68.32 | 0 | 0 | 3304.18 | 0 | 0 | 3304.18
2022012820 | 6 | 0.58782 | 47025.6 | 0 | 0 | 0.06244 | 2185.4 | 6e-05 | 0.84 | 40000 | 0 | 2185.4 | 0 | 0.84 | 0 | 0 | 4839.36 | 0 | 0 | 4839.36
2022012821 | 6 | 0.59357 | 47485.6 | 0 | 0 | 0.06522 | 2282.7 | 6e-05 | 0.84 | 40000 | 0 | 2282.7 | 0 | 0.84 | 0 | 0 | 5202.06 | 0 | 0 | 5202.06
2022012822 | 6 | 0.59242 | 47393.6 | 0 | 0 | 0.08062 | 2821.7 | 6e-05 | 0.84 | 40000 | 0 | 2821.7 | 0 | 0.84 | 0 | 0 | 4571.06 | 0 | 0 | 4571.06
2022012823 | 6 | 0.58184 | 46547.2 | 0 | 0 | 0.10536 | 3687.6 | 6e-05 | 0.84 | 40000 | 0 | 3687.6 | 0 | 0.84 | 0 | 0 | 2858.76 | 0 | 0 | 2858.76
2022012824 | 6 | 0.57143 | 45714.4 | 0 | 0 | 0.13632 | 4771.2 | 6e-05 | 0.84 | 40000 | 0 | 4771.2 | 0 | 0.84 | 0 | 0 | 942.36 | 0 | 0 | 942.36
2022012901 | 7 | 0.56318 | 45054.4 | 0 | 0 | 0.16733 | 5856.55 | 6e-05 | 0.84 | 40000 | 0 | 5054.4 | 802.15 | 0 | 0.84 | 802.99 | 0 | 0 | 0 | 0
2022012902 | 7 | 0.56496 | 45196.8 | 0 | 0 | 0.22028 | 7709.8 | 6e-05 | 0.84 | 40000 | 0 | 5196.8 | 2513 | 0 | 0.84 | 2513.84 | 0 | 0 | 0 | 0
2022012903 | 7 | 0.56987 | 45589.6 | 0 | 0 | 0.27262 | 9541.7 | 6e-05 | 0.84 | 40000 | 0 | 5589.6 | 3952.1 | 0 | 0.84 | 3952.94 | 0 | 0 | 0 | 0
2022012904 | 7 | 0.57865 | 46292 | 0 | 0 | 0.30802 | 10780.7 | 6e-05 | 0.84 | 40000 | 0 | 6292 | 4488.7 | 0 | 0.84 | 4489.54 | 0 | 0 | 0 | 0
2022012905 | 7 | 0.59253 | 47402.4 | 0 | 0 | 0.32355 | 11324.25 | 0 | 0 | 40000 | 0 | 7402.4 | 3921.85 | 0 | 0 | 3921.85 | 0 | 0 | 0 | 0
2022012906 | 7 | 0.61192 | 48953.6 | 0 | 0 | 0.33157 | 11604.95 | 0 | 0 | 40000 | 0 | 8953.6 | 2651.35 | 0 | 0 | 2651.35 | 0 | 0 | 0 | 0
2022012907 | 7 | 0.63861 | 51088.8 | 0 | 0 | 0.31806 | 11132.1 | 0 | 0 | 40000 | 0 | 11088.8 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 0 | 0
2022012908 | 7 | 0.66177 | 52941.6 | 0 | 0 | 0.32298 | 11304.3 | 0.01304 | 182.56 | 40000 | 0 | 11304.3 | 0 | 182.56 | 0 | 0 | 1454.74 | 0 | 0 | 1454.74
2022012909 | 7 | 0.65696 | 52556.8 | 0 | 0 | 0.31905 | 11166.75 | 0.33532 | 4694.48 | 40000 | 0 | 11166.75 | 0 | 1390.05 | 3304.43 | 3304.43 | 0 | 0 | 0 | 0
2022012910 | 7 | 0.62529 | 50023.2 | 0 | 0 | 0.22094 | 7732.9 | 0.75286 | 10540.04 | 40000 | 0 | 7732.9 | 0 | 2290.3 | 8249.74 | 8249.74 | 0 | 0 | 0 | 0
2022012911 | 7 | 0.58747 | 46997.6 | 0 | 0 | 0.16836 | 5892.6 | 0.77474 | 10846.36 | 40000 | 0 | 5892.6 | 0 | 1105 | 9741.36 | 9741.36 | 0 | 0 | 0 | 0
2022012912 | 7 | 0.5525 | 44200 | 0 | 0 | 0.22837 | 7992.95 | 0.7673 | 10742.2 | 40000 | 0 | 4200 | 3792.95 | 0 | 10742.2 | 14535.15 | 0 | 0 | 0 | 0
2022012913 | 7 | 0.52336 | 41868.8 | 0 | 0 | 0.27962 | 9786.7 | 0.70289 | 9840.46 | 40000 | 0 | 1868.8 | 7917.9 | 0 | 9840.46 | 17758.36 | 0 | 0 | 0 | 0
2022012914 | 7 | 0.4994 | 39952 | 0 | 0 | 0.27693 | 9692.55 | 0.68189 | 9546.46 | 39952 | 48 | 0 | 9692.55 | 0 | 9546.46 | 19287.01 | 0 | 0 | 0 | 0
2022012915 | 7 | 0.48333 | 38666.4 | 0 | 0 | 0.24737 | 8657.95 | 0.75177 | 10524.78 | 38666.4 | 1333.6 | 0 | 8657.95 | 0 | 10524.78 | 20516.33 | 0 | 0 | 0 | 0
2022012916 | 7 | 0.47545 | 38036 | 0 | 0 | 0.23359 | 8175.65 | 0.80283 | 11239.62 | 38036 | 1964 | 0 | 8175.65 | 0 | 11239.62 | 21379.27 | 0 | 0 | 0 | 0
2022012917 | 7 | 0.475 | 38000 | 0 | 0 | 0.22237 | 7782.95 | 0.71389 | 9994.46 | 38000 | 2000 | 0 | 7782.95 | 0 | 9994.46 | 19777.41 | 0 | 0 | 0 | 0
2022012918 | 7 | 0.48446 | 38756.8 | 0 | 0 | 0.20843 | 7295.05 | 0.26767 | 3747.38 | 38756.8 | 1243.2 | 0 | 7295.05 | 0 | 3747.38 | 12285.63 | 0 | 0 | 0 | 0
2022012919 | 7 | 0.51236 | 40988.8 | 0 | 0 | 0.2223 | 7780.5 | 0.00564 | 78.96 | 40000 | 0 | 988.8 | 6791.7 | 0 | 78.96 | 6870.66 | 0 | 0 | 0 | 0
2022012920 | 7 | 0.52211 | 41768.8 | 0 | 0 | 0.2681 | 9383.5 | 0 | 0 | 40000 | 0 | 1768.8 | 7614.7 | 0 | 0 | 7614.7 | 0 | 0 | 0 | 0
2022012921 | 7 | 0.52646 | 42116.8 | 0 | 0 | 0.34554 | 12093.9 | 0 | 0 | 40000 | 0 | 2116.8 | 9977.1 | 0 | 0 | 9977.1 | 0 | 0 | 0 | 0
2022012922 | 7 | 0.52778 | 42222.4 | 0 | 0 | 0.46408 | 16242.8 | 0 | 0 | 40000 | 0 | 2222.4 | 14020.4 | 0 | 0 | 14020.4 | 0 | 0 | 0 | 0
2022012923 | 7 | 0.52253 | 41802.4 | 0 | 0 | 0.50149 | 17552.15 | 0 | 0 | 40000 | 0 | 1802.4 | 15749.75 | 0 | 0 | 15749.75 | 0 | 0 | 0 | 0
2022012924 | 7 | 0.51369 | 41095.2 | 0 | 0 | 0.51094 | 17882.9 | 0 | 0 | 40000 | 0 | 1095.2 | 16787.7 | 0 | 0 | 16787.7 | 0 | 0 | 0 | 0
2022013001 | 1 | 0.50758 | 40606.4 | 0 | 0 | 0.51636 | 18072.6 | 0 | 0 | 40000 | 0 | 606.4 | 17466.2 | 0 | 0 | 17466.2 | 0 | 0 | 0 | 0
2022013002 | 1 | 0.5042 | 40336 | 0 | 0 | 0.51619 | 18066.65 | 0 | 0 | 40000 | 0 | 336 | 17730.65 | 0 | 0 | 17730.65 | 0 | 0 | 0 | 0
2022013003 | 1 | 0.50797 | 40637.6 | 0 | 0 | 0.50739 | 17758.65 | 0 | 0 | 40000 | 0 | 637.6 | 17121.05 | 0 | 0 | 17121.05 | 0 | 0 | 0 | 0
2022013004 | 1 | 0.51458 | 41166.4 | 0 | 0 | 0.49953 | 17483.55 | 0 | 0 | 40000 | 0 | 1166.4 | 16317.15 | 0 | 0 | 16317.15 | 0 | 0 | 0 | 0
2022013005 | 1 | 0.52392 | 41913.6 | 0 | 0 | 0.46304 | 16206.4 | 0 | 0 | 40000 | 0 | 1913.6 | 14292.8 | 0 | 0 | 14292.8 | 0 | 0 | 0 | 0
2022013006 | 1 | 0.53756 | 43004.8 | 0 | 0 | 0.38512 | 13479.2 | 0 | 0 | 40000 | 0 | 3004.8 | 10474.4 | 0 | 0 | 10474.4 | 0 | 0 | 0 | 0
2022013007 | 1 | 0.55951 | 44760.8 | 0 | 0 | 0.34306 | 12007.1 | 0 | 0 | 40000 | 0 | 4760.8 | 7246.3 | 0 | 0 | 7246.3 | 0 | 0 | 0 | 0
2022013008 | 1 | 0.58125 | 46500 | 0 | 0 | 0.30842 | 10794.7 | 0.01223 | 171.22 | 40000 | 0 | 6500 | 4294.7 | 0 | 171.22 | 4465.92 | 0 | 0 | 0 | 0
2022013009 | 1 | 0.58041 | 46432.8 | 0 | 0 | 0.25684 | 8989.4 | 0.31483 | 4407.62 | 40000 | 0 | 6432.8 | 2556.6 | 0 | 4407.62 | 6964.22 | 0 | 0 | 0 | 0
2022013010 | 1 | 0.55679 | 44543.2 | 0 | 0 | 0.14961 | 5236.35 | 0.70431 | 9860.34 | 40000 | 0 | 4543.2 | 693.15 | 0 | 9860.34 | 10553.49 | 0 | 0 | 0 | 0
2022013011 | 1 | 0.5291 | 42328 | 0 | 0 | 0.12075 | 4226.25 | 0.76321 | 10684.94 | 40000 | 0 | 2328 | 1898.25 | 0 | 10684.94 | 12583.19 | 0 | 0 | 0 | 0
2022013012 | 1 | 0.50637 | 40509.6 | 0 | 0 | 0.14632 | 5121.2 | 0.73556 | 10297.84 | 40000 | 0 | 509.6 | 4611.6 | 0 | 10297.84 | 14909.44 | 0 | 0 | 0 | 0
2022013013 | 1 | 0.48994 | 39195.2 | 0 | 0 | 0.14235 | 4982.25 | 0.70177 | 9824.78 | 39195.2 | 804.8 | 0 | 4982.25 | 0 | 9824.78 | 15611.83 | 0 | 0 | 0 | 0
2022013014 | 1 | 0.47811 | 38248.8 | 0 | 0 | 0.17206 | 6022.1 | 0.70158 | 9822.12 | 38248.8 | 1751.2 | 0 | 6022.1 | 0 | 9822.12 | 17595.42 | 0 | 0 | 0 | 0
2022013015 | 1 | 0.47143 | 37714.4 | 0 | 0 | 0.20098 | 7034.3 | 0.65211 | 9129.54 | 37714.4 | 2285.6 | 0 | 7034.3 | 0 | 9129.54 | 18449.44 | 0 | 0 | 0 | 0
2022013016 | 1 | 0.46907 | 37525.6 | 0 | 0 | 0.21299 | 7454.65 | 0.55507 | 7770.98 | 37525.6 | 2474.4 | 0 | 7454.65 | 0 | 7770.98 | 17700.03 | 0 | 0 | 0 | 0
2022013017 | 1 | 0.47118 | 37694.4 | 0 | 0 | 0.20133 | 7046.55 | 0.4527 | 6337.8 | 37694.4 | 2305.6 | 0 | 7046.55 | 0 | 6337.8 | 15689.95 | 0 | 0 | 0 | 0
2022013018 | 1 | 0.4856 | 38848 | 0 | 0 | 0.19753 | 6913.55 | 0.13084 | 1831.76 | 38848 | 1152 | 0 | 6913.55 | 0 | 1831.76 | 9897.31 | 0 | 0 | 0 | 0
2022013019 | 1 | 0.51179 | 40943.2 | 0 | 0 | 0.23319 | 8161.65 | 0.00234 | 32.76 | 40000 | 0 | 943.2 | 7218.45 | 0 | 32.76 | 7251.21 | 0 | 0 | 0 | 0
2022013020 | 1 | 0.51891 | 41512.8 | 0 | 0 | 0.29153 | 10203.55 | 0 | 0 | 40000 | 0 | 1512.8 | 8690.75 | 0 | 0 | 8690.75 | 0 | 0 | 0 | 0
2022013021 | 1 | 0.51246 | 40996.8 | 0 | 0 | 0.31331 | 10965.85 | 0 | 0 | 40000 | 0 | 996.8 | 9969.05 | 0 | 0 | 9969.05 | 0 | 0 | 0 | 0
2022013022 | 1 | 0.50413 | 40330.4 | 0 | 0 | 0.305 | 10675 | 0 | 0 | 40000 | 0 | 330.4 | 10344.6 | 0 | 0 | 10344.6 | 0 | 0 | 0 | 0
2022013023 | 1 | 0.48175 | 38540 | 0 | 0 | 0.30065 | 10522.75 | 0 | 0 | 38540 | 1460 | 0 | 10522.75 | 0 | 0 | 11982.75 | 0 | 0 | 0 | 0
2022013024 | 1 | 0.45946 | 36756.8 | 0 | 0 | 0.33726 | 11804.1 | 0 | 0 | 36756.8 | 3243.2 | 0 | 11804.1 | 0 | 0 | 15047.3 | 0 | 0 | 0 | 0
2022013101 | 2 | 0.44404 | 35523.2 | 0 | 0 | 0.39855 | 13949.25 | 0 | 0 | 35523.2 | 4476.8 | 0 | 13949.25 | 0 | 0 | 18426.05 | 0 | 0 | 0 | 0
2022013102 | 2 | 0.43733 | 34986.4 | 0 | 0 | 0.42247 | 14786.45 | 0 | 0 | 34986.4 | 5013.6 | 0 | 14786.45 | 0 | 0 | 19800.05 | 0 | 0 | 0 | 0
2022013103 | 2 | 0.43492 | 34793.6 | 0 | 0 | 0.40565 | 14197.75 | 0 | 0 | 34793.6 | 5206.4 | 0 | 14197.75 | 0 | 0 | 19404.15 | 0 | 0 | 0 | 0
2022013104 | 2 | 0.43883 | 35106.4 | 0 | 0 | 0.36518 | 12781.3 | 0 | 0 | 35106.4 | 4893.6 | 0 | 12781.3 | 0 | 0 | 17674.9 | 0 | 0 | 0 | 0
2022013105 | 2 | 0.45145 | 36116 | 0 | 0 | 0.32195 | 11268.25 | 0 | 0 | 36116 | 3884 | 0 | 11268.25 | 0 | 0 | 15152.25 | 0 | 0 | 0 | 0
2022013106 | 2 | 0.48077 | 38461.6 | 0 | 0 | 0.30303 | 10606.05 | 0 | 0 | 38461.6 | 1538.4 | 0 | 10606.05 | 0 | 0 | 12144.45 | 0 | 0 | 0 | 0
2022013107 | 2 | 0.52365 | 41892 | 0 | 0 | 0.23968 | 8388.8 | 0 | 0 | 40000 | 0 | 1892 | 6496.8 | 0 | 0 | 6496.8 | 0 | 0 | 0 | 0
2022013108 | 2 | 0.5454 | 43632 | 0 | 0 | 0.19739 | 6908.65 | 0.00394 | 55.16 | 40000 | 0 | 3632 | 3276.65 | 0 | 55.16 | 3331.81 | 0 | 0 | 0 | 0
2022013109 | 2 | 0.54123 | 43298.4 | 0 | 0 | 0.14881 | 5208.35 | 0.1568 | 2195.2 | 40000 | 0 | 3298.4 | 1909.95 | 0 | 2195.2 | 4105.15 | 0 | 0 | 0 | 0
2022013110 | 2 | 0.53787 | 43029.6 | 0 | 0 | 0.10081 | 3528.35 | 0.41411 | 5797.54 | 40000 | 0 | 3029.6 | 498.75 | 0 | 5797.54 | 6296.29 | 0 | 0 | 0 | 0
2022013111 | 2 | 0.53297 | 42637.6 | 0 | 0 | 0.08637 | 3022.95 | 0.50965 | 7135.1 | 40000 | 0 | 2637.6 | 385.35 | 0 | 7135.1 | 7520.45 | 0 | 0 | 0 | 0
2022013112 | 2 | 0.52791 | 42232.8 | 0 | 0 | 0.11905 | 4166.75 | 0.59142 | 8279.88 | 40000 | 0 | 2232.8 | 1933.95 | 0 | 8279.88 | 10213.83 | 0 | 0 | 0 | 0
2022013113 | 2 | 0.52489 | 41991.2 | 0 | 0 | 0.14184 | 4964.4 | 0.62333 | 8726.62 | 40000 | 0 | 1991.2 | 2973.2 | 0 | 8726.62 | 11699.82 | 0 | 0 | 0 | 0
2022013114 | 2 | 0.52272 | 41817.6 | 0 | 0 | 0.15231 | 5330.85 | 0.62687 | 8776.18 | 40000 | 0 | 1817.6 | 3513.25 | 0 | 8776.18 | 12289.43 | 0 | 0 | 0 | 0
2022013115 | 2 | 0.51736 | 41388.8 | 0 | 0 | 0.19375 | 6781.25 | 0.65806 | 9212.84 | 40000 | 0 | 1388.8 | 5392.45 | 0 | 9212.84 | 14605.29 | 0 | 0 | 0 | 0
2022013116 | 2 | 0.51529 | 41223.2 | 0 | 0 | 0.21559 | 7545.65 | 0.64636 | 9049.04 | 40000 | 0 | 1223.2 | 6322.45 | 0 | 9049.04 | 15371.49 | 0 | 0 | 0 | 0
2022013117 | 2 | 0.51942 | 41553.6 | 0 | 0 | 0.21707 | 7597.45 | 0.59026 | 8263.64 | 40000 | 0 | 1553.6 | 6043.85 | 0 | 8263.64 | 14307.49 | 0 | 0 | 0 | 0
2022013118 | 2 | 0.52955 | 42364 | 0 | 0 | 0.2079 | 7276.5 | 0.26025 | 3643.5 | 40000 | 0 | 2364 | 4912.5 | 0 | 3643.5 | 8556 | 0 | 0 | 0 | 0
2022013119 | 2 | 0.54715 | 43772 | 0 | 0 | 0.25246 | 8836.1 | 0.00635 | 88.9 | 40000 | 0 | 3772 | 5064.1 | 0 | 88.9 | 5153 | 0 | 0 | 0 | 0
2022013120 | 2 | 0.5468 | 43744 | 0 | 0 | 0.3643 | 12750.5 | 0 | 0 | 40000 | 0 | 3744 | 9006.5 | 0 | 0 | 9006.5 | 0 | 0 | 0 | 0
2022013121 | 2 | 0.53841 | 43072.8 | 0 | 0 | 0.42942 | 15029.7 | 0 | 0 | 40000 | 0 | 3072.8 | 11956.9 | 0 | 0 | 11956.9 | 0 | 0 | 0 | 0
2022013122 | 2 | 0.5196 | 41568 | 0 | 0 | 0.43758 | 15315.3 | 0 | 0 | 40000 | 0 | 1568 | 13747.3 | 0 | 0 | 13747.3 | 0 | 0 | 0 | 0
2022013123 | 2 | 0.49115 | 39292 | 0 | 0 | 0.43141 | 15099.35 | 0 | 0 | 39292 | 708 | 0 | 15099.35 | 0 | 0 | 15807.35 | 0 | 0 | 0 | 0
2022013124 | 2 | 0.46493 | 37194.4 | 0 | 0 | 0.42674 | 14935.9 | 0 | 0 | 37194.4 | 2805.6 | 0 | 14935.9 | 0 | 0 | 17741.5 | 0 | 0 | 0 | 0
2022020101 | 3 | 0.44689 | 35751.2 | 0 | 0 | 0.42076 | 14726.6 | 0 | 0 | 35751.2 | 4248.8 | 0 | 14726.6 | 0 | 0 | 18975.4 | 0 | 0 | 0 | 0
2022020102 | 3 | 0.43492 | 34793.6 | 0 | 0 | 0.4054 | 14189 | 0 | 0 | 34793.6 | 5206.4 | 0 | 14189 | 0 | 0 | 19395.4 | 0 | 0 | 0 | 0
2022020103 | 3 | 0.43147 | 34517.6 | 0 | 0 | 0.39675 | 13886.25 | 0 | 0 | 34517.6 | 5482.4 | 0 | 13886.25 | 0 | 0 | 19368.65 | 0 | 0 | 0 | 0
2022020104 | 3 | 0.43184 | 34547.2 | 0 | 0 | 0.39322 | 13762.7 | 0 | 0 | 34547.2 | 5452.8 | 0 | 13762.7 | 0 | 0 | 19215.5 | 0 | 0 | 0 | 0
2022020105 | 3 | 0.44046 | 35236.8 | 0 | 0 | 0.3874 | 13559 | 0 | 0 | 35236.8 | 4763.2 | 0 | 13559 | 0 | 0 | 18322.2 | 0 | 0 | 0 | 0
2022020106 | 3 | 0.46646 | 37316.8 | 0 | 0 | 0.38949 | 13632.15 | 0 | 0 | 37316.8 | 2683.2 | 0 | 13632.15 | 0 | 0 | 16315.35 | 0 | 0 | 0 | 0
2022020107 | 3 | 0.50606 | 40484.8 | 0 | 0 | 0.40644 | 14225.4 | 0 | 0 | 40000 | 0 | 484.8 | 13740.6 | 0 | 0 | 13740.6 | 0 | 0 | 0 | 0
2022020108 | 3 | 0.52514 | 42011.2 | 0 | 0 | 0.41174 | 14410.9 | 0.00213 | 29.82 | 40000 | 0 | 2011.2 | 12399.7 | 0 | 29.82 | 12429.52 | 0 | 0 | 0 | 0
2022020109 | 3 | 0.52433 | 41946.4 | 0 | 0 | 0.39023 | 13658.05 | 0.08536 | 1195.04 | 40000 | 0 | 1946.4 | 11711.65 | 0 | 1195.04 | 12906.69 | 0 | 0 | 0 | 0
2022020110 | 3 | 0.52436 | 41948.8 | 0 | 0 | 0.35483 | 12419.05 | 0.23478 | 3286.92 | 40000 | 0 | 1948.8 | 10470.25 | 0 | 3286.92 | 13757.17 | 0 | 0 | 0 | 0
2022020111 | 3 | 0.52033 | 41626.4 | 0 | 0 | 0.32041 | 11214.35 | 0.31844 | 4458.16 | 40000 | 0 | 1626.4 | 9587.95 | 0 | 4458.16 | 14046.11 | 0 | 0 | 0 | 0
2022020112 | 3 | 0.51329 | 41063.2 | 0 | 0 | 0.28751 | 10062.85 | 0.40246 | 5634.44 | 40000 | 0 | 1063.2 | 8999.65 | 0 | 5634.44 | 14634.09 | 0 | 0 | 0 | 0
2022020113 | 3 | 0.50756 | 40604.8 | 0 | 0 | 0.25192 | 8817.2 | 0.49158 | 6882.12 | 40000 | 0 | 604.8 | 8212.4 | 0 | 6882.12 | 15094.52 | 0 | 0 | 0 | 0
2022020114 | 3 | 0.50254 | 40203.2 | 0 | 0 | 0.21085 | 7379.75 | 0.55051 | 7707.14 | 40000 | 0 | 203.2 | 7176.55 | 0 | 7707.14 | 14883.69 | 0 | 0 | 0 | 0
2022020115 | 3 | 0.49906 | 39924.8 | 0 | 0 | 0.18126 | 6344.1 | 0.63268 | 8857.52 | 39924.8 | 75.2 | 0 | 6344.1 | 0 | 8857.52 | 15276.82 | 0 | 0 | 0 | 0
2022020116 | 3 | 0.49641 | 39712.8 | 0 | 0 | 0.18457 | 6459.95 | 0.54777 | 7668.78 | 39712.8 | 287.2 | 0 | 6459.95 | 0 | 7668.78 | 14415.93 | 0 | 0 | 0 | 0
2022020117 | 3 | 0.49885 | 39908 | 0 | 0 | 0.19228 | 6729.8 | 0.47063 | 6588.82 | 39908 | 92 | 0 | 6729.8 | 0 | 6588.82 | 13410.62 | 0 | 0 | 0 | 0
2022020118 | 3 | 0.50733 | 40586.4 | 0 | 0 | 0.19442 | 6804.7 | 0.18337 | 2567.18 | 40000 | 0 | 586.4 | 6218.3 | 0 | 2567.18 | 8785.48 | 0 | 0 | 0 | 0
2022020119 | 3 | 0.52642 | 42113.6 | 0 | 0 | 0.23456 | 8209.6 | 0.00196 | 27.44 | 40000 | 0 | 2113.6 | 6096 | 0 | 27.44 | 6123.44 | 0 | 0 | 0 | 0
2022020120 | 3 | 0.52914 | 42331.2 | 0 | 0 | 0.32405 | 11341.75 | 6e-05 | 0.84 | 40000 | 0 | 2331.2 | 9010.55 | 0 | 0.84 | 9011.39 | 0 | 0 | 0 | 0
2022020121 | 3 | 0.52087 | 41669.6 | 0 | 0 | 0.3893 | 13625.5 | 6e-05 | 0.84 | 40000 | 0 | 1669.6 | 11955.9 | 0 | 0.84 | 11956.74 | 0 | 0 | 0 | 0
2022020122 | 3 | 0.50522 | 40417.6 | 0 | 0 | 0.42343 | 14820.05 | 6e-05 | 0.84 | 40000 | 0 | 417.6 | 14402.45 | 0 | 0.84 | 14403.29 | 0 | 0 | 0 | 0
2022020123 | 3 | 0.48061 | 38448.8 | 0 | 0 | 0.45722 | 16002.7 | 6e-05 | 0.84 | 38448.8 | 1551.2 | 0 | 16002.7 | 0 | 0.84 | 17554.74 | 0 | 0 | 0 | 0
2022020124 | 3 | 0.45598 | 36478.4 | 0 | 0 | 0.44595 | 15608.25 | 0 | 0 | 36478.4 | 3521.6 | 0 | 15608.25 | 0 | 0 | 19129.85 | 0 | 0 | 0 | 0
2022020201 | 4 | 0.43828 | 35062.4 | 0 | 0 | 0.43453 | 15208.55 | 0 | 0 | 35062.4 | 4937.6 | 0 | 15208.55 | 0 | 0 | 20146.15 | 0 | 0 | 0 | 0
2022020202 | 4 | 0.42815 | 34252 | 0 | 0 | 0.42775 | 14971.25 | 0 | 0 | 34252 | 5748 | 0 | 14971.25 | 0 | 0 | 20719.25 | 0 | 0 | 0 | 0
2022020203 | 4 | 0.42465 | 33972 | 0 | 0 | 0.42621 | 14917.35 | 0 | 0 | 33972 | 6028 | 0 | 14917.35 | 0 | 0 | 20945.35 | 0 | 0 | 0 | 0
2022020204 | 4 | 0.42516 | 34012.8 | 0 | 0 | 0.42518 | 14881.3 | 0 | 0 | 34012.8 | 5987.2 | 0 | 14881.3 | 0 | 0 | 20868.5 | 0 | 0 | 0 | 0
2022020205 | 4 | 0.43653 | 34922.4 | 0 | 0 | 0.43945 | 15380.75 | 0 | 0 | 34922.4 | 5077.6 | 0 | 15380.75 | 0 | 0 | 20458.35 | 0 | 0 | 0 | 0
2022020206 | 4 | 0.46518 | 37214.4 | 0 | 0 | 0.48089 | 16831.15 | 0 | 0 | 37214.4 | 2785.6 | 0 | 16831.15 | 0 | 0 | 19616.75 | 0 | 0 | 0 | 0
2022020207 | 4 | 0.5089 | 40712 | 0 | 0 | 0.51682 | 18088.7 | 0 | 0 | 40000 | 0 | 712 | 17376.7 | 0 | 0 | 17376.7 | 0 | 0 | 0 | 0
2022020208 | 4 | 0.53486 | 42788.8 | 0 | 0 | 0.54148 | 18951.8 | 0.00104 | 14.56 | 40000 | 0 | 2788.8 | 16163 | 0 | 14.56 | 16177.56 | 0 | 0 | 0 | 0
2022020209 | 4 | 0.54297 | 43437.6 | 0 | 0 | 0.53648 | 18776.8 | 0.01074 | 150.36 | 40000 | 0 | 3437.6 | 15339.2 | 0 | 150.36 | 15489.56 | 0 | 0 | 0 | 0
2022020210 | 4 | 0.55145 | 44116 | 0 | 0 | 0.54612 | 19114.2 | 0.03143 | 440.02 | 40000 | 0 | 4116 | 14998.2 | 0 | 440.02 | 15438.22 | 0 | 0 | 0 | 0
2022020211 | 4 | 0.56059 | 44847.2 | 0 | 0 | 0.55174 | 19310.9 | 0.079 | 1106 | 40000 | 0 | 4847.2 | 14463.7 | 0 | 1106 | 15569.7 | 0 | 0 | 0 | 0
2022020212 | 4 | 0.56722 | 45377.6 | 0 | 0 | 0.51584 | 18054.4 | 0.12801 | 1792.14 | 40000 | 0 | 5377.6 | 12676.8 | 0 | 1792.14 | 14468.94 | 0 | 0 | 0 | 0
2022020213 | 4 | 0.57384 | 45907.2 | 0 | 0 | 0.50544 | 17690.4 | 0.16296 | 2281.44 | 40000 | 0 | 5907.2 | 11783.2 | 0 | 2281.44 | 14064.64 | 0 | 0 | 0 | 0
2022020214 | 4 | 0.57933 | 46346.4 | 0 | 0 | 0.50915 | 17820.25 | 0.1801 | 2521.4 | 40000 | 0 | 6346.4 | 11473.85 | 0 | 2521.4 | 13995.25 | 0 | 0 | 0 | 0
2022020215 | 4 | 0.58183 | 46546.4 | 0 | 0 | 0.49982 | 17493.7 | 0.15715 | 2200.1 | 40000 | 0 | 6546.4 | 10947.3 | 0 | 2200.1 | 13147.4 | 0 | 0 | 0 | 0
2022020216 | 4 | 0.58713 | 46970.4 | 0 | 0 | 0.4944 | 17304 | 0.10392 | 1454.88 | 40000 | 0 | 6970.4 | 10333.6 | 0 | 1454.88 | 11788.48 | 0 | 0 | 0 | 0
2022020217 | 4 | 0.60367 | 48293.6 | 0 | 0 | 0.49908 | 17467.8 | 0.05785 | 809.9 | 40000 | 0 | 8293.6 | 9174.2 | 0 | 809.9 | 9984.1 | 0 | 0 | 0 | 0
2022020218 | 4 | 0.62933 | 50346.4 | 0 | 0 | 0.49169 | 17209.15 | 0.0147 | 205.8 | 40000 | 0 | 10346.4 | 6862.75 | 0 | 205.8 | 7068.55 | 0 | 0 | 0 | 0
2022020219 | 4 | 0.65293 | 52234.4 | 0 | 0 | 0.4919 | 17216.5 | 0.00013 | 1.82 | 40000 | 0 | 12234.4 | 4982.1 | 0 | 1.82 | 4983.92 | 0 | 0 | 0 | 0
2022020220 | 4 | 0.65787 | 52629.6 | 0 | 0 | 0.50331 | 17615.85 | 0 | 0 | 40000 | 0 | 12629.6 | 4986.25 | 0 | 0 | 4986.25 | 0 | 0 | 0 | 0
2022020221 | 4 | 0.65401 | 52320.8 | 0 | 0 | 0.50297 | 17603.95 | 0 | 0 | 40000 | 0 | 12320.8 | 5283.15 | 0 | 0 | 5283.15 | 0 | 0 | 0 | 0
2022020222 | 4 | 0.64459 | 51567.2 | 0 | 0 | 0.50226 | 17579.1 | 0 | 0 | 40000 | 0 | 11567.2 | 6011.9 | 0 | 0 | 6011.9 | 0 | 0 | 0 | 0
2022020223 | 4 | 0.62549 | 50039.2 | 0 | 0 | 0.50631 | 17720.85 | 0 | 0 | 40000 | 0 | 10039.2 | 7681.65 | 0 | 0 | 7681.65 | 0 | 0 | 0 | 0
2022020224 | 4 | 0.60616 | 48492.8 | 0 | 0 | 0.50774 | 17770.9 | 0 | 0 | 40000 | 0 | 8492.8 | 9278.1 | 0 | 0 | 9278.1 | 0 | 0 | 0 | 0
2022020301 | 5 | 0.59344 | 47475.2 | 0 | 0 | 0.49973 | 17490.55 | 0 | 0 | 40000 | 0 | 7475.2 | 10015.35 | 0 | 0 | 10015.35 | 0 | 0 | 0 | 0
2022020302 | 5 | 0.592 | 47360 | 0 | 0 | 0.48533 | 16986.55 | 0 | 0 | 40000 | 0 | 7360 | 9626.55 | 0 | 0 | 9626.55 | 0 | 0 | 0 | 0
2022020303 | 5 | 0.60021 | 48016.8 | 0 | 0 | 0.5036 | 17626 | 0 | 0 | 40000 | 0 | 8016.8 | 9609.2 | 0 | 0 | 9609.2 | 0 | 0 | 0 | 0
2022020304 | 5 | 0.61454 | 49163.2 | 0 | 0 | 0.5298 | 18543 | 0 | 0 | 40000 | 0 | 9163.2 | 9379.8 | 0 | 0 | 9379.8 | 0 | 0 | 0 | 0
2022020305 | 5 | 0.63467 | 50773.6 | 0 | 0 | 0.53851 | 18847.85 | 0 | 0 | 40000 | 0 | 10773.6 | 8074.25 | 0 | 0 | 8074.25 | 0 | 0 | 0 | 0
2022020306 | 5 | 0.66578 | 53262.4 | 0 | 0 | 0.53875 | 18856.25 | 0 | 0 | 40000 | 0 | 13262.4 | 5593.85 | 0 | 0 | 5593.85 | 0 | 0 | 0 | 0
2022020307 | 5 | 0.70634 | 56507.2 | 0 | 0 | 0.53668 | 18783.8 | 0 | 0 | 40000 | 0 | 16507.2 | 2276.6 | 0 | 0 | 2276.6 | 0 | 0 | 0 | 0
2022020308 | 5 | 0.73775 | 59020 | 0 | 0 | 0.52419 | 18346.65 | 0.00101 | 14.14 | 40000 | 0 | 18346.65 | 0 | 14.14 | 0 | 0 | 659.21 | 0 | 0 | 659.21
2022020309 | 5 | 0.75723 | 60578.4 | 0 | 0 | 0.50264 | 17592.4 | 0.04024 | 563.36 | 40000 | 0 | 17592.4 | 0 | 563.36 | 0 | 0 | 2422.64 | 0 | 0 | 2422.64
2022020310 | 5 | 0.7778 | 62224 | 0 | 0 | 0.50196 | 17568.6 | 0.1278 | 1789.2 | 40000 | 0 | 17568.6 | 0 | 1789.2 | 0 | 0 | 2866.2 | 0 | 0 | 2866.2
2022020311 | 5 | 0.79275 | 63420 | 0 | 0 | 0.5051 | 17678.5 | 0.23704 | 3318.56 | 40000 | 0 | 17678.5 | 0 | 3318.56 | 0 | 0 | 2422.94 | 0 | 0 | 2422.94
2022020312 | 5 | 0.80065 | 64052 | 0 | 0 | 0.49979 | 17492.65 | 0.33381 | 4673.34 | 40000 | 0 | 17492.65 | 0 | 4673.34 | 0 | 0 | 1886.01 | 0 | 0 | 1886.01
2022020313 | 5 | 0.80239 | 64191.2 | 0 | 0 | 0.50342 | 17619.7 | 0.36217 | 5070.38 | 40000 | 0 | 17619.7 | 0 | 5070.38 | 0 | 0 | 1501.12 | 0 | 0 | 1501.12
2022020314 | 5 | 0.80062 | 64049.6 | 0 | 0 | 0.51039 | 17863.65 | 0.37449 | 5242.86 | 40000 | 0 | 17863.65 | 0 | 5242.86 | 0 | 0 | 943.09 | 0 | 0 | 943.09
2022020315 | 5 | 0.79794 | 63835.2 | 0 | 0 | 0.51028 | 17859.8 | 0.33906 | 4746.84 | 40000 | 0 | 17859.8 | 0 | 4746.84 | 0 | 0 | 1228.56 | 0 | 0 | 1228.56
2022020316 | 5 | 0.80031 | 64024.8 | 0 | 0 | 0.50179 | 17562.65 | 0.32035 | 4484.9 | 40000 | 0 | 17562.65 | 0 | 4484.9 | 0 | 0 | 1977.25 | 0 | 0 | 1977.25
2022020317 | 5 | 0.80996 | 64796.8 | 0 | 0 | 0.482 | 16870 | 0.3004 | 4205.6 | 40000 | 0 | 16870 | 0 | 4205.6 | 0 | 0 | 3721.2 | 0 | 0 | 3721.2
2022020318 | 5 | 0.82784 | 66227.2 | 0 | 0 | 0.45728 | 16004.8 | 0.16103 | 2254.42 | 40000 | 0 | 16004.8 | 0 | 2254.42 | 0 | 0 | 7967.98 | 0 | 0 | 7967.98
2022020319 | 5 | 0.85002 | 68001.6 | 0 | 0 | 0.43146 | 15101.1 | 0.00651 | 91.14 | 40000 | 0 | 15101.1 | 0 | 91.14 | 0 | 0 | 12809.36 | 0 | 0 | 12809.36
2022020320 | 5 | 0.84989 | 67991.2 | 0 | 0 | 0.42691 | 14941.85 | 6e-05 | 0.84 | 40000 | 0 | 14941.85 | 0 | 0.84 | 0 | 0 | 13048.51 | 0 | 0 | 13048.51
2022020321 | 5 | 0.84311 | 67448.8 | 0 | 0 | 0.43076 | 15076.6 | 0 | 0 | 40000 | 0 | 15076.6 | 0 | 0 | 0 | 0 | 12372.2 | 0 | 0 | 12372.2
2022020322 | 5 | 0.82964 | 66371.2 | 0 | 0 | 0.44502 | 15575.7 | 0 | 0 | 40000 | 0 | 15575.7 | 0 | 0 | 0 | 0 | 10795.5 | 0 | 0 | 10795.5
2022020323 | 5 | 0.80757 | 64605.6 | 0 | 0 | 0.45951 | 16082.85 | 0 | 0 | 40000 | 0 | 16082.85 | 0 | 0 | 0 | 0 | 8522.75 | 0 | 0 | 8522.75
2022020324 | 5 | 0.79074 | 63259.2 | 0 | 0 | 0.46754 | 16363.9 | 0 | 0 | 40000 | 0 | 16363.9 | 0 | 0 | 0 | 0 | 6895.3 | 0 | 0 | 6895.3
2022020401 | 6 | 0.77975 | 62380 | 0 | 0 | 0.47113 | 16489.55 | 0 | 0 | 40000 | 0 | 16489.55 | 0 | 0 | 0 | 0 | 5890.45 | 0 | 0 | 5890.45
2022020402 | 6 | 0.77547 | 62037.6 | 0 | 0 | 0.46188 | 16165.8 | 0 | 0 | 40000 | 0 | 16165.8 | 0 | 0 | 0 | 0 | 5871.8 | 0 | 0 | 5871.8
2022020403 | 6 | 0.77532 | 62025.6 | 0 | 0 | 0.42779 | 14972.65 | 0 | 0 | 40000 | 0 | 14972.65 | 0 | 0 | 0 | 0 | 7052.95 | 0 | 0 | 7052.95
2022020404 | 6 | 0.77757 | 62205.6 | 0 | 0 | 0.39545 | 13840.75 | 0 | 0 | 40000 | 0 | 13840.75 | 0 | 0 | 0 | 0 | 8364.85 | 0 | 0 | 8364.85
2022020405 | 6 | 0.78604 | 62883.2 | 0 | 0 | 0.39044 | 13665.4 | 0 | 0 | 40000 | 0 | 13665.4 | 0 | 0 | 0 | 0 | 9217.8 | 0 | 0 | 9217.8
2022020406 | 6 | 0.8053 | 64424 | 0 | 0 | 0.37933 | 13276.55 | 0 | 0 | 40000 | 0 | 13276.55 | 0 | 0 | 0 | 0 | 11147.45 | 0 | 0 | 11147.45
2022020407 | 6 | 0.82904 | 66323.2 | 0 | 0 | 0.37756 | 13214.6 | 0 | 0 | 40000 | 0 | 13214.6 | 0 | 0 | 0 | 0 | 13108.6 | 0 | 0 | 13108.6
2022020408 | 6 | 0.84894 | 67915.2 | 0 | 0 | 0.39239 | 13733.65 | 0.00504 | 70.56 | 40000 | 0 | 13733.65 | 0 | 70.56 | 0 | 0 | 14110.99 | 0 | 0 | 14110.99
2022020409 | 6 | 0.85946 | 68756.8 | 0 | 0 | 0.37951 | 13282.85 | 0.23608 | 3305.12 | 40000 | 0 | 13282.85 | 0 | 3305.12 | 0 | 0 | 12168.83 | 0 | 0 | 12168.83
2022020410 | 6 | 0.86262 | 69009.6 | 0 | 0 | 0.32102 | 11235.7 | 0.57447 | 8042.58 | 40000 | 0 | 11235.7 | 0 | 8042.58 | 0 | 0 | 9731.32 | 0 | 0 | 9731.32
2022020411 | 6 | 0.8503 | 68024 | 0 | 0 | 0.28393 | 9937.55 | 0.67244 | 9414.16 | 40000 | 0 | 9937.55 | 0 | 9414.16 | 0 | 0 | 8672.29 | 0 | 0 | 8672.29
2022020412 | 6 | 0.82657 | 66125.6 | 0 | 0 | 0.27682 | 9688.7 | 0.70721 | 9900.94 | 40000 | 0 | 9688.7 | 0 | 9900.94 | 0 | 0 | 6535.96 | 0 | 0 | 6535.96
2022020413 | 6 | 0.79753 | 63802.4 | 0 | 0 | 0.29106 | 10187.1 | 0.71271 | 9977.94 | 40000 | 0 | 10187.1 | 0 | 9977.94 | 0 | 0 | 3637.36 | 0 | 0 | 3637.36
2022020414 | 6 | 0.76711 | 61368.8 | 0 | 0 | 0.29345 | 10270.75 | 0.72261 | 10116.54 | 40000 | 0 | 10270.75 | 0 | 10116.54 | 0 | 0 | 981.51 | 0 | 0 | 981.51
2022020415 | 6 | 0.73992 | 59193.6 | 0 | 0 | 0.27841 | 9744.35 | 0.74839 | 10477.46 | 40000 | 0 | 9744.35 | 0 | 9449.25 | 1028.21 | 1028.21 | 0 | 0 | 0 | 0
2022020416 | 6 | 0.72084 | 57667.2 | 0 | 0 | 0.25881 | 9058.35 | 0.76648 | 10730.72 | 40000 | 0 | 9058.35 | 0 | 8608.85 | 2121.87 | 2121.87 | 0 | 0 | 0 | 0
2022020417 | 6 | 0.71458 | 57166.4 | 0 | 0 | 0.23403 | 8191.05 | 0.73586 | 10302.04 | 40000 | 0 | 8191.05 | 0 | 8975.35 | 1326.69 | 1326.69 | 0 | 0 | 0 | 0
2022020418 | 6 | 0.72842 | 58273.6 | 0 | 0 | 0.2018 | 7063 | 0.33628 | 4707.92 | 40000 | 0 | 7063 | 0 | 4707.92 | 0 | 0 | 6502.68 | 0 | 0 | 6502.68
2022020419 | 6 | 0.76406 | 61124.8 | 0 | 0 | 0.16046 | 5616.1 | 0.01181 | 165.34 | 40000 | 0 | 5616.1 | 0 | 165.34 | 0 | 0 | 15343.36 | 0 | 0 | 15343.36
2022020420 | 6 | 0.77266 | 61812.8 | 0 | 0 | 0.13395 | 4688.25 | 0 | 0 | 40000 | 0 | 4688.25 | 0 | 0 | 0 | 0 | 17124.55 | 0 | 0 | 17124.55
2022020421 | 6 | 0.76979 | 61583.2 | 0 | 0 | 0.13873 | 4855.55 | 0 | 0 | 40000 | 0 | 4855.55 | 0 | 0 | 0 | 0 | 16727.65 | 0 | 0 | 16727.65
2022020422 | 6 | 0.76342 | 61073.6 | 0 | 0 | 0.15229 | 5330.15 | 0 | 0 | 40000 | 0 | 5330.15 | 0 | 0 | 0 | 0 | 15743.45 | 0 | 0 | 15743.45
2022020423 | 6 | 0.75012 | 60009.6 | 0 | 0 | 0.1695 | 5932.5 | 0 | 0 | 40000 | 0 | 5932.5 | 0 | 0 | 0 | 0 | 14077.1 | 0 | 0 | 14077.1
2022020424 | 6 | 0.73327 | 58661.6 | 0 | 0 | 0.18724 | 6553.4 | 0 | 0 | 40000 | 0 | 6553.4 | 0 | 0 | 0 | 0 | 12108.2 | 0 | 0 | 12108.2
2022020501 | 7 | 0.7239 | 57912 | 0 | 0 | 0.20756 | 7264.6 | 0 | 0 | 40000 | 0 | 7264.6 | 0 | 0 | 0 | 0 | 10647.4 | 0 | 0 | 10647.4
2022020502 | 7 | 0.72183 | 57746.4 | 0 | 0 | 0.21943 | 7680.05 | 0 | 0 | 40000 | 0 | 7680.05 | 0 | 0 | 0 | 0 | 10066.35 | 0 | 0 | 10066.35
2022020503 | 7 | 0.72449 | 57959.2 | 0 | 0 | 0.21861 | 7651.35 | 0 | 0 | 40000 | 0 | 7651.35 | 0 | 0 | 0 | 0 | 10307.85 | 0 | 0 | 10307.85
2022020504 | 7 | 0.73103 | 58482.4 | 0 | 0 | 0.22014 | 7704.9 | 0 | 0 | 40000 | 0 | 7704.9 | 0 | 0 | 0 | 0 | 10777.5 | 0 | 0 | 10777.5
2022020505 | 7 | 0.74566 | 59652.8 | 0 | 0 | 0.22227 | 7779.45 | 0 | 0 | 40000 | 0 | 7779.45 | 0 | 0 | 0 | 0 | 11873.35 | 0 | 0 | 11873.35
2022020506 | 7 | 0.76343 | 61074.4 | 0 | 0 | 0.22779 | 7972.65 | 0 | 0 | 40000 | 0 | 7972.65 | 0 | 0 | 0 | 0 | 13101.75 | 0 | 0 | 13101.75
2022020507 | 7 | 0.78666 | 62932.8 | 0 | 0 | 0.21509 | 7528.15 | 0 | 0 | 40000 | 0 | 7528.15 | 0 | 0 | 0 | 0 | 15404.65 | 0 | 0 | 15404.65
2022020508 | 7 | 0.80394 | 64315.2 | 0 | 0 | 0.2118 | 7413 | 0.01839 | 257.46 | 40000 | 0 | 7413 | 0 | 257.46 | 0 | 0 | 16644.74 | 0 | 0 | 16644.74
2022020509 | 7 | 0.78989 | 63191.2 | 0 | 0 | 0.20296 | 7103.6 | 0.38218 | 5350.52 | 40000 | 0 | 7103.6 | 0 | 5350.52 | 0 | 0 | 10737.08 | 0 | 0 | 10737.08
2022020510 | 7 | 0.75185 | 60148 | 0 | 0 | 0.17614 | 6164.9 | 0.80385 | 11253.9 | 40000 | 0 | 6164.9 | 0 | 11253.9 | 0 | 0 | 2729.2 | 0 | 0 | 2729.2
2022020511 | 7 | 0.70605 | 56484 | 0 | 0 | 0.1598 | 5593 | 0.84717 | 11860.38 | 40000 | 0 | 5593 | 0 | 10891 | 969.38 | 969.38 | 0 | 0 | 0 | 0
2022020512 | 7 | 0.66493 | 53194.4 | 0 | 0 | 0.22587 | 7905.45 | 0.8283 | 11596.2 | 40000 | 0 | 7905.45 | 0 | 5288.95 | 6307.25 | 6307.25 | 0 | 0 | 0 | 0
2022020513 | 7 | 0.6274 | 50192 | 0 | 0 | 0.29667 | 10383.45 | 0.7917 | 11083.8 | 40000 | 0 | 10192 | 191.45 | 0 | 11083.8 | 11275.25 | 0 | 0 | 0 | 0
2022020514 | 7 | 0.59443 | 47554.4 | 0 | 0 | 0.31886 | 11160.1 | 0.71603 | 10024.42 | 40000 | 0 | 7554.4 | 3605.7 | 0 | 10024.42 | 13630.12 | 0 | 0 | 0 | 0
2022020515 | 7 | 0.56603 | 45282.4 | 0 | 0 | 0.33081 | 11578.35 | 0.56095 | 7853.3 | 40000 | 0 | 5282.4 | 6295.95 | 0 | 7853.3 | 14149.25 | 0 | 0 | 0 | 0
2022020516 | 7 | 0.54739 | 43791.2 | 0 | 0 | 0.33283 | 11649.05 | 0.45684 | 6395.76 | 40000 | 0 | 3791.2 | 7857.85 | 0 | 6395.76 | 14253.61 | 0 | 0 | 0 | 0
2022020517 | 7 | 0.54421 | 43536.8 | 0 | 0 | 0.33949 | 11882.15 | 0.44825 | 6275.5 | 40000 | 0 | 3536.8 | 8345.35 | 0 | 6275.5 | 14620.85 | 0 | 0 | 0 | 0
2022020518 | 7 | 0.56392 | 45113.6 | 0 | 0 | 0.35895 | 12563.25 | 0.31146 | 4360.44 | 40000 | 0 | 5113.6 | 7449.65 | 0 | 4360.44 | 11810.09 | 0 | 0 | 0 | 0
2022020519 | 7 | 0.6101 | 48808 | 0 | 0 | 0.42211 | 14773.85 | 0.01326 | 185.64 | 40000 | 0 | 8808 | 5965.85 | 0 | 185.64 | 6151.49 | 0 | 0 | 0 | 0
2022020520 | 7 | 0.63689 | 50951.2 | 0 | 0 | 0.52688 | 18440.8 | 0 | 0 | 40000 | 0 | 10951.2 | 7489.6 | 0 | 0 | 7489.6 | 0 | 0 | 0 | 0
2022020521 | 7 | 0.65308 | 52246.4 | 0 | 0 | 0.57297 | 20053.95 | 0 | 0 | 40000 | 0 | 12246.4 | 7807.55 | 0 | 0 | 7807.55 | 0 | 0 | 0 | 0
2022020522 | 7 | 0.66044 | 52835.2 | 0 | 0 | 0.57312 | 20059.2 | 0 | 0 | 40000 | 0 | 12835.2 | 7224 | 0 | 0 | 7224 | 0 | 0 | 0 | 0
2022020523 | 7 | 0.65671 | 52536.8 | 0 | 0 | 0.57612 | 20164.2 | 0 | 0 | 40000 | 0 | 12536.8 | 7627.4 | 0 | 0 | 7627.4 | 0 | 0 | 0 | 0
2022020524 | 7 | 0.65027 | 52021.6 | 0 | 0 | 0.56937 | 19927.95 | 0 | 0 | 40000 | 0 | 12021.6 | 7906.35 | 0 | 0 | 7906.35 | 0 | 0 | 0 | 0
2022020601 | 1 | 0.64653 | 51722.4 | 0 | 0 | 0.55057 | 19269.95 | 0 | 0 | 40000 | 0 | 11722.4 | 7547.55 | 0 | 0 | 7547.55 | 0 | 0 | 0 | 0
2022020602 | 1 | 0.64822 | 51857.6 | 0 | 0 | 0.54125 | 18943.75 | 0 | 0 | 40000 | 0 | 11857.6 | 7086.15 | 0 | 0 | 7086.15 | 0 | 0 | 0 | 0
2022020603 | 1 | 0.65303 | 52242.4 | 0 | 0 | 0.52409 | 18343.15 | 0 | 0 | 40000 | 0 | 12242.4 | 6100.75 | 0 | 0 | 6100.75 | 0 | 0 | 0 | 0
2022020604 | 1 | 0.66 | 52800 | 0 | 0 | 0.4907 | 17174.5 | 0 | 0 | 40000 | 0 | 12800 | 4374.5 | 0 | 0 | 4374.5 | 0 | 0 | 0 | 0
2022020605 | 1 | 0.66978 | 53582.4 | 0 | 0 | 0.4629 | 16201.5 | 0 | 0 | 40000 | 0 | 13582.4 | 2619.1 | 0 | 0 | 2619.1 | 0 | 0 | 0 | 0
2022020606 | 1 | 0.68341 | 54672.8 | 0 | 0 | 0.43805 | 15331.75 | 0 | 0 | 40000 | 0 | 14672.8 | 658.95 | 0 | 0 | 658.95 | 0 | 0 | 0 | 0
2022020607 | 1 | 0.70124 | 56099.2 | 0 | 0 | 0.40934 | 14326.9 | 0 | 0 | 40000 | 0 | 14326.9 | 0 | 0 | 0 | 0 | 1772.3 | 0 | 0 | 1772.3
2022020608 | 1 | 0.71607 | 57285.6 | 0 | 0 | 0.39156 | 13704.6 | 0.0209 | 292.6 | 40000 | 0 | 13704.6 | 0 | 292.6 | 0 | 0 | 3288.4 | 0 | 0 | 3288.4
2022020609 | 1 | 0.70009 | 56007.2 | 0 | 0 | 0.33292 | 11652.2 | 0.39711 | 5559.54 | 40000 | 0 | 11652.2 | 0 | 4355 | 1204.54 | 1204.54 | 0 | 0 | 0 | 0
2022020610 | 1 | 0.66415 | 53132 | 0 | 0 | 0.23614 | 8264.9 | 0.82211 | 11509.54 | 40000 | 0 | 8264.9 | 0 | 4867.1 | 6642.44 | 6642.44 | 0 | 0 | 0 | 0
2022020611 | 1 | 0.62453 | 49962.4 | 0 | 0 | 0.21191 | 7416.85 | 0.84253 | 11795.42 | 40000 | 0 | 7416.85 | 0 | 2545.55 | 9249.87 | 9249.87 | 0 | 0 | 0 | 0
2022020612 | 1 | 0.58561 | 46848.8 | 0 | 0 | 0.21908 | 7667.8 | 0.81357 | 11389.98 | 40000 | 0 | 6848.8 | 819 | 0 | 11389.98 | 12208.98 | 0 | 0 | 0 | 0
2022020613 | 1 | 0.55374 | 44299.2 | 0 | 0 | 0.23279 | 8147.65 | 0.78734 | 11022.76 | 40000 | 0 | 4299.2 | 3848.45 | 0 | 11022.76 | 14871.21 | 0 | 0 | 0 | 0
2022020614 | 1 | 0.52722 | 42177.6 | 0 | 0 | 0.2504 | 8764 | 0.73213 | 10249.82 | 40000 | 0 | 2177.6 | 6586.4 | 0 | 10249.82 | 16836.22 | 0 | 0 | 0 | 0
2022020615 | 1 | 0.50974 | 40779.2 | 0 | 0 | 0.27625 | 9668.75 | 0.70158 | 9822.12 | 40000 | 0 | 779.2 | 8889.55 | 0 | 9822.12 | 18711.67 | 0 | 0 | 0 | 0
2022020616 | 1 | 0.49985 | 39988 | 0 | 0 | 0.31292 | 10952.2 | 0.53846 | 7538.44 | 39988 | 12 | 0 | 10952.2 | 0 | 7538.44 | 18502.64 | 0 | 0 | 0 | 0
2022020617 | 1 | 0.50143 | 40114.4 | 0 | 0 | 0.3442 | 12047 | 0.38829 | 5436.06 | 40000 | 0 | 114.4 | 11932.6 | 0 | 5436.06 | 17368.66 | 0 | 0 | 0 | 0
2022020618 | 1 | 0.51965 | 41572 | 0 | 0 | 0.35581 | 12453.35 | 0.23091 | 3232.74 | 40000 | 0 | 1572 | 10881.35 | 0 | 3232.74 | 14114.09 | 0 | 0 | 0 | 0
2022020619 | 1 | 0.55452 | 44361.6 | 0 | 0 | 0.35387 | 12385.45 | 0.01136 | 159.04 | 40000 | 0 | 4361.6 | 8023.85 | 0 | 159.04 | 8182.89 | 0 | 0 | 0 | 0
2022020620 | 1 | 0.57313 | 45850.4 | 0 | 0 | 0.3825 | 13387.5 | 0.00015 | 2.1 | 40000 | 0 | 5850.4 | 7537.1 | 0 | 2.1 | 7539.2 | 0 | 0 | 0 | 0
2022020621 | 1 | 0.57975 | 46380 | 0 | 0 | 0.39287 | 13750.45 | 0.00015 | 2.1 | 40000 | 0 | 6380 | 7370.45 | 0 | 2.1 | 7372.55 | 0 | 0 | 0 | 0
2022020622 | 1 | 0.57659 | 46127.2 | 0 | 0 | 0.38184 | 13364.4 | 0.00015 | 2.1 | 40000 | 0 | 6127.2 | 7237.2 | 0 | 2.1 | 7239.3 | 0 | 0 | 0 | 0
2022020623 | 1 | 0.5604 | 44832 | 0 | 0 | 0.37605 | 13161.75 | 0.00015 | 2.1 | 40000 | 0 | 4832 | 8329.75 | 0 | 2.1 | 8331.85 | 0 | 0 | 0 | 0
2022020624 | 1 | 0.54378 | 43502.4 | 0 | 0 | 0.36712 | 12849.2 | 0.00015 | 2.1 | 40000 | 0 | 3502.4 | 9346.8 | 0 | 2.1 | 9348.9 | 0 | 0 | 0 | 0
2022020701 | 2 | 0.53377 | 42701.6 | 0 | 0 | 0.34945 | 12230.75 | 0.00015 | 2.1 | 40000 | 0 | 2701.6 | 9529.15 | 0 | 2.1 | 9531.25 | 0 | 0 | 0 | 0
2022020702 | 2 | 0.53051 | 42440.8 | 0 | 0 | 0.35168 | 12308.8 | 0.00015 | 2.1 | 40000 | 0 | 2440.8 | 9868 | 0 | 2.1 | 9870.1 | 0 | 0 | 0 | 0
2022020703 | 2 | 0.53462 | 42769.6 | 0 | 0 | 0.34253 | 11988.55 | 0.00015 | 2.1 | 40000 | 0 | 2769.6 | 9218.95 | 0 | 2.1 | 9221.05 | 0 | 0 | 0 | 0
2022020704 | 2 | 0.54514 | 43611.2 | 0 | 0 | 0.33084 | 11579.4 | 0.00015 | 2.1 | 40000 | 0 | 3611.2 | 7968.2 | 0 | 2.1 | 7970.3 | 0 | 0 | 0 | 0
2022020705 | 2 | 0.56536 | 45228.8 | 0 | 0 | 0.31006 | 10852.1 | 0.00015 | 2.1 | 40000 | 0 | 5228.8 | 5623.3 | 0 | 2.1 | 5625.4 | 0 | 0 | 0 | 0
2022020706 | 2 | 0.6017 | 48136 | 0 | 0 | 0.28367 | 9928.45 | 0.00015 | 2.1 | 40000 | 0 | 8136 | 1792.45 | 0 | 2.1 | 1794.55 | 0 | 0 | 0 | 0
2022020707 | 2 | 0.65342 | 52273.6 | 0 | 0 | 0.26891 | 9411.85 | 0.00015 | 2.1 | 40000 | 0 | 9411.85 | 0 | 2.1 | 0 | 0 | 2859.65 | 0 | 0 | 2859.65
2022020708 | 2 | 0.67837 | 54269.6 | 0 | 0 | 0.26535 | 9287.25 | 0.01665 | 233.1 | 40000 | 0 | 9287.25 | 0 | 233.1 | 0 | 0 | 4749.25 | 0 | 0 | 4749.25
2022020709 | 2 | 0.6588 | 52704 | 0 | 0 | 0.22577 | 7901.95 | 0.37111 | 5195.54 | 40000 | 0 | 7901.95 | 0 | 4802.05 | 393.49 | 393.49 | 0 | 0 | 0 | 0
2022020710 | 2 | 0.62668 | 50134.4 | 0 | 0 | 0.14831 | 5190.85 | 0.78551 | 10997.14 | 40000 | 0 | 5190.85 | 0 | 4943.55 | 6053.59 | 6053.59 | 0 | 0 | 0 | 0
2022020711 | 2 | 0.59797 | 47837.6 | 0 | 0 | 0.12756 | 4464.6 | 0.83196 | 11647.44 | 40000 | 0 | 4464.6 | 0 | 3373 | 8274.44 | 8274.44 | 0 | 0 | 0 | 0
2022020712 | 2 | 0.5718 | 45744 | 0 | 0 | 0.14893 | 5212.55 | 0.81211 | 11369.54 | 40000 | 0 | 5212.55 | 0 | 531.45 | 10838.09 | 10838.09 | 0 | 0 | 0 | 0
2022020713 | 2 | 0.54905 | 43924 | 0 | 0 | 0.16448 | 5756.8 | 0.80054 | 11207.56 | 40000 | 0 | 3924 | 1832.8 | 0 | 11207.56 | 13040.36 | 0 | 0 | 0 | 0
2022020714 | 2 | 0.53116 | 42492.8 | 0 | 0 | 0.1572 | 5502 | 0.80478 | 11266.92 | 40000 | 0 | 2492.8 | 3009.2 | 0 | 11266.92 | 14276.12 | 0 | 0 | 0 | 0
2022020715 | 2 | 0.51761 | 41408.8 | 0 | 0 | 0.16009 | 5603.15 | 0.82267 | 11517.38 | 40000 | 0 | 1408.8 | 4194.35 | 0 | 11517.38 | 15711.73 | 0 | 0 | 0 | 0
2022020716 | 2 | 0.51031 | 40824.8 | 0 | 0 | 0.15789 | 5526.15 | 0.83624 | 11707.36 | 40000 | 0 | 824.8 | 4701.35 | 0 | 11707.36 | 16408.71 | 0 | 0 | 0 | 0
2022020717 | 2 | 0.5134 | 41072 | 0 | 0 | 0.15216 | 5325.6 | 0.77216 | 10810.24 | 40000 | 0 | 1072 | 4253.6 | 0 | 10810.24 | 15063.84 | 0 | 0 | 0 | 0
2022020718 | 2 | 0.52782 | 42225.6 | 0 | 0 | 0.10856 | 3799.6 | 0.35874 | 5022.36 | 40000 | 0 | 2225.6 | 1574 | 0 | 5022.36 | 6596.36 | 0 | 0 | 0 | 0
2022020719 | 2 | 0.56555 | 45244 | 0 | 0 | 0.07919 | 2771.65 | 0.0151 | 211.4 | 40000 | 0 | 2771.65 | 0 | 211.4 | 0 | 0 | 2260.95 | 0 | 0 | 2260.95
2022020720 | 2 | 0.58288 | 46630.4 | 0 | 0 | 0.08309 | 2908.15 | 0 | 0 | 40000 | 0 | 2908.15 | 0 | 0 | 0 | 0 | 3722.25 | 0 | 0 | 3722.25
2022020721 | 2 | 0.5889 | 47112 | 0 | 0 | 0.12095 | 4233.25 | 0 | 0 | 40000 | 0 | 4233.25 | 0 | 0 | 0 | 0 | 2878.75 | 0 | 0 | 2878.75
2022020722 | 2 | 0.58486 | 46788.8 | 0 | 0 | 0.16593 | 5807.55 | 0 | 0 | 40000 | 0 | 5807.55 | 0 | 0 | 0 | 0 | 981.25 | 0 | 0 | 981.25
2022020723 | 2 | 0.56811 | 45448.8 | 0 | 0 | 0.23244 | 8135.4 | 0 | 0 | 40000 | 0 | 5448.8 | 2686.6 | 0 | 0 | 2686.6 | 0 | 0 | 0 | 0
2022020724 | 2 | 0.55169 | 44135.2 | 0 | 0 | 0.30923 | 10823.05 | 0 | 0 | 40000 | 0 | 4135.2 | 6687.85 | 0 | 0 | 6687.85 | 0 | 0 | 0 | 0
2022020801 | 3 | 0.54522 | 43617.6 | 0 | 0 | 0.36449 | 12757.15 | 0 | 0 | 40000 | 0 | 3617.6 | 9139.55 | 0 | 0 | 9139.55 | 0 | 0 | 0 | 0
2022020802 | 3 | 0.54817 | 43853.6 | 0 | 0 | 0.39156 | 13704.6 | 0 | 0 | 40000 | 0 | 3853.6 | 9851 | 0 | 0 | 9851 | 0 | 0 | 0 | 0
2022020803 | 3 | 0.55715 | 44572 | 0 | 0 | 0.41795 | 14628.25 | 0 | 0 | 40000 | 0 | 4572 | 10056.25 | 0 | 0 | 10056.25 | 0 | 0 | 0 | 0
2022020804 | 3 | 0.57013 | 45610.4 | 0 | 0 | 0.4407 | 15424.5 | 0 | 0 | 40000 | 0 | 5610.4 | 9814.1 | 0 | 0 | 9814.1 | 0 | 0 | 0 | 0
2022020805 | 3 | 0.59363 | 47490.4 | 0 | 0 | 0.45692 | 15992.2 | 0 | 0 | 40000 | 0 | 7490.4 | 8501.8 | 0 | 0 | 8501.8 | 0 | 0 | 0 | 0
2022020806 | 3 | 0.63429 | 50743.2 | 0 | 0 | 0.45653 | 15978.55 | 0 | 0 | 40000 | 0 | 10743.2 | 5235.35 | 0 | 0 | 5235.35 | 0 | 0 | 0 | 0
2022020807 | 3 | 0.68925 | 55140 | 0 | 0 | 0.45695 | 15993.25 | 0 | 0 | 40000 | 0 | 15140 | 853.25 | 0 | 0 | 853.25 | 0 | 0 | 0 | 0
2022020808 | 3 | 0.70933 | 56746.4 | 0 | 0 | 0.45443 | 15905.05 | 0.02292 | 320.88 | 40000 | 0 | 15905.05 | 0 | 320.88 | 0 | 0 | 520.47 | 0 | 0 | 520.47
2022020809 | 3 | 0.67779 | 54223.2 | 0 | 0 | 0.42278 | 14797.3 | 0.39739 | 5563.46 | 40000 | 0 | 14223.2 | 574.1 | 0 | 5563.46 | 6137.56 | 0 | 0 | 0 | 0
2022020810 | 3 | 0.6296 | 50368 | 0 | 0 | 0.30606 | 10712.1 | 0.78163 | 10942.82 | 40000 | 0 | 10368 | 344.1 | 0 | 10942.82 | 11286.92 | 0 | 0 | 0 | 0
2022020811 | 3 | 0.5887 | 47096 | 0 | 0 | 0.26845 | 9395.75 | 0.85897 | 12025.58 | 40000 | 0 | 7096 | 2299.75 | 0 | 12025.58 | 14325.33 | 0 | 0 | 0 | 0
2022020812 | 3 | 0.55634 | 44507.2 | 0 | 0 | 0.28015 | 9805.25 | 0.80361 | 11250.54 | 40000 | 0 | 4507.2 | 5298.05 | 0 | 11250.54 | 16548.59 | 0 | 0 | 0 | 0
2022020813 | 3 | 0.53122 | 42497.6 | 0 | 0 | 0.32183 | 11264.05 | 0.639 | 8946 | 40000 | 0 | 2497.6 | 8766.45 | 0 | 8946 | 17712.45 | 0 | 0 | 0 | 0
2022020814 | 3 | 0.5153 | 41224 | 0 | 0 | 0.36516 | 12780.6 | 0.45555 | 6377.7 | 40000 | 0 | 1224 | 11556.6 | 0 | 6377.7 | 17934.3 | 0 | 0 | 0 | 0
2022020815 | 3 | 0.50278 | 40222.4 | 0 | 0 | 0.37325 | 13063.75 | 0.42457 | 5943.98 | 40000 | 0 | 222.4 | 12841.35 | 0 | 5943.98 | 18785.33 | 0 | 0 | 0 | 0
2022020816 | 3 | 0.49706 | 39764.8 | 0 | 0 | 0.3917 | 13709.5 | 0.4532 | 6344.8 | 39764.8 | 235.2 | 0 | 13709.5 | 0 | 6344.8 | 20289.5 | 0 | 0 | 0 | 0
2022020817 | 3 | 0.50016 | 40012.8 | 0 | 0 | 0.3743 | 13100.5 | 0.53843 | 7538.02 | 40000 | 0 | 12.8 | 13087.7 | 0 | 7538.02 | 20625.72 | 0 | 0 | 0 | 0
2022020818 | 3 | 0.50936 | 40748.8 | 0 | 0 | 0.32892 | 11512.2 | 0.34161 | 4782.54 | 40000 | 0 | 748.8 | 10763.4 | 0 | 4782.54 | 15545.94 | 0 | 0 | 0 | 0
2022020819 | 3 | 0.53869 | 43095.2 | 0 | 0 | 0.28385 | 9934.75 | 0.01642 | 229.88 | 40000 | 0 | 3095.2 | 6839.55 | 0 | 229.88 | 7069.43 | 0 | 0 | 0 | 0
2022020820 | 3 | 0.55277 | 44221.6 | 0 | 0 | 0.32493 | 11372.55 | 9e-05 | 1.26 | 40000 | 0 | 4221.6 | 7150.95 | 0 | 1.26 | 7152.21 | 0 | 0 | 0 | 0
2022020821 | 3 | 0.55505 | 44404 | 0 | 0 | 0.36903 | 12916.05 | 9e-05 | 1.26 | 40000 | 0 | 4404 | 8512.05 | 0 | 1.26 | 8513.31 | 0 | 0 | 0 | 0
2022020822 | 3 | 0.54917 | 43933.6 | 0 | 0 | 0.38574 | 13500.9 | 9e-05 | 1.26 | 40000 | 0 | 3933.6 | 9567.3 | 0 | 1.26 | 9568.56 | 0 | 0 | 0 | 0
2022020823 | 3 | 0.53296 | 42636.8 | 0 | 0 | 0.38639 | 13523.65 | 9e-05 | 1.26 | 40000 | 0 | 2636.8 | 10886.85 | 0 | 1.26 | 10888.11 | 0 | 0 | 0 | 0
2022020824 | 3 | 0.5136 | 41088 | 0 | 0 | 0.38392 | 13437.2 | 8e-05 | 1.12 | 40000 | 0 | 1088 | 12349.2 | 0 | 1.12 | 12350.32 | 0 | 0 | 0 | 0
2022020901 | 4 | 0.50455 | 40364 | 0 | 0 | 0.34859 | 12200.65 | 8e-05 | 1.12 | 40000 | 0 | 364 | 11836.65 | 0 | 1.12 | 11837.77 | 0 | 0 | 0 | 0
2022020902 | 4 | 0.50398 | 40318.4 | 0 | 0 | 0.29023 | 10158.05 | 8e-05 | 1.12 | 40000 | 0 | 318.4 | 9839.65 | 0 | 1.12 | 9840.77 | 0 | 0 | 0 | 0
2022020903 | 4 | 0.51001 | 40800.8 | 0 | 0 | 0.24038 | 8413.3 | 8e-05 | 1.12 | 40000 | 0 | 800.8 | 7612.5 | 0 | 1.12 | 7613.62 | 0 | 0 | 0 | 0
2022020904 | 4 | 0.52197 | 41757.6 | 0 | 0 | 0.19787 | 6925.45 | 8e-05 | 1.12 | 40000 | 0 | 1757.6 | 5167.85 | 0 | 1.12 | 5168.97 | 0 | 0 | 0 | 0
2022020905 | 4 | 0.54581 | 43664.8 | 0 | 0 | 0.16859 | 5900.65 | 8e-05 | 1.12 | 40000 | 0 | 3664.8 | 2235.85 | 0 | 1.12 | 2236.97 | 0 | 0 | 0 | 0
2022020906 | 4 | 0.58421 | 46736.8 | 0 | 0 | 0.1402 | 4907 | 8e-05 | 1.12 | 40000 | 0 | 4907 | 0 | 1.12 | 0 | 0 | 1828.68 | 0 | 0 | 1828.68
2022020907 | 4 | 0.64016 | 51212.8 | 0 | 0 | 0.12116 | 4240.6 | 8e-05 | 1.12 | 40000 | 0 | 4240.6 | 0 | 1.12 | 0 | 0 | 6971.08 | 0 | 0 | 6971.08
2022020908 | 4 | 0.66094 | 52875.2 | 0 | 0 | 0.10817 | 3785.95 | 0.02174 | 304.36 | 40000 | 0 | 3785.95 | 0 | 304.36 | 0 | 0 | 8784.89 | 0 | 0 | 8784.89
2022020909 | 4 | 0.63535 | 50828 | 0 | 0 | 0.09902 | 3465.7 | 0.39751 | 5565.14 | 40000 | 0 | 3465.7 | 0 | 5565.14 | 0 | 0 | 1797.16 | 0 | 0 | 1797.16
2022020910 | 4 | 0.59477 | 47581.6 | 0 | 0 | 0.05678 | 1987.3 | 0.76867 | 10761.38 | 40000 | 0 | 1987.3 | 0 | 5594.3 | 5167.08 | 5167.08 | 0 | 0 | 0 | 0
2022020911 | 4 | 0.56 | 44800 | 0 | 0 | 0.04386 | 1535.1 | 0.8038 | 11253.2 | 40000 | 0 | 1535.1 | 0 | 3264.9 | 7988.3 | 7988.3 | 0 | 0 | 0 | 0
2022020912 | 4 | 0.53071 | 42456.8 | 0 | 0 | 0.04651 | 1627.85 | 0.78602 | 11004.28 | 40000 | 0 | 1627.85 | 0 | 828.95 | 10175.33 | 10175.33 | 0 | 0 | 0 | 0
2022020913 | 4 | 0.51057 | 40845.6 | 0 | 0 | 0.04569 | 1599.15 | 0.76995 | 10779.3 | 40000 | 0 | 845.6 | 753.55 | 0 | 10779.3 | 11532.85 | 0 | 0 | 0 | 0
2022020914 | 4 | 0.50079 | 40063.2 | 0 | 0 | 0.0438 | 1533 | 0.76998 | 10779.72 | 40000 | 0 | 63.2 | 1469.8 | 0 | 10779.72 | 12249.52 | 0 | 0 | 0 | 0
2022020915 | 4 | 0.49383 | 39506.4 | 0 | 0 | 0.03627 | 1269.45 | 0.78498 | 10989.72 | 39506.4 | 493.6 | 0 | 1269.45 | 0 | 10989.72 | 12752.77 | 0 | 0 | 0 | 0
2022020916 | 4 | 0.49028 | 39222.4 | 0 | 0 | 0.03919 | 1371.65 | 0.80005 | 11200.7 | 39222.4 | 777.6 | 0 | 1371.65 | 0 | 11200.7 | 13349.95 | 0 | 0 | 0 | 0
2022020917 | 4 | 0.49324 | 39459.2 | 0 | 0 | 0.05193 | 1817.55 | 0.73514 | 10291.96 | 39459.2 | 540.8 | 0 | 1817.55 | 0 | 10291.96 | 12650.31 | 0 | 0 | 0 | 0
2022020918 | 4 | 0.50127 | 40101.6 | 0 | 0 | 0.06765 | 2367.75 | 0.35122 | 4917.08 | 40000 | 0 | 101.6 | 2266.15 | 0 | 4917.08 | 7183.23 | 0 | 0 | 0 | 0
2022020919 | 4 | 0.52276 | 41820.8 | 0 | 0 | 0.11121 | 3892.35 | 0.01689 | 236.46 | 40000 | 0 | 1820.8 | 2071.55 | 0 | 236.46 | 2308.01 | 0 | 0 | 0 | 0
2022020920 | 4 | 0.53068 | 42454.4 | 0 | 0 | 0.19361 | 6776.35 | 6e-05 | 0.84 | 40000 | 0 | 2454.4 | 4321.95 | 0 | 0.84 | 4322.79 | 0 | 0 | 0 | 0
2022020921 | 4 | 0.53041 | 42432.8 | 0 | 0 | 0.24156 | 8454.6 | 6e-05 | 0.84 | 40000 | 0 | 2432.8 | 6021.8 | 0 | 0.84 | 6022.64 | 0 | 0 | 0 | 0
2022020922 | 4 | 0.52142 | 41713.6 | 0 | 0 | 0.27068 | 9473.8 | 5e-05 | 0.7 | 40000 | 0 | 1713.6 | 7760.2 | 0 | 0.7 | 7760.9 | 0 | 0 | 0 | 0
2022020923 | 4 | 0.50457 | 40365.6 | 0 | 0 | 0.28142 | 9849.7 | 5e-05 | 0.7 | 40000 | 0 | 365.6 | 9484.1 | 0 | 0.7 | 9484.8 | 0 | 0 | 0 | 0
2022020924 | 4 | 0.48687 | 38949.6 | 0 | 0 | 0.28955 | 10134.25 | 5e-05 | 0.7 | 38949.6 | 1050.4 | 0 | 10134.25 | 0 | 0.7 | 11185.35 | 0 | 0 | 0 | 0
2022021001 | 5 | 0.47749 | 38199.2 | 0 | 0 | 0.29616 | 10365.6 | 5e-05 | 0.7 | 38199.2 | 1800.8 | 0 | 10365.6 | 0 | 0.7 | 12167.1 | 0 | 0 | 0 | 0
2022021002 | 5 | 0.4763 | 38104 | 0 | 0 | 0.28379 | 9932.65 | 5e-05 | 0.7 | 38104 | 1896 | 0 | 9932.65 | 0 | 0.7 | 11829.35 | 0 | 0 | 0 | 0
2022021003 | 5 | 0.48144 | 38515.2 | 0 | 0 | 0.26986 | 9445.1 | 5e-05 | 0.7 | 38515.2 | 1484.8 | 0 | 9445.1 | 0 | 0.7 | 10930.6 | 0 | 0 | 0 | 0
2022021004 | 5 | 0.49184 | 39347.2 | 0 | 0 | 0.22801 | 7980.35 | 5e-05 | 0.7 | 39347.2 | 652.8 | 0 | 7980.35 | 0 | 0.7 | 8633.85 | 0 | 0 | 0 | 0
2022021005 | 5 | 0.51124 | 40899.2 | 0 | 0 | 0.19404 | 6791.4 | 5e-05 | 0.7 | 40000 | 0 | 899.2 | 5892.2 | 0 | 0.7 | 5892.9 | 0 | 0 | 0 | 0
2022021006 | 5 | 0.55053 | 44042.4 | 0 | 0 | 0.17538 | 6138.3 | 5e-05 | 0.7 | 40000 | 0 | 4042.4 | 2095.9 | 0 | 0.7 | 2096.6 | 0 | 0 | 0 | 0
2022021007 | 5 | 0.60617 | 48493.6 | 0 | 0 | 0.15904 | 5566.4 | 6e-05 | 0.84 | 40000 | 0 | 5566.4 | 0 | 0.84 | 0 | 0 | 2926.36 | 0 | 0 | 2926.36
2022021008 | 5 | 0.62844 | 50275.2 | 0 | 0 | 0.178 | 6230 | 0.02301 | 322.14 | 40000 | 0 | 6230 | 0 | 322.14 | 0 | 0 | 3723.06 | 0 | 0 | 3723.06
2022021009 | 5 | 0.6051 | 48408 | 0 | 0 | 0.16655 | 5829.25 | 0.34358 | 4810.12 | 40000 | 0 | 5829.25 | 0 | 2578.75 | 2231.37 | 2231.37 | 0 | 0 | 0 | 0
2022021010 | 5 | 0.57015 | 45612 | 0 | 0 | 0.10551 | 3692.85 | 0.71612 | 10025.68 | 40000 | 0 | 3692.85 | 0 | 1919.15 | 8106.53 | 8106.53 | 0 | 0 | 0 | 0
2022021011 | 5 | 0.54046 | 43236.8 | 0 | 0 | 0.08135 | 2847.25 | 0.78606 | 11004.84 | 40000 | 0 | 2847.25 | 0 | 389.55 | 10615.29 | 10615.29 | 0 | 0 | 0 | 0
2022021012 | 5 | 0.51653 | 41322.4 | 0 | 0 | 0.0549 | 1921.5 | 0.74207 | 10388.98 | 40000 | 0 | 1322.4 | 599.1 | 0 | 10388.98 | 10988.08 | 0 | 0 | 0 | 0
2022021013 | 5 | 0.50257 | 40205.6 | 0 | 0 | 0.03103 | 1086.05 | 0.72513 | 10151.82 | 40000 | 0 | 205.6 | 880.45 | 0 | 10151.82 | 11032.27 | 0 | 0 | 0 | 0
2022021014 | 5 | 0.49604 | 39683.2 | 0 | 0 | 0.01912 | 669.2 | 0.72886 | 10204.04 | 39683.2 | 316.8 | 0 | 669.2 | 0 | 10204.04 | 11190.04 | 0 | 0 | 0 | 0
2022021015 | 5 | 0.49275 | 39420 | 0 | 0 | 0.02733 | 956.55 | 0.75638 | 10589.32 | 39420 | 580 | 0 | 956.55 | 0 | 10589.32 | 12125.87 | 0 | 0 | 0 | 0
2022021016 | 5 | 0.49055 | 39244 | 0 | 0 | 0.03721 | 1302.35 | 0.77149 | 10800.86 | 39244 | 756 | 0 | 1302.35 | 0 | 10800.86 | 12859.21 | 0 | 0 | 0 | 0
2022021017 | 5 | 0.49263 | 39410.4 | 0 | 0 | 0.03696 | 1293.6 | 0.70836 | 9917.04 | 39410.4 | 589.6 | 0 | 1293.6 | 0 | 9917.04 | 11800.24 | 0 | 0 | 0 | 0
2022021018 | 5 | 0.49897 | 39917.6 | 0 | 0 | 0.04543 | 1590.05 | 0.33769 | 4727.66 | 39917.6 | 82.4 | 0 | 1590.05 | 0 | 4727.66 | 6400.11 | 0 | 0 | 0 | 0
2022021019 | 5 | 0.51825 | 41460 | 0 | 0 | 0.06775 | 2371.25 | 0.0164 | 229.6 | 40000 | 0 | 1460 | 911.25 | 0 | 229.6 | 1140.85 | 0 | 0 | 0 | 0
2022021020 | 5 | 0.52582 | 42065.6 | 0 | 0 | 0.10804 | 3781.4 | 0 | 0 | 40000 | 0 | 2065.6 | 1715.8 | 0 | 0 | 1715.8 | 0 | 0 | 0 | 0
2022021021 | 5 | 0.52231 | 41784.8 | 0 | 0 | 0.15221 | 5327.35 | 0 | 0 | 40000 | 0 | 1784.8 | 3542.55 | 0 | 0 | 3542.55 | 0 | 0 | 0 | 0
2022021022 | 5 | 0.51231 | 40984.8 | 0 | 0 | 0.19916 | 6970.6 | 0 | 0 | 40000 | 0 | 984.8 | 5985.8 | 0 | 0 | 5985.8 | 0 | 0 | 0 | 0
2022021023 | 5 | 0.49211 | 39368.8 | 0 | 0 | 0.27554 | 9643.9 | 0 | 0 | 39368.8 | 631.2 | 0 | 9643.9 | 0 | 0 | 10275.1 | 0 | 0 | 0 | 0
2022021024 | 5 | 0.47268 | 37814.4 | 0 | 0 | 0.37895 | 13263.25 | 0 | 0 | 37814.4 | 2185.6 | 0 | 13263.25 | 0 | 0 | 15448.85 | 0 | 0 | 0 | 0
2022021101 | 6 | 0.46218 | 36974.4 | 0 | 0 | 0.46373 | 16230.55 | 0 | 0 | 36974.4 | 3025.6 | 0 | 16230.55 | 0 | 0 | 19256.15 | 0 | 0 | 0 | 0
2022021102 | 6 | 0.4605 | 36840 | 0 | 0 | 0.51234 | 17931.9 | 0 | 0 | 36840 | 3160 | 0 | 17931.9 | 0 | 0 | 21091.9 | 0 | 0 | 0 | 0
2022021103 | 6 | 0.46338 | 37070.4 | 0 | 0 | 0.53585 | 18754.75 | 0 | 0 | 37070.4 | 2929.6 | 0 | 18754.75 | 0 | 0 | 21684.35 | 0 | 0 | 0 | 0
2022021104 | 6 | 0.47006 | 37604.8 | 0 | 0 | 0.54378 | 19032.3 | 0 | 0 | 37604.8 | 2395.2 | 0 | 19032.3 | 0 | 0 | 21427.5 | 0 | 0 | 0 | 0
2022021105 | 6 | 0.486 | 38880 | 0 | 0 | 0.54383 | 19034.05 | 0 | 0 | 38880 | 1120 | 0 | 19034.05 | 0 | 0 | 20154.05 | 0 | 0 | 0 | 0
2022021106 | 6 | 0.52007 | 41605.6 | 0 | 0 | 0.54363 | 19027.05 | 0 | 0 | 40000 | 0 | 1605.6 | 17421.45 | 0 | 0 | 17421.45 | 0 | 0 | 0 | 0
2022021107 | 6 | 0.56775 | 45420 | 0 | 0 | 0.53664 | 18782.4 | 0 | 0 | 40000 | 0 | 5420 | 13362.4 | 0 | 0 | 13362.4 | 0 | 0 | 0 | 0
2022021108 | 6 | 0.58869 | 47095.2 | 0 | 0 | 0.53438 | 18703.3 | 0.01854 | 259.56 | 40000 | 0 | 7095.2 | 11608.1 | 0 | 259.56 | 11867.66 | 0 | 0 | 0 | 0
2022021109 | 6 | 0.57365 | 45892 | 0 | 0 | 0.48897 | 17113.95 | 0.23933 | 3350.62 | 40000 | 0 | 5892 | 11221.95 | 0 | 3350.62 | 14572.57 | 0 | 0 | 0 | 0
2022021110 | 6 | 0.54879 | 43903.2 | 0 | 0 | 0.3991 | 13968.5 | 0.58257 | 8155.98 | 40000 | 0 | 3903.2 | 10065.3 | 0 | 8155.98 | 18221.28 | 0 | 0 | 0 | 0
2022021111 | 6 | 0.52853 | 42282.4 | 0 | 0 | 0.39343 | 13770.05 | 0.65104 | 9114.56 | 40000 | 0 | 2282.4 | 11487.65 | 0 | 9114.56 | 20602.21 | 0 | 0 | 0 | 0
2022021112 | 6 | 0.51213 | 40970.4 | 0 | 0 | 0.38154 | 13353.9 | 0.67001 | 9380.14 | 40000 | 0 | 970.4 | 12383.5 | 0 | 9380.14 | 21763.64 | 0 | 0 | 0 | 0
2022021113 | 6 | 0.50223 | 40178.4 | 0 | 0 | 0.36234 | 12681.9 | 0.74543 | 10436.02 | 40000 | 0 | 178.4 | 12503.5 | 0 | 10436.02 | 22939.52 | 0 | 0 | 0 | 0
2022021114 | 6 | 0.49937 | 39949.6 | 0 | 0 | 0.34459 | 12060.65 | 0.74672 | 10454.08 | 39949.6 | 50.4 | 0 | 12060.65 | 0 | 10454.08 | 22565.13 | 0 | 0 | 0 | 0
2022021115 | 6 | 0.49751 | 39800.8 | 0 | 0 | 0.34016 | 11905.6 | 0.76501 | 10710.14 | 39800.8 | 199.2 | 0 | 11905.6 | 0 | 10710.14 | 22814.94 | 0 | 0 | 0 | 0
2022021116 | 6 | 0.49947 | 39957.6 | 0 | 0 | 0.37669 | 13184.15 | 0.77576 | 10860.64 | 39957.6 | 42.4 | 0 | 13184.15 | 0 | 10860.64 | 24087.19 | 0 | 0 | 0 | 0
2022021117 | 6 | 0.50231 | 40184.8 | 0 | 0 | 0.43467 | 15213.45 | 0.6281 | 8793.4 | 40000 | 0 | 184.8 | 15028.65 | 0 | 8793.4 | 23822.05 | 0 | 0 | 0 | 0
2022021118 | 6 | 0.50492 | 40393.6 | 0 | 0 | 0.52827 | 18489.45 | 0.29435 | 4120.9 | 40000 | 0 | 393.6 | 18095.85 | 0 | 4120.9 | 22216.75 | 0 | 0 | 0 | 0
2022021119 | 6 | 0.51308 | 41046.4 | 0 | 0 | 0.59753 | 20913.55 | 0.01602 | 224.28 | 40000 | 0 | 1046.4 | 19867.15 | 0 | 224.28 | 20091.43 | 0 | 0 | 0 | 0
2022021120 | 6 | 0.51418 | 41134.4 | 0 | 0 | 0.6285 | 21997.5 | 0 | 0 | 40000 | 0 | 1134.4 | 20863.1 | 0 | 0 | 20863.1 | 0 | 0 | 0 | 0
2022021121 | 6 | 0.50704 | 40563.2 | 0 | 0 | 0.65359 | 22875.65 | 0 | 0 | 40000 | 0 | 563.2 | 22312.45 | 0 | 0 | 22312.45 | 0 | 0 | 0 | 0
2022021122 | 6 | 0.49611 | 39688.8 | 0 | 0 | 0.64405 | 22541.75 | 0 | 0 | 39688.8 | 311.2 | 0 | 22541.75 | 0 | 0 | 22852.95 | 0 | 0 | 0 | 0
2022021123 | 6 | 0.4798 | 38384 | 0 | 0 | 0.62875 | 22006.25 | 0 | 0 | 38384 | 1616 | 0 | 22006.25 | 0 | 0 | 23622.25 | 0 | 0 | 0 | 0
2022021124 | 6 | 0.46056 | 36844.8 | 0 | 0 | 0.61229 | 21430.15 | 0 | 0 | 36844.8 | 3155.2 | 0 | 21430.15 | 0 | 0 | 24585.35 | 0 | 0 | 0 | 0
2022021201 | 7 | 0.44319 | 35455.2 | 0 | 0 | 0.59871 | 20954.85 | 0 | 0 | 35455.2 | 4544.8 | 0 | 20954.85 | 0 | 0 | 25499.65 | 0 | 0 | 0 | 0
2022021202 | 7 | 0.43497 | 34797.6 | 0 | 0 | 0.581 | 20335 | 0 | 0 | 34797.6 | 5202.4 | 0 | 20335 | 0 | 0 | 25537.4 | 0 | 0 | 0 | 0
2022021203 | 7 | 0.43286 | 34628.8 | 0 | 0 | 0.58274 | 20395.9 | 0 | 0 | 34628.8 | 5371.2 | 0 | 20395.9 | 0 | 0 | 25767.1 | 0 | 0 | 0 | 0
2022021204 | 7 | 0.43536 | 34828.8 | 0 | 0 | 0.59124 | 20693.4 | 0 | 0 | 34828.8 | 5171.2 | 0 | 20693.4 | 0 | 0 | 25864.6 | 0 | 0 | 0 | 0
2022021205 | 7 | 0.44099 | 35279.2 | 0 | 0 | 0.59183 | 20714.05 | 0 | 0 | 35279.2 | 4720.8 | 0 | 20714.05 | 0 | 0 | 25434.85 | 0 | 0 | 0 | 0
2022021206 | 7 | 0.45685 | 36548 | 0 | 0 | 0.59578 | 20852.3 | 0 | 0 | 36548 | 3452 | 0 | 20852.3 | 0 | 0 | 24304.3 | 0 | 0 | 0 | 0
2022021207 | 7 | 0.4797 | 38376 | 0 | 0 | 0.59948 | 20981.8 | 0 | 0 | 38376 | 1624 | 0 | 20981.8 | 0 | 0 | 22605.8 | 0 | 0 | 0 | 0
2022021208 | 7 | 0.50787 | 40629.6 | 0 | 0 | 0.59485 | 20819.75 | 0.0041 | 57.4 | 40000 | 0 | 629.6 | 20190.15 | 0 | 57.4 | 20247.55 | 0 | 0 | 0 | 0
2022021209 | 7 | 0.53556 | 42844.8 | 0 | 0 | 0.57748 | 20211.8 | 0.08297 | 1161.58 | 40000 | 0 | 2844.8 | 17367 | 0 | 1161.58 | 18528.58 | 0 | 0 | 0 | 0
2022021210 | 7 | 0.55897 | 44717.6 | 0 | 0 | 0.54785 | 19174.75 | 0.20132 | 2818.48 | 40000 | 0 | 4717.6 | 14457.15 | 0 | 2818.48 | 17275.63 | 0 | 0 | 0 | 0
2022021211 | 7 | 0.57341 | 45872.8 | 0 | 0 | 0.53707 | 18797.45 | 0.28914 | 4047.96 | 40000 | 0 | 5872.8 | 12924.65 | 0 | 4047.96 | 16972.61 | 0 | 0 | 0 | 0
2022021212 | 7 | 0.57643 | 46114.4 | 0 | 0 | 0.51843 | 18145.05 | 0.49054 | 6867.56 | 40000 | 0 | 6114.4 | 12030.65 | 0 | 6867.56 | 18898.21 | 0 | 0 | 0 | 0
2022021213 | 7 | 0.57601 | 46080.8 | 0 | 0 | 0.46248 | 16186.8 | 0.60775 | 8508.5 | 40000 | 0 | 6080.8 | 10106 | 0 | 8508.5 | 18614.5 | 0 | 0 | 0 | 0
2022021214 | 7 | 0.56875 | 45500 | 0 | 0 | 0.38831 | 13590.85 | 0.68665 | 9613.1 | 40000 | 0 | 5500 | 8090.85 | 0 | 9613.1 | 17703.95 | 0 | 0 | 0 | 0
2022021215 | 7 | 0.55317 | 44253.6 | 0 | 0 | 0.31844 | 11145.4 | 0.73198 | 10247.72 | 40000 | 0 | 4253.6 | 6891.8 | 0 | 10247.72 | 17139.52 | 0 | 0 | 0 | 0
2022021216 | 7 | 0.54172 | 43337.6 | 0 | 0 | 0.27776 | 9721.6 | 0.79478 | 11126.92 | 40000 | 0 | 3337.6 | 6384 | 0 | 11126.92 | 17510.92 | 0 | 0 | 0 | 0
2022021217 | 7 | 0.53986 | 43188.8 | 0 | 0 | 0.25448 | 8906.8 | 0.75254 | 10535.56 | 40000 | 0 | 3188.8 | 5718 | 0 | 10535.56 | 16253.56 | 0 | 0 | 0 | 0
2022021218 | 7 | 0.55383 | 44306.4 | 0 | 0 | 0.22944 | 8030.4 | 0.3768 | 5275.2 | 40000 | 0 | 4306.4 | 3724 | 0 | 5275.2 | 8999.2 | 0 | 0 | 0 | 0
2022021219 | 7 | 0.5899 | 47192 | 0 | 0 | 0.19383 | 6784.05 | 0.02146 | 300.44 | 40000 | 0 | 6784.05 | 0 | 300.44 | 0 | 0 | 107.51 | 0 | 0 | 107.51
2022021220 | 7 | 0.60789 | 48631.2 | 0 | 0 | 0.18828 | 6589.8 | 6e-05 | 0.84 | 40000 | 0 | 6589.8 | 0 | 0.84 | 0 | 0 | 2040.56 | 0 | 0 | 2040.56
2022021221 | 7 | 0.61462 | 49169.6 | 0 | 0 | 0.19397 | 6788.95 | 6e-05 | 0.84 | 40000 | 0 | 6788.95 | 0 | 0.84 | 0 | 0 | 2379.81 | 0 | 0 | 2379.81
2022021222 | 7 | 0.61686 | 49348.8 | 0 | 0 | 0.20413 | 7144.55 | 6e-05 | 0.84 | 40000 | 0 | 7144.55 | 0 | 0.84 | 0 | 0 | 2203.41 | 0 | 0 | 2203.41
2022021223 | 7 | 0.61144 | 48915.2 | 0 | 0 | 0.24208 | 8472.8 | 6e-05 | 0.84 | 40000 | 0 | 8472.8 | 0 | 0.84 | 0 | 0 | 441.56 | 0 | 0 | 441.56
2022021224 | 7 | 0.60394 | 48315.2 | 0 | 0 | 0.29556 | 10344.6 | 6e-05 | 0.84 | 40000 | 0 | 8315.2 | 2029.4 | 0 | 0.84 | 2030.24 | 0 | 0 | 0 | 0
2022021301 | 1 | 0.59953 | 47962.4 | 0 | 0 | 0.36567 | 12798.45 | 6e-05 | 0.84 | 40000 | 0 | 7962.4 | 4836.05 | 0 | 0.84 | 4836.89 | 0 | 0 | 0 | 0
2022021302 | 1 | 0.59952 | 47961.6 | 0 | 0 | 0.40125 | 14043.75 | 6e-05 | 0.84 | 40000 | 0 | 7961.6 | 6082.15 | 0 | 0.84 | 6082.99 | 0 | 0 | 0 | 0
2022021303 | 1 | 0.60284 | 48227.2 | 0 | 0 | 0.41651 | 14577.85 | 6e-05 | 0.84 | 40000 | 0 | 8227.2 | 6350.65 | 0 | 0.84 | 6351.49 | 0 | 0 | 0 | 0
2022021304 | 1 | 0.6098 | 48784 | 0 | 0 | 0.41699 | 14594.65 | 6e-05 | 0.84 | 40000 | 0 | 8784 | 5810.65 | 0 | 0.84 | 5811.49 | 0 | 0 | 0 | 0
2022021305 | 1 | 0.62 | 49600 | 0 | 0 | 0.4066 | 14231 | 6e-05 | 0.84 | 40000 | 0 | 9600 | 4631 | 0 | 0.84 | 4631.84 | 0 | 0 | 0 | 0
2022021306 | 1 | 0.6356 | 50848 | 0 | 0 | 0.38932 | 13626.2 | 6e-05 | 0.84 | 40000 | 0 | 10848 | 2778.2 | 0 | 0.84 | 2779.04 | 0 | 0 | 0 | 0
2022021307 | 1 | 0.65756 | 52604.8 | 0 | 0 | 0.3841 | 13443.5 | 6e-05 | 0.84 | 40000 | 0 | 12604.8 | 838.7 | 0 | 0.84 | 839.54 | 0 | 0 | 0 | 0
2022021308 | 1 | 0.67385 | 53908 | 0 | 0 | 0.34983 | 12244.05 | 0.03377 | 472.78 | 40000 | 0 | 12244.05 | 0 | 472.78 | 0 | 0 | 1191.17 | 0 | 0 | 1191.17
2022021309 | 1 | 0.66194 | 52955.2 | 0 | 0 | 0.27327 | 9564.45 | 0.47364 | 6630.96 | 40000 | 0 | 9564.45 | 0 | 3390.75 | 3240.21 | 3240.21 | 0 | 0 | 0 | 0
2022021310 | 1 | 0.63131 | 50504.8 | 0 | 0 | 0.14212 | 4974.2 | 0.84384 | 11813.76 | 40000 | 0 | 4974.2 | 0 | 5530.6 | 6283.16 | 6283.16 | 0 | 0 | 0 | 0
2022021311 | 1 | 0.59468 | 47574.4 | 0 | 0 | 0.11652 | 4078.2 | 0.86653 | 12131.42 | 40000 | 0 | 4078.2 | 0 | 3496.2 | 8635.22 | 8635.22 | 0 | 0 | 0 | 0
2022021312 | 1 | 0.55913 | 44730.4 | 0 | 0 | 0.08552 | 2993.2 | 0.84764 | 11866.96 | 40000 | 0 | 2993.2 | 0 | 1737.2 | 10129.76 | 10129.76 | 0 | 0 | 0 | 0
2022021313 | 1 | 0.52875 | 42300 | 0 | 0 | 0.05458 | 1910.3 | 0.82739 | 11583.46 | 40000 | 0 | 1910.3 | 0 | 389.7 | 11193.76 | 11193.76 | 0 | 0 | 0 | 0
2022021314 | 1 | 0.50517 | 40413.6 | 0 | 0 | 0.04988 | 1745.8 | 0.83002 | 11620.28 | 40000 | 0 | 413.6 | 1332.2 | 0 | 11620.28 | 12952.48 | 0 | 0 | 0 | 0
2022021315 | 1 | 0.48831 | 39064.8 | 0 | 0 | 0.05918 | 2071.3 | 0.85129 | 11918.06 | 39064.8 | 935.2 | 0 | 2071.3 | 0 | 11918.06 | 14924.56 | 0 | 0 | 0 | 0
2022021316 | 1 | 0.4808 | 38464 | 0 | 0 | 0.07485 | 2619.75 | 0.86783 | 12149.62 | 38464 | 1536 | 0 | 2619.75 | 0 | 12149.62 | 16305.37 | 0 | 0 | 0 | 0
2022021317 | 1 | 0.48251 | 38600.8 | 0 | 0 | 0.09179 | 3212.65 | 0.81188 | 11366.32 | 38600.8 | 1399.2 | 0 | 3212.65 | 0 | 11366.32 | 15978.17 | 0 | 0 | 0 | 0
2022021318 | 1 | 0.48766 | 39012.8 | 0 | 0 | 0.09991 | 3496.85 | 0.41799 | 5851.86 | 39012.8 | 987.2 | 0 | 3496.85 | 0 | 5851.86 | 10335.91 | 0 | 0 | 0 | 0
2022021319 | 1 | 0.50682 | 40545.6 | 0 | 0 | 0.11048 | 3866.8 | 0.02462 | 344.68 | 40000 | 0 | 545.6 | 3321.2 | 0 | 344.68 | 3665.88 | 0 | 0 | 0 | 0
2022021320 | 1 | 0.5203 | 41624 | 0 | 0 | 0.17886 | 6260.1 | 0 | 0 | 40000 | 0 | 1624 | 4636.1 | 0 | 0 | 4636.1 | 0 | 0 | 0 | 0
2022021321 | 1 | 0.52945 | 42356 | 0 | 0 | 0.27727 | 9704.45 | 0 | 0 | 40000 | 0 | 2356 | 7348.45 | 0 | 0 | 7348.45 | 0 | 0 | 0 | 0
2022021322 | 1 | 0.54098 | 43278.4 | 0 | 0 | 0.38822 | 13587.7 | 0 | 0 | 40000 | 0 | 3278.4 | 10309.3 | 0 | 0 | 10309.3 | 0 | 0 | 0 | 0
2022021323 | 1 | 0.53589 | 42871.2 | 0 | 0 | 0.48516 | 16980.6 | 0 | 0 | 40000 | 0 | 2871.2 | 14109.4 | 0 | 0 | 14109.4 | 0 | 0 | 0 | 0
2022021324 | 1 | 0.52271 | 41816.8 | 0 | 0 | 0.54413 | 19044.55 | 0 | 0 | 40000 | 0 | 1816.8 | 17227.75 | 0 | 0 | 17227.75 | 0 | 0 | 0 | 0
2022021401 | 2 | 0.51443 | 41154.4 | 0 | 0 | 0.58878 | 20607.3 | 0 | 0 | 40000 | 0 | 1154.4 | 19452.9 | 0 | 0 | 19452.9 | 0 | 0 | 0 | 0
2022021402 | 2 | 0.51474 | 41179.2 | 0 | 0 | 0.59691 | 20891.85 | 0 | 0 | 40000 | 0 | 1179.2 | 19712.65 | 0 | 0 | 19712.65 | 0 | 0 | 0 | 0
2022021403 | 2 | 0.51874 | 41499.2 | 0 | 0 | 0.5951 | 20828.5 | 0 | 0 | 40000 | 0 | 1499.2 | 19329.3 | 0 | 0 | 19329.3 | 0 | 0 | 0 | 0
2022021404 | 2 | 0.52981 | 42384.8 | 0 | 0 | 0.5926 | 20741 | 0 | 0 | 40000 | 0 | 2384.8 | 18356.2 | 0 | 0 | 18356.2 | 0 | 0 | 0 | 0
2022021405 | 2 | 0.55015 | 44012 | 0 | 0 | 0.57958 | 20285.3 | 0 | 0 | 40000 | 0 | 4012 | 16273.3 | 0 | 0 | 16273.3 | 0 | 0 | 0 | 0
2022021406 | 2 | 0.58823 | 47058.4 | 0 | 0 | 0.54036 | 18912.6 | 0 | 0 | 40000 | 0 | 7058.4 | 11854.2 | 0 | 0 | 11854.2 | 0 | 0 | 0 | 0
2022021407 | 2 | 0.64399 | 51519.2 | 0 | 0 | 0.50733 | 17756.55 | 0 | 0 | 40000 | 0 | 11519.2 | 6237.35 | 0 | 0 | 6237.35 | 0 | 0 | 0 | 0
2022021408 | 2 | 0.66569 | 53255.2 | 0 | 0 | 0.47899 | 16764.65 | 0.03528 | 493.92 | 40000 | 0 | 13255.2 | 3509.45 | 0 | 493.92 | 4003.37 | 0 | 0 | 0 | 0
2022021409 | 2 | 0.63959 | 51167.2 | 0 | 0 | 0.41536 | 14537.6 | 0.48548 | 6796.72 | 40000 | 0 | 11167.2 | 3370.4 | 0 | 6796.72 | 10167.12 | 0 | 0 | 0 | 0
2022021410 | 2 | 0.59951 | 47960.8 | 0 | 0 | 0.26818 | 9386.3 | 0.84791 | 11870.74 | 40000 | 0 | 7960.8 | 1425.5 | 0 | 11870.74 | 13296.24 | 0 | 0 | 0 | 0
2022021411 | 2 | 0.56514 | 45211.2 | 0 | 0 | 0.23232 | 8131.2 | 0.87127 | 12197.78 | 40000 | 0 | 5211.2 | 2920 | 0 | 12197.78 | 15117.78 | 0 | 0 | 0 | 0
2022021412 | 2 | 0.5368 | 42944 | 0 | 0 | 0.23154 | 8103.9 | 0.8522 | 11930.8 | 40000 | 0 | 2944 | 5159.9 | 0 | 11930.8 | 17090.7 | 0 | 0 | 0 | 0
2022021413 | 2 | 0.51571 | 41256.8 | 0 | 0 | 0.23758 | 8315.3 | 0.83422 | 11679.08 | 40000 | 0 | 1256.8 | 7058.5 | 0 | 11679.08 | 18737.58 | 0 | 0 | 0 | 0
2022021414 | 2 | 0.50439 | 40351.2 | 0 | 0 | 0.2693 | 9425.5 | 0.8316 | 11642.4 | 40000 | 0 | 351.2 | 9074.3 | 0 | 11642.4 | 20716.7 | 0 | 0 | 0 | 0
2022021415 | 2 | 0.49484 | 39587.2 | 0 | 0 | 0.29877 | 10456.95 | 0.85024 | 11903.36 | 39587.2 | 412.8 | 0 | 10456.95 | 0 | 11903.36 | 22773.11 | 0 | 0 | 0 | 0
2022021416 | 2 | 0.49083 | 39266.4 | 0 | 0 | 0.32581 | 11403.35 | 0.85552 | 11977.28 | 39266.4 | 733.6 | 0 | 11403.35 | 0 | 11977.28 | 24114.23 | 0 | 0 | 0 | 0
2022021417 | 2 | 0.49316 | 39452.8 | 0 | 0 | 0.34831 | 12190.85 | 0.78862 | 11040.68 | 39452.8 | 547.2 | 0 | 12190.85 | 0 | 11040.68 | 23778.73 | 0 | 0 | 0 | 0
2022021418 | 2 | 0.49843 | 39874.4 | 0 | 0 | 0.37844 | 13245.4 | 0.40812 | 5713.68 | 39874.4 | 125.6 | 0 | 13245.4 | 0 | 5713.68 | 19084.68 | 0 | 0 | 0 | 0
2022021419 | 2 | 0.52055 | 41644 | 0 | 0 | 0.42355 | 14824.25 | 0.02551 | 357.14 | 40000 | 0 | 1644 | 13180.25 | 0 | 357.14 | 13537.39 | 0 | 0 | 0 | 0
2022021420 | 2 | 0.53358 | 42686.4 | 0 | 0 | 0.56378 | 19732.3 | 6e-05 | 0.84 | 40000 | 0 | 2686.4 | 17045.9 | 0 | 0.84 | 17046.74 | 0 | 0 | 0 | 0
2022021421 | 2 | 0.53365 | 42692 | 0 | 0 | 0.63514 | 22229.9 | 6e-05 | 0.84 | 40000 | 0 | 2692 | 19537.9 | 0 | 0.84 | 19538.74 | 0 | 0 | 0 | 0
2022021422 | 2 | 0.52423 | 41938.4 | 0 | 0 | 0.64312 | 22509.2 | 6e-05 | 0.84 | 40000 | 0 | 1938.4 | 20570.8 | 0 | 0.84 | 20571.64 | 0 | 0 | 0 | 0
2022021423 | 2 | 0.50429 | 40343.2 | 0 | 0 | 0.63754 | 22313.9 | 6e-05 | 0.84 | 40000 | 0 | 343.2 | 21970.7 | 0 | 0.84 | 21971.54 | 0 | 0 | 0 | 0
2022021424 | 2 | 0.48353 | 38682.4 | 0 | 0 | 0.63229 | 22130.15 | 6e-05 | 0.84 | 38682.4 | 1317.6 | 0 | 22130.15 | 0 | 0.84 | 23448.59 | 0 | 0 | 0 | 0
2022021501 | 3 | 0.47229 | 37783.2 | 0 | 0 | 0.63836 | 22342.6 | 6e-05 | 0.84 | 37783.2 | 2216.8 | 0 | 22342.6 | 0 | 0.84 | 24560.24 | 0 | 0 | 0 | 0
2022021502 | 3 | 0.46857 | 37485.6 | 0 | 0 | 0.63642 | 22274.7 | 6e-05 | 0.84 | 37485.6 | 2514.4 | 0 | 22274.7 | 0 | 0.84 | 24789.94 | 0 | 0 | 0 | 0
2022021503 | 3 | 0.47017 | 37613.6 | 0 | 0 | 0.63983 | 22394.05 | 6e-05 | 0.84 | 37613.6 | 2386.4 | 0 | 22394.05 | 0 | 0.84 | 24781.29 | 0 | 0 | 0 | 0
2022021504 | 3 | 0.47883 | 38306.4 | 0 | 0 | 0.64015 | 22405.25 | 6e-05 | 0.84 | 38306.4 | 1693.6 | 0 | 22405.25 | 0 | 0.84 | 24099.69 | 0 | 0 | 0 | 0
2022021505 | 3 | 0.49606 | 39684.8 | 0 | 0 | 0.64339 | 22518.65 | 6e-05 | 0.84 | 39684.8 | 315.2 | 0 | 22518.65 | 0 | 0.84 | 22834.69 | 0 | 0 | 0 | 0
2022021506 | 3 | 0.53087 | 42469.6 | 0 | 0 | 0.64877 | 22706.95 | 6e-05 | 0.84 | 40000 | 0 | 2469.6 | 20237.35 | 0 | 0.84 | 20238.19 | 0 | 0 | 0 | 0
2022021507 | 3 | 0.58274 | 46619.2 | 0 | 0 | 0.65563 | 22947.05 | 6e-05 | 0.84 | 40000 | 0 | 6619.2 | 16327.85 | 0 | 0.84 | 16328.69 | 0 | 0 | 0 | 0
2022021508 | 3 | 0.59974 | 47979.2 | 0 | 0 | 0.64157 | 22454.95 | 0.02394 | 335.16 | 40000 | 0 | 7979.2 | 14475.75 | 0 | 335.16 | 14810.91 | 0 | 0 | 0 | 0
2022021509 | 3 | 0.57855 | 46284 | 0 | 0 | 0.59291 | 20751.85 | 0.24632 | 3448.48 | 40000 | 0 | 6284 | 14467.85 | 0 | 3448.48 | 17916.33 | 0 | 0 | 0 | 0
2022021510 | 3 | 0.55247 | 44197.6 | 0 | 0 | 0.55274 | 19345.9 | 0.40253 | 5635.42 | 40000 | 0 | 4197.6 | 15148.3 | 0 | 5635.42 | 20783.72 | 0 | 0 | 0 | 0
2022021511 | 3 | 0.53183 | 42546.4 | 0 | 0 | 0.59362 | 20776.7 | 0.33227 | 4651.78 | 40000 | 0 | 2546.4 | 18230.3 | 0 | 4651.78 | 22882.08 | 0 | 0 | 0 | 0
2022021512 | 3 | 0.51759 | 41407.2 | 0 | 0 | 0.61712 | 21599.2 | 0.18967 | 2655.38 | 40000 | 0 | 1407.2 | 20192 | 0 | 2655.38 | 22847.38 | 0 | 0 | 0 | 0
2022021513 | 3 | 0.50546 | 40436.8 | 0 | 0 | 0.60555 | 21194.25 | 0.15736 | 2203.04 | 40000 | 0 | 436.8 | 20757.45 | 0 | 2203.04 | 22960.49 | 0 | 0 | 0 | 0
2022021514 | 3 | 0.50045 | 40036 | 0 | 0 | 0.60233 | 21081.55 | 0.15582 | 2181.48 | 40000 | 0 | 36 | 21045.55 | 0 | 2181.48 | 23227.03 | 0 | 0 | 0 | 0
2022021515 | 3 | 0.49756 | 39804.8 | 0 | 0 | 0.61635 | 21572.25 | 0.14637 | 2049.18 | 39804.8 | 195.2 | 0 | 21572.25 | 0 | 2049.18 | 23816.63 | 0 | 0 | 0 | 0
2022021516 | 3 | 0.49772 | 39817.6 | 0 | 0 | 0.62158 | 21755.3 | 0.14553 | 2037.42 | 39817.6 | 182.4 | 0 | 21755.3 | 0 | 2037.42 | 23975.12 | 0 | 0 | 0 | 0
2022021517 | 3 | 0.50035 | 40028 | 0 | 0 | 0.6236 | 21826 | 0.11928 | 1669.92 | 40000 | 0 | 28 | 21798 | 0 | 1669.92 | 23467.92 | 0 | 0 | 0 | 0
2022021518 | 3 | 0.50711 | 40568.8 | 0 | 0 | 0.64088 | 22430.8 | 0.03989 | 558.46 | 40000 | 0 | 568.8 | 21862 | 0 | 558.46 | 22420.46 | 0 | 0 | 0 | 0
2022021519 | 3 | 0.52513 | 42010.4 | 0 | 0 | 0.65786 | 23025.1 | 0.00202 | 28.28 | 40000 | 0 | 2010.4 | 21014.7 | 0 | 28.28 | 21042.98 | 0 | 0 | 0 | 0
2022021520 | 3 | 0.5326 | 42608 | 0 | 0 | 0.67768 | 23718.8 | 0.00014 | 1.96 | 40000 | 0 | 2608 | 21110.8 | 0 | 1.96 | 21112.76 | 0 | 0 | 0 | 0
2022021521 | 3 | 0.52502 | 42001.6 | 0 | 0 | 0.67983 | 23794.05 | 0.00014 | 1.96 | 40000 | 0 | 2001.6 | 21792.45 | 0 | 1.96 | 21794.41 | 0 | 0 | 0 | 0
2022021522 | 3 | 0.50875 | 40700 | 0 | 0 | 0.66937 | 23427.95 | 0.00014 | 1.96 | 40000 | 0 | 700 | 22727.95 | 0 | 1.96 | 22729.91 | 0 | 0 | 0 | 0
2022021523 | 3 | 0.48048 | 38438.4 | 0 | 0 | 0.64558 | 22595.3 | 0.00014 | 1.96 | 38438.4 | 1561.6 | 0 | 22595.3 | 0 | 1.96 | 24158.86 | 0 | 0 | 0 | 0
2022021524 | 3 | 0.45163 | 36130.4 | 0 | 0 | 0.60595 | 21208.25 | 0.00014 | 1.96 | 36130.4 | 3869.6 | 0 | 21208.25 | 0 | 1.96 | 25079.81 | 0 | 0 | 0 | 0
2022021601 | 4 | 0.43189 | 34551.2 | 0 | 0 | 0.57596 | 20158.6 | 0.00014 | 1.96 | 34551.2 | 5448.8 | 0 | 20158.6 | 0 | 1.96 | 25609.36 | 0 | 0 | 0 | 0
2022021602 | 4 | 0.4211 | 33688 | 0 | 0 | 0.57132 | 19996.2 | 0.00014 | 1.96 | 33688 | 6312 | 0 | 19996.2 | 0 | 1.96 | 26310.16 | 0 | 0 | 0 | 0
2022021603 | 4 | 0.41427 | 33141.6 | 0 | 0 | 0.56411 | 19743.85 | 0.00014 | 1.96 | 33141.6 | 6858.4 | 0 | 19743.85 | 0 | 1.96 | 26604.21 | 0 | 0 | 0 | 0
2022021604 | 4 | 0.41403 | 33122.4 | 0 | 0 | 0.56792 | 19877.2 | 0.00014 | 1.96 | 33122.4 | 6877.6 | 0 | 19877.2 | 0 | 1.96 | 26756.76 | 0 | 0 | 0 | 0
2022021605 | 4 | 0.42205 | 33764 | 0 | 0 | 0.57305 | 20056.75 | 0.00014 | 1.96 | 33764 | 6236 | 0 | 20056.75 | 0 | 1.96 | 26294.71 | 0 | 0 | 0 | 0
2022021606 | 4 | 0.44543 | 35634.4 | 0 | 0 | 0.59136 | 20697.6 | 0.00014 | 1.96 | 35634.4 | 4365.6 | 0 | 20697.6 | 0 | 1.96 | 25065.16 | 0 | 0 | 0 | 0
2022021607 | 4 | 0.48532 | 38825.6 | 0 | 0 | 0.62755 | 21964.25 | 0.00014 | 1.96 | 38825.6 | 1174.4 | 0 | 21964.25 | 0 | 1.96 | 23140.61 | 0 | 0 | 0 | 0
2022021608 | 4 | 0.50193 | 40154.4 | 0 | 0 | 0.6415 | 22452.5 | 0.00599 | 83.86 | 40000 | 0 | 154.4 | 22298.1 | 0 | 83.86 | 22381.96 | 0 | 0 | 0 | 0
2022021609 | 4 | 0.50503 | 40402.4 | 0 | 0 | 0.61872 | 21655.2 | 0.08693 | 1217.02 | 40000 | 0 | 402.4 | 21252.8 | 0 | 1217.02 | 22469.82 | 0 | 0 | 0 | 0
2022021610 | 4 | 0.50852 | 40681.6 | 0 | 0 | 0.59956 | 20984.6 | 0.21541 | 3015.74 | 40000 | 0 | 681.6 | 20303 | 0 | 3015.74 | 23318.74 | 0 | 0 | 0 | 0
2022021611 | 4 | 0.51398 | 41118.4 | 0 | 0 | 0.59658 | 20880.3 | 0.2499 | 3498.6 | 40000 | 0 | 1118.4 | 19761.9 | 0 | 3498.6 | 23260.5 | 0 | 0 | 0 | 0
2022021612 | 4 | 0.51788 | 41430.4 | 0 | 0 | 0.58608 | 20512.8 | 0.28465 | 3985.1 | 40000 | 0 | 1430.4 | 19082.4 | 0 | 3985.1 | 23067.5 | 0 | 0 | 0 | 0
2022021613 | 4 | 0.51708 | 41366.4 | 0 | 0 | 0.55676 | 19486.6 | 0.35766 | 5007.24 | 40000 | 0 | 1366.4 | 18120.2 | 0 | 5007.24 | 23127.44 | 0 | 0 | 0 | 0
2022021614 | 4 | 0.51714 | 41371.2 | 0 | 0 | 0.53288 | 18650.8 | 0.43079 | 6031.06 | 40000 | 0 | 1371.2 | 17279.6 | 0 | 6031.06 | 23310.66 | 0 | 0 | 0 | 0
2022021615 | 4 | 0.51817 | 41453.6 | 0 | 0 | 0.52927 | 18524.45 | 0.45218 | 6330.52 | 40000 | 0 | 1453.6 | 17070.85 | 0 | 6330.52 | 23401.37 | 0 | 0 | 0 | 0
2022021616 | 4 | 0.5188 | 41504 | 0 | 0 | 0.54588 | 19105.8 | 0.39203 | 5488.42 | 40000 | 0 | 1504 | 17601.8 | 0 | 5488.42 | 23090.22 | 0 | 0 | 0 | 0
2022021617 | 4 | 0.52348 | 41878.4 | 0 | 0 | 0.601 | 21035 | 0.23989 | 3358.46 | 40000 | 0 | 1878.4 | 19156.6 | 0 | 3358.46 | 22515.06 | 0 | 0 | 0 | 0
2022021618 | 4 | 0.53033 | 42426.4 | 0 | 0 | 0.64688 | 22640.8 | 0.10249 | 1434.86 | 40000 | 0 | 2426.4 | 20214.4 | 0 | 1434.86 | 21649.26 | 0 | 0 | 0 | 0
2022021619 | 4 | 0.54211 | 43368.8 | 0 | 0 | 0.67362 | 23576.7 | 0.00829 | 116.06 | 40000 | 0 | 3368.8 | 20207.9 | 0 | 116.06 | 20323.96 | 0 | 0 | 0 | 0
2022021620 | 4 | 0.54454 | 43563.2 | 0 | 0 | 0.69912 | 24469.2 | 0 | 0 | 40000 | 0 | 3563.2 | 20906 | 0 | 0 | 20906 | 0 | 0 | 0 | 0
2022021621 | 4 | 0.53435 | 42748 | 0 | 0 | 0.6938 | 24283 | 0 | 0 | 40000 | 0 | 2748 | 21535 | 0 | 0 | 21535 | 0 | 0 | 0 | 0
2022021622 | 4 | 0.51563 | 41250.4 | 0 | 0 | 0.68511 | 23978.85 | 0 | 0 | 40000 | 0 | 1250.4 | 22728.45 | 0 | 0 | 22728.45 | 0 | 0 | 0 | 0
2022021623 | 4 | 0.48605 | 38884 | 0 | 0 | 0.6477 | 22669.5 | 0 | 0 | 38884 | 1116 | 0 | 22669.5 | 0 | 0 | 23785.5 | 0 | 0 | 0 | 0
2022021624 | 4 | 0.45721 | 36576.8 | 0 | 0 | 0.60683 | 21239.05 | 0 | 0 | 36576.8 | 3423.2 | 0 | 21239.05 | 0 | 0 | 24662.25 | 0 | 0 | 0 | 0
2022021701 | 5 | 0.43527 | 34821.6 | 0 | 0 | 0.5717 | 20009.5 | 0 | 0 | 34821.6 | 5178.4 | 0 | 20009.5 | 0 | 0 | 25187.9 | 0 | 0 | 0 | 0
2022021702 | 5 | 0.42142 | 33713.6 | 0 | 0 | 0.54092 | 18932.2 | 0 | 0 | 33713.6 | 6286.4 | 0 | 18932.2 | 0 | 0 | 25218.6 | 0 | 0 | 0 | 0
2022021703 | 5 | 0.41457 | 33165.6 | 0 | 0 | 0.52597 | 18408.95 | 0 | 0 | 33165.6 | 6834.4 | 0 | 18408.95 | 0 | 0 | 25243.35 | 0 | 0 | 0 | 0
2022021704 | 5 | 0.41173 | 32938.4 | 0 | 0 | 0.53891 | 18861.85 | 0 | 0 | 32938.4 | 7061.6 | 0 | 18861.85 | 0 | 0 | 25923.45 | 0 | 0 | 0 | 0
2022021705 | 5 | 0.41832 | 33465.6 | 0 | 0 | 0.55849 | 19547.15 | 0 | 0 | 33465.6 | 6534.4 | 0 | 19547.15 | 0 | 0 | 26081.55 | 0 | 0 | 0 | 0
2022021706 | 5 | 0.44132 | 35305.6 | 0 | 0 | 0.58673 | 20535.55 | 0 | 0 | 35305.6 | 4694.4 | 0 | 20535.55 | 0 | 0 | 25229.95 | 0 | 0 | 0 | 0
2022021707 | 5 | 0.48089 | 38471.2 | 0 | 0 | 0.63636 | 22272.6 | 0 | 0 | 38471.2 | 1528.8 | 0 | 22272.6 | 0 | 0 | 23801.4 | 0 | 0 | 0 | 0
2022021708 | 5 | 0.5032 | 40256 | 0 | 0 | 0.63784 | 22324.4 | 0.00694 | 97.16 | 40000 | 0 | 256 | 22068.4 | 0 | 97.16 | 22165.56 | 0 | 0 | 0 | 0
2022021709 | 5 | 0.51162 | 40929.6 | 0 | 0 | 0.61667 | 21583.45 | 0.1144 | 1601.6 | 40000 | 0 | 929.6 | 20653.85 | 0 | 1601.6 | 22255.45 | 0 | 0 | 0 | 0
2022021710 | 5 | 0.52662 | 42129.6 | 0 | 0 | 0.61358 | 21475.3 | 0.15832 | 2216.48 | 40000 | 0 | 2129.6 | 19345.7 | 0 | 2216.48 | 21562.18 | 0 | 0 | 0 | 0
2022021711 | 5 | 0.5411 | 43288 | 0 | 0 | 0.63565 | 22247.75 | 0.17152 | 2401.28 | 40000 | 0 | 3288 | 18959.75 | 0 | 2401.28 | 21361.03 | 0 | 0 | 0 | 0
2022021712 | 5 | 0.55511 | 44408.8 | 0 | 0 | 0.65005 | 22751.75 | 0.18614 | 2605.96 | 40000 | 0 | 4408.8 | 18342.95 | 0 | 2605.96 | 20948.91 | 0 | 0 | 0 | 0
2022021713 | 5 | 0.56509 | 45207.2 | 0 | 0 | 0.64846 | 22696.1 | 0.20133 | 2818.62 | 40000 | 0 | 5207.2 | 17488.9 | 0 | 2818.62 | 20307.52 | 0 | 0 | 0 | 0
2022021714 | 5 | 0.57144 | 45715.2 | 0 | 0 | 0.63419 | 22196.65 | 0.27918 | 3908.52 | 40000 | 0 | 5715.2 | 16481.45 | 0 | 3908.52 | 20389.97 | 0 | 0 | 0 | 0
2022021715 | 5 | 0.57634 | 46107.2 | 0 | 0 | 0.61776 | 21621.6 | 0.33392 | 4674.88 | 40000 | 0 | 6107.2 | 15514.4 | 0 | 4674.88 | 20189.28 | 0 | 0 | 0 | 0
2022021716 | 5 | 0.58057 | 46445.6 | 0 | 0 | 0.59348 | 20771.8 | 0.39446 | 5522.44 | 40000 | 0 | 6445.6 | 14326.2 | 0 | 5522.44 | 19848.64 | 0 | 0 | 0 | 0
2022021717 | 5 | 0.58937 | 47149.6 | 0 | 0 | 0.54902 | 19215.7 | 0.51024 | 7143.36 | 40000 | 0 | 7149.6 | 12066.1 | 0 | 7143.36 | 19209.46 | 0 | 0 | 0 | 0
2022021718 | 5 | 0.5954 | 47632 | 0 | 0 | 0.48164 | 16857.4 | 0.34574 | 4840.36 | 40000 | 0 | 7632 | 9225.4 | 0 | 4840.36 | 14065.76 | 0 | 0 | 0 | 0
2022021719 | 5 | 0.61435 | 49148 | 0 | 0 | 0.38511 | 13478.85 | 0.02498 | 349.72 | 40000 | 0 | 9148 | 4330.85 | 0 | 349.72 | 4680.57 | 0 | 0 | 0 | 0
2022021720 | 5 | 0.62553 | 50042.4 | 0 | 0 | 0.33409 | 11693.15 | 0 | 0 | 40000 | 0 | 10042.4 | 1650.75 | 0 | 0 | 1650.75 | 0 | 0 | 0 | 0
2022021721 | 5 | 0.62689 | 50151.2 | 0 | 0 | 0.32628 | 11419.8 | 0 | 0 | 40000 | 0 | 10151.2 | 1268.6 | 0 | 0 | 1268.6 | 0 | 0 | 0 | 0
2022021722 | 5 | 0.61959 | 49567.2 | 0 | 0 | 0.32236 | 11282.6 | 0 | 0 | 40000 | 0 | 9567.2 | 1715.4 | 0 | 0 | 1715.4 | 0 | 0 | 0 | 0
2022021723 | 5 | 0.59913 | 47930.4 | 0 | 0 | 0.30783 | 10774.05 | 0 | 0 | 40000 | 0 | 7930.4 | 2843.65 | 0 | 0 | 2843.65 | 0 | 0 | 0 | 0
2022021724 | 5 | 0.58191 | 46552.8 | 0 | 0 | 0.29689 | 10391.15 | 0 | 0 | 40000 | 0 | 6552.8 | 3838.35 | 0 | 0 | 3838.35 | 0 | 0 | 0 | 0
2022021801 | 6 | 0.57386 | 45908.8 | 0 | 0 | 0.28836 | 10092.6 | 0 | 0 | 40000 | 0 | 5908.8 | 4183.8 | 0 | 0 | 4183.8 | 0 | 0 | 0 | 0
2022021802 | 6 | 0.57207 | 45765.6 | 0 | 0 | 0.2514 | 8799 | 0 | 0 | 40000 | 0 | 5765.6 | 3033.4 | 0 | 0 | 3033.4 | 0 | 0 | 0 | 0
2022021803 | 6 | 0.57803 | 46242.4 | 0 | 0 | 0.23144 | 8100.4 | 0 | 0 | 40000 | 0 | 6242.4 | 1858 | 0 | 0 | 1858 | 0 | 0 | 0 | 0
2022021804 | 6 | 0.59005 | 47204 | 0 | 0 | 0.21507 | 7527.45 | 0 | 0 | 40000 | 0 | 7204 | 323.45 | 0 | 0 | 323.45 | 0 | 0 | 0 | 0
2022021805 | 6 | 0.60829 | 48663.2 | 0 | 0 | 0.20505 | 7176.75 | 0 | 0 | 40000 | 0 | 7176.75 | 0 | 0 | 0 | 0 | 1486.45 | 0 | 0 | 1486.45
2022021806 | 6 | 0.64318 | 51454.4 | 0 | 0 | 0.1995 | 6982.5 | 0 | 0 | 40000 | 0 | 6982.5 | 0 | 0 | 0 | 0 | 4471.9 | 0 | 0 | 4471.9
2022021807 | 6 | 0.69702 | 55761.6 | 0 | 0 | 0.21176 | 7411.6 | 5e-05 | 0.7 | 40000 | 0 | 7411.6 | 0 | 0.7 | 0 | 0 | 8349.3 | 0 | 0 | 8349.3
2022021808 | 6 | 0.72354 | 57883.2 | 0 | 0 | 0.22961 | 8036.35 | 0.03514 | 491.96 | 40000 | 0 | 8036.35 | 0 | 491.96 | 0 | 0 | 9354.89 | 0 | 0 | 9354.89
2022021809 | 6 | 0.71216 | 56972.8 | 0 | 0 | 0.23277 | 8146.95 | 0.45107 | 6314.98 | 40000 | 0 | 8146.95 | 0 | 6314.98 | 0 | 0 | 2510.87 | 0 | 0 | 2510.87
2022021810 | 6 | 0.68334 | 54667.2 | 0 | 0 | 0.17709 | 6198.15 | 0.7934 | 11107.6 | 40000 | 0 | 6198.15 | 0 | 8469.05 | 2638.55 | 2638.55 | 0 | 0 | 0 | 0
2022021811 | 6 | 0.65102 | 52081.6 | 0 | 0 | 0.1321 | 4623.5 | 0.84648 | 11850.72 | 40000 | 0 | 4623.5 | 0 | 7458.1 | 4392.62 | 4392.62 | 0 | 0 | 0 | 0
2022021812 | 6 | 0.6157 | 49256 | 0 | 0 | 0.09668 | 3383.8 | 0.84356 | 11809.84 | 40000 | 0 | 3383.8 | 0 | 5872.2 | 5937.64 | 5937.64 | 0 | 0 | 0 | 0
2022021813 | 6 | 0.58087 | 46469.6 | 0 | 0 | 0.07456 | 2609.6 | 0.82882 | 11603.48 | 40000 | 0 | 2609.6 | 0 | 3860 | 7743.48 | 7743.48 | 0 | 0 | 0 | 0
2022021814 | 6 | 0.55471 | 44376.8 | 0 | 0 | 0.0637 | 2229.5 | 0.82802 | 11592.28 | 40000 | 0 | 2229.5 | 0 | 2147.3 | 9444.98 | 9444.98 | 0 | 0 | 0 | 0
2022021815 | 6 | 0.53322 | 42657.6 | 0 | 0 | 0.0549 | 1921.5 | 0.84515 | 11832.1 | 40000 | 0 | 1921.5 | 0 | 736.1 | 11096 | 11096 | 0 | 0 | 0 | 0
2022021816 | 6 | 0.51894 | 41515.2 | 0 | 0 | 0.05139 | 1798.65 | 0.85522 | 11973.08 | 40000 | 0 | 1515.2 | 283.45 | 0 | 11973.08 | 12256.53 | 0 | 0 | 0 | 0
2022021817 | 6 | 0.51518 | 41214.4 | 0 | 0 | 0.04969 | 1739.15 | 0.81238 | 11373.32 | 40000 | 0 | 1214.4 | 524.75 | 0 | 11373.32 | 11898.07 | 0 | 0 | 0 | 0
2022021818 | 6 | 0.52294 | 41835.2 | 0 | 0 | 0.0459 | 1606.5 | 0.44444 | 6222.16 | 40000 | 0 | 1606.5 | 0 | 228.7 | 5993.46 | 5993.46 | 0 | 0 | 0 | 0
2022021819 | 6 | 0.55217 | 44173.6 | 0 | 0 | 0.05726 | 2004.1 | 0.03331 | 466.34 | 40000 | 0 | 2004.1 | 0 | 466.34 | 0 | 0 | 1703.16 | 0 | 0 | 1703.16
2022021820 | 6 | 0.56883 | 45506.4 | 0 | 0 | 0.09554 | 3343.9 | 6e-05 | 0.84 | 40000 | 0 | 3343.9 | 0 | 0.84 | 0 | 0 | 2161.66 | 0 | 0 | 2161.66
2022021821 | 6 | 0.57378 | 45902.4 | 0 | 0 | 0.15576 | 5451.6 | 6e-05 | 0.84 | 40000 | 0 | 5451.6 | 0 | 0.84 | 0 | 0 | 449.96 | 0 | 0 | 449.96
2022021822 | 6 | 0.57348 | 45878.4 | 0 | 0 | 0.21665 | 7582.75 | 6e-05 | 0.84 | 40000 | 0 | 5878.4 | 1704.35 | 0 | 0.84 | 1705.19 | 0 | 0 | 0 | 0
2022021823 | 6 | 0.56666 | 45332.8 | 0 | 0 | 0.24863 | 8702.05 | 6e-05 | 0.84 | 40000 | 0 | 5332.8 | 3369.25 | 0 | 0.84 | 3370.09 | 0 | 0 | 0 | 0
2022021824 | 6 | 0.55612 | 44489.6 | 0 | 0 | 0.25499 | 8924.65 | 6e-05 | 0.84 | 40000 | 0 | 4489.6 | 4435.05 | 0 | 0.84 | 4435.89 | 0 | 0 | 0 | 0
2022021901 | 7 | 0.54906 | 43924.8 | 0 | 0 | 0.25601 | 8960.35 | 6e-05 | 0.84 | 40000 | 0 | 3924.8 | 5035.55 | 0 | 0.84 | 5036.39 | 0 | 0 | 0 | 0
2022021902 | 7 | 0.54758 | 43806.4 | 0 | 0 | 0.26808 | 9382.8 | 6e-05 | 0.84 | 40000 | 0 | 3806.4 | 5576.4 | 0 | 0.84 | 5577.24 | 0 | 0 | 0 | 0
2022021903 | 7 | 0.55035 | 44028 | 0 | 0 | 0.26792 | 9377.2 | 6e-05 | 0.84 | 40000 | 0 | 4028 | 5349.2 | 0 | 0.84 | 5350.04 | 0 | 0 | 0 | 0
2022021904 | 7 | 0.55628 | 44502.4 | 0 | 0 | 0.26566 | 9298.1 | 6e-05 | 0.84 | 40000 | 0 | 4502.4 | 4795.7 | 0 | 0.84 | 4796.54 | 0 | 0 | 0 | 0
2022021905 | 7 | 0.56761 | 45408.8 | 0 | 0 | 0.24953 | 8733.55 | 6e-05 | 0.84 | 40000 | 0 | 5408.8 | 3324.75 | 0 | 0.84 | 3325.59 | 0 | 0 | 0 | 0
2022021906 | 7 | 0.58792 | 47033.6 | 0 | 0 | 0.22905 | 8016.75 | 6e-05 | 0.84 | 40000 | 0 | 7033.6 | 983.15 | 0 | 0.84 | 983.99 | 0 | 0 | 0 | 0
2022021907 | 7 | 0.61522 | 49217.6 | 0 | 0 | 0.20515 | 7180.25 | 6e-05 | 0.84 | 40000 | 0 | 7180.25 | 0 | 0.84 | 0 | 0 | 2036.51 | 0 | 0 | 2036.51
2022021908 | 7 | 0.63445 | 50756 | 0 | 0 | 0.20156 | 7054.6 | 0.04317 | 604.38 | 40000 | 0 | 7054.6 | 0 | 604.38 | 0 | 0 | 3097.02 | 0 | 0 | 3097.02
2022021909 | 7 | 0.62246 | 49796.8 | 0 | 0 | 0.15821 | 5537.35 | 0.47243 | 6614.02 | 40000 | 0 | 5537.35 | 0 | 4259.45 | 2354.57 | 2354.57 | 0 | 0 | 0 | 0
2022021910 | 7 | 0.59185 | 47348 | 0 | 0 | 0.10556 | 3694.6 | 0.78538 | 10995.32 | 40000 | 0 | 3694.6 | 0 | 3653.4 | 7341.92 | 7341.92 | 0 | 0 | 0 | 0
2022021911 | 7 | 0.561 | 44880 | 0 | 0 | 0.11252 | 3938.2 | 0.81797 | 11451.58 | 40000 | 0 | 3938.2 | 0 | 941.8 | 10509.78 | 10509.78 | 0 | 0 | 0 | 0
2022021912 | 7 | 0.5299 | 42392 | 0 | 0 | 0.136 | 4760 | 0.81706 | 11438.84 | 40000 | 0 | 2392 | 2368 | 0 | 11438.84 | 13806.84 | 0 | 0 | 0 | 0
2022021913 | 7 | 0.50466 | 40372.8 | 0 | 0 | 0.17892 | 6262.2 | 0.81578 | 11420.92 | 40000 | 0 | 372.8 | 5889.4 | 0 | 11420.92 | 17310.32 | 0 | 0 | 0 | 0
2022021914 | 7 | 0.48672 | 38937.6 | 0 | 0 | 0.21211 | 7423.85 | 0.82314 | 11523.96 | 38937.6 | 1062.4 | 0 | 7423.85 | 0 | 11523.96 | 20010.21 | 0 | 0 | 0 | 0
2022021915 | 7 | 0.47496 | 37996.8 | 0 | 0 | 0.2421 | 8473.5 | 0.82137 | 11499.18 | 37996.8 | 2003.2 | 0 | 8473.5 | 0 | 11499.18 | 21975.88 | 0 | 0 | 0 | 0
2022021916 | 7 | 0.47108 | 37686.4 | 0 | 0 | 0.26676 | 9336.6 | 0.83532 | 11694.48 | 37686.4 | 2313.6 | 0 | 9336.6 | 0 | 11694.48 | 23344.68 | 0 | 0 | 0 | 0
2022021917 | 7 | 0.47344 | 37875.2 | 0 | 0 | 0.30014 | 10504.9 | 0.78957 | 11053.98 | 37875.2 | 2124.8 | 0 | 10504.9 | 0 | 11053.98 | 23683.68 | 0 | 0 | 0 | 0
2022021918 | 7 | 0.47883 | 38306.4 | 0 | 0 | 0.32633 | 11421.55 | 0.44114 | 6175.96 | 38306.4 | 1693.6 | 0 | 11421.55 | 0 | 6175.96 | 19291.11 | 0 | 0 | 0 | 0
2022021919 | 7 | 0.49769 | 39815.2 | 0 | 0 | 0.34318 | 12011.3 | 0.03475 | 486.5 | 39815.2 | 184.8 | 0 | 12011.3 | 0 | 486.5 | 12682.6 | 0 | 0 | 0 | 0
2022021920 | 7 | 0.51079 | 40863.2 | 0 | 0 | 0.45459 | 15910.65 | 8e-05 | 1.12 | 40000 | 0 | 863.2 | 15047.45 | 0 | 1.12 | 15048.57 | 0 | 0 | 0 | 0
2022021921 | 7 | 0.51471 | 41176.8 | 0 | 0 | 0.57019 | 19956.65 | 8e-05 | 1.12 | 40000 | 0 | 1176.8 | 18779.85 | 0 | 1.12 | 18780.97 | 0 | 0 | 0 | 0
2022021922 | 7 | 0.51447 | 41157.6 | 0 | 0 | 0.6083 | 21290.5 | 8e-05 | 1.12 | 40000 | 0 | 1157.6 | 20132.9 | 0 | 1.12 | 20134.02 | 0 | 0 | 0 | 0
2022021923 | 7 | 0.50914 | 40731.2 | 0 | 0 | 0.6105 | 21367.5 | 8e-05 | 1.12 | 40000 | 0 | 731.2 | 20636.3 | 0 | 1.12 | 20637.42 | 0 | 0 | 0 | 0
2022021924 | 7 | 0.49952 | 39961.6 | 0 | 0 | 0.60516 | 21180.6 | 8e-05 | 1.12 | 39961.6 | 38.4 | 0 | 21180.6 | 0 | 1.12 | 21220.12 | 0 | 0 | 0 | 0
2022022001 | 1 | 0.4923 | 39384 | 0 | 0 | 0.59837 | 20942.95 | 8e-05 | 1.12 | 39384 | 616 | 0 | 20942.95 | 0 | 1.12 | 21560.07 | 0 | 0 | 0 | 0
2022022002 | 1 | 0.48845 | 39076 | 0 | 0 | 0.60089 | 21031.15 | 8e-05 | 1.12 | 39076 | 924 | 0 | 21031.15 | 0 | 1.12 | 21956.27 | 0 | 0 | 0 | 0
2022022003 | 1 | 0.48735 | 38988 | 0 | 0 | 0.60499 | 21174.65 | 8e-05 | 1.12 | 38988 | 1012 | 0 | 21174.65 | 0 | 1.12 | 22187.77 | 0 | 0 | 0 | 0
2022022004 | 1 | 0.4892 | 39136 | 0 | 0 | 0.60565 | 21197.75 | 8e-05 | 1.12 | 39136 | 864 | 0 | 21197.75 | 0 | 1.12 | 22062.87 | 0 | 0 | 0 | 0
2022022005 | 1 | 0.49433 | 39546.4 | 0 | 0 | 0.59968 | 20988.8 | 8e-05 | 1.12 | 39546.4 | 453.6 | 0 | 20988.8 | 0 | 1.12 | 21443.52 | 0 | 0 | 0 | 0
2022022006 | 1 | 0.50662 | 40529.6 | 0 | 0 | 0.59788 | 20925.8 | 8e-05 | 1.12 | 40000 | 0 | 529.6 | 20396.2 | 0 | 1.12 | 20397.32 | 0 | 0 | 0 | 0
2022022007 | 1 | 0.52277 | 41821.6 | 0 | 0 | 0.59439 | 20803.65 | 9e-05 | 1.26 | 40000 | 0 | 1821.6 | 18982.05 | 0 | 1.26 | 18983.31 | 0 | 0 | 0 | 0
2022022008 | 1 | 0.53772 | 43017.6 | 0 | 0 | 0.59554 | 20843.9 | 0.02156 | 301.84 | 40000 | 0 | 3017.6 | 17826.3 | 0 | 301.84 | 18128.14 | 0 | 0 | 0 | 0
2022022009 | 1 | 0.5422 | 43376 | 0 | 0 | 0.55863 | 19552.05 | 0.18357 | 2569.98 | 40000 | 0 | 3376 | 16176.05 | 0 | 2569.98 | 18746.03 | 0 | 0 | 0 | 0
2022022010 | 1 | 0.53563 | 42850.4 | 0 | 0 | 0.5204 | 18214 | 0.29784 | 4169.76 | 40000 | 0 | 2850.4 | 15363.6 | 0 | 4169.76 | 19533.36 | 0 | 0 | 0 | 0
2022022011 | 1 | 0.51262 | 41009.6 | 0 | 0 | 0.50739 | 17758.65 | 0.36329 | 5086.06 | 40000 | 0 | 1009.6 | 16749.05 | 0 | 5086.06 | 21835.11 | 0 | 0 | 0 | 0
2022022012 | 1 | 0.49258 | 39406.4 | 0 | 0 | 0.48696 | 17043.6 | 0.45596 | 6383.44 | 39406.4 | 593.6 | 0 | 17043.6 | 0 | 6383.44 | 24020.64 | 0 | 0 | 0 | 0
2022022013 | 1 | 0.47902 | 38321.6 | 0 | 0 | 0.46927 | 16424.45 | 0.51763 | 7246.82 | 38321.6 | 1678.4 | 0 | 16424.45 | 0 | 7246.82 | 25349.67 | 0 | 0 | 0 | 0
2022022014 | 1 | 0.46943 | 37554.4 | 0 | 0 | 0.45746 | 16011.1 | 0.57565 | 8059.1 | 37554.4 | 2445.6 | 0 | 16011.1 | 0 | 8059.1 | 26515.8 | 0 | 0 | 0 | 0
2022022015 | 1 | 0.46855 | 37484 | 0 | 0 | 0.46909 | 16418.15 | 0.56413 | 7897.82 | 37484 | 2516 | 0 | 16418.15 | 0 | 7897.82 | 26831.97 | 0 | 0 | 0 | 0
2022022016 | 1 | 0.46861 | 37488.8 | 0 | 0 | 0.48793 | 17077.55 | 0.51764 | 7246.96 | 37488.8 | 2511.2 | 0 | 17077.55 | 0 | 7246.96 | 26835.71 | 0 | 0 | 0 | 0
2022022017 | 1 | 0.4736 | 37888 | 0 | 0 | 0.49543 | 17340.05 | 0.45855 | 6419.7 | 37888 | 2112 | 0 | 17340.05 | 0 | 6419.7 | 25871.75 | 0 | 0 | 0 | 0
2022022018 | 1 | 0.48322 | 38657.6 | 0 | 0 | 0.51402 | 17990.7 | 0.30101 | 4214.14 | 38657.6 | 1342.4 | 0 | 17990.7 | 0 | 4214.14 | 23547.24 | 0 | 0 | 0 | 0
2022022019 | 1 | 0.49989 | 39991.2 | 0 | 0 | 0.53985 | 18894.75 | 0.03363 | 470.82 | 39991.2 | 8.8 | 0 | 18894.75 | 0 | 470.82 | 19374.37 | 0 | 0 | 0 | 0
2022022020 | 1 | 0.50924 | 40739.2 | 0 | 0 | 0.59323 | 20763.05 | 7e-05 | 0.98 | 40000 | 0 | 739.2 | 20023.85 | 0 | 0.98 | 20024.83 | 0 | 0 | 0 | 0
2022022021 | 1 | 0.50397 | 40317.6 | 0 | 0 | 0.60822 | 21287.7 | 7e-05 | 0.98 | 40000 | 0 | 317.6 | 20970.1 | 0 | 0.98 | 20971.08 | 0 | 0 | 0 | 0
2022022022 | 1 | 0.49203 | 39362.4 | 0 | 0 | 0.61137 | 21397.95 | 7e-05 | 0.98 | 39362.4 | 637.6 | 0 | 21397.95 | 0 | 0.98 | 22036.53 | 0 | 0 | 0 | 0
2022022023 | 1 | 0.47242 | 37793.6 | 0 | 0 | 0.63105 | 22086.75 | 7e-05 | 0.98 | 37793.6 | 2206.4 | 0 | 22086.75 | 0 | 0.98 | 24294.13 | 0 | 0 | 0 | 0
2022022024 | 1 | 0.44996 | 35996.8 | 0 | 0 | 0.62772 | 21970.2 | 7e-05 | 0.98 | 35996.8 | 4003.2 | 0 | 21970.2 | 0 | 0.98 | 25974.38 | 0 | 0 | 0 | 0
2022022101 | 2 | 0.43223 | 34578.4 | 0 | 0 | 0.60889 | 21311.15 | 7e-05 | 0.98 | 34578.4 | 5421.6 | 0 | 21311.15 | 0 | 0.98 | 26733.73 | 0 | 0 | 0 | 0
2022022102 | 2 | 0.42209 | 33767.2 | 0 | 0 | 0.59881 | 20958.35 | 7e-05 | 0.98 | 33767.2 | 6232.8 | 0 | 20958.35 | 0 | 0.98 | 27192.13 | 0 | 0 | 0 | 0
2022022103 | 2 | 0.41686 | 33348.8 | 0 | 0 | 0.59012 | 20654.2 | 7e-05 | 0.98 | 33348.8 | 6651.2 | 0 | 20654.2 | 0 | 0.98 | 27306.38 | 0 | 0 | 0 | 0
2022022104 | 2 | 0.4162 | 33296 | 0 | 0 | 0.58739 | 20558.65 | 7e-05 | 0.98 | 33296 | 6704 | 0 | 20558.65 | 0 | 0.98 | 27263.63 | 0 | 0 | 0 | 0
2022022105 | 2 | 0.42448 | 33958.4 | 0 | 0 | 0.59463 | 20812.05 | 7e-05 | 0.98 | 33958.4 | 6041.6 | 0 | 20812.05 | 0 | 0.98 | 26854.63 | 0 | 0 | 0 | 0
2022022106 | 2 | 0.4442 | 35536 | 0 | 0 | 0.62615 | 21915.25 | 7e-05 | 0.98 | 35536 | 4464 | 0 | 21915.25 | 0 | 0.98 | 26380.23 | 0 | 0 | 0 | 0
2022022107 | 2 | 0.47576 | 38060.8 | 0 | 0 | 0.65867 | 23053.45 | 7e-05 | 0.98 | 38060.8 | 1939.2 | 0 | 23053.45 | 0 | 0.98 | 24993.63 | 0 | 0 | 0 | 0
2022022108 | 2 | 0.49362 | 39489.6 | 0 | 0 | 0.67018 | 23456.3 | 0.0183 | 256.2 | 39489.6 | 510.4 | 0 | 23456.3 | 0 | 256.2 | 24222.9 | 0 | 0 | 0 | 0
2022022109 | 2 | 0.50386 | 40308.8 | 0 | 0 | 0.61559 | 21545.65 | 0.20708 | 2899.12 | 40000 | 0 | 308.8 | 21236.85 | 0 | 2899.12 | 24135.97 | 0 | 0 | 0 | 0
2022022110 | 2 | 0.51275 | 41020 | 0 | 0 | 0.55856 | 19549.6 | 0.38689 | 5416.46 | 40000 | 0 | 1020 | 18529.6 | 0 | 5416.46 | 23946.06 | 0 | 0 | 0 | 0
2022022111 | 2 | 0.51941 | 41552.8 | 0 | 0 | 0.56131 | 19645.85 | 0.37449 | 5242.86 | 40000 | 0 | 1552.8 | 18093.05 | 0 | 5242.86 | 23335.91 | 0 | 0 | 0 | 0
2022022112 | 2 | 0.52473 | 41978.4 | 0 | 0 | 0.5531 | 19358.5 | 0.40328 | 5645.92 | 40000 | 0 | 1978.4 | 17380.1 | 0 | 5645.92 | 23026.02 | 0 | 0 | 0 | 0
2022022113 | 2 | 0.52993 | 42394.4 | 0 | 0 | 0.57599 | 20159.65 | 0.35247 | 4934.58 | 40000 | 0 | 2394.4 | 17765.25 | 0 | 4934.58 | 22699.83 | 0 | 0 | 0 | 0
2022022114 | 2 | 0.53982 | 43185.6 | 0 | 0 | 0.59842 | 20944.7 | 0.34399 | 4815.86 | 40000 | 0 | 3185.6 | 17759.1 | 0 | 4815.86 | 22574.96 | 0 | 0 | 0 | 0
2022022115 | 2 | 0.54787 | 43829.6 | 0 | 0 | 0.59248 | 20736.8 | 0.30245 | 4234.3 | 40000 | 0 | 3829.6 | 16907.2 | 0 | 4234.3 | 21141.5 | 0 | 0 | 0 | 0
2022022116 | 2 | 0.55541 | 44432.8 | 0 | 0 | 0.56792 | 19877.2 | 0.27548 | 3856.72 | 40000 | 0 | 4432.8 | 15444.4 | 0 | 3856.72 | 19301.12 | 0 | 0 | 0 | 0
2022022117 | 2 | 0.56129 | 44903.2 | 0 | 0 | 0.5602 | 19607 | 0.21774 | 3048.36 | 40000 | 0 | 4903.2 | 14703.8 | 0 | 3048.36 | 17752.16 | 0 | 0 | 0 | 0
2022022118 | 2 | 0.56378 | 45102.4 | 0 | 0 | 0.59419 | 20796.65 | 0.11972 | 1676.08 | 40000 | 0 | 5102.4 | 15694.25 | 0 | 1676.08 | 17370.33 | 0 | 0 | 0 | 0
2022022119 | 2 | 0.5719 | 45752 | 0 | 0 | 0.59942 | 20979.7 | 0.00862 | 120.68 | 40000 | 0 | 5752 | 15227.7 | 0 | 120.68 | 15348.38 | 0 | 0 | 0 | 0
2022022120 | 2 | 0.57299 | 45839.2 | 0 | 0 | 0.61213 | 21424.55 | 0 | 0 | 40000 | 0 | 5839.2 | 15585.35 | 0 | 0 | 15585.35 | 0 | 0 | 0 | 0
2022022121 | 2 | 0.56141 | 44912.8 | 0 | 0 | 0.64595 | 22608.25 | 0 | 0 | 40000 | 0 | 4912.8 | 17695.45 | 0 | 0 | 17695.45 | 0 | 0 | 0 | 0
2022022122 | 2 | 0.54172 | 43337.6 | 0 | 0 | 0.64859 | 22700.65 | 5e-05 | 0.7 | 40000 | 0 | 3337.6 | 19363.05 | 0 | 0.7 | 19363.75 | 0 | 0 | 0 | 0
2022022123 | 2 | 0.51293 | 41034.4 | 0 | 0 | 0.6563 | 22970.5 | 5e-05 | 0.7 | 40000 | 0 | 1034.4 | 21936.1 | 0 | 0.7 | 21936.8 | 0 | 0 | 0 | 0
2022022124 | 2 | 0.4812 | 38496 | 0 | 0 | 0.63911 | 22368.85 | 5e-05 | 0.7 | 38496 | 1504 | 0 | 22368.85 | 0 | 0.7 | 23873.55 | 0 | 0 | 0 | 0
2022022201 | 3 | 0.45323 | 36258.4 | 0 | 0 | 0.6029 | 21101.5 | 0 | 0 | 36258.4 | 3741.6 | 0 | 21101.5 | 0 | 0 | 24843.1 | 0 | 0 | 0 | 0
2022022202 | 3 | 0.43523 | 34818.4 | 0 | 0 | 0.57692 | 20192.2 | 0 | 0 | 34818.4 | 5181.6 | 0 | 20192.2 | 0 | 0 | 25373.8 | 0 | 0 | 0 | 0
2022022203 | 3 | 0.42417 | 33933.6 | 0 | 0 | 0.55714 | 19499.9 | 5e-05 | 0.7 | 33933.6 | 6066.4 | 0 | 19499.9 | 0 | 0.7 | 25567 | 0 | 0 | 0 | 0
2022022204 | 3 | 0.41893 | 33514.4 | 0 | 0 | 0.55034 | 19261.9 | 0 | 0 | 33514.4 | 6485.6 | 0 | 19261.9 | 0 | 0 | 25747.5 | 0 | 0 | 0 | 0
2022022205 | 3 | 0.42363 | 33890.4 | 0 | 0 | 0.54879 | 19207.65 | 0 | 0 | 33890.4 | 6109.6 | 0 | 19207.65 | 0 | 0 | 25317.25 | 0 | 0 | 0 | 0
2022022206 | 3 | 0.44323 | 35458.4 | 0 | 0 | 0.5619 | 19666.5 | 0 | 0 | 35458.4 | 4541.6 | 0 | 19666.5 | 0 | 0 | 24208.1 | 0 | 0 | 0 | 0
2022022207 | 3 | 0.48065 | 38452 | 0 | 0 | 0.54981 | 19243.35 | 6e-05 | 0.84 | 38452 | 1548 | 0 | 19243.35 | 0 | 0.84 | 20792.19 | 0 | 0 | 0 | 0
2022022208 | 3 | 0.49699 | 39759.2 | 0 | 0 | 0.53353 | 18673.55 | 0.01924 | 269.36 | 39759.2 | 240.8 | 0 | 18673.55 | 0 | 269.36 | 19183.71 | 0 | 0 | 0 | 0
2022022209 | 3 | 0.505 | 40400 | 0 | 0 | 0.49525 | 17333.75 | 0.26046 | 3646.44 | 40000 | 0 | 400 | 16933.75 | 0 | 3646.44 | 20580.19 | 0 | 0 | 0 | 0
2022022210 | 3 | 0.5158 | 41264 | 0 | 0 | 0.43963 | 15387.05 | 0.51843 | 7258.02 | 40000 | 0 | 1264 | 14123.05 | 0 | 7258.02 | 21381.07 | 0 | 0 | 0 | 0
2022022211 | 3 | 0.53022 | 42417.6 | 0 | 0 | 0.38761 | 13566.35 | 0.63012 | 8821.68 | 40000 | 0 | 2417.6 | 11148.75 | 0 | 8821.68 | 19970.43 | 0 | 0 | 0 | 0
2022022212 | 3 | 0.54291 | 43432.8 | 0 | 0 | 0.34016 | 11905.6 | 0.68808 | 9633.12 | 40000 | 0 | 3432.8 | 8472.8 | 0 | 9633.12 | 18105.92 | 0 | 0 | 0 | 0
2022022213 | 3 | 0.55095 | 44076 | 0 | 0 | 0.32241 | 11284.35 | 0.72613 | 10165.82 | 40000 | 0 | 4076 | 7208.35 | 0 | 10165.82 | 17374.17 | 0 | 0 | 0 | 0
2022022214 | 3 | 0.55729 | 44583.2 | 0 | 0 | 0.31636 | 11072.6 | 0.75262 | 10536.68 | 40000 | 0 | 4583.2 | 6489.4 | 0 | 10536.68 | 17026.08 | 0 | 0 | 0 | 0
2022022215 | 3 | 0.56269 | 45015.2 | 0 | 0 | 0.32426 | 11349.1 | 0.75589 | 10582.46 | 40000 | 0 | 5015.2 | 6333.9 | 0 | 10582.46 | 16916.36 | 0 | 0 | 0 | 0
2022022216 | 3 | 0.569 | 45520 | 0 | 0 | 0.36419 | 12746.65 | 0.72677 | 10174.78 | 40000 | 0 | 5520 | 7226.65 | 0 | 10174.78 | 17401.43 | 0 | 0 | 0 | 0
2022022217 | 3 | 0.57509 | 46007.2 | 0 | 0 | 0.42777 | 14971.95 | 0.62637 | 8769.18 | 40000 | 0 | 6007.2 | 8964.75 | 0 | 8769.18 | 17733.93 | 0 | 0 | 0 | 0
2022022218 | 3 | 0.58106 | 46484.8 | 0 | 0 | 0.52825 | 18488.75 | 0.33409 | 4677.26 | 40000 | 0 | 6484.8 | 12003.95 | 0 | 4677.26 | 16681.21 | 0 | 0 | 0 | 0
2022022219 | 3 | 0.59778 | 47822.4 | 0 | 0 | 0.63766 | 22318.1 | 0.02736 | 383.04 | 40000 | 0 | 7822.4 | 14495.7 | 0 | 383.04 | 14878.74 | 0 | 0 | 0 | 0
2022022220 | 3 | 0.60799 | 48639.2 | 0 | 0 | 0.69824 | 24438.4 | 6e-05 | 0.84 | 40000 | 0 | 8639.2 | 15799.2 | 0 | 0.84 | 15800.04 | 0 | 0 | 0 | 0
2022022221 | 3 | 0.60447 | 48357.6 | 0 | 0 | 0.71898 | 25164.3 | 6e-05 | 0.84 | 40000 | 0 | 8357.6 | 16806.7 | 0 | 0.84 | 16807.54 | 0 | 0 | 0 | 0
2022022222 | 3 | 0.59117 | 47293.6 | 0 | 0 | 0.72192 | 25267.2 | 6e-05 | 0.84 | 40000 | 0 | 7293.6 | 17973.6 | 0 | 0.84 | 17974.44 | 0 | 0 | 0 | 0
2022022223 | 3 | 0.56839 | 45471.2 | 0 | 0 | 0.72309 | 25308.15 | 6e-05 | 0.84 | 40000 | 0 | 5471.2 | 19836.95 | 0 | 0.84 | 19837.79 | 0 | 0 | 0 | 0
2022022224 | 3 | 0.54558 | 43646.4 | 0 | 0 | 0.71883 | 25159.05 | 6e-05 | 0.84 | 40000 | 0 | 3646.4 | 21512.65 | 0 | 0.84 | 21513.49 | 0 | 0 | 0 | 0
2022022301 | 4 | 0.52973 | 42378.4 | 0 | 0 | 0.71186 | 24915.1 | 6e-05 | 0.84 | 40000 | 0 | 2378.4 | 22536.7 | 0 | 0.84 | 22537.54 | 0 | 0 | 0 | 0
2022022302 | 4 | 0.52103 | 41682.4 | 0 | 0 | 0.70402 | 24640.7 | 6e-05 | 0.84 | 40000 | 0 | 1682.4 | 22958.3 | 0 | 0.84 | 22959.14 | 0 | 0 | 0 | 0
2022022303 | 4 | 0.51765 | 41412 | 0 | 0 | 0.69771 | 24419.85 | 6e-05 | 0.84 | 40000 | 0 | 1412 | 23007.85 | 0 | 0.84 | 23008.69 | 0 | 0 | 0 | 0
2022022304 | 4 | 0.5211 | 41688 | 0 | 0 | 0.68565 | 23997.75 | 6e-05 | 0.84 | 40000 | 0 | 1688 | 22309.75 | 0 | 0.84 | 22310.59 | 0 | 0 | 0 | 0
2022022305 | 4 | 0.53634 | 42907.2 | 0 | 0 | 0.66007 | 23102.45 | 6e-05 | 0.84 | 40000 | 0 | 2907.2 | 20195.25 | 0 | 0.84 | 20196.09 | 0 | 0 | 0 | 0
2022022306 | 4 | 0.5689 | 45512 | 0 | 0 | 0.6349 | 22221.5 | 6e-05 | 0.84 | 40000 | 0 | 5512 | 16709.5 | 0 | 0.84 | 16710.34 | 0 | 0 | 0 | 0
2022022307 | 4 | 0.61983 | 49586.4 | 0 | 0 | 0.59983 | 20994.05 | 6e-05 | 0.84 | 40000 | 0 | 9586.4 | 11407.65 | 0 | 0.84 | 11408.49 | 0 | 0 | 0 | 0
2022022308 | 4 | 0.65151 | 52120.8 | 0 | 0 | 0.53879 | 18857.65 | 0.00522 | 73.08 | 40000 | 0 | 12120.8 | 6736.85 | 0 | 73.08 | 6809.93 | 0 | 0 | 0 | 0
2022022309 | 4 | 0.66755 | 53404 | 0 | 0 | 0.48105 | 16836.75 | 0.05613 | 785.82 | 40000 | 0 | 13404 | 3432.75 | 0 | 785.82 | 4218.57 | 0 | 0 | 0 | 0
2022022310 | 4 | 0.68374 | 54699.2 | 0 | 0 | 0.43199 | 15119.65 | 0.13965 | 1955.1 | 40000 | 0 | 14699.2 | 420.45 | 0 | 1955.1 | 2375.55 | 0 | 0 | 0 | 0
2022022311 | 4 | 0.69774 | 55819.2 | 0 | 0 | 0.36339 | 12718.65 | 0.26069 | 3649.66 | 40000 | 0 | 12718.65 | 0 | 3100.55 | 549.11 | 549.11 | 0 | 0 | 0 | 0
2022022312 | 4 | 0.70789 | 56631.2 | 0 | 0 | 0.31009 | 10853.15 | 0.3617 | 5063.8 | 40000 | 0 | 10853.15 | 0 | 5063.8 | 0 | 0 | 714.25 | 0 | 0 | 714.25
2022022313 | 4 | 0.71483 | 57186.4 | 0 | 0 | 0.28292 | 9902.2 | 0.40988 | 5738.32 | 40000 | 0 | 9902.2 | 0 | 5738.32 | 0 | 0 | 1545.88 | 0 | 0 | 1545.88
2022022314 | 4 | 0.71934 | 57547.2 | 0 | 0 | 0.26753 | 9363.55 | 0.44071 | 6169.94 | 40000 | 0 | 9363.55 | 0 | 6169.94 | 0 | 0 | 2013.71 | 0 | 0 | 2013.71
2022022315 | 4 | 0.7181 | 57448 | 0 | 0 | 0.26417 | 9245.95 | 0.44219 | 6190.66 | 40000 | 0 | 9245.95 | 0 | 6190.66 | 0 | 0 | 2011.39 | 0 | 0 | 2011.39
2022022316 | 4 | 0.71999 | 57599.2 | 0 | 0 | 0.24302 | 8505.7 | 0.42562 | 5958.68 | 40000 | 0 | 8505.7 | 0 | 5958.68 | 0 | 0 | 3134.82 | 0 | 0 | 3134.82
2022022317 | 4 | 0.7327 | 58616 | 0 | 0 | 0.22848 | 7996.8 | 0.34587 | 4842.18 | 40000 | 0 | 7996.8 | 0 | 4842.18 | 0 | 0 | 5777.02 | 0 | 0 | 5777.02
2022022318 | 4 | 0.75193 | 60154.4 | 0 | 0 | 0.21018 | 7356.3 | 0.19899 | 2785.86 | 40000 | 0 | 7356.3 | 0 | 2785.86 | 0 | 0 | 10012.24 | 0 | 0 | 10012.24
2022022319 | 4 | 0.77077 | 61661.6 | 0 | 0 | 0.20448 | 7156.8 | 0.02288 | 320.32 | 40000 | 0 | 7156.8 | 0 | 320.32 | 0 | 0 | 14184.48 | 0 | 0 | 14184.48
2022022320 | 4 | 0.77219 | 61775.2 | 0 | 0 | 0.22117 | 7740.95 | 0 | 0 | 40000 | 0 | 7740.95 | 0 | 0 | 0 | 0 | 14034.25 | 0 | 0 | 14034.25
2022022321 | 4 | 0.76359 | 61087.2 | 0 | 0 | 0.20905 | 7316.75 | 0 | 0 | 40000 | 0 | 7316.75 | 0 | 0 | 0 | 0 | 13770.45 | 0 | 0 | 13770.45
2022022322 | 4 | 0.74111 | 59288.8 | 0 | 0 | 0.15892 | 5562.2 | 0 | 0 | 40000 | 0 | 5562.2 | 0 | 0 | 0 | 0 | 13726.6 | 0 | 0 | 13726.6
2022022323 | 4 | 0.71625 | 57300 | 0 | 0 | 0.11214 | 3924.9 | 0 | 0 | 40000 | 0 | 3924.9 | 0 | 0 | 0 | 0 | 13375.1 | 0 | 0 | 13375.1
2022022324 | 4 | 0.69029 | 55223.2 | 0 | 0 | 0.08283 | 2899.05 | 0 | 0 | 40000 | 0 | 2899.05 | 0 | 0 | 0 | 0 | 12324.15 | 0 | 0 | 12324.15
2022022401 | 5 | 0.67659 | 54127.2 | 0 | 0 | 0.06403 | 2241.05 | 0 | 0 | 40000 | 0 | 2241.05 | 0 | 0 | 0 | 0 | 11886.15 | 0 | 0 | 11886.15
2022022402 | 5 | 0.67088 | 53670.4 | 0 | 0 | 0.04958 | 1735.3 | 0 | 0 | 40000 | 0 | 1735.3 | 0 | 0 | 0 | 0 | 11935.1 | 0 | 0 | 11935.1
2022022403 | 5 | 0.67161 | 53728.8 | 0 | 0 | 0.04267 | 1493.45 | 0 | 0 | 40000 | 0 | 1493.45 | 0 | 0 | 0 | 0 | 12235.35 | 0 | 0 | 12235.35
2022022404 | 5 | 0.67588 | 54070.4 | 0 | 0 | 0.04525 | 1583.75 | 0 | 0 | 40000 | 0 | 1583.75 | 0 | 0 | 0 | 0 | 12486.65 | 0 | 0 | 12486.65
2022022405 | 5 | 0.68761 | 55008.8 | 0 | 0 | 0.03603 | 1261.05 | 0 | 0 | 40000 | 0 | 1261.05 | 0 | 0 | 0 | 0 | 13747.75 | 0 | 0 | 13747.75
2022022406 | 5 | 0.71207 | 56965.6 | 0 | 0 | 0.03433 | 1201.55 | 0 | 0 | 40000 | 0 | 1201.55 | 0 | 0 | 0 | 0 | 15764.05 | 0 | 0 | 15764.05
2022022407 | 5 | 0.74462 | 59569.6 | 0 | 0 | 0.0363 | 1270.5 | 0 | 0 | 40000 | 0 | 1270.5 | 0 | 0 | 0 | 0 | 18299.1 | 0 | 0 | 18299.1
2022022408 | 5 | 0.759 | 60720 | 0 | 0 | 0.03315 | 1160.25 | 0.00339 | 47.46 | 40000 | 0 | 1160.25 | 0 | 47.46 | 0 | 0 | 19512.29 | 0 | 0 | 19512.29
2022022409 | 5 | 0.76357 | 61085.6 | 0 | 0 | 0.02418 | 846.3 | 0.04028 | 563.92 | 40000 | 0 | 846.3 | 0 | 563.92 | 0 | 0 | 19675.38 | 0 | 0 | 19675.38
2022022410 | 5 | 0.76479 | 61183.2 | 0 | 0 | 0.01964 | 687.4 | 0.12159 | 1702.26 | 40000 | 0 | 687.4 | 0 | 1702.26 | 0 | 0 | 18793.54 | 0 | 0 | 18793.54
2022022411 | 5 | 0.76111 | 60888.8 | 0 | 0 | 0.01647 | 576.45 | 0.21834 | 3056.76 | 40000 | 0 | 576.45 | 0 | 3056.76 | 0 | 0 | 17255.59 | 0 | 0 | 17255.59
2022022412 | 5 | 0.75776 | 60620.8 | 0 | 0 | 0.0216 | 756 | 0.37837 | 5297.18 | 40000 | 0 | 756 | 0 | 5297.18 | 0 | 0 | 14567.62 | 0 | 0 | 14567.62
2022022413 | 5 | 0.74795 | 59836 | 0 | 0 | 0.03577 | 1251.95 | 0.5324 | 7453.6 | 40000 | 0 | 1251.95 | 0 | 7453.6 | 0 | 0 | 11130.45 | 0 | 0 | 11130.45
2022022414 | 5 | 0.73471 | 58776.8 | 0 | 0 | 0.05821 | 2037.35 | 0.5737 | 8031.8 | 40000 | 0 | 2037.35 | 0 | 8031.8 | 0 | 0 | 8707.65 | 0 | 0 | 8707.65
2022022415 | 5 | 0.72263 | 57810.4 | 0 | 0 | 0.07784 | 2724.4 | 0.5781 | 8093.4 | 40000 | 0 | 2724.4 | 0 | 8093.4 | 0 | 0 | 6992.6 | 0 | 0 | 6992.6
2022022416 | 5 | 0.7181 | 57448 | 0 | 0 | 0.11666 | 4083.1 | 0.57332 | 8026.48 | 40000 | 0 | 4083.1 | 0 | 8026.48 | 0 | 0 | 5338.42 | 0 | 0 | 5338.42
2022022417 | 5 | 0.72214 | 57771.2 | 0 | 0 | 0.13536 | 4737.6 | 0.56641 | 7929.74 | 40000 | 0 | 4737.6 | 0 | 7929.74 | 0 | 0 | 5103.86 | 0 | 0 | 5103.86
2022022418 | 5 | 0.73432 | 58745.6 | 0 | 0 | 0.14114 | 4939.9 | 0.3294 | 4611.6 | 40000 | 0 | 4939.9 | 0 | 4611.6 | 0 | 0 | 9194.1 | 0 | 0 | 9194.1
2022022419 | 5 | 0.75484 | 60387.2 | 0 | 0 | 0.14054 | 4918.9 | 0.02977 | 416.78 | 40000 | 0 | 4918.9 | 0 | 416.78 | 0 | 0 | 15051.52 | 0 | 0 | 15051.52
2022022420 | 5 | 0.75948 | 60758.4 | 0 | 0 | 0.15051 | 5267.85 | 0 | 0 | 40000 | 0 | 5267.85 | 0 | 0 | 0 | 0 | 15490.55 | 0 | 0 | 15490.55
2022022421 | 5 | 0.75503 | 60402.4 | 0 | 0 | 0.16269 | 5694.15 | 0 | 0 | 40000 | 0 | 5694.15 | 0 | 0 | 0 | 0 | 14708.25 | 0 | 0 | 14708.25
2022022422 | 5 | 0.7398 | 59184 | 0 | 0 | 0.18314 | 6409.9 | 0 | 0 | 40000 | 0 | 6409.9 | 0 | 0 | 0 | 0 | 12774.1 | 0 | 0 | 12774.1
2022022423 | 5 | 0.71252 | 57001.6 | 0 | 0 | 0.19654 | 6878.9 | 0 | 0 | 40000 | 0 | 6878.9 | 0 | 0 | 0 | 0 | 10122.7 | 0 | 0 | 10122.7
2022022424 | 5 | 0.68986 | 55188.8 | 0 | 0 | 0.18716 | 6550.6 | 0 | 0 | 40000 | 0 | 6550.6 | 0 | 0 | 0 | 0 | 8638.2 | 0 | 0 | 8638.2
2022022501 | 6 | 0.67695 | 54156 | 0 | 0 | 0.15685 | 5489.75 | 0 | 0 | 40000 | 0 | 5489.75 | 0 | 0 | 0 | 0 | 8666.25 | 0 | 0 | 8666.25
2022022502 | 6 | 0.67093 | 53674.4 | 0 | 0 | 0.14157 | 4954.95 | 0 | 0 | 40000 | 0 | 4954.95 | 0 | 0 | 0 | 0 | 8719.45 | 0 | 0 | 8719.45
2022022503 | 6 | 0.67444 | 53955.2 | 0 | 0 | 0.12534 | 4386.9 | 0 | 0 | 40000 | 0 | 4386.9 | 0 | 0 | 0 | 0 | 9568.3 | 0 | 0 | 9568.3
2022022504 | 6 | 0.68302 | 54641.6 | 0 | 0 | 0.12792 | 4477.2 | 0 | 0 | 40000 | 0 | 4477.2 | 0 | 0 | 0 | 0 | 10164.4 | 0 | 0 | 10164.4
2022022505 | 6 | 0.70084 | 56067.2 | 0 | 0 | 0.15066 | 5273.1 | 0 | 0 | 40000 | 0 | 5273.1 | 0 | 0 | 0 | 0 | 10794.1 | 0 | 0 | 10794.1
2022022506 | 6 | 0.73298 | 58638.4 | 0 | 0 | 0.19383 | 6784.05 | 0 | 0 | 40000 | 0 | 6784.05 | 0 | 0 | 0 | 0 | 11854.35 | 0 | 0 | 11854.35
2022022507 | 6 | 0.77966 | 62372.8 | 0 | 0 | 0.2082 | 7287 | 0 | 0 | 40000 | 0 | 7287 | 0 | 0 | 0 | 0 | 15085.8 | 0 | 0 | 15085.8
2022022508 | 6 | 0.79981 | 63984.8 | 0 | 0 | 0.20634 | 7221.9 | 0.03479 | 487.06 | 40000 | 0 | 7221.9 | 0 | 487.06 | 0 | 0 | 16275.84 | 0 | 0 | 16275.84
2022022509 | 6 | 0.7959 | 63672 | 0 | 0 | 0.19377 | 6781.95 | 0.24372 | 3412.08 | 40000 | 0 | 6781.95 | 0 | 3412.08 | 0 | 0 | 13477.97 | 0 | 0 | 13477.97
2022022510 | 6 | 0.78601 | 62880.8 | 0 | 0 | 0.21784 | 7624.4 | 0.47718 | 6680.52 | 40000 | 0 | 7624.4 | 0 | 6680.52 | 0 | 0 | 8575.88 | 0 | 0 | 8575.88
2022022511 | 6 | 0.76809 | 61447.2 | 0 | 0 | 0.2189 | 7661.5 | 0.56196 | 7867.44 | 40000 | 0 | 7661.5 | 0 | 7867.44 | 0 | 0 | 5918.26 | 0 | 0 | 5918.26
2022022512 | 6 | 0.74774 | 59819.2 | 0 | 0 | 0.211 | 7385 | 0.62419 | 8738.66 | 40000 | 0 | 7385 | 0 | 8738.66 | 0 | 0 | 3695.54 | 0 | 0 | 3695.54
2022022513 | 6 | 0.7257 | 58056 | 0 | 0 | 0.20388 | 7135.8 | 0.61133 | 8558.62 | 40000 | 0 | 7135.8 | 0 | 8558.62 | 0 | 0 | 2361.58 | 0 | 0 | 2361.58
2022022514 | 6 | 0.70917 | 56733.6 | 0 | 0 | 0.21385 | 7484.75 | 0.61782 | 8649.48 | 40000 | 0 | 7484.75 | 0 | 8649.48 | 0 | 0 | 599.37 | 0 | 0 | 599.37
2022022515 | 6 | 0.69797 | 55837.6 | 0 | 0 | 0.20787 | 7275.45 | 0.52075 | 7290.5 | 40000 | 0 | 7275.45 | 0 | 7290.5 | 0 | 0 | 1271.65 | 0 | 0 | 1271.65
2022022516 | 6 | 0.69788 | 55830.4 | 0 | 0 | 0.22071 | 7724.85 | 0.49313 | 6903.82 | 40000 | 0 | 7724.85 | 0 | 6903.82 | 0 | 0 | 1201.73 | 0 | 0 | 1201.73
2022022517 | 6 | 0.70622 | 56497.6 | 0 | 0 | 0.22758 | 7965.3 | 0.41043 | 5746.02 | 40000 | 0 | 7965.3 | 0 | 5746.02 | 0 | 0 | 2786.28 | 0 | 0 | 2786.28
2022022518 | 6 | 0.71576 | 57260.8 | 0 | 0 | 0.26185 | 9164.75 | 0.21194 | 2967.16 | 40000 | 0 | 9164.75 | 0 | 2967.16 | 0 | 0 | 5128.89 | 0 | 0 | 5128.89
2022022519 | 6 | 0.72768 | 58214.4 | 0 | 0 | 0.27727 | 9704.45 | 0.01262 | 176.68 | 40000 | 0 | 9704.45 | 0 | 176.68 | 0 | 0 | 8333.27 | 0 | 0 | 8333.27
2022022520 | 6 | 0.72602 | 58081.6 | 0 | 0 | 0.26191 | 9166.85 | 0 | 0 | 40000 | 0 | 9166.85 | 0 | 0 | 0 | 0 | 8914.75 | 0 | 0 | 8914.75
2022022521 | 6 | 0.71567 | 57253.6 | 0 | 0 | 0.25848 | 9046.8 | 0 | 0 | 40000 | 0 | 9046.8 | 0 | 0 | 0 | 0 | 8206.8 | 0 | 0 | 8206.8
2022022522 | 6 | 0.69941 | 55952.8 | 0 | 0 | 0.24897 | 8713.95 | 0 | 0 | 40000 | 0 | 8713.95 | 0 | 0 | 0 | 0 | 7238.85 | 0 | 0 | 7238.85
2022022523 | 6 | 0.67401 | 53920.8 | 0 | 0 | 0.21913 | 7669.55 | 0 | 0 | 40000 | 0 | 7669.55 | 0 | 0 | 0 | 0 | 6251.25 | 0 | 0 | 6251.25
2022022524 | 6 | 0.65094 | 52075.2 | 0 | 0 | 0.18096 | 6333.6 | 0 | 0 | 40000 | 0 | 6333.6 | 0 | 0 | 0 | 0 | 5741.6 | 0 | 0 | 5741.6
2022022601 | 7 | 0.63428 | 50742.4 | 0 | 0 | 0.14784 | 5174.4 | 0 | 0 | 40000 | 0 | 5174.4 | 0 | 0 | 0 | 0 | 5568 | 0 | 0 | 5568
2022022602 | 7 | 0.62475 | 49980 | 0 | 0 | 0.13387 | 4685.45 | 0 | 0 | 40000 | 0 | 4685.45 | 0 | 0 | 0 | 0 | 5294.55 | 0 | 0 | 5294.55
2022022603 | 7 | 0.61908 | 49526.4 | 0 | 0 | 0.13441 | 4704.35 | 0 | 0 | 40000 | 0 | 4704.35 | 0 | 0 | 0 | 0 | 4822.05 | 0 | 0 | 4822.05
2022022604 | 7 | 0.61877 | 49501.6 | 0 | 0 | 0.12784 | 4474.4 | 0 | 0 | 40000 | 0 | 4474.4 | 0 | 0 | 0 | 0 | 5027.2 | 0 | 0 | 5027.2
2022022605 | 7 | 0.62566 | 50052.8 | 0 | 0 | 0.12148 | 4251.8 | 0 | 0 | 40000 | 0 | 4251.8 | 0 | 0 | 0 | 0 | 5801 | 0 | 0 | 5801
2022022606 | 7 | 0.63911 | 51128.8 | 0 | 0 | 0.12173 | 4260.55 | 0 | 0 | 40000 | 0 | 4260.55 | 0 | 0 | 0 | 0 | 6868.25 | 0 | 0 | 6868.25
2022022607 | 7 | 0.66013 | 52810.4 | 0 | 0 | 0.12811 | 4483.85 | 0 | 0 | 40000 | 0 | 4483.85 | 0 | 0 | 0 | 0 | 8326.55 | 0 | 0 | 8326.55
2022022608 | 7 | 0.67803 | 54242.4 | 0 | 0 | 0.12241 | 4284.35 | 0.00619 | 86.66 | 40000 | 0 | 4284.35 | 0 | 86.66 | 0 | 0 | 9871.39 | 0 | 0 | 9871.39
2022022609 | 7 | 0.69688 | 55750.4 | 0 | 0 | 0.09989 | 3496.15 | 0.10493 | 1469.02 | 40000 | 0 | 3496.15 | 0 | 1469.02 | 0 | 0 | 10785.23 | 0 | 0 | 10785.23
2022022610 | 7 | 0.71126 | 56900.8 | 0 | 0 | 0.0739 | 2586.5 | 0.28118 | 3936.52 | 40000 | 0 | 2586.5 | 0 | 3936.52 | 0 | 0 | 10377.78 | 0 | 0 | 10377.78
2022022611 | 7 | 0.71541 | 57232.8 | 0 | 0 | 0.05453 | 1908.55 | 0.41299 | 5781.86 | 40000 | 0 | 1908.55 | 0 | 5781.86 | 0 | 0 | 9542.39 | 0 | 0 | 9542.39
2022022612 | 7 | 0.70707 | 56565.6 | 0 | 0 | 0.04285 | 1499.75 | 0.52628 | 7367.92 | 40000 | 0 | 1499.75 | 0 | 7367.92 | 0 | 0 | 7697.93 | 0 | 0 | 7697.93
2022022613 | 7 | 0.69262 | 55409.6 | 0 | 0 | 0.04132 | 1446.2 | 0.58671 | 8213.94 | 40000 | 0 | 1446.2 | 0 | 8213.94 | 0 | 0 | 5749.46 | 0 | 0 | 5749.46
2022022614 | 7 | 0.67927 | 54341.6 | 0 | 0 | 0.04301 | 1505.35 | 0.58534 | 8194.76 | 40000 | 0 | 1505.35 | 0 | 8194.76 | 0 | 0 | 4641.49 | 0 | 0 | 4641.49
2022022615 | 7 | 0.66788 | 53430.4 | 0 | 0 | 0.04917 | 1720.95 | 0.57733 | 8082.62 | 40000 | 0 | 1720.95 | 0 | 8082.62 | 0 | 0 | 3626.83 | 0 | 0 | 3626.83
2022022616 | 7 | 0.664 | 53120 | 0 | 0 | 0.06513 | 2279.55 | 0.55402 | 7756.28 | 40000 | 0 | 2279.55 | 0 | 7756.28 | 0 | 0 | 3084.17 | 0 | 0 | 3084.17
2022022617 | 7 | 0.66511 | 53208.8 | 0 | 0 | 0.07974 | 2790.9 | 0.52932 | 7410.48 | 40000 | 0 | 2790.9 | 0 | 7410.48 | 0 | 0 | 3007.42 | 0 | 0 | 3007.42
2022022618 | 7 | 0.6698 | 53584 | 0 | 0 | 0.08958 | 3135.3 | 0.35312 | 4943.68 | 40000 | 0 | 3135.3 | 0 | 4943.68 | 0 | 0 | 5505.02 | 0 | 0 | 5505.02
2022022619 | 7 | 0.68294 | 54635.2 | 0 | 0 | 0.09444 | 3305.4 | 0.04239 | 593.46 | 40000 | 0 | 3305.4 | 0 | 593.46 | 0 | 0 | 10736.34 | 0 | 0 | 10736.34
2022022620 | 7 | 0.685 | 54800 | 0 | 0 | 0.09936 | 3477.6 | 0.00012 | 1.68 | 40000 | 0 | 3477.6 | 0 | 1.68 | 0 | 0 | 11320.72 | 0 | 0 | 11320.72
2022022621 | 7 | 0.67773 | 54218.4 | 0 | 0 | 0.09106 | 3187.1 | 0.00012 | 1.68 | 40000 | 0 | 3187.1 | 0 | 1.68 | 0 | 0 | 11029.62 | 0 | 0 | 11029.62
2022022622 | 7 | 0.66472 | 53177.6 | 0 | 0 | 0.08867 | 3103.45 | 0.00012 | 1.68 | 40000 | 0 | 3103.45 | 0 | 1.68 | 0 | 0 | 10072.47 | 0 | 0 | 10072.47
2022022623 | 7 | 0.64518 | 51614.4 | 0 | 0 | 0.08964 | 3137.4 | 0.00012 | 1.68 | 40000 | 0 | 3137.4 | 0 | 1.68 | 0 | 0 | 8475.32 | 0 | 0 | 8475.32
2022022624 | 7 | 0.62485 | 49988 | 0 | 0 | 0.08722 | 3052.7 | 0.00012 | 1.68 | 40000 | 0 | 3052.7 | 0 | 1.68 | 0 | 0 | 6933.62 | 0 | 0 | 6933.62
2022022701 | 1 | 0.60976 | 48780.8 | 0 | 0 | 0.11167 | 3908.45 | 0.00012 | 1.68 | 40000 | 0 | 3908.45 | 0 | 1.68 | 0 | 0 | 4870.67 | 0 | 0 | 4870.67
2022022702 | 1 | 0.60043 | 48034.4 | 0 | 0 | 0.14401 | 5040.35 | 0.00012 | 1.68 | 40000 | 0 | 5040.35 | 0 | 1.68 | 0 | 0 | 2992.37 | 0 | 0 | 2992.37
2022022703 | 1 | 0.59887 | 47909.6 | 0 | 0 | 0.18345 | 6420.75 | 0.00012 | 1.68 | 40000 | 0 | 6420.75 | 0 | 1.68 | 0 | 0 | 1487.17 | 0 | 0 | 1487.17
2022022704 | 1 | 0.60246 | 48196.8 | 0 | 0 | 0.22871 | 8004.85 | 0.00011 | 1.54 | 40000 | 0 | 8004.85 | 0 | 1.54 | 0 | 0 | 190.41 | 0 | 0 | 190.41
2022022705 | 1 | 0.61088 | 48870.4 | 0 | 0 | 0.26594 | 9307.9 | 0.00011 | 1.54 | 40000 | 0 | 8870.4 | 437.5 | 0 | 1.54 | 439.04 | 0 | 0 | 0 | 0
2022022706 | 1 | 0.62611 | 50088.8 | 0 | 0 | 0.29816 | 10435.6 | 0.00011 | 1.54 | 40000 | 0 | 10088.8 | 346.8 | 0 | 1.54 | 348.34 | 0 | 0 | 0 | 0
2022022707 | 1 | 0.64762 | 51809.6 | 0 | 0 | 0.30479 | 10667.65 | 0.00013 | 1.82 | 40000 | 0 | 10667.65 | 0 | 1.82 | 0 | 0 | 1140.13 | 0 | 0 | 1140.13
2022022708 | 1 | 0.66211 | 52968.8 | 0 | 0 | 0.2958 | 10353 | 0.06704 | 938.56 | 40000 | 0 | 10353 | 0 | 938.56 | 0 | 0 | 1677.24 | 0 | 0 | 1677.24
2022022709 | 1 | 0.65733 | 52586.4 | 0 | 0 | 0.24316 | 8510.6 | 0.5372 | 7520.8 | 40000 | 0 | 8510.6 | 0 | 4075.8 | 3445 | 3445 | 0 | 0 | 0 | 0
2022022710 | 1 | 0.64147 | 51317.6 | 0 | 0 | 0.17644 | 6175.4 | 0.80043 | 11206.02 | 40000 | 0 | 6175.4 | 0 | 5142.2 | 6063.82 | 6063.82 | 0 | 0 | 0 | 0
2022022711 | 1 | 0.61858 | 49486.4 | 0 | 0 | 0.18707 | 6547.45 | 0.82955 | 11613.7 | 40000 | 0 | 6547.45 | 0 | 2938.95 | 8674.75 | 8674.75 | 0 | 0 | 0 | 0
2022022712 | 1 | 0.59181 | 47344.8 | 0 | 0 | 0.17734 | 6206.9 | 0.83698 | 11717.72 | 40000 | 0 | 6206.9 | 0 | 1137.9 | 10579.82 | 10579.82 | 0 | 0 | 0 | 0
2022022713 | 1 | 0.56634 | 45307.2 | 0 | 0 | 0.16132 | 5646.2 | 0.84488 | 11828.32 | 40000 | 0 | 5307.2 | 339 | 0 | 11828.32 | 12167.32 | 0 | 0 | 0 | 0
2022022714 | 1 | 0.54065 | 43252 | 0 | 0 | 0.15337 | 5367.95 | 0.85268 | 11937.52 | 40000 | 0 | 3252 | 2115.95 | 0 | 11937.52 | 14053.47 | 0 | 0 | 0 | 0
2022022715 | 1 | 0.5183 | 41464 | 0 | 0 | 0.13341 | 4669.35 | 0.85989 | 12038.46 | 40000 | 0 | 1464 | 3205.35 | 0 | 12038.46 | 15243.81 | 0 | 0 | 0 | 0
2022022716 | 1 | 0.50636 | 40508.8 | 0 | 0 | 0.11422 | 3997.7 | 0.87263 | 12216.82 | 40000 | 0 | 508.8 | 3488.9 | 0 | 12216.82 | 15705.72 | 0 | 0 | 0 | 0
2022022717 | 1 | 0.5041 | 40328 | 0 | 0 | 0.09629 | 3370.15 | 0.8363 | 11708.2 | 40000 | 0 | 328 | 3042.15 | 0 | 11708.2 | 14750.35 | 0 | 0 | 0 | 0
2022022718 | 1 | 0.51529 | 41223.2 | 0 | 0 | 0.07792 | 2727.2 | 0.51496 | 7209.44 | 40000 | 0 | 1223.2 | 1504 | 0 | 7209.44 | 8713.44 | 0 | 0 | 0 | 0
2022022719 | 1 | 0.55097 | 44077.6 | 0 | 0 | 0.05911 | 2068.85 | 0.05469 | 765.66 | 40000 | 0 | 2068.85 | 0 | 765.66 | 0 | 0 | 1243.09 | 0 | 0 | 1243.09
2022022720 | 1 | 0.58071 | 46456.8 | 0 | 0 | 0.07073 | 2475.55 | 6e-05 | 0.84 | 40000 | 0 | 2475.55 | 0 | 0.84 | 0 | 0 | 3980.41 | 0 | 0 | 3980.41
2022022721 | 1 | 0.59054 | 47243.2 | 0 | 0 | 0.10148 | 3551.8 | 6e-05 | 0.84 | 40000 | 0 | 3551.8 | 0 | 0.84 | 0 | 0 | 3690.56 | 0 | 0 | 3690.56
2022022722 | 1 | 0.59135 | 47308 | 0 | 0 | 0.12789 | 4476.15 | 6e-05 | 0.84 | 40000 | 0 | 4476.15 | 0 | 0.84 | 0 | 0 | 2831.01 | 0 | 0 | 2831.01
2022022723 | 1 | 0.57944 | 46355.2 | 0 | 0 | 0.1628 | 5698 | 6e-05 | 0.84 | 40000 | 0 | 5698 | 0 | 0.84 | 0 | 0 | 656.36 | 0 | 0 | 656.36
2022022724 | 1 | 0.56677 | 45341.6 | 0 | 0 | 0.20181 | 7063.35 | 6e-05 | 0.84 | 40000 | 0 | 5341.6 | 1721.75 | 0 | 0.84 | 1722.59 | 0 | 0 | 0 | 0
2022022801 | 2 | 0.56108 | 44886.4 | 0 | 0 | 0.24305 | 8506.75 | 6e-05 | 0.84 | 40000 | 0 | 4886.4 | 3620.35 | 0 | 0.84 | 3621.19 | 0 | 0 | 0 | 0
2022022802 | 2 | 0.56499 | 45199.2 | 0 | 0 | 0.27897 | 9763.95 | 6e-05 | 0.84 | 40000 | 0 | 5199.2 | 4564.75 | 0 | 0.84 | 4565.59 | 0 | 0 | 0 | 0
2022022803 | 2 | 0.57431 | 45944.8 | 0 | 0 | 0.30888 | 10810.8 | 6e-05 | 0.84 | 40000 | 0 | 5944.8 | 4866 | 0 | 0.84 | 4866.84 | 0 | 0 | 0 | 0
2022022804 | 2 | 0.58903 | 47122.4 | 0 | 0 | 0.32821 | 11487.35 | 6e-05 | 0.84 | 40000 | 0 | 7122.4 | 4364.95 | 0 | 0.84 | 4365.79 | 0 | 0 | 0 | 0
2022022805 | 2 | 0.61574 | 49259.2 | 0 | 0 | 0.3307 | 11574.5 | 6e-05 | 0.84 | 40000 | 0 | 9259.2 | 2315.3 | 0 | 0.84 | 2316.14 | 0 | 0 | 0 | 0
2022022806 | 2 | 0.66045 | 52836 | 0 | 0 | 0.31472 | 11015.2 | 6e-05 | 0.84 | 40000 | 0 | 11015.2 | 0 | 0.84 | 0 | 0 | 1819.96 | 0 | 0 | 1819.96
2022022807 | 2 | 0.72104 | 57683.2 | 0 | 0 | 0.31206 | 10922.1 | 0.00015 | 2.1 | 40000 | 0 | 10922.1 | 0 | 2.1 | 0 | 0 | 6759 | 0 | 0 | 6759
2022022808 | 2 | 0.73408 | 58726.4 | 0 | 0 | 0.31155 | 10904.25 | 0.09233 | 1292.62 | 40000 | 0 | 10904.25 | 0 | 1292.62 | 0 | 0 | 6529.53 | 0 | 0 | 6529.53
2022022809 | 2 | 0.68635 | 54908 | 0 | 0 | 0.26276 | 9196.6 | 0.52165 | 7303.1 | 40000 | 0 | 9196.6 | 0 | 5711.4 | 1591.7 | 1591.7 | 0 | 0 | 0 | 0
2022022810 | 2 | 0.63304 | 50643.2 | 0 | 0 | 0.15434 | 5401.9 | 0.74412 | 10417.68 | 40000 | 0 | 5401.9 | 0 | 5241.3 | 5176.38 | 5176.38 | 0 | 0 | 0 | 0
2022022811 | 2 | 0.59142 | 47313.6 | 0 | 0 | 0.13718 | 4801.3 | 0.79565 | 11139.1 | 40000 | 0 | 4801.3 | 0 | 2512.3 | 8626.8 | 8626.8 | 0 | 0 | 0 | 0
2022022812 | 2 | 0.55875 | 44700 | 0 | 0 | 0.12024 | 4208.4 | 0.77458 | 10844.12 | 40000 | 0 | 4208.4 | 0 | 491.6 | 10352.52 | 10352.52 | 0 | 0 | 0 | 0
2022022813 | 2 | 0.5302 | 42416 | 0 | 0 | 0.10156 | 3554.6 | 0.75361 | 10550.54 | 40000 | 0 | 2416 | 1138.6 | 0 | 10550.54 | 11689.14 | 0 | 0 | 0 | 0
2022022814 | 2 | 0.5124 | 40992 | 0 | 0 | 0.0937 | 3279.5 | 0.70928 | 9929.92 | 40000 | 0 | 992 | 2287.5 | 0 | 9929.92 | 12217.42 | 0 | 0 | 0 | 0
2022022815 | 2 | 0.49923 | 39938.4 | 0 | 0 | 0.08131 | 2845.85 | 0.61015 | 8542.1 | 39938.4 | 61.6 | 0 | 2845.85 | 0 | 8542.1 | 11449.55 | 0 | 0 | 0 | 0
2022022816 | 2 | 0.49412 | 39529.6 | 0 | 0 | 0.07097 | 2483.95 | 0.44308 | 6203.12 | 39529.6 | 470.4 | 0 | 2483.95 | 0 | 6203.12 | 9157.47 | 0 | 0 | 0 | 0
2022022817 | 2 | 0.49745 | 39796 | 0 | 0 | 0.06488 | 2270.8 | 0.32873 | 4602.22 | 39796 | 204 | 0 | 2270.8 | 0 | 4602.22 | 7077.02 | 0 | 0 | 0 | 0
2022022818 | 2 | 0.5059 | 40472 | 0 | 0 | 0.07136 | 2497.6 | 0.16998 | 2379.72 | 40000 | 0 | 472 | 2025.6 | 0 | 2379.72 | 4405.32 | 0 | 0 | 0 | 0
2022022819 | 2 | 0.52966 | 42372.8 | 0 | 0 | 0.10197 | 3568.95 | 0.02129 | 298.06 | 40000 | 0 | 2372.8 | 1196.15 | 0 | 298.06 | 1494.21 | 0 | 0 | 0 | 0
2022022820 | 2 | 0.54639 | 43711.2 | 0 | 0 | 0.15273 | 5345.55 | 0 | 0 | 40000 | 0 | 3711.2 | 1634.35 | 0 | 0 | 1634.35 | 0 | 0 | 0 | 0
2022022821 | 2 | 0.54715 | 43772 | 0 | 0 | 0.22239 | 7783.65 | 0 | 0 | 40000 | 0 | 3772 | 4011.65 | 0 | 0 | 4011.65 | 0 | 0 | 0 | 0
2022022822 | 2 | 0.53868 | 43094.4 | 0 | 0 | 0.27887 | 9760.45 | 0 | 0 | 40000 | 0 | 3094.4 | 6666.05 | 0 | 0 | 6666.05 | 0 | 0 | 0 | 0
2022022823 | 2 | 0.51889 | 41511.2 | 0 | 0 | 0.32457 | 11359.95 | 0 | 0 | 40000 | 0 | 1511.2 | 9848.75 | 0 | 0 | 9848.75 | 0 | 0 | 0 | 0
2022022824 | 2 | 0.50023 | 40018.4 | 0 | 0 | 0.34824 | 12188.4 | 0 | 0 | 40000 | 0 | 18.4 | 12170 | 0 | 0 | 12170 | 0 | 0 | 0 | 0
2022030101 | 3 | 0.49045 | 39236 | 0 | 0 | 0.36388 | 12735.8 | 0 | 0 | 39236 | 764 | 0 | 12735.8 | 0 | 0 | 13499.8 | 0 | 0 | 0 | 0
2022030102 | 3 | 0.4915 | 39320 | 0 | 0 | 0.3645 | 12757.5 | 0 | 0 | 39320 | 680 | 0 | 12757.5 | 0 | 0 | 13437.5 | 0 | 0 | 0 | 0
2022030103 | 3 | 0.49652 | 39721.6 | 0 | 0 | 0.34252 | 11988.2 | 0 | 0 | 39721.6 | 278.4 | 0 | 11988.2 | 0 | 0 | 12266.6 | 0 | 0 | 0 | 0
2022030104 | 3 | 0.50844 | 40675.2 | 0 | 0 | 0.30389 | 10636.15 | 0 | 0 | 40000 | 0 | 675.2 | 9960.95 | 0 | 0 | 9960.95 | 0 | 0 | 0 | 0
2022030105 | 3 | 0.53038 | 42430.4 | 0 | 0 | 0.26175 | 9161.25 | 0 | 0 | 40000 | 0 | 2430.4 | 6730.85 | 0 | 0 | 6730.85 | 0 | 0 | 0 | 0
2022030106 | 3 | 0.57286 | 45828.8 | 0 | 0 | 0.22343 | 7820.05 | 0 | 0 | 40000 | 0 | 5828.8 | 1991.25 | 0 | 0 | 1991.25 | 0 | 0 | 0 | 0
2022030107 | 3 | 0.63075 | 50460 | 0 | 0 | 0.19607 | 6862.45 | 0.00012 | 1.68 | 40000 | 0 | 6862.45 | 0 | 1.68 | 0 | 0 | 3595.87 | 0 | 0 | 3595.87
2022030108 | 3 | 0.64507 | 51605.6 | 0 | 0 | 0.16207 | 5672.45 | 0.06279 | 879.06 | 40000 | 0 | 5672.45 | 0 | 879.06 | 0 | 0 | 5054.09 | 0 | 0 | 5054.09
2022030109 | 3 | 0.6113 | 48904 | 0 | 0 | 0.11276 | 3946.6 | 0.32114 | 4495.96 | 40000 | 0 | 3946.6 | 0 | 4495.96 | 0 | 0 | 461.44 | 0 | 0 | 461.44
2022030110 | 3 | 0.5713 | 45704 | 0 | 0 | 0.07511 | 2628.85 | 0.50185 | 7025.9 | 40000 | 0 | 2628.85 | 0 | 3075.15 | 3950.75 | 3950.75 | 0 | 0 | 0 | 0
2022030111 | 3 | 0.54109 | 43287.2 | 0 | 0 | 0.067 | 2345 | 0.58955 | 8253.7 | 40000 | 0 | 2345 | 0 | 942.2 | 7311.5 | 7311.5 | 0 | 0 | 0 | 0
2022030112 | 3 | 0.51828 | 41462.4 | 0 | 0 | 0.043 | 1505 | 0.63904 | 8946.56 | 40000 | 0 | 1462.4 | 42.6 | 0 | 8946.56 | 8989.16 | 0 | 0 | 0 | 0
2022030113 | 3 | 0.50316 | 40252.8 | 0 | 0 | 0.03557 | 1244.95 | 0.63638 | 8909.32 | 40000 | 0 | 252.8 | 992.15 | 0 | 8909.32 | 9901.47 | 0 | 0 | 0 | 0
2022030114 | 3 | 0.49561 | 39648.8 | 0 | 0 | 0.03954 | 1383.9 | 0.62744 | 8784.16 | 39648.8 | 351.2 | 0 | 1383.9 | 0 | 8784.16 | 10519.26 | 0 | 0 | 0 | 0
2022030115 | 3 | 0.49209 | 39367.2 | 0 | 0 | 0.04946 | 1731.1 | 0.57299 | 8021.86 | 39367.2 | 632.8 | 0 | 1731.1 | 0 | 8021.86 | 10385.76 | 0 | 0 | 0 | 0
2022030116 | 3 | 0.49002 | 39201.6 | 0 | 0 | 0.05659 | 1980.65 | 0.516 | 7224 | 39201.6 | 798.4 | 0 | 1980.65 | 0 | 7224 | 10003.05 | 0 | 0 | 0 | 0
2022030117 | 3 | 0.49588 | 39670.4 | 0 | 0 | 0.05558 | 1945.3 | 0.35572 | 4980.08 | 39670.4 | 329.6 | 0 | 1945.3 | 0 | 4980.08 | 7254.98 | 0 | 0 | 0 | 0
2022030118 | 3 | 0.50104 | 40083.2 | 0 | 0 | 0.06243 | 2185.05 | 0.14397 | 2015.58 | 40000 | 0 | 83.2 | 2101.85 | 0 | 2015.58 | 4117.43 | 0 | 0 | 0 | 0
2022030119 | 3 | 0.51643 | 41314.4 | 0 | 0 | 0.08935 | 3127.25 | 0.01515 | 212.1 | 40000 | 0 | 1314.4 | 1812.85 | 0 | 212.1 | 2024.95 | 0 | 0 | 0 | 0
2022030120 | 3 | 0.52783 | 42226.4 | 0 | 0 | 0.14846 | 5196.1 | 0 | 0 | 40000 | 0 | 2226.4 | 2969.7 | 0 | 0 | 2969.7 | 0 | 0 | 0 | 0
2022030121 | 3 | 0.52039 | 41631.2 | 0 | 0 | 0.19868 | 6953.8 | 0 | 0 | 40000 | 0 | 1631.2 | 5322.6 | 0 | 0 | 5322.6 | 0 | 0 | 0 | 0
2022030122 | 3 | 0.50845 | 40676 | 0 | 0 | 0.21926 | 7674.1 | 0 | 0 | 40000 | 0 | 676 | 6998.1 | 0 | 0 | 6998.1 | 0 | 0 | 0 | 0
2022030123 | 3 | 0.48684 | 38947.2 | 0 | 0 | 0.23616 | 8265.6 | 0 | 0 | 38947.2 | 1052.8 | 0 | 8265.6 | 0 | 0 | 9318.4 | 0 | 0 | 0 | 0
2022030124 | 3 | 0.46351 | 37080.8 | 0 | 0 | 0.24711 | 8648.85 | 0 | 0 | 37080.8 | 2919.2 | 0 | 8648.85 | 0 | 0 | 11568.05 | 0 | 0 | 0 | 0
2022030201 | 4 | 0.44867 | 35893.6 | 0 | 0 | 0.25308 | 8857.8 | 0 | 0 | 35893.6 | 4106.4 | 0 | 8857.8 | 0 | 0 | 12964.2 | 0 | 0 | 0 | 0
2022030202 | 4 | 0.443 | 35440 | 0 | 0 | 0.24003 | 8401.05 | 0 | 0 | 35440 | 4560 | 0 | 8401.05 | 0 | 0 | 12961.05 | 0 | 0 | 0 | 0
2022030203 | 4 | 0.44394 | 35515.2 | 0 | 0 | 0.21364 | 7477.4 | 0 | 0 | 35515.2 | 4484.8 | 0 | 7477.4 | 0 | 0 | 11962.2 | 0 | 0 | 0 | 0
2022030204 | 4 | 0.4532 | 36256 | 0 | 0 | 0.18695 | 6543.25 | 0 | 0 | 36256 | 3744 | 0 | 6543.25 | 0 | 0 | 10287.25 | 0 | 0 | 0 | 0
2022030205 | 4 | 0.47137 | 37709.6 | 0 | 0 | 0.17655 | 6179.25 | 0 | 0 | 37709.6 | 2290.4 | 0 | 6179.25 | 0 | 0 | 8469.65 | 0 | 0 | 0 | 0
2022030206 | 4 | 0.50832 | 40665.6 | 0 | 0 | 0.16059 | 5620.65 | 0 | 0 | 40000 | 0 | 665.6 | 4955.05 | 0 | 0 | 4955.05 | 0 | 0 | 0 | 0
2022030207 | 4 | 0.56281 | 45024.8 | 0 | 0 | 0.14113 | 4939.55 | 0.00012 | 1.68 | 40000 | 0 | 4939.55 | 0 | 1.68 | 0 | 0 | 83.57 | 0 | 0 | 83.57
2022030208 | 4 | 0.5791 | 46328 | 0 | 0 | 0.12576 | 4401.6 | 0.07821 | 1094.94 | 40000 | 0 | 4401.6 | 0 | 1094.94 | 0 | 0 | 831.46 | 0 | 0 | 831.46
2022030209 | 4 | 0.55599 | 44479.2 | 0 | 0 | 0.09044 | 3165.4 | 0.49064 | 6868.96 | 40000 | 0 | 3165.4 | 0 | 1313.8 | 5555.16 | 5555.16 | 0 | 0 | 0 | 0
2022030210 | 4 | 0.52984 | 42387.2 | 0 | 0 | 0.04615 | 1615.25 | 0.74948 | 10492.72 | 40000 | 0 | 1615.25 | 0 | 771.95 | 9720.77 | 9720.77 | 0 | 0 | 0 | 0
2022030211 | 4 | 0.51005 | 40804 | 0 | 0 | 0.04281 | 1498.35 | 0.79194 | 11087.16 | 40000 | 0 | 804 | 694.35 | 0 | 11087.16 | 11781.51 | 0 | 0 | 0 | 0
2022030212 | 4 | 0.49966 | 39972.8 | 0 | 0 | 0.03684 | 1289.4 | 0.77189 | 10806.46 | 39972.8 | 27.2 | 0 | 1289.4 | 0 | 10806.46 | 12123.06 | 0 | 0 | 0 | 0
2022030213 | 4 | 0.4932 | 39456 | 0 | 0 | 0.04066 | 1423.1 | 0.77505 | 10850.7 | 39456 | 544 | 0 | 1423.1 | 0 | 10850.7 | 12817.8 | 0 | 0 | 0 | 0
2022030214 | 4 | 0.49352 | 39481.6 | 0 | 0 | 0.05635 | 1972.25 | 0.77448 | 10842.72 | 39481.6 | 518.4 | 0 | 1972.25 | 0 | 10842.72 | 13333.37 | 0 | 0 | 0 | 0
2022030215 | 4 | 0.49547 | 39637.6 | 0 | 0 | 0.06745 | 2360.75 | 0.76042 | 10645.88 | 39637.6 | 362.4 | 0 | 2360.75 | 0 | 10645.88 | 13369.03 | 0 | 0 | 0 | 0
2022030216 | 4 | 0.49851 | 39880.8 | 0 | 0 | 0.07766 | 2718.1 | 0.7404 | 10365.6 | 39880.8 | 119.2 | 0 | 2718.1 | 0 | 10365.6 | 13202.9 | 0 | 0 | 0 | 0
2022030217 | 4 | 0.50346 | 40276.8 | 0 | 0 | 0.08782 | 3073.7 | 0.65162 | 9122.68 | 40000 | 0 | 276.8 | 2796.9 | 0 | 9122.68 | 11919.58 | 0 | 0 | 0 | 0
2022030218 | 4 | 0.50684 | 40547.2 | 0 | 0 | 0.09839 | 3443.65 | 0.37668 | 5273.52 | 40000 | 0 | 547.2 | 2896.45 | 0 | 5273.52 | 8169.97 | 0 | 0 | 0 | 0
2022030219 | 4 | 0.51582 | 41265.6 | 0 | 0 | 0.12593 | 4407.55 | 0.04813 | 673.82 | 40000 | 0 | 1265.6 | 3141.95 | 0 | 673.82 | 3815.77 | 0 | 0 | 0 | 0
2022030220 | 4 | 0.52328 | 41862.4 | 0 | 0 | 0.18639 | 6523.65 | 6e-05 | 0.84 | 40000 | 0 | 1862.4 | 4661.25 | 0 | 0.84 | 4662.09 | 0 | 0 | 0 | 0
2022030221 | 4 | 0.51511 | 41208.8 | 0 | 0 | 0.26249 | 9187.15 | 6e-05 | 0.84 | 40000 | 0 | 1208.8 | 7978.35 | 0 | 0.84 | 7979.19 | 0 | 0 | 0 | 0
2022030222 | 4 | 0.49902 | 39921.6 | 0 | 0 | 0.32148 | 11251.8 | 0 | 0 | 39921.6 | 78.4 | 0 | 11251.8 | 0 | 0 | 11330.2 | 0 | 0 | 0 | 0
2022030223 | 4 | 0.47276 | 37820.8 | 0 | 0 | 0.35349 | 12372.15 | 0 | 0 | 37820.8 | 2179.2 | 0 | 12372.15 | 0 | 0 | 14551.35 | 0 | 0 | 0 | 0
2022030224 | 4 | 0.44617 | 35693.6 | 0 | 0 | 0.37012 | 12954.2 | 0 | 0 | 35693.6 | 4306.4 | 0 | 12954.2 | 0 | 0 | 17260.6 | 0 | 0 | 0 | 0
2022030301 | 5 | 0.42723 | 34178.4 | 0 | 0 | 0.35863 | 12552.05 | 0 | 0 | 34178.4 | 5821.6 | 0 | 12552.05 | 0 | 0 | 18373.65 | 0 | 0 | 0 | 0
2022030302 | 5 | 0.41755 | 33404 | 0 | 0 | 0.34059 | 11920.65 | 0 | 0 | 33404 | 6596 | 0 | 11920.65 | 0 | 0 | 18516.65 | 0 | 0 | 0 | 0
2022030303 | 5 | 0.4152 | 33216 | 0 | 0 | 0.29872 | 10455.2 | 0 | 0 | 33216 | 6784 | 0 | 10455.2 | 0 | 0 | 17239.2 | 0 | 0 | 0 | 0
2022030304 | 5 | 0.41846 | 33476.8 | 0 | 0 | 0.26379 | 9232.65 | 0 | 0 | 33476.8 | 6523.2 | 0 | 9232.65 | 0 | 0 | 15755.85 | 0 | 0 | 0 | 0
2022030305 | 5 | 0.43152 | 34521.6 | 0 | 0 | 0.24805 | 8681.75 | 0 | 0 | 34521.6 | 5478.4 | 0 | 8681.75 | 0 | 0 | 14160.15 | 0 | 0 | 0 | 0
2022030306 | 5 | 0.46244 | 36995.2 | 0 | 0 | 0.21095 | 7383.25 | 0 | 0 | 36995.2 | 3004.8 | 0 | 7383.25 | 0 | 0 | 10388.05 | 0 | 0 | 0 | 0
2022030307 | 5 | 0.50815 | 40652 | 0 | 0 | 0.17536 | 6137.6 | 6e-05 | 0.84 | 40000 | 0 | 652 | 5485.6 | 0 | 0.84 | 5486.44 | 0 | 0 | 0 | 0
2022030308 | 5 | 0.52253 | 41802.4 | 0 | 0 | 0.15743 | 5510.05 | 0.07484 | 1047.76 | 40000 | 0 | 1802.4 | 3707.65 | 0 | 1047.76 | 4755.41 | 0 | 0 | 0 | 0
2022030309 | 5 | 0.51696 | 41356.8 | 0 | 0 | 0.12414 | 4344.9 | 0.52476 | 7346.64 | 40000 | 0 | 1356.8 | 2988.1 | 0 | 7346.64 | 10334.74 | 0 | 0 | 0 | 0
2022030310 | 5 | 0.50785 | 40628 | 0 | 0 | 0.06912 | 2419.2 | 0.75454 | 10563.56 | 40000 | 0 | 628 | 1791.2 | 0 | 10563.56 | 12354.76 | 0 | 0 | 0 | 0
2022030311 | 5 | 0.50206 | 40164.8 | 0 | 0 | 0.07532 | 2636.2 | 0.75343 | 10548.02 | 40000 | 0 | 164.8 | 2471.4 | 0 | 10548.02 | 13019.42 | 0 | 0 | 0 | 0
2022030312 | 5 | 0.50148 | 40118.4 | 0 | 0 | 0.06834 | 2391.9 | 0.76217 | 10670.38 | 40000 | 0 | 118.4 | 2273.5 | 0 | 10670.38 | 12943.88 | 0 | 0 | 0 | 0
2022030313 | 5 | 0.50377 | 40301.6 | 0 | 0 | 0.08953 | 3133.55 | 0.75517 | 10572.38 | 40000 | 0 | 301.6 | 2831.95 | 0 | 10572.38 | 13404.33 | 0 | 0 | 0 | 0
2022030314 | 5 | 0.50918 | 40734.4 | 0 | 0 | 0.13003 | 4551.05 | 0.70692 | 9896.88 | 40000 | 0 | 734.4 | 3816.65 | 0 | 9896.88 | 13713.53 | 0 | 0 | 0 | 0
2022030315 | 5 | 0.51585 | 41268 | 0 | 0 | 0.15753 | 5513.55 | 0.70945 | 9932.3 | 40000 | 0 | 1268 | 4245.55 | 0 | 9932.3 | 14177.85 | 0 | 0 | 0 | 0
2022030316 | 5 | 0.52102 | 41681.6 | 0 | 0 | 0.1768 | 6188 | 0.67547 | 9456.58 | 40000 | 0 | 1681.6 | 4506.4 | 0 | 9456.58 | 13962.98 | 0 | 0 | 0 | 0
2022030317 | 5 | 0.52482 | 41985.6 | 0 | 0 | 0.20566 | 7198.1 | 0.54028 | 7563.92 | 40000 | 0 | 1985.6 | 5212.5 | 0 | 7563.92 | 12776.42 | 0 | 0 | 0 | 0
2022030318 | 5 | 0.52534 | 42027.2 | 0 | 0 | 0.21952 | 7683.2 | 0.2357 | 3299.8 | 40000 | 0 | 2027.2 | 5656 | 0 | 3299.8 | 8955.8 | 0 | 0 | 0 | 0
2022030319 | 5 | 0.53039 | 42431.2 | 0 | 0 | 0.24003 | 8401.05 | 0.02356 | 329.84 | 40000 | 0 | 2431.2 | 5969.85 | 0 | 329.84 | 6299.69 | 0 | 0 | 0 | 0
2022030320 | 5 | 0.53565 | 42852 | 0 | 0 | 0.31477 | 11016.95 | 0 | 0 | 40000 | 0 | 2852 | 8164.95 | 0 | 0 | 8164.95 | 0 | 0 | 0 | 0
2022030321 | 5 | 0.5276 | 42208 | 0 | 0 | 0.4328 | 15148 | 0 | 0 | 40000 | 0 | 2208 | 12940 | 0 | 0 | 12940 | 0 | 0 | 0 | 0
2022030322 | 5 | 0.51015 | 40812 | 0 | 0 | 0.50678 | 17737.3 | 0 | 0 | 40000 | 0 | 812 | 16925.3 | 0 | 0 | 16925.3 | 0 | 0 | 0 | 0
2022030323 | 5 | 0.4839 | 38712 | 0 | 0 | 0.52471 | 18364.85 | 0 | 0 | 38712 | 1288 | 0 | 18364.85 | 0 | 0 | 19652.85 | 0 | 0 | 0 | 0
2022030324 | 5 | 0.4549 | 36392 | 0 | 0 | 0.51479 | 18017.65 | 0 | 0 | 36392 | 3608 | 0 | 18017.65 | 0 | 0 | 21625.65 | 0 | 0 | 0 | 0
2022030401 | 6 | 0.43322 | 34657.6 | 0 | 0 | 0.51744 | 18110.4 | 0 | 0 | 34657.6 | 5342.4 | 0 | 18110.4 | 0 | 0 | 23452.8 | 0 | 0 | 0 | 0
2022030402 | 6 | 0.41905 | 33524 | 0 | 0 | 0.51761 | 18116.35 | 0 | 0 | 33524 | 6476 | 0 | 18116.35 | 0 | 0 | 24592.35 | 0 | 0 | 0 | 0
2022030403 | 6 | 0.41252 | 33001.6 | 0 | 0 | 0.51449 | 18007.15 | 0 | 0 | 33001.6 | 6998.4 | 0 | 18007.15 | 0 | 0 | 25005.55 | 0 | 0 | 0 | 0
2022030404 | 6 | 0.41183 | 32946.4 | 0 | 0 | 0.5146 | 18011 | 0 | 0 | 32946.4 | 7053.6 | 0 | 18011 | 0 | 0 | 25064.6 | 0 | 0 | 0 | 0
2022030405 | 6 | 0.41974 | 33579.2 | 0 | 0 | 0.51938 | 18178.3 | 0 | 0 | 33579.2 | 6420.8 | 0 | 18178.3 | 0 | 0 | 24599.1 | 0 | 0 | 0 | 0
2022030406 | 6 | 0.44303 | 35442.4 | 0 | 0 | 0.53828 | 18839.8 | 0 | 0 | 35442.4 | 4557.6 | 0 | 18839.8 | 0 | 0 | 23397.4 | 0 | 0 | 0 | 0
2022030407 | 6 | 0.48199 | 38559.2 | 0 | 0 | 0.56712 | 19849.2 | 6e-05 | 0.84 | 38559.2 | 1440.8 | 0 | 19849.2 | 0 | 0.84 | 21290.84 | 0 | 0 | 0 | 0
2022030408 | 6 | 0.49967 | 39973.6 | 0 | 0 | 0.56105 | 19636.75 | 0.03595 | 503.3 | 39973.6 | 26.4 | 0 | 19636.75 | 0 | 503.3 | 20166.45 | 0 | 0 | 0 | 0
2022030409 | 6 | 0.50672 | 40537.6 | 0 | 0 | 0.51816 | 18135.6 | 0.25483 | 3567.62 | 40000 | 0 | 537.6 | 17598 | 0 | 3567.62 | 21165.62 | 0 | 0 | 0 | 0
2022030410 | 6 | 0.51617 | 41293.6 | 0 | 0 | 0.54852 | 19198.2 | 0.30847 | 4318.58 | 40000 | 0 | 1293.6 | 17904.6 | 0 | 4318.58 | 22223.18 | 0 | 0 | 0 | 0
2022030411 | 6 | 0.51888 | 41510.4 | 0 | 0 | 0.56958 | 19935.3 | 0.27013 | 3781.82 | 40000 | 0 | 1510.4 | 18424.9 | 0 | 3781.82 | 22206.72 | 0 | 0 | 0 | 0
2022030412 | 6 | 0.52263 | 41810.4 | 0 | 0 | 0.56856 | 19899.6 | 0.23712 | 3319.68 | 40000 | 0 | 1810.4 | 18089.2 | 0 | 3319.68 | 21408.88 | 0 | 0 | 0 | 0
2022030413 | 6 | 0.52442 | 41953.6 | 0 | 0 | 0.57407 | 20092.45 | 0.24979 | 3497.06 | 40000 | 0 | 1953.6 | 18138.85 | 0 | 3497.06 | 21635.91 | 0 | 0 | 0 | 0
2022030414 | 6 | 0.52744 | 42195.2 | 0 | 0 | 0.57107 | 19987.45 | 0.29326 | 4105.64 | 40000 | 0 | 2195.2 | 17792.25 | 0 | 4105.64 | 21897.89 | 0 | 0 | 0 | 0
2022030415 | 6 | 0.52899 | 42319.2 | 0 | 0 | 0.5738 | 20083 | 0.3147 | 4405.8 | 40000 | 0 | 2319.2 | 17763.8 | 0 | 4405.8 | 22169.6 | 0 | 0 | 0 | 0
2022030416 | 6 | 0.53017 | 42413.6 | 0 | 0 | 0.58838 | 20593.3 | 0.24723 | 3461.22 | 40000 | 0 | 2413.6 | 18179.7 | 0 | 3461.22 | 21640.92 | 0 | 0 | 0 | 0
2022030417 | 6 | 0.53099 | 42479.2 | 0 | 0 | 0.60569 | 21199.15 | 0.13648 | 1910.72 | 40000 | 0 | 2479.2 | 18719.95 | 0 | 1910.72 | 20630.67 | 0 | 0 | 0 | 0
2022030418 | 6 | 0.52961 | 42368.8 | 0 | 0 | 0.62302 | 21805.7 | 0.06731 | 942.34 | 40000 | 0 | 2368.8 | 19436.9 | 0 | 942.34 | 20379.24 | 0 | 0 | 0 | 0
2022030419 | 6 | 0.53148 | 42518.4 | 0 | 0 | 0.61845 | 21645.75 | 0.01192 | 166.88 | 40000 | 0 | 2518.4 | 19127.35 | 0 | 166.88 | 19294.23 | 0 | 0 | 0 | 0
2022030420 | 6 | 0.53207 | 42565.6 | 0 | 0 | 0.63239 | 22133.65 | 0 | 0 | 40000 | 0 | 2565.6 | 19568.05 | 0 | 0 | 19568.05 | 0 | 0 | 0 | 0
2022030421 | 6 | 0.5209 | 41672 | 0 | 0 | 0.63467 | 22213.45 | 0 | 0 | 40000 | 0 | 1672 | 20541.45 | 0 | 0 | 20541.45 | 0 | 0 | 0 | 0
2022030422 | 6 | 0.50822 | 40657.6 | 0 | 0 | 0.64519 | 22581.65 | 0 | 0 | 40000 | 0 | 657.6 | 21924.05 | 0 | 0 | 21924.05 | 0 | 0 | 0 | 0
2022030423 | 6 | 0.48875 | 39100 | 0 | 0 | 0.63017 | 22055.95 | 0 | 0 | 39100 | 900 | 0 | 22055.95 | 0 | 0 | 22955.95 | 0 | 0 | 0 | 0
2022030424 | 6 | 0.46498 | 37198.4 | 0 | 0 | 0.6188 | 21658 | 0 | 0 | 37198.4 | 2801.6 | 0 | 21658 | 0 | 0 | 24459.6 | 0 | 0 | 0 | 0
2022030501 | 7 | 0.44424 | 35539.2 | 0 | 0 | 0.6124 | 21434 | 0 | 0 | 35539.2 | 4460.8 | 0 | 21434 | 0 | 0 | 25894.8 | 0 | 0 | 0 | 0
2022030502 | 7 | 0.4295 | 34360 | 0 | 0 | 0.60622 | 21217.7 | 0 | 0 | 34360 | 5640 | 0 | 21217.7 | 0 | 0 | 26857.7 | 0 | 0 | 0 | 0
2022030503 | 7 | 0.42046 | 33636.8 | 0 | 0 | 0.59715 | 20900.25 | 0 | 0 | 33636.8 | 6363.2 | 0 | 20900.25 | 0 | 0 | 27263.45 | 0 | 0 | 0 | 0
2022030504 | 7 | 0.4153 | 33224 | 0 | 0 | 0.58634 | 20521.9 | 0 | 0 | 33224 | 6776 | 0 | 20521.9 | 0 | 0 | 27297.9 | 0 | 0 | 0 | 0
2022030505 | 7 | 0.41444 | 33155.2 | 0 | 0 | 0.57306 | 20057.1 | 0 | 0 | 33155.2 | 6844.8 | 0 | 20057.1 | 0 | 0 | 26901.9 | 0 | 0 | 0 | 0
2022030506 | 7 | 0.42165 | 33732 | 0 | 0 | 0.57004 | 19951.4 | 0 | 0 | 33732 | 6268 | 0 | 19951.4 | 0 | 0 | 26219.4 | 0 | 0 | 0 | 0
2022030507 | 7 | 0.43456 | 34764.8 | 0 | 0 | 0.56996 | 19948.6 | 0.0001 | 1.4 | 34764.8 | 5235.2 | 0 | 19948.6 | 0 | 1.4 | 25185.2 | 0 | 0 | 0 | 0
2022030508 | 7 | 0.44942 | 35953.6 | 0 | 0 | 0.54574 | 19100.9 | 0.05993 | 839.02 | 35953.6 | 4046.4 | 0 | 19100.9 | 0 | 839.02 | 23986.32 | 0 | 0 | 0 | 0
2022030509 | 7 | 0.47248 | 37798.4 | 0 | 0 | 0.47871 | 16754.85 | 0.40553 | 5677.42 | 37798.4 | 2201.6 | 0 | 16754.85 | 0 | 5677.42 | 24633.87 | 0 | 0 | 0 | 0
2022030510 | 7 | 0.49416 | 39532.8 | 0 | 0 | 0.49132 | 17196.2 | 0.53097 | 7433.58 | 39532.8 | 467.2 | 0 | 17196.2 | 0 | 7433.58 | 25096.98 | 0 | 0 | 0 | 0
2022030511 | 7 | 0.51103 | 40882.4 | 0 | 0 | 0.53561 | 18746.35 | 0.44679 | 6255.06 | 40000 | 0 | 882.4 | 17863.95 | 0 | 6255.06 | 24119.01 | 0 | 0 | 0 | 0
2022030512 | 7 | 0.52356 | 41884.8 | 0 | 0 | 0.55274 | 19345.9 | 0.38233 | 5352.62 | 40000 | 0 | 1884.8 | 17461.1 | 0 | 5352.62 | 22813.72 | 0 | 0 | 0 | 0
2022030513 | 7 | 0.52872 | 42297.6 | 0 | 0 | 0.55676 | 19486.6 | 0.33446 | 4682.44 | 40000 | 0 | 2297.6 | 17189 | 0 | 4682.44 | 21871.44 | 0 | 0 | 0 | 0
2022030514 | 7 | 0.53031 | 42424.8 | 0 | 0 | 0.5501 | 19253.5 | 0.33176 | 4644.64 | 40000 | 0 | 2424.8 | 16828.7 | 0 | 4644.64 | 21473.34 | 0 | 0 | 0 | 0
2022030515 | 7 | 0.53149 | 42519.2 | 0 | 0 | 0.52221 | 18277.35 | 0.38316 | 5364.24 | 40000 | 0 | 2519.2 | 15758.15 | 0 | 5364.24 | 21122.39 | 0 | 0 | 0 | 0
2022030516 | 7 | 0.53571 | 42856.8 | 0 | 0 | 0.50699 | 17744.65 | 0.35618 | 4986.52 | 40000 | 0 | 2856.8 | 14887.85 | 0 | 4986.52 | 19874.37 | 0 | 0 | 0 | 0
2022030517 | 7 | 0.53852 | 43081.6 | 0 | 0 | 0.50479 | 17667.65 | 0.29858 | 4180.12 | 40000 | 0 | 3081.6 | 14586.05 | 0 | 4180.12 | 18766.17 | 0 | 0 | 0 | 0
2022030518 | 7 | 0.53521 | 42816.8 | 0 | 0 | 0.47123 | 16493.05 | 0.29242 | 4093.88 | 40000 | 0 | 2816.8 | 13676.25 | 0 | 4093.88 | 17770.13 | 0 | 0 | 0 | 0
2022030519 | 7 | 0.5348 | 42784 | 0 | 0 | 0.39197 | 13718.95 | 0.06636 | 929.04 | 40000 | 0 | 2784 | 10934.95 | 0 | 929.04 | 11863.99 | 0 | 0 | 0 | 0
2022030520 | 7 | 0.53641 | 42912.8 | 0 | 0 | 0.35404 | 12391.4 | 0 | 0 | 40000 | 0 | 2912.8 | 9478.6 | 0 | 0 | 9478.6 | 0 | 0 | 0 | 0
2022030521 | 7 | 0.52337 | 41869.6 | 0 | 0 | 0.34292 | 12002.2 | 0 | 0 | 40000 | 0 | 1869.6 | 10132.6 | 0 | 0 | 10132.6 | 0 | 0 | 0 | 0
2022030522 | 7 | 0.50941 | 40752.8 | 0 | 0 | 0.3571 | 12498.5 | 0 | 0 | 40000 | 0 | 752.8 | 11745.7 | 0 | 0 | 11745.7 | 0 | 0 | 0 | 0
2022030523 | 7 | 0.4923 | 39384 | 0 | 0 | 0.40762 | 14266.7 | 0 | 0 | 39384 | 616 | 0 | 14266.7 | 0 | 0 | 14882.7 | 0 | 0 | 0 | 0
2022030524 | 7 | 0.47398 | 37918.4 | 0 | 0 | 0.51389 | 17986.15 | 0 | 0 | 37918.4 | 2081.6 | 0 | 17986.15 | 0 | 0 | 20067.75 | 0 | 0 | 0 | 0
2022030601 | 1 | 0.45575 | 36460 | 0 | 0 | 0.59235 | 20732.25 | 0 | 0 | 36460 | 3540 | 0 | 20732.25 | 0 | 0 | 24272.25 | 0 | 0 | 0 | 0
2022030602 | 1 | 0.43988 | 35190.4 | 0 | 0 | 0.60972 | 21340.2 | 0 | 0 | 35190.4 | 4809.6 | 0 | 21340.2 | 0 | 0 | 26149.8 | 0 | 0 | 0 | 0
2022030603 | 1 | 0.42897 | 34317.6 | 0 | 0 | 0.60705 | 21246.75 | 0 | 0 | 34317.6 | 5682.4 | 0 | 21246.75 | 0 | 0 | 26929.15 | 0 | 0 | 0 | 0
2022030604 | 1 | 0.42184 | 33747.2 | 0 | 0 | 0.59932 | 20976.2 | 0 | 0 | 33747.2 | 6252.8 | 0 | 20976.2 | 0 | 0 | 27229 | 0 | 0 | 0 | 0
2022030605 | 1 | 0.41913 | 33530.4 | 0 | 0 | 0.58424 | 20448.4 | 0 | 0 | 33530.4 | 6469.6 | 0 | 20448.4 | 0 | 0 | 26918 | 0 | 0 | 0 | 0
2022030606 | 1 | 0.42133 | 33706.4 | 0 | 0 | 0.57657 | 20179.95 | 0 | 0 | 33706.4 | 6293.6 | 0 | 20179.95 | 0 | 0 | 26473.55 | 0 | 0 | 0 | 0
2022030607 | 1 | 0.42766 | 34212.8 | 0 | 0 | 0.5523 | 19330.5 | 0 | 0 | 34212.8 | 5787.2 | 0 | 19330.5 | 0 | 0 | 25117.7 | 0 | 0 | 0 | 0
2022030608 | 1 | 0.43713 | 34970.4 | 0 | 0 | 0.56147 | 19651.45 | 0.03339 | 467.46 | 34970.4 | 5029.6 | 0 | 19651.45 | 0 | 467.46 | 25148.51 | 0 | 0 | 0 | 0
2022030609 | 1 | 0.46321 | 37056.8 | 0 | 0 | 0.56812 | 19884.2 | 0.2423 | 3392.2 | 37056.8 | 2943.2 | 0 | 19884.2 | 0 | 3392.2 | 26219.6 | 0 | 0 | 0 | 0
2022030610 | 1 | 0.48839 | 39071.2 | 0 | 0 | 0.55321 | 19362.35 | 0.38015 | 5322.1 | 39071.2 | 928.8 | 0 | 19362.35 | 0 | 5322.1 | 25613.25 | 0 | 0 | 0 | 0
2022030611 | 1 | 0.50742 | 40593.6 | 0 | 0 | 0.49998 | 17499.3 | 0.53907 | 7546.98 | 40000 | 0 | 593.6 | 16905.7 | 0 | 7546.98 | 24452.68 | 0 | 0 | 0 | 0
2022030612 | 1 | 0.52195 | 41756 | 0 | 0 | 0.46715 | 16350.25 | 0.57447 | 8042.58 | 40000 | 0 | 1756 | 14594.25 | 0 | 8042.58 | 22636.83 | 0 | 0 | 0 | 0
2022030613 | 1 | 0.53169 | 42535.2 | 0 | 0 | 0.44321 | 15512.35 | 0.60779 | 8509.06 | 40000 | 0 | 2535.2 | 12977.15 | 0 | 8509.06 | 21486.21 | 0 | 0 | 0 | 0
2022030614 | 1 | 0.53815 | 43052 | 0 | 0 | 0.43799 | 15329.65 | 0.60983 | 8537.62 | 40000 | 0 | 3052 | 12277.65 | 0 | 8537.62 | 20815.27 | 0 | 0 | 0 | 0
2022030615 | 1 | 0.54081 | 43264.8 | 0 | 0 | 0.45822 | 16037.7 | 0.58489 | 8188.46 | 40000 | 0 | 3264.8 | 12772.9 | 0 | 8188.46 | 20961.36 | 0 | 0 | 0 | 0
2022030616 | 1 | 0.54364 | 43491.2 | 0 | 0 | 0.50932 | 17826.2 | 0.44288 | 6200.32 | 40000 | 0 | 3491.2 | 14335 | 0 | 6200.32 | 20535.32 | 0 | 0 | 0 | 0
2022030617 | 1 | 0.54663 | 43730.4 | 0 | 0 | 0.5513 | 19295.5 | 0.30234 | 4232.76 | 40000 | 0 | 3730.4 | 15565.1 | 0 | 4232.76 | 19797.86 | 0 | 0 | 0 | 0
2022030618 | 1 | 0.54758 | 43806.4 | 0 | 0 | 0.57796 | 20228.6 | 0.17566 | 2459.24 | 40000 | 0 | 3806.4 | 16422.2 | 0 | 2459.24 | 18881.44 | 0 | 0 | 0 | 0
2022030619 | 1 | 0.55224 | 44179.2 | 0 | 0 | 0.59825 | 20938.75 | 0.04334 | 606.76 | 40000 | 0 | 4179.2 | 16759.55 | 0 | 606.76 | 17366.31 | 0 | 0 | 0 | 0
2022030620 | 1 | 0.55865 | 44692 | 0 | 0 | 0.61169 | 21409.15 | 0 | 0 | 40000 | 0 | 4692 | 16717.15 | 0 | 0 | 16717.15 | 0 | 0 | 0 | 0
2022030621 | 1 | 0.55027 | 44021.6 | 0 | 0 | 0.61908 | 21667.8 | 0 | 0 | 40000 | 0 | 4021.6 | 17646.2 | 0 | 0 | 17646.2 | 0 | 0 | 0 | 0
2022030622 | 1 | 0.53396 | 42716.8 | 0 | 0 | 0.6038 | 21133 | 0 | 0 | 40000 | 0 | 2716.8 | 18416.2 | 0 | 0 | 18416.2 | 0 | 0 | 0 | 0
2022030623 | 1 | 0.50962 | 40769.6 | 0 | 0 | 0.59062 | 20671.7 | 0 | 0 | 40000 | 0 | 769.6 | 19902.1 | 0 | 0 | 19902.1 | 0 | 0 | 0 | 0
2022030624 | 1 | 0.48314 | 38651.2 | 0 | 0 | 0.58724 | 20553.4 | 0 | 0 | 38651.2 | 1348.8 | 0 | 20553.4 | 0 | 0 | 21902.2 | 0 | 0 | 0 | 0
2022030701 | 2 | 0.46147 | 36917.6 | 0 | 0 | 0.58102 | 20335.7 | 0 | 0 | 36917.6 | 3082.4 | 0 | 20335.7 | 0 | 0 | 23418.1 | 0 | 0 | 0 | 0
2022030702 | 2 | 0.4478 | 35824 | 0 | 0 | 0.58907 | 20617.45 | 0 | 0 | 35824 | 4176 | 0 | 20617.45 | 0 | 0 | 24793.45 | 0 | 0 | 0 | 0
2022030703 | 2 | 0.44169 | 35335.2 | 0 | 0 | 0.5916 | 20706 | 0 | 0 | 35335.2 | 4664.8 | 0 | 20706 | 0 | 0 | 25370.8 | 0 | 0 | 0 | 0
2022030704 | 2 | 0.44539 | 35631.2 | 0 | 0 | 0.58908 | 20617.8 | 0 | 0 | 35631.2 | 4368.8 | 0 | 20617.8 | 0 | 0 | 24986.6 | 0 | 0 | 0 | 0
2022030705 | 2 | 0.45776 | 36620.8 | 0 | 0 | 0.57555 | 20144.25 | 0 | 0 | 36620.8 | 3379.2 | 0 | 20144.25 | 0 | 0 | 23523.45 | 0 | 0 | 0 | 0
2022030706 | 2 | 0.48621 | 38896.8 | 0 | 0 | 0.54722 | 19152.7 | 0 | 0 | 38896.8 | 1103.2 | 0 | 19152.7 | 0 | 0 | 20255.9 | 0 | 0 | 0 | 0
2022030707 | 2 | 0.53334 | 42667.2 | 0 | 0 | 0.53052 | 18568.2 | 0 | 0 | 40000 | 0 | 2667.2 | 15901 | 0 | 0 | 15901 | 0 | 0 | 0 | 0
2022030708 | 2 | 0.56127 | 44901.6 | 0 | 0 | 0.53473 | 18715.55 | 0.06254 | 875.56 | 40000 | 0 | 4901.6 | 13813.95 | 0 | 875.56 | 14689.51 | 0 | 0 | 0 | 0
2022030709 | 2 | 0.57557 | 46045.6 | 0 | 0 | 0.5232 | 18312 | 0.3588 | 5023.2 | 40000 | 0 | 6045.6 | 12266.4 | 0 | 5023.2 | 17289.6 | 0 | 0 | 0 | 0
2022030710 | 2 | 0.58428 | 46742.4 | 0 | 0 | 0.54662 | 19131.7 | 0.346 | 4844 | 40000 | 0 | 6742.4 | 12389.3 | 0 | 4844 | 17233.3 | 0 | 0 | 0 | 0
2022030711 | 2 | 0.58566 | 46852.8 | 0 | 0 | 0.48798 | 17079.3 | 0.55163 | 7722.82 | 40000 | 0 | 6852.8 | 10226.5 | 0 | 7722.82 | 17949.32 | 0 | 0 | 0 | 0
2022030712 | 2 | 0.58084 | 46467.2 | 0 | 0 | 0.42359 | 14825.65 | 0.71908 | 10067.12 | 40000 | 0 | 6467.2 | 8358.45 | 0 | 10067.12 | 18425.57 | 0 | 0 | 0 | 0
2022030713 | 2 | 0.57063 | 45650.4 | 0 | 0 | 0.34414 | 12044.9 | 0.72571 | 10159.94 | 40000 | 0 | 5650.4 | 6394.5 | 0 | 10159.94 | 16554.44 | 0 | 0 | 0 | 0
2022030714 | 2 | 0.55877 | 44701.6 | 0 | 0 | 0.29431 | 10300.85 | 0.72021 | 10082.94 | 40000 | 0 | 4701.6 | 5599.25 | 0 | 10082.94 | 15682.19 | 0 | 0 | 0 | 0
2022030715 | 2 | 0.54528 | 43622.4 | 0 | 0 | 0.26133 | 9146.55 | 0.70853 | 9919.42 | 40000 | 0 | 3622.4 | 5524.15 | 0 | 9919.42 | 15443.57 | 0 | 0 | 0 | 0
2022030716 | 2 | 0.53646 | 42916.8 | 0 | 0 | 0.24966 | 8738.1 | 0.6847 | 9585.8 | 40000 | 0 | 2916.8 | 5821.3 | 0 | 9585.8 | 15407.1 | 0 | 0 | 0 | 0
2022030717 | 2 | 0.53922 | 43137.6 | 0 | 0 | 0.23996 | 8398.6 | 0.61789 | 8650.46 | 40000 | 0 | 3137.6 | 5261 | 0 | 8650.46 | 13911.46 | 0 | 0 | 0 | 0
2022030718 | 2 | 0.55048 | 44038.4 | 0 | 0 | 0.23269 | 8144.15 | 0.39526 | 5533.64 | 40000 | 0 | 4038.4 | 4105.75 | 0 | 5533.64 | 9639.39 | 0 | 0 | 0 | 0
2022030719 | 2 | 0.57804 | 46243.2 | 0 | 0 | 0.21848 | 7646.8 | 0.05446 | 762.44 | 40000 | 0 | 6243.2 | 1403.6 | 0 | 762.44 | 2166.04 | 0 | 0 | 0 | 0
2022030720 | 2 | 0.59508 | 47606.4 | 0 | 0 | 0.23938 | 8378.3 | 0 | 0 | 40000 | 0 | 7606.4 | 771.9 | 0 | 0 | 771.9 | 0 | 0 | 0 | 0
2022030721 | 2 | 0.5912 | 47296 | 0 | 0 | 0.28581 | 10003.35 | 0 | 0 | 40000 | 0 | 7296 | 2707.35 | 0 | 0 | 2707.35 | 0 | 0 | 0 | 0
2022030722 | 2 | 0.57558 | 46046.4 | 0 | 0 | 0.31566 | 11048.1 | 0 | 0 | 40000 | 0 | 6046.4 | 5001.7 | 0 | 0 | 5001.7 | 0 | 0 | 0 | 0
2022030723 | 2 | 0.55093 | 44074.4 | 0 | 0 | 0.3402 | 11907 | 0 | 0 | 40000 | 0 | 4074.4 | 7832.6 | 0 | 0 | 7832.6 | 0 | 0 | 0 | 0
2022030724 | 2 | 0.52836 | 42268.8 | 0 | 0 | 0.3368 | 11788 | 0 | 0 | 40000 | 0 | 2268.8 | 9519.2 | 0 | 0 | 9519.2 | 0 | 0 | 0 | 0
2022030801 | 3 | 0.51421 | 41136.8 | 0 | 0 | 0.2903 | 10160.5 | 0 | 0 | 40000 | 0 | 1136.8 | 9023.7 | 0 | 0 | 9023.7 | 0 | 0 | 0 | 0
2022030802 | 3 | 0.51001 | 40800.8 | 0 | 0 | 0.25647 | 8976.45 | 0 | 0 | 40000 | 0 | 800.8 | 8175.65 | 0 | 0 | 8175.65 | 0 | 0 | 0 | 0
2022030803 | 3 | 0.50831 | 40664.8 | 0 | 0 | 0.23747 | 8311.45 | 0 | 0 | 40000 | 0 | 664.8 | 7646.65 | 0 | 0 | 7646.65 | 0 | 0 | 0 | 0
2022030804 | 3 | 0.51442 | 41153.6 | 0 | 0 | 0.21295 | 7453.25 | 0 | 0 | 40000 | 0 | 1153.6 | 6299.65 | 0 | 0 | 6299.65 | 0 | 0 | 0 | 0
2022030805 | 3 | 0.53039 | 42431.2 | 0 | 0 | 0.21253 | 7438.55 | 0 | 0 | 40000 | 0 | 2431.2 | 5007.35 | 0 | 0 | 5007.35 | 0 | 0 | 0 | 0
2022030806 | 3 | 0.56359 | 45087.2 | 0 | 0 | 0.2047 | 7164.5 | 0 | 0 | 40000 | 0 | 5087.2 | 2077.3 | 0 | 0 | 2077.3 | 0 | 0 | 0 | 0
2022030807 | 3 | 0.61356 | 49084.8 | 0 | 0 | 0.17261 | 6041.35 | 0.00022 | 3.08 | 40000 | 0 | 6041.35 | 0 | 3.08 | 0 | 0 | 3040.37 | 0 | 0 | 3040.37
2022030808 | 3 | 0.63452 | 50761.6 | 0 | 0 | 0.1426 | 4991 | 0.03867 | 541.38 | 40000 | 0 | 4991 | 0 | 541.38 | 0 | 0 | 5229.22 | 0 | 0 | 5229.22
2022030809 | 3 | 0.63481 | 50784.8 | 0 | 0 | 0.09499 | 3324.65 | 0.31248 | 4374.72 | 40000 | 0 | 3324.65 | 0 | 4374.72 | 0 | 0 | 3085.43 | 0 | 0 | 3085.43
2022030810 | 3 | 0.63543 | 50834.4 | 0 | 0 | 0.06731 | 2355.85 | 0.52608 | 7365.12 | 40000 | 0 | 2355.85 | 0 | 7365.12 | 0 | 0 | 1113.43 | 0 | 0 | 1113.43
2022030811 | 3 | 0.63482 | 50785.6 | 0 | 0 | 0.04975 | 1741.25 | 0.61028 | 8543.92 | 40000 | 0 | 1741.25 | 0 | 8543.92 | 0 | 0 | 500.43 | 0 | 0 | 500.43
2022030812 | 3 | 0.62582 | 50065.6 | 0 | 0 | 0.05449 | 1907.15 | 0.67233 | 9412.62 | 40000 | 0 | 1907.15 | 0 | 8158.45 | 1254.17 | 1254.17 | 0 | 0 | 0 | 0
2022030813 | 3 | 0.61313 | 49050.4 | 0 | 0 | 0.06465 | 2262.75 | 0.71247 | 9974.58 | 40000 | 0 | 2262.75 | 0 | 6787.65 | 3186.93 | 3186.93 | 0 | 0 | 0 | 0
2022030814 | 3 | 0.59988 | 47990.4 | 0 | 0 | 0.06105 | 2136.75 | 0.73189 | 10246.46 | 40000 | 0 | 2136.75 | 0 | 5853.65 | 4392.81 | 4392.81 | 0 | 0 | 0 | 0
2022030815 | 3 | 0.58113 | 46490.4 | 0 | 0 | 0.05588 | 1955.8 | 0.74468 | 10425.52 | 40000 | 0 | 1955.8 | 0 | 4534.6 | 5890.92 | 5890.92 | 0 | 0 | 0 | 0
2022030816 | 3 | 0.56782 | 45425.6 | 0 | 0 | 0.06793 | 2377.55 | 0.75731 | 10602.34 | 40000 | 0 | 2377.55 | 0 | 3048.05 | 7554.29 | 7554.29 | 0 | 0 | 0 | 0
2022030817 | 3 | 0.56452 | 45161.6 | 0 | 0 | 0.07857 | 2749.95 | 0.7652 | 10712.8 | 40000 | 0 | 2749.95 | 0 | 2411.65 | 8301.15 | 8301.15 | 0 | 0 | 0 | 0
2022030818 | 3 | 0.57277 | 45821.6 | 0 | 0 | 0.07134 | 2496.9 | 0.54073 | 7570.22 | 40000 | 0 | 2496.9 | 0 | 3324.7 | 4245.52 | 4245.52 | 0 | 0 | 0 | 0
2022030819 | 3 | 0.5976 | 47808 | 0 | 0 | 0.05743 | 2010.05 | 0.07921 | 1108.94 | 40000 | 0 | 2010.05 | 0 | 1108.94 | 0 | 0 | 4689.01 | 0 | 0 | 4689.01
2022030820 | 3 | 0.61823 | 49458.4 | 0 | 0 | 0.07197 | 2518.95 | 0 | 0 | 40000 | 0 | 2518.95 | 0 | 0 | 0 | 0 | 6939.45 | 0 | 0 | 6939.45
2022030821 | 3 | 0.61825 | 49460 | 0 | 0 | 0.10392 | 3637.2 | 0 | 0 | 40000 | 0 | 3637.2 | 0 | 0 | 0 | 0 | 5822.8 | 0 | 0 | 5822.8
2022030822 | 3 | 0.60639 | 48511.2 | 0 | 0 | 0.15205 | 5321.75 | 0 | 0 | 40000 | 0 | 5321.75 | 0 | 0 | 0 | 0 | 3189.45 | 0 | 0 | 3189.45
2022030823 | 3 | 0.58414 | 46731.2 | 0 | 0 | 0.18293 | 6402.55 | 0 | 0 | 40000 | 0 | 6402.55 | 0 | 0 | 0 | 0 | 328.65 | 0 | 0 | 328.65
2022030824 | 3 | 0.56298 | 45038.4 | 0 | 0 | 0.21121 | 7392.35 | 0 | 0 | 40000 | 0 | 5038.4 | 2353.95 | 0 | 0 | 2353.95 | 0 | 0 | 0 | 0
2022030901 | 4 | 0.55161 | 44128.8 | 0 | 0 | 0.21483 | 7519.05 | 0 | 0 | 40000 | 0 | 4128.8 | 3390.25 | 0 | 0 | 3390.25 | 0 | 0 | 0 | 0
2022030902 | 4 | 0.54762 | 43809.6 | 0 | 0 | 0.19616 | 6865.6 | 0 | 0 | 40000 | 0 | 3809.6 | 3056 | 0 | 0 | 3056 | 0 | 0 | 0 | 0
2022030903 | 4 | 0.55008 | 44006.4 | 0 | 0 | 0.18747 | 6561.45 | 0 | 0 | 40000 | 0 | 4006.4 | 2555.05 | 0 | 0 | 2555.05 | 0 | 0 | 0 | 0
2022030904 | 4 | 0.55861 | 44688.8 | 0 | 0 | 0.20136 | 7047.6 | 0 | 0 | 40000 | 0 | 4688.8 | 2358.8 | 0 | 0 | 2358.8 | 0 | 0 | 0 | 0
2022030905 | 4 | 0.57496 | 45996.8 | 0 | 0 | 0.21275 | 7446.25 | 0 | 0 | 40000 | 0 | 5996.8 | 1449.45 | 0 | 0 | 1449.45 | 0 | 0 | 0 | 0
2022030906 | 4 | 0.61281 | 49024.8 | 0 | 0 | 0.23315 | 8160.25 | 0 | 0 | 40000 | 0 | 8160.25 | 0 | 0 | 0 | 0 | 864.55 | 0 | 0 | 864.55
2022030907 | 4 | 0.66254 | 53003.2 | 0 | 0 | 0.25016 | 8755.6 | 0.0003 | 4.2 | 40000 | 0 | 8755.6 | 0 | 4.2 | 0 | 0 | 4243.4 | 0 | 0 | 4243.4
2022030908 | 4 | 0.67374 | 53899.2 | 0 | 0 | 0.24927 | 8724.45 | 0.12182 | 1705.48 | 40000 | 0 | 8724.45 | 0 | 1705.48 | 0 | 0 | 3469.27 | 0 | 0 | 3469.27
2022030909 | 4 | 0.64659 | 51727.2 | 0 | 0 | 0.20067 | 7023.45 | 0.63016 | 8822.24 | 40000 | 0 | 7023.45 | 0 | 4703.75 | 4118.49 | 4118.49 | 0 | 0 | 0 | 0
2022030910 | 4 | 0.61669 | 49335.2 | 0 | 0 | 0.21691 | 7591.85 | 0.83956 | 11753.84 | 40000 | 0 | 7591.85 | 0 | 1743.35 | 10010.49 | 10010.49 | 0 | 0 | 0 | 0
2022030911 | 4 | 0.59148 | 47318.4 | 0 | 0 | 0.25386 | 8885.1 | 0.84661 | 11852.54 | 40000 | 0 | 7318.4 | 1566.7 | 0 | 11852.54 | 13419.24 | 0 | 0 | 0 | 0
2022030912 | 4 | 0.56686 | 45348.8 | 0 | 0 | 0.26458 | 9260.3 | 0.84373 | 11812.22 | 40000 | 0 | 5348.8 | 3911.5 | 0 | 11812.22 | 15723.72 | 0 | 0 | 0 | 0
2022030913 | 4 | 0.54548 | 43638.4 | 0 | 0 | 0.27198 | 9519.3 | 0.84192 | 11786.88 | 40000 | 0 | 3638.4 | 5880.9 | 0 | 11786.88 | 17667.78 | 0 | 0 | 0 | 0
2022030914 | 4 | 0.52871 | 42296.8 | 0 | 0 | 0.28376 | 9931.6 | 0.81994 | 11479.16 | 40000 | 0 | 2296.8 | 7634.8 | 0 | 11479.16 | 19113.96 | 0 | 0 | 0 | 0
2022030915 | 4 | 0.51593 | 41274.4 | 0 | 0 | 0.29848 | 10446.8 | 0.76654 | 10731.56 | 40000 | 0 | 1274.4 | 9172.4 | 0 | 10731.56 | 19903.96 | 0 | 0 | 0 | 0
2022030916 | 4 | 0.50885 | 40708 | 0 | 0 | 0.31893 | 11162.55 | 0.70864 | 9920.96 | 40000 | 0 | 708 | 10454.55 | 0 | 9920.96 | 20375.51 | 0 | 0 | 0 | 0
2022030917 | 4 | 0.50836 | 40668.8 | 0 | 0 | 0.34416 | 12045.6 | 0.61793 | 8651.02 | 40000 | 0 | 668.8 | 11376.8 | 0 | 8651.02 | 20027.82 | 0 | 0 | 0 | 0
2022030918 | 4 | 0.51502 | 41201.6 | 0 | 0 | 0.3575 | 12512.5 | 0.44183 | 6185.62 | 40000 | 0 | 1201.6 | 11310.9 | 0 | 6185.62 | 17496.52 | 0 | 0 | 0 | 0
2022030919 | 4 | 0.53396 | 42716.8 | 0 | 0 | 0.40412 | 14144.2 | 0.08058 | 1128.12 | 40000 | 0 | 2716.8 | 11427.4 | 0 | 1128.12 | 12555.52 | 0 | 0 | 0 | 0
2022030920 | 4 | 0.55581 | 44464.8 | 0 | 0 | 0.47314 | 16559.9 | 0 | 0 | 40000 | 0 | 4464.8 | 12095.1 | 0 | 0 | 12095.1 | 0 | 0 | 0 | 0
2022030921 | 4 | 0.5607 | 44856 | 0 | 0 | 0.50879 | 17807.65 | 0 | 0 | 40000 | 0 | 4856 | 12951.65 | 0 | 0 | 12951.65 | 0 | 0 | 0 | 0
2022030922 | 4 | 0.55328 | 44262.4 | 0 | 0 | 0.52855 | 18499.25 | 0 | 0 | 40000 | 0 | 4262.4 | 14236.85 | 0 | 0 | 14236.85 | 0 | 0 | 0 | 0
2022030923 | 4 | 0.53456 | 42764.8 | 0 | 0 | 0.51672 | 18085.2 | 0 | 0 | 40000 | 0 | 2764.8 | 15320.4 | 0 | 0 | 15320.4 | 0 | 0 | 0 | 0
2022030924 | 4 | 0.5165 | 41320 | 0 | 0 | 0.50479 | 17667.65 | 0 | 0 | 40000 | 0 | 1320 | 16347.65 | 0 | 0 | 16347.65 | 0 | 0 | 0 | 0
2022031001 | 5 | 0.50665 | 40532 | 0 | 0 | 0.48839 | 17093.65 | 0 | 0 | 40000 | 0 | 532 | 16561.65 | 0 | 0 | 16561.65 | 0 | 0 | 0 | 0
2022031002 | 5 | 0.50414 | 40331.2 | 0 | 0 | 0.48083 | 16829.05 | 0 | 0 | 40000 | 0 | 331.2 | 16497.85 | 0 | 0 | 16497.85 | 0 | 0 | 0 | 0
2022031003 | 5 | 0.5064 | 40512 | 0 | 0 | 0.47621 | 16667.35 | 0 | 0 | 40000 | 0 | 512 | 16155.35 | 0 | 0 | 16155.35 | 0 | 0 | 0 | 0
2022031004 | 5 | 0.51519 | 41215.2 | 0 | 0 | 0.48218 | 16876.3 | 0 | 0 | 40000 | 0 | 1215.2 | 15661.1 | 0 | 0 | 15661.1 | 0 | 0 | 0 | 0
2022031005 | 5 | 0.531 | 42480 | 0 | 0 | 0.4818 | 16863 | 0 | 0 | 40000 | 0 | 2480 | 14383 | 0 | 0 | 14383 | 0 | 0 | 0 | 0
2022031006 | 5 | 0.56573 | 45258.4 | 0 | 0 | 0.47837 | 16742.95 | 0 | 0 | 40000 | 0 | 5258.4 | 11484.55 | 0 | 0 | 11484.55 | 0 | 0 | 0 | 0
2022031007 | 5 | 0.6154 | 49232 | 0 | 0 | 0.47616 | 16665.6 | 0.00062 | 8.68 | 40000 | 0 | 9232 | 7433.6 | 0 | 8.68 | 7442.28 | 0 | 0 | 0 | 0
2022031008 | 5 | 0.62219 | 49775.2 | 0 | 0 | 0.46099 | 16134.65 | 0.12689 | 1776.46 | 40000 | 0 | 9775.2 | 6359.45 | 0 | 1776.46 | 8135.91 | 0 | 0 | 0 | 0
2022031009 | 5 | 0.59258 | 47406.4 | 0 | 0 | 0.33851 | 11847.85 | 0.57646 | 8070.44 | 40000 | 0 | 7406.4 | 4441.45 | 0 | 8070.44 | 12511.89 | 0 | 0 | 0 | 0
2022031010 | 5 | 0.56525 | 45220 | 0 | 0 | 0.26076 | 9126.6 | 0.8255 | 11557 | 40000 | 0 | 5220 | 3906.6 | 0 | 11557 | 15463.6 | 0 | 0 | 0 | 0
2022031011 | 5 | 0.54172 | 43337.6 | 0 | 0 | 0.21999 | 7699.65 | 0.87172 | 12204.08 | 40000 | 0 | 3337.6 | 4362.05 | 0 | 12204.08 | 16566.13 | 0 | 0 | 0 | 0
2022031012 | 5 | 0.52319 | 41855.2 | 0 | 0 | 0.17012 | 5954.2 | 0.86699 | 12137.86 | 40000 | 0 | 1855.2 | 4099 | 0 | 12137.86 | 16236.86 | 0 | 0 | 0 | 0
2022031013 | 5 | 0.50615 | 40492 | 0 | 0 | 0.13589 | 4756.15 | 0.86204 | 12068.56 | 40000 | 0 | 492 | 4264.15 | 0 | 12068.56 | 16332.71 | 0 | 0 | 0 | 0
2022031014 | 5 | 0.49861 | 39888.8 | 0 | 0 | 0.13832 | 4841.2 | 0.85597 | 11983.58 | 39888.8 | 111.2 | 0 | 4841.2 | 0 | 11983.58 | 16935.98 | 0 | 0 | 0 | 0
2022031015 | 5 | 0.4953 | 39624 | 0 | 0 | 0.15514 | 5429.9 | 0.85786 | 12010.04 | 39624 | 376 | 0 | 5429.9 | 0 | 12010.04 | 17815.94 | 0 | 0 | 0 | 0
2022031016 | 5 | 0.4962 | 39696 | 0 | 0 | 0.19481 | 6818.35 | 0.85921 | 12028.94 | 39696 | 304 | 0 | 6818.35 | 0 | 12028.94 | 19151.29 | 0 | 0 | 0 | 0
2022031017 | 5 | 0.50152 | 40121.6 | 0 | 0 | 0.24127 | 8444.45 | 0.82561 | 11558.54 | 40000 | 0 | 121.6 | 8322.85 | 0 | 11558.54 | 19881.39 | 0 | 0 | 0 | 0
2022031018 | 5 | 0.50583 | 40466.4 | 0 | 0 | 0.31135 | 10897.25 | 0.53783 | 7529.62 | 40000 | 0 | 466.4 | 10430.85 | 0 | 7529.62 | 17960.47 | 0 | 0 | 0 | 0
2022031019 | 5 | 0.5172 | 41376 | 0 | 0 | 0.43306 | 15157.1 | 0.08305 | 1162.7 | 40000 | 0 | 1376 | 13781.1 | 0 | 1162.7 | 14943.8 | 0 | 0 | 0 | 0
2022031020 | 5 | 0.5315 | 42520 | 0 | 0 | 0.49196 | 17218.6 | 0 | 0 | 40000 | 0 | 2520 | 14698.6 | 0 | 0 | 14698.6 | 0 | 0 | 0 | 0
2022031021 | 5 | 0.52845 | 42276 | 0 | 0 | 0.50396 | 17638.6 | 0 | 0 | 40000 | 0 | 2276 | 15362.6 | 0 | 0 | 15362.6 | 0 | 0 | 0 | 0
2022031022 | 5 | 0.51722 | 41377.6 | 0 | 0 | 0.51279 | 17947.65 | 0 | 0 | 40000 | 0 | 1377.6 | 16570.05 | 0 | 0 | 16570.05 | 0 | 0 | 0 | 0
2022031023 | 5 | 0.49707 | 39765.6 | 0 | 0 | 0.51703 | 18096.05 | 0 | 0 | 39765.6 | 234.4 | 0 | 18096.05 | 0 | 0 | 18330.45 | 0 | 0 | 0 | 0
2022031024 | 5 | 0.47648 | 38118.4 | 0 | 0 | 0.52142 | 18249.7 | 0 | 0 | 38118.4 | 1881.6 | 0 | 18249.7 | 0 | 0 | 20131.3 | 0 | 0 | 0 | 0
2022031101 | 6 | 0.46239 | 36991.2 | 0 | 0 | 0.52009 | 18203.15 | 0 | 0 | 36991.2 | 3008.8 | 0 | 18203.15 | 0 | 0 | 21211.95 | 0 | 0 | 0 | 0
2022031102 | 6 | 0.45856 | 36684.8 | 0 | 0 | 0.54613 | 19114.55 | 0 | 0 | 36684.8 | 3315.2 | 0 | 19114.55 | 0 | 0 | 22429.75 | 0 | 0 | 0 | 0
2022031103 | 6 | 0.46238 | 36990.4 | 0 | 0 | 0.55803 | 19531.05 | 0 | 0 | 36990.4 | 3009.6 | 0 | 19531.05 | 0 | 0 | 22540.65 | 0 | 0 | 0 | 0
2022031104 | 6 | 0.47088 | 37670.4 | 0 | 0 | 0.56638 | 19823.3 | 0 | 0 | 37670.4 | 2329.6 | 0 | 19823.3 | 0 | 0 | 22152.9 | 0 | 0 | 0 | 0
2022031105 | 6 | 0.48894 | 39115.2 | 0 | 0 | 0.57427 | 20099.45 | 0 | 0 | 39115.2 | 884.8 | 0 | 20099.45 | 0 | 0 | 20984.25 | 0 | 0 | 0 | 0
2022031106 | 6 | 0.52109 | 41687.2 | 0 | 0 | 0.58511 | 20478.85 | 0 | 0 | 40000 | 0 | 1687.2 | 18791.65 | 0 | 0 | 18791.65 | 0 | 0 | 0 | 0
2022031107 | 6 | 0.56885 | 45508 | 0 | 0 | 0.58816 | 20585.6 | 0.00013 | 1.82 | 40000 | 0 | 5508 | 15077.6 | 0 | 1.82 | 15079.42 | 0 | 0 | 0 | 0
2022031108 | 6 | 0.59363 | 47490.4 | 0 | 0 | 0.5779 | 20226.5 | 0.02259 | 316.26 | 40000 | 0 | 7490.4 | 12736.1 | 0 | 316.26 | 13052.36 | 0 | 0 | 0 | 0
2022031109 | 6 | 0.61026 | 48820.8 | 0 | 0 | 0.55473 | 19415.55 | 0.09864 | 1380.96 | 40000 | 0 | 8820.8 | 10594.75 | 0 | 1380.96 | 11975.71 | 0 | 0 | 0 | 0
2022031110 | 6 | 0.62521 | 50016.8 | 0 | 0 | 0.53383 | 18684.05 | 0.20709 | 2899.26 | 40000 | 0 | 10016.8 | 8667.25 | 0 | 2899.26 | 11566.51 | 0 | 0 | 0 | 0
2022031111 | 6 | 0.63451 | 50760.8 | 0 | 0 | 0.52538 | 18388.3 | 0.25365 | 3551.1 | 40000 | 0 | 10760.8 | 7627.5 | 0 | 3551.1 | 11178.6 | 0 | 0 | 0 | 0
2022031112 | 6 | 0.64017 | 51213.6 | 0 | 0 | 0.53019 | 18556.65 | 0.29184 | 4085.76 | 40000 | 0 | 11213.6 | 7343.05 | 0 | 4085.76 | 11428.81 | 0 | 0 | 0 | 0
2022031113 | 6 | 0.64267 | 51413.6 | 0 | 0 | 0.56463 | 19762.05 | 0.26331 | 3686.34 | 40000 | 0 | 11413.6 | 8348.45 | 0 | 3686.34 | 12034.79 | 0 | 0 | 0 | 0
2022031114 | 6 | 0.64649 | 51719.2 | 0 | 0 | 0.59379 | 20782.65 | 0.26258 | 3676.12 | 40000 | 0 | 11719.2 | 9063.45 | 0 | 3676.12 | 12739.57 | 0 | 0 | 0 | 0
2022031115 | 6 | 0.64562 | 51649.6 | 0 | 0 | 0.61712 | 21599.2 | 0.33662 | 4712.68 | 40000 | 0 | 11649.6 | 9949.6 | 0 | 4712.68 | 14662.28 | 0 | 0 | 0 | 0
2022031116 | 6 | 0.64232 | 51385.6 | 0 | 0 | 0.61959 | 21685.65 | 0.36958 | 5174.12 | 40000 | 0 | 11385.6 | 10300.05 | 0 | 5174.12 | 15474.17 | 0 | 0 | 0 | 0
2022031117 | 6 | 0.64437 | 51549.6 | 0 | 0 | 0.58591 | 20506.85 | 0.41179 | 5765.06 | 40000 | 0 | 11549.6 | 8957.25 | 0 | 5765.06 | 14722.31 | 0 | 0 | 0 | 0
2022031118 | 6 | 0.64957 | 51965.6 | 0 | 0 | 0.511 | 17885 | 0.42351 | 5929.14 | 40000 | 0 | 11965.6 | 5919.4 | 0 | 5929.14 | 11848.54 | 0 | 0 | 0 | 0
2022031119 | 6 | 0.66566 | 53252.8 | 0 | 0 | 0.41237 | 14432.95 | 0.0877 | 1227.8 | 40000 | 0 | 13252.8 | 1180.15 | 0 | 1227.8 | 2407.95 | 0 | 0 | 0 | 0
2022031120 | 6 | 0.6805 | 54440 | 0 | 0 | 0.35189 | 12316.15 | 0.00014 | 1.96 | 40000 | 0 | 12316.15 | 0 | 1.96 | 0 | 0 | 2121.89 | 0 | 0 | 2121.89
2022031121 | 6 | 0.67881 | 54304.8 | 0 | 0 | 0.34061 | 11921.35 | 0 | 0 | 40000 | 0 | 11921.35 | 0 | 0 | 0 | 0 | 2383.45 | 0 | 0 | 2383.45
2022031122 | 6 | 0.67327 | 53861.6 | 0 | 0 | 0.31626 | 11069.1 | 0 | 0 | 40000 | 0 | 11069.1 | 0 | 0 | 0 | 0 | 2792.5 | 0 | 0 | 2792.5
2022031123 | 6 | 0.66026 | 52820.8 | 0 | 0 | 0.29712 | 10399.2 | 0 | 0 | 40000 | 0 | 10399.2 | 0 | 0 | 0 | 0 | 2421.6 | 0 | 0 | 2421.6
2022031124 | 6 | 0.64638 | 51710.4 | 0 | 0 | 0.26548 | 9291.8 | 0 | 0 | 40000 | 0 | 9291.8 | 0 | 0 | 0 | 0 | 2418.6 | 0 | 0 | 2418.6
2022031201 | 7 | 0.63757 | 51005.6 | 0 | 0 | 0.23948 | 8381.8 | 0 | 0 | 40000 | 0 | 8381.8 | 0 | 0 | 0 | 0 | 2623.8 | 0 | 0 | 2623.8
2022031202 | 7 | 0.63475 | 50780 | 0 | 0 | 0.22912 | 8019.2 | 0 | 0 | 40000 | 0 | 8019.2 | 0 | 0 | 0 | 0 | 2760.8 | 0 | 0 | 2760.8
2022031203 | 7 | 0.63662 | 50929.6 | 0 | 0 | 0.23473 | 8215.55 | 0 | 0 | 40000 | 0 | 8215.55 | 0 | 0 | 0 | 0 | 2714.05 | 0 | 0 | 2714.05
2022031204 | 7 | 0.64209 | 51367.2 | 0 | 0 | 0.26439 | 9253.65 | 0 | 0 | 40000 | 0 | 9253.65 | 0 | 0 | 0 | 0 | 2113.55 | 0 | 0 | 2113.55
2022031205 | 7 | 0.65422 | 52337.6 | 0 | 0 | 0.28154 | 9853.9 | 0 | 0 | 40000 | 0 | 9853.9 | 0 | 0 | 0 | 0 | 2483.7 | 0 | 0 | 2483.7
2022031206 | 7 | 0.67367 | 53893.6 | 0 | 0 | 0.31864 | 11152.4 | 0 | 0 | 40000 | 0 | 11152.4 | 0 | 0 | 0 | 0 | 2741.2 | 0 | 0 | 2741.2
2022031207 | 7 | 0.69936 | 55948.8 | 0 | 0 | 0.36972 | 12940.2 | 0.00139 | 19.46 | 40000 | 0 | 12940.2 | 0 | 19.46 | 0 | 0 | 2989.14 | 0 | 0 | 2989.14
2022031208 | 7 | 0.70653 | 56522.4 | 0 | 0 | 0.40119 | 14041.65 | 0.17235 | 2412.9 | 40000 | 0 | 14041.65 | 0 | 2412.9 | 0 | 0 | 67.85 | 0 | 0 | 67.85
2022031209 | 7 | 0.68425 | 54740 | 0 | 0 | 0.36085 | 12629.75 | 0.72447 | 10142.58 | 40000 | 0 | 12629.75 | 0 | 2110.25 | 8032.33 | 8032.33 | 0 | 0 | 0 | 0
2022031210 | 7 | 0.65255 | 52204 | 0 | 0 | 0.35145 | 12300.75 | 0.8823 | 12352.2 | 40000 | 0 | 12204 | 96.75 | 0 | 12352.2 | 12448.95 | 0 | 0 | 0 | 0
2022031211 | 7 | 0.61798 | 49438.4 | 0 | 0 | 0.33737 | 11807.95 | 0.89085 | 12471.9 | 40000 | 0 | 9438.4 | 2369.55 | 0 | 12471.9 | 14841.45 | 0 | 0 | 0 | 0
2022031212 | 7 | 0.58364 | 46691.2 | 0 | 0 | 0.31607 | 11062.45 | 0.88779 | 12429.06 | 40000 | 0 | 6691.2 | 4371.25 | 0 | 12429.06 | 16800.31 | 0 | 0 | 0 | 0
2022031213 | 7 | 0.55309 | 44247.2 | 0 | 0 | 0.33296 | 11653.6 | 0.85694 | 11997.16 | 40000 | 0 | 4247.2 | 7406.4 | 0 | 11997.16 | 19403.56 | 0 | 0 | 0 | 0
2022031214 | 7 | 0.52598 | 42078.4 | 0 | 0 | 0.35748 | 12511.8 | 0.81461 | 11404.54 | 40000 | 0 | 2078.4 | 10433.4 | 0 | 11404.54 | 21837.94 | 0 | 0 | 0 | 0
2022031215 | 7 | 0.50369 | 40295.2 | 0 | 0 | 0.3715 | 13002.5 | 0.72366 | 10131.24 | 40000 | 0 | 295.2 | 12707.3 | 0 | 10131.24 | 22838.54 | 0 | 0 | 0 | 0
2022031216 | 7 | 0.49077 | 39261.6 | 0 | 0 | 0.37906 | 13267.1 | 0.63556 | 8897.84 | 39261.6 | 738.4 | 0 | 13267.1 | 0 | 8897.84 | 22903.34 | 0 | 0 | 0 | 0
2022031217 | 7 | 0.48918 | 39134.4 | 0 | 0 | 0.36632 | 12821.2 | 0.64564 | 9038.96 | 39134.4 | 865.6 | 0 | 12821.2 | 0 | 9038.96 | 22725.76 | 0 | 0 | 0 | 0
2022031218 | 7 | 0.49616 | 39692.8 | 0 | 0 | 0.39044 | 13665.4 | 0.52446 | 7342.44 | 39692.8 | 307.2 | 0 | 13665.4 | 0 | 7342.44 | 21315.04 | 0 | 0 | 0 | 0
2022031219 | 7 | 0.51596 | 41276.8 | 0 | 0 | 0.39476 | 13816.6 | 0.10228 | 1431.92 | 40000 | 0 | 1276.8 | 12539.8 | 0 | 1431.92 | 13971.72 | 0 | 0 | 0 | 0
2022031220 | 7 | 0.54483 | 43586.4 | 0 | 0 | 0.49975 | 17491.25 | 0 | 0 | 40000 | 0 | 3586.4 | 13904.85 | 0 | 0 | 13904.85 | 0 | 0 | 0 | 0
2022031221 | 7 | 0.55966 | 44772.8 | 0 | 0 | 0.62469 | 21864.15 | 0 | 0 | 40000 | 0 | 4772.8 | 17091.35 | 0 | 0 | 17091.35 | 0 | 0 | 0 | 0
2022031222 | 7 | 0.56594 | 45275.2 | 0 | 0 | 0.63334 | 22166.9 | 0 | 0 | 40000 | 0 | 5275.2 | 16891.7 | 0 | 0 | 16891.7 | 0 | 0 | 0 | 0
2022031223 | 7 | 0.56224 | 44979.2 | 0 | 0 | 0.63435 | 22202.25 | 0 | 0 | 40000 | 0 | 4979.2 | 17223.05 | 0 | 0 | 17223.05 | 0 | 0 | 0 | 0
2022031224 | 7 | 0.55712 | 44569.6 | 0 | 0 | 0.63348 | 22171.8 | 0 | 0 | 40000 | 0 | 4569.6 | 17602.2 | 0 | 0 | 17602.2 | 0 | 0 | 0 | 0
2022031301 | 1 | 0.55332 | 44265.6 | 0 | 0 | 0.61975 | 21691.25 | 0 | 0 | 40000 | 0 | 4265.6 | 17425.65 | 0 | 0 | 17425.65 | 0 | 0 | 0 | 0
2022031303 | 1 | 0.552 | 44160 | 0 | 0 | 0.61296 | 21453.6 | 0 | 0 | 40000 | 0 | 4160 | 17293.6 | 0 | 0 | 17293.6 | 0 | 0 | 0 | 0
2022031304 | 1 | 0.55724 | 44579.2 | 0 | 0 | 0.61275 | 21446.25 | 0 | 0 | 40000 | 0 | 4579.2 | 16867.05 | 0 | 0 | 16867.05 | 0 | 0 | 0 | 0
2022031305 | 1 | 0.56709 | 45367.2 | 0 | 0 | 0.61263 | 21442.05 | 0 | 0 | 40000 | 0 | 5367.2 | 16074.85 | 0 | 0 | 16074.85 | 0 | 0 | 0 | 0
2022031306 | 1 | 0.57936 | 46348.8 | 0 | 0 | 0.60294 | 21102.9 | 0 | 0 | 40000 | 0 | 6348.8 | 14754.1 | 0 | 0 | 14754.1 | 0 | 0 | 0 | 0
2022031307 | 1 | 0.59655 | 47724 | 0 | 0 | 0.59713 | 20899.55 | 0 | 0 | 40000 | 0 | 7724 | 13175.55 | 0 | 0 | 13175.55 | 0 | 0 | 0 | 0
2022031308 | 1 | 0.61756 | 49404.8 | 0 | 0 | 0.59706 | 20897.1 | 0.0015 | 21 | 40000 | 0 | 9404.8 | 11492.3 | 0 | 21 | 11513.3 | 0 | 0 | 0 | 0
2022031309 | 1 | 0.61948 | 49558.4 | 0 | 0 | 0.57296 | 20053.6 | 0.12372 | 1732.08 | 40000 | 0 | 9558.4 | 10495.2 | 0 | 1732.08 | 12227.28 | 0 | 0 | 0 | 0
2022031310 | 1 | 0.59725 | 47780 | 0 | 0 | 0.50472 | 17665.2 | 0.39805 | 5572.7 | 40000 | 0 | 7780 | 9885.2 | 0 | 5572.7 | 15457.9 | 0 | 0 | 0 | 0
2022031311 | 1 | 0.57102 | 45681.6 | 0 | 0 | 0.57348 | 20071.8 | 0.41531 | 5814.34 | 40000 | 0 | 5681.6 | 14390.2 | 0 | 5814.34 | 20204.54 | 0 | 0 | 0 | 0
2022031312 | 1 | 0.54598 | 43678.4 | 0 | 0 | 0.62316 | 21810.6 | 0.3708 | 5191.2 | 40000 | 0 | 3678.4 | 18132.2 | 0 | 5191.2 | 23323.4 | 0 | 0 | 0 | 0
2022031313 | 1 | 0.5233 | 41864 | 0 | 0 | 0.62973 | 22040.55 | 0.35308 | 4943.12 | 40000 | 0 | 1864 | 20176.55 | 0 | 4943.12 | 25119.67 | 0 | 0 | 0 | 0
2022031314 | 1 | 0.5037 | 40296 | 0 | 0 | 0.62619 | 21916.65 | 0.34816 | 4874.24 | 40000 | 0 | 296 | 21620.65 | 0 | 4874.24 | 26494.89 | 0 | 0 | 0 | 0
2022031315 | 1 | 0.48811 | 39048.8 | 0 | 0 | 0.63012 | 22054.2 | 0.29838 | 4177.32 | 39048.8 | 951.2 | 0 | 22054.2 | 0 | 4177.32 | 27182.72 | 0 | 0 | 0 | 0
2022031316 | 1 | 0.47927 | 38341.6 | 0 | 0 | 0.63668 | 22283.8 | 0.24958 | 3494.12 | 38341.6 | 1658.4 | 0 | 22283.8 | 0 | 3494.12 | 27436.32 | 0 | 0 | 0 | 0
2022031317 | 1 | 0.47576 | 38060.8 | 0 | 0 | 0.64293 | 22502.55 | 0.2006 | 2808.4 | 38060.8 | 1939.2 | 0 | 22502.55 | 0 | 2808.4 | 27250.15 | 0 | 0 | 0 | 0
2022031318 | 1 | 0.47991 | 38392.8 | 0 | 0 | 0.65229 | 22830.15 | 0.1649 | 2308.6 | 38392.8 | 1607.2 | 0 | 22830.15 | 0 | 2308.6 | 26745.95 | 0 | 0 | 0 | 0
2022031319 | 1 | 0.48709 | 38967.2 | 0 | 0 | 0.65121 | 22792.35 | 0.09476 | 1326.64 | 38967.2 | 1032.8 | 0 | 22792.35 | 0 | 1326.64 | 25151.79 | 0 | 0 | 0 | 0
2022031320 | 1 | 0.50324 | 40259.2 | 0 | 0 | 0.63817 | 22335.95 | 0.01805 | 252.7 | 40000 | 0 | 259.2 | 22076.75 | 0 | 252.7 | 22329.45 | 0 | 0 | 0 | 0
2022031321 | 1 | 0.5209 | 41672 | 0 | 0 | 0.64113 | 22439.55 | 0 | 0 | 40000 | 0 | 1672 | 20767.55 | 0 | 0 | 20767.55 | 0 | 0 | 0 | 0
2022031322 | 1 | 0.51633 | 41306.4 | 0 | 0 | 0.64535 | 22587.25 | 0 | 0 | 40000 | 0 | 1306.4 | 21280.85 | 0 | 0 | 21280.85 | 0 | 0 | 0 | 0
2022031323 | 1 | 0.5011 | 40088 | 0 | 0 | 0.64949 | 22732.15 | 0 | 0 | 40000 | 0 | 88 | 22644.15 | 0 | 0 | 22644.15 | 0 | 0 | 0 | 0
2022031324 | 1 | 0.48092 | 38473.6 | 0 | 0 | 0.64442 | 22554.7 | 0 | 0 | 38473.6 | 1526.4 | 0 | 22554.7 | 0 | 0 | 24081.1 | 0 | 0 | 0 | 0
2022031401 | 2 | 0.46536 | 37228.8 | 0 | 0 | 0.65104 | 22786.4 | 0 | 0 | 37228.8 | 2771.2 | 0 | 22786.4 | 0 | 0 | 25557.6 | 0 | 0 | 0 | 0
2022031402 | 2 | 0.45565 | 36452 | 0 | 0 | 0.64367 | 22528.45 | 0 | 0 | 36452 | 3548 | 0 | 22528.45 | 0 | 0 | 26076.45 | 0 | 0 | 0 | 0
2022031403 | 2 | 0.45219 | 36175.2 | 0 | 0 | 0.63539 | 22238.65 | 0 | 0 | 36175.2 | 3824.8 | 0 | 22238.65 | 0 | 0 | 26063.45 | 0 | 0 | 0 | 0
2022031404 | 2 | 0.45348 | 36278.4 | 0 | 0 | 0.6249 | 21871.5 | 0 | 0 | 36278.4 | 3721.6 | 0 | 21871.5 | 0 | 0 | 25593.1 | 0 | 0 | 0 | 0
2022031405 | 2 | 0.4624 | 36992 | 0 | 0 | 0.61839 | 21643.65 | 0 | 0 | 36992 | 3008 | 0 | 21643.65 | 0 | 0 | 24651.65 | 0 | 0 | 0 | 0
2022031406 | 2 | 0.48307 | 38645.6 | 0 | 0 | 0.62127 | 21744.45 | 0 | 0 | 38645.6 | 1354.4 | 0 | 21744.45 | 0 | 0 | 23098.85 | 0 | 0 | 0 | 0
2022031407 | 2 | 0.51609 | 41287.2 | 0 | 0 | 0.62523 | 21883.05 | 0 | 0 | 40000 | 0 | 1287.2 | 20595.85 | 0 | 0 | 20595.85 | 0 | 0 | 0 | 0
2022031408 | 2 | 0.53917 | 43133.6 | 0 | 0 | 0.62677 | 21936.95 | 0.0006 | 8.4 | 40000 | 0 | 3133.6 | 18803.35 | 0 | 8.4 | 18811.75 | 0 | 0 | 0 | 0
2022031409 | 2 | 0.54368 | 43494.4 | 0 | 0 | 0.59778 | 20922.3 | 0.12176 | 1704.64 | 40000 | 0 | 3494.4 | 17427.9 | 0 | 1704.64 | 19132.54 | 0 | 0 | 0 | 0
2022031410 | 2 | 0.54136 | 43308.8 | 0 | 0 | 0.52103 | 18236.05 | 0.38013 | 5321.82 | 40000 | 0 | 3308.8 | 14927.25 | 0 | 5321.82 | 20249.07 | 0 | 0 | 0 | 0
2022031411 | 2 | 0.53608 | 42886.4 | 0 | 0 | 0.53614 | 18764.9 | 0.42105 | 5894.7 | 40000 | 0 | 2886.4 | 15878.5 | 0 | 5894.7 | 21773.2 | 0 | 0 | 0 | 0
2022031412 | 2 | 0.53078 | 42462.4 | 0 | 0 | 0.55342 | 19369.7 | 0.44664 | 6252.96 | 40000 | 0 | 2462.4 | 16907.3 | 0 | 6252.96 | 23160.26 | 0 | 0 | 0 | 0
2022031413 | 2 | 0.52466 | 41972.8 | 0 | 0 | 0.54997 | 19248.95 | 0.48684 | 6815.76 | 40000 | 0 | 1972.8 | 17276.15 | 0 | 6815.76 | 24091.91 | 0 | 0 | 0 | 0
2022031414 | 2 | 0.52187 | 41749.6 | 0 | 0 | 0.5691 | 19918.5 | 0.40834 | 5716.76 | 40000 | 0 | 1749.6 | 18168.9 | 0 | 5716.76 | 23885.66 | 0 | 0 | 0 | 0
2022031415 | 2 | 0.51869 | 41495.2 | 0 | 0 | 0.5714 | 19999 | 0.40603 | 5684.42 | 40000 | 0 | 1495.2 | 18503.8 | 0 | 5684.42 | 24188.22 | 0 | 0 | 0 | 0
2022031416 | 2 | 0.5192 | 41536 | 0 | 0 | 0.57854 | 20248.9 | 0.35188 | 4926.32 | 40000 | 0 | 1536 | 18712.9 | 0 | 4926.32 | 23639.22 | 0 | 0 | 0 | 0
2022031417 | 2 | 0.52356 | 41884.8 | 0 | 0 | 0.57829 | 20240.15 | 0.35716 | 5000.24 | 40000 | 0 | 1884.8 | 18355.35 | 0 | 5000.24 | 23355.59 | 0 | 0 | 0 | 0
2022031418 | 2 | 0.52889 | 42311.2 | 0 | 0 | 0.57999 | 20299.65 | 0.28211 | 3949.54 | 40000 | 0 | 2311.2 | 17988.45 | 0 | 3949.54 | 21937.99 | 0 | 0 | 0 | 0
2022031419 | 2 | 0.53122 | 42497.6 | 0 | 0 | 0.59368 | 20778.8 | 0.17763 | 2486.82 | 40000 | 0 | 2497.6 | 18281.2 | 0 | 2486.82 | 20768.02 | 0 | 0 | 0 | 0
2022031420 | 2 | 0.53254 | 42603.2 | 0 | 0 | 0.61065 | 21372.75 | 0.03925 | 549.5 | 40000 | 0 | 2603.2 | 18769.55 | 0 | 549.5 | 19319.05 | 0 | 0 | 0 | 0
2022031421 | 2 | 0.53374 | 42699.2 | 0 | 0 | 0.57716 | 20200.6 | 0 | 0 | 40000 | 0 | 2699.2 | 17501.4 | 0 | 0 | 17501.4 | 0 | 0 | 0 | 0
2022031422 | 2 | 0.51975 | 41580 | 0 | 0 | 0.58974 | 20640.9 | 0 | 0 | 40000 | 0 | 1580 | 19060.9 | 0 | 0 | 19060.9 | 0 | 0 | 0 | 0
2022031423 | 2 | 0.49508 | 39606.4 | 0 | 0 | 0.55442 | 19404.7 | 0 | 0 | 39606.4 | 393.6 | 0 | 19404.7 | 0 | 0 | 19798.3 | 0 | 0 | 0 | 0
2022031424 | 2 | 0.46763 | 37410.4 | 0 | 0 | 0.49132 | 17196.2 | 0 | 0 | 37410.4 | 2589.6 | 0 | 17196.2 | 0 | 0 | 19785.8 | 0 | 0 | 0 | 0
2022031501 | 3 | 0.44534 | 35627.2 | 0 | 0 | 0.4201 | 14703.5 | 0 | 0 | 35627.2 | 4372.8 | 0 | 14703.5 | 0 | 0 | 19076.3 | 0 | 0 | 0 | 0
2022031502 | 3 | 0.42914 | 34331.2 | 0 | 0 | 0.37998 | 13299.3 | 0 | 0 | 34331.2 | 5668.8 | 0 | 13299.3 | 0 | 0 | 18968.1 | 0 | 0 | 0 | 0
2022031503 | 3 | 0.42048 | 33638.4 | 0 | 0 | 0.34444 | 12055.4 | 0 | 0 | 33638.4 | 6361.6 | 0 | 12055.4 | 0 | 0 | 18417 | 0 | 0 | 0 | 0
2022031504 | 3 | 0.41783 | 33426.4 | 0 | 0 | 0.36509 | 12778.15 | 0 | 0 | 33426.4 | 6573.6 | 0 | 12778.15 | 0 | 0 | 19351.75 | 0 | 0 | 0 | 0
2022031505 | 3 | 0.42714 | 34171.2 | 0 | 0 | 0.40931 | 14325.85 | 0 | 0 | 34171.2 | 5828.8 | 0 | 14325.85 | 0 | 0 | 20154.65 | 0 | 0 | 0 | 0
2022031506 | 3 | 0.44963 | 35970.4 | 0 | 0 | 0.43344 | 15170.4 | 0 | 0 | 35970.4 | 4029.6 | 0 | 15170.4 | 0 | 0 | 19200 | 0 | 0 | 0 | 0
2022031507 | 3 | 0.48422 | 38737.6 | 0 | 0 | 0.45451 | 15907.85 | 0 | 0 | 38737.6 | 1262.4 | 0 | 15907.85 | 0 | 0 | 17170.25 | 0 | 0 | 0 | 0
2022031508 | 3 | 0.5114 | 40912 | 0 | 0 | 0.46385 | 16234.75 | 0.00117 | 16.38 | 40000 | 0 | 912 | 15322.75 | 0 | 16.38 | 15339.13 | 0 | 0 | 0 | 0
2022031509 | 3 | 0.51969 | 41575.2 | 0 | 0 | 0.46463 | 16262.05 | 0.1669 | 2336.6 | 40000 | 0 | 1575.2 | 14686.85 | 0 | 2336.6 | 17023.45 | 0 | 0 | 0 | 0
2022031510 | 3 | 0.51744 | 41395.2 | 0 | 0 | 0.36751 | 12862.85 | 0.65249 | 9134.86 | 40000 | 0 | 1395.2 | 11467.65 | 0 | 9134.86 | 20602.51 | 0 | 0 | 0 | 0
2022031511 | 3 | 0.51351 | 41080.8 | 0 | 0 | 0.34253 | 11988.55 | 0.81132 | 11358.48 | 40000 | 0 | 1080.8 | 10907.75 | 0 | 11358.48 | 22266.23 | 0 | 0 | 0 | 0
2022031512 | 3 | 0.50714 | 40571.2 | 0 | 0 | 0.30305 | 10606.75 | 0.82028 | 11483.92 | 40000 | 0 | 571.2 | 10035.55 | 0 | 11483.92 | 21519.47 | 0 | 0 | 0 | 0
2022031513 | 3 | 0.50021 | 40016.8 | 0 | 0 | 0.24803 | 8681.05 | 0.84362 | 11810.68 | 40000 | 0 | 16.8 | 8664.25 | 0 | 11810.68 | 20474.93 | 0 | 0 | 0 | 0
2022031514 | 3 | 0.49871 | 39896.8 | 0 | 0 | 0.21623 | 7568.05 | 0.84155 | 11781.7 | 39896.8 | 103.2 | 0 | 7568.05 | 0 | 11781.7 | 19452.95 | 0 | 0 | 0 | 0
2022031515 | 3 | 0.49984 | 39987.2 | 0 | 0 | 0.20612 | 7214.2 | 0.83135 | 11638.9 | 39987.2 | 12.8 | 0 | 7214.2 | 0 | 11638.9 | 18865.9 | 0 | 0 | 0 | 0
2022031516 | 3 | 0.50199 | 40159.2 | 0 | 0 | 0.18468 | 6463.8 | 0.83908 | 11747.12 | 40000 | 0 | 159.2 | 6304.6 | 0 | 11747.12 | 18051.72 | 0 | 0 | 0 | 0
2022031517 | 3 | 0.50651 | 40520.8 | 0 | 0 | 0.16836 | 5892.6 | 0.82874 | 11602.36 | 40000 | 0 | 520.8 | 5371.8 | 0 | 11602.36 | 16974.16 | 0 | 0 | 0 | 0
2022031518 | 3 | 0.51001 | 40800.8 | 0 | 0 | 0.13637 | 4772.95 | 0.82478 | 11546.92 | 40000 | 0 | 800.8 | 3972.15 | 0 | 11546.92 | 15519.07 | 0 | 0 | 0 | 0
2022031519 | 3 | 0.51137 | 40909.6 | 0 | 0 | 0.10433 | 3651.55 | 0.60133 | 8418.62 | 40000 | 0 | 909.6 | 2741.95 | 0 | 8418.62 | 11160.57 | 0 | 0 | 0 | 0
2022031520 | 3 | 0.51338 | 41070.4 | 0 | 0 | 0.07996 | 2798.6 | 0.10795 | 1511.3 | 40000 | 0 | 1070.4 | 1728.2 | 0 | 1511.3 | 3239.5 | 0 | 0 | 0 | 0
2022031521 | 3 | 0.51796 | 41436.8 | 0 | 0 | 0.10264 | 3592.4 | 0 | 0 | 40000 | 0 | 1436.8 | 2155.6 | 0 | 0 | 2155.6 | 0 | 0 | 0 | 0
2022031522 | 3 | 0.50579 | 40463.2 | 0 | 0 | 0.15805 | 5531.75 | 0 | 0 | 40000 | 0 | 463.2 | 5068.55 | 0 | 0 | 5068.55 | 0 | 0 | 0 | 0
2022031523 | 3 | 0.48147 | 38517.6 | 0 | 0 | 0.21798 | 7629.3 | 0 | 0 | 38517.6 | 1482.4 | 0 | 7629.3 | 0 | 0 | 9111.7 | 0 | 0 | 0 | 0
2022031524 | 3 | 0.45513 | 36410.4 | 0 | 0 | 0.28315 | 9910.25 | 0 | 0 | 36410.4 | 3589.6 | 0 | 9910.25 | 0 | 0 | 13499.85 | 0 | 0 | 0 | 0
2022031601 | 4 | 0.43518 | 34814.4 | 0 | 0 | 0.36698 | 12844.3 | 0 | 0 | 34814.4 | 5185.6 | 0 | 12844.3 | 0 | 0 | 18029.9 | 0 | 0 | 0 | 0
2022031602 | 4 | 0.42435 | 33948 | 0 | 0 | 0.4417 | 15459.5 | 0 | 0 | 33948 | 6052 | 0 | 15459.5 | 0 | 0 | 21511.5 | 0 | 0 | 0 | 0
2022031603 | 4 | 0.41958 | 33566.4 | 0 | 0 | 0.48344 | 16920.4 | 0 | 0 | 33566.4 | 6433.6 | 0 | 16920.4 | 0 | 0 | 23354 | 0 | 0 | 0 | 0
2022031604 | 4 | 0.42094 | 33675.2 | 0 | 0 | 0.50182 | 17563.7 | 0 | 0 | 33675.2 | 6324.8 | 0 | 17563.7 | 0 | 0 | 23888.5 | 0 | 0 | 0 | 0
2022031605 | 4 | 0.43184 | 34547.2 | 0 | 0 | 0.52038 | 18213.3 | 0 | 0 | 34547.2 | 5452.8 | 0 | 18213.3 | 0 | 0 | 23666.1 | 0 | 0 | 0 | 0
2022031606 | 4 | 0.45765 | 36612 | 0 | 0 | 0.54993 | 19247.55 | 0 | 0 | 36612 | 3388 | 0 | 19247.55 | 0 | 0 | 22635.55 | 0 | 0 | 0 | 0
2022031607 | 4 | 0.49366 | 39492.8 | 0 | 0 | 0.56557 | 19794.95 | 0 | 0 | 39492.8 | 507.2 | 0 | 19794.95 | 0 | 0 | 20302.15 | 0 | 0 | 0 | 0
2022031608 | 4 | 0.52265 | 41812 | 0 | 0 | 0.57437 | 20102.95 | 0.00212 | 29.68 | 40000 | 0 | 1812 | 18290.95 | 0 | 29.68 | 18320.63 | 0 | 0 | 0 | 0
2022031609 | 4 | 0.52806 | 42244.8 | 0 | 0 | 0.54098 | 18934.3 | 0.18233 | 2552.62 | 40000 | 0 | 2244.8 | 16689.5 | 0 | 2552.62 | 19242.12 | 0 | 0 | 0 | 0
2022031610 | 4 | 0.51504 | 41203.2 | 0 | 0 | 0.46945 | 16430.75 | 0.45211 | 6329.54 | 40000 | 0 | 1203.2 | 15227.55 | 0 | 6329.54 | 21557.09 | 0 | 0 | 0 | 0
2022031611 | 4 | 0.50624 | 40499.2 | 0 | 0 | 0.45029 | 15760.15 | 0.56618 | 7926.52 | 40000 | 0 | 499.2 | 15260.95 | 0 | 7926.52 | 23187.47 | 0 | 0 | 0 | 0
2022031612 | 4 | 0.50082 | 40065.6 | 0 | 0 | 0.46105 | 16136.75 | 0.52703 | 7378.42 | 40000 | 0 | 65.6 | 16071.15 | 0 | 7378.42 | 23449.57 | 0 | 0 | 0 | 0
2022031613 | 4 | 0.49926 | 39940.8 | 0 | 0 | 0.43871 | 15354.85 | 0.57396 | 8035.44 | 39940.8 | 59.2 | 0 | 15354.85 | 0 | 8035.44 | 23449.49 | 0 | 0 | 0 | 0
2022031614 | 4 | 0.50481 | 40384.8 | 0 | 0 | 0.40587 | 14205.45 | 0.70842 | 9917.88 | 40000 | 0 | 384.8 | 13820.65 | 0 | 9917.88 | 23738.53 | 0 | 0 | 0 | 0
2022031615 | 4 | 0.51347 | 41077.6 | 0 | 0 | 0.38759 | 13565.65 | 0.8058 | 11281.2 | 40000 | 0 | 1077.6 | 12488.05 | 0 | 11281.2 | 23769.25 | 0 | 0 | 0 | 0
2022031616 | 4 | 0.52446 | 41956.8 | 0 | 0 | 0.40581 | 14203.35 | 0.81821 | 11454.94 | 40000 | 0 | 1956.8 | 12246.55 | 0 | 11454.94 | 23701.49 | 0 | 0 | 0 | 0
2022031617 | 4 | 0.53634 | 42907.2 | 0 | 0 | 0.45628 | 15969.8 | 0.78394 | 10975.16 | 40000 | 0 | 2907.2 | 13062.6 | 0 | 10975.16 | 24037.76 | 0 | 0 | 0 | 0
2022031618 | 4 | 0.54482 | 43585.6 | 0 | 0 | 0.50062 | 17521.7 | 0.68596 | 9603.44 | 40000 | 0 | 3585.6 | 13936.1 | 0 | 9603.44 | 23539.54 | 0 | 0 | 0 | 0
2022031619 | 4 | 0.54245 | 43396 | 0 | 0 | 0.52507 | 18377.45 | 0.45599 | 6383.86 | 40000 | 0 | 3396 | 14981.45 | 0 | 6383.86 | 21365.31 | 0 | 0 | 0 | 0
2022031620 | 4 | 0.53226 | 42580.8 | 0 | 0 | 0.51549 | 18042.15 | 0.08875 | 1242.5 | 40000 | 0 | 2580.8 | 15461.35 | 0 | 1242.5 | 16703.85 | 0 | 0 | 0 | 0
2022031621 | 4 | 0.53508 | 42806.4 | 0 | 0 | 0.57707 | 20197.45 | 0 | 0 | 40000 | 0 | 2806.4 | 17391.05 | 0 | 0 | 17391.05 | 0 | 0 | 0 | 0
2022031622 | 4 | 0.52059 | 41647.2 | 0 | 0 | 0.64335 | 22517.25 | 0 | 0 | 40000 | 0 | 1647.2 | 20870.05 | 0 | 0 | 20870.05 | 0 | 0 | 0 | 0
2022031623 | 4 | 0.49601 | 39680.8 | 0 | 0 | 0.66015 | 23105.25 | 0 | 0 | 39680.8 | 319.2 | 0 | 23105.25 | 0 | 0 | 23424.45 | 0 | 0 | 0 | 0
2022031624 | 4 | 0.46533 | 37226.4 | 0 | 0 | 0.63846 | 22346.1 | 0 | 0 | 37226.4 | 2773.6 | 0 | 22346.1 | 0 | 0 | 25119.7 | 0 | 0 | 0 | 0
2022031701 | 5 | 0.43998 | 35198.4 | 0 | 0 | 0.60893 | 21312.55 | 0 | 0 | 35198.4 | 4801.6 | 0 | 21312.55 | 0 | 0 | 26114.15 | 0 | 0 | 0 | 0
2022031702 | 5 | 0.42409 | 33927.2 | 0 | 0 | 0.59422 | 20797.7 | 0 | 0 | 33927.2 | 6072.8 | 0 | 20797.7 | 0 | 0 | 26870.5 | 0 | 0 | 0 | 0
2022031703 | 5 | 0.41335 | 33068 | 0 | 0 | 0.58294 | 20402.9 | 0 | 0 | 33068 | 6932 | 0 | 20402.9 | 0 | 0 | 27334.9 | 0 | 0 | 0 | 0
2022031704 | 5 | 0.41025 | 32820 | 0 | 0 | 0.58265 | 20392.75 | 0 | 0 | 32820 | 7180 | 0 | 20392.75 | 0 | 0 | 27572.75 | 0 | 0 | 0 | 0
2022031705 | 5 | 0.41576 | 33260.8 | 0 | 0 | 0.58546 | 20491.1 | 0 | 0 | 33260.8 | 6739.2 | 0 | 20491.1 | 0 | 0 | 27230.3 | 0 | 0 | 0 | 0
2022031706 | 5 | 0.43474 | 34779.2 | 0 | 0 | 0.61451 | 21507.85 | 0 | 0 | 34779.2 | 5220.8 | 0 | 21507.85 | 0 | 0 | 26728.65 | 0 | 0 | 0 | 0
2022031707 | 5 | 0.46362 | 37089.6 | 0 | 0 | 0.64729 | 22655.15 | 0 | 0 | 37089.6 | 2910.4 | 0 | 22655.15 | 0 | 0 | 25565.55 | 0 | 0 | 0 | 0
2022031708 | 5 | 0.48708 | 38966.4 | 0 | 0 | 0.65477 | 22916.95 | 0.00206 | 28.84 | 38966.4 | 1033.6 | 0 | 22916.95 | 0 | 28.84 | 23979.39 | 0 | 0 | 0 | 0
2022031709 | 5 | 0.49686 | 39748.8 | 0 | 0 | 0.63012 | 22054.2 | 0.16365 | 2291.1 | 39748.8 | 251.2 | 0 | 22054.2 | 0 | 2291.1 | 24596.5 | 0 | 0 | 0 | 0
2022031710 | 5 | 0.50389 | 40311.2 | 0 | 0 | 0.57258 | 20040.3 | 0.4527 | 6337.8 | 40000 | 0 | 311.2 | 19729.1 | 0 | 6337.8 | 26066.9 | 0 | 0 | 0 | 0
2022031711 | 5 | 0.51007 | 40805.6 | 0 | 0 | 0.59707 | 20897.45 | 0.41845 | 5858.3 | 40000 | 0 | 805.6 | 20091.85 | 0 | 5858.3 | 25950.15 | 0 | 0 | 0 | 0
2022031712 | 5 | 0.51347 | 41077.6 | 0 | 0 | 0.61017 | 21355.95 | 0.36908 | 5167.12 | 40000 | 0 | 1077.6 | 20278.35 | 0 | 5167.12 | 25445.47 | 0 | 0 | 0 | 0
2022031713 | 5 | 0.51888 | 41510.4 | 0 | 0 | 0.59841 | 20944.35 | 0.35766 | 5007.24 | 40000 | 0 | 1510.4 | 19433.95 | 0 | 5007.24 | 24441.19 | 0 | 0 | 0 | 0
2022031714 | 5 | 0.52534 | 42027.2 | 0 | 0 | 0.57883 | 20259.05 | 0.35795 | 5011.3 | 40000 | 0 | 2027.2 | 18231.85 | 0 | 5011.3 | 23243.15 | 0 | 0 | 0 | 0
2022031715 | 5 | 0.52873 | 42298.4 | 0 | 0 | 0.58751 | 20562.85 | 0.28643 | 4010.02 | 40000 | 0 | 2298.4 | 18264.45 | 0 | 4010.02 | 22274.47 | 0 | 0 | 0 | 0
2022031716 | 5 | 0.53162 | 42529.6 | 0 | 0 | 0.60001 | 21000.35 | 0.25123 | 3517.22 | 40000 | 0 | 2529.6 | 18470.75 | 0 | 3517.22 | 21987.97 | 0 | 0 | 0 | 0
2022031717 | 5 | 0.5336 | 42688 | 0 | 0 | 0.59937 | 20977.95 | 0.18631 | 2608.34 | 40000 | 0 | 2688 | 18289.95 | 0 | 2608.34 | 20898.29 | 0 | 0 | 0 | 0
2022031718 | 5 | 0.53565 | 42852 | 0 | 0 | 0.60263 | 21092.05 | 0.20289 | 2840.46 | 40000 | 0 | 2852 | 18240.05 | 0 | 2840.46 | 21080.51 | 0 | 0 | 0 | 0
2022031719 | 5 | 0.53586 | 42868.8 | 0 | 0 | 0.61527 | 21534.45 | 0.1539 | 2154.6 | 40000 | 0 | 2868.8 | 18665.65 | 0 | 2154.6 | 20820.25 | 0 | 0 | 0 | 0
2022031720 | 5 | 0.53496 | 42796.8 | 0 | 0 | 0.63155 | 22104.25 | 0.02728 | 381.92 | 40000 | 0 | 2796.8 | 19307.45 | 0 | 381.92 | 19689.37 | 0 | 0 | 0 | 0
2022031721 | 5 | 0.53597 | 42877.6 | 0 | 0 | 0.65011 | 22753.85 | 0 | 0 | 40000 | 0 | 2877.6 | 19876.25 | 0 | 0 | 19876.25 | 0 | 0 | 0 | 0
2022031722 | 5 | 0.52521 | 42016.8 | 0 | 0 | 0.64057 | 22419.95 | 0 | 0 | 40000 | 0 | 2016.8 | 20403.15 | 0 | 0 | 20403.15 | 0 | 0 | 0 | 0
2022031723 | 5 | 0.50316 | 40252.8 | 0 | 0 | 0.60414 | 21144.9 | 0 | 0 | 40000 | 0 | 252.8 | 20892.1 | 0 | 0 | 20892.1 | 0 | 0 | 0 | 0
2022031724 | 5 | 0.47628 | 38102.4 | 0 | 0 | 0.57777 | 20221.95 | 0 | 0 | 38102.4 | 1897.6 | 0 | 20221.95 | 0 | 0 | 22119.55 | 0 | 0 | 0 | 0
2022031801 | 6 | 0.45321 | 36256.8 | 0 | 0 | 0.55681 | 19488.35 | 0 | 0 | 36256.8 | 3743.2 | 0 | 19488.35 | 0 | 0 | 23231.55 | 0 | 0 | 0 | 0
2022031802 | 6 | 0.43686 | 34948.8 | 0 | 0 | 0.53599 | 18759.65 | 0 | 0 | 34948.8 | 5051.2 | 0 | 18759.65 | 0 | 0 | 23810.85 | 0 | 0 | 0 | 0
2022031803 | 6 | 0.42654 | 34123.2 | 0 | 0 | 0.51644 | 18075.4 | 0 | 0 | 34123.2 | 5876.8 | 0 | 18075.4 | 0 | 0 | 23952.2 | 0 | 0 | 0 | 0
2022031804 | 6 | 0.42355 | 33884 | 0 | 0 | 0.51376 | 17981.6 | 0 | 0 | 33884 | 6116 | 0 | 17981.6 | 0 | 0 | 24097.6 | 0 | 0 | 0 | 0
2022031805 | 6 | 0.4292 | 34336 | 0 | 0 | 0.5219 | 18266.5 | 0 | 0 | 34336 | 5664 | 0 | 18266.5 | 0 | 0 | 23930.5 | 0 | 0 | 0 | 0
2022031806 | 6 | 0.44739 | 35791.2 | 0 | 0 | 0.54853 | 19198.55 | 0 | 0 | 35791.2 | 4208.8 | 0 | 19198.55 | 0 | 0 | 23407.35 | 0 | 0 | 0 | 0
2022031807 | 6 | 0.47702 | 38161.6 | 0 | 0 | 0.57905 | 20266.75 | 0 | 0 | 38161.6 | 1838.4 | 0 | 20266.75 | 0 | 0 | 22105.15 | 0 | 0 | 0 | 0
2022031808 | 6 | 0.50195 | 40156 | 0 | 0 | 0.59681 | 20888.35 | 0.00103 | 14.42 | 40000 | 0 | 156 | 20732.35 | 0 | 14.42 | 20746.77 | 0 | 0 | 0 | 0
2022031809 | 6 | 0.51406 | 41124.8 | 0 | 0 | 0.57975 | 20291.25 | 0.16924 | 2369.36 | 40000 | 0 | 1124.8 | 19166.45 | 0 | 2369.36 | 21535.81 | 0 | 0 | 0 | 0
2022031810 | 6 | 0.52329 | 41863.2 | 0 | 0 | 0.55776 | 19521.6 | 0.49764 | 6966.96 | 40000 | 0 | 1863.2 | 17658.4 | 0 | 6966.96 | 24625.36 | 0 | 0 | 0 | 0
2022031811 | 6 | 0.5227 | 41816 | 0 | 0 | 0.58164 | 20357.4 | 0.4461 | 6245.4 | 40000 | 0 | 1816 | 18541.4 | 0 | 6245.4 | 24786.8 | 0 | 0 | 0 | 0
2022031812 | 6 | 0.5183 | 41464 | 0 | 0 | 0.55708 | 19497.8 | 0.51936 | 7271.04 | 40000 | 0 | 1464 | 18033.8 | 0 | 7271.04 | 25304.84 | 0 | 0 | 0 | 0
2022031813 | 6 | 0.50969 | 40775.2 | 0 | 0 | 0.47035 | 16462.25 | 0.71976 | 10076.64 | 40000 | 0 | 775.2 | 15687.05 | 0 | 10076.64 | 25763.69 | 0 | 0 | 0 | 0
2022031814 | 6 | 0.50306 | 40244.8 | 0 | 0 | 0.38796 | 13578.6 | 0.80981 | 11337.34 | 40000 | 0 | 244.8 | 13333.8 | 0 | 11337.34 | 24671.14 | 0 | 0 | 0 | 0
2022031815 | 6 | 0.4984 | 39872 | 0 | 0 | 0.32667 | 11433.45 | 0.78356 | 10969.84 | 39872 | 128 | 0 | 11433.45 | 0 | 10969.84 | 22531.29 | 0 | 0 | 0 | 0
2022031816 | 6 | 0.49746 | 39796.8 | 0 | 0 | 0.28781 | 10073.35 | 0.75667 | 10593.38 | 39796.8 | 203.2 | 0 | 10073.35 | 0 | 10593.38 | 20869.93 | 0 | 0 | 0 | 0
2022031817 | 6 | 0.49825 | 39860 | 0 | 0 | 0.25435 | 8902.25 | 0.73069 | 10229.66 | 39860 | 140 | 0 | 8902.25 | 0 | 10229.66 | 19271.91 | 0 | 0 | 0 | 0
2022031818 | 6 | 0.49896 | 39916.8 | 0 | 0 | 0.21497 | 7523.95 | 0.6661 | 9325.4 | 39916.8 | 83.2 | 0 | 7523.95 | 0 | 9325.4 | 16932.55 | 0 | 0 | 0 | 0
2022031819 | 6 | 0.49541 | 39632.8 | 0 | 0 | 0.15824 | 5538.4 | 0.35823 | 5015.22 | 39632.8 | 367.2 | 0 | 5538.4 | 0 | 5015.22 | 10920.82 | 0 | 0 | 0 | 0
2022031820 | 6 | 0.49669 | 39735.2 | 0 | 0 | 0.09257 | 3239.95 | 0.06991 | 978.74 | 39735.2 | 264.8 | 0 | 3239.95 | 0 | 978.74 | 4483.49 | 0 | 0 | 0 | 0
2022031821 | 6 | 0.50522 | 40417.6 | 0 | 0 | 0.06887 | 2410.45 | 8e-05 | 1.12 | 40000 | 0 | 417.6 | 1992.85 | 0 | 1.12 | 1993.97 | 0 | 0 | 0 | 0
2022031822 | 6 | 0.4965 | 39720 | 0 | 0 | 0.06765 | 2367.75 | 0 | 0 | 39720 | 280 | 0 | 2367.75 | 0 | 0 | 2647.75 | 0 | 0 | 0 | 0
2022031823 | 6 | 0.48237 | 38589.6 | 0 | 0 | 0.06143 | 2150.05 | 0 | 0 | 38589.6 | 1410.4 | 0 | 2150.05 | 0 | 0 | 3560.45 | 0 | 0 | 0 | 0
2022031824 | 6 | 0.46459 | 37167.2 | 0 | 0 | 0.0685 | 2397.5 | 0 | 0 | 37167.2 | 2832.8 | 0 | 2397.5 | 0 | 0 | 5230.3 | 0 | 0 | 0 | 0
2022031901 | 7 | 0.44954 | 35963.2 | 0 | 0 | 0.098 | 3430 | 0 | 0 | 35963.2 | 4036.8 | 0 | 3430 | 0 | 0 | 7466.8 | 0 | 0 | 0 | 0
2022031902 | 7 | 0.44022 | 35217.6 | 0 | 0 | 0.11787 | 4125.45 | 0 | 0 | 35217.6 | 4782.4 | 0 | 4125.45 | 0 | 0 | 8907.85 | 0 | 0 | 0 | 0
2022031903 | 7 | 0.43532 | 34825.6 | 0 | 0 | 0.14558 | 5095.3 | 0 | 0 | 34825.6 | 5174.4 | 0 | 5095.3 | 0 | 0 | 10269.7 | 0 | 0 | 0 | 0
2022031904 | 7 | 0.4346 | 34768 | 0 | 0 | 0.17127 | 5994.45 | 0 | 0 | 34768 | 5232 | 0 | 5994.45 | 0 | 0 | 11226.45 | 0 | 0 | 0 | 0
2022031905 | 7 | 0.44095 | 35276 | 0 | 0 | 0.19986 | 6995.1 | 0 | 0 | 35276 | 4724 | 0 | 6995.1 | 0 | 0 | 11719.1 | 0 | 0 | 0 | 0
2022031906 | 7 | 0.45437 | 36349.6 | 0 | 0 | 0.23783 | 8324.05 | 0 | 0 | 36349.6 | 3650.4 | 0 | 8324.05 | 0 | 0 | 11974.45 | 0 | 0 | 0 | 0
2022031907 | 7 | 0.47674 | 38139.2 | 0 | 0 | 0.27229 | 9530.15 | 0 | 0 | 38139.2 | 1860.8 | 0 | 9530.15 | 0 | 0 | 11390.95 | 0 | 0 | 0 | 0
2022031908 | 7 | 0.49826 | 39860.8 | 0 | 0 | 0.31757 | 11114.95 | 0.00391 | 54.74 | 39860.8 | 139.2 | 0 | 11114.95 | 0 | 54.74 | 11308.89 | 0 | 0 | 0 | 0
2022031909 | 7 | 0.51224 | 40979.2 | 0 | 0 | 0.34538 | 12088.3 | 0.23567 | 3299.38 | 40000 | 0 | 979.2 | 11109.1 | 0 | 3299.38 | 14408.48 | 0 | 0 | 0 | 0
2022031910 | 7 | 0.50871 | 40696.8 | 0 | 0 | 0.28694 | 10042.9 | 0.75191 | 10526.74 | 40000 | 0 | 696.8 | 9346.1 | 0 | 10526.74 | 19872.84 | 0 | 0 | 0 | 0
2022031911 | 7 | 0.50045 | 40036 | 0 | 0 | 0.32466 | 11363.1 | 0.85844 | 12018.16 | 40000 | 0 | 36 | 11327.1 | 0 | 12018.16 | 23345.26 | 0 | 0 | 0 | 0
2022031912 | 7 | 0.4874 | 38992 | 0 | 0 | 0.32568 | 11398.8 | 0.86894 | 12165.16 | 38992 | 1008 | 0 | 11398.8 | 0 | 12165.16 | 24571.96 | 0 | 0 | 0 | 0
2022031913 | 7 | 0.47789 | 38231.2 | 0 | 0 | 0.27282 | 9548.7 | 0.87767 | 12287.38 | 38231.2 | 1768.8 | 0 | 9548.7 | 0 | 12287.38 | 23604.88 | 0 | 0 | 0 | 0
2022031914 | 7 | 0.47132 | 37705.6 | 0 | 0 | 0.20626 | 7219.1 | 0.87481 | 12247.34 | 37705.6 | 2294.4 | 0 | 7219.1 | 0 | 12247.34 | 21760.84 | 0 | 0 | 0 | 0
2022031915 | 7 | 0.47089 | 37671.2 | 0 | 0 | 0.18128 | 6344.8 | 0.87362 | 12230.68 | 37671.2 | 2328.8 | 0 | 6344.8 | 0 | 12230.68 | 20904.28 | 0 | 0 | 0 | 0
2022031916 | 7 | 0.47457 | 37965.6 | 0 | 0 | 0.19403 | 6791.05 | 0.87425 | 12239.5 | 37965.6 | 2034.4 | 0 | 6791.05 | 0 | 12239.5 | 21064.95 | 0 | 0 | 0 | 0
2022031917 | 7 | 0.48342 | 38673.6 | 0 | 0 | 0.21115 | 7390.25 | 0.86782 | 12149.48 | 38673.6 | 1326.4 | 0 | 7390.25 | 0 | 12149.48 | 20866.13 | 0 | 0 | 0 | 0
2022031918 | 7 | 0.49158 | 39326.4 | 0 | 0 | 0.21819 | 7636.65 | 0.80543 | 11276.02 | 39326.4 | 673.6 | 0 | 7636.65 | 0 | 11276.02 | 19586.27 | 0 | 0 | 0 | 0
2022031919 | 7 | 0.49282 | 39425.6 | 0 | 0 | 0.22227 | 7779.45 | 0.5197 | 7275.8 | 39425.6 | 574.4 | 0 | 7779.45 | 0 | 7275.8 | 15629.65 | 0 | 0 | 0 | 0
2022031920 | 7 | 0.49126 | 39300.8 | 0 | 0 | 0.21867 | 7653.45 | 0.07396 | 1035.44 | 39300.8 | 699.2 | 0 | 7653.45 | 0 | 1035.44 | 9388.09 | 0 | 0 | 0 | 0
2022031921 | 7 | 0.49312 | 39449.6 | 0 | 0 | 0.26488 | 9270.8 | 0 | 0 | 39449.6 | 550.4 | 0 | 9270.8 | 0 | 0 | 9821.2 | 0 | 0 | 0 | 0
2022031922 | 7 | 0.48275 | 38620 | 0 | 0 | 0.37942 | 13279.7 | 0 | 0 | 38620 | 1380 | 0 | 13279.7 | 0 | 0 | 14659.7 | 0 | 0 | 0 | 0
2022031923 | 7 | 0.46705 | 37364 | 0 | 0 | 0.48181 | 16863.35 | 0 | 0 | 37364 | 2636 | 0 | 16863.35 | 0 | 0 | 19499.35 | 0 | 0 | 0 | 0
2022031924 | 7 | 0.44948 | 35958.4 | 0 | 0 | 0.55133 | 19296.55 | 0 | 0 | 35958.4 | 4041.6 | 0 | 19296.55 | 0 | 0 | 23338.15 | 0 | 0 | 0 | 0
2022032001 | 1 | 0.43274 | 34619.2 | 0 | 0 | 0.57623 | 20168.05 | 0 | 0 | 34619.2 | 5380.8 | 0 | 20168.05 | 0 | 0 | 25548.85 | 0 | 0 | 0 | 0
2022032002 | 1 | 0.42062 | 33649.6 | 0 | 0 | 0.56784 | 19874.4 | 0 | 0 | 33649.6 | 6350.4 | 0 | 19874.4 | 0 | 0 | 26224.8 | 0 | 0 | 0 | 0
2022032003 | 1 | 0.41222 | 32977.6 | 0 | 0 | 0.55518 | 19431.3 | 0 | 0 | 32977.6 | 7022.4 | 0 | 19431.3 | 0 | 0 | 26453.7 | 0 | 0 | 0 | 0
2022032004 | 1 | 0.41104 | 32883.2 | 0 | 0 | 0.55319 | 19361.65 | 0 | 0 | 32883.2 | 7116.8 | 0 | 19361.65 | 0 | 0 | 26478.45 | 0 | 0 | 0 | 0
2022032005 | 1 | 0.41332 | 33065.6 | 0 | 0 | 0.5491 | 19218.5 | 0 | 0 | 33065.6 | 6934.4 | 0 | 19218.5 | 0 | 0 | 26152.9 | 0 | 0 | 0 | 0
2022032006 | 1 | 0.42055 | 33644 | 0 | 0 | 0.54482 | 19068.7 | 0 | 0 | 33644 | 6356 | 0 | 19068.7 | 0 | 0 | 25424.7 | 0 | 0 | 0 | 0
2022032007 | 1 | 0.43506 | 34804.8 | 0 | 0 | 0.55423 | 19398.05 | 0 | 0 | 34804.8 | 5195.2 | 0 | 19398.05 | 0 | 0 | 24593.25 | 0 | 0 | 0 | 0
2022032008 | 1 | 0.45301 | 36240.8 | 0 | 0 | 0.56244 | 19685.4 | 0.00324 | 45.36 | 36240.8 | 3759.2 | 0 | 19685.4 | 0 | 45.36 | 23489.96 | 0 | 0 | 0 | 0
2022032009 | 1 | 0.46702 | 37361.6 | 0 | 0 | 0.55026 | 19259.1 | 0.1457 | 2039.8 | 37361.6 | 2638.4 | 0 | 19259.1 | 0 | 2039.8 | 23937.3 | 0 | 0 | 0 | 0
2022032010 | 1 | 0.47142 | 37713.6 | 0 | 0 | 0.51511 | 18028.85 | 0.36347 | 5088.58 | 37713.6 | 2286.4 | 0 | 18028.85 | 0 | 5088.58 | 25403.83 | 0 | 0 | 0 | 0
2022032011 | 1 | 0.47225 | 37780 | 0 | 0 | 0.57329 | 20065.15 | 0.31524 | 4413.36 | 37780 | 2220 | 0 | 20065.15 | 0 | 4413.36 | 26698.51 | 0 | 0 | 0 | 0
2022032012 | 1 | 0.47148 | 37718.4 | 0 | 0 | 0.61894 | 21662.9 | 0.2583 | 3616.2 | 37718.4 | 2281.6 | 0 | 21662.9 | 0 | 3616.2 | 27560.7 | 0 | 0 | 0 | 0
2022032013 | 1 | 0.47243 | 37794.4 | 0 | 0 | 0.63638 | 22273.3 | 0.23458 | 3284.12 | 37794.4 | 2205.6 | 0 | 22273.3 | 0 | 3284.12 | 27763.02 | 0 | 0 | 0 | 0
2022032014 | 1 | 0.47501 | 38000.8 | 0 | 0 | 0.64289 | 22501.15 | 0.23955 | 3353.7 | 38000.8 | 1999.2 | 0 | 22501.15 | 0 | 3353.7 | 27854.05 | 0 | 0 | 0 | 0
2022032015 | 1 | 0.47982 | 38385.6 | 0 | 0 | 0.64624 | 22618.4 | 0.25144 | 3520.16 | 38385.6 | 1614.4 | 0 | 22618.4 | 0 | 3520.16 | 27752.96 | 0 | 0 | 0 | 0
2022032016 | 1 | 0.48809 | 39047.2 | 0 | 0 | 0.65222 | 22827.7 | 0.24898 | 3485.72 | 39047.2 | 952.8 | 0 | 22827.7 | 0 | 3485.72 | 27266.22 | 0 | 0 | 0 | 0
2022032017 | 1 | 0.49751 | 39800.8 | 0 | 0 | 0.65898 | 23064.3 | 0.24615 | 3446.1 | 39800.8 | 199.2 | 0 | 23064.3 | 0 | 3446.1 | 26709.6 | 0 | 0 | 0 | 0
2022032018 | 1 | 0.50692 | 40553.6 | 0 | 0 | 0.66193 | 23167.55 | 0.26085 | 3651.9 | 40000 | 0 | 553.6 | 22613.95 | 0 | 3651.9 | 26265.85 | 0 | 0 | 0 | 0
2022032019 | 1 | 0.51101 | 40880.8 | 0 | 0 | 0.67232 | 23531.2 | 0.16208 | 2269.12 | 40000 | 0 | 880.8 | 22650.4 | 0 | 2269.12 | 24919.52 | 0 | 0 | 0 | 0
2022032020 | 1 | 0.5156 | 41248 | 0 | 0 | 0.68646 | 24026.1 | 0.03046 | 426.44 | 40000 | 0 | 1248 | 22778.1 | 0 | 426.44 | 23204.54 | 0 | 0 | 0 | 0
2022032021 | 1 | 0.5265 | 42120 | 0 | 0 | 0.6921 | 24223.5 | 0 | 0 | 40000 | 0 | 2120 | 22103.5 | 0 | 0 | 22103.5 | 0 | 0 | 0 | 0
2022032022 | 1 | 0.51517 | 41213.6 | 0 | 0 | 0.69397 | 24288.95 | 0 | 0 | 40000 | 0 | 1213.6 | 23075.35 | 0 | 0 | 23075.35 | 0 | 0 | 0 | 0
2022032023 | 1 | 0.48987 | 39189.6 | 0 | 0 | 0.68084 | 23829.4 | 0 | 0 | 39189.6 | 810.4 | 0 | 23829.4 | 0 | 0 | 24639.8 | 0 | 0 | 0 | 0
2022032024 | 1 | 0.4587 | 36696 | 0 | 0 | 0.65097 | 22783.95 | 0 | 0 | 36696 | 3304 | 0 | 22783.95 | 0 | 0 | 26087.95 | 0 | 0 | 0 | 0
2022032101 | 2 | 0.43385 | 34708 | 0 | 0 | 0.62875 | 22006.25 | 0 | 0 | 34708 | 5292 | 0 | 22006.25 | 0 | 0 | 27298.25 | 0 | 0 | 0 | 0
2022032102 | 2 | 0.41796 | 33436.8 | 0 | 0 | 0.61499 | 21524.65 | 0 | 0 | 33436.8 | 6563.2 | 0 | 21524.65 | 0 | 0 | 28087.85 | 0 | 0 | 0 | 0
2022032103 | 2 | 0.41143 | 32914.4 | 0 | 0 | 0.60516 | 21180.6 | 0 | 0 | 32914.4 | 7085.6 | 0 | 21180.6 | 0 | 0 | 28266.2 | 0 | 0 | 0 | 0
2022032104 | 2 | 0.41104 | 32883.2 | 0 | 0 | 0.60721 | 21252.35 | 0 | 0 | 32883.2 | 7116.8 | 0 | 21252.35 | 0 | 0 | 28369.15 | 0 | 0 | 0 | 0
2022032105 | 2 | 0.41711 | 33368.8 | 0 | 0 | 0.60934 | 21326.9 | 0 | 0 | 33368.8 | 6631.2 | 0 | 21326.9 | 0 | 0 | 27958.1 | 0 | 0 | 0 | 0
2022032106 | 2 | 0.43785 | 35028 | 0 | 0 | 0.61671 | 21584.85 | 0 | 0 | 35028 | 4972 | 0 | 21584.85 | 0 | 0 | 26556.85 | 0 | 0 | 0 | 0
2022032107 | 2 | 0.4755 | 38040 | 0 | 0 | 0.6493 | 22725.5 | 0 | 0 | 38040 | 1960 | 0 | 22725.5 | 0 | 0 | 24685.5 | 0 | 0 | 0 | 0
2022032108 | 2 | 0.49952 | 39961.6 | 0 | 0 | 0.63567 | 22248.45 | 0.00018 | 2.52 | 39961.6 | 38.4 | 0 | 22248.45 | 0 | 2.52 | 22289.37 | 0 | 0 | 0 | 0
2022032109 | 2 | 0.50486 | 40388.8 | 0 | 0 | 0.56407 | 19742.45 | 0.0779 | 1090.6 | 40000 | 0 | 388.8 | 19353.65 | 0 | 1090.6 | 20444.25 | 0 | 0 | 0 | 0
2022032110 | 2 | 0.51521 | 41216.8 | 0 | 0 | 0.53467 | 18713.45 | 0.24772 | 3468.08 | 40000 | 0 | 1216.8 | 17496.65 | 0 | 3468.08 | 20964.73 | 0 | 0 | 0 | 0
2022032111 | 2 | 0.52921 | 42336.8 | 0 | 0 | 0.5813 | 20345.5 | 0.32099 | 4493.86 | 40000 | 0 | 2336.8 | 18008.7 | 0 | 4493.86 | 22502.56 | 0 | 0 | 0 | 0
2022032112 | 2 | 0.54076 | 43260.8 | 0 | 0 | 0.56607 | 19812.45 | 0.34618 | 4846.52 | 40000 | 0 | 3260.8 | 16551.65 | 0 | 4846.52 | 21398.17 | 0 | 0 | 0 | 0
2022032113 | 2 | 0.54478 | 43582.4 | 0 | 0 | 0.51838 | 18143.3 | 0.4555 | 6377 | 40000 | 0 | 3582.4 | 14560.9 | 0 | 6377 | 20937.9 | 0 | 0 | 0 | 0
2022032114 | 2 | 0.5475 | 43800 | 0 | 0 | 0.50056 | 17519.6 | 0.46733 | 6542.62 | 40000 | 0 | 3800 | 13719.6 | 0 | 6542.62 | 20262.22 | 0 | 0 | 0 | 0
2022032115 | 2 | 0.54749 | 43799.2 | 0 | 0 | 0.49433 | 17301.55 | 0.43479 | 6087.06 | 40000 | 0 | 3799.2 | 13502.35 | 0 | 6087.06 | 19589.41 | 0 | 0 | 0 | 0
2022032116 | 2 | 0.55002 | 44001.6 | 0 | 0 | 0.52023 | 18208.05 | 0.41444 | 5802.16 | 40000 | 0 | 4001.6 | 14206.45 | 0 | 5802.16 | 20008.61 | 0 | 0 | 0 | 0
2022032117 | 2 | 0.55619 | 44495.2 | 0 | 0 | 0.54325 | 19013.75 | 0.3436 | 4810.4 | 40000 | 0 | 4495.2 | 14518.55 | 0 | 4810.4 | 19328.95 | 0 | 0 | 0 | 0
2022032118 | 2 | 0.56335 | 45068 | 0 | 0 | 0.58895 | 20613.25 | 0.23543 | 3296.02 | 40000 | 0 | 5068 | 15545.25 | 0 | 3296.02 | 18841.27 | 0 | 0 | 0 | 0
2022032119 | 2 | 0.55859 | 44687.2 | 0 | 0 | 0.59945 | 20980.75 | 0.17078 | 2390.92 | 40000 | 0 | 4687.2 | 16293.55 | 0 | 2390.92 | 18684.47 | 0 | 0 | 0 | 0
2022032120 | 2 | 0.55288 | 44230.4 | 0 | 0 | 0.62545 | 21890.75 | 0.0432 | 604.8 | 40000 | 0 | 4230.4 | 17660.35 | 0 | 604.8 | 18265.15 | 0 | 0 | 0 | 0
2022032121 | 2 | 0.5521 | 44168 | 0 | 0 | 0.599 | 20965 | 0 | 0 | 40000 | 0 | 4168 | 16797 | 0 | 0 | 16797 | 0 | 0 | 0 | 0
2022032122 | 2 | 0.53871 | 43096.8 | 0 | 0 | 0.60709 | 21248.15 | 0 | 0 | 40000 | 0 | 3096.8 | 18151.35 | 0 | 0 | 18151.35 | 0 | 0 | 0 | 0
2022032123 | 2 | 0.51332 | 41065.6 | 0 | 0 | 0.59244 | 20735.4 | 0 | 0 | 40000 | 0 | 1065.6 | 19669.8 | 0 | 0 | 19669.8 | 0 | 0 | 0 | 0
2022032124 | 2 | 0.48083 | 38466.4 | 0 | 0 | 0.5432 | 19012 | 0 | 0 | 38466.4 | 1533.6 | 0 | 19012 | 0 | 0 | 20545.6 | 0 | 0 | 0 | 0
2022032201 | 3 | 0.45287 | 36229.6 | 0 | 0 | 0.48684 | 17039.4 | 0 | 0 | 36229.6 | 3770.4 | 0 | 17039.4 | 0 | 0 | 20809.8 | 0 | 0 | 0 | 0
2022032202 | 3 | 0.43783 | 35026.4 | 0 | 0 | 0.47601 | 16660.35 | 0 | 0 | 35026.4 | 4973.6 | 0 | 16660.35 | 0 | 0 | 21633.95 | 0 | 0 | 0 | 0
2022032203 | 3 | 0.42948 | 34358.4 | 0 | 0 | 0.54479 | 19067.65 | 0 | 0 | 34358.4 | 5641.6 | 0 | 19067.65 | 0 | 0 | 24709.25 | 0 | 0 | 0 | 0
2022032204 | 3 | 0.42732 | 34185.6 | 0 | 0 | 0.56619 | 19816.65 | 0 | 0 | 34185.6 | 5814.4 | 0 | 19816.65 | 0 | 0 | 25631.05 | 0 | 0 | 0 | 0
2022032205 | 3 | 0.43178 | 34542.4 | 0 | 0 | 0.58163 | 20357.05 | 0 | 0 | 34542.4 | 5457.6 | 0 | 20357.05 | 0 | 0 | 25814.65 | 0 | 0 | 0 | 0
2022032206 | 3 | 0.45212 | 36169.6 | 0 | 0 | 0.57927 | 20274.45 | 0 | 0 | 36169.6 | 3830.4 | 0 | 20274.45 | 0 | 0 | 24104.85 | 0 | 0 | 0 | 0
2022032207 | 3 | 0.49 | 39200 | 0 | 0 | 0.59751 | 20912.85 | 0 | 0 | 39200 | 800 | 0 | 20912.85 | 0 | 0 | 21712.85 | 0 | 0 | 0 | 0
2022032208 | 3 | 0.51144 | 40915.2 | 0 | 0 | 0.62495 | 21873.25 | 0.00062 | 8.68 | 40000 | 0 | 915.2 | 20958.05 | 0 | 8.68 | 20966.73 | 0 | 0 | 0 | 0
2022032209 | 3 | 0.51111 | 40888.8 | 0 | 0 | 0.61224 | 21428.4 | 0.06094 | 853.16 | 40000 | 0 | 888.8 | 20539.6 | 0 | 853.16 | 21392.76 | 0 | 0 | 0 | 0
2022032210 | 3 | 0.51618 | 41294.4 | 0 | 0 | 0.6115 | 21402.5 | 0.16636 | 2329.04 | 40000 | 0 | 1294.4 | 20108.1 | 0 | 2329.04 | 22437.14 | 0 | 0 | 0 | 0
2022032211 | 3 | 0.52201 | 41760.8 | 0 | 0 | 0.63666 | 22283.1 | 0.20501 | 2870.14 | 40000 | 0 | 1760.8 | 20522.3 | 0 | 2870.14 | 23392.44 | 0 | 0 | 0 | 0
2022032212 | 3 | 0.52825 | 42260 | 0 | 0 | 0.64751 | 22662.85 | 0.22752 | 3185.28 | 40000 | 0 | 2260 | 20402.85 | 0 | 3185.28 | 23588.13 | 0 | 0 | 0 | 0
2022032213 | 3 | 0.53182 | 42545.6 | 0 | 0 | 0.64925 | 22723.75 | 0.21864 | 3060.96 | 40000 | 0 | 2545.6 | 20178.15 | 0 | 3060.96 | 23239.11 | 0 | 0 | 0 | 0
2022032214 | 3 | 0.5355 | 42840 | 0 | 0 | 0.64351 | 22522.85 | 0.2378 | 3329.2 | 40000 | 0 | 2840 | 19682.85 | 0 | 3329.2 | 23012.05 | 0 | 0 | 0 | 0
2022032215 | 3 | 0.53591 | 42872.8 | 0 | 0 | 0.63806 | 22332.1 | 0.24448 | 3422.72 | 40000 | 0 | 2872.8 | 19459.3 | 0 | 3422.72 | 22882.02 | 0 | 0 | 0 | 0
2022032216 | 3 | 0.53728 | 42982.4 | 0 | 0 | 0.64622 | 22617.7 | 0.20657 | 2891.98 | 40000 | 0 | 2982.4 | 19635.3 | 0 | 2891.98 | 22527.28 | 0 | 0 | 0 | 0
2022032217 | 3 | 0.54419 | 43535.2 | 0 | 0 | 0.66237 | 23182.95 | 0.16049 | 2246.86 | 40000 | 0 | 3535.2 | 19647.75 | 0 | 2246.86 | 21894.61 | 0 | 0 | 0 | 0
2022032218 | 3 | 0.55169 | 44135.2 | 0 | 0 | 0.67108 | 23487.8 | 0.14707 | 2058.98 | 40000 | 0 | 4135.2 | 19352.6 | 0 | 2058.98 | 21411.58 | 0 | 0 | 0 | 0
2022032219 | 3 | 0.55254 | 44203.2 | 0 | 0 | 0.6587 | 23054.5 | 0.0957 | 1339.8 | 40000 | 0 | 4203.2 | 18851.3 | 0 | 1339.8 | 20191.1 | 0 | 0 | 0 | 0
2022032220 | 3 | 0.55672 | 44537.6 | 0 | 0 | 0.64909 | 22718.15 | 0.02372 | 332.08 | 40000 | 0 | 4537.6 | 18180.55 | 0 | 332.08 | 18512.63 | 0 | 0 | 0 | 0
2022032221 | 3 | 0.56235 | 44988 | 0 | 0 | 0.58349 | 20422.15 | 0 | 0 | 40000 | 0 | 4988 | 15434.15 | 0 | 0 | 15434.15 | 0 | 0 | 0 | 0
2022032222 | 3 | 0.54677 | 43741.6 | 0 | 0 | 0.5432 | 19012 | 0 | 0 | 40000 | 0 | 3741.6 | 15270.4 | 0 | 0 | 15270.4 | 0 | 0 | 0 | 0
2022032223 | 3 | 0.51812 | 41449.6 | 0 | 0 | 0.5383 | 18840.5 | 0 | 0 | 40000 | 0 | 1449.6 | 17390.9 | 0 | 0 | 17390.9 | 0 | 0 | 0 | 0
2022032224 | 3 | 0.48767 | 39013.6 | 0 | 0 | 0.5695 | 19932.5 | 0 | 0 | 39013.6 | 986.4 | 0 | 19932.5 | 0 | 0 | 20918.9 | 0 | 0 | 0 | 0
2022032301 | 4 | 0.46731 | 37384.8 | 0 | 0 | 0.58702 | 20545.7 | 0 | 0 | 37384.8 | 2615.2 | 0 | 20545.7 | 0 | 0 | 23160.9 | 0 | 0 | 0 | 0
2022032302 | 4 | 0.45711 | 36568.8 | 0 | 0 | 0.5763 | 20170.5 | 0 | 0 | 36568.8 | 3431.2 | 0 | 20170.5 | 0 | 0 | 23601.7 | 0 | 0 | 0 | 0
2022032303 | 4 | 0.45314 | 36251.2 | 0 | 0 | 0.55877 | 19556.95 | 0 | 0 | 36251.2 | 3748.8 | 0 | 19556.95 | 0 | 0 | 23305.75 | 0 | 0 | 0 | 0
2022032304 | 4 | 0.45522 | 36417.6 | 0 | 0 | 0.54554 | 19093.9 | 0 | 0 | 36417.6 | 3582.4 | 0 | 19093.9 | 0 | 0 | 22676.3 | 0 | 0 | 0 | 0
2022032305 | 4 | 0.46719 | 37375.2 | 0 | 0 | 0.53147 | 18601.45 | 0 | 0 | 37375.2 | 2624.8 | 0 | 18601.45 | 0 | 0 | 21226.25 | 0 | 0 | 0 | 0
2022032306 | 4 | 0.49644 | 39715.2 | 0 | 0 | 0.52378 | 18332.3 | 0 | 0 | 39715.2 | 284.8 | 0 | 18332.3 | 0 | 0 | 18617.1 | 0 | 0 | 0 | 0
2022032307 | 4 | 0.54642 | 43713.6 | 0 | 0 | 0.53128 | 18594.8 | 0 | 0 | 40000 | 0 | 3713.6 | 14881.2 | 0 | 0 | 14881.2 | 0 | 0 | 0 | 0
2022032308 | 4 | 0.57317 | 45853.6 | 0 | 0 | 0.52001 | 18200.35 | 0.00652 | 91.28 | 40000 | 0 | 5853.6 | 12346.75 | 0 | 91.28 | 12438.03 | 0 | 0 | 0 | 0
2022032309 | 4 | 0.56332 | 45065.6 | 0 | 0 | 0.45128 | 15794.8 | 0.26757 | 3745.98 | 40000 | 0 | 5065.6 | 10729.2 | 0 | 3745.98 | 14475.18 | 0 | 0 | 0 | 0
2022032310 | 4 | 0.55001 | 44000.8 | 0 | 0 | 0.38381 | 13433.35 | 0.69823 | 9775.22 | 40000 | 0 | 4000.8 | 9432.55 | 0 | 9775.22 | 19207.77 | 0 | 0 | 0 | 0
2022032311 | 4 | 0.53506 | 42804.8 | 0 | 0 | 0.38206 | 13372.1 | 0.75171 | 10523.94 | 40000 | 0 | 2804.8 | 10567.3 | 0 | 10523.94 | 21091.24 | 0 | 0 | 0 | 0
2022032312 | 4 | 0.52293 | 41834.4 | 0 | 0 | 0.40546 | 14191.1 | 0.75682 | 10595.48 | 40000 | 0 | 1834.4 | 12356.7 | 0 | 10595.48 | 22952.18 | 0 | 0 | 0 | 0
2022032313 | 4 | 0.51437 | 41149.6 | 0 | 0 | 0.45402 | 15890.7 | 0.60704 | 8498.56 | 40000 | 0 | 1149.6 | 14741.1 | 0 | 8498.56 | 23239.66 | 0 | 0 | 0 | 0
2022032314 | 4 | 0.50726 | 40580.8 | 0 | 0 | 0.48464 | 16962.4 | 0.44534 | 6234.76 | 40000 | 0 | 580.8 | 16381.6 | 0 | 6234.76 | 22616.36 | 0 | 0 | 0 | 0
2022032315 | 4 | 0.50023 | 40018.4 | 0 | 0 | 0.49605 | 17361.75 | 0.40618 | 5686.52 | 40000 | 0 | 18.4 | 17343.35 | 0 | 5686.52 | 23029.87 | 0 | 0 | 0 | 0
2022032316 | 4 | 0.49861 | 39888.8 | 0 | 0 | 0.49079 | 17177.65 | 0.40685 | 5695.9 | 39888.8 | 111.2 | 0 | 17177.65 | 0 | 5695.9 | 22984.75 | 0 | 0 | 0 | 0
2022032317 | 4 | 0.49967 | 39973.6 | 0 | 0 | 0.4972 | 17402 | 0.36906 | 5166.84 | 39973.6 | 26.4 | 0 | 17402 | 0 | 5166.84 | 22595.24 | 0 | 0 | 0 | 0
2022032318 | 4 | 0.50263 | 40210.4 | 0 | 0 | 0.48825 | 17088.75 | 0.3503 | 4904.2 | 40000 | 0 | 210.4 | 16878.35 | 0 | 4904.2 | 21782.55 | 0 | 0 | 0 | 0
2022032319 | 4 | 0.50315 | 40252 | 0 | 0 | 0.47609 | 16663.15 | 0.23307 | 3262.98 | 40000 | 0 | 252 | 16411.15 | 0 | 3262.98 | 19674.13 | 0 | 0 | 0 | 0
2022032320 | 4 | 0.5114 | 40912 | 0 | 0 | 0.41657 | 14579.95 | 0.07478 | 1046.92 | 40000 | 0 | 912 | 13667.95 | 0 | 1046.92 | 14714.87 | 0 | 0 | 0 | 0
2022032321 | 4 | 0.52551 | 42040.8 | 0 | 0 | 0.32682 | 11438.7 | 0.00019 | 2.66 | 40000 | 0 | 2040.8 | 9397.9 | 0 | 2.66 | 9400.56 | 0 | 0 | 0 | 0
2022032322 | 4 | 0.51564 | 41251.2 | 0 | 0 | 0.25095 | 8783.25 | 0 | 0 | 40000 | 0 | 1251.2 | 7532.05 | 0 | 0 | 7532.05 | 0 | 0 | 0 | 0
2022032323 | 4 | 0.4937 | 39496 | 0 | 0 | 0.22641 | 7924.35 | 0 | 0 | 39496 | 504 | 0 | 7924.35 | 0 | 0 | 8428.35 | 0 | 0 | 0 | 0
2022032324 | 4 | 0.46845 | 37476 | 0 | 0 | 0.18723 | 6553.05 | 0 | 0 | 37476 | 2524 | 0 | 6553.05 | 0 | 0 | 9077.05 | 0 | 0 | 0 | 0
2022032401 | 5 | 0.45257 | 36205.6 | 0 | 0 | 0.15054 | 5268.9 | 0 | 0 | 36205.6 | 3794.4 | 0 | 5268.9 | 0 | 0 | 9063.3 | 0 | 0 | 0 | 0
2022032402 | 5 | 0.4455 | 35640 | 0 | 0 | 0.14977 | 5241.95 | 0 | 0 | 35640 | 4360 | 0 | 5241.95 | 0 | 0 | 9601.95 | 0 | 0 | 0 | 0
2022032403 | 5 | 0.44545 | 35636 | 0 | 0 | 0.2148 | 7518 | 0 | 0 | 35636 | 4364 | 0 | 7518 | 0 | 0 | 11882 | 0 | 0 | 0 | 0
2022032404 | 5 | 0.4516 | 36128 | 0 | 0 | 0.27656 | 9679.6 | 0 | 0 | 36128 | 3872 | 0 | 9679.6 | 0 | 0 | 13551.6 | 0 | 0 | 0 | 0
2022032405 | 5 | 0.46613 | 37290.4 | 0 | 0 | 0.3268 | 11438 | 0 | 0 | 37290.4 | 2709.6 | 0 | 11438 | 0 | 0 | 14147.6 | 0 | 0 | 0 | 0
2022032406 | 5 | 0.49978 | 39982.4 | 0 | 0 | 0.37898 | 13264.3 | 0 | 0 | 39982.4 | 17.6 | 0 | 13264.3 | 0 | 0 | 13281.9 | 0 | 0 | 0 | 0
2022032407 | 5 | 0.55306 | 44244.8 | 0 | 0 | 0.41039 | 14363.65 | 0 | 0 | 40000 | 0 | 4244.8 | 10118.85 | 0 | 0 | 10118.85 | 0 | 0 | 0 | 0
2022032408 | 5 | 0.58218 | 46574.4 | 0 | 0 | 0.41327 | 14464.45 | 0.0075 | 105 | 40000 | 0 | 6574.4 | 7890.05 | 0 | 105 | 7995.05 | 0 | 0 | 0 | 0
2022032409 | 5 | 0.57051 | 45640.8 | 0 | 0 | 0.3725 | 13037.5 | 0.29163 | 4082.82 | 40000 | 0 | 5640.8 | 7396.7 | 0 | 4082.82 | 11479.52 | 0 | 0 | 0 | 0
2022032410 | 5 | 0.54866 | 43892.8 | 0 | 0 | 0.22375 | 7831.25 | 0.78711 | 11019.54 | 40000 | 0 | 3892.8 | 3938.45 | 0 | 11019.54 | 14957.99 | 0 | 0 | 0 | 0
2022032411 | 5 | 0.5312 | 42496 | 0 | 0 | 0.20179 | 7062.65 | 0.86261 | 12076.54 | 40000 | 0 | 2496 | 4566.65 | 0 | 12076.54 | 16643.19 | 0 | 0 | 0 | 0
2022032412 | 5 | 0.51639 | 41311.2 | 0 | 0 | 0.30725 | 10753.75 | 0.84957 | 11893.98 | 40000 | 0 | 1311.2 | 9442.55 | 0 | 11893.98 | 21336.53 | 0 | 0 | 0 | 0
2022032413 | 5 | 0.50698 | 40558.4 | 0 | 0 | 0.42552 | 14893.2 | 0.66636 | 9329.04 | 40000 | 0 | 558.4 | 14334.8 | 0 | 9329.04 | 23663.84 | 0 | 0 | 0 | 0
2022032414 | 5 | 0.50241 | 40192.8 | 0 | 0 | 0.47172 | 16510.2 | 0.56529 | 7914.06 | 40000 | 0 | 192.8 | 16317.4 | 0 | 7914.06 | 24231.46 | 0 | 0 | 0 | 0
2022032415 | 5 | 0.49844 | 39875.2 | 0 | 0 | 0.47172 | 16510.2 | 0.52432 | 7340.48 | 39875.2 | 124.8 | 0 | 16510.2 | 0 | 7340.48 | 23975.48 | 0 | 0 | 0 | 0
2022032416 | 5 | 0.49762 | 39809.6 | 0 | 0 | 0.45308 | 15857.8 | 0.53319 | 7464.66 | 39809.6 | 190.4 | 0 | 15857.8 | 0 | 7464.66 | 23512.86 | 0 | 0 | 0 | 0
2022032417 | 5 | 0.50158 | 40126.4 | 0 | 0 | 0.41119 | 14391.65 | 0.67109 | 9395.26 | 40000 | 0 | 126.4 | 14265.25 | 0 | 9395.26 | 23660.51 | 0 | 0 | 0 | 0
2022032418 | 5 | 0.50522 | 40417.6 | 0 | 0 | 0.33613 | 11764.55 | 0.79633 | 11148.62 | 40000 | 0 | 417.6 | 11346.95 | 0 | 11148.62 | 22495.57 | 0 | 0 | 0 | 0
2022032419 | 5 | 0.50289 | 40231.2 | 0 | 0 | 0.21246 | 7436.1 | 0.63753 | 8925.42 | 40000 | 0 | 231.2 | 7204.9 | 0 | 8925.42 | 16130.32 | 0 | 0 | 0 | 0
2022032420 | 5 | 0.50657 | 40525.6 | 0 | 0 | 0.08432 | 2951.2 | 0.14287 | 2000.18 | 40000 | 0 | 525.6 | 2425.6 | 0 | 2000.18 | 4425.78 | 0 | 0 | 0 | 0
2022032421 | 5 | 0.51856 | 41484.8 | 0 | 0 | 0.05878 | 2057.3 | 0.00019 | 2.66 | 40000 | 0 | 1484.8 | 572.5 | 0 | 2.66 | 575.16 | 0 | 0 | 0 | 0
2022032422 | 5 | 0.50849 | 40679.2 | 0 | 0 | 0.08469 | 2964.15 | 0 | 0 | 40000 | 0 | 679.2 | 2284.95 | 0 | 0 | 2284.95 | 0 | 0 | 0 | 0
2022032423 | 5 | 0.48589 | 38871.2 | 0 | 0 | 0.11808 | 4132.8 | 0 | 0 | 38871.2 | 1128.8 | 0 | 4132.8 | 0 | 0 | 5261.6 | 0 | 0 | 0 | 0
2022032424 | 5 | 0.46049 | 36839.2 | 0 | 0 | 0.16674 | 5835.9 | 0 | 0 | 36839.2 | 3160.8 | 0 | 5835.9 | 0 | 0 | 8996.7 | 0 | 0 | 0 | 0
2022032501 | 6 | 0.44188 | 35350.4 | 0 | 0 | 0.19616 | 6865.6 | 0 | 0 | 35350.4 | 4649.6 | 0 | 6865.6 | 0 | 0 | 11515.2 | 0 | 0 | 0 | 0
2022032502 | 6 | 0.43229 | 34583.2 | 0 | 0 | 0.22007 | 7702.45 | 0 | 0 | 34583.2 | 5416.8 | 0 | 7702.45 | 0 | 0 | 13119.25 | 0 | 0 | 0 | 0
2022032503 | 6 | 0.43105 | 34484 | 0 | 0 | 0.24069 | 8424.15 | 0 | 0 | 34484 | 5516 | 0 | 8424.15 | 0 | 0 | 13940.15 | 0 | 0 | 0 | 0
2022032504 | 6 | 0.43452 | 34761.6 | 0 | 0 | 0.24316 | 8510.6 | 0 | 0 | 34761.6 | 5238.4 | 0 | 8510.6 | 0 | 0 | 13749 | 0 | 0 | 0 | 0
2022032505 | 6 | 0.4461 | 35688 | 0 | 0 | 0.24149 | 8452.15 | 0 | 0 | 35688 | 4312 | 0 | 8452.15 | 0 | 0 | 12764.15 | 0 | 0 | 0 | 0
2022032506 | 6 | 0.47844 | 38275.2 | 0 | 0 | 0.22047 | 7716.45 | 0 | 0 | 38275.2 | 1724.8 | 0 | 7716.45 | 0 | 0 | 9441.25 | 0 | 0 | 0 | 0
2022032507 | 6 | 0.52818 | 42254.4 | 0 | 0 | 0.19918 | 6971.3 | 0 | 0 | 40000 | 0 | 2254.4 | 4716.9 | 0 | 0 | 4716.9 | 0 | 0 | 0 | 0
2022032508 | 6 | 0.5566 | 44528 | 0 | 0 | 0.18059 | 6320.65 | 0.00905 | 126.7 | 40000 | 0 | 4528 | 1792.65 | 0 | 126.7 | 1919.35 | 0 | 0 | 0 | 0
2022032509 | 6 | 0.54808 | 43846.4 | 0 | 0 | 0.14575 | 5101.25 | 0.31162 | 4362.68 | 40000 | 0 | 3846.4 | 1254.85 | 0 | 4362.68 | 5617.53 | 0 | 0 | 0 | 0
2022032510 | 6 | 0.52948 | 42358.4 | 0 | 0 | 0.06402 | 2240.7 | 0.78577 | 11000.78 | 40000 | 0 | 2240.7 | 0 | 117.7 | 10883.08 | 10883.08 | 0 | 0 | 0 | 0
2022032511 | 6 | 0.51425 | 41140 | 0 | 0 | 0.03527 | 1234.45 | 0.85777 | 12008.78 | 40000 | 0 | 1140 | 94.45 | 0 | 12008.78 | 12103.23 | 0 | 0 | 0 | 0
2022032512 | 6 | 0.50685 | 40548 | 0 | 0 | 0.05162 | 1806.7 | 0.86333 | 12086.62 | 40000 | 0 | 548 | 1258.7 | 0 | 12086.62 | 13345.32 | 0 | 0 | 0 | 0
2022032513 | 6 | 0.5028 | 40224 | 0 | 0 | 0.04768 | 1668.8 | 0.86032 | 12044.48 | 40000 | 0 | 224 | 1444.8 | 0 | 12044.48 | 13489.28 | 0 | 0 | 0 | 0
2022032514 | 6 | 0.51038 | 40830.4 | 0 | 0 | 0.0298 | 1043 | 0.85298 | 11941.72 | 40000 | 0 | 830.4 | 212.6 | 0 | 11941.72 | 12154.32 | 0 | 0 | 0 | 0
2022032515 | 6 | 0.52072 | 41657.6 | 0 | 0 | 0.0431 | 1508.5 | 0.85569 | 11979.66 | 40000 | 0 | 1508.5 | 0 | 149.1 | 11830.56 | 11830.56 | 0 | 0 | 0 | 0
2022032516 | 6 | 0.53341 | 42672.8 | 0 | 0 | 0.06831 | 2390.85 | 0.85707 | 11998.98 | 40000 | 0 | 2390.85 | 0 | 281.95 | 11717.03 | 11717.03 | 0 | 0 | 0 | 0
2022032517 | 6 | 0.54805 | 43844 | 0 | 0 | 0.10122 | 3542.7 | 0.85146 | 11920.44 | 40000 | 0 | 3542.7 | 0 | 301.3 | 11619.14 | 11619.14 | 0 | 0 | 0 | 0
2022032518 | 6 | 0.55863 | 44690.4 | 0 | 0 | 0.14642 | 5124.7 | 0.81981 | 11477.34 | 40000 | 0 | 4690.4 | 434.3 | 0 | 11477.34 | 11911.64 | 0 | 0 | 0 | 0
2022032519 | 6 | 0.55556 | 44444.8 | 0 | 0 | 0.15573 | 5450.55 | 0.60583 | 8481.62 | 40000 | 0 | 4444.8 | 1005.75 | 0 | 8481.62 | 9487.37 | 0 | 0 | 0 | 0
2022032520 | 6 | 0.54373 | 43498.4 | 0 | 0 | 0.18333 | 6416.55 | 0.12997 | 1819.58 | 40000 | 0 | 3498.4 | 2918.15 | 0 | 1819.58 | 4737.73 | 0 | 0 | 0 | 0
2022032521 | 6 | 0.53663 | 42930.4 | 0 | 0 | 0.28394 | 9937.9 | 0.0002 | 2.8 | 40000 | 0 | 2930.4 | 7007.5 | 0 | 2.8 | 7010.3 | 0 | 0 | 0 | 0
2022032522 | 6 | 0.51793 | 41434.4 | 0 | 0 | 0.38311 | 13408.85 | 0 | 0 | 40000 | 0 | 1434.4 | 11974.45 | 0 | 0 | 11974.45 | 0 | 0 | 0 | 0
2022032523 | 6 | 0.49226 | 39380.8 | 0 | 0 | 0.43492 | 15222.2 | 0 | 0 | 39380.8 | 619.2 | 0 | 15222.2 | 0 | 0 | 15841.4 | 0 | 0 | 0 | 0
2022032524 | 6 | 0.4646 | 37168 | 0 | 0 | 0.48873 | 17105.55 | 0 | 0 | 37168 | 2832 | 0 | 17105.55 | 0 | 0 | 19937.55 | 0 | 0 | 0 | 0
2022032601 | 7 | 0.44092 | 35273.6 | 0 | 0 | 0.55296 | 19353.6 | 0 | 0 | 35273.6 | 4726.4 | 0 | 19353.6 | 0 | 0 | 24080 | 0 | 0 | 0 | 0
2022032602 | 7 | 0.42287 | 33829.6 | 0 | 0 | 0.53929 | 18875.15 | 0 | 0 | 33829.6 | 6170.4 | 0 | 18875.15 | 0 | 0 | 25045.55 | 0 | 0 | 0 | 0
2022032603 | 7 | 0.41123 | 32898.4 | 0 | 0 | 0.49209 | 17223.15 | 0 | 0 | 32898.4 | 7101.6 | 0 | 17223.15 | 0 | 0 | 24324.75 | 0 | 0 | 0 | 0
2022032604 | 7 | 0.40401 | 32320.8 | 0 | 0 | 0.42864 | 15002.4 | 0 | 0 | 32320.8 | 7679.2 | 0 | 15002.4 | 0 | 0 | 22681.6 | 0 | 0 | 0 | 0
2022032605 | 7 | 0.40507 | 32405.6 | 0 | 0 | 0.36827 | 12889.45 | 0 | 0 | 32405.6 | 7594.4 | 0 | 12889.45 | 0 | 0 | 20483.85 | 0 | 0 | 0 | 0
2022032606 | 7 | 0.41383 | 33106.4 | 0 | 0 | 0.38145 | 13350.75 | 0 | 0 | 33106.4 | 6893.6 | 0 | 13350.75 | 0 | 0 | 20244.35 | 0 | 0 | 0 | 0
2022032607 | 7 | 0.43036 | 34428.8 | 0 | 0 | 0.37677 | 13186.95 | 0 | 0 | 34428.8 | 5571.2 | 0 | 13186.95 | 0 | 0 | 18758.15 | 0 | 0 | 0 | 0
2022032608 | 7 | 0.44971 | 35976.8 | 0 | 0 | 0.35447 | 12406.45 | 0.00773 | 108.22 | 35976.8 | 4023.2 | 0 | 12406.45 | 0 | 108.22 | 16537.87 | 0 | 0 | 0 | 0
2022032609 | 7 | 0.46546 | 37236.8 | 0 | 0 | 0.30728 | 10754.8 | 0.3035 | 4249 | 37236.8 | 2763.2 | 0 | 10754.8 | 0 | 4249 | 17767 | 0 | 0 | 0 | 0
2022032610 | 7 | 0.47366 | 37892.8 | 0 | 0 | 0.20516 | 7180.6 | 0.78778 | 11028.92 | 37892.8 | 2107.2 | 0 | 7180.6 | 0 | 11028.92 | 20316.72 | 0 | 0 | 0 | 0
2022032611 | 7 | 0.48002 | 38401.6 | 0 | 0 | 0.18269 | 6394.15 | 0.87118 | 12196.52 | 38401.6 | 1598.4 | 0 | 6394.15 | 0 | 12196.52 | 20189.07 | 0 | 0 | 0 | 0
2022032612 | 7 | 0.48663 | 38930.4 | 0 | 0 | 0.19355 | 6774.25 | 0.87225 | 12211.5 | 38930.4 | 1069.6 | 0 | 6774.25 | 0 | 12211.5 | 20055.35 | 0 | 0 | 0 | 0
2022032613 | 7 | 0.49427 | 39541.6 | 0 | 0 | 0.17551 | 6142.85 | 0.87004 | 12180.56 | 39541.6 | 458.4 | 0 | 6142.85 | 0 | 12180.56 | 18781.81 | 0 | 0 | 0 | 0
2022032614 | 7 | 0.50529 | 40423.2 | 0 | 0 | 0.15695 | 5493.25 | 0.868 | 12152 | 40000 | 0 | 423.2 | 5070.05 | 0 | 12152 | 17222.05 | 0 | 0 | 0 | 0
2022032615 | 7 | 0.52308 | 41846.4 | 0 | 0 | 0.13779 | 4822.65 | 0.86383 | 12093.62 | 40000 | 0 | 1846.4 | 2976.25 | 0 | 12093.62 | 15069.87 | 0 | 0 | 0 | 0
2022032616 | 7 | 0.54431 | 43544.8 | 0 | 0 | 0.13462 | 4711.7 | 0.85931 | 12030.34 | 40000 | 0 | 3544.8 | 1166.9 | 0 | 12030.34 | 13197.24 | 0 | 0 | 0 | 0
2022032617 | 7 | 0.56316 | 45052.8 | 0 | 0 | 0.14831 | 5190.85 | 0.84616 | 11846.24 | 40000 | 0 | 5052.8 | 138.05 | 0 | 11846.24 | 11984.29 | 0 | 0 | 0 | 0
2022032618 | 7 | 0.57364 | 45891.2 | 0 | 0 | 0.17316 | 6060.6 | 0.78884 | 11043.76 | 40000 | 0 | 5891.2 | 169.4 | 0 | 11043.76 | 11213.16 | 0 | 0 | 0 | 0
2022032619 | 7 | 0.57028 | 45622.4 | 0 | 0 | 0.20325 | 7113.75 | 0.58448 | 8182.72 | 40000 | 0 | 5622.4 | 1491.35 | 0 | 8182.72 | 9674.07 | 0 | 0 | 0 | 0
2022032620 | 7 | 0.55102 | 44081.6 | 0 | 0 | 0.23584 | 8254.4 | 0.11432 | 1600.48 | 40000 | 0 | 4081.6 | 4172.8 | 0 | 1600.48 | 5773.28 | 0 | 0 | 0 | 0
2022032621 | 7 | 0.5459 | 43672 | 0 | 0 | 0.31895 | 11163.25 | 0.00013 | 1.82 | 40000 | 0 | 3672 | 7491.25 | 0 | 1.82 | 7493.07 | 0 | 0 | 0 | 0
2022032622 | 7 | 0.52648 | 42118.4 | 0 | 0 | 0.42775 | 14971.25 | 0 | 0 | 40000 | 0 | 2118.4 | 12852.85 | 0 | 0 | 12852.85 | 0 | 0 | 0 | 0
2022032623 | 7 | 0.50199 | 40159.2 | 0 | 0 | 0.51117 | 17890.95 | 0 | 0 | 40000 | 0 | 159.2 | 17731.75 | 0 | 0 | 17731.75 | 0 | 0 | 0 | 0
2022032624 | 7 | 0.47517 | 38013.6 | 0 | 0 | 0.55671 | 19484.85 | 0 | 0 | 38013.6 | 1986.4 | 0 | 19484.85 | 0 | 0 | 21471.25 | 0 | 0 | 0 | 0
2022032701 | 1 | 0.44954 | 35963.2 | 0 | 0 | 0.56748 | 19861.8 | 0 | 0 | 35963.2 | 4036.8 | 0 | 19861.8 | 0 | 0 | 23898.6 | 0 | 0 | 0 | 0
2022032702 | 1 | 0.42826 | 34260.8 | 0 | 0 | 0.55586 | 19455.1 | 0 | 0 | 34260.8 | 5739.2 | 0 | 19455.1 | 0 | 0 | 25194.3 | 0 | 0 | 0 | 0
2022032703 | 1 | 0.41511 | 33208.8 | 0 | 0 | 0.56014 | 19604.9 | 0 | 0 | 33208.8 | 6791.2 | 0 | 19604.9 | 0 | 0 | 26396.1 | 0 | 0 | 0 | 0
2022032704 | 1 | 0.40753 | 32602.4 | 0 | 0 | 0.57231 | 20030.85 | 0 | 0 | 32602.4 | 7397.6 | 0 | 20030.85 | 0 | 0 | 27428.45 | 0 | 0 | 0 | 0
2022032705 | 1 | 0.4051 | 32408 | 0 | 0 | 0.57194 | 20017.9 | 0 | 0 | 32408 | 7592 | 0 | 20017.9 | 0 | 0 | 27609.9 | 0 | 0 | 0 | 0
2022032706 | 1 | 0.40782 | 32625.6 | 0 | 0 | 0.57424 | 20098.4 | 0 | 0 | 32625.6 | 7374.4 | 0 | 20098.4 | 0 | 0 | 27472.8 | 0 | 0 | 0 | 0
2022032707 | 1 | 0.41437 | 33149.6 | 0 | 0 | 0.57809 | 20233.15 | 0 | 0 | 33149.6 | 6850.4 | 0 | 20233.15 | 0 | 0 | 27083.55 | 0 | 0 | 0 | 0
2022032708 | 1 | 0.42371 | 33896.8 | 0 | 0 | 0.56836 | 19892.6 | 0.0087 | 121.8 | 33896.8 | 6103.2 | 0 | 19892.6 | 0 | 121.8 | 26117.6 | 0 | 0 | 0 | 0
2022032709 | 1 | 0.44063 | 35250.4 | 0 | 0 | 0.53571 | 18749.85 | 0.24622 | 3447.08 | 35250.4 | 4749.6 | 0 | 18749.85 | 0 | 3447.08 | 26946.53 | 0 | 0 | 0 | 0
2022032710 | 1 | 0.45928 | 36742.4 | 0 | 0 | 0.45558 | 15945.3 | 0.64035 | 8964.9 | 36742.4 | 3257.6 | 0 | 15945.3 | 0 | 8964.9 | 28167.8 | 0 | 0 | 0 | 0
2022032711 | 1 | 0.47333 | 37866.4 | 0 | 0 | 0.43922 | 15372.7 | 0.70482 | 9867.48 | 37866.4 | 2133.6 | 0 | 15372.7 | 0 | 9867.48 | 27373.78 | 0 | 0 | 0 | 0
2022032712 | 1 | 0.4881 | 39048 | 0 | 0 | 0.4212 | 14742 | 0.76013 | 10641.82 | 39048 | 952 | 0 | 14742 | 0 | 10641.82 | 26335.82 | 0 | 0 | 0 | 0
2022032713 | 1 | 0.5057 | 40456 | 0 | 0 | 0.40428 | 14149.8 | 0.7949 | 11128.6 | 40000 | 0 | 456 | 13693.8 | 0 | 11128.6 | 24822.4 | 0 | 0 | 0 | 0
2022032714 | 1 | 0.52447 | 41957.6 | 0 | 0 | 0.36378 | 12732.3 | 0.83323 | 11665.22 | 40000 | 0 | 1957.6 | 10774.7 | 0 | 11665.22 | 22439.92 | 0 | 0 | 0 | 0
2022032715 | 1 | 0.5464 | 43712 | 0 | 0 | 0.34317 | 12010.95 | 0.84281 | 11799.34 | 40000 | 0 | 3712 | 8298.95 | 0 | 11799.34 | 20098.29 | 0 | 0 | 0 | 0
2022032716 | 1 | 0.56995 | 45596 | 0 | 0 | 0.34309 | 12008.15 | 0.84061 | 11768.54 | 40000 | 0 | 5596 | 6412.15 | 0 | 11768.54 | 18180.69 | 0 | 0 | 0 | 0
2022032717 | 1 | 0.59199 | 47359.2 | 0 | 0 | 0.35608 | 12462.8 | 0.80698 | 11297.72 | 40000 | 0 | 7359.2 | 5103.6 | 0 | 11297.72 | 16401.32 | 0 | 0 | 0 | 0
2022032718 | 1 | 0.60643 | 48514.4 | 0 | 0 | 0.37764 | 13217.4 | 0.74765 | 10467.1 | 40000 | 0 | 8514.4 | 4703 | 0 | 10467.1 | 15170.1 | 0 | 0 | 0 | 0
2022032719 | 1 | 0.60261 | 48208.8 | 0 | 0 | 0.43335 | 15167.25 | 0.46523 | 6513.22 | 40000 | 0 | 8208.8 | 6958.45 | 0 | 6513.22 | 13471.67 | 0 | 0 | 0 | 0
2022032720 | 1 | 0.58849 | 47079.2 | 0 | 0 | 0.48001 | 16800.35 | 0.08411 | 1177.54 | 40000 | 0 | 7079.2 | 9721.15 | 0 | 1177.54 | 10898.69 | 0 | 0 | 0 | 0
2022032721 | 1 | 0.58616 | 46892.8 | 0 | 0 | 0.58043 | 20315.05 | 0.00029 | 4.06 | 40000 | 0 | 6892.8 | 13422.25 | 0 | 4.06 | 13426.31 | 0 | 0 | 0 | 0
2022032722 | 1 | 0.56639 | 45311.2 | 0 | 0 | 0.65529 | 22935.15 | 0 | 0 | 40000 | 0 | 5311.2 | 17623.95 | 0 | 0 | 17623.95 | 0 | 0 | 0 | 0
2022032723 | 1 | 0.53157 | 42525.6 | 0 | 0 | 0.66288 | 23200.8 | 0 | 0 | 40000 | 0 | 2525.6 | 20675.2 | 0 | 0 | 20675.2 | 0 | 0 | 0 | 0
2022032724 | 1 | 0.49091 | 39272.8 | 0 | 0 | 0.64494 | 22572.9 | 0 | 0 | 39272.8 | 727.2 | 0 | 22572.9 | 0 | 0 | 23300.1 | 0 | 0 | 0 | 0
2022032801 | 2 | 0.4569 | 36552 | 0 | 0 | 0.6261 | 21913.5 | 0 | 0 | 36552 | 3448 | 0 | 21913.5 | 0 | 0 | 25361.5 | 0 | 0 | 0 | 0
2022032802 | 2 | 0.43555 | 34844 | 0 | 0 | 0.604 | 21140 | 0 | 0 | 34844 | 5156 | 0 | 21140 | 0 | 0 | 26296 | 0 | 0 | 0 | 0
2022032803 | 2 | 0.42268 | 33814.4 | 0 | 0 | 0.59513 | 20829.55 | 0 | 0 | 33814.4 | 6185.6 | 0 | 20829.55 | 0 | 0 | 27015.15 | 0 | 0 | 0 | 0
2022032804 | 2 | 0.41675 | 33340 | 0 | 0 | 0.57742 | 20209.7 | 0 | 0 | 33340 | 6660 | 0 | 20209.7 | 0 | 0 | 26869.7 | 0 | 0 | 0 | 0
2022032805 | 2 | 0.41915 | 33532 | 0 | 0 | 0.55649 | 19477.15 | 0 | 0 | 33532 | 6468 | 0 | 19477.15 | 0 | 0 | 25945.15 | 0 | 0 | 0 | 0
2022032806 | 2 | 0.43694 | 34955.2 | 0 | 0 | 0.55964 | 19587.4 | 0 | 0 | 34955.2 | 5044.8 | 0 | 19587.4 | 0 | 0 | 24632.2 | 0 | 0 | 0 | 0
2022032807 | 2 | 0.47188 | 37750.4 | 0 | 0 | 0.54502 | 19075.7 | 0 | 0 | 37750.4 | 2249.6 | 0 | 19075.7 | 0 | 0 | 21325.3 | 0 | 0 | 0 | 0
2022032808 | 2 | 0.48801 | 39040.8 | 0 | 0 | 0.52572 | 18400.2 | 0.00709 | 99.26 | 39040.8 | 959.2 | 0 | 18400.2 | 0 | 99.26 | 19458.66 | 0 | 0 | 0 | 0
2022032809 | 2 | 0.49253 | 39402.4 | 0 | 0 | 0.48201 | 16870.35 | 0.26011 | 3641.54 | 39402.4 | 597.6 | 0 | 16870.35 | 0 | 3641.54 | 21109.49 | 0 | 0 | 0 | 0
2022032810 | 2 | 0.50643 | 40514.4 | 0 | 0 | 0.44828 | 15689.8 | 0.62446 | 8742.44 | 40000 | 0 | 514.4 | 15175.4 | 0 | 8742.44 | 23917.84 | 0 | 0 | 0 | 0
2022032811 | 2 | 0.52222 | 41777.6 | 0 | 0 | 0.44252 | 15488.2 | 0.71296 | 9981.44 | 40000 | 0 | 1777.6 | 13710.6 | 0 | 9981.44 | 23692.04 | 0 | 0 | 0 | 0
2022032812 | 2 | 0.53603 | 42882.4 | 0 | 0 | 0.42249 | 14787.15 | 0.74942 | 10491.88 | 40000 | 0 | 2882.4 | 11904.75 | 0 | 10491.88 | 22396.63 | 0 | 0 | 0 | 0
2022032813 | 2 | 0.55186 | 44148.8 | 0 | 0 | 0.39165 | 13707.75 | 0.77769 | 10887.66 | 40000 | 0 | 4148.8 | 9558.95 | 0 | 10887.66 | 20446.61 | 0 | 0 | 0 | 0
2022032814 | 2 | 0.57157 | 45725.6 | 0 | 0 | 0.38464 | 13462.4 | 0.77575 | 10860.5 | 40000 | 0 | 5725.6 | 7736.8 | 0 | 10860.5 | 18597.3 | 0 | 0 | 0 | 0
2022032815 | 2 | 0.59272 | 47417.6 | 0 | 0 | 0.40971 | 14339.85 | 0.74702 | 10458.28 | 40000 | 0 | 7417.6 | 6922.25 | 0 | 10458.28 | 17380.53 | 0 | 0 | 0 | 0
2022032816 | 2 | 0.61368 | 49094.4 | 0 | 0 | 0.47547 | 16641.45 | 0.67126 | 9397.64 | 40000 | 0 | 9094.4 | 7547.05 | 0 | 9397.64 | 16944.69 | 0 | 0 | 0 | 0
2022032817 | 2 | 0.63119 | 50495.2 | 0 | 0 | 0.51484 | 18019.4 | 0.5906 | 8268.4 | 40000 | 0 | 10495.2 | 7524.2 | 0 | 8268.4 | 15792.6 | 0 | 0 | 0 | 0
2022032818 | 2 | 0.63729 | 50983.2 | 0 | 0 | 0.53649 | 18777.15 | 0.47545 | 6656.3 | 40000 | 0 | 10983.2 | 7793.95 | 0 | 6656.3 | 14450.25 | 0 | 0 | 0 | 0
2022032819 | 2 | 0.62576 | 50060.8 | 0 | 0 | 0.56629 | 19820.15 | 0.29104 | 4074.56 | 40000 | 0 | 10060.8 | 9759.35 | 0 | 4074.56 | 13833.91 | 0 | 0 | 0 | 0
2022032820 | 2 | 0.60808 | 48646.4 | 0 | 0 | 0.57547 | 20141.45 | 0.03506 | 490.84 | 40000 | 0 | 8646.4 | 11495.05 | 0 | 490.84 | 11985.89 | 0 | 0 | 0 | 0
2022032821 | 2 | 0.60573 | 48458.4 | 0 | 0 | 0.61872 | 21655.2 | 6e-05 | 0.84 | 40000 | 0 | 8458.4 | 13196.8 | 0 | 0.84 | 13197.64 | 0 | 0 | 0 | 0
2022032822 | 2 | 0.58506 | 46804.8 | 0 | 0 | 0.66528 | 23284.8 | 0 | 0 | 40000 | 0 | 6804.8 | 16480 | 0 | 0 | 16480 | 0 | 0 | 0 | 0
2022032823 | 2 | 0.54898 | 43918.4 | 0 | 0 | 0.67199 | 23519.65 | 0 | 0 | 40000 | 0 | 3918.4 | 19601.25 | 0 | 0 | 19601.25 | 0 | 0 | 0 | 0
2022032824 | 2 | 0.50951 | 40760.8 | 0 | 0 | 0.67919 | 23771.65 | 0 | 0 | 40000 | 0 | 760.8 | 23010.85 | 0 | 0 | 23010.85 | 0 | 0 | 0 | 0
2022032901 | 3 | 0.47964 | 38371.2 | 0 | 0 | 0.68567 | 23998.45 | 0 | 0 | 38371.2 | 1628.8 | 0 | 23998.45 | 0 | 0 | 25627.25 | 0 | 0 | 0 | 0
2022032902 | 3 | 0.45978 | 36782.4 | 0 | 0 | 0.67452 | 23608.2 | 0 | 0 | 36782.4 | 3217.6 | 0 | 23608.2 | 0 | 0 | 26825.8 | 0 | 0 | 0 | 0
2022032903 | 3 | 0.446 | 35680 | 0 | 0 | 0.66404 | 23241.4 | 0 | 0 | 35680 | 4320 | 0 | 23241.4 | 0 | 0 | 27561.4 | 0 | 0 | 0 | 0
2022032904 | 3 | 0.44017 | 35213.6 | 0 | 0 | 0.65986 | 23095.1 | 0 | 0 | 35213.6 | 4786.4 | 0 | 23095.1 | 0 | 0 | 27881.5 | 0 | 0 | 0 | 0
2022032905 | 3 | 0.44358 | 35486.4 | 0 | 0 | 0.66017 | 23105.95 | 0 | 0 | 35486.4 | 4513.6 | 0 | 23105.95 | 0 | 0 | 27619.55 | 0 | 0 | 0 | 0
2022032906 | 3 | 0.46326 | 37060.8 | 0 | 0 | 0.66586 | 23305.1 | 0 | 0 | 37060.8 | 2939.2 | 0 | 23305.1 | 0 | 0 | 26244.3 | 0 | 0 | 0 | 0
2022032907 | 3 | 0.50016 | 40012.8 | 0 | 0 | 0.66729 | 23355.15 | 0 | 0 | 40000 | 0 | 12.8 | 23342.35 | 0 | 0 | 23342.35 | 0 | 0 | 0 | 0
2022032908 | 3 | 0.51725 | 41380 | 0 | 0 | 0.66425 | 23248.75 | 0.00162 | 22.68 | 40000 | 0 | 1380 | 21868.75 | 0 | 22.68 | 21891.43 | 0 | 0 | 0 | 0
2022032909 | 3 | 0.52303 | 41842.4 | 0 | 0 | 0.64628 | 22619.8 | 0.13036 | 1825.04 | 40000 | 0 | 1842.4 | 20777.4 | 0 | 1825.04 | 22602.44 | 0 | 0 | 0 | 0
2022032910 | 3 | 0.53458 | 42766.4 | 0 | 0 | 0.61944 | 21680.4 | 0.31275 | 4378.5 | 40000 | 0 | 2766.4 | 18914 | 0 | 4378.5 | 23292.5 | 0 | 0 | 0 | 0
2022032911 | 3 | 0.55036 | 44028.8 | 0 | 0 | 0.64077 | 22426.95 | 0.29161 | 4082.54 | 40000 | 0 | 4028.8 | 18398.15 | 0 | 4082.54 | 22480.69 | 0 | 0 | 0 | 0
2022032912 | 3 | 0.56522 | 45217.6 | 0 | 0 | 0.64703 | 22646.05 | 0.29884 | 4183.76 | 40000 | 0 | 5217.6 | 17428.45 | 0 | 4183.76 | 21612.21 | 0 | 0 | 0 | 0
2022032913 | 3 | 0.57861 | 46288.8 | 0 | 0 | 0.63787 | 22325.45 | 0.31411 | 4397.54 | 40000 | 0 | 6288.8 | 16036.65 | 0 | 4397.54 | 20434.19 | 0 | 0 | 0 | 0
2022032914 | 3 | 0.59003 | 47202.4 | 0 | 0 | 0.63561 | 22246.35 | 0.32265 | 4517.1 | 40000 | 0 | 7202.4 | 15043.95 | 0 | 4517.1 | 19561.05 | 0 | 0 | 0 | 0
2022032915 | 3 | 0.6016 | 48128 | 0 | 0 | 0.64322 | 22512.7 | 0.31727 | 4441.78 | 40000 | 0 | 8128 | 14384.7 | 0 | 4441.78 | 18826.48 | 0 | 0 | 0 | 0
2022032916 | 3 | 0.60872 | 48697.6 | 0 | 0 | 0.65432 | 22901.2 | 0.27131 | 3798.34 | 40000 | 0 | 8697.6 | 14203.6 | 0 | 3798.34 | 18001.94 | 0 | 0 | 0 | 0
2022032917 | 3 | 0.61347 | 49077.6 | 0 | 0 | 0.65617 | 22965.95 | 0.25932 | 3630.48 | 40000 | 0 | 9077.6 | 13888.35 | 0 | 3630.48 | 17518.83 | 0 | 0 | 0 | 0
2022032918 | 3 | 0.61215 | 48972 | 0 | 0 | 0.66548 | 23291.8 | 0.22196 | 3107.44 | 40000 | 0 | 8972 | 14319.8 | 0 | 3107.44 | 17427.24 | 0 | 0 | 0 | 0
2022032919 | 3 | 0.59901 | 47920.8 | 0 | 0 | 0.67249 | 23537.15 | 0.1474 | 2063.6 | 40000 | 0 | 7920.8 | 15616.35 | 0 | 2063.6 | 17679.95 | 0 | 0 | 0 | 0
2022032920 | 3 | 0.59523 | 47618.4 | 0 | 0 | 0.68044 | 23815.4 | 0.03635 | 508.9 | 40000 | 0 | 7618.4 | 16197 | 0 | 508.9 | 16705.9 | 0 | 0 | 0 | 0
2022032921 | 3 | 0.60137 | 48109.6 | 0 | 0 | 0.69816 | 24435.6 | 0.00014 | 1.96 | 40000 | 0 | 8109.6 | 16326 | 0 | 1.96 | 16327.96 | 0 | 0 | 0 | 0
2022032922 | 3 | 0.58642 | 46913.6 | 0 | 0 | 0.66843 | 23395.05 | 0 | 0 | 40000 | 0 | 6913.6 | 16481.45 | 0 | 0 | 16481.45 | 0 | 0 | 0 | 0
2022032923 | 3 | 0.55481 | 44384.8 | 0 | 0 | 0.63888 | 22360.8 | 0 | 0 | 40000 | 0 | 4384.8 | 17976 | 0 | 0 | 17976 | 0 | 0 | 0 | 0
2022032924 | 3 | 0.51911 | 41528.8 | 0 | 0 | 0.60925 | 21323.75 | 0 | 0 | 40000 | 0 | 1528.8 | 19794.95 | 0 | 0 | 19794.95 | 0 | 0 | 0 | 0
2022033001 | 4 | 0.4878 | 39024 | 0 | 0 | 0.56182 | 19663.7 | 0 | 0 | 39024 | 976 | 0 | 19663.7 | 0 | 0 | 20639.7 | 0 | 0 | 0 | 0
2022033002 | 4 | 0.46798 | 37438.4 | 0 | 0 | 0.50822 | 17787.7 | 0 | 0 | 37438.4 | 2561.6 | 0 | 17787.7 | 0 | 0 | 20349.3 | 0 | 0 | 0 | 0
2022033003 | 4 | 0.45794 | 36635.2 | 0 | 0 | 0.54294 | 19002.9 | 0 | 0 | 36635.2 | 3364.8 | 0 | 19002.9 | 0 | 0 | 22367.7 | 0 | 0 | 0 | 0
2022033004 | 4 | 0.45121 | 36096.8 | 0 | 0 | 0.55612 | 19464.2 | 0 | 0 | 36096.8 | 3903.2 | 0 | 19464.2 | 0 | 0 | 23367.4 | 0 | 0 | 0 | 0
2022033005 | 4 | 0.45346 | 36276.8 | 0 | 0 | 0.59339 | 20768.65 | 0 | 0 | 36276.8 | 3723.2 | 0 | 20768.65 | 0 | 0 | 24491.85 | 0 | 0 | 0 | 0
2022033006 | 4 | 0.46937 | 37549.6 | 0 | 0 | 0.5974 | 20909 | 0 | 0 | 37549.6 | 2450.4 | 0 | 20909 | 0 | 0 | 23359.4 | 0 | 0 | 0 | 0
2022033007 | 4 | 0.49901 | 39920.8 | 0 | 0 | 0.59085 | 20679.75 | 0 | 0 | 39920.8 | 79.2 | 0 | 20679.75 | 0 | 0 | 20758.95 | 0 | 0 | 0 | 0
2022033008 | 4 | 0.51686 | 41348.8 | 0 | 0 | 0.58199 | 20369.65 | 0.00249 | 34.86 | 40000 | 0 | 1348.8 | 19020.85 | 0 | 34.86 | 19055.71 | 0 | 0 | 0 | 0
2022033009 | 4 | 0.51956 | 41564.8 | 0 | 0 | 0.60973 | 21340.55 | 0.06782 | 949.48 | 40000 | 0 | 1564.8 | 19775.75 | 0 | 949.48 | 20725.23 | 0 | 0 | 0 | 0
2022033010 | 4 | 0.52553 | 42042.4 | 0 | 0 | 0.61818 | 21636.3 | 0.11648 | 1630.72 | 40000 | 0 | 2042.4 | 19593.9 | 0 | 1630.72 | 21224.62 | 0 | 0 | 0 | 0
2022033011 | 4 | 0.52989 | 42391.2 | 0 | 0 | 0.64634 | 22621.9 | 0.18849 | 2638.86 | 40000 | 0 | 2391.2 | 20230.7 | 0 | 2638.86 | 22869.56 | 0 | 0 | 0 | 0
2022033012 | 4 | 0.52995 | 42396 | 0 | 0 | 0.65933 | 23076.55 | 0.23744 | 3324.16 | 40000 | 0 | 2396 | 20680.55 | 0 | 3324.16 | 24004.71 | 0 | 0 | 0 | 0
2022033013 | 4 | 0.53606 | 42884.8 | 0 | 0 | 0.65788 | 23025.8 | 0.28495 | 3989.3 | 40000 | 0 | 2884.8 | 20141 | 0 | 3989.3 | 24130.3 | 0 | 0 | 0 | 0
2022033014 | 4 | 0.54634 | 43707.2 | 0 | 0 | 0.64837 | 22692.95 | 0.31555 | 4417.7 | 40000 | 0 | 3707.2 | 18985.75 | 0 | 4417.7 | 23403.45 | 0 | 0 | 0 | 0
2022033015 | 4 | 0.55407 | 44325.6 | 0 | 0 | 0.61246 | 21436.1 | 0.36636 | 5129.04 | 40000 | 0 | 4325.6 | 17110.5 | 0 | 5129.04 | 22239.54 | 0 | 0 | 0 | 0
2022033016 | 4 | 0.56114 | 44891.2 | 0 | 0 | 0.55526 | 19434.1 | 0.42505 | 5950.7 | 40000 | 0 | 4891.2 | 14542.9 | 0 | 5950.7 | 20493.6 | 0 | 0 | 0 | 0
2022033017 | 4 | 0.56928 | 45542.4 | 0 | 0 | 0.48716 | 17050.6 | 0.48902 | 6846.28 | 40000 | 0 | 5542.4 | 11508.2 | 0 | 6846.28 | 18354.48 | 0 | 0 | 0 | 0
2022033018 | 4 | 0.57265 | 45812 | 0 | 0 | 0.41248 | 14436.8 | 0.59399 | 8315.86 | 40000 | 0 | 5812 | 8624.8 | 0 | 8315.86 | 16940.66 | 0 | 0 | 0 | 0
2022033019 | 4 | 0.56343 | 45074.4 | 0 | 0 | 0.32302 | 11305.7 | 0.45048 | 6306.72 | 40000 | 0 | 5074.4 | 6231.3 | 0 | 6306.72 | 12538.02 | 0 | 0 | 0 | 0
2022033020 | 4 | 0.55171 | 44136.8 | 0 | 0 | 0.20479 | 7167.65 | 0.1018 | 1425.2 | 40000 | 0 | 4136.8 | 3030.85 | 0 | 1425.2 | 4456.05 | 0 | 0 | 0 | 0
2022033021 | 4 | 0.55381 | 44304.8 | 0 | 0 | 0.1534 | 5369 | 0.00018 | 2.52 | 40000 | 0 | 4304.8 | 1064.2 | 0 | 2.52 | 1066.72 | 0 | 0 | 0 | 0
2022033022 | 4 | 0.53488 | 42790.4 | 0 | 0 | 0.17547 | 6141.45 | 0 | 0 | 40000 | 0 | 2790.4 | 3351.05 | 0 | 0 | 3351.05 | 0 | 0 | 0 | 0
2022033023 | 4 | 0.50095 | 40076 | 0 | 0 | 0.21331 | 7465.85 | 0 | 0 | 40000 | 0 | 76 | 7389.85 | 0 | 0 | 7389.85 | 0 | 0 | 0 | 0
2022033024 | 4 | 0.46318 | 37054.4 | 0 | 0 | 0.23257 | 8139.95 | 0 | 0 | 37054.4 | 2945.6 | 0 | 8139.95 | 0 | 0 | 11085.55 | 0 | 0 | 0 | 0
2022033101 | 5 | 0.43704 | 34963.2 | 0 | 0 | 0.23694 | 8292.9 | 0 | 0 | 34963.2 | 5036.8 | 0 | 8292.9 | 0 | 0 | 13329.7 | 0 | 0 | 0 | 0
2022033102 | 5 | 0.42279 | 33823.2 | 0 | 0 | 0.18355 | 6424.25 | 0 | 0 | 33823.2 | 6176.8 | 0 | 6424.25 | 0 | 0 | 12601.05 | 0 | 0 | 0 | 0
2022033103 | 5 | 0.41399 | 33119.2 | 0 | 0 | 0.19459 | 6810.65 | 0 | 0 | 33119.2 | 6880.8 | 0 | 6810.65 | 0 | 0 | 13691.45 | 0 | 0 | 0 | 0
2022033104 | 5 | 0.41097 | 32877.6 | 0 | 0 | 0.24623 | 8618.05 | 0 | 0 | 32877.6 | 7122.4 | 0 | 8618.05 | 0 | 0 | 15740.45 | 0 | 0 | 0 | 0
2022033105 | 5 | 0.41769 | 33415.2 | 0 | 0 | 0.3047 | 10664.5 | 0 | 0 | 33415.2 | 6584.8 | 0 | 10664.5 | 0 | 0 | 17249.3 | 0 | 0 | 0 | 0
2022033106 | 5 | 0.44163 | 35330.4 | 0 | 0 | 0.27755 | 9714.25 | 0 | 0 | 35330.4 | 4669.6 | 0 | 9714.25 | 0 | 0 | 14383.85 | 0 | 0 | 0 | 0
2022033107 | 5 | 0.48407 | 38725.6 | 0 | 0 | 0.25808 | 9032.8 | 0 | 0 | 38725.6 | 1274.4 | 0 | 9032.8 | 0 | 0 | 10307.2 | 0 | 0 | 0 | 0
2022033108 | 5 | 0.50481 | 40384.8 | 0 | 0 | 0.2278 | 7973 | 0.01003 | 140.42 | 40000 | 0 | 384.8 | 7588.2 | 0 | 140.42 | 7728.62 | 0 | 0 | 0 | 0
2022033109 | 5 | 0.50484 | 40387.2 | 0 | 0 | 0.20325 | 7113.75 | 0.29278 | 4098.92 | 40000 | 0 | 387.2 | 6726.55 | 0 | 4098.92 | 10825.47 | 0 | 0 | 0 | 0
2022033110 | 5 | 0.50671 | 40536.8 | 0 | 0 | 0.14085 | 4929.75 | 0.69266 | 9697.24 | 40000 | 0 | 536.8 | 4392.95 | 0 | 9697.24 | 14090.19 | 0 | 0 | 0 | 0
2022033111 | 5 | 0.50279 | 40223.2 | 0 | 0 | 0.13268 | 4643.8 | 0.81474 | 11406.36 | 40000 | 0 | 223.2 | 4420.6 | 0 | 11406.36 | 15826.96 | 0 | 0 | 0 | 0
2022033112 | 5 | 0.49941 | 39952.8 | 0 | 0 | 0.12239 | 4283.65 | 0.85595 | 11983.3 | 39952.8 | 47.2 | 0 | 4283.65 | 0 | 11983.3 | 16314.15 | 0 | 0 | 0 | 0
2022033113 | 5 | 0.50009 | 40007.2 | 0 | 0 | 0.10866 | 3803.1 | 0.8697 | 12175.8 | 40000 | 0 | 7.2 | 3795.9 | 0 | 12175.8 | 15971.7 | 0 | 0 | 0 | 0
2022033114 | 5 | 0.50454 | 40363.2 | 0 | 0 | 0.11501 | 4025.35 | 0.85383 | 11953.62 | 40000 | 0 | 363.2 | 3662.15 | 0 | 11953.62 | 15615.77 | 0 | 0 | 0 | 0
2022033115 | 5 | 0.51143 | 40914.4 | 0 | 0 | 0.11786 | 4125.1 | 0.8479 | 11870.6 | 40000 | 0 | 914.4 | 3210.7 | 0 | 11870.6 | 15081.3 | 0 | 0 | 0 | 0
2022033116 | 5 | 0.52067 | 41653.6 | 0 | 0 | 0.1083 | 3790.5 | 0.85138 | 11919.32 | 40000 | 0 | 1653.6 | 2136.9 | 0 | 11919.32 | 14056.22 | 0 | 0 | 0 | 0
2022033117 | 5 | 0.533 | 42640 | 0 | 0 | 0.09491 | 3321.85 | 0.84082 | 11771.48 | 40000 | 0 | 2640 | 681.85 | 0 | 11771.48 | 12453.33 | 0 | 0 | 0 | 0
2022033118 | 5 | 0.54184 | 43347.2 | 0 | 0 | 0.09663 | 3382.05 | 0.80888 | 11324.32 | 40000 | 0 | 3347.2 | 34.85 | 0 | 11324.32 | 11359.17 | 0 | 0 | 0 | 0
2022033119 | 5 | 0.53881 | 43104.8 | 0 | 0 | 0.0987 | 3454.5 | 0.58028 | 8123.92 | 40000 | 0 | 3104.8 | 349.7 | 0 | 8123.92 | 8473.62 | 0 | 0 | 0 | 0
2022033120 | 5 | 0.5343 | 42744 | 0 | 0 | 0.10522 | 3682.7 | 0.12425 | 1739.5 | 40000 | 0 | 2744 | 938.7 | 0 | 1739.5 | 2678.2 | 0 | 0 | 0 | 0
2022033121 | 5 | 0.53636 | 42908.8 | 0 | 0 | 0.09566 | 3348.1 | 0.00022 | 3.08 | 40000 | 0 | 2908.8 | 439.3 | 0 | 3.08 | 442.38 | 0 | 0 | 0 | 0
2022033122 | 5 | 0.52059 | 41647.2 | 0 | 0 | 0.13044 | 4565.4 | 0 | 0 | 40000 | 0 | 1647.2 | 2918.2 | 0 | 0 | 2918.2 | 0 | 0 | 0 | 0
2022033123 | 5 | 0.49119 | 39295.2 | 0 | 0 | 0.20521 | 7182.35 | 0 | 0 | 39295.2 | 704.8 | 0 | 7182.35 | 0 | 0 | 7887.15 | 0 | 0 | 0 | 0
2022033124 | 5 | 0.45641 | 36512.8 | 0 | 0 | 0.29319 | 10261.65 | 0 | 0 | 36512.8 | 3487.2 | 0 | 10261.65 | 0 | 0 | 13748.85 | 0 | 0 | 0 | 0
2022040101 | 6 | 0.43352 | 34681.6 | 0 | 0 | 0.38518 | 13481.3 | 0 | 0 | 34681.6 | 5318.4 | 0 | 13481.3 | 0 | 0 | 18799.7 | 0 | 0 | 0 | 0
2022040102 | 6 | 0.42135 | 33708 | 0 | 0 | 0.44612 | 15614.2 | 0 | 0 | 33708 | 6292 | 0 | 15614.2 | 0 | 0 | 21906.2 | 0 | 0 | 0 | 0
2022040103 | 6 | 0.41476 | 33180.8 | 0 | 0 | 0.48127 | 16844.45 | 0 | 0 | 33180.8 | 6819.2 | 0 | 16844.45 | 0 | 0 | 23663.65 | 0 | 0 | 0 | 0
2022040104 | 6 | 0.41605 | 33284 | 0 | 0 | 0.51446 | 18006.1 | 0 | 0 | 33284 | 6716 | 0 | 18006.1 | 0 | 0 | 24722.1 | 0 | 0 | 0 | 0
2022040105 | 6 | 0.42416 | 33932.8 | 0 | 0 | 0.52971 | 18539.85 | 0 | 0 | 33932.8 | 6067.2 | 0 | 18539.85 | 0 | 0 | 24607.05 | 0 | 0 | 0 | 0
2022040106 | 6 | 0.44821 | 35856.8 | 0 | 0 | 0.53755 | 18814.25 | 0 | 0 | 35856.8 | 4143.2 | 0 | 18814.25 | 0 | 0 | 22957.45 | 0 | 0 | 0 | 0
2022040107 | 6 | 0.48568 | 38854.4 | 0 | 0 | 0.53526 | 18734.1 | 0 | 0 | 38854.4 | 1145.6 | 0 | 18734.1 | 0 | 0 | 19879.7 | 0 | 0 | 0 | 0
2022040108 | 6 | 0.50591 | 40472.8 | 0 | 0 | 0.54028 | 18909.8 | 0.01552 | 217.28 | 40000 | 0 | 472.8 | 18437 | 0 | 217.28 | 18654.28 | 0 | 0 | 0 | 0
2022040109 | 6 | 0.50661 | 40528.8 | 0 | 0 | 0.50737 | 17757.95 | 0.2083 | 2916.2 | 40000 | 0 | 528.8 | 17229.15 | 0 | 2916.2 | 20145.35 | 0 | 0 | 0 | 0
2022040110 | 6 | 0.50865 | 40692 | 0 | 0 | 0.49198 | 17219.3 | 0.38473 | 5386.22 | 40000 | 0 | 692 | 16527.3 | 0 | 5386.22 | 21913.52 | 0 | 0 | 0 | 0
2022040111 | 6 | 0.50951 | 40760.8 | 0 | 0 | 0.55561 | 19446.35 | 0.3455 | 4837 | 40000 | 0 | 760.8 | 18685.55 | 0 | 4837 | 23522.55 | 0 | 0 | 0 | 0
2022040112 | 6 | 0.51003 | 40802.4 | 0 | 0 | 0.58341 | 20419.35 | 0.34366 | 4811.24 | 40000 | 0 | 802.4 | 19616.95 | 0 | 4811.24 | 24428.19 | 0 | 0 | 0 | 0
2022040113 | 6 | 0.5135 | 41080 | 0 | 0 | 0.6023 | 21080.5 | 0.33644 | 4710.16 | 40000 | 0 | 1080 | 20000.5 | 0 | 4710.16 | 24710.66 | 0 | 0 | 0 | 0
2022040114 | 6 | 0.52043 | 41634.4 | 0 | 0 | 0.61734 | 21606.9 | 0.3168 | 4435.2 | 40000 | 0 | 1634.4 | 19972.5 | 0 | 4435.2 | 24407.7 | 0 | 0 | 0 | 0
2022040115 | 6 | 0.52759 | 42207.2 | 0 | 0 | 0.62472 | 21865.2 | 0.31445 | 4402.3 | 40000 | 0 | 2207.2 | 19658 | 0 | 4402.3 | 24060.3 | 0 | 0 | 0 | 0
2022040116 | 6 | 0.53795 | 43036 | 0 | 0 | 0.62948 | 22031.8 | 0.31268 | 4377.52 | 40000 | 0 | 3036 | 18995.8 | 0 | 4377.52 | 23373.32 | 0 | 0 | 0 | 0
2022040117 | 6 | 0.54855 | 43884 | 0 | 0 | 0.62654 | 21928.9 | 0.33283 | 4659.62 | 40000 | 0 | 3884 | 18044.9 | 0 | 4659.62 | 22704.52 | 0 | 0 | 0 | 0
2022040118 | 6 | 0.55521 | 44416.8 | 0 | 0 | 0.61589 | 21556.15 | 0.33132 | 4638.48 | 40000 | 0 | 4416.8 | 17139.35 | 0 | 4638.48 | 21777.83 | 0 | 0 | 0 | 0
2022040119 | 6 | 0.54603 | 43682.4 | 0 | 0 | 0.59022 | 20657.7 | 0.25153 | 3521.42 | 40000 | 0 | 3682.4 | 16975.3 | 0 | 3521.42 | 20496.72 | 0 | 0 | 0 | 0
2022040120 | 6 | 0.53397 | 42717.6 | 0 | 0 | 0.55906 | 19567.1 | 0.1028 | 1439.2 | 40000 | 0 | 2717.6 | 16849.5 | 0 | 1439.2 | 18288.7 | 0 | 0 | 0 | 0
2022040121 | 6 | 0.53343 | 42674.4 | 0 | 0 | 0.53997 | 18898.95 | 0.0005 | 7 | 40000 | 0 | 2674.4 | 16224.55 | 0 | 7 | 16231.55 | 0 | 0 | 0 | 0
2022040122 | 6 | 0.51918 | 41534.4 | 0 | 0 | 0.52361 | 18326.35 | 0 | 0 | 40000 | 0 | 1534.4 | 16791.95 | 0 | 0 | 16791.95 | 0 | 0 | 0 | 0
2022040123 | 6 | 0.4932 | 39456 | 0 | 0 | 0.45572 | 15950.2 | 0 | 0 | 39456 | 544 | 0 | 15950.2 | 0 | 0 | 16494.2 | 0 | 0 | 0 | 0
2022040124 | 6 | 0.46534 | 37227.2 | 0 | 0 | 0.38734 | 13556.9 | 0 | 0 | 37227.2 | 2772.8 | 0 | 13556.9 | 0 | 0 | 16329.7 | 0 | 0 | 0 | 0
2022040201 | 7 | 0.43953 | 35162.4 | 0 | 0 | 0.34073 | 11925.55 | 0 | 0 | 35162.4 | 4837.6 | 0 | 11925.55 | 0 | 0 | 16763.15 | 0 | 0 | 0 | 0
2022040202 | 7 | 0.42086 | 33668.8 | 0 | 0 | 0.28985 | 10144.75 | 0 | 0 | 33668.8 | 6331.2 | 0 | 10144.75 | 0 | 0 | 16475.95 | 0 | 0 | 0 | 0
2022040203 | 7 | 0.40858 | 32686.4 | 0 | 0 | 0.26398 | 9239.3 | 0 | 0 | 32686.4 | 7313.6 | 0 | 9239.3 | 0 | 0 | 16552.9 | 0 | 0 | 0 | 0
2022040204 | 7 | 0.4037 | 32296 | 0 | 0 | 0.2549 | 8921.5 | 0 | 0 | 32296 | 7704 | 0 | 8921.5 | 0 | 0 | 16625.5 | 0 | 0 | 0 | 0
2022040205 | 7 | 0.40364 | 32291.2 | 0 | 0 | 0.25719 | 9001.65 | 0 | 0 | 32291.2 | 7708.8 | 0 | 9001.65 | 0 | 0 | 16710.45 | 0 | 0 | 0 | 0
2022040206 | 7 | 0.41166 | 32932.8 | 0 | 0 | 0.22924 | 8023.4 | 0 | 0 | 32932.8 | 7067.2 | 0 | 8023.4 | 0 | 0 | 15090.6 | 0 | 0 | 0 | 0
2022040207 | 7 | 0.42459 | 33967.2 | 0 | 0 | 0.16246 | 5686.1 | 0 | 0 | 33967.2 | 6032.8 | 0 | 5686.1 | 0 | 0 | 11718.9 | 0 | 0 | 0 | 0
2022040208 | 7 | 0.43942 | 35153.6 | 0 | 0 | 0.11789 | 4126.15 | 0.01324 | 185.36 | 35153.6 | 4846.4 | 0 | 4126.15 | 0 | 185.36 | 9157.91 | 0 | 0 | 0 | 0
2022040209 | 7 | 0.45381 | 36304.8 | 0 | 0 | 0.09717 | 3400.95 | 0.32415 | 4538.1 | 36304.8 | 3695.2 | 0 | 3400.95 | 0 | 4538.1 | 11634.25 | 0 | 0 | 0 | 0
2022040210 | 7 | 0.4688 | 37504 | 0 | 0 | 0.07145 | 2500.75 | 0.72928 | 10209.92 | 37504 | 2496 | 0 | 2500.75 | 0 | 10209.92 | 15206.67 | 0 | 0 | 0 | 0
2022040211 | 7 | 0.48252 | 38601.6 | 0 | 0 | 0.06108 | 2137.8 | 0.80784 | 11309.76 | 38601.6 | 1398.4 | 0 | 2137.8 | 0 | 11309.76 | 14845.96 | 0 | 0 | 0 | 0
2022040212 | 7 | 0.49734 | 39787.2 | 0 | 0 | 0.06679 | 2337.65 | 0.82945 | 11612.3 | 39787.2 | 212.8 | 0 | 2337.65 | 0 | 11612.3 | 14162.75 | 0 | 0 | 0 | 0
2022040213 | 7 | 0.50783 | 40626.4 | 0 | 0 | 0.0623 | 2180.5 | 0.83382 | 11673.48 | 40000 | 0 | 626.4 | 1554.1 | 0 | 11673.48 | 13227.58 | 0 | 0 | 0 | 0
2022040214 | 7 | 0.52071 | 41656.8 | 0 | 0 | 0.06572 | 2300.2 | 0.83751 | 11725.14 | 40000 | 0 | 1656.8 | 643.4 | 0 | 11725.14 | 12368.54 | 0 | 0 | 0 | 0
2022040215 | 7 | 0.538 | 43040 | 0 | 0 | 0.07621 | 2667.35 | 0.8383 | 11736.2 | 40000 | 0 | 2667.35 | 0 | 372.65 | 11363.55 | 11363.55 | 0 | 0 | 0 | 0
2022040216 | 7 | 0.5586 | 44688 | 0 | 0 | 0.08758 | 3065.3 | 0.84197 | 11787.58 | 40000 | 0 | 3065.3 | 0 | 1622.7 | 10164.88 | 10164.88 | 0 | 0 | 0 | 0
2022040217 | 7 | 0.57789 | 46231.2 | 0 | 0 | 0.10068 | 3523.8 | 0.84276 | 11798.64 | 40000 | 0 | 3523.8 | 0 | 2707.4 | 9091.24 | 9091.24 | 0 | 0 | 0 | 0
2022040218 | 7 | 0.58863 | 47090.4 | 0 | 0 | 0.13107 | 4587.45 | 0.81492 | 11408.88 | 40000 | 0 | 4587.45 | 0 | 2502.95 | 8905.93 | 8905.93 | 0 | 0 | 0 | 0
2022040219 | 7 | 0.58408 | 46726.4 | 0 | 0 | 0.16228 | 5679.8 | 0.6307 | 8829.8 | 40000 | 0 | 5679.8 | 0 | 1046.6 | 7783.2 | 7783.2 | 0 | 0 | 0 | 0
2022040220 | 7 | 0.56393 | 45114.4 | 0 | 0 | 0.19371 | 6779.85 | 0.16017 | 2242.38 | 40000 | 0 | 5114.4 | 1665.45 | 0 | 2242.38 | 3907.83 | 0 | 0 | 0 | 0
2022040221 | 7 | 0.55111 | 44088.8 | 0 | 0 | 0.23869 | 8354.15 | 0.00056 | 7.84 | 40000 | 0 | 4088.8 | 4265.35 | 0 | 7.84 | 4273.19 | 0 | 0 | 0 | 0
2022040222 | 7 | 0.5316 | 42528 | 0 | 0 | 0.3163 | 11070.5 | 0 | 0 | 40000 | 0 | 2528 | 8542.5 | 0 | 0 | 8542.5 | 0 | 0 | 0 | 0
2022040223 | 7 | 0.50638 | 40510.4 | 0 | 0 | 0.39958 | 13985.3 | 0 | 0 | 40000 | 0 | 510.4 | 13474.9 | 0 | 0 | 13474.9 | 0 | 0 | 0 | 0
2022040224 | 7 | 0.47849 | 38279.2 | 0 | 0 | 0.49896 | 17463.6 | 0 | 0 | 38279.2 | 1720.8 | 0 | 17463.6 | 0 | 0 | 19184.4 | 0 | 0 | 0 | 0
2022040301 | 1 | 0.45466 | 36372.8 | 0 | 0 | 0.55922 | 19572.7 | 0 | 0 | 36372.8 | 3627.2 | 0 | 19572.7 | 0 | 0 | 23199.9 | 0 | 0 | 0 | 0
2022040302 | 1 | 0.43415 | 34732 | 0 | 0 | 0.56987 | 19945.45 | 0 | 0 | 34732 | 5268 | 0 | 19945.45 | 0 | 0 | 25213.45 | 0 | 0 | 0 | 0
2022040303 | 1 | 0.42231 | 33784.8 | 0 | 0 | 0.56056 | 19619.6 | 0 | 0 | 33784.8 | 6215.2 | 0 | 19619.6 | 0 | 0 | 25834.8 | 0 | 0 | 0 | 0
2022040304 | 1 | 0.41378 | 33102.4 | 0 | 0 | 0.54521 | 19082.35 | 0 | 0 | 33102.4 | 6897.6 | 0 | 19082.35 | 0 | 0 | 25979.95 | 0 | 0 | 0 | 0
2022040305 | 1 | 0.41119 | 32895.2 | 0 | 0 | 0.53632 | 18771.2 | 0 | 0 | 32895.2 | 7104.8 | 0 | 18771.2 | 0 | 0 | 25876 | 0 | 0 | 0 | 0
2022040306 | 1 | 0.41381 | 33104.8 | 0 | 0 | 0.53555 | 18744.25 | 0 | 0 | 33104.8 | 6895.2 | 0 | 18744.25 | 0 | 0 | 25639.45 | 0 | 0 | 0 | 0
2022040307 | 1 | 0.42044 | 33635.2 | 0 | 0 | 0.53554 | 18743.9 | 0 | 0 | 33635.2 | 6364.8 | 0 | 18743.9 | 0 | 0 | 25108.7 | 0 | 0 | 0 | 0
2022040308 | 1 | 0.42901 | 34320.8 | 0 | 0 | 0.53395 | 18688.25 | 0.01508 | 211.12 | 34320.8 | 5679.2 | 0 | 18688.25 | 0 | 211.12 | 24578.57 | 0 | 0 | 0 | 0
2022040309 | 1 | 0.44736 | 35788.8 | 0 | 0 | 0.50644 | 17725.4 | 0.1737 | 2431.8 | 35788.8 | 4211.2 | 0 | 17725.4 | 0 | 2431.8 | 24368.4 | 0 | 0 | 0 | 0
2022040310 | 1 | 0.46641 | 37312.8 | 0 | 0 | 0.48623 | 17018.05 | 0.30343 | 4248.02 | 37312.8 | 2687.2 | 0 | 17018.05 | 0 | 4248.02 | 23953.27 | 0 | 0 | 0 | 0
2022040311 | 1 | 0.48758 | 39006.4 | 0 | 0 | 0.49291 | 17251.85 | 0.31218 | 4370.52 | 39006.4 | 993.6 | 0 | 17251.85 | 0 | 4370.52 | 22615.97 | 0 | 0 | 0 | 0
2022040312 | 1 | 0.506 | 40480 | 0 | 0 | 0.49175 | 17211.25 | 0.37305 | 5222.7 | 40000 | 0 | 480 | 16731.25 | 0 | 5222.7 | 21953.95 | 0 | 0 | 0 | 0
2022040313 | 1 | 0.5267 | 42136 | 0 | 0 | 0.49517 | 17330.95 | 0.41703 | 5838.42 | 40000 | 0 | 2136 | 15194.95 | 0 | 5838.42 | 21033.37 | 0 | 0 | 0 | 0
2022040314 | 1 | 0.54631 | 43704.8 | 0 | 0 | 0.46567 | 16298.45 | 0.5779 | 8090.6 | 40000 | 0 | 3704.8 | 12593.65 | 0 | 8090.6 | 20684.25 | 0 | 0 | 0 | 0
2022040315 | 1 | 0.56721 | 45376.8 | 0 | 0 | 0.426 | 14910 | 0.75721 | 10600.94 | 40000 | 0 | 5376.8 | 9533.2 | 0 | 10600.94 | 20134.14 | 0 | 0 | 0 | 0
2022040316 | 1 | 0.58855 | 47084 | 0 | 0 | 0.42563 | 14897.05 | 0.78179 | 10945.06 | 40000 | 0 | 7084 | 7813.05 | 0 | 10945.06 | 18758.11 | 0 | 0 | 0 | 0
2022040317 | 1 | 0.60611 | 48488.8 | 0 | 0 | 0.46433 | 16251.55 | 0.70177 | 9824.78 | 40000 | 0 | 8488.8 | 7762.75 | 0 | 9824.78 | 17587.53 | 0 | 0 | 0 | 0
2022040318 | 1 | 0.61703 | 49362.4 | 0 | 0 | 0.50794 | 17777.9 | 0.49512 | 6931.68 | 40000 | 0 | 9362.4 | 8415.5 | 0 | 6931.68 | 15347.18 | 0 | 0 | 0 | 0
2022040319 | 1 | 0.61384 | 49107.2 | 0 | 0 | 0.55306 | 19357.1 | 0.29167 | 4083.38 | 40000 | 0 | 9107.2 | 10249.9 | 0 | 4083.38 | 14333.28 | 0 | 0 | 0 | 0
2022040320 | 1 | 0.59646 | 47716.8 | 0 | 0 | 0.55116 | 19290.6 | 0.07019 | 982.66 | 40000 | 0 | 7716.8 | 11573.8 | 0 | 982.66 | 12556.46 | 0 | 0 | 0 | 0
2022040321 | 1 | 0.59197 | 47357.6 | 0 | 0 | 0.58734 | 20556.9 | 0.00046 | 6.44 | 40000 | 0 | 7357.6 | 13199.3 | 0 | 6.44 | 13205.74 | 0 | 0 | 0 | 0
2022040322 | 1 | 0.57349 | 45879.2 | 0 | 0 | 0.6175 | 21612.5 | 0 | 0 | 40000 | 0 | 5879.2 | 15733.3 | 0 | 0 | 15733.3 | 0 | 0 | 0 | 0
2022040323 | 1 | 0.53741 | 42992.8 | 0 | 0 | 0.60078 | 21027.3 | 0 | 0 | 40000 | 0 | 2992.8 | 18034.5 | 0 | 0 | 18034.5 | 0 | 0 | 0 | 0
2022040324 | 1 | 0.49584 | 39667.2 | 0 | 0 | 0.58321 | 20412.35 | 0 | 0 | 39667.2 | 332.8 | 0 | 20412.35 | 0 | 0 | 20745.15 | 0 | 0 | 0 | 0
2022040401 | 2 | 0.46215 | 36972 | 0 | 0 | 0.56482 | 19768.7 | 0 | 0 | 36972 | 3028 | 0 | 19768.7 | 0 | 0 | 22796.7 | 0 | 0 | 0 | 0
2022040402 | 2 | 0.43906 | 35124.8 | 0 | 0 | 0.5465 | 19127.5 | 0 | 0 | 35124.8 | 4875.2 | 0 | 19127.5 | 0 | 0 | 24002.7 | 0 | 0 | 0 | 0
2022040403 | 2 | 0.4262 | 34096 | 0 | 0 | 0.50115 | 17540.25 | 0 | 0 | 34096 | 5904 | 0 | 17540.25 | 0 | 0 | 23444.25 | 0 | 0 | 0 | 0
2022040404 | 2 | 0.42194 | 33755.2 | 0 | 0 | 0.45816 | 16035.6 | 0 | 0 | 33755.2 | 6244.8 | 0 | 16035.6 | 0 | 0 | 22280.4 | 0 | 0 | 0 | 0
2022040405 | 2 | 0.42594 | 34075.2 | 0 | 0 | 0.40566 | 14198.1 | 0 | 0 | 34075.2 | 5924.8 | 0 | 14198.1 | 0 | 0 | 20122.9 | 0 | 0 | 0 | 0
2022040406 | 2 | 0.44534 | 35627.2 | 0 | 0 | 0.38594 | 13507.9 | 0 | 0 | 35627.2 | 4372.8 | 0 | 13507.9 | 0 | 0 | 17880.7 | 0 | 0 | 0 | 0
2022040407 | 2 | 0.47773 | 38218.4 | 0 | 0 | 0.35733 | 12506.55 | 0 | 0 | 38218.4 | 1781.6 | 0 | 12506.55 | 0 | 0 | 14288.15 | 0 | 0 | 0 | 0
2022040408 | 2 | 0.49646 | 39716.8 | 0 | 0 | 0.30398 | 10639.3 | 0.00701 | 98.14 | 39716.8 | 283.2 | 0 | 10639.3 | 0 | 98.14 | 11020.64 | 0 | 0 | 0 | 0
2022040409 | 2 | 0.50342 | 40273.6 | 0 | 0 | 0.2569 | 8991.5 | 0.1534 | 2147.6 | 40000 | 0 | 273.6 | 8717.9 | 0 | 2147.6 | 10865.5 | 0 | 0 | 0 | 0
2022040410 | 2 | 0.51592 | 41273.6 | 0 | 0 | 0.2518 | 8813 | 0.37503 | 5250.42 | 40000 | 0 | 1273.6 | 7539.4 | 0 | 5250.42 | 12789.82 | 0 | 0 | 0 | 0
2022040411 | 2 | 0.52862 | 42289.6 | 0 | 0 | 0.26068 | 9123.8 | 0.43518 | 6092.52 | 40000 | 0 | 2289.6 | 6834.2 | 0 | 6092.52 | 12926.72 | 0 | 0 | 0 | 0
2022040412 | 2 | 0.54533 | 43626.4 | 0 | 0 | 0.24441 | 8554.35 | 0.50859 | 7120.26 | 40000 | 0 | 3626.4 | 4927.95 | 0 | 7120.26 | 12048.21 | 0 | 0 | 0 | 0
2022040413 | 2 | 0.5587 | 44696 | 0 | 0 | 0.21876 | 7656.6 | 0.54462 | 7624.68 | 40000 | 0 | 4696 | 2960.6 | 0 | 7624.68 | 10585.28 | 0 | 0 | 0 | 0
2022040414 | 2 | 0.56936 | 45548.8 | 0 | 0 | 0.20159 | 7055.65 | 0.58071 | 8129.94 | 40000 | 0 | 5548.8 | 1506.85 | 0 | 8129.94 | 9636.79 | 0 | 0 | 0 | 0
2022040415 | 2 | 0.57517 | 46013.6 | 0 | 0 | 0.19422 | 6797.7 | 0.57526 | 8053.64 | 40000 | 0 | 6013.6 | 784.1 | 0 | 8053.64 | 8837.74 | 0 | 0 | 0 | 0
2022040416 | 2 | 0.58081 | 46464.8 | 0 | 0 | 0.18684 | 6539.4 | 0.59734 | 8362.76 | 40000 | 0 | 6464.8 | 74.6 | 0 | 8362.76 | 8437.36 | 0 | 0 | 0 | 0
2022040417 | 2 | 0.59079 | 47263.2 | 0 | 0 | 0.19203 | 6721.05 | 0.56161 | 7862.54 | 40000 | 0 | 6721.05 | 0 | 542.15 | 7320.39 | 7320.39 | 0 | 0 | 0 | 0
2022040418 | 2 | 0.59537 | 47629.6 | 0 | 0 | 0.19709 | 6898.15 | 0.55177 | 7724.78 | 40000 | 0 | 6898.15 | 0 | 731.45 | 6993.33 | 6993.33 | 0 | 0 | 0 | 0
2022040419 | 2 | 0.59041 | 47232.8 | 0 | 0 | 0.20445 | 7155.75 | 0.43167 | 6043.38 | 40000 | 0 | 7155.75 | 0 | 77.05 | 5966.33 | 5966.33 | 0 | 0 | 0 | 0
2022040420 | 2 | 0.58713 | 46970.4 | 0 | 0 | 0.19709 | 6898.15 | 0.12474 | 1746.36 | 40000 | 0 | 6898.15 | 0 | 72.25 | 1674.11 | 1674.11 | 0 | 0 | 0 | 0
2022040421 | 2 | 0.58644 | 46915.2 | 0 | 0 | 0.19628 | 6869.8 | 0.00066 | 9.24 | 40000 | 0 | 6869.8 | 0 | 9.24 | 0 | 0 | 36.16 | 0 | 0 | 36.16
2022040422 | 2 | 0.56842 | 45473.6 | 0 | 0 | 0.1716 | 6006 | 0 | 0 | 40000 | 0 | 5473.6 | 532.4 | 0 | 0 | 532.4 | 0 | 0 | 0 | 0
2022040423 | 2 | 0.53786 | 43028.8 | 0 | 0 | 0.15803 | 5531.05 | 0 | 0 | 40000 | 0 | 3028.8 | 2502.25 | 0 | 0 | 2502.25 | 0 | 0 | 0 | 0
2022040424 | 2 | 0.49826 | 39860.8 | 0 | 0 | 0.1658 | 5803 | 0 | 0 | 39860.8 | 139.2 | 0 | 5803 | 0 | 0 | 5942.2 | 0 | 0 | 0 | 0
2022040501 | 3 | 0.46657 | 37325.6 | 0 | 0 | 0.16435 | 5752.25 | 0 | 0 | 37325.6 | 2674.4 | 0 | 5752.25 | 0 | 0 | 8426.65 | 0 | 0 | 0 | 0
2022040502 | 3 | 0.44667 | 35733.6 | 0 | 0 | 0.18179 | 6362.65 | 0 | 0 | 35733.6 | 4266.4 | 0 | 6362.65 | 0 | 0 | 10629.05 | 0 | 0 | 0 | 0
2022040503 | 3 | 0.43361 | 34688.8 | 0 | 0 | 0.1964 | 6874 | 0 | 0 | 34688.8 | 5311.2 | 0 | 6874 | 0 | 0 | 12185.2 | 0 | 0 | 0 | 0
2022040504 | 3 | 0.43123 | 34498.4 | 0 | 0 | 0.23551 | 8242.85 | 0 | 0 | 34498.4 | 5501.6 | 0 | 8242.85 | 0 | 0 | 13744.45 | 0 | 0 | 0 | 0
2022040505 | 3 | 0.43779 | 35023.2 | 0 | 0 | 0.28659 | 10030.65 | 0 | 0 | 35023.2 | 4976.8 | 0 | 10030.65 | 0 | 0 | 15007.45 | 0 | 0 | 0 | 0
2022040506 | 3 | 0.45881 | 36704.8 | 0 | 0 | 0.31887 | 11160.45 | 0 | 0 | 36704.8 | 3295.2 | 0 | 11160.45 | 0 | 0 | 14455.65 | 0 | 0 | 0 | 0
2022040507 | 3 | 0.49697 | 39757.6 | 0 | 0 | 0.3533 | 12365.5 | 0 | 0 | 39757.6 | 242.4 | 0 | 12365.5 | 0 | 0 | 12607.9 | 0 | 0 | 0 | 0
2022040508 | 3 | 0.51536 | 41228.8 | 0 | 0 | 0.39278 | 13747.3 | 0.01447 | 202.58 | 40000 | 0 | 1228.8 | 12518.5 | 0 | 202.58 | 12721.08 | 0 | 0 | 0 | 0
2022040509 | 3 | 0.52572 | 42057.6 | 0 | 0 | 0.40349 | 14122.15 | 0.24993 | 3499.02 | 40000 | 0 | 2057.6 | 12064.55 | 0 | 3499.02 | 15563.57 | 0 | 0 | 0 | 0
2022040510 | 3 | 0.53972 | 43177.6 | 0 | 0 | 0.37123 | 12993.05 | 0.43429 | 6080.06 | 40000 | 0 | 3177.6 | 9815.45 | 0 | 6080.06 | 15895.51 | 0 | 0 | 0 | 0
2022040511 | 3 | 0.56185 | 44948 | 0 | 0 | 0.36616 | 12815.6 | 0.51874 | 7262.36 | 40000 | 0 | 4948 | 7867.6 | 0 | 7262.36 | 15129.96 | 0 | 0 | 0 | 0
2022040512 | 3 | 0.5855 | 46840 | 0 | 0 | 0.39409 | 13793.15 | 0.49015 | 6862.1 | 40000 | 0 | 6840 | 6953.15 | 0 | 6862.1 | 13815.25 | 0 | 0 | 0 | 0
2022040513 | 3 | 0.61866 | 49492.8 | 0 | 0 | 0.4381 | 15333.5 | 0.38927 | 5449.78 | 40000 | 0 | 9492.8 | 5840.7 | 0 | 5449.78 | 11290.48 | 0 | 0 | 0 | 0
2022040514 | 3 | 0.64995 | 51996 | 0 | 0 | 0.46172 | 16160.2 | 0.33823 | 4735.22 | 40000 | 0 | 11996 | 4164.2 | 0 | 4735.22 | 8899.42 | 0 | 0 | 0 | 0
2022040515 | 3 | 0.67731 | 54184.8 | 0 | 0 | 0.46342 | 16219.7 | 0.33083 | 4631.62 | 40000 | 0 | 14184.8 | 2034.9 | 0 | 4631.62 | 6666.52 | 0 | 0 | 0 | 0
2022040516 | 3 | 0.70424 | 56339.2 | 0 | 0 | 0.4653 | 16285.5 | 0.30745 | 4304.3 | 40000 | 0 | 16285.5 | 0 | 53.7 | 4250.6 | 4250.6 | 0 | 0 | 0 | 0
2022040517 | 3 | 0.7261 | 58088 | 0 | 0 | 0.48158 | 16855.3 | 0.28502 | 3990.28 | 40000 | 0 | 16855.3 | 0 | 1232.7 | 2757.58 | 2757.58 | 0 | 0 | 0 | 0
2022040518 | 3 | 0.73253 | 58602.4 | 0 | 0 | 0.4985 | 17447.5 | 0.25967 | 3635.38 | 40000 | 0 | 17447.5 | 0 | 1154.9 | 2480.48 | 2480.48 | 0 | 0 | 0 | 0
2022040519 | 3 | 0.71719 | 57375.2 | 0 | 0 | 0.51156 | 17904.6 | 0.21256 | 2975.84 | 40000 | 0 | 17375.2 | 529.4 | 0 | 2975.84 | 3505.24 | 0 | 0 | 0 | 0
2022040520 | 3 | 0.69328 | 55462.4 | 0 | 0 | 0.50792 | 17777.2 | 0.10554 | 1477.56 | 40000 | 0 | 15462.4 | 2314.8 | 0 | 1477.56 | 3792.36 | 0 | 0 | 0 | 0
2022040521 | 3 | 0.67586 | 54068.8 | 0 | 0 | 0.49303 | 17256.05 | 0.00067 | 9.38 | 40000 | 0 | 14068.8 | 3187.25 | 0 | 9.38 | 3196.63 | 0 | 0 | 0 | 0
2022040522 | 3 | 0.64703 | 51762.4 | 0 | 0 | 0.5432 | 19012 | 0 | 0 | 40000 | 0 | 11762.4 | 7249.6 | 0 | 0 | 7249.6 | 0 | 0 | 0 | 0
2022040523 | 3 | 0.60241 | 48192.8 | 0 | 0 | 0.57053 | 19968.55 | 0 | 0 | 40000 | 0 | 8192.8 | 11775.75 | 0 | 0 | 11775.75 | 0 | 0 | 0 | 0
2022040524 | 3 | 0.55511 | 44408.8 | 0 | 0 | 0.58305 | 20406.75 | 0 | 0 | 40000 | 0 | 4408.8 | 15997.95 | 0 | 0 | 15997.95 | 0 | 0 | 0 | 0
2022040601 | 4 | 0.51748 | 41398.4 | 0 | 0 | 0.59599 | 20859.65 | 0 | 0 | 40000 | 0 | 1398.4 | 19461.25 | 0 | 0 | 19461.25 | 0 | 0 | 0 | 0
2022040602 | 4 | 0.49182 | 39345.6 | 0 | 0 | 0.59511 | 20828.85 | 0 | 0 | 39345.6 | 654.4 | 0 | 20828.85 | 0 | 0 | 21483.25 | 0 | 0 | 0 | 0
2022040603 | 4 | 0.47336 | 37868.8 | 0 | 0 | 0.58643 | 20525.05 | 0 | 0 | 37868.8 | 2131.2 | 0 | 20525.05 | 0 | 0 | 22656.25 | 0 | 0 | 0 | 0
2022040604 | 4 | 0.46145 | 36916 | 0 | 0 | 0.57783 | 20224.05 | 0 | 0 | 36916 | 3084 | 0 | 20224.05 | 0 | 0 | 23308.05 | 0 | 0 | 0 | 0
2022040605 | 4 | 0.45704 | 36563.2 | 0 | 0 | 0.57756 | 20214.6 | 0 | 0 | 36563.2 | 3436.8 | 0 | 20214.6 | 0 | 0 | 23651.4 | 0 | 0 | 0 | 0
2022040606 | 4 | 0.46949 | 37559.2 | 0 | 0 | 0.58164 | 20357.4 | 0 | 0 | 37559.2 | 2440.8 | 0 | 20357.4 | 0 | 0 | 22798.2 | 0 | 0 | 0 | 0
2022040607 | 4 | 0.50155 | 40124 | 0 | 0 | 0.5838 | 20433 | 0 | 0 | 40000 | 0 | 124 | 20309 | 0 | 0 | 20309 | 0 | 0 | 0 | 0
2022040608 | 4 | 0.51542 | 41233.6 | 0 | 0 | 0.56294 | 19702.9 | 0.0165 | 231 | 40000 | 0 | 1233.6 | 18469.3 | 0 | 231 | 18700.3 | 0 | 0 | 0 | 0
2022040609 | 4 | 0.51922 | 41537.6 | 0 | 0 | 0.49966 | 17488.1 | 0.25701 | 3598.14 | 40000 | 0 | 1537.6 | 15950.5 | 0 | 3598.14 | 19548.64 | 0 | 0 | 0 | 0
2022040610 | 4 | 0.52733 | 42186.4 | 0 | 0 | 0.49829 | 17440.15 | 0.28996 | 4059.44 | 40000 | 0 | 2186.4 | 15253.75 | 0 | 4059.44 | 19313.19 | 0 | 0 | 0 | 0
2022040611 | 4 | 0.53935 | 43148 | 0 | 0 | 0.52117 | 18240.95 | 0.27638 | 3869.32 | 40000 | 0 | 3148 | 15092.95 | 0 | 3869.32 | 18962.27 | 0 | 0 | 0 | 0
2022040612 | 4 | 0.54894 | 43915.2 | 0 | 0 | 0.5204 | 18214 | 0.32508 | 4551.12 | 40000 | 0 | 3915.2 | 14298.8 | 0 | 4551.12 | 18849.92 | 0 | 0 | 0 | 0
2022040613 | 4 | 0.55603 | 44482.4 | 0 | 0 | 0.51653 | 18078.55 | 0.41577 | 5820.78 | 40000 | 0 | 4482.4 | 13596.15 | 0 | 5820.78 | 19416.93 | 0 | 0 | 0 | 0
2022040614 | 4 | 0.56741 | 45392.8 | 0 | 0 | 0.48741 | 17059.35 | 0.56375 | 7892.5 | 40000 | 0 | 5392.8 | 11666.55 | 0 | 7892.5 | 19559.05 | 0 | 0 | 0 | 0
2022040615 | 4 | 0.57716 | 46172.8 | 0 | 0 | 0.44312 | 15509.2 | 0.73762 | 10326.68 | 40000 | 0 | 6172.8 | 9336.4 | 0 | 10326.68 | 19663.08 | 0 | 0 | 0 | 0
2022040616 | 4 | 0.5868 | 46944 | 0 | 0 | 0.44589 | 15606.15 | 0.81474 | 11406.36 | 40000 | 0 | 6944 | 8662.15 | 0 | 11406.36 | 20068.51 | 0 | 0 | 0 | 0
2022040617 | 4 | 0.59647 | 47717.6 | 0 | 0 | 0.4535 | 15872.5 | 0.79508 | 11131.12 | 40000 | 0 | 7717.6 | 8154.9 | 0 | 11131.12 | 19286.02 | 0 | 0 | 0 | 0
2022040618 | 4 | 0.59911 | 47928.8 | 0 | 0 | 0.45794 | 16027.9 | 0.77346 | 10828.44 | 40000 | 0 | 7928.8 | 8099.1 | 0 | 10828.44 | 18927.54 | 0 | 0 | 0 | 0
2022040619 | 4 | 0.58563 | 46850.4 | 0 | 0 | 0.45652 | 15978.2 | 0.60932 | 8530.48 | 40000 | 0 | 6850.4 | 9127.8 | 0 | 8530.48 | 17658.28 | 0 | 0 | 0 | 0
2022040620 | 4 | 0.56623 | 45298.4 | 0 | 0 | 0.4379 | 15326.5 | 0.16105 | 2254.7 | 40000 | 0 | 5298.4 | 10028.1 | 0 | 2254.7 | 12282.8 | 0 | 0 | 0 | 0
2022040621 | 4 | 0.56378 | 45102.4 | 0 | 0 | 0.40807 | 14282.45 | 0.00097 | 13.58 | 40000 | 0 | 5102.4 | 9180.05 | 0 | 13.58 | 9193.63 | 0 | 0 | 0 | 0
2022040622 | 4 | 0.54093 | 43274.4 | 0 | 0 | 0.41704 | 14596.4 | 0 | 0 | 40000 | 0 | 3274.4 | 11322 | 0 | 0 | 11322 | 0 | 0 | 0 | 0
2022040623 | 4 | 0.50421 | 40336.8 | 0 | 0 | 0.43282 | 15148.7 | 0 | 0 | 40000 | 0 | 336.8 | 14811.9 | 0 | 0 | 14811.9 | 0 | 0 | 0 | 0
2022040624 | 4 | 0.4626 | 37008 | 0 | 0 | 0.49079 | 17177.65 | 0 | 0 | 37008 | 2992 | 0 | 17177.65 | 0 | 0 | 20169.65 | 0 | 0 | 0 | 0
2022040701 | 5 | 0.43313 | 34650.4 | 0 | 0 | 0.48024 | 16808.4 | 0 | 0 | 34650.4 | 5349.6 | 0 | 16808.4 | 0 | 0 | 22158 | 0 | 0 | 0 | 0
2022040702 | 5 | 0.4151 | 33208 | 0 | 0 | 0.48127 | 16844.45 | 0 | 0 | 33208 | 6792 | 0 | 16844.45 | 0 | 0 | 23636.45 | 0 | 0 | 0 | 0
2022040703 | 5 | 0.40474 | 32379.2 | 0 | 0 | 0.49149 | 17202.15 | 0 | 0 | 32379.2 | 7620.8 | 0 | 17202.15 | 0 | 0 | 24822.95 | 0 | 0 | 0 | 0
2022040704 | 5 | 0.40022 | 32017.6 | 0 | 0 | 0.48013 | 16804.55 | 0 | 0 | 32017.6 | 7982.4 | 0 | 16804.55 | 0 | 0 | 24786.95 | 0 | 0 | 0 | 0
2022040705 | 5 | 0.40513 | 32410.4 | 0 | 0 | 0.45019 | 15756.65 | 0 | 0 | 32410.4 | 7589.6 | 0 | 15756.65 | 0 | 0 | 23346.25 | 0 | 0 | 0 | 0
2022040706 | 5 | 0.4282 | 34256 | 0 | 0 | 0.43132 | 15096.2 | 0 | 0 | 34256 | 5744 | 0 | 15096.2 | 0 | 0 | 20840.2 | 0 | 0 | 0 | 0
2022040707 | 5 | 0.46805 | 37444 | 0 | 0 | 0.42751 | 14962.85 | 0 | 0 | 37444 | 2556 | 0 | 14962.85 | 0 | 0 | 17518.85 | 0 | 0 | 0 | 0
2022040708 | 5 | 0.4856 | 38848 | 0 | 0 | 0.42033 | 14711.55 | 0.02858 | 400.12 | 38848 | 1152 | 0 | 14711.55 | 0 | 400.12 | 16263.67 | 0 | 0 | 0 | 0
2022040709 | 5 | 0.48762 | 39009.6 | 0 | 0 | 0.37657 | 13179.95 | 0.39467 | 5525.38 | 39009.6 | 990.4 | 0 | 13179.95 | 0 | 5525.38 | 19695.73 | 0 | 0 | 0 | 0
2022040710 | 5 | 0.49261 | 39408.8 | 0 | 0 | 0.36994 | 12947.9 | 0.76221 | 10670.94 | 39408.8 | 591.2 | 0 | 12947.9 | 0 | 10670.94 | 24210.04 | 0 | 0 | 0 | 0
2022040711 | 5 | 0.50033 | 40026.4 | 0 | 0 | 0.49499 | 17324.65 | 0.66916 | 9368.24 | 40000 | 0 | 26.4 | 17298.25 | 0 | 9368.24 | 26666.49 | 0 | 0 | 0 | 0
2022040712 | 5 | 0.50222 | 40177.6 | 0 | 0 | 0.48746 | 17061.1 | 0.73599 | 10303.86 | 40000 | 0 | 177.6 | 16883.5 | 0 | 10303.86 | 27187.36 | 0 | 0 | 0 | 0
2022040713 | 5 | 0.5041 | 40328 | 0 | 0 | 0.4358 | 15253 | 0.83313 | 11663.82 | 40000 | 0 | 328 | 14925 | 0 | 11663.82 | 26588.82 | 0 | 0 | 0 | 0
2022040714 | 5 | 0.50791 | 40632.8 | 0 | 0 | 0.39685 | 13889.75 | 0.84913 | 11887.82 | 40000 | 0 | 632.8 | 13256.95 | 0 | 11887.82 | 25144.77 | 0 | 0 | 0 | 0
2022040715 | 5 | 0.51102 | 40881.6 | 0 | 0 | 0.38619 | 13516.65 | 0.84518 | 11832.52 | 40000 | 0 | 881.6 | 12635.05 | 0 | 11832.52 | 24467.57 | 0 | 0 | 0 | 0
2022040716 | 5 | 0.51792 | 41433.6 | 0 | 0 | 0.39066 | 13673.1 | 0.82309 | 11523.26 | 40000 | 0 | 1433.6 | 12239.5 | 0 | 11523.26 | 23762.76 | 0 | 0 | 0 | 0
2022040717 | 5 | 0.52666 | 42132.8 | 0 | 0 | 0.40269 | 14094.15 | 0.78547 | 10996.58 | 40000 | 0 | 2132.8 | 11961.35 | 0 | 10996.58 | 22957.93 | 0 | 0 | 0 | 0
2022040718 | 5 | 0.5327 | 42616 | 0 | 0 | 0.39574 | 13850.9 | 0.77003 | 10780.42 | 40000 | 0 | 2616 | 11234.9 | 0 | 10780.42 | 22015.32 | 0 | 0 | 0 | 0
2022040719 | 5 | 0.52758 | 42206.4 | 0 | 0 | 0.36135 | 12647.25 | 0.59745 | 8364.3 | 40000 | 0 | 2206.4 | 10440.85 | 0 | 8364.3 | 18805.15 | 0 | 0 | 0 | 0
2022040720 | 5 | 0.52221 | 41776.8 | 0 | 0 | 0.31189 | 10916.15 | 0.16944 | 2372.16 | 40000 | 0 | 1776.8 | 9139.35 | 0 | 2372.16 | 11511.51 | 0 | 0 | 0 | 0
2022040721 | 5 | 0.52428 | 41942.4 | 0 | 0 | 0.24667 | 8633.45 | 0.00097 | 13.58 | 40000 | 0 | 1942.4 | 6691.05 | 0 | 13.58 | 6704.63 | 0 | 0 | 0 | 0
2022040722 | 5 | 0.50972 | 40777.6 | 0 | 0 | 0.23628 | 8269.8 | 0 | 0 | 40000 | 0 | 777.6 | 7492.2 | 0 | 0 | 7492.2 | 0 | 0 | 0 | 0
2022040723 | 5 | 0.48051 | 38440.8 | 0 | 0 | 0.25819 | 9036.65 | 0 | 0 | 38440.8 | 1559.2 | 0 | 9036.65 | 0 | 0 | 10595.85 | 0 | 0 | 0 | 0
2022040724 | 5 | 0.44937 | 35949.6 | 0 | 0 | 0.27043 | 9465.05 | 0 | 0 | 35949.6 | 4050.4 | 0 | 9465.05 | 0 | 0 | 13515.45 | 0 | 0 | 0 | 0
2022040801 | 6 | 0.42579 | 34063.2 | 0 | 0 | 0.28189 | 9866.15 | 0 | 0 | 34063.2 | 5936.8 | 0 | 9866.15 | 0 | 0 | 15802.95 | 0 | 0 | 0 | 0
2022040802 | 6 | 0.41148 | 32918.4 | 0 | 0 | 0.28337 | 9917.95 | 0 | 0 | 32918.4 | 7081.6 | 0 | 9917.95 | 0 | 0 | 16999.55 | 0 | 0 | 0 | 0
2022040803 | 6 | 0.4042 | 32336 | 0 | 0 | 0.29645 | 10375.75 | 0 | 0 | 32336 | 7664 | 0 | 10375.75 | 0 | 0 | 18039.75 | 0 | 0 | 0 | 0
2022040804 | 6 | 0.4041 | 32328 | 0 | 0 | 0.30098 | 10534.3 | 0 | 0 | 32328 | 7672 | 0 | 10534.3 | 0 | 0 | 18206.3 | 0 | 0 | 0 | 0
2022040805 | 6 | 0.41133 | 32906.4 | 0 | 0 | 0.31419 | 10996.65 | 0 | 0 | 32906.4 | 7093.6 | 0 | 10996.65 | 0 | 0 | 18090.25 | 0 | 0 | 0 | 0
2022040806 | 6 | 0.43448 | 34758.4 | 0 | 0 | 0.30385 | 10634.75 | 0 | 0 | 34758.4 | 5241.6 | 0 | 10634.75 | 0 | 0 | 15876.35 | 0 | 0 | 0 | 0
2022040807 | 6 | 0.47493 | 37994.4 | 0 | 0 | 0.28888 | 10110.8 | 0 | 0 | 37994.4 | 2005.6 | 0 | 10110.8 | 0 | 0 | 12116.4 | 0 | 0 | 0 | 0
2022040808 | 6 | 0.49539 | 39631.2 | 0 | 0 | 0.29375 | 10281.25 | 0.02996 | 419.44 | 39631.2 | 368.8 | 0 | 10281.25 | 0 | 419.44 | 11069.49 | 0 | 0 | 0 | 0
2022040809 | 6 | 0.49832 | 39865.6 | 0 | 0 | 0.26026 | 9109.1 | 0.42582 | 5961.48 | 39865.6 | 134.4 | 0 | 9109.1 | 0 | 5961.48 | 15204.98 | 0 | 0 | 0 | 0
2022040810 | 6 | 0.4994 | 39952 | 0 | 0 | 0.23262 | 8141.7 | 0.80046 | 11206.44 | 39952 | 48 | 0 | 8141.7 | 0 | 11206.44 | 19396.14 | 0 | 0 | 0 | 0
2022040811 | 6 | 0.49963 | 39970.4 | 0 | 0 | 0.24489 | 8571.15 | 0.84417 | 11818.38 | 39970.4 | 29.6 | 0 | 8571.15 | 0 | 11818.38 | 20419.13 | 0 | 0 | 0 | 0
2022040812 | 6 | 0.49822 | 39857.6 | 0 | 0 | 0.23914 | 8369.9 | 0.85127 | 11917.78 | 39857.6 | 142.4 | 0 | 8369.9 | 0 | 11917.78 | 20430.08 | 0 | 0 | 0 | 0
2022040813 | 6 | 0.49738 | 39790.4 | 0 | 0 | 0.24562 | 8596.7 | 0.85206 | 11928.84 | 39790.4 | 209.6 | 0 | 8596.7 | 0 | 11928.84 | 20735.14 | 0 | 0 | 0 | 0
2022040814 | 6 | 0.50021 | 40016.8 | 0 | 0 | 0.23328 | 8164.8 | 0.84319 | 11804.66 | 40000 | 0 | 16.8 | 8148 | 0 | 11804.66 | 19952.66 | 0 | 0 | 0 | 0
2022040815 | 6 | 0.50394 | 40315.2 | 0 | 0 | 0.23227 | 8129.45 | 0.8534 | 11947.6 | 40000 | 0 | 315.2 | 7814.25 | 0 | 11947.6 | 19761.85 | 0 | 0 | 0 | 0
2022040816 | 6 | 0.50911 | 40728.8 | 0 | 0 | 0.25793 | 9027.55 | 0.85176 | 11924.64 | 40000 | 0 | 728.8 | 8298.75 | 0 | 11924.64 | 20223.39 | 0 | 0 | 0 | 0
2022040817 | 6 | 0.51572 | 41257.6 | 0 | 0 | 0.28844 | 10095.4 | 0.84682 | 11855.48 | 40000 | 0 | 1257.6 | 8837.8 | 0 | 11855.48 | 20693.28 | 0 | 0 | 0 | 0
2022040818 | 6 | 0.51883 | 41506.4 | 0 | 0 | 0.28525 | 9983.75 | 0.82633 | 11568.62 | 40000 | 0 | 1506.4 | 8477.35 | 0 | 11568.62 | 20045.97 | 0 | 0 | 0 | 0
2022040819 | 6 | 0.51396 | 41116.8 | 0 | 0 | 0.23324 | 8163.4 | 0.64888 | 9084.32 | 40000 | 0 | 1116.8 | 7046.6 | 0 | 9084.32 | 16130.92 | 0 | 0 | 0 | 0
2022040820 | 6 | 0.50621 | 40496.8 | 0 | 0 | 0.15424 | 5398.4 | 0.17522 | 2453.08 | 40000 | 0 | 496.8 | 4901.6 | 0 | 2453.08 | 7354.68 | 0 | 0 | 0 | 0
2022040821 | 6 | 0.5075 | 40600 | 0 | 0 | 0.11998 | 4199.3 | 0.00128 | 17.92 | 40000 | 0 | 600 | 3599.3 | 0 | 17.92 | 3617.22 | 0 | 0 | 0 | 0
2022040822 | 6 | 0.49788 | 39830.4 | 0 | 0 | 0.13326 | 4664.1 | 0 | 0 | 39830.4 | 169.6 | 0 | 4664.1 | 0 | 0 | 4833.7 | 0 | 0 | 0 | 0
2022040823 | 6 | 0.47653 | 38122.4 | 0 | 0 | 0.16032 | 5611.2 | 0 | 0 | 38122.4 | 1877.6 | 0 | 5611.2 | 0 | 0 | 7488.8 | 0 | 0 | 0 | 0
2022040824 | 6 | 0.45218 | 36174.4 | 0 | 0 | 0.2002 | 7007 | 0 | 0 | 36174.4 | 3825.6 | 0 | 7007 | 0 | 0 | 10832.6 | 0 | 0 | 0 | 0
2022040901 | 7 | 0.43124 | 34499.2 | 0 | 0 | 0.25796 | 9028.6 | 0 | 0 | 34499.2 | 5500.8 | 0 | 9028.6 | 0 | 0 | 14529.4 | 0 | 0 | 0 | 0
2022040902 | 7 | 0.41869 | 33495.2 | 0 | 0 | 0.31023 | 10858.05 | 0 | 0 | 33495.2 | 6504.8 | 0 | 10858.05 | 0 | 0 | 17362.85 | 0 | 0 | 0 | 0
2022040903 | 7 | 0.41162 | 32929.6 | 0 | 0 | 0.37877 | 13256.95 | 0 | 0 | 32929.6 | 7070.4 | 0 | 13256.95 | 0 | 0 | 20327.35 | 0 | 0 | 0 | 0
2022040904 | 7 | 0.41013 | 32810.4 | 0 | 0 | 0.46822 | 16387.7 | 0 | 0 | 32810.4 | 7189.6 | 0 | 16387.7 | 0 | 0 | 23577.3 | 0 | 0 | 0 | 0
2022040905 | 7 | 0.41521 | 33216.8 | 0 | 0 | 0.55758 | 19515.3 | 0 | 0 | 33216.8 | 6783.2 | 0 | 19515.3 | 0 | 0 | 26298.5 | 0 | 0 | 0 | 0
2022040906 | 7 | 0.42789 | 34231.2 | 0 | 0 | 0.6083 | 21290.5 | 0 | 0 | 34231.2 | 5768.8 | 0 | 21290.5 | 0 | 0 | 27059.3 | 0 | 0 | 0 | 0
2022040907 | 7 | 0.4473 | 35784 | 0 | 0 | 0.64721 | 22652.35 | 0 | 0 | 35784 | 4216 | 0 | 22652.35 | 0 | 0 | 26868.35 | 0 | 0 | 0 | 0
2022040908 | 7 | 0.46535 | 37228 | 0 | 0 | 0.64036 | 22412.6 | 0.03543 | 496.02 | 37228 | 2772 | 0 | 22412.6 | 0 | 496.02 | 25680.62 | 0 | 0 | 0 | 0
2022040909 | 7 | 0.47782 | 38225.6 | 0 | 0 | 0.57993 | 20297.55 | 0.31116 | 4356.24 | 38225.6 | 1774.4 | 0 | 20297.55 | 0 | 4356.24 | 26428.19 | 0 | 0 | 0 | 0
2022040910 | 7 | 0.4851 | 38808 | 0 | 0 | 0.54606 | 19112.1 | 0.51473 | 7206.22 | 38808 | 1192 | 0 | 19112.1 | 0 | 7206.22 | 27510.32 | 0 | 0 | 0 | 0
2022040911 | 7 | 0.48697 | 38957.6 | 0 | 0 | 0.59922 | 20972.7 | 0.46237 | 6473.18 | 38957.6 | 1042.4 | 0 | 20972.7 | 0 | 6473.18 | 28488.28 | 0 | 0 | 0 | 0
2022040912 | 7 | 0.49111 | 39288.8 | 0 | 0 | 0.61435 | 21502.25 | 0.42842 | 5997.88 | 39288.8 | 711.2 | 0 | 21502.25 | 0 | 5997.88 | 28211.33 | 0 | 0 | 0 | 0
2022040913 | 7 | 0.49615 | 39692 | 0 | 0 | 0.6298 | 22043 | 0.3982 | 5574.8 | 39692 | 308 | 0 | 22043 | 0 | 5574.8 | 27925.8 | 0 | 0 | 0 | 0
2022040914 | 7 | 0.50774 | 40619.2 | 0 | 0 | 0.64305 | 22506.75 | 0.39713 | 5559.82 | 40000 | 0 | 619.2 | 21887.55 | 0 | 5559.82 | 27447.37 | 0 | 0 | 0 | 0
2022040915 | 7 | 0.52259 | 41807.2 | 0 | 0 | 0.64703 | 22646.05 | 0.40729 | 5702.06 | 40000 | 0 | 1807.2 | 20838.85 | 0 | 5702.06 | 26540.91 | 0 | 0 | 0 | 0
2022040916 | 7 | 0.53959 | 43167.2 | 0 | 0 | 0.65765 | 23017.75 | 0.38819 | 5434.66 | 40000 | 0 | 3167.2 | 19850.55 | 0 | 5434.66 | 25285.21 | 0 | 0 | 0 | 0
2022040917 | 7 | 0.55879 | 44703.2 | 0 | 0 | 0.66609 | 23313.15 | 0.37163 | 5202.82 | 40000 | 0 | 4703.2 | 18609.95 | 0 | 5202.82 | 23812.77 | 0 | 0 | 0 | 0
2022040918 | 7 | 0.57171 | 45736.8 | 0 | 0 | 0.66364 | 23227.4 | 0.36964 | 5174.96 | 40000 | 0 | 5736.8 | 17490.6 | 0 | 5174.96 | 22665.56 | 0 | 0 | 0 | 0
2022040919 | 7 | 0.5706 | 45648 | 0 | 0 | 0.65794 | 23027.9 | 0.29835 | 4176.9 | 40000 | 0 | 5648 | 17379.9 | 0 | 4176.9 | 21556.8 | 0 | 0 | 0 | 0
2022040920 | 7 | 0.55619 | 44495.2 | 0 | 0 | 0.66313 | 23209.55 | 0.11791 | 1650.74 | 40000 | 0 | 4495.2 | 18714.35 | 0 | 1650.74 | 20365.09 | 0 | 0 | 0 | 0
2022040921 | 7 | 0.5517 | 44136 | 0 | 0 | 0.70707 | 24747.45 | 0.00125 | 17.5 | 40000 | 0 | 4136 | 20611.45 | 0 | 17.5 | 20628.95 | 0 | 0 | 0 | 0
2022040922 | 7 | 0.53689 | 42951.2 | 0 | 0 | 0.72134 | 25246.9 | 0 | 0 | 40000 | 0 | 2951.2 | 22295.7 | 0 | 0 | 22295.7 | 0 | 0 | 0 | 0
2022040923 | 7 | 0.51194 | 40955.2 | 0 | 0 | 0.70949 | 24832.15 | 0 | 0 | 40000 | 0 | 955.2 | 23876.95 | 0 | 0 | 23876.95 | 0 | 0 | 0 | 0
2022040924 | 7 | 0.4837 | 38696 | 0 | 0 | 0.70319 | 24611.65 | 0 | 0 | 38696 | 1304 | 0 | 24611.65 | 0 | 0 | 25915.65 | 0 | 0 | 0 | 0
2022041001 | 1 | 0.45795 | 36636 | 0 | 0 | 0.69519 | 24331.65 | 0 | 0 | 36636 | 3364 | 0 | 24331.65 | 0 | 0 | 27695.65 | 0 | 0 | 0 | 0
2022041002 | 1 | 0.43864 | 35091.2 | 0 | 0 | 0.67671 | 23684.85 | 0 | 0 | 35091.2 | 4908.8 | 0 | 23684.85 | 0 | 0 | 28593.65 | 0 | 0 | 0 | 0
2022041003 | 1 | 0.42312 | 33849.6 | 0 | 0 | 0.64855 | 22699.25 | 0 | 0 | 33849.6 | 6150.4 | 0 | 22699.25 | 0 | 0 | 28849.65 | 0 | 0 | 0 | 0
2022041004 | 1 | 0.41312 | 33049.6 | 0 | 0 | 0.62475 | 21866.25 | 0 | 0 | 33049.6 | 6950.4 | 0 | 21866.25 | 0 | 0 | 28816.65 | 0 | 0 | 0 | 0
2022041005 | 1 | 0.40997 | 32797.6 | 0 | 0 | 0.61952 | 21683.2 | 0 | 0 | 32797.6 | 7202.4 | 0 | 21683.2 | 0 | 0 | 28885.6 | 0 | 0 | 0 | 0
2022041006 | 1 | 0.41119 | 32895.2 | 0 | 0 | 0.62491 | 21871.85 | 0 | 0 | 32895.2 | 7104.8 | 0 | 21871.85 | 0 | 0 | 28976.65 | 0 | 0 | 0 | 0
2022041007 | 1 | 0.41857 | 33485.6 | 0 | 0 | 0.63951 | 22382.85 | 0 | 0 | 33485.6 | 6514.4 | 0 | 22382.85 | 0 | 0 | 28897.25 | 0 | 0 | 0 | 0
2022041008 | 1 | 0.42636 | 34108.8 | 0 | 0 | 0.65089 | 22781.15 | 0.01648 | 230.72 | 34108.8 | 5891.2 | 0 | 22781.15 | 0 | 230.72 | 28903.07 | 0 | 0 | 0 | 0
2022041009 | 1 | 0.4493 | 35944 | 0 | 0 | 0.64551 | 22592.85 | 0.21771 | 3047.94 | 35944 | 4056 | 0 | 22592.85 | 0 | 3047.94 | 29696.79 | 0 | 0 | 0 | 0
2022041010 | 1 | 0.47453 | 37962.4 | 0 | 0 | 0.61579 | 21552.65 | 0.39106 | 5474.84 | 37962.4 | 2037.6 | 0 | 21552.65 | 0 | 5474.84 | 29065.09 | 0 | 0 | 0 | 0
2022041011 | 1 | 0.49842 | 39873.6 | 0 | 0 | 0.58645 | 20525.75 | 0.49879 | 6983.06 | 39873.6 | 126.4 | 0 | 20525.75 | 0 | 6983.06 | 27635.21 | 0 | 0 | 0 | 0
2022041012 | 1 | 0.51897 | 41517.6 | 0 | 0 | 0.53449 | 18707.15 | 0.61844 | 8658.16 | 40000 | 0 | 1517.6 | 17189.55 | 0 | 8658.16 | 25847.71 | 0 | 0 | 0 | 0
2022041013 | 1 | 0.53402 | 42721.6 | 0 | 0 | 0.46601 | 16310.35 | 0.58669 | 8213.66 | 40000 | 0 | 2721.6 | 13588.75 | 0 | 8213.66 | 21802.41 | 0 | 0 | 0 | 0
2022041014 | 1 | 0.55174 | 44139.2 | 0 | 0 | 0.4167 | 14584.5 | 0.5759 | 8062.6 | 40000 | 0 | 4139.2 | 10445.3 | 0 | 8062.6 | 18507.9 | 0 | 0 | 0 | 0
2022041015 | 1 | 0.57067 | 45653.6 | 0 | 0 | 0.4128 | 14448 | 0.59835 | 8376.9 | 40000 | 0 | 5653.6 | 8794.4 | 0 | 8376.9 | 17171.3 | 0 | 0 | 0 | 0
2022041016 | 1 | 0.58962 | 47169.6 | 0 | 0 | 0.45115 | 15790.25 | 0.5914 | 8279.6 | 40000 | 0 | 7169.6 | 8620.65 | 0 | 8279.6 | 16900.25 | 0 | 0 | 0 | 0
2022041017 | 1 | 0.59849 | 47879.2 | 0 | 0 | 0.47771 | 16719.85 | 0.57772 | 8088.08 | 40000 | 0 | 7879.2 | 8840.65 | 0 | 8088.08 | 16928.73 | 0 | 0 | 0 | 0
2022041018 | 1 | 0.60304 | 48243.2 | 0 | 0 | 0.50228 | 17579.8 | 0.50367 | 7051.38 | 40000 | 0 | 8243.2 | 9336.6 | 0 | 7051.38 | 16387.98 | 0 | 0 | 0 | 0
2022041019 | 1 | 0.59758 | 47806.4 | 0 | 0 | 0.5091 | 17818.5 | 0.42876 | 6002.64 | 40000 | 0 | 7806.4 | 10012.1 | 0 | 6002.64 | 16014.74 | 0 | 0 | 0 | 0
2022041020 | 1 | 0.59133 | 47306.4 | 0 | 0 | 0.50634 | 17721.9 | 0.16034 | 2244.76 | 40000 | 0 | 7306.4 | 10415.5 | 0 | 2244.76 | 12660.26 | 0 | 0 | 0 | 0
2022041021 | 1 | 0.59211 | 47368.8 | 0 | 0 | 0.52041 | 18214.35 | 0.0058 | 81.2 | 40000 | 0 | 7368.8 | 10845.55 | 0 | 81.2 | 10926.75 | 0 | 0 | 0 | 0
2022041022 | 1 | 0.57748 | 46198.4 | 0 | 0 | 0.54305 | 19006.75 | 0 | 0 | 40000 | 0 | 6198.4 | 12808.35 | 0 | 0 | 12808.35 | 0 | 0 | 0 | 0
2022041023 | 1 | 0.54747 | 43797.6 | 0 | 0 | 0.54331 | 19015.85 | 0 | 0 | 40000 | 0 | 3797.6 | 15218.25 | 0 | 0 | 15218.25 | 0 | 0 | 0 | 0
2022041024 | 1 | 0.50978 | 40782.4 | 0 | 0 | 0.54226 | 18979.1 | 0 | 0 | 40000 | 0 | 782.4 | 18196.7 | 0 | 0 | 18196.7 | 0 | 0 | 0 | 0
2022041101 | 2 | 0.47996 | 38396.8 | 0 | 0 | 0.574 | 20090 | 0 | 0 | 38396.8 | 1603.2 | 0 | 20090 | 0 | 0 | 21693.2 | 0 | 0 | 0 | 0
2022041102 | 2 | 0.46097 | 36877.6 | 0 | 0 | 0.59854 | 20948.9 | 0 | 0 | 36877.6 | 3122.4 | 0 | 20948.9 | 0 | 0 | 24071.3 | 0 | 0 | 0 | 0
2022041103 | 2 | 0.45196 | 36156.8 | 0 | 0 | 0.61604 | 21561.4 | 0 | 0 | 36156.8 | 3843.2 | 0 | 21561.4 | 0 | 0 | 25404.6 | 0 | 0 | 0 | 0
2022041104 | 2 | 0.44782 | 35825.6 | 0 | 0 | 0.61948 | 21681.8 | 0 | 0 | 35825.6 | 4174.4 | 0 | 21681.8 | 0 | 0 | 25856.2 | 0 | 0 | 0 | 0
2022041105 | 2 | 0.45398 | 36318.4 | 0 | 0 | 0.59953 | 20983.55 | 0 | 0 | 36318.4 | 3681.6 | 0 | 20983.55 | 0 | 0 | 24665.15 | 0 | 0 | 0 | 0
2022041106 | 2 | 0.47113 | 37690.4 | 0 | 0 | 0.53541 | 18739.35 | 0 | 0 | 37690.4 | 2309.6 | 0 | 18739.35 | 0 | 0 | 21048.95 | 0 | 0 | 0 | 0
2022041107 | 2 | 0.5022 | 40176 | 0 | 0 | 0.48363 | 16927.05 | 0 | 0 | 40000 | 0 | 176 | 16751.05 | 0 | 0 | 16751.05 | 0 | 0 | 0 | 0
2022041108 | 2 | 0.51832 | 41465.6 | 0 | 0 | 0.44618 | 15616.3 | 0.02289 | 320.46 | 40000 | 0 | 1465.6 | 14150.7 | 0 | 320.46 | 14471.16 | 0 | 0 | 0 | 0
2022041109 | 2 | 0.52797 | 42237.6 | 0 | 0 | 0.38214 | 13374.9 | 0.35014 | 4901.96 | 40000 | 0 | 2237.6 | 11137.3 | 0 | 4901.96 | 16039.26 | 0 | 0 | 0 | 0
2022041110 | 2 | 0.54757 | 43805.6 | 0 | 0 | 0.3506 | 12271 | 0.64678 | 9054.92 | 40000 | 0 | 3805.6 | 8465.4 | 0 | 9054.92 | 17520.32 | 0 | 0 | 0 | 0
2022041111 | 2 | 0.56795 | 45436 | 0 | 0 | 0.35899 | 12564.65 | 0.72168 | 10103.52 | 40000 | 0 | 5436 | 7128.65 | 0 | 10103.52 | 17232.17 | 0 | 0 | 0 | 0
2022041112 | 2 | 0.58497 | 46797.6 | 0 | 0 | 0.32685 | 11439.75 | 0.74376 | 10412.64 | 40000 | 0 | 6797.6 | 4642.15 | 0 | 10412.64 | 15054.79 | 0 | 0 | 0 | 0
2022041113 | 2 | 0.60581 | 48464.8 | 0 | 0 | 0.24686 | 8640.1 | 0.77061 | 10788.54 | 40000 | 0 | 8464.8 | 175.3 | 0 | 10788.54 | 10963.84 | 0 | 0 | 0 | 0
2022041114 | 2 | 0.62427 | 49941.6 | 0 | 0 | 0.18923 | 6623.05 | 0.77121 | 10796.94 | 40000 | 0 | 6623.05 | 0 | 3318.55 | 7478.39 | 7478.39 | 0 | 0 | 0 | 0
2022041115 | 2 | 0.64212 | 51369.6 | 0 | 0 | 0.16988 | 5945.8 | 0.76434 | 10700.76 | 40000 | 0 | 5945.8 | 0 | 5423.8 | 5276.96 | 5276.96 | 0 | 0 | 0 | 0
2022041116 | 2 | 0.65911 | 52728.8 | 0 | 0 | 0.17824 | 6238.4 | 0.761 | 10654 | 40000 | 0 | 6238.4 | 0 | 6490.4 | 4163.6 | 4163.6 | 0 | 0 | 0 | 0
2022041117 | 2 | 0.67648 | 54118.4 | 0 | 0 | 0.19987 | 6995.45 | 0.73939 | 10351.46 | 40000 | 0 | 6995.45 | 0 | 7122.95 | 3228.51 | 3228.51 | 0 | 0 | 0 | 0
2022041118 | 2 | 0.68235 | 54588 | 0 | 0 | 0.21787 | 7625.45 | 0.7374 | 10323.6 | 40000 | 0 | 7625.45 | 0 | 6962.55 | 3361.05 | 3361.05 | 0 | 0 | 0 | 0
2022041119 | 2 | 0.67275 | 53820 | 0 | 0 | 0.25562 | 8946.7 | 0.58092 | 8132.88 | 40000 | 0 | 8946.7 | 0 | 4873.3 | 3259.58 | 3259.58 | 0 | 0 | 0 | 0
2022041120 | 2 | 0.65659 | 52527.2 | 0 | 0 | 0.27868 | 9753.8 | 0.18379 | 2573.06 | 40000 | 0 | 9753.8 | 0 | 2573.06 | 0 | 0 | 200.34 | 0 | 0 | 200.34
2022041121 | 2 | 0.6494 | 51952 | 0 | 0 | 0.32239 | 11283.65 | 0.00192 | 26.88 | 40000 | 0 | 11283.65 | 0 | 26.88 | 0 | 0 | 641.47 | 0 | 0 | 641.47
2022041122 | 2 | 0.63191 | 50552.8 | 0 | 0 | 0.42026 | 14709.1 | 0 | 0 | 40000 | 0 | 10552.8 | 4156.3 | 0 | 0 | 4156.3 | 0 | 0 | 0 | 0
2022041123 | 2 | 0.59478 | 47582.4 | 0 | 0 | 0.5212 | 18242 | 0 | 0 | 40000 | 0 | 7582.4 | 10659.6 | 0 | 0 | 10659.6 | 0 | 0 | 0 | 0
2022041124 | 2 | 0.55258 | 44206.4 | 0 | 0 | 0.59475 | 20816.25 | 0 | 0 | 40000 | 0 | 4206.4 | 16609.85 | 0 | 0 | 16609.85 | 0 | 0 | 0 | 0
2022041201 | 3 | 0.52015 | 41612 | 0 | 0 | 0.61789 | 21626.15 | 0 | 0 | 40000 | 0 | 1612 | 20014.15 | 0 | 0 | 20014.15 | 0 | 0 | 0 | 0
2022041202 | 3 | 0.49788 | 39830.4 | 0 | 0 | 0.61109 | 21388.15 | 0 | 0 | 39830.4 | 169.6 | 0 | 21388.15 | 0 | 0 | 21557.75 | 0 | 0 | 0 | 0
2022041203 | 3 | 0.48246 | 38596.8 | 0 | 0 | 0.5898 | 20643 | 0 | 0 | 38596.8 | 1403.2 | 0 | 20643 | 0 | 0 | 22046.2 | 0 | 0 | 0 | 0
2022041204 | 3 | 0.47685 | 38148 | 0 | 0 | 0.57472 | 20115.2 | 0 | 0 | 38148 | 1852 | 0 | 20115.2 | 0 | 0 | 21967.2 | 0 | 0 | 0 | 0
2022041205 | 3 | 0.48084 | 38467.2 | 0 | 0 | 0.57731 | 20205.85 | 0 | 0 | 38467.2 | 1532.8 | 0 | 20205.85 | 0 | 0 | 21738.65 | 0 | 0 | 0 | 0
2022041206 | 3 | 0.49921 | 39936.8 | 0 | 0 | 0.59634 | 20871.9 | 0 | 0 | 39936.8 | 63.2 | 0 | 20871.9 | 0 | 0 | 20935.1 | 0 | 0 | 0 | 0
2022041207 | 3 | 0.53379 | 42703.2 | 0 | 0 | 0.60819 | 21286.65 | 0 | 0 | 40000 | 0 | 2703.2 | 18583.45 | 0 | 0 | 18583.45 | 0 | 0 | 0 | 0
2022041208 | 3 | 0.54965 | 43972 | 0 | 0 | 0.58996 | 20648.6 | 0.01007 | 140.98 | 40000 | 0 | 3972 | 16676.6 | 0 | 140.98 | 16817.58 | 0 | 0 | 0 | 0
2022041209 | 3 | 0.55607 | 44485.6 | 0 | 0 | 0.55192 | 19317.2 | 0.15893 | 2225.02 | 40000 | 0 | 4485.6 | 14831.6 | 0 | 2225.02 | 17056.62 | 0 | 0 | 0 | 0
2022041210 | 3 | 0.56815 | 45452 | 0 | 0 | 0.53535 | 18737.25 | 0.21901 | 3066.14 | 40000 | 0 | 5452 | 13285.25 | 0 | 3066.14 | 16351.39 | 0 | 0 | 0 | 0
2022041211 | 3 | 0.58262 | 46609.6 | 0 | 0 | 0.54191 | 18966.85 | 0.23469 | 3285.66 | 40000 | 0 | 6609.6 | 12357.25 | 0 | 3285.66 | 15642.91 | 0 | 0 | 0 | 0
2022041212 | 3 | 0.59681 | 47744.8 | 0 | 0 | 0.52871 | 18504.85 | 0.31631 | 4428.34 | 40000 | 0 | 7744.8 | 10760.05 | 0 | 4428.34 | 15188.39 | 0 | 0 | 0 | 0
2022041213 | 3 | 0.61294 | 49035.2 | 0 | 0 | 0.52548 | 18391.8 | 0.35626 | 4987.64 | 40000 | 0 | 9035.2 | 9356.6 | 0 | 4987.64 | 14344.24 | 0 | 0 | 0 | 0
2022041214 | 3 | 0.63532 | 50825.6 | 0 | 0 | 0.53737 | 18807.95 | 0.36556 | 5117.84 | 40000 | 0 | 10825.6 | 7982.35 | 0 | 5117.84 | 13100.19 | 0 | 0 | 0 | 0
2022041215 | 3 | 0.65378 | 52302.4 | 0 | 0 | 0.5669 | 19841.5 | 0.31323 | 4385.22 | 40000 | 0 | 12302.4 | 7539.1 | 0 | 4385.22 | 11924.32 | 0 | 0 | 0 | 0
2022041216 | 3 | 0.66642 | 53313.6 | 0 | 0 | 0.58558 | 20495.3 | 0.29689 | 4156.46 | 40000 | 0 | 13313.6 | 7181.7 | 0 | 4156.46 | 11338.16 | 0 | 0 | 0 | 0
2022041217 | 3 | 0.67648 | 54118.4 | 0 | 0 | 0.60799 | 21279.65 | 0.24113 | 3375.82 | 40000 | 0 | 14118.4 | 7161.25 | 0 | 3375.82 | 10537.07 | 0 | 0 | 0 | 0
2022041218 | 3 | 0.68178 | 54542.4 | 0 | 0 | 0.61864 | 21652.4 | 0.17494 | 2449.16 | 40000 | 0 | 14542.4 | 7110 | 0 | 2449.16 | 9559.16 | 0 | 0 | 0 | 0
2022041219 | 3 | 0.66973 | 53578.4 | 0 | 0 | 0.60527 | 21184.45 | 0.13386 | 1874.04 | 40000 | 0 | 13578.4 | 7606.05 | 0 | 1874.04 | 9480.09 | 0 | 0 | 0 | 0
2022041220 | 3 | 0.65006 | 52004.8 | 0 | 0 | 0.60506 | 21177.1 | 0.05816 | 814.24 | 40000 | 0 | 12004.8 | 9172.3 | 0 | 814.24 | 9986.54 | 0 | 0 | 0 | 0
2022041221 | 3 | 0.63845 | 51076 | 0 | 0 | 0.60301 | 21105.35 | 0.00139 | 19.46 | 40000 | 0 | 11076 | 10029.35 | 0 | 19.46 | 10048.81 | 0 | 0 | 0 | 0
2022041222 | 3 | 0.618 | 49440 | 0 | 0 | 0.60733 | 21256.55 | 0 | 0 | 40000 | 0 | 9440 | 11816.55 | 0 | 0 | 11816.55 | 0 | 0 | 0 | 0
2022041223 | 3 | 0.58208 | 46566.4 | 0 | 0 | 0.58227 | 20379.45 | 0 | 0 | 40000 | 0 | 6566.4 | 13813.05 | 0 | 0 | 13813.05 | 0 | 0 | 0 | 0
2022041224 | 3 | 0.54158 | 43326.4 | 0 | 0 | 0.57398 | 20089.3 | 0 | 0 | 40000 | 0 | 3326.4 | 16762.9 | 0 | 0 | 16762.9 | 0 | 0 | 0 | 0
2022041301 | 4 | 0.51321 | 41056.8 | 0 | 0 | 0.58219 | 20376.65 | 0 | 0 | 40000 | 0 | 1056.8 | 19319.85 | 0 | 0 | 19319.85 | 0 | 0 | 0 | 0
2022041302 | 4 | 0.49385 | 39508 | 0 | 0 | 0.57776 | 20221.6 | 0 | 0 | 39508 | 492 | 0 | 20221.6 | 0 | 0 | 20713.6 | 0 | 0 | 0 | 0
2022041303 | 4 | 0.48278 | 38622.4 | 0 | 0 | 0.58225 | 20378.75 | 0 | 0 | 38622.4 | 1377.6 | 0 | 20378.75 | 0 | 0 | 21756.35 | 0 | 0 | 0 | 0
2022041304 | 4 | 0.4783 | 38264 | 0 | 0 | 0.59516 | 20830.6 | 0 | 0 | 38264 | 1736 | 0 | 20830.6 | 0 | 0 | 22566.6 | 0 | 0 | 0 | 0
2022041305 | 4 | 0.48443 | 38754.4 | 0 | 0 | 0.59487 | 20820.45 | 0 | 0 | 38754.4 | 1245.6 | 0 | 20820.45 | 0 | 0 | 22066.05 | 0 | 0 | 0 | 0
2022041306 | 4 | 0.50471 | 40376.8 | 0 | 0 | 0.58689 | 20541.15 | 0 | 0 | 40000 | 0 | 376.8 | 20164.35 | 0 | 0 | 20164.35 | 0 | 0 | 0 | 0
2022041307 | 4 | 0.54054 | 43243.2 | 0 | 0 | 0.60783 | 21274.05 | 0 | 0 | 40000 | 0 | 3243.2 | 18030.85 | 0 | 0 | 18030.85 | 0 | 0 | 0 | 0
2022041308 | 4 | 0.55721 | 44576.8 | 0 | 0 | 0.61434 | 21501.9 | 0.0162 | 226.8 | 40000 | 0 | 4576.8 | 16925.1 | 0 | 226.8 | 17151.9 | 0 | 0 | 0 | 0
2022041309 | 4 | 0.56397 | 45117.6 | 0 | 0 | 0.5507 | 19274.5 | 0.2205 | 3087 | 40000 | 0 | 5117.6 | 14156.9 | 0 | 3087 | 17243.9 | 0 | 0 | 0 | 0
2022041310 | 4 | 0.57359 | 45887.2 | 0 | 0 | 0.4829 | 16901.5 | 0.39364 | 5510.96 | 40000 | 0 | 5887.2 | 11014.3 | 0 | 5510.96 | 16525.26 | 0 | 0 | 0 | 0
2022041311 | 4 | 0.59111 | 47288.8 | 0 | 0 | 0.39256 | 13739.6 | 0.66888 | 9364.32 | 40000 | 0 | 7288.8 | 6450.8 | 0 | 9364.32 | 15815.12 | 0 | 0 | 0 | 0
2022041312 | 4 | 0.60609 | 48487.2 | 0 | 0 | 0.405 | 14175 | 0.6695 | 9373 | 40000 | 0 | 8487.2 | 5687.8 | 0 | 9373 | 15060.8 | 0 | 0 | 0 | 0
2022041313 | 4 | 0.62206 | 49764.8 | 0 | 0 | 0.43836 | 15342.6 | 0.6011 | 8415.4 | 40000 | 0 | 9764.8 | 5577.8 | 0 | 8415.4 | 13993.2 | 0 | 0 | 0 | 0
2022041314 | 4 | 0.63494 | 50795.2 | 0 | 0 | 0.452 | 15820 | 0.521 | 7294 | 40000 | 0 | 10795.2 | 5024.8 | 0 | 7294 | 12318.8 | 0 | 0 | 0 | 0
2022041315 | 4 | 0.64323 | 51458.4 | 0 | 0 | 0.46341 | 16219.35 | 0.45316 | 6344.24 | 40000 | 0 | 11458.4 | 4760.95 | 0 | 6344.24 | 11105.19 | 0 | 0 | 0 | 0
2022041316 | 4 | 0.64949 | 51959.2 | 0 | 0 | 0.45829 | 16040.15 | 0.48815 | 6834.1 | 40000 | 0 | 11959.2 | 4080.95 | 0 | 6834.1 | 10915.05 | 0 | 0 | 0 | 0
2022041317 | 4 | 0.6613 | 52904 | 0 | 0 | 0.44043 | 15415.05 | 0.5388 | 7543.2 | 40000 | 0 | 12904 | 2511.05 | 0 | 7543.2 | 10054.25 | 0 | 0 | 0 | 0
2022041318 | 4 | 0.6681 | 53448 | 0 | 0 | 0.42302 | 14805.7 | 0.59171 | 8283.94 | 40000 | 0 | 13448 | 1357.7 | 0 | 8283.94 | 9641.64 | 0 | 0 | 0 | 0
2022041319 | 4 | 0.65614 | 52491.2 | 0 | 0 | 0.3534 | 12369 | 0.61075 | 8550.5 | 40000 | 0 | 12369 | 0 | 122.2 | 8428.3 | 8428.3 | 0 | 0 | 0 | 0
2022041320 | 4 | 0.63035 | 50428 | 0 | 0 | 0.24997 | 8748.95 | 0.19771 | 2767.94 | 40000 | 0 | 8748.95 | 0 | 1679.05 | 1088.89 | 1088.89 | 0 | 0 | 0 | 0
2022041321 | 4 | 0.61561 | 49248.8 | 0 | 0 | 0.19319 | 6761.65 | 0.00231 | 32.34 | 40000 | 0 | 6761.65 | 0 | 32.34 | 0 | 0 | 2454.81 | 0 | 0 | 2454.81
2022041322 | 4 | 0.59217 | 47373.6 | 0 | 0 | 0.21002 | 7350.7 | 0 | 0 | 40000 | 0 | 7350.7 | 0 | 0 | 0 | 0 | 22.9 | 0 | 0 | 22.9
2022041323 | 4 | 0.54908 | 43926.4 | 0 | 0 | 0.21473 | 7515.55 | 0 | 0 | 40000 | 0 | 3926.4 | 3589.15 | 0 | 0 | 3589.15 | 0 | 0 | 0 | 0
2022041324 | 4 | 0.50358 | 40286.4 | 0 | 0 | 0.22268 | 7793.8 | 0 | 0 | 40000 | 0 | 286.4 | 7507.4 | 0 | 0 | 7507.4 | 0 | 0 | 0 | 0
2022041401 | 5 | 0.46725 | 37380 | 0 | 0 | 0.23116 | 8090.6 | 0 | 0 | 37380 | 2620 | 0 | 8090.6 | 0 | 0 | 10710.6 | 0 | 0 | 0 | 0
2022041402 | 5 | 0.442 | 35360 | 0 | 0 | 0.25387 | 8885.45 | 0 | 0 | 35360 | 4640 | 0 | 8885.45 | 0 | 0 | 13525.45 | 0 | 0 | 0 | 0
2022041403 | 5 | 0.42632 | 34105.6 | 0 | 0 | 0.29455 | 10309.25 | 0 | 0 | 34105.6 | 5894.4 | 0 | 10309.25 | 0 | 0 | 16203.65 | 0 | 0 | 0 | 0
2022041404 | 5 | 0.4186 | 33488 | 0 | 0 | 0.34031 | 11910.85 | 0 | 0 | 33488 | 6512 | 0 | 11910.85 | 0 | 0 | 18422.85 | 0 | 0 | 0 | 0
2022041405 | 5 | 0.42062 | 33649.6 | 0 | 0 | 0.3892 | 13622 | 0 | 0 | 33649.6 | 6350.4 | 0 | 13622 | 0 | 0 | 19972.4 | 0 | 0 | 0 | 0
2022041406 | 5 | 0.4395 | 35160 | 0 | 0 | 0.41053 | 14368.55 | 0 | 0 | 35160 | 4840 | 0 | 14368.55 | 0 | 0 | 19208.55 | 0 | 0 | 0 | 0
2022041407 | 5 | 0.47508 | 38006.4 | 0 | 0 | 0.41756 | 14614.6 | 0 | 0 | 38006.4 | 1993.6 | 0 | 14614.6 | 0 | 0 | 16608.2 | 0 | 0 | 0 | 0
2022041408 | 5 | 0.49168 | 39334.4 | 0 | 0 | 0.38607 | 13512.45 | 0.05306 | 742.84 | 39334.4 | 665.6 | 0 | 13512.45 | 0 | 742.84 | 14920.89 | 0 | 0 | 0 | 0
2022041409 | 5 | 0.49884 | 39907.2 | 0 | 0 | 0.31657 | 11079.95 | 0.46554 | 6517.56 | 39907.2 | 92.8 | 0 | 11079.95 | 0 | 6517.56 | 17690.31 | 0 | 0 | 0 | 0
2022041410 | 5 | 0.50603 | 40482.4 | 0 | 0 | 0.32252 | 11288.2 | 0.71202 | 9968.28 | 40000 | 0 | 482.4 | 10805.8 | 0 | 9968.28 | 20774.08 | 0 | 0 | 0 | 0
2022041411 | 5 | 0.51615 | 41292 | 0 | 0 | 0.37822 | 13237.7 | 0.70472 | 9866.08 | 40000 | 0 | 1292 | 11945.7 | 0 | 9866.08 | 21811.78 | 0 | 0 | 0 | 0
2022041412 | 5 | 0.52643 | 42114.4 | 0 | 0 | 0.37695 | 13193.25 | 0.75471 | 10565.94 | 40000 | 0 | 2114.4 | 11078.85 | 0 | 10565.94 | 21644.79 | 0 | 0 | 0 | 0
2022041413 | 5 | 0.53749 | 42999.2 | 0 | 0 | 0.38042 | 13314.7 | 0.80785 | 11309.9 | 40000 | 0 | 2999.2 | 10315.5 | 0 | 11309.9 | 21625.4 | 0 | 0 | 0 | 0
2022041414 | 5 | 0.55434 | 44347.2 | 0 | 0 | 0.39132 | 13696.2 | 0.81621 | 11426.94 | 40000 | 0 | 4347.2 | 9349 | 0 | 11426.94 | 20775.94 | 0 | 0 | 0 | 0
2022041415 | 5 | 0.56997 | 45597.6 | 0 | 0 | 0.42076 | 14726.6 | 0.78051 | 10927.14 | 40000 | 0 | 5597.6 | 9129 | 0 | 10927.14 | 20056.14 | 0 | 0 | 0 | 0
2022041416 | 5 | 0.58613 | 46890.4 | 0 | 0 | 0.45088 | 15780.8 | 0.68019 | 9522.66 | 40000 | 0 | 6890.4 | 8890.4 | 0 | 9522.66 | 18413.06 | 0 | 0 | 0 | 0
2022041417 | 5 | 0.60387 | 48309.6 | 0 | 0 | 0.49614 | 17364.9 | 0.54974 | 7696.36 | 40000 | 0 | 8309.6 | 9055.3 | 0 | 7696.36 | 16751.66 | 0 | 0 | 0 | 0
2022041418 | 5 | 0.61034 | 48827.2 | 0 | 0 | 0.52977 | 18541.95 | 0.4299 | 6018.6 | 40000 | 0 | 8827.2 | 9714.75 | 0 | 6018.6 | 15733.35 | 0 | 0 | 0 | 0
2022041419 | 5 | 0.60087 | 48069.6 | 0 | 0 | 0.54729 | 19155.15 | 0.28257 | 3955.98 | 40000 | 0 | 8069.6 | 11085.55 | 0 | 3955.98 | 15041.53 | 0 | 0 | 0 | 0
2022041420 | 5 | 0.58378 | 46702.4 | 0 | 0 | 0.55953 | 19583.55 | 0.09409 | 1317.26 | 40000 | 0 | 6702.4 | 12881.15 | 0 | 1317.26 | 14198.41 | 0 | 0 | 0 | 0
2022041421 | 5 | 0.5769 | 46152 | 0 | 0 | 0.58153 | 20353.55 | 0.00223 | 31.22 | 40000 | 0 | 6152 | 14201.55 | 0 | 31.22 | 14232.77 | 0 | 0 | 0 | 0
2022041422 | 5 | 0.55806 | 44644.8 | 0 | 0 | 0.5785 | 20247.5 | 0 | 0 | 40000 | 0 | 4644.8 | 15602.7 | 0 | 0 | 15602.7 | 0 | 0 | 0 | 0
2022041423 | 5 | 0.52762 | 42209.6 | 0 | 0 | 0.56904 | 19916.4 | 0 | 0 | 40000 | 0 | 2209.6 | 17706.8 | 0 | 0 | 17706.8 | 0 | 0 | 0 | 0
2022041424 | 5 | 0.49161 | 39328.8 | 0 | 0 | 0.55242 | 19334.7 | 0 | 0 | 39328.8 | 671.2 | 0 | 19334.7 | 0 | 0 | 20005.9 | 0 | 0 | 0 | 0
2022041501 | 6 | 0.46018 | 36814.4 | 0 | 0 | 0.53962 | 18886.7 | 0 | 0 | 36814.4 | 3185.6 | 0 | 18886.7 | 0 | 0 | 22072.3 | 0 | 0 | 0 | 0
2022041502 | 6 | 0.4413 | 35304 | 0 | 0 | 0.51725 | 18103.75 | 0 | 0 | 35304 | 4696 | 0 | 18103.75 | 0 | 0 | 22799.75 | 0 | 0 | 0 | 0
2022041503 | 6 | 0.43156 | 34524.8 | 0 | 0 | 0.50127 | 17544.45 | 0 | 0 | 34524.8 | 5475.2 | 0 | 17544.45 | 0 | 0 | 23019.65 | 0 | 0 | 0 | 0
2022041504 | 6 | 0.42588 | 34070.4 | 0 | 0 | 0.49701 | 17395.35 | 0 | 0 | 34070.4 | 5929.6 | 0 | 17395.35 | 0 | 0 | 23324.95 | 0 | 0 | 0 | 0
2022041505 | 6 | 0.42852 | 34281.6 | 0 | 0 | 0.49667 | 17383.45 | 0 | 0 | 34281.6 | 5718.4 | 0 | 17383.45 | 0 | 0 | 23101.85 | 0 | 0 | 0 | 0
2022041506 | 6 | 0.44008 | 35206.4 | 0 | 0 | 0.49801 | 17430.35 | 0 | 0 | 35206.4 | 4793.6 | 0 | 17430.35 | 0 | 0 | 22223.95 | 0 | 0 | 0 | 0
2022041507 | 6 | 0.46055 | 36844 | 0 | 0 | 0.49554 | 17343.9 | 0 | 0 | 36844 | 3156 | 0 | 17343.9 | 0 | 0 | 20499.9 | 0 | 0 | 0 | 0
2022041508 | 6 | 0.47412 | 37929.6 | 0 | 0 | 0.49415 | 17295.25 | 0.02019 | 282.66 | 37929.6 | 2070.4 | 0 | 17295.25 | 0 | 282.66 | 19648.31 | 0 | 0 | 0 | 0
2022041509 | 6 | 0.49042 | 39233.6 | 0 | 0 | 0.46897 | 16413.95 | 0.13905 | 1946.7 | 39233.6 | 766.4 | 0 | 16413.95 | 0 | 1946.7 | 19127.05 | 0 | 0 | 0 | 0
2022041510 | 6 | 0.50989 | 40791.2 | 0 | 0 | 0.46669 | 16334.15 | 0.18122 | 2537.08 | 40000 | 0 | 791.2 | 15542.95 | 0 | 2537.08 | 18080.03 | 0 | 0 | 0 | 0
2022041511 | 6 | 0.52571 | 42056.8 | 0 | 0 | 0.46695 | 16343.25 | 0.23737 | 3323.18 | 40000 | 0 | 2056.8 | 14286.45 | 0 | 3323.18 | 17609.63 | 0 | 0 | 0 | 0
2022041512 | 6 | 0.54082 | 43265.6 | 0 | 0 | 0.43375 | 15181.25 | 0.39232 | 5492.48 | 40000 | 0 | 3265.6 | 11915.65 | 0 | 5492.48 | 17408.13 | 0 | 0 | 0 | 0
2022041513 | 6 | 0.55813 | 44650.4 | 0 | 0 | 0.39537 | 13837.95 | 0.5453 | 7634.2 | 40000 | 0 | 4650.4 | 9187.55 | 0 | 7634.2 | 16821.75 | 0 | 0 | 0 | 0
2022041514 | 6 | 0.57187 | 45749.6 | 0 | 0 | 0.34858 | 12200.3 | 0.68675 | 9614.5 | 40000 | 0 | 5749.6 | 6450.7 | 0 | 9614.5 | 16065.2 | 0 | 0 | 0 | 0
2022041515 | 6 | 0.58809 | 47047.2 | 0 | 0 | 0.33849 | 11847.15 | 0.64524 | 9033.36 | 40000 | 0 | 7047.2 | 4799.95 | 0 | 9033.36 | 13833.31 | 0 | 0 | 0 | 0
2022041516 | 6 | 0.60658 | 48526.4 | 0 | 0 | 0.36108 | 12637.8 | 0.61408 | 8597.12 | 40000 | 0 | 8526.4 | 4111.4 | 0 | 8597.12 | 12708.52 | 0 | 0 | 0 | 0
2022041517 | 6 | 0.6237 | 49896 | 0 | 0 | 0.37951 | 13282.85 | 0.61761 | 8646.54 | 40000 | 0 | 9896 | 3386.85 | 0 | 8646.54 | 12033.39 | 0 | 0 | 0 | 0
2022041518 | 6 | 0.63298 | 50638.4 | 0 | 0 | 0.38905 | 13616.75 | 0.59039 | 8265.46 | 40000 | 0 | 10638.4 | 2978.35 | 0 | 8265.46 | 11243.81 | 0 | 0 | 0 | 0
2022041519 | 6 | 0.62655 | 50124 | 0 | 0 | 0.38308 | 13407.8 | 0.42773 | 5988.22 | 40000 | 0 | 10124 | 3283.8 | 0 | 5988.22 | 9272.02 | 0 | 0 | 0 | 0
2022041520 | 6 | 0.61178 | 48942.4 | 0 | 0 | 0.3407 | 11924.5 | 0.10407 | 1456.98 | 40000 | 0 | 8942.4 | 2982.1 | 0 | 1456.98 | 4439.08 | 0 | 0 | 0 | 0
2022041521 | 6 | 0.60744 | 48595.2 | 0 | 0 | 0.36493 | 12772.55 | 0.00108 | 15.12 | 40000 | 0 | 8595.2 | 4177.35 | 0 | 15.12 | 4192.47 | 0 | 0 | 0 | 0
2022041522 | 6 | 0.59203 | 47362.4 | 0 | 0 | 0.4026 | 14091 | 0 | 0 | 40000 | 0 | 7362.4 | 6728.6 | 0 | 0 | 6728.6 | 0 | 0 | 0 | 0
2022041523 | 6 | 0.56854 | 45483.2 | 0 | 0 | 0.43811 | 15333.85 | 0 | 0 | 40000 | 0 | 5483.2 | 9850.65 | 0 | 0 | 9850.65 | 0 | 0 | 0 | 0
2022041524 | 6 | 0.54267 | 43413.6 | 0 | 0 | 0.48831 | 17090.85 | 0 | 0 | 40000 | 0 | 3413.6 | 13677.25 | 0 | 0 | 13677.25 | 0 | 0 | 0 | 0
2022041601 | 7 | 0.5146 | 41168 | 0 | 0 | 0.52244 | 18285.4 | 0 | 0 | 40000 | 0 | 1168 | 17117.4 | 0 | 0 | 17117.4 | 0 | 0 | 0 | 0
2022041602 | 7 | 0.4961 | 39688 | 0 | 0 | 0.53782 | 18823.7 | 0 | 0 | 39688 | 312 | 0 | 18823.7 | 0 | 0 | 19135.7 | 0 | 0 | 0 | 0
2022041603 | 7 | 0.48134 | 38507.2 | 0 | 0 | 0.54122 | 18942.7 | 0 | 0 | 38507.2 | 1492.8 | 0 | 18942.7 | 0 | 0 | 20435.5 | 0 | 0 | 0 | 0
2022041604 | 7 | 0.47307 | 37845.6 | 0 | 0 | 0.51428 | 17999.8 | 0 | 0 | 37845.6 | 2154.4 | 0 | 17999.8 | 0 | 0 | 20154.2 | 0 | 0 | 0 | 0
2022041605 | 7 | 0.46893 | 37514.4 | 0 | 0 | 0.5074 | 17759 | 0 | 0 | 37514.4 | 2485.6 | 0 | 17759 | 0 | 0 | 20244.6 | 0 | 0 | 0 | 0
2022041606 | 7 | 0.47019 | 37615.2 | 0 | 0 | 0.48132 | 16846.2 | 0 | 0 | 37615.2 | 2384.8 | 0 | 16846.2 | 0 | 0 | 19231 | 0 | 0 | 0 | 0
2022041607 | 7 | 0.47464 | 37971.2 | 0 | 0 | 0.45623 | 15968.05 | 0 | 0 | 37971.2 | 2028.8 | 0 | 15968.05 | 0 | 0 | 17996.85 | 0 | 0 | 0 | 0
2022041608 | 7 | 0.48271 | 38616.8 | 0 | 0 | 0.46154 | 16153.9 | 0.02177 | 304.78 | 38616.8 | 1383.2 | 0 | 16153.9 | 0 | 304.78 | 17841.88 | 0 | 0 | 0 | 0
2022041609 | 7 | 0.50724 | 40579.2 | 0 | 0 | 0.43428 | 15199.8 | 0.25612 | 3585.68 | 40000 | 0 | 579.2 | 14620.6 | 0 | 3585.68 | 18206.28 | 0 | 0 | 0 | 0
2022041610 | 7 | 0.53615 | 42892 | 0 | 0 | 0.44333 | 15516.55 | 0.35149 | 4920.86 | 40000 | 0 | 2892 | 12624.55 | 0 | 4920.86 | 17545.41 | 0 | 0 | 0 | 0
2022041611 | 7 | 0.55521 | 44416.8 | 0 | 0 | 0.46289 | 16201.15 | 0.33048 | 4626.72 | 40000 | 0 | 4416.8 | 11784.35 | 0 | 4626.72 | 16411.07 | 0 | 0 | 0 | 0
2022041612 | 7 | 0.57103 | 45682.4 | 0 | 0 | 0.43666 | 15283.1 | 0.43012 | 6021.68 | 40000 | 0 | 5682.4 | 9600.7 | 0 | 6021.68 | 15622.38 | 0 | 0 | 0 | 0
2022041613 | 7 | 0.58216 | 46572.8 | 0 | 0 | 0.36514 | 12779.9 | 0.60072 | 8410.08 | 40000 | 0 | 6572.8 | 6207.1 | 0 | 8410.08 | 14617.18 | 0 | 0 | 0 | 0
2022041614 | 7 | 0.59281 | 47424.8 | 0 | 0 | 0.31225 | 10928.75 | 0.65465 | 9165.1 | 40000 | 0 | 7424.8 | 3503.95 | 0 | 9165.1 | 12669.05 | 0 | 0 | 0 | 0
2022041615 | 7 | 0.60028 | 48022.4 | 0 | 0 | 0.25194 | 8817.9 | 0.65467 | 9165.38 | 40000 | 0 | 8022.4 | 795.5 | 0 | 9165.38 | 9960.88 | 0 | 0 | 0 | 0
2022041616 | 7 | 0.60825 | 48660 | 0 | 0 | 0.19836 | 6942.6 | 0.64299 | 9001.86 | 40000 | 0 | 6942.6 | 0 | 1717.4 | 7284.46 | 7284.46 | 0 | 0 | 0 | 0
2022041617 | 7 | 0.61719 | 49375.2 | 0 | 0 | 0.18669 | 6534.15 | 0.59568 | 8339.52 | 40000 | 0 | 6534.15 | 0 | 2841.05 | 5498.47 | 5498.47 | 0 | 0 | 0 | 0
2022041618 | 7 | 0.6185 | 49480 | 0 | 0 | 0.17685 | 6189.75 | 0.47027 | 6583.78 | 40000 | 0 | 6189.75 | 0 | 3290.25 | 3293.53 | 3293.53 | 0 | 0 | 0 | 0
2022041619 | 7 | 0.60622 | 48497.6 | 0 | 0 | 0.18037 | 6312.95 | 0.35448 | 4962.72 | 40000 | 0 | 6312.95 | 0 | 2184.65 | 2778.07 | 2778.07 | 0 | 0 | 0 | 0
2022041620 | 7 | 0.58722 | 46977.6 | 0 | 0 | 0.19259 | 6740.65 | 0.08181 | 1145.34 | 40000 | 0 | 6740.65 | 0 | 236.95 | 908.39 | 908.39 | 0 | 0 | 0 | 0
2022041621 | 7 | 0.58486 | 46788.8 | 0 | 0 | 0.22326 | 7814.1 | 0.00233 | 32.62 | 40000 | 0 | 6788.8 | 1025.3 | 0 | 32.62 | 1057.92 | 0 | 0 | 0 | 0
2022041622 | 7 | 0.56843 | 45474.4 | 0 | 0 | 0.27007 | 9452.45 | 0 | 0 | 40000 | 0 | 5474.4 | 3978.05 | 0 | 0 | 3978.05 | 0 | 0 | 0 | 0
2022041623 | 7 | 0.54256 | 43404.8 | 0 | 0 | 0.28261 | 9891.35 | 0 | 0 | 40000 | 0 | 3404.8 | 6486.55 | 0 | 0 | 6486.55 | 0 | 0 | 0 | 0
2022041624 | 7 | 0.51298 | 41038.4 | 0 | 0 | 0.27396 | 9588.6 | 0 | 0 | 40000 | 0 | 1038.4 | 8550.2 | 0 | 0 | 8550.2 | 0 | 0 | 0 | 0
2022041701 | 1 | 0.48422 | 38737.6 | 0 | 0 | 0.2532 | 8862 | 0 | 0 | 38737.6 | 1262.4 | 0 | 8862 | 0 | 0 | 10124.4 | 0 | 0 | 0 | 0
2022041702 | 1 | 0.46115 | 36892 | 0 | 0 | 0.22729 | 7955.15 | 0 | 0 | 36892 | 3108 | 0 | 7955.15 | 0 | 0 | 11063.15 | 0 | 0 | 0 | 0
2022041703 | 1 | 0.44492 | 35593.6 | 0 | 0 | 0.1987 | 6954.5 | 0 | 0 | 35593.6 | 4406.4 | 0 | 6954.5 | 0 | 0 | 11360.9 | 0 | 0 | 0 | 0
2022041704 | 1 | 0.43497 | 34797.6 | 0 | 0 | 0.13076 | 4576.6 | 0 | 0 | 34797.6 | 5202.4 | 0 | 4576.6 | 0 | 0 | 9779 | 0 | 0 | 0 | 0
2022041705 | 1 | 0.4298 | 34384 | 0 | 0 | 0.10342 | 3619.7 | 0 | 0 | 34384 | 5616 | 0 | 3619.7 | 0 | 0 | 9235.7 | 0 | 0 | 0 | 0
2022041706 | 1 | 0.43062 | 34449.6 | 0 | 0 | 0.10155 | 3554.25 | 0 | 0 | 34449.6 | 5550.4 | 0 | 3554.25 | 0 | 0 | 9104.65 | 0 | 0 | 0 | 0
2022041707 | 1 | 0.43683 | 34946.4 | 0 | 0 | 0.08948 | 3131.8 | 0 | 0 | 34946.4 | 5053.6 | 0 | 3131.8 | 0 | 0 | 8185.4 | 0 | 0 | 0 | 0
2022041708 | 1 | 0.44412 | 35529.6 | 0 | 0 | 0.10064 | 3522.4 | 0.02689 | 376.46 | 35529.6 | 4470.4 | 0 | 3522.4 | 0 | 376.46 | 8369.26 | 0 | 0 | 0 | 0
2022041709 | 1 | 0.46462 | 37169.6 | 0 | 0 | 0.11115 | 3890.25 | 0.31627 | 4427.78 | 37169.6 | 2830.4 | 0 | 3890.25 | 0 | 4427.78 | 11148.43 | 0 | 0 | 0 | 0
2022041710 | 1 | 0.49176 | 39340.8 | 0 | 0 | 0.12061 | 4221.35 | 0.55957 | 7833.98 | 39340.8 | 659.2 | 0 | 4221.35 | 0 | 7833.98 | 12714.53 | 0 | 0 | 0 | 0
2022041711 | 1 | 0.51277 | 41021.6 | 0 | 0 | 0.13076 | 4576.6 | 0.63152 | 8841.28 | 40000 | 0 | 1021.6 | 3555 | 0 | 8841.28 | 12396.28 | 0 | 0 | 0 | 0
2022041712 | 1 | 0.53106 | 42484.8 | 0 | 0 | 0.18005 | 6301.75 | 0.68611 | 9605.54 | 40000 | 0 | 2484.8 | 3816.95 | 0 | 9605.54 | 13422.49 | 0 | 0 | 0 | 0
2022041713 | 1 | 0.55225 | 44180 | 0 | 0 | 0.23511 | 8228.85 | 0.72322 | 10125.08 | 40000 | 0 | 4180 | 4048.85 | 0 | 10125.08 | 14173.93 | 0 | 0 | 0 | 0
2022041714 | 1 | 0.56923 | 45538.4 | 0 | 0 | 0.25892 | 9062.2 | 0.71887 | 10064.18 | 40000 | 0 | 5538.4 | 3523.8 | 0 | 10064.18 | 13587.98 | 0 | 0 | 0 | 0
2022041715 | 1 | 0.58427 | 46741.6 | 0 | 0 | 0.2289 | 8011.5 | 0.73629 | 10308.06 | 40000 | 0 | 6741.6 | 1269.9 | 0 | 10308.06 | 11577.96 | 0 | 0 | 0 | 0
2022041716 | 1 | 0.59958 | 47966.4 | 0 | 0 | 0.19119 | 6691.65 | 0.76434 | 10700.76 | 40000 | 0 | 6691.65 | 0 | 1274.75 | 9426.01 | 9426.01 | 0 | 0 | 0 | 0
2022041717 | 1 | 0.61375 | 49100 | 0 | 0 | 0.1576 | 5516 | 0.74344 | 10408.16 | 40000 | 0 | 5516 | 0 | 3584 | 6824.16 | 6824.16 | 0 | 0 | 0 | 0
2022041718 | 1 | 0.62063 | 49650.4 | 0 | 0 | 0.13568 | 4748.8 | 0.72776 | 10188.64 | 40000 | 0 | 4748.8 | 0 | 4901.6 | 5287.04 | 5287.04 | 0 | 0 | 0 | 0
2022041719 | 1 | 0.61699 | 49359.2 | 0 | 0 | 0.12838 | 4493.3 | 0.5921 | 8289.4 | 40000 | 0 | 4493.3 | 0 | 4865.9 | 3423.5 | 3423.5 | 0 | 0 | 0 | 0
2022041720 | 1 | 0.60489 | 48391.2 | 0 | 0 | 0.15434 | 5401.9 | 0.20073 | 2810.22 | 40000 | 0 | 5401.9 | 0 | 2810.22 | 0 | 0 | 179.08 | 0 | 0 | 179.08
2022041721 | 1 | 0.60145 | 48116 | 0 | 0 | 0.22739 | 7958.65 | 0.00313 | 43.82 | 40000 | 0 | 7958.65 | 0 | 43.82 | 0 | 0 | 113.53 | 0 | 0 | 113.53
2022041722 | 1 | 0.58607 | 46885.6 | 0 | 0 | 0.32846 | 11496.1 | 0 | 0 | 40000 | 0 | 6885.6 | 4610.5 | 0 | 0 | 4610.5 | 0 | 0 | 0 | 0
2022041723 | 1 | 0.55497 | 44397.6 | 0 | 0 | 0.3833 | 13415.5 | 0 | 0 | 40000 | 0 | 4397.6 | 9017.9 | 0 | 0 | 9017.9 | 0 | 0 | 0 | 0
2022041724 | 1 | 0.5153 | 41224 | 0 | 0 | 0.40478 | 14167.3 | 0 | 0 | 40000 | 0 | 1224 | 12943.3 | 0 | 0 | 12943.3 | 0 | 0 | 0 | 0
2022041801 | 2 | 0.48133 | 38506.4 | 0 | 0 | 0.38788 | 13575.8 | 0 | 0 | 38506.4 | 1493.6 | 0 | 13575.8 | 0 | 0 | 15069.4 | 0 | 0 | 0 | 0
2022041802 | 2 | 0.45707 | 36565.6 | 0 | 0 | 0.35946 | 12581.1 | 0 | 0 | 36565.6 | 3434.4 | 0 | 12581.1 | 0 | 0 | 16015.5 | 0 | 0 | 0 | 0
2022041803 | 2 | 0.44205 | 35364 | 0 | 0 | 0.34013 | 11904.55 | 0 | 0 | 35364 | 4636 | 0 | 11904.55 | 0 | 0 | 16540.55 | 0 | 0 | 0 | 0
2022041804 | 2 | 0.42754 | 34203.2 | 0 | 0 | 0.31312 | 10959.2 | 0 | 0 | 34203.2 | 5796.8 | 0 | 10959.2 | 0 | 0 | 16756 | 0 | 0 | 0 | 0
2022041805 | 2 | 0.43102 | 34481.6 | 0 | 0 | 0.29425 | 10298.75 | 0 | 0 | 34481.6 | 5518.4 | 0 | 10298.75 | 0 | 0 | 15817.15 | 0 | 0 | 0 | 0
2022041806 | 2 | 0.44711 | 35768.8 | 0 | 0 | 0.30741 | 10759.35 | 0 | 0 | 35768.8 | 4231.2 | 0 | 10759.35 | 0 | 0 | 14990.55 | 0 | 0 | 0 | 0
2022041807 | 2 | 0.47104 | 37683.2 | 0 | 0 | 0.30846 | 10796.1 | 0 | 0 | 37683.2 | 2316.8 | 0 | 10796.1 | 0 | 0 | 13112.9 | 0 | 0 | 0 | 0
2022041808 | 2 | 0.48324 | 38659.2 | 0 | 0 | 0.34361 | 12026.35 | 0.03922 | 549.08 | 38659.2 | 1340.8 | 0 | 12026.35 | 0 | 549.08 | 13916.23 | 0 | 0 | 0 | 0
2022041809 | 2 | 0.49741 | 39792.8 | 0 | 0 | 0.32423 | 11348.05 | 0.36327 | 5085.78 | 39792.8 | 207.2 | 0 | 11348.05 | 0 | 5085.78 | 16641.03 | 0 | 0 | 0 | 0
2022041810 | 2 | 0.51466 | 41172.8 | 0 | 0 | 0.37962 | 13286.7 | 0.58018 | 8122.52 | 40000 | 0 | 1172.8 | 12113.9 | 0 | 8122.52 | 20236.42 | 0 | 0 | 0 | 0
2022041811 | 2 | 0.5293 | 42344 | 0 | 0 | 0.38619 | 13516.65 | 0.64754 | 9065.56 | 40000 | 0 | 2344 | 11172.65 | 0 | 9065.56 | 20238.21 | 0 | 0 | 0 | 0
2022041812 | 2 | 0.54197 | 43357.6 | 0 | 0 | 0.36417 | 12745.95 | 0.70656 | 9891.84 | 40000 | 0 | 3357.6 | 9388.35 | 0 | 9891.84 | 19280.19 | 0 | 0 | 0 | 0
2022041813 | 2 | 0.55567 | 44453.6 | 0 | 0 | 0.34922 | 12222.7 | 0.76065 | 10649.1 | 40000 | 0 | 4453.6 | 7769.1 | 0 | 10649.1 | 18418.2 | 0 | 0 | 0 | 0
2022041814 | 2 | 0.56999 | 45599.2 | 0 | 0 | 0.34147 | 11951.45 | 0.79307 | 11102.98 | 40000 | 0 | 5599.2 | 6352.25 | 0 | 11102.98 | 17455.23 | 0 | 0 | 0 | 0
2022041815 | 2 | 0.58587 | 46869.6 | 0 | 0 | 0.34337 | 12017.95 | 0.79278 | 11098.92 | 40000 | 0 | 6869.6 | 5148.35 | 0 | 11098.92 | 16247.27 | 0 | 0 | 0 | 0
2022041816 | 2 | 0.60241 | 48192.8 | 0 | 0 | 0.34402 | 12040.7 | 0.79954 | 11193.56 | 40000 | 0 | 8192.8 | 3847.9 | 0 | 11193.56 | 15041.46 | 0 | 0 | 0 | 0
2022041817 | 2 | 0.6158 | 49264 | 0 | 0 | 0.36006 | 12602.1 | 0.77071 | 10789.94 | 40000 | 0 | 9264 | 3338.1 | 0 | 10789.94 | 14128.04 | 0 | 0 | 0 | 0
2022041818 | 2 | 0.62032 | 49625.6 | 0 | 0 | 0.39271 | 13744.85 | 0.70748 | 9904.72 | 40000 | 0 | 9625.6 | 4119.25 | 0 | 9904.72 | 14023.97 | 0 | 0 | 0 | 0
2022041819 | 2 | 0.61155 | 48924 | 0 | 0 | 0.44043 | 15415.05 | 0.53146 | 7440.44 | 40000 | 0 | 8924 | 6491.05 | 0 | 7440.44 | 13931.49 | 0 | 0 | 0 | 0
2022041820 | 2 | 0.59338 | 47470.4 | 0 | 0 | 0.45165 | 15807.75 | 0.16814 | 2353.96 | 40000 | 0 | 7470.4 | 8337.35 | 0 | 2353.96 | 10691.31 | 0 | 0 | 0 | 0
2022041821 | 2 | 0.58854 | 47083.2 | 0 | 0 | 0.44658 | 15630.3 | 0.02606 | 364.84 | 40000 | 0 | 7083.2 | 8547.1 | 0 | 364.84 | 8911.94 | 0 | 0 | 0 | 0
2022041822 | 2 | 0.56723 | 45378.4 | 0 | 0 | 0.49277 | 17246.95 | 0.02406 | 336.84 | 40000 | 0 | 5378.4 | 11868.55 | 0 | 336.84 | 12205.39 | 0 | 0 | 0 | 0
2022041823 | 2 | 0.52924 | 42339.2 | 0 | 0 | 0.51566 | 18048.1 | 0.02406 | 336.84 | 40000 | 0 | 2339.2 | 15708.9 | 0 | 336.84 | 16045.74 | 0 | 0 | 0 | 0
2022041824 | 2 | 0.48706 | 38964.8 | 0 | 0 | 0.53677 | 18786.95 | 0.01067 | 149.38 | 38964.8 | 1035.2 | 0 | 18786.95 | 0 | 149.38 | 19971.53 | 0 | 0 | 0 | 0
2022041901 | 3 | 0.45495 | 36396 | 0 | 0 | 0.5599 | 19596.5 | 0 | 0 | 36396 | 3604 | 0 | 19596.5 | 0 | 0 | 23200.5 | 0 | 0 | 0 | 0
2022041902 | 3 | 0.43428 | 34742.4 | 0 | 0 | 0.55957 | 19584.95 | 0 | 0 | 34742.4 | 5257.6 | 0 | 19584.95 | 0 | 0 | 24842.55 | 0 | 0 | 0 | 0
2022041903 | 3 | 0.4224 | 33792 | 0 | 0 | 0.53046 | 18566.1 | 0 | 0 | 33792 | 6208 | 0 | 18566.1 | 0 | 0 | 24774.1 | 0 | 0 | 0 | 0
2022041904 | 3 | 0.4169 | 33352 | 0 | 0 | 0.51283 | 17949.05 | 0 | 0 | 33352 | 6648 | 0 | 17949.05 | 0 | 0 | 24597.05 | 0 | 0 | 0 | 0
2022041905 | 3 | 0.42034 | 33627.2 | 0 | 0 | 0.49451 | 17307.85 | 0 | 0 | 33627.2 | 6372.8 | 0 | 17307.85 | 0 | 0 | 23680.65 | 0 | 0 | 0 | 0
2022041906 | 3 | 0.43874 | 35099.2 | 0 | 0 | 0.50022 | 17507.7 | 0 | 0 | 35099.2 | 4900.8 | 0 | 17507.7 | 0 | 0 | 22408.5 | 0 | 0 | 0 | 0
2022041907 | 3 | 0.47339 | 37871.2 | 0 | 0 | 0.51244 | 17935.4 | 5e-05 | 0.7 | 37871.2 | 2128.8 | 0 | 17935.4 | 0 | 0.7 | 20064.9 | 0 | 0 | 0 | 0
2022041908 | 3 | 0.48896 | 39116.8 | 0 | 0 | 0.52865 | 18502.75 | 0.0231 | 323.4 | 39116.8 | 883.2 | 0 | 18502.75 | 0 | 323.4 | 19709.35 | 0 | 0 | 0 | 0
2022041909 | 3 | 0.4944 | 39552 | 0 | 0 | 0.5332 | 18662 | 0.14809 | 2073.26 | 39552 | 448 | 0 | 18662 | 0 | 2073.26 | 21183.26 | 0 | 0 | 0 | 0
2022041910 | 3 | 0.50433 | 40346.4 | 0 | 0 | 0.56064 | 19622.4 | 0.22504 | 3150.56 | 40000 | 0 | 346.4 | 19276 | 0 | 3150.56 | 22426.56 | 0 | 0 | 0 | 0
2022041911 | 3 | 0.51414 | 41131.2 | 0 | 0 | 0.57464 | 20112.4 | 0.21549 | 3016.86 | 40000 | 0 | 1131.2 | 18981.2 | 0 | 3016.86 | 21998.06 | 0 | 0 | 0 | 0
2022041912 | 3 | 0.52542 | 42033.6 | 0 | 0 | 0.5841 | 20443.5 | 0.25702 | 3598.28 | 40000 | 0 | 2033.6 | 18409.9 | 0 | 3598.28 | 22008.18 | 0 | 0 | 0 | 0
2022041913 | 3 | 0.53416 | 42732.8 | 0 | 0 | 0.60039 | 21013.65 | 0.27055 | 3787.7 | 40000 | 0 | 2732.8 | 18280.85 | 0 | 3787.7 | 22068.55 | 0 | 0 | 0 | 0
2022041914 | 3 | 0.54396 | 43516.8 | 0 | 0 | 0.60872 | 21305.2 | 0.26508 | 3711.12 | 40000 | 0 | 3516.8 | 17788.4 | 0 | 3711.12 | 21499.52 | 0 | 0 | 0 | 0
2022041915 | 3 | 0.5527 | 44216 | 0 | 0 | 0.62699 | 21944.65 | 0.25486 | 3568.04 | 40000 | 0 | 4216 | 17728.65 | 0 | 3568.04 | 21296.69 | 0 | 0 | 0 | 0
2022041916 | 3 | 0.55541 | 44432.8 | 0 | 0 | 0.62851 | 21997.85 | 0.22702 | 3178.28 | 40000 | 0 | 4432.8 | 17565.05 | 0 | 3178.28 | 20743.33 | 0 | 0 | 0 | 0
2022041917 | 3 | 0.55992 | 44793.6 | 0 | 0 | 0.63212 | 22124.2 | 0.18152 | 2541.28 | 40000 | 0 | 4793.6 | 17330.6 | 0 | 2541.28 | 19871.88 | 0 | 0 | 0 | 0
2022041918 | 3 | 0.56024 | 44819.2 | 0 | 0 | 0.63807 | 22332.45 | 0.12282 | 1719.48 | 40000 | 0 | 4819.2 | 17513.25 | 0 | 1719.48 | 19232.73 | 0 | 0 | 0 | 0
2022041919 | 3 | 0.55759 | 44607.2 | 0 | 0 | 0.6494 | 22729 | 0.0538 | 753.2 | 40000 | 0 | 4607.2 | 18121.8 | 0 | 753.2 | 18875 | 0 | 0 | 0 | 0
2022041920 | 3 | 0.55761 | 44608.8 | 0 | 0 | 0.65595 | 22958.25 | 0.01687 | 236.18 | 40000 | 0 | 4608.8 | 18349.45 | 0 | 236.18 | 18585.63 | 0 | 0 | 0 | 0
2022041921 | 3 | 0.56444 | 45155.2 | 0 | 0 | 0.65959 | 23085.65 | 0.00045 | 6.3 | 40000 | 0 | 5155.2 | 17930.45 | 0 | 6.3 | 17936.75 | 0 | 0 | 0 | 0
2022041922 | 3 | 0.552 | 44160 | 0 | 0 | 0.65283 | 22849.05 | 0 | 0 | 40000 | 0 | 4160 | 18689.05 | 0 | 0 | 18689.05 | 0 | 0 | 0 | 0
2022041923 | 3 | 0.52584 | 42067.2 | 0 | 0 | 0.64631 | 22620.85 | 0 | 0 | 40000 | 0 | 2067.2 | 20553.65 | 0 | 0 | 20553.65 | 0 | 0 | 0 | 0
2022041924 | 3 | 0.49288 | 39430.4 | 0 | 0 | 0.63975 | 22391.25 | 0 | 0 | 39430.4 | 569.6 | 0 | 22391.25 | 0 | 0 | 22960.85 | 0 | 0 | 0 | 0
2022042001 | 4 | 0.46807 | 37445.6 | 0 | 0 | 0.63995 | 22398.25 | 0 | 0 | 37445.6 | 2554.4 | 0 | 22398.25 | 0 | 0 | 24952.65 | 0 | 0 | 0 | 0
2022042002 | 4 | 0.45414 | 36331.2 | 0 | 0 | 0.63938 | 22378.3 | 0 | 0 | 36331.2 | 3668.8 | 0 | 22378.3 | 0 | 0 | 26047.1 | 0 | 0 | 0 | 0
2022042003 | 4 | 0.44621 | 35696.8 | 0 | 0 | 0.63884 | 22359.4 | 0 | 0 | 35696.8 | 4303.2 | 0 | 22359.4 | 0 | 0 | 26662.6 | 0 | 0 | 0 | 0
2022042004 | 4 | 0.44213 | 35370.4 | 0 | 0 | 0.6302 | 22057 | 0 | 0 | 35370.4 | 4629.6 | 0 | 22057 | 0 | 0 | 26686.6 | 0 | 0 | 0 | 0
2022042005 | 4 | 0.44761 | 35808.8 | 0 | 0 | 0.62316 | 21810.6 | 0 | 0 | 35808.8 | 4191.2 | 0 | 21810.6 | 0 | 0 | 26001.8 | 0 | 0 | 0 | 0
2022042006 | 4 | 0.46847 | 37477.6 | 0 | 0 | 0.63008 | 22052.8 | 0 | 0 | 37477.6 | 2522.4 | 0 | 22052.8 | 0 | 0 | 24575.2 | 0 | 0 | 0 | 0
2022042007 | 4 | 0.50066 | 40052.8 | 0 | 0 | 0.61555 | 21544.25 | 0 | 0 | 40000 | 0 | 52.8 | 21491.45 | 0 | 0 | 21491.45 | 0 | 0 | 0 | 0
2022042008 | 4 | 0.52153 | 41722.4 | 0 | 0 | 0.61079 | 21377.65 | 0.0147 | 205.8 | 40000 | 0 | 1722.4 | 19655.25 | 0 | 205.8 | 19861.05 | 0 | 0 | 0 | 0
2022042009 | 4 | 0.52954 | 42363.2 | 0 | 0 | 0.56788 | 19875.8 | 0.12274 | 1718.36 | 40000 | 0 | 2363.2 | 17512.6 | 0 | 1718.36 | 19230.96 | 0 | 0 | 0 | 0
2022042010 | 4 | 0.54534 | 43627.2 | 0 | 0 | 0.57409 | 20093.15 | 0.19102 | 2674.28 | 40000 | 0 | 3627.2 | 16465.95 | 0 | 2674.28 | 19140.23 | 0 | 0 | 0 | 0
2022042011 | 4 | 0.5633 | 45064 | 0 | 0 | 0.5731 | 20058.5 | 0.2467 | 3453.8 | 40000 | 0 | 5064 | 14994.5 | 0 | 3453.8 | 18448.3 | 0 | 0 | 0 | 0
2022042012 | 4 | 0.58073 | 46458.4 | 0 | 0 | 0.56756 | 19864.6 | 0.2914 | 4079.6 | 40000 | 0 | 6458.4 | 13406.2 | 0 | 4079.6 | 17485.8 | 0 | 0 | 0 | 0
2022042013 | 4 | 0.59853 | 47882.4 | 0 | 0 | 0.51763 | 18117.05 | 0.46578 | 6520.92 | 40000 | 0 | 7882.4 | 10234.65 | 0 | 6520.92 | 16755.57 | 0 | 0 | 0 | 0
2022042014 | 4 | 0.61931 | 49544.8 | 0 | 0 | 0.46332 | 16216.2 | 0.64562 | 9038.68 | 40000 | 0 | 9544.8 | 6671.4 | 0 | 9038.68 | 15710.08 | 0 | 0 | 0 | 0
2022042015 | 4 | 0.64035 | 51228 | 0 | 0 | 0.41455 | 14509.25 | 0.68314 | 9563.96 | 40000 | 0 | 11228 | 3281.25 | 0 | 9563.96 | 12845.21 | 0 | 0 | 0 | 0
2022042016 | 4 | 0.65694 | 52555.2 | 0 | 0 | 0.38631 | 13520.85 | 0.66335 | 9286.9 | 40000 | 0 | 12555.2 | 965.65 | 0 | 9286.9 | 10252.55 | 0 | 0 | 0 | 0
2022042017 | 4 | 0.67458 | 53966.4 | 0 | 0 | 0.37462 | 13111.7 | 0.66565 | 9319.1 | 40000 | 0 | 13111.7 | 0 | 854.7 | 8464.4 | 8464.4 | 0 | 0 | 0 | 0
2022042018 | 4 | 0.68436 | 54748.8 | 0 | 0 | 0.36798 | 12879.3 | 0.62806 | 8792.84 | 40000 | 0 | 12879.3 | 0 | 1869.5 | 6923.34 | 6923.34 | 0 | 0 | 0 | 0
2022042019 | 4 | 0.67693 | 54154.4 | 0 | 0 | 0.36158 | 12655.3 | 0.51112 | 7155.68 | 40000 | 0 | 12655.3 | 0 | 1499.1 | 5656.58 | 5656.58 | 0 | 0 | 0 | 0
2022042020 | 4 | 0.65979 | 52783.2 | 0 | 0 | 0.34181 | 11963.35 | 0.20078 | 2810.92 | 40000 | 0 | 11963.35 | 0 | 819.85 | 1991.07 | 1991.07 | 0 | 0 | 0 | 0
2022042021 | 4 | 0.65325 | 52260 | 0 | 0 | 0.35509 | 12428.15 | 0.00388 | 54.32 | 40000 | 0 | 12260 | 168.15 | 0 | 54.32 | 222.47 | 0 | 0 | 0 | 0
2022042022 | 4 | 0.63777 | 51021.6 | 0 | 0 | 0.4369 | 15291.5 | 0 | 0 | 40000 | 0 | 11021.6 | 4269.9 | 0 | 0 | 4269.9 | 0 | 0 | 0 | 0
2022042023 | 4 | 0.60165 | 48132 | 0 | 0 | 0.55141 | 19299.35 | 0 | 0 | 40000 | 0 | 8132 | 11167.35 | 0 | 0 | 11167.35 | 0 | 0 | 0 | 0
2022042024 | 4 | 0.56323 | 45058.4 | 0 | 0 | 0.61895 | 21663.25 | 0 | 0 | 40000 | 0 | 5058.4 | 16604.85 | 0 | 0 | 16604.85 | 0 | 0 | 0 | 0
2022042101 | 5 | 0.52705 | 42164 | 0 | 0 | 0.62633 | 21921.55 | 0 | 0 | 40000 | 0 | 2164 | 19757.55 | 0 | 0 | 19757.55 | 0 | 0 | 0 | 0
2022042102 | 5 | 0.50393 | 40314.4 | 0 | 0 | 0.62681 | 21938.35 | 0 | 0 | 40000 | 0 | 314.4 | 21623.95 | 0 | 0 | 21623.95 | 0 | 0 | 0 | 0
2022042103 | 5 | 0.48812 | 39049.6 | 0 | 0 | 0.61748 | 21611.8 | 0 | 0 | 39049.6 | 950.4 | 0 | 21611.8 | 0 | 0 | 22562.2 | 0 | 0 | 0 | 0
2022042104 | 5 | 0.48181 | 38544.8 | 0 | 0 | 0.61068 | 21373.8 | 0 | 0 | 38544.8 | 1455.2 | 0 | 21373.8 | 0 | 0 | 22829 | 0 | 0 | 0 | 0
2022042105 | 5 | 0.48425 | 38740 | 0 | 0 | 0.60381 | 21133.35 | 0 | 0 | 38740 | 1260 | 0 | 21133.35 | 0 | 0 | 22393.35 | 0 | 0 | 0 | 0
2022042106 | 5 | 0.50286 | 40228.8 | 0 | 0 | 0.60649 | 21227.15 | 0 | 0 | 40000 | 0 | 228.8 | 20998.35 | 0 | 0 | 20998.35 | 0 | 0 | 0 | 0
2022042107 | 5 | 0.5341 | 42728 | 0 | 0 | 0.60613 | 21214.55 | 0 | 0 | 40000 | 0 | 2728 | 18486.55 | 0 | 0 | 18486.55 | 0 | 0 | 0 | 0
2022042108 | 5 | 0.55043 | 44034.4 | 0 | 0 | 0.57901 | 20265.35 | 0.03359 | 470.26 | 40000 | 0 | 4034.4 | 16230.95 | 0 | 470.26 | 16701.21 | 0 | 0 | 0 | 0
2022042109 | 5 | 0.5611 | 44888 | 0 | 0 | 0.55709 | 19498.15 | 0.26442 | 3701.88 | 40000 | 0 | 4888 | 14610.15 | 0 | 3701.88 | 18312.03 | 0 | 0 | 0 | 0
2022042110 | 5 | 0.57825 | 46260 | 0 | 0 | 0.56436 | 19752.6 | 0.29511 | 4131.54 | 40000 | 0 | 6260 | 13492.6 | 0 | 4131.54 | 17624.14 | 0 | 0 | 0 | 0
2022042111 | 5 | 0.59961 | 47968.8 | 0 | 0 | 0.55066 | 19273.1 | 0.40531 | 5674.34 | 40000 | 0 | 7968.8 | 11304.3 | 0 | 5674.34 | 16978.64 | 0 | 0 | 0 | 0
2022042112 | 5 | 0.61759 | 49407.2 | 0 | 0 | 0.5201 | 18203.5 | 0.54682 | 7655.48 | 40000 | 0 | 9407.2 | 8796.3 | 0 | 7655.48 | 16451.78 | 0 | 0 | 0 | 0
2022042113 | 5 | 0.63524 | 50819.2 | 0 | 0 | 0.48123 | 16843.05 | 0.69198 | 9687.72 | 40000 | 0 | 10819.2 | 6023.85 | 0 | 9687.72 | 15711.57 | 0 | 0 | 0 | 0
2022042114 | 5 | 0.65501 | 52400.8 | 0 | 0 | 0.44329 | 15515.15 | 0.71845 | 10058.3 | 40000 | 0 | 12400.8 | 3114.35 | 0 | 10058.3 | 13172.65 | 0 | 0 | 0 | 0
2022042115 | 5 | 0.67376 | 53900.8 | 0 | 0 | 0.45286 | 15850.1 | 0.72608 | 10165.12 | 40000 | 0 | 13900.8 | 1949.3 | 0 | 10165.12 | 12114.42 | 0 | 0 | 0 | 0
2022042116 | 5 | 0.68818 | 55054.4 | 0 | 0 | 0.50049 | 17517.15 | 0.68059 | 9528.26 | 40000 | 0 | 15054.4 | 2462.75 | 0 | 9528.26 | 11991.01 | 0 | 0 | 0 | 0
2022042117 | 5 | 0.69792 | 55833.6 | 0 | 0 | 0.55099 | 19284.65 | 0.56734 | 7942.76 | 40000 | 0 | 15833.6 | 3451.05 | 0 | 7942.76 | 11393.81 | 0 | 0 | 0 | 0
2022042118 | 5 | 0.69434 | 55547.2 | 0 | 0 | 0.60428 | 21149.8 | 0.37943 | 5312.02 | 40000 | 0 | 15547.2 | 5602.6 | 0 | 5312.02 | 10914.62 | 0 | 0 | 0 | 0
2022042119 | 5 | 0.68008 | 54406.4 | 0 | 0 | 0.63368 | 22178.8 | 0.25172 | 3524.08 | 40000 | 0 | 14406.4 | 7772.4 | 0 | 3524.08 | 11296.48 | 0 | 0 | 0 | 0
2022042120 | 5 | 0.66666 | 53332.8 | 0 | 0 | 0.65365 | 22877.75 | 0.0832 | 1164.8 | 40000 | 0 | 13332.8 | 9544.95 | 0 | 1164.8 | 10709.75 | 0 | 0 | 0 | 0
2022042121 | 5 | 0.66539 | 53231.2 | 0 | 0 | 0.67283 | 23549.05 | 0.00309 | 43.26 | 40000 | 0 | 13231.2 | 10317.85 | 0 | 43.26 | 10361.11 | 0 | 0 | 0 | 0
2022042122 | 5 | 0.64652 | 51721.6 | 0 | 0 | 0.67739 | 23708.65 | 0 | 0 | 40000 | 0 | 11721.6 | 11987.05 | 0 | 0 | 11987.05 | 0 | 0 | 0 | 0
2022042123 | 5 | 0.6108 | 48864 | 0 | 0 | 0.66438 | 23253.3 | 0 | 0 | 40000 | 0 | 8864 | 14389.3 | 0 | 0 | 14389.3 | 0 | 0 | 0 | 0
2022042124 | 5 | 0.56978 | 45582.4 | 0 | 0 | 0.65282 | 22848.7 | 0 | 0 | 40000 | 0 | 5582.4 | 17266.3 | 0 | 0 | 17266.3 | 0 | 0 | 0 | 0
2022042201 | 6 | 0.5343 | 42744 | 0 | 0 | 0.66151 | 23152.85 | 0 | 0 | 40000 | 0 | 2744 | 20408.85 | 0 | 0 | 20408.85 | 0 | 0 | 0 | 0
2022042202 | 6 | 0.51024 | 40819.2 | 0 | 0 | 0.66079 | 23127.65 | 0 | 0 | 40000 | 0 | 819.2 | 22308.45 | 0 | 0 | 22308.45 | 0 | 0 | 0 | 0
2022042203 | 6 | 0.49349 | 39479.2 | 0 | 0 | 0.65722 | 23002.7 | 0 | 0 | 39479.2 | 520.8 | 0 | 23002.7 | 0 | 0 | 23523.5 | 0 | 0 | 0 | 0
2022042204 | 6 | 0.48467 | 38773.6 | 0 | 0 | 0.6531 | 22858.5 | 0 | 0 | 38773.6 | 1226.4 | 0 | 22858.5 | 0 | 0 | 24084.9 | 0 | 0 | 0 | 0
2022042205 | 6 | 0.48796 | 39036.8 | 0 | 0 | 0.64903 | 22716.05 | 0 | 0 | 39036.8 | 963.2 | 0 | 22716.05 | 0 | 0 | 23679.25 | 0 | 0 | 0 | 0
2022042206 | 6 | 0.50493 | 40394.4 | 0 | 0 | 0.64857 | 22699.95 | 0 | 0 | 40000 | 0 | 394.4 | 22305.55 | 0 | 0 | 22305.55 | 0 | 0 | 0 | 0
2022042207 | 6 | 0.53761 | 43008.8 | 0 | 0 | 0.65263 | 22842.05 | 0 | 0 | 40000 | 0 | 3008.8 | 19833.25 | 0 | 0 | 19833.25 | 0 | 0 | 0 | 0
2022042208 | 6 | 0.54586 | 43668.8 | 0 | 0 | 0.66088 | 23130.8 | 0.0202 | 282.8 | 40000 | 0 | 3668.8 | 19462 | 0 | 282.8 | 19744.8 | 0 | 0 | 0 | 0
2022042209 | 6 | 0.55984 | 44787.2 | 0 | 0 | 0.66054 | 23118.9 | 0.10855 | 1519.7 | 40000 | 0 | 4787.2 | 18331.7 | 0 | 1519.7 | 19851.4 | 0 | 0 | 0 | 0
2022042210 | 6 | 0.58207 | 46565.6 | 0 | 0 | 0.65942 | 23079.7 | 0.14931 | 2090.34 | 40000 | 0 | 6565.6 | 16514.1 | 0 | 2090.34 | 18604.44 | 0 | 0 | 0 | 0
2022042211 | 6 | 0.60236 | 48188.8 | 0 | 0 | 0.66108 | 23137.8 | 0.16123 | 2257.22 | 40000 | 0 | 8188.8 | 14949 | 0 | 2257.22 | 17206.22 | 0 | 0 | 0 | 0
2022042212 | 6 | 0.62177 | 49741.6 | 0 | 0 | 0.67055 | 23469.25 | 0.15268 | 2137.52 | 40000 | 0 | 9741.6 | 13727.65 | 0 | 2137.52 | 15865.17 | 0 | 0 | 0 | 0
2022042213 | 6 | 0.64236 | 51388.8 | 0 | 0 | 0.67151 | 23502.85 | 0.18021 | 2522.94 | 40000 | 0 | 11388.8 | 12114.05 | 0 | 2522.94 | 14636.99 | 0 | 0 | 0 | 0
2022042214 | 6 | 0.66259 | 53007.2 | 0 | 0 | 0.6716 | 23506 | 0.19259 | 2696.26 | 40000 | 0 | 13007.2 | 10498.8 | 0 | 2696.26 | 13195.06 | 0 | 0 | 0 | 0
2022042215 | 6 | 0.6744 | 53952 | 0 | 0 | 0.66069 | 23124.15 | 0.2019 | 2826.6 | 40000 | 0 | 13952 | 9172.15 | 0 | 2826.6 | 11998.75 | 0 | 0 | 0 | 0
2022042216 | 6 | 0.68796 | 55036.8 | 0 | 0 | 0.6509 | 22781.5 | 0.22662 | 3172.68 | 40000 | 0 | 15036.8 | 7744.7 | 0 | 3172.68 | 10917.38 | 0 | 0 | 0 | 0
2022042217 | 6 | 0.70089 | 56071.2 | 0 | 0 | 0.64922 | 22722.7 | 0.2437 | 3411.8 | 40000 | 0 | 16071.2 | 6651.5 | 0 | 3411.8 | 10063.3 | 0 | 0 | 0 | 0
2022042218 | 6 | 0.70278 | 56222.4 | 0 | 0 | 0.65256 | 22839.6 | 0.24629 | 3448.06 | 40000 | 0 | 16222.4 | 6617.2 | 0 | 3448.06 | 10065.26 | 0 | 0 | 0 | 0
2022042219 | 6 | 0.67991 | 54392.8 | 0 | 0 | 0.65496 | 22923.6 | 0.19113 | 2675.82 | 40000 | 0 | 14392.8 | 8530.8 | 0 | 2675.82 | 11206.62 | 0 | 0 | 0 | 0
2022042220 | 6 | 0.65213 | 52170.4 | 0 | 0 | 0.65377 | 22881.95 | 0.07744 | 1084.16 | 40000 | 0 | 12170.4 | 10711.55 | 0 | 1084.16 | 11795.71 | 0 | 0 | 0 | 0
2022042221 | 6 | 0.64111 | 51288.8 | 0 | 0 | 0.67458 | 23610.3 | 0.00248 | 34.72 | 40000 | 0 | 11288.8 | 12321.5 | 0 | 34.72 | 12356.22 | 0 | 0 | 0 | 0
2022042222 | 6 | 0.62012 | 49609.6 | 0 | 0 | 0.67075 | 23476.25 | 0 | 0 | 40000 | 0 | 9609.6 | 13866.65 | 0 | 0 | 13866.65 | 0 | 0 | 0 | 0
2022042223 | 6 | 0.58937 | 47149.6 | 0 | 0 | 0.67206 | 23522.1 | 0 | 0 | 40000 | 0 | 7149.6 | 16372.5 | 0 | 0 | 16372.5 | 0 | 0 | 0 | 0
2022042224 | 6 | 0.55442 | 44353.6 | 0 | 0 | 0.66775 | 23371.25 | 0 | 0 | 40000 | 0 | 4353.6 | 19017.65 | 0 | 0 | 19017.65 | 0 | 0 | 0 | 0
2022042301 | 7 | 0.52368 | 41894.4 | 0 | 0 | 0.66743 | 23360.05 | 0 | 0 | 40000 | 0 | 1894.4 | 21465.65 | 0 | 0 | 21465.65 | 0 | 0 | 0 | 0
2022042302 | 7 | 0.49912 | 39929.6 | 0 | 0 | 0.66199 | 23169.65 | 0 | 0 | 39929.6 | 70.4 | 0 | 23169.65 | 0 | 0 | 23240.05 | 0 | 0 | 0 | 0
2022042303 | 7 | 0.48001 | 38400.8 | 0 | 0 | 0.65674 | 22985.9 | 0 | 0 | 38400.8 | 1599.2 | 0 | 22985.9 | 0 | 0 | 24585.1 | 0 | 0 | 0 | 0
2022042304 | 7 | 0.47106 | 37684.8 | 0 | 0 | 0.65598 | 22959.3 | 0 | 0 | 37684.8 | 2315.2 | 0 | 22959.3 | 0 | 0 | 25274.5 | 0 | 0 | 0 | 0
2022042305 | 7 | 0.4646 | 37168 | 0 | 0 | 0.64846 | 22696.1 | 0 | 0 | 37168 | 2832 | 0 | 22696.1 | 0 | 0 | 25528.1 | 0 | 0 | 0 | 0
2022042306 | 7 | 0.46648 | 37318.4 | 0 | 0 | 0.64634 | 22621.9 | 0 | 0 | 37318.4 | 2681.6 | 0 | 22621.9 | 0 | 0 | 25303.5 | 0 | 0 | 0 | 0
2022042307 | 7 | 0.47508 | 38006.4 | 0 | 0 | 0.64317 | 22510.95 | 5e-05 | 0.7 | 38006.4 | 1993.6 | 0 | 22510.95 | 0 | 0.7 | 24505.25 | 0 | 0 | 0 | 0
2022042308 | 7 | 0.48617 | 38893.6 | 0 | 0 | 0.64795 | 22678.25 | 0.02642 | 369.88 | 38893.6 | 1106.4 | 0 | 22678.25 | 0 | 369.88 | 24154.53 | 0 | 0 | 0 | 0
2022042309 | 7 | 0.51057 | 40845.6 | 0 | 0 | 0.6362 | 22267 | 0.13377 | 1872.78 | 40000 | 0 | 845.6 | 21421.4 | 0 | 1872.78 | 23294.18 | 0 | 0 | 0 | 0
2022042310 | 7 | 0.53688 | 42950.4 | 0 | 0 | 0.62986 | 22045.1 | 0.19811 | 2773.54 | 40000 | 0 | 2950.4 | 19094.7 | 0 | 2773.54 | 21868.24 | 0 | 0 | 0 | 0
2022042311 | 7 | 0.56285 | 45028 | 0 | 0 | 0.61328 | 21464.8 | 0.31014 | 4341.96 | 40000 | 0 | 5028 | 16436.8 | 0 | 4341.96 | 20778.76 | 0 | 0 | 0 | 0
2022042312 | 7 | 0.5854 | 46832 | 0 | 0 | 0.58867 | 20603.45 | 0.40415 | 5658.1 | 40000 | 0 | 6832 | 13771.45 | 0 | 5658.1 | 19429.55 | 0 | 0 | 0 | 0
2022042313 | 7 | 0.60171 | 48136.8 | 0 | 0 | 0.55866 | 19553.1 | 0.51418 | 7198.52 | 40000 | 0 | 8136.8 | 11416.3 | 0 | 7198.52 | 18614.82 | 0 | 0 | 0 | 0
2022042314 | 7 | 0.61811 | 49448.8 | 0 | 0 | 0.53433 | 18701.55 | 0.60924 | 8529.36 | 40000 | 0 | 9448.8 | 9252.75 | 0 | 8529.36 | 17782.11 | 0 | 0 | 0 | 0
2022042315 | 7 | 0.63256 | 50604.8 | 0 | 0 | 0.53921 | 18872.35 | 0.60786 | 8510.04 | 40000 | 0 | 10604.8 | 8267.55 | 0 | 8510.04 | 16777.59 | 0 | 0 | 0 | 0
2022042316 | 7 | 0.64585 | 51668 | 0 | 0 | 0.56636 | 19822.6 | 0.52048 | 7286.72 | 40000 | 0 | 11668 | 8154.6 | 0 | 7286.72 | 15441.32 | 0 | 0 | 0 | 0
2022042317 | 7 | 0.65526 | 52420.8 | 0 | 0 | 0.58382 | 20433.7 | 0.47345 | 6628.3 | 40000 | 0 | 12420.8 | 8012.9 | 0 | 6628.3 | 14641.2 | 0 | 0 | 0 | 0
2022042318 | 7 | 0.65325 | 52260 | 0 | 0 | 0.59101 | 20685.35 | 0.4437 | 6211.8 | 40000 | 0 | 12260 | 8425.35 | 0 | 6211.8 | 14637.15 | 0 | 0 | 0 | 0
2022042319 | 7 | 0.64088 | 51270.4 | 0 | 0 | 0.60042 | 21014.7 | 0.32077 | 4490.78 | 40000 | 0 | 11270.4 | 9744.3 | 0 | 4490.78 | 14235.08 | 0 | 0 | 0 | 0
2022042320 | 7 | 0.61994 | 49595.2 | 0 | 0 | 0.59902 | 20965.7 | 0.1519 | 2126.6 | 40000 | 0 | 9595.2 | 11370.5 | 0 | 2126.6 | 13497.1 | 0 | 0 | 0 | 0
2022042321 | 7 | 0.61191 | 48952.8 | 0 | 0 | 0.56956 | 19934.6 | 0.00581 | 81.34 | 40000 | 0 | 8952.8 | 10981.8 | 0 | 81.34 | 11063.14 | 0 | 0 | 0 | 0
2022042322 | 7 | 0.59714 | 47771.2 | 0 | 0 | 0.58862 | 20601.7 | 0 | 0 | 40000 | 0 | 7771.2 | 12830.5 | 0 | 0 | 12830.5 | 0 | 0 | 0 | 0
2022042323 | 7 | 0.57252 | 45801.6 | 0 | 0 | 0.60473 | 21165.55 | 0 | 0 | 40000 | 0 | 5801.6 | 15363.95 | 0 | 0 | 15363.95 | 0 | 0 | 0 | 0
2022042324 | 7 | 0.54115 | 43292 | 0 | 0 | 0.61766 | 21618.1 | 0 | 0 | 40000 | 0 | 3292 | 18326.1 | 0 | 0 | 18326.1 | 0 | 0 | 0 | 0
2022042401 | 1 | 0.51521 | 41216.8 | 0 | 0 | 0.58871 | 20604.85 | 0 | 0 | 40000 | 0 | 1216.8 | 19388.05 | 0 | 0 | 19388.05 | 0 | 0 | 0 | 0
2022042402 | 1 | 0.48899 | 39119.2 | 0 | 0 | 0.57261 | 20041.35 | 0 | 0 | 39119.2 | 880.8 | 0 | 20041.35 | 0 | 0 | 20922.15 | 0 | 0 | 0 | 0
2022042403 | 1 | 0.47192 | 37753.6 | 0 | 0 | 0.52682 | 18438.7 | 0 | 0 | 37753.6 | 2246.4 | 0 | 18438.7 | 0 | 0 | 20685.1 | 0 | 0 | 0 | 0
2022042404 | 1 | 0.45971 | 36776.8 | 0 | 0 | 0.49416 | 17295.6 | 0 | 0 | 36776.8 | 3223.2 | 0 | 17295.6 | 0 | 0 | 20518.8 | 0 | 0 | 0 | 0
2022042405 | 1 | 0.45515 | 36412 | 0 | 0 | 0.45569 | 15949.15 | 0 | 0 | 36412 | 3588 | 0 | 15949.15 | 0 | 0 | 19537.15 | 0 | 0 | 0 | 0
2022042406 | 1 | 0.45367 | 36293.6 | 0 | 0 | 0.40988 | 14345.8 | 0 | 0 | 36293.6 | 3706.4 | 0 | 14345.8 | 0 | 0 | 18052.2 | 0 | 0 | 0 | 0
2022042407 | 1 | 0.45623 | 36498.4 | 0 | 0 | 0.40328 | 14114.8 | 5e-05 | 0.7 | 36498.4 | 3501.6 | 0 | 14114.8 | 0 | 0.7 | 17617.1 | 0 | 0 | 0 | 0
2022042408 | 1 | 0.46197 | 36957.6 | 0 | 0 | 0.42744 | 14960.4 | 0.03055 | 427.7 | 36957.6 | 3042.4 | 0 | 14960.4 | 0 | 427.7 | 18430.5 | 0 | 0 | 0 | 0
2022042409 | 1 | 0.48564 | 38851.2 | 0 | 0 | 0.45222 | 15827.7 | 0.23659 | 3312.26 | 38851.2 | 1148.8 | 0 | 15827.7 | 0 | 3312.26 | 20288.76 | 0 | 0 | 0 | 0
2022042410 | 1 | 0.51886 | 41508.8 | 0 | 0 | 0.49722 | 17402.7 | 0.36661 | 5132.54 | 40000 | 0 | 1508.8 | 15893.9 | 0 | 5132.54 | 21026.44 | 0 | 0 | 0 | 0
2022042411 | 1 | 0.54793 | 43834.4 | 0 | 0 | 0.50456 | 17659.6 | 0.44583 | 6241.62 | 40000 | 0 | 3834.4 | 13825.2 | 0 | 6241.62 | 20066.82 | 0 | 0 | 0 | 0
2022042412 | 1 | 0.57537 | 46029.6 | 0 | 0 | 0.49579 | 17352.65 | 0.53932 | 7550.48 | 40000 | 0 | 6029.6 | 11323.05 | 0 | 7550.48 | 18873.53 | 0 | 0 | 0 | 0
2022042413 | 1 | 0.59718 | 47774.4 | 0 | 0 | 0.49213 | 17224.55 | 0.547 | 7658 | 40000 | 0 | 7774.4 | 9450.15 | 0 | 7658 | 17108.15 | 0 | 0 | 0 | 0
2022042414 | 1 | 0.61206 | 48964.8 | 0 | 0 | 0.48503 | 16976.05 | 0.53793 | 7531.02 | 40000 | 0 | 8964.8 | 8011.25 | 0 | 7531.02 | 15542.27 | 0 | 0 | 0 | 0
2022042415 | 1 | 0.63104 | 50483.2 | 0 | 0 | 0.46977 | 16441.95 | 0.5965 | 8351 | 40000 | 0 | 10483.2 | 5958.75 | 0 | 8351 | 14309.75 | 0 | 0 | 0 | 0
2022042416 | 1 | 0.64515 | 51612 | 0 | 0 | 0.45268 | 15843.8 | 0.57822 | 8095.08 | 40000 | 0 | 11612 | 4231.8 | 0 | 8095.08 | 12326.88 | 0 | 0 | 0 | 0
2022042417 | 1 | 0.65445 | 52356 | 0 | 0 | 0.42925 | 15023.75 | 0.56874 | 7962.36 | 40000 | 0 | 12356 | 2667.75 | 0 | 7962.36 | 10630.11 | 0 | 0 | 0 | 0
2022042418 | 1 | 0.65606 | 52484.8 | 0 | 0 | 0.42328 | 14814.8 | 0.53539 | 7495.46 | 40000 | 0 | 12484.8 | 2330 | 0 | 7495.46 | 9825.46 | 0 | 0 | 0 | 0
2022042419 | 1 | 0.64452 | 51561.6 | 0 | 0 | 0.42293 | 14802.55 | 0.44446 | 6222.44 | 40000 | 0 | 11561.6 | 3240.95 | 0 | 6222.44 | 9463.39 | 0 | 0 | 0 | 0
2022042420 | 1 | 0.62336 | 49868.8 | 0 | 0 | 0.42022 | 14707.7 | 0.16757 | 2345.98 | 40000 | 0 | 9868.8 | 4838.9 | 0 | 2345.98 | 7184.88 | 0 | 0 | 0 | 0
2022042421 | 1 | 0.61839 | 49471.2 | 0 | 0 | 0.43733 | 15306.55 | 0.00487 | 68.18 | 40000 | 0 | 9471.2 | 5835.35 | 0 | 68.18 | 5903.53 | 0 | 0 | 0 | 0
2022042422 | 1 | 0.60178 | 48142.4 | 0 | 0 | 0.45458 | 15910.3 | 0 | 0 | 40000 | 0 | 8142.4 | 7767.9 | 0 | 0 | 7767.9 | 0 | 0 | 0 | 0
2022042423 | 1 | 0.57017 | 45613.6 | 0 | 0 | 0.46829 | 16390.15 | 0 | 0 | 40000 | 0 | 5613.6 | 10776.55 | 0 | 0 | 10776.55 | 0 | 0 | 0 | 0
2022042424 | 1 | 0.53057 | 42445.6 | 0 | 0 | 0.49287 | 17250.45 | 0 | 0 | 40000 | 0 | 2445.6 | 14804.85 | 0 | 0 | 14804.85 | 0 | 0 | 0 | 0
2022042501 | 2 | 0.49946 | 39956.8 | 0 | 0 | 0.51188 | 17915.8 | 0 | 0 | 39956.8 | 43.2 | 0 | 17915.8 | 0 | 0 | 17959 | 0 | 0 | 0 | 0
2022042502 | 2 | 0.47825 | 38260 | 0 | 0 | 0.48939 | 17128.65 | 0 | 0 | 38260 | 1740 | 0 | 17128.65 | 0 | 0 | 18868.65 | 0 | 0 | 0 | 0
2022042503 | 2 | 0.46219 | 36975.2 | 0 | 0 | 0.44142 | 15449.7 | 0 | 0 | 36975.2 | 3024.8 | 0 | 15449.7 | 0 | 0 | 18474.5 | 0 | 0 | 0 | 0
2022042504 | 2 | 0.45713 | 36570.4 | 0 | 0 | 0.42237 | 14782.95 | 0 | 0 | 36570.4 | 3429.6 | 0 | 14782.95 | 0 | 0 | 18212.55 | 0 | 0 | 0 | 0
2022042505 | 2 | 0.46107 | 36885.6 | 0 | 0 | 0.43833 | 15341.55 | 0 | 0 | 36885.6 | 3114.4 | 0 | 15341.55 | 0 | 0 | 18455.95 | 0 | 0 | 0 | 0
2022042506 | 2 | 0.47842 | 38273.6 | 0 | 0 | 0.46724 | 16353.4 | 0 | 0 | 38273.6 | 1726.4 | 0 | 16353.4 | 0 | 0 | 18079.8 | 0 | 0 | 0 | 0
2022042507 | 2 | 0.50547 | 40437.6 | 0 | 0 | 0.49724 | 17403.4 | 0 | 0 | 40000 | 0 | 437.6 | 16965.8 | 0 | 0 | 16965.8 | 0 | 0 | 0 | 0
2022042508 | 2 | 0.52435 | 41948 | 0 | 0 | 0.53899 | 18864.65 | 0.01592 | 222.88 | 40000 | 0 | 1948 | 16916.65 | 0 | 222.88 | 17139.53 | 0 | 0 | 0 | 0
2022042509 | 2 | 0.53564 | 42851.2 | 0 | 0 | 0.56773 | 19870.55 | 0.11787 | 1650.18 | 40000 | 0 | 2851.2 | 17019.35 | 0 | 1650.18 | 18669.53 | 0 | 0 | 0 | 0
2022042510 | 2 | 0.55369 | 44295.2 | 0 | 0 | 0.59711 | 20898.85 | 0.18334 | 2566.76 | 40000 | 0 | 4295.2 | 16603.65 | 0 | 2566.76 | 19170.41 | 0 | 0 | 0 | 0
2022042511 | 2 | 0.56852 | 45481.6 | 0 | 0 | 0.60217 | 21075.95 | 0.21049 | 2946.86 | 40000 | 0 | 5481.6 | 15594.35 | 0 | 2946.86 | 18541.21 | 0 | 0 | 0 | 0
2022042512 | 2 | 0.58238 | 46590.4 | 0 | 0 | 0.58891 | 20611.85 | 0.26129 | 3658.06 | 40000 | 0 | 6590.4 | 14021.45 | 0 | 3658.06 | 17679.51 | 0 | 0 | 0 | 0
2022042513 | 2 | 0.59197 | 47357.6 | 0 | 0 | 0.53064 | 18572.4 | 0.42795 | 5991.3 | 40000 | 0 | 7357.6 | 11214.8 | 0 | 5991.3 | 17206.1 | 0 | 0 | 0 | 0
2022042514 | 2 | 0.59613 | 47690.4 | 0 | 0 | 0.47602 | 16660.7 | 0.54636 | 7649.04 | 40000 | 0 | 7690.4 | 8970.3 | 0 | 7649.04 | 16619.34 | 0 | 0 | 0 | 0
2022042515 | 2 | 0.58927 | 47141.6 | 0 | 0 | 0.46166 | 16158.1 | 0.57589 | 8062.46 | 40000 | 0 | 7141.6 | 9016.5 | 0 | 8062.46 | 17078.96 | 0 | 0 | 0 | 0
2022042516 | 2 | 0.57094 | 45675.2 | 0 | 0 | 0.45382 | 15883.7 | 0.58764 | 8226.96 | 40000 | 0 | 5675.2 | 10208.5 | 0 | 8226.96 | 18435.46 | 0 | 0 | 0 | 0
2022042517 | 2 | 0.56222 | 44977.6 | 0 | 0 | 0.44331 | 15515.85 | 0.56371 | 7891.94 | 40000 | 0 | 4977.6 | 10538.25 | 0 | 7891.94 | 18430.19 | 0 | 0 | 0 | 0
2022042518 | 2 | 0.55818 | 44654.4 | 0 | 0 | 0.44972 | 15740.2 | 0.53157 | 7441.98 | 40000 | 0 | 4654.4 | 11085.8 | 0 | 7441.98 | 18527.78 | 0 | 0 | 0 | 0
2022042519 | 2 | 0.54892 | 43913.6 | 0 | 0 | 0.46824 | 16388.4 | 0.47478 | 6646.92 | 40000 | 0 | 3913.6 | 12474.8 | 0 | 6646.92 | 19121.72 | 0 | 0 | 0 | 0
2022042520 | 2 | 0.53941 | 43152.8 | 0 | 0 | 0.47009 | 16453.15 | 0.19255 | 2695.7 | 40000 | 0 | 3152.8 | 13300.35 | 0 | 2695.7 | 15996.05 | 0 | 0 | 0 | 0
2022042521 | 2 | 0.53947 | 43157.6 | 0 | 0 | 0.41991 | 14696.85 | 0.00497 | 69.58 | 40000 | 0 | 3157.6 | 11539.25 | 0 | 69.58 | 11608.83 | 0 | 0 | 0 | 0
2022042522 | 2 | 0.52504 | 42003.2 | 0 | 0 | 0.40125 | 14043.75 | 0 | 0 | 40000 | 0 | 2003.2 | 12040.55 | 0 | 0 | 12040.55 | 0 | 0 | 0 | 0
2022042523 | 2 | 0.49483 | 39586.4 | 0 | 0 | 0.41674 | 14585.9 | 0 | 0 | 39586.4 | 413.6 | 0 | 14585.9 | 0 | 0 | 14999.5 | 0 | 0 | 0 | 0
2022042524 | 2 | 0.46022 | 36817.6 | 0 | 0 | 0.38239 | 13383.65 | 0 | 0 | 36817.6 | 3182.4 | 0 | 13383.65 | 0 | 0 | 16566.05 | 0 | 0 | 0 | 0
2022042601 | 3 | 0.43628 | 34902.4 | 0 | 0 | 0.35137 | 12297.95 | 0 | 0 | 34902.4 | 5097.6 | 0 | 12297.95 | 0 | 0 | 17395.55 | 0 | 0 | 0 | 0
2022042602 | 3 | 0.42118 | 33694.4 | 0 | 0 | 0.36984 | 12944.4 | 0 | 0 | 33694.4 | 6305.6 | 0 | 12944.4 | 0 | 0 | 19250 | 0 | 0 | 0 | 0
2022042603 | 3 | 0.41205 | 32964 | 0 | 0 | 0.35274 | 12345.9 | 0 | 0 | 32964 | 7036 | 0 | 12345.9 | 0 | 0 | 19381.9 | 0 | 0 | 0 | 0
2022042604 | 3 | 0.40795 | 32636 | 0 | 0 | 0.33085 | 11579.75 | 0 | 0 | 32636 | 7364 | 0 | 11579.75 | 0 | 0 | 18943.75 | 0 | 0 | 0 | 0
2022042605 | 3 | 0.41184 | 32947.2 | 0 | 0 | 0.30898 | 10814.3 | 0 | 0 | 32947.2 | 7052.8 | 0 | 10814.3 | 0 | 0 | 17867.1 | 0 | 0 | 0 | 0
2022042606 | 3 | 0.43068 | 34454.4 | 0 | 0 | 0.30129 | 10545.15 | 0 | 0 | 34454.4 | 5545.6 | 0 | 10545.15 | 0 | 0 | 16090.75 | 0 | 0 | 0 | 0
2022042607 | 3 | 0.46534 | 37227.2 | 0 | 0 | 0.31185 | 10914.75 | 0.00028 | 3.92 | 37227.2 | 2772.8 | 0 | 10914.75 | 0 | 3.92 | 13691.47 | 0 | 0 | 0 | 0
2022042608 | 3 | 0.48171 | 38536.8 | 0 | 0 | 0.27415 | 9595.25 | 0.07086 | 992.04 | 38536.8 | 1463.2 | 0 | 9595.25 | 0 | 992.04 | 12050.49 | 0 | 0 | 0 | 0
2022042609 | 3 | 0.48841 | 39072.8 | 0 | 0 | 0.22967 | 8038.45 | 0.3895 | 5453 | 39072.8 | 927.2 | 0 | 8038.45 | 0 | 5453 | 14418.65 | 0 | 0 | 0 | 0
2022042610 | 3 | 0.49406 | 39524.8 | 0 | 0 | 0.26895 | 9413.25 | 0.55628 | 7787.92 | 39524.8 | 475.2 | 0 | 9413.25 | 0 | 7787.92 | 17676.37 | 0 | 0 | 0 | 0
2022042611 | 3 | 0.49926 | 39940.8 | 0 | 0 | 0.27488 | 9620.8 | 0.60393 | 8455.02 | 39940.8 | 59.2 | 0 | 9620.8 | 0 | 8455.02 | 18135.02 | 0 | 0 | 0 | 0
2022042612 | 3 | 0.50538 | 40430.4 | 0 | 0 | 0.2311 | 8088.5 | 0.6459 | 9042.6 | 40000 | 0 | 430.4 | 7658.1 | 0 | 9042.6 | 16700.7 | 0 | 0 | 0 | 0
2022042613 | 3 | 0.51112 | 40889.6 | 0 | 0 | 0.20819 | 7286.65 | 0.65924 | 9229.36 | 40000 | 0 | 889.6 | 6397.05 | 0 | 9229.36 | 15626.41 | 0 | 0 | 0 | 0
2022042614 | 3 | 0.52003 | 41602.4 | 0 | 0 | 0.20586 | 7205.1 | 0.67607 | 9464.98 | 40000 | 0 | 1602.4 | 5602.7 | 0 | 9464.98 | 15067.68 | 0 | 0 | 0 | 0
2022042615 | 3 | 0.53235 | 42588 | 0 | 0 | 0.20917 | 7320.95 | 0.70721 | 9900.94 | 40000 | 0 | 2588 | 4732.95 | 0 | 9900.94 | 14633.89 | 0 | 0 | 0 | 0
2022042616 | 3 | 0.5448 | 43584 | 0 | 0 | 0.21629 | 7570.15 | 0.72026 | 10083.64 | 40000 | 0 | 3584 | 3986.15 | 0 | 10083.64 | 14069.79 | 0 | 0 | 0 | 0
2022042617 | 3 | 0.55947 | 44757.6 | 0 | 0 | 0.22368 | 7828.8 | 0.72959 | 10214.26 | 40000 | 0 | 4757.6 | 3071.2 | 0 | 10214.26 | 13285.46 | 0 | 0 | 0 | 0
2022042618 | 3 | 0.57 | 45600 | 0 | 0 | 0.24144 | 8450.4 | 0.67753 | 9485.42 | 40000 | 0 | 5600 | 2850.4 | 0 | 9485.42 | 12335.82 | 0 | 0 | 0 | 0
2022042619 | 3 | 0.56715 | 45372 | 0 | 0 | 0.27675 | 9686.25 | 0.55413 | 7757.82 | 40000 | 0 | 5372 | 4314.25 | 0 | 7757.82 | 12072.07 | 0 | 0 | 0 | 0
2022042620 | 3 | 0.55895 | 44716 | 0 | 0 | 0.30435 | 10652.25 | 0.22075 | 3090.5 | 40000 | 0 | 4716 | 5936.25 | 0 | 3090.5 | 9026.75 | 0 | 0 | 0 | 0
2022042621 | 3 | 0.56042 | 44833.6 | 0 | 0 | 0.30338 | 10618.3 | 0.00522 | 73.08 | 40000 | 0 | 4833.6 | 5784.7 | 0 | 73.08 | 5857.78 | 0 | 0 | 0 | 0
2022042622 | 3 | 0.54769 | 43815.2 | 0 | 0 | 0.35108 | 12287.8 | 0 | 0 | 40000 | 0 | 3815.2 | 8472.6 | 0 | 0 | 8472.6 | 0 | 0 | 0 | 0
2022042623 | 3 | 0.51616 | 41292.8 | 0 | 0 | 0.41372 | 14480.2 | 0 | 0 | 40000 | 0 | 1292.8 | 13187.4 | 0 | 0 | 13187.4 | 0 | 0 | 0 | 0
2022042624 | 3 | 0.47969 | 38375.2 | 0 | 0 | 0.45822 | 16037.7 | 0 | 0 | 38375.2 | 1624.8 | 0 | 16037.7 | 0 | 0 | 17662.5 | 0 | 0 | 0 | 0
2022042701 | 4 | 0.45109 | 36087.2 | 0 | 0 | 0.4619 | 16166.5 | 0 | 0 | 36087.2 | 3912.8 | 0 | 16166.5 | 0 | 0 | 20079.3 | 0 | 0 | 0 | 0
2022042702 | 4 | 0.43103 | 34482.4 | 0 | 0 | 0.45121 | 15792.35 | 0 | 0 | 34482.4 | 5517.6 | 0 | 15792.35 | 0 | 0 | 21309.95 | 0 | 0 | 0 | 0
2022042703 | 4 | 0.41902 | 33521.6 | 0 | 0 | 0.45522 | 15932.7 | 0 | 0 | 33521.6 | 6478.4 | 0 | 15932.7 | 0 | 0 | 22411.1 | 0 | 0 | 0 | 0
2022042704 | 4 | 0.41545 | 33236 | 0 | 0 | 0.45146 | 15801.1 | 0 | 0 | 33236 | 6764 | 0 | 15801.1 | 0 | 0 | 22565.1 | 0 | 0 | 0 | 0
2022042705 | 4 | 0.41895 | 33516 | 0 | 0 | 0.4271 | 14948.5 | 0 | 0 | 33516 | 6484 | 0 | 14948.5 | 0 | 0 | 21432.5 | 0 | 0 | 0 | 0
2022042706 | 4 | 0.43705 | 34964 | 0 | 0 | 0.41466 | 14513.1 | 0 | 0 | 34964 | 5036 | 0 | 14513.1 | 0 | 0 | 19549.1 | 0 | 0 | 0 | 0
2022042707 | 4 | 0.47047 | 37637.6 | 0 | 0 | 0.40649 | 14227.15 | 0.00037 | 5.18 | 37637.6 | 2362.4 | 0 | 14227.15 | 0 | 5.18 | 16594.73 | 0 | 0 | 0 | 0
2022042708 | 4 | 0.48373 | 38698.4 | 0 | 0 | 0.3972 | 13902 | 0.05014 | 701.96 | 38698.4 | 1301.6 | 0 | 13902 | 0 | 701.96 | 15905.56 | 0 | 0 | 0 | 0
2022042709 | 4 | 0.49349 | 39479.2 | 0 | 0 | 0.35635 | 12472.25 | 0.23024 | 3223.36 | 39479.2 | 520.8 | 0 | 12472.25 | 0 | 3223.36 | 16216.41 | 0 | 0 | 0 | 0
2022042710 | 4 | 0.5064 | 40512 | 0 | 0 | 0.37485 | 13119.75 | 0.40289 | 5640.46 | 40000 | 0 | 512 | 12607.75 | 0 | 5640.46 | 18248.21 | 0 | 0 | 0 | 0
2022042711 | 4 | 0.52134 | 41707.2 | 0 | 0 | 0.40645 | 14225.75 | 0.55995 | 7839.3 | 40000 | 0 | 1707.2 | 12518.55 | 0 | 7839.3 | 20357.85 | 0 | 0 | 0 | 0
2022042712 | 4 | 0.53722 | 42977.6 | 0 | 0 | 0.43371 | 15179.85 | 0.59438 | 8321.32 | 40000 | 0 | 2977.6 | 12202.25 | 0 | 8321.32 | 20523.57 | 0 | 0 | 0 | 0
2022042713 | 4 | 0.55328 | 44262.4 | 0 | 0 | 0.47162 | 16506.7 | 0.55581 | 7781.34 | 40000 | 0 | 4262.4 | 12244.3 | 0 | 7781.34 | 20025.64 | 0 | 0 | 0 | 0
2022042714 | 4 | 0.57196 | 45756.8 | 0 | 0 | 0.49499 | 17324.65 | 0.50303 | 7042.42 | 40000 | 0 | 5756.8 | 11567.85 | 0 | 7042.42 | 18610.27 | 0 | 0 | 0 | 0
2022042715 | 4 | 0.5901 | 47208 | 0 | 0 | 0.51817 | 18135.95 | 0.47952 | 6713.28 | 40000 | 0 | 7208 | 10927.95 | 0 | 6713.28 | 17641.23 | 0 | 0 | 0 | 0
2022042716 | 4 | 0.60675 | 48540 | 0 | 0 | 0.54283 | 18999.05 | 0.42444 | 5942.16 | 40000 | 0 | 8540 | 10459.05 | 0 | 5942.16 | 16401.21 | 0 | 0 | 0 | 0
2022042717 | 4 | 0.62244 | 49795.2 | 0 | 0 | 0.57961 | 20286.35 | 0.36125 | 5057.5 | 40000 | 0 | 9795.2 | 10491.15 | 0 | 5057.5 | 15548.65 | 0 | 0 | 0 | 0
2022042718 | 4 | 0.62842 | 50273.6 | 0 | 0 | 0.58939 | 20628.65 | 0.34614 | 4845.96 | 40000 | 0 | 10273.6 | 10355.05 | 0 | 4845.96 | 15201.01 | 0 | 0 | 0 | 0
2022042719 | 4 | 0.61859 | 49487.2 | 0 | 0 | 0.59834 | 20941.9 | 0.2623 | 3672.2 | 40000 | 0 | 9487.2 | 11454.7 | 0 | 3672.2 | 15126.9 | 0 | 0 | 0 | 0
2022042720 | 4 | 0.60383 | 48306.4 | 0 | 0 | 0.6084 | 21294 | 0.08144 | 1140.16 | 40000 | 0 | 8306.4 | 12987.6 | 0 | 1140.16 | 14127.76 | 0 | 0 | 0 | 0
2022042721 | 4 | 0.59688 | 47750.4 | 0 | 0 | 0.57721 | 20202.35 | 0.00235 | 32.9 | 40000 | 0 | 7750.4 | 12451.95 | 0 | 32.9 | 12484.85 | 0 | 0 | 0 | 0
2022042722 | 4 | 0.58033 | 46426.4 | 0 | 0 | 0.58841 | 20594.35 | 0 | 0 | 40000 | 0 | 6426.4 | 14167.95 | 0 | 0 | 14167.95 | 0 | 0 | 0 | 0
2022042723 | 4 | 0.54531 | 43624.8 | 0 | 0 | 0.61385 | 21484.75 | 0 | 0 | 40000 | 0 | 3624.8 | 17859.95 | 0 | 0 | 17859.95 | 0 | 0 | 0 | 0
2022042724 | 4 | 0.50627 | 40501.6 | 0 | 0 | 0.61992 | 21697.2 | 0 | 0 | 40000 | 0 | 501.6 | 21195.6 | 0 | 0 | 21195.6 | 0 | 0 | 0 | 0
2022042801 | 5 | 0.47511 | 38008.8 | 0 | 0 | 0.63529 | 22235.15 | 0 | 0 | 38008.8 | 1991.2 | 0 | 22235.15 | 0 | 0 | 24226.35 | 0 | 0 | 0 | 0
2022042802 | 5 | 0.45483 | 36386.4 | 0 | 0 | 0.63535 | 22237.25 | 0 | 0 | 36386.4 | 3613.6 | 0 | 22237.25 | 0 | 0 | 25850.85 | 0 | 0 | 0 | 0
2022042803 | 5 | 0.44214 | 35371.2 | 0 | 0 | 0.61481 | 21518.35 | 0 | 0 | 35371.2 | 4628.8 | 0 | 21518.35 | 0 | 0 | 26147.15 | 0 | 0 | 0 | 0
2022042804 | 5 | 0.43647 | 34917.6 | 0 | 0 | 0.60209 | 21073.15 | 0 | 0 | 34917.6 | 5082.4 | 0 | 21073.15 | 0 | 0 | 26155.55 | 0 | 0 | 0 | 0
2022042805 | 5 | 0.43752 | 35001.6 | 0 | 0 | 0.58653 | 20528.55 | 0 | 0 | 35001.6 | 4998.4 | 0 | 20528.55 | 0 | 0 | 25526.95 | 0 | 0 | 0 | 0
2022042806 | 5 | 0.45464 | 36371.2 | 0 | 0 | 0.55257 | 19339.95 | 0 | 0 | 36371.2 | 3628.8 | 0 | 19339.95 | 0 | 0 | 22968.75 | 0 | 0 | 0 | 0
2022042807 | 5 | 0.48637 | 38909.6 | 0 | 0 | 0.53144 | 18600.4 | 0.0003 | 4.2 | 38909.6 | 1090.4 | 0 | 18600.4 | 0 | 4.2 | 19695 | 0 | 0 | 0 | 0
2022042808 | 5 | 0.50275 | 40220 | 0 | 0 | 0.49634 | 17371.9 | 0.05921 | 828.94 | 40000 | 0 | 220 | 17151.9 | 0 | 828.94 | 17980.84 | 0 | 0 | 0 | 0
2022042809 | 5 | 0.52121 | 41696.8 | 0 | 0 | 0.48376 | 16931.6 | 0.3564 | 4989.6 | 40000 | 0 | 1696.8 | 15234.8 | 0 | 4989.6 | 20224.4 | 0 | 0 | 0 | 0
2022042810 | 5 | 0.54197 | 43357.6 | 0 | 0 | 0.52875 | 18506.25 | 0.46878 | 6562.92 | 40000 | 0 | 3357.6 | 15148.65 | 0 | 6562.92 | 21711.57 | 0 | 0 | 0 | 0
2022042811 | 5 | 0.5611 | 44888 | 0 | 0 | 0.54464 | 19062.4 | 0.55176 | 7724.64 | 40000 | 0 | 4888 | 14174.4 | 0 | 7724.64 | 21899.04 | 0 | 0 | 0 | 0
2022042812 | 5 | 0.58097 | 46477.6 | 0 | 0 | 0.52949 | 18532.15 | 0.6554 | 9175.6 | 40000 | 0 | 6477.6 | 12054.55 | 0 | 9175.6 | 21230.15 | 0 | 0 | 0 | 0
2022042813 | 5 | 0.6027 | 48216 | 0 | 0 | 0.52752 | 18463.2 | 0.69105 | 9674.7 | 40000 | 0 | 8216 | 10247.2 | 0 | 9674.7 | 19921.9 | 0 | 0 | 0 | 0
2022042814 | 5 | 0.62551 | 50040.8 | 0 | 0 | 0.53443 | 18705.05 | 0.72374 | 10132.36 | 40000 | 0 | 10040.8 | 8664.25 | 0 | 10132.36 | 18796.61 | 0 | 0 | 0 | 0
2022042815 | 5 | 0.6431 | 51448 | 0 | 0 | 0.56475 | 19766.25 | 0.65571 | 9179.94 | 40000 | 0 | 11448 | 8318.25 | 0 | 9179.94 | 17498.19 | 0 | 0 | 0 | 0
2022042816 | 5 | 0.65876 | 52700.8 | 0 | 0 | 0.59765 | 20917.75 | 0.56566 | 7919.24 | 40000 | 0 | 12700.8 | 8216.95 | 0 | 7919.24 | 16136.19 | 0 | 0 | 0 | 0
2022042817 | 5 | 0.67233 | 53786.4 | 0 | 0 | 0.61185 | 21414.75 | 0.51132 | 7158.48 | 40000 | 0 | 13786.4 | 7628.35 | 0 | 7158.48 | 14786.83 | 0 | 0 | 0 | 0
2022042818 | 5 | 0.67895 | 54316 | 0 | 0 | 0.63686 | 22290.1 | 0.43878 | 6142.92 | 40000 | 0 | 14316 | 7974.1 | 0 | 6142.92 | 14117.02 | 0 | 0 | 0 | 0
2022042819 | 5 | 0.66714 | 53371.2 | 0 | 0 | 0.63114 | 22089.9 | 0.39519 | 5532.66 | 40000 | 0 | 13371.2 | 8718.7 | 0 | 5532.66 | 14251.36 | 0 | 0 | 0 | 0
2022042820 | 5 | 0.65345 | 52276 | 0 | 0 | 0.6495 | 22732.5 | 0.19871 | 2781.94 | 40000 | 0 | 12276 | 10456.5 | 0 | 2781.94 | 13238.44 | 0 | 0 | 0 | 0
2022042821 | 5 | 0.64337 | 51469.6 | 0 | 0 | 0.65836 | 23042.6 | 0.01516 | 212.24 | 40000 | 0 | 11469.6 | 11573 | 0 | 212.24 | 11785.24 | 0 | 0 | 0 | 0
2022042822 | 5 | 0.62584 | 50067.2 | 0 | 0 | 0.67184 | 23514.4 | 0.00893 | 125.02 | 40000 | 0 | 10067.2 | 13447.2 | 0 | 125.02 | 13572.22 | 0 | 0 | 0 | 0
2022042823 | 5 | 0.58872 | 47097.6 | 0 | 0 | 0.68574 | 24000.9 | 0.00893 | 125.02 | 40000 | 0 | 7097.6 | 16903.3 | 0 | 125.02 | 17028.32 | 0 | 0 | 0 | 0
2022042824 | 5 | 0.54799 | 43839.2 | 0 | 0 | 0.68368 | 23928.8 | 0.00892 | 124.88 | 40000 | 0 | 3839.2 | 20089.6 | 0 | 124.88 | 20214.48 | 0 | 0 | 0 | 0
2022042901 | 6 | 0.51528 | 41222.4 | 0 | 0 | 0.67345 | 23570.75 | 0.00892 | 124.88 | 40000 | 0 | 1222.4 | 22348.35 | 0 | 124.88 | 22473.23 | 0 | 0 | 0 | 0
2022042902 | 6 | 0.49317 | 39453.6 | 0 | 0 | 0.67062 | 23471.7 | 0.00892 | 124.88 | 39453.6 | 546.4 | 0 | 23471.7 | 0 | 124.88 | 24142.98 | 0 | 0 | 0 | 0
2022042903 | 6 | 0.47582 | 38065.6 | 0 | 0 | 0.65734 | 23006.9 | 0.00892 | 124.88 | 38065.6 | 1934.4 | 0 | 23006.9 | 0 | 124.88 | 25066.18 | 0 | 0 | 0 | 0
2022042904 | 6 | 0.47756 | 38204.8 | 0 | 0 | 0.65125 | 22793.75 | 0.00892 | 124.88 | 38204.8 | 1795.2 | 0 | 22793.75 | 0 | 124.88 | 24713.83 | 0 | 0 | 0 | 0
2022042905 | 6 | 0.47998 | 38398.4 | 0 | 0 | 0.65069 | 22774.15 | 0.00892 | 124.88 | 38398.4 | 1601.6 | 0 | 22774.15 | 0 | 124.88 | 24500.63 | 0 | 0 | 0 | 0
2022042906 | 6 | 0.49177 | 39341.6 | 0 | 0 | 0.64992 | 22747.2 | 0.00893 | 125.02 | 39341.6 | 658.4 | 0 | 22747.2 | 0 | 125.02 | 23530.62 | 0 | 0 | 0 | 0
2022042907 | 6 | 0.51589 | 41271.2 | 0 | 0 | 0.64346 | 22521.1 | 0.00105 | 14.7 | 40000 | 0 | 1271.2 | 21249.9 | 0 | 14.7 | 21264.6 | 0 | 0 | 0 | 0
2022042908 | 6 | 0.53353 | 42682.4 | 0 | 0 | 0.61899 | 21664.65 | 0.05891 | 824.74 | 40000 | 0 | 2682.4 | 18982.25 | 0 | 824.74 | 19806.99 | 0 | 0 | 0 | 0
2022042909 | 6 | 0.55007 | 44005.6 | 0 | 0 | 0.5871 | 20548.5 | 0.28295 | 3961.3 | 40000 | 0 | 4005.6 | 16542.9 | 0 | 3961.3 | 20504.2 | 0 | 0 | 0 | 0
2022042910 | 6 | 0.5673 | 45384 | 0 | 0 | 0.60209 | 21073.15 | 0.30892 | 4324.88 | 40000 | 0 | 5384 | 15689.15 | 0 | 4324.88 | 20014.03 | 0 | 0 | 0 | 0
2022042911 | 6 | 0.59061 | 47248.8 | 0 | 0 | 0.59435 | 20802.25 | 0.38593 | 5403.02 | 40000 | 0 | 7248.8 | 13553.45 | 0 | 5403.02 | 18956.47 | 0 | 0 | 0 | 0
2022042912 | 6 | 0.6101 | 48808 | 0 | 0 | 0.57862 | 20251.7 | 0.47821 | 6694.94 | 40000 | 0 | 8808 | 11443.7 | 0 | 6694.94 | 18138.64 | 0 | 0 | 0 | 0
2022042913 | 6 | 0.62931 | 50344.8 | 0 | 0 | 0.56163 | 19657.05 | 0.60476 | 8466.64 | 40000 | 0 | 10344.8 | 9312.25 | 0 | 8466.64 | 17778.89 | 0 | 0 | 0 | 0
2022042914 | 6 | 0.65077 | 52061.6 | 0 | 0 | 0.54849 | 19197.15 | 0.64781 | 9069.34 | 40000 | 0 | 12061.6 | 7135.55 | 0 | 9069.34 | 16204.89 | 0 | 0 | 0 | 0
2022042915 | 6 | 0.67095 | 53676 | 0 | 0 | 0.5618 | 19663 | 0.64213 | 8989.82 | 40000 | 0 | 13676 | 5987 | 0 | 8989.82 | 14976.82 | 0 | 0 | 0 | 0
2022042916 | 6 | 0.68324 | 54659.2 | 0 | 0 | 0.57557 | 20144.95 | 0.61312 | 8583.68 | 40000 | 0 | 14659.2 | 5485.75 | 0 | 8583.68 | 14069.43 | 0 | 0 | 0 | 0
2022042917 | 6 | 0.69416 | 55532.8 | 0 | 0 | 0.59088 | 20680.8 | 0.56943 | 7972.02 | 40000 | 0 | 15532.8 | 5148 | 0 | 7972.02 | 13120.02 | 0 | 0 | 0 | 0
2022042918 | 6 | 0.69282 | 55425.6 | 0 | 0 | 0.59515 | 20830.25 | 0.5249 | 7348.6 | 40000 | 0 | 15425.6 | 5404.65 | 0 | 7348.6 | 12753.25 | 0 | 0 | 0 | 0
2022042919 | 6 | 0.67857 | 54285.6 | 0 | 0 | 0.59182 | 20713.7 | 0.43474 | 6086.36 | 40000 | 0 | 14285.6 | 6428.1 | 0 | 6086.36 | 12514.46 | 0 | 0 | 0 | 0
2022042920 | 6 | 0.65602 | 52481.6 | 0 | 0 | 0.57369 | 20079.15 | 0.21823 | 3055.22 | 40000 | 0 | 12481.6 | 7597.55 | 0 | 3055.22 | 10652.77 | 0 | 0 | 0 | 0
2022042921 | 6 | 0.64392 | 51513.6 | 0 | 0 | 0.54108 | 18937.8 | 0.00766 | 107.24 | 40000 | 0 | 11513.6 | 7424.2 | 0 | 107.24 | 7531.44 | 0 | 0 | 0 | 0
2022042922 | 6 | 0.62815 | 50252 | 0 | 0 | 0.57257 | 20039.95 | 0 | 0 | 40000 | 0 | 10252 | 9787.95 | 0 | 0 | 9787.95 | 0 | 0 | 0 | 0
2022042923 | 6 | 0.60139 | 48111.2 | 0 | 0 | 0.60045 | 21015.75 | 0 | 0 | 40000 | 0 | 8111.2 | 12904.55 | 0 | 0 | 12904.55 | 0 | 0 | 0 | 0
2022042924 | 6 | 0.56756 | 45404.8 | 0 | 0 | 0.63112 | 22089.2 | 0 | 0 | 40000 | 0 | 5404.8 | 16684.4 | 0 | 0 | 16684.4 | 0 | 0 | 0 | 0
2022043001 | 7 | 0.53559 | 42847.2 | 0 | 0 | 0.63857 | 22349.95 | 0 | 0 | 40000 | 0 | 2847.2 | 19502.75 | 0 | 0 | 19502.75 | 0 | 0 | 0 | 0
2022043002 | 7 | 0.51151 | 40920.8 | 0 | 0 | 0.61959 | 21685.65 | 0 | 0 | 40000 | 0 | 920.8 | 20764.85 | 0 | 0 | 20764.85 | 0 | 0 | 0 | 0
2022043003 | 7 | 0.49315 | 39452 | 0 | 0 | 0.58156 | 20354.6 | 0 | 0 | 39452 | 548 | 0 | 20354.6 | 0 | 0 | 20902.6 | 0 | 0 | 0 | 0
2022043004 | 7 | 0.481 | 38480 | 0 | 0 | 0.55212 | 19324.2 | 0 | 0 | 38480 | 1520 | 0 | 19324.2 | 0 | 0 | 20844.2 | 0 | 0 | 0 | 0
2022043005 | 7 | 0.4759 | 38072 | 0 | 0 | 0.50896 | 17813.6 | 0 | 0 | 38072 | 1928 | 0 | 17813.6 | 0 | 0 | 19741.6 | 0 | 0 | 0 | 0
2022043006 | 7 | 0.47677 | 38141.6 | 0 | 0 | 0.48199 | 16869.65 | 0 | 0 | 38141.6 | 1858.4 | 0 | 16869.65 | 0 | 0 | 18728.05 | 0 | 0 | 0 | 0
2022043007 | 7 | 0.48171 | 38536.8 | 0 | 0 | 0.41704 | 14596.4 | 8e-05 | 1.12 | 38536.8 | 1463.2 | 0 | 14596.4 | 0 | 1.12 | 16060.72 | 0 | 0 | 0 | 0
2022043008 | 7 | 0.49375 | 39500 | 0 | 0 | 0.4169 | 14591.5 | 0.06765 | 947.1 | 39500 | 500 | 0 | 14591.5 | 0 | 947.1 | 16038.6 | 0 | 0 | 0 | 0
2022043009 | 7 | 0.52301 | 41840.8 | 0 | 0 | 0.41727 | 14604.45 | 0.40079 | 5611.06 | 40000 | 0 | 1840.8 | 12763.65 | 0 | 5611.06 | 18374.71 | 0 | 0 | 0 | 0
2022043010 | 7 | 0.55364 | 44291.2 | 0 | 0 | 0.49843 | 17445.05 | 0.39525 | 5533.5 | 40000 | 0 | 4291.2 | 13153.85 | 0 | 5533.5 | 18687.35 | 0 | 0 | 0 | 0
2022043011 | 7 | 0.57825 | 46260 | 0 | 0 | 0.52629 | 18420.15 | 0.33218 | 4650.52 | 40000 | 0 | 6260 | 12160.15 | 0 | 4650.52 | 16810.67 | 0 | 0 | 0 | 0
2022043012 | 7 | 0.59776 | 47820.8 | 0 | 0 | 0.4822 | 16877 | 0.46645 | 6530.3 | 40000 | 0 | 7820.8 | 9056.2 | 0 | 6530.3 | 15586.5 | 0 | 0 | 0 | 0
2022043013 | 7 | 0.61703 | 49362.4 | 0 | 0 | 0.39472 | 13815.2 | 0.66241 | 9273.74 | 40000 | 0 | 9362.4 | 4452.8 | 0 | 9273.74 | 13726.54 | 0 | 0 | 0 | 0
2022043014 | 7 | 0.64105 | 51284 | 0 | 0 | 0.29117 | 10190.95 | 0.77789 | 10890.46 | 40000 | 0 | 10190.95 | 0 | 1093.05 | 9797.41 | 9797.41 | 0 | 0 | 0 | 0
2022043015 | 7 | 0.66435 | 53148 | 0 | 0 | 0.19766 | 6918.1 | 0.79807 | 11172.98 | 40000 | 0 | 6918.1 | 0 | 6229.9 | 4943.08 | 4943.08 | 0 | 0 | 0 | 0
2022043016 | 7 | 0.68241 | 54592.8 | 0 | 0 | 0.16317 | 5710.95 | 0.81057 | 11347.98 | 40000 | 0 | 5710.95 | 0 | 8881.85 | 2466.13 | 2466.13 | 0 | 0 | 0 | 0
2022043017 | 7 | 0.69468 | 55574.4 | 0 | 0 | 0.15226 | 5329.1 | 0.81844 | 11458.16 | 40000 | 0 | 5329.1 | 0 | 10245.3 | 1212.86 | 1212.86 | 0 | 0 | 0 | 0
2022043018 | 7 | 0.69415 | 55532 | 0 | 0 | 0.14978 | 5242.3 | 0.77604 | 10864.56 | 40000 | 0 | 5242.3 | 0 | 10289.7 | 574.86 | 574.86 | 0 | 0 | 0 | 0
2022043019 | 7 | 0.67789 | 54231.2 | 0 | 0 | 0.16649 | 5827.15 | 0.6353 | 8894.2 | 40000 | 0 | 5827.15 | 0 | 8404.05 | 490.15 | 490.15 | 0 | 0 | 0 | 0
2022043020 | 7 | 0.64981 | 51984.8 | 0 | 0 | 0.17503 | 6126.05 | 0.24075 | 3370.5 | 40000 | 0 | 6126.05 | 0 | 3370.5 | 0 | 0 | 2488.25 | 0 | 0 | 2488.25
2022043021 | 7 | 0.63158 | 50526.4 | 0 | 0 | 0.19868 | 6953.8 | 0.00711 | 99.54 | 40000 | 0 | 6953.8 | 0 | 99.54 | 0 | 0 | 3473.06 | 0 | 0 | 3473.06
2022043022 | 7 | 0.60688 | 48550.4 | 0 | 0 | 0.24687 | 8640.45 | 0 | 0 | 40000 | 0 | 8550.4 | 90.05 | 0 | 0 | 90.05 | 0 | 0 | 0 | 0
2022043023 | 7 | 0.57446 | 45956.8 | 0 | 0 | 0.28975 | 10141.25 | 0 | 0 | 40000 | 0 | 5956.8 | 4184.45 | 0 | 0 | 4184.45 | 0 | 0 | 0 | 0
2022043024 | 7 | 0.54014 | 43211.2 | 0 | 0 | 0.31619 | 11066.65 | 0 | 0 | 40000 | 0 | 3211.2 | 7855.45 | 0 | 0 | 7855.45 | 0 | 0 | 0 | 0
2022050101 | 1 | 0.50863 | 40690.4 | 0 | 0 | 0.33912 | 11869.2 | 0 | 0 | 40000 | 0 | 690.4 | 11178.8 | 0 | 0 | 11178.8 | 0 | 0 | 0 | 0
2022050102 | 1 | 0.48263 | 38610.4 | 0 | 0 | 0.36171 | 12659.85 | 0 | 0 | 38610.4 | 1389.6 | 0 | 12659.85 | 0 | 0 | 14049.45 | 0 | 0 | 0 | 0
2022050103 | 1 | 0.46571 | 37256.8 | 0 | 0 | 0.36032 | 12611.2 | 0 | 0 | 37256.8 | 2743.2 | 0 | 12611.2 | 0 | 0 | 15354.4 | 0 | 0 | 0 | 0
2022050104 | 1 | 0.45385 | 36308 | 0 | 0 | 0.36168 | 12658.8 | 0 | 0 | 36308 | 3692 | 0 | 12658.8 | 0 | 0 | 16350.8 | 0 | 0 | 0 | 0
2022050105 | 1 | 0.44576 | 35660.8 | 0 | 0 | 0.38296 | 13403.6 | 0 | 0 | 35660.8 | 4339.2 | 0 | 13403.6 | 0 | 0 | 17742.8 | 0 | 0 | 0 | 0
2022050106 | 1 | 0.44683 | 35746.4 | 0 | 0 | 0.41293 | 14452.55 | 0 | 0 | 35746.4 | 4253.6 | 0 | 14452.55 | 0 | 0 | 18706.15 | 0 | 0 | 0 | 0
2022050107 | 1 | 0.44839 | 35871.2 | 0 | 0 | 0.43859 | 15350.65 | 0.00052 | 7.28 | 35871.2 | 4128.8 | 0 | 15350.65 | 0 | 7.28 | 19486.73 | 0 | 0 | 0 | 0
2022050108 | 1 | 0.45644 | 36515.2 | 0 | 0 | 0.45012 | 15754.2 | 0.05215 | 730.1 | 36515.2 | 3484.8 | 0 | 15754.2 | 0 | 730.1 | 19969.1 | 0 | 0 | 0 | 0
2022050109 | 1 | 0.48353 | 38682.4 | 0 | 0 | 0.45195 | 15818.25 | 0.23439 | 3281.46 | 38682.4 | 1317.6 | 0 | 15818.25 | 0 | 3281.46 | 20417.31 | 0 | 0 | 0 | 0
2022050110 | 1 | 0.51859 | 41487.2 | 0 | 0 | 0.51105 | 17886.75 | 0.35857 | 5019.98 | 40000 | 0 | 1487.2 | 16399.55 | 0 | 5019.98 | 21419.53 | 0 | 0 | 0 | 0
2022050111 | 1 | 0.5525 | 44200 | 0 | 0 | 0.56426 | 19749.1 | 0.41311 | 5783.54 | 40000 | 0 | 4200 | 15549.1 | 0 | 5783.54 | 21332.64 | 0 | 0 | 0 | 0
2022050112 | 1 | 0.58462 | 46769.6 | 0 | 0 | 0.58141 | 20349.35 | 0.42839 | 5997.46 | 40000 | 0 | 6769.6 | 13579.75 | 0 | 5997.46 | 19577.21 | 0 | 0 | 0 | 0
2022050113 | 1 | 0.61311 | 49048.8 | 0 | 0 | 0.58985 | 20644.75 | 0.4589 | 6424.6 | 40000 | 0 | 9048.8 | 11595.95 | 0 | 6424.6 | 18020.55 | 0 | 0 | 0 | 0
2022050114 | 1 | 0.63949 | 51159.2 | 0 | 0 | 0.59592 | 20857.2 | 0.494 | 6916 | 40000 | 0 | 11159.2 | 9698 | 0 | 6916 | 16614 | 0 | 0 | 0 | 0
2022050115 | 1 | 0.66247 | 52997.6 | 0 | 0 | 0.59498 | 20824.3 | 0.50894 | 7125.16 | 40000 | 0 | 12997.6 | 7826.7 | 0 | 7125.16 | 14951.86 | 0 | 0 | 0 | 0
2022050116 | 1 | 0.68396 | 54716.8 | 0 | 0 | 0.60573 | 21200.55 | 0.45875 | 6422.5 | 40000 | 0 | 14716.8 | 6483.75 | 0 | 6422.5 | 12906.25 | 0 | 0 | 0 | 0
2022050117 | 1 | 0.69748 | 55798.4 | 0 | 0 | 0.62229 | 21780.15 | 0.40394 | 5655.16 | 40000 | 0 | 15798.4 | 5981.75 | 0 | 5655.16 | 11636.91 | 0 | 0 | 0 | 0
2022050118 | 1 | 0.70219 | 56175.2 | 0 | 0 | 0.636 | 22260 | 0.27683 | 3875.62 | 40000 | 0 | 16175.2 | 6084.8 | 0 | 3875.62 | 9960.42 | 0 | 0 | 0 | 0
2022050119 | 1 | 0.69364 | 55491.2 | 0 | 0 | 0.63415 | 22195.25 | 0.20501 | 2870.14 | 40000 | 0 | 15491.2 | 6704.05 | 0 | 2870.14 | 9574.19 | 0 | 0 | 0 | 0
2022050120 | 1 | 0.67278 | 53822.4 | 0 | 0 | 0.62218 | 21776.3 | 0.08256 | 1155.84 | 40000 | 0 | 13822.4 | 7953.9 | 0 | 1155.84 | 9109.74 | 0 | 0 | 0 | 0
2022050121 | 1 | 0.66543 | 53234.4 | 0 | 0 | 0.58456 | 20459.6 | 0.00448 | 62.72 | 40000 | 0 | 13234.4 | 7225.2 | 0 | 62.72 | 7287.92 | 0 | 0 | 0 | 0
2022050122 | 1 | 0.64592 | 51673.6 | 0 | 0 | 0.56333 | 19716.55 | 0 | 0 | 40000 | 0 | 11673.6 | 8042.95 | 0 | 0 | 8042.95 | 0 | 0 | 0 | 0
2022050123 | 1 | 0.61191 | 48952.8 | 0 | 0 | 0.60337 | 21117.95 | 0 | 0 | 40000 | 0 | 8952.8 | 12165.15 | 0 | 0 | 12165.15 | 0 | 0 | 0 | 0
2022050124 | 1 | 0.57173 | 45738.4 | 0 | 0 | 0.63396 | 22188.6 | 0 | 0 | 40000 | 0 | 5738.4 | 16450.2 | 0 | 0 | 16450.2 | 0 | 0 | 0 | 0
2022050201 | 2 | 0.53584 | 42867.2 | 0 | 0 | 0.62607 | 21912.45 | 0 | 0 | 40000 | 0 | 2867.2 | 19045.25 | 0 | 0 | 19045.25 | 0 | 0 | 0 | 0
2022050202 | 2 | 0.51276 | 41020.8 | 0 | 0 | 0.60738 | 21258.3 | 0 | 0 | 40000 | 0 | 1020.8 | 20237.5 | 0 | 0 | 20237.5 | 0 | 0 | 0 | 0
2022050203 | 2 | 0.49793 | 39834.4 | 0 | 0 | 0.61336 | 21467.6 | 0 | 0 | 39834.4 | 165.6 | 0 | 21467.6 | 0 | 0 | 21633.2 | 0 | 0 | 0 | 0
2022050204 | 2 | 0.48752 | 39001.6 | 0 | 0 | 0.61619 | 21566.65 | 0 | 0 | 39001.6 | 998.4 | 0 | 21566.65 | 0 | 0 | 22565.05 | 0 | 0 | 0 | 0
2022050205 | 2 | 0.49019 | 39215.2 | 0 | 0 | 0.60091 | 21031.85 | 0 | 0 | 39215.2 | 784.8 | 0 | 21031.85 | 0 | 0 | 21816.65 | 0 | 0 | 0 | 0
2022050206 | 2 | 0.50521 | 40416.8 | 0 | 0 | 0.62839 | 21993.65 | 0 | 0 | 40000 | 0 | 416.8 | 21576.85 | 0 | 0 | 21576.85 | 0 | 0 | 0 | 0
2022050207 | 2 | 0.53843 | 43074.4 | 0 | 0 | 0.65676 | 22986.6 | 0 | 0 | 40000 | 0 | 3074.4 | 19912.2 | 0 | 0 | 19912.2 | 0 | 0 | 0 | 0
2022050208 | 2 | 0.55632 | 44505.6 | 0 | 0 | 0.66559 | 23295.65 | 0.04372 | 612.08 | 40000 | 0 | 4505.6 | 18790.05 | 0 | 612.08 | 19402.13 | 0 | 0 | 0 | 0
2022050209 | 2 | 0.57218 | 45774.4 | 0 | 0 | 0.62982 | 22043.7 | 0.25709 | 3599.26 | 40000 | 0 | 5774.4 | 16269.3 | 0 | 3599.26 | 19868.56 | 0 | 0 | 0 | 0
2022050210 | 2 | 0.59524 | 47619.2 | 0 | 0 | 0.63355 | 22174.25 | 0.34114 | 4775.96 | 40000 | 0 | 7619.2 | 14555.05 | 0 | 4775.96 | 19331.01 | 0 | 0 | 0 | 0
2022050211 | 2 | 0.62604 | 50083.2 | 0 | 0 | 0.63454 | 22208.9 | 0.37791 | 5290.74 | 40000 | 0 | 10083.2 | 12125.7 | 0 | 5290.74 | 17416.44 | 0 | 0 | 0 | 0
2022050212 | 2 | 0.653 | 52240 | 0 | 0 | 0.63313 | 22159.55 | 0.39572 | 5540.08 | 40000 | 0 | 12240 | 9919.55 | 0 | 5540.08 | 15459.63 | 0 | 0 | 0 | 0
2022050213 | 2 | 0.67969 | 54375.2 | 0 | 0 | 0.61688 | 21590.8 | 0.45751 | 6405.14 | 40000 | 0 | 14375.2 | 7215.6 | 0 | 6405.14 | 13620.74 | 0 | 0 | 0 | 0
2022050214 | 2 | 0.70216 | 56172.8 | 0 | 0 | 0.57865 | 20252.75 | 0.62923 | 8809.22 | 40000 | 0 | 16172.8 | 4079.95 | 0 | 8809.22 | 12889.17 | 0 | 0 | 0 | 0
2022050215 | 2 | 0.71305 | 57044 | 0 | 0 | 0.54844 | 19195.4 | 0.66734 | 9342.76 | 40000 | 0 | 17044 | 2151.4 | 0 | 9342.76 | 11494.16 | 0 | 0 | 0 | 0
2022050216 | 2 | 0.71924 | 57539.2 | 0 | 0 | 0.53451 | 18707.85 | 0.68964 | 9654.96 | 40000 | 0 | 17539.2 | 1168.65 | 0 | 9654.96 | 10823.61 | 0 | 0 | 0 | 0
2022050217 | 2 | 0.72743 | 58194.4 | 0 | 0 | 0.53648 | 18776.8 | 0.68221 | 9550.94 | 40000 | 0 | 18194.4 | 582.4 | 0 | 9550.94 | 10133.34 | 0 | 0 | 0 | 0
2022050218 | 2 | 0.73209 | 58567.2 | 0 | 0 | 0.5317 | 18609.5 | 0.67582 | 9461.48 | 40000 | 0 | 18567.2 | 42.3 | 0 | 9461.48 | 9503.78 | 0 | 0 | 0 | 0
2022050219 | 2 | 0.72245 | 57796 | 0 | 0 | 0.53682 | 18788.7 | 0.5797 | 8115.8 | 40000 | 0 | 17796 | 992.7 | 0 | 8115.8 | 9108.5 | 0 | 0 | 0 | 0
2022050220 | 2 | 0.69886 | 55908.8 | 0 | 0 | 0.50965 | 17837.75 | 0.23934 | 3350.76 | 40000 | 0 | 15908.8 | 1928.95 | 0 | 3350.76 | 5279.71 | 0 | 0 | 0 | 0
2022050221 | 2 | 0.68284 | 54627.2 | 0 | 0 | 0.47634 | 16671.9 | 0.00888 | 124.32 | 40000 | 0 | 14627.2 | 2044.7 | 0 | 124.32 | 2169.02 | 0 | 0 | 0 | 0
2022050222 | 2 | 0.6687 | 53496 | 0 | 0 | 0.49396 | 17288.6 | 0 | 0 | 40000 | 0 | 13496 | 3792.6 | 0 | 0 | 3792.6 | 0 | 0 | 0 | 0
2022050223 | 2 | 0.63067 | 50453.6 | 0 | 0 | 0.55812 | 19534.2 | 0 | 0 | 40000 | 0 | 10453.6 | 9080.6 | 0 | 0 | 9080.6 | 0 | 0 | 0 | 0
2022050224 | 2 | 0.59053 | 47242.4 | 0 | 0 | 0.62222 | 21777.7 | 0 | 0 | 40000 | 0 | 7242.4 | 14535.3 | 0 | 0 | 14535.3 | 0 | 0 | 0 | 0
2022050301 | 3 | 0.55818 | 44654.4 | 0 | 0 | 0.6331 | 22158.5 | 0 | 0 | 40000 | 0 | 4654.4 | 17504.1 | 0 | 0 | 17504.1 | 0 | 0 | 0 | 0
2022050302 | 3 | 0.53052 | 42441.6 | 0 | 0 | 0.62304 | 21806.4 | 0 | 0 | 40000 | 0 | 2441.6 | 19364.8 | 0 | 0 | 19364.8 | 0 | 0 | 0 | 0
2022050303 | 3 | 0.50887 | 40709.6 | 0 | 0 | 0.60882 | 21308.7 | 0 | 0 | 40000 | 0 | 709.6 | 20599.1 | 0 | 0 | 20599.1 | 0 | 0 | 0 | 0
2022050304 | 3 | 0.49745 | 39796 | 0 | 0 | 0.5743 | 20100.5 | 0 | 0 | 39796 | 204 | 0 | 20100.5 | 0 | 0 | 20304.5 | 0 | 0 | 0 | 0
2022050305 | 3 | 0.4975 | 39800 | 0 | 0 | 0.51349 | 17972.15 | 0 | 0 | 39800 | 200 | 0 | 17972.15 | 0 | 0 | 18172.15 | 0 | 0 | 0 | 0
2022050306 | 3 | 0.51069 | 40855.2 | 0 | 0 | 0.47625 | 16668.75 | 0 | 0 | 40000 | 0 | 855.2 | 15813.55 | 0 | 0 | 15813.55 | 0 | 0 | 0 | 0
2022050307 | 3 | 0.53921 | 43136.8 | 0 | 0 | 0.45268 | 15843.8 | 8e-05 | 1.12 | 40000 | 0 | 3136.8 | 12707 | 0 | 1.12 | 12708.12 | 0 | 0 | 0 | 0
2022050308 | 3 | 0.54943 | 43954.4 | 0 | 0 | 0.43031 | 15060.85 | 0.04889 | 684.46 | 40000 | 0 | 3954.4 | 11106.45 | 0 | 684.46 | 11790.91 | 0 | 0 | 0 | 0
2022050309 | 3 | 0.55966 | 44772.8 | 0 | 0 | 0.41438 | 14503.3 | 0.27774 | 3888.36 | 40000 | 0 | 4772.8 | 9730.5 | 0 | 3888.36 | 13618.86 | 0 | 0 | 0 | 0
2022050310 | 3 | 0.57177 | 45741.6 | 0 | 0 | 0.34732 | 12156.2 | 0.39924 | 5589.36 | 40000 | 0 | 5741.6 | 6414.6 | 0 | 5589.36 | 12003.96 | 0 | 0 | 0 | 0
2022050311 | 3 | 0.58435 | 46748 | 0 | 0 | 0.25855 | 9049.25 | 0.44975 | 6296.5 | 40000 | 0 | 6748 | 2301.25 | 0 | 6296.5 | 8597.75 | 0 | 0 | 0 | 0
2022050312 | 3 | 0.59983 | 47986.4 | 0 | 0 | 0.19987 | 6995.45 | 0.56149 | 7860.86 | 40000 | 0 | 6995.45 | 0 | 990.95 | 6869.91 | 6869.91 | 0 | 0 | 0 | 0
2022050313 | 3 | 0.61514 | 49211.2 | 0 | 0 | 0.16078 | 5627.3 | 0.62879 | 8803.06 | 40000 | 0 | 5627.3 | 0 | 3583.9 | 5219.16 | 5219.16 | 0 | 0 | 0 | 0
2022050314 | 3 | 0.63099 | 50479.2 | 0 | 0 | 0.14446 | 5056.1 | 0.66901 | 9366.14 | 40000 | 0 | 5056.1 | 0 | 5423.1 | 3943.04 | 3943.04 | 0 | 0 | 0 | 0
2022050315 | 3 | 0.64512 | 51609.6 | 0 | 0 | 0.14452 | 5058.2 | 0.66909 | 9367.26 | 40000 | 0 | 5058.2 | 0 | 6551.4 | 2815.86 | 2815.86 | 0 | 0 | 0 | 0
2022050316 | 3 | 0.65967 | 52773.6 | 0 | 0 | 0.15044 | 5265.4 | 0.62661 | 8772.54 | 40000 | 0 | 5265.4 | 0 | 7508.2 | 1264.34 | 1264.34 | 0 | 0 | 0 | 0
2022050317 | 3 | 0.67415 | 53932 | 0 | 0 | 0.18519 | 6481.65 | 0.54882 | 7683.48 | 40000 | 0 | 6481.65 | 0 | 7450.35 | 233.13 | 233.13 | 0 | 0 | 0 | 0
2022050318 | 3 | 0.67678 | 54142.4 | 0 | 0 | 0.23239 | 8133.65 | 0.38972 | 5456.08 | 40000 | 0 | 8133.65 | 0 | 5456.08 | 0 | 0 | 552.67 | 0 | 0 | 552.67
2022050319 | 3 | 0.66436 | 53148.8 | 0 | 0 | 0.26658 | 9330.3 | 0.21437 | 3001.18 | 40000 | 0 | 9330.3 | 0 | 3001.18 | 0 | 0 | 817.32 | 0 | 0 | 817.32
2022050320 | 3 | 0.64747 | 51797.6 | 0 | 0 | 0.29656 | 10379.6 | 0.06538 | 915.32 | 40000 | 0 | 10379.6 | 0 | 915.32 | 0 | 0 | 502.68 | 0 | 0 | 502.68
2022050321 | 3 | 0.64221 | 51376.8 | 0 | 0 | 0.32015 | 11205.25 | 0.00368 | 51.52 | 40000 | 0 | 11205.25 | 0 | 51.52 | 0 | 0 | 120.03 | 0 | 0 | 120.03
2022050322 | 3 | 0.62139 | 49711.2 | 0 | 0 | 0.33902 | 11865.7 | 0.00241 | 33.74 | 40000 | 0 | 9711.2 | 2154.5 | 0 | 33.74 | 2188.24 | 0 | 0 | 0 | 0
2022050323 | 3 | 0.58665 | 46932 | 0 | 0 | 0.36487 | 12770.45 | 0.00241 | 33.74 | 40000 | 0 | 6932 | 5838.45 | 0 | 33.74 | 5872.19 | 0 | 0 | 0 | 0
2022050324 | 3 | 0.5457 | 43656 | 0 | 0 | 0.37302 | 13055.7 | 0.0002 | 2.8 | 40000 | 0 | 3656 | 9399.7 | 0 | 2.8 | 9402.5 | 0 | 0 | 0 | 0
2022050401 | 4 | 0.51324 | 41059.2 | 0 | 0 | 0.37707 | 13197.45 | 0 | 0 | 40000 | 0 | 1059.2 | 12138.25 | 0 | 0 | 12138.25 | 0 | 0 | 0 | 0
2022050402 | 4 | 0.49309 | 39447.2 | 0 | 0 | 0.39989 | 13996.15 | 0 | 0 | 39447.2 | 552.8 | 0 | 13996.15 | 0 | 0 | 14548.95 | 0 | 0 | 0 | 0
2022050403 | 4 | 0.48072 | 38457.6 | 0 | 0 | 0.40668 | 14233.8 | 0 | 0 | 38457.6 | 1542.4 | 0 | 14233.8 | 0 | 0 | 15776.2 | 0 | 0 | 0 | 0
2022050404 | 4 | 0.47501 | 38000.8 | 0 | 0 | 0.38766 | 13568.1 | 0 | 0 | 38000.8 | 1999.2 | 0 | 13568.1 | 0 | 0 | 15567.3 | 0 | 0 | 0 | 0
2022050405 | 4 | 0.47762 | 38209.6 | 0 | 0 | 0.37483 | 13119.05 | 0 | 0 | 38209.6 | 1790.4 | 0 | 13119.05 | 0 | 0 | 14909.45 | 0 | 0 | 0 | 0
2022050406 | 4 | 0.49692 | 39753.6 | 0 | 0 | 0.36449 | 12757.15 | 0 | 0 | 39753.6 | 246.4 | 0 | 12757.15 | 0 | 0 | 13003.55 | 0 | 0 | 0 | 0
2022050407 | 4 | 0.5296 | 42368 | 0 | 0 | 0.35896 | 12563.6 | 0.0001 | 1.4 | 40000 | 0 | 2368 | 10195.6 | 0 | 1.4 | 10197 | 0 | 0 | 0 | 0
2022050408 | 4 | 0.54461 | 43568.8 | 0 | 0 | 0.34029 | 11910.15 | 0.02063 | 288.82 | 40000 | 0 | 3568.8 | 8341.35 | 0 | 288.82 | 8630.17 | 0 | 0 | 0 | 0
2022050409 | 4 | 0.55838 | 44670.4 | 0 | 0 | 0.35444 | 12405.4 | 0.13909 | 1947.26 | 40000 | 0 | 4670.4 | 7735 | 0 | 1947.26 | 9682.26 | 0 | 0 | 0 | 0
2022050410 | 4 | 0.57869 | 46295.2 | 0 | 0 | 0.37063 | 12972.05 | 0.31755 | 4445.7 | 40000 | 0 | 6295.2 | 6676.85 | 0 | 4445.7 | 11122.55 | 0 | 0 | 0 | 0
2022050411 | 4 | 0.60507 | 48405.6 | 0 | 0 | 0.40557 | 14194.95 | 0.44845 | 6278.3 | 40000 | 0 | 8405.6 | 5789.35 | 0 | 6278.3 | 12067.65 | 0 | 0 | 0 | 0
2022050412 | 4 | 0.63347 | 50677.6 | 0 | 0 | 0.44934 | 15726.9 | 0.47599 | 6663.86 | 40000 | 0 | 10677.6 | 5049.3 | 0 | 6663.86 | 11713.16 | 0 | 0 | 0 | 0
2022050413 | 4 | 0.66077 | 52861.6 | 0 | 0 | 0.49012 | 17154.2 | 0.5644 | 7901.6 | 40000 | 0 | 12861.6 | 4292.6 | 0 | 7901.6 | 12194.2 | 0 | 0 | 0 | 0
2022050414 | 4 | 0.68647 | 54917.6 | 0 | 0 | 0.50653 | 17728.55 | 0.58858 | 8240.12 | 40000 | 0 | 14917.6 | 2810.95 | 0 | 8240.12 | 11051.07 | 0 | 0 | 0 | 0
2022050415 | 4 | 0.71163 | 56930.4 | 0 | 0 | 0.51931 | 18175.85 | 0.58311 | 8163.54 | 40000 | 0 | 16930.4 | 1245.45 | 0 | 8163.54 | 9408.99 | 0 | 0 | 0 | 0
2022050416 | 4 | 0.7277 | 58216 | 0 | 0 | 0.54521 | 19082.35 | 0.57268 | 8017.52 | 40000 | 0 | 18216 | 866.35 | 0 | 8017.52 | 8883.87 | 0 | 0 | 0 | 0
2022050417 | 4 | 0.73733 | 58986.4 | 0 | 0 | 0.56006 | 19602.1 | 0.44384 | 6213.76 | 40000 | 0 | 18986.4 | 615.7 | 0 | 6213.76 | 6829.46 | 0 | 0 | 0 | 0
2022050418 | 4 | 0.73865 | 59092 | 0 | 0 | 0.58005 | 20301.75 | 0.37571 | 5259.94 | 40000 | 0 | 19092 | 1209.75 | 0 | 5259.94 | 6469.69 | 0 | 0 | 0 | 0
2022050419 | 4 | 0.72452 | 57961.6 | 0 | 0 | 0.61083 | 21379.05 | 0.2978 | 4169.2 | 40000 | 0 | 17961.6 | 3417.45 | 0 | 4169.2 | 7586.65 | 0 | 0 | 0 | 0
2022050420 | 4 | 0.70257 | 56205.6 | 0 | 0 | 0.61396 | 21488.6 | 0.11885 | 1663.9 | 40000 | 0 | 16205.6 | 5283 | 0 | 1663.9 | 6946.9 | 0 | 0 | 0 | 0
2022050421 | 4 | 0.69122 | 55297.6 | 0 | 0 | 0.58658 | 20530.3 | 0.00755 | 105.7 | 40000 | 0 | 15297.6 | 5232.7 | 0 | 105.7 | 5338.4 | 0 | 0 | 0 | 0
2022050422 | 4 | 0.67271 | 53816.8 | 0 | 0 | 0.60751 | 21262.85 | 0 | 0 | 40000 | 0 | 13816.8 | 7446.05 | 0 | 0 | 7446.05 | 0 | 0 | 0 | 0
2022050423 | 4 | 0.63768 | 51014.4 | 0 | 0 | 0.5907 | 20674.5 | 0 | 0 | 40000 | 0 | 11014.4 | 9660.1 | 0 | 0 | 9660.1 | 0 | 0 | 0 | 0
2022050424 | 4 | 0.59452 | 47561.6 | 0 | 0 | 0.59511 | 20828.85 | 0 | 0 | 40000 | 0 | 7561.6 | 13267.25 | 0 | 0 | 13267.25 | 0 | 0 | 0 | 0
2022050501 | 5 | 0.55927 | 44741.6 | 0 | 0 | 0.58186 | 20365.1 | 0 | 0 | 40000 | 0 | 4741.6 | 15623.5 | 0 | 0 | 15623.5 | 0 | 0 | 0 | 0
2022050502 | 5 | 0.53414 | 42731.2 | 0 | 0 | 0.59988 | 20995.8 | 0 | 0 | 40000 | 0 | 2731.2 | 18264.6 | 0 | 0 | 18264.6 | 0 | 0 | 0 | 0
2022050503 | 5 | 0.51665 | 41332 | 0 | 0 | 0.60291 | 21101.85 | 0 | 0 | 40000 | 0 | 1332 | 19769.85 | 0 | 0 | 19769.85 | 0 | 0 | 0 | 0
2022050504 | 5 | 0.50722 | 40577.6 | 0 | 0 | 0.59284 | 20749.4 | 0 | 0 | 40000 | 0 | 577.6 | 20171.8 | 0 | 0 | 20171.8 | 0 | 0 | 0 | 0
2022050505 | 5 | 0.50797 | 40637.6 | 0 | 0 | 0.56607 | 19812.45 | 0 | 0 | 40000 | 0 | 637.6 | 19174.85 | 0 | 0 | 19174.85 | 0 | 0 | 0 | 0
2022050506 | 5 | 0.52719 | 42175.2 | 0 | 0 | 0.4919 | 17216.5 | 0 | 0 | 40000 | 0 | 2175.2 | 15041.3 | 0 | 0 | 15041.3 | 0 | 0 | 0 | 0
2022050507 | 5 | 0.55758 | 44606.4 | 0 | 0 | 0.45925 | 16073.75 | 0.00013 | 1.82 | 40000 | 0 | 4606.4 | 11467.35 | 0 | 1.82 | 11469.17 | 0 | 0 | 0 | 0
2022050508 | 5 | 0.57157 | 45725.6 | 0 | 0 | 0.44239 | 15483.65 | 0.04245 | 594.3 | 40000 | 0 | 5725.6 | 9758.05 | 0 | 594.3 | 10352.35 | 0 | 0 | 0 | 0
2022050509 | 5 | 0.5862 | 46896 | 0 | 0 | 0.44541 | 15589.35 | 0.25972 | 3636.08 | 40000 | 0 | 6896 | 8693.35 | 0 | 3636.08 | 12329.43 | 0 | 0 | 0 | 0
2022050510 | 5 | 0.60415 | 48332 | 0 | 0 | 0.47524 | 16633.4 | 0.42443 | 5942.02 | 40000 | 0 | 8332 | 8301.4 | 0 | 5942.02 | 14243.42 | 0 | 0 | 0 | 0
2022050511 | 5 | 0.63221 | 50576.8 | 0 | 0 | 0.49551 | 17342.85 | 0.5524 | 7733.6 | 40000 | 0 | 10576.8 | 6766.05 | 0 | 7733.6 | 14499.65 | 0 | 0 | 0 | 0
2022050512 | 5 | 0.65007 | 52005.6 | 0 | 0 | 0.45704 | 15996.4 | 0.59827 | 8375.78 | 40000 | 0 | 12005.6 | 3990.8 | 0 | 8375.78 | 12366.58 | 0 | 0 | 0 | 0
2022050513 | 5 | 0.66764 | 53411.2 | 0 | 0 | 0.43403 | 15191.05 | 0.61887 | 8664.18 | 40000 | 0 | 13411.2 | 1779.85 | 0 | 8664.18 | 10444.03 | 0 | 0 | 0 | 0
2022050514 | 5 | 0.67788 | 54230.4 | 0 | 0 | 0.42446 | 14856.1 | 0.61092 | 8552.88 | 40000 | 0 | 14230.4 | 625.7 | 0 | 8552.88 | 9178.58 | 0 | 0 | 0 | 0
2022050515 | 5 | 0.67952 | 54361.6 | 0 | 0 | 0.40656 | 14229.6 | 0.60516 | 8472.24 | 40000 | 0 | 14229.6 | 0 | 132 | 8340.24 | 8340.24 | 0 | 0 | 0 | 0
2022050516 | 5 | 0.68028 | 54422.4 | 0 | 0 | 0.39912 | 13969.2 | 0.60485 | 8467.9 | 40000 | 0 | 13969.2 | 0 | 453.2 | 8014.7 | 8014.7 | 0 | 0 | 0 | 0
2022050517 | 5 | 0.69149 | 55319.2 | 0 | 0 | 0.41066 | 14373.1 | 0.56587 | 7922.18 | 40000 | 0 | 14373.1 | 0 | 946.1 | 6976.08 | 6976.08 | 0 | 0 | 0 | 0
2022050518 | 5 | 0.69113 | 55290.4 | 0 | 0 | 0.40184 | 14064.4 | 0.54505 | 7630.7 | 40000 | 0 | 14064.4 | 0 | 1226 | 6404.7 | 6404.7 | 0 | 0 | 0 | 0
2022050519 | 5 | 0.67827 | 54261.6 | 0 | 0 | 0.34116 | 11940.6 | 0.56365 | 7891.1 | 40000 | 0 | 11940.6 | 0 | 2321 | 5570.1 | 5570.1 | 0 | 0 | 0 | 0
2022050520 | 5 | 0.65302 | 52241.6 | 0 | 0 | 0.23346 | 8171.1 | 0.25728 | 3601.92 | 40000 | 0 | 8171.1 | 0 | 3601.92 | 0 | 0 | 468.58 | 0 | 0 | 468.58
2022050521 | 5 | 0.63112 | 50489.6 | 0 | 0 | 0.13708 | 4797.8 | 0.01078 | 150.92 | 40000 | 0 | 4797.8 | 0 | 150.92 | 0 | 0 | 5540.88 | 0 | 0 | 5540.88
2022050522 | 5 | 0.60574 | 48459.2 | 0 | 0 | 0.11516 | 4030.6 | 0 | 0 | 40000 | 0 | 4030.6 | 0 | 0 | 0 | 0 | 4428.6 | 0 | 0 | 4428.6
2022050523 | 5 | 0.56587 | 45269.6 | 0 | 0 | 0.11419 | 3996.65 | 0 | 0 | 40000 | 0 | 3996.65 | 0 | 0 | 0 | 0 | 1272.95 | 0 | 0 | 1272.95
2022050524 | 5 | 0.52431 | 41944.8 | 0 | 0 | 0.13614 | 4764.9 | 0 | 0 | 40000 | 0 | 1944.8 | 2820.1 | 0 | 0 | 2820.1 | 0 | 0 | 0 | 0
2022050601 | 6 | 0.49139 | 39311.2 | 0 | 0 | 0.18087 | 6330.45 | 0 | 0 | 39311.2 | 688.8 | 0 | 6330.45 | 0 | 0 | 7019.25 | 0 | 0 | 0 | 0
2022050602 | 6 | 0.46902 | 37521.6 | 0 | 0 | 0.2324 | 8134 | 0 | 0 | 37521.6 | 2478.4 | 0 | 8134 | 0 | 0 | 10612.4 | 0 | 0 | 0 | 0
2022050603 | 6 | 0.45872 | 36697.6 | 0 | 0 | 0.31305 | 10956.75 | 0 | 0 | 36697.6 | 3302.4 | 0 | 10956.75 | 0 | 0 | 14259.15 | 0 | 0 | 0 | 0
2022050604 | 6 | 0.45081 | 36064.8 | 0 | 0 | 0.3373 | 11805.5 | 0 | 0 | 36064.8 | 3935.2 | 0 | 11805.5 | 0 | 0 | 15740.7 | 0 | 0 | 0 | 0
2022050605 | 6 | 0.45192 | 36153.6 | 0 | 0 | 0.33449 | 11707.15 | 0 | 0 | 36153.6 | 3846.4 | 0 | 11707.15 | 0 | 0 | 15553.55 | 0 | 0 | 0 | 0
2022050606 | 6 | 0.4664 | 37312 | 0 | 0 | 0.31893 | 11162.55 | 0 | 0 | 37312 | 2688 | 0 | 11162.55 | 0 | 0 | 13850.55 | 0 | 0 | 0 | 0
2022050607 | 6 | 0.49392 | 39513.6 | 0 | 0 | 0.28013 | 9804.55 | 0.00134 | 18.76 | 39513.6 | 486.4 | 0 | 9804.55 | 0 | 18.76 | 10309.71 | 0 | 0 | 0 | 0
2022050608 | 6 | 0.51099 | 40879.2 | 0 | 0 | 0.22143 | 7750.05 | 0.14325 | 2005.5 | 40000 | 0 | 879.2 | 6870.85 | 0 | 2005.5 | 8876.35 | 0 | 0 | 0 | 0
2022050609 | 6 | 0.53028 | 42422.4 | 0 | 0 | 0.17113 | 5989.55 | 0.56588 | 7922.32 | 40000 | 0 | 2422.4 | 3567.15 | 0 | 7922.32 | 11489.47 | 0 | 0 | 0 | 0
2022050610 | 6 | 0.55383 | 44306.4 | 0 | 0 | 0.17219 | 6026.65 | 0.73426 | 10279.64 | 40000 | 0 | 4306.4 | 1720.25 | 0 | 10279.64 | 11999.89 | 0 | 0 | 0 | 0
2022050611 | 6 | 0.58538 | 46830.4 | 0 | 0 | 0.19524 | 6833.4 | 0.76672 | 10734.08 | 40000 | 0 | 6830.4 | 3 | 0 | 10734.08 | 10737.08 | 0 | 0 | 0 | 0
2022050612 | 6 | 0.62131 | 49704.8 | 0 | 0 | 0.1946 | 6811 | 0.78082 | 10931.48 | 40000 | 0 | 6811 | 0 | 2893.8 | 8037.68 | 8037.68 | 0 | 0 | 0 | 0
2022050613 | 6 | 0.65871 | 52696.8 | 0 | 0 | 0.17436 | 6102.6 | 0.78099 | 10933.86 | 40000 | 0 | 6102.6 | 0 | 6594.2 | 4339.66 | 4339.66 | 0 | 0 | 0 | 0
2022050614 | 6 | 0.69664 | 55731.2 | 0 | 0 | 0.15847 | 5546.45 | 0.77851 | 10899.14 | 40000 | 0 | 5546.45 | 0 | 10184.75 | 714.39 | 714.39 | 0 | 0 | 0 | 0
2022050615 | 6 | 0.73088 | 58470.4 | 0 | 0 | 0.18195 | 6368.25 | 0.77481 | 10847.34 | 40000 | 0 | 6368.25 | 0 | 10847.34 | 0 | 0 | 1254.81 | 0 | 0 | 1254.81
2022050616 | 6 | 0.75858 | 60686.4 | 0 | 0 | 0.19714 | 6899.9 | 0.76571 | 10719.94 | 40000 | 0 | 6899.9 | 0 | 10719.94 | 0 | 0 | 3066.56 | 0 | 0 | 3066.56
2022050617 | 6 | 0.77959 | 62367.2 | 0 | 0 | 0.21491 | 7521.85 | 0.74599 | 10443.86 | 40000 | 0 | 7521.85 | 0 | 10443.86 | 0 | 0 | 4401.49 | 0 | 0 | 4401.49
2022050618 | 6 | 0.78639 | 62911.2 | 0 | 0 | 0.22473 | 7865.55 | 0.73064 | 10228.96 | 40000 | 0 | 7865.55 | 0 | 10228.96 | 0 | 0 | 4816.69 | 0 | 0 | 4816.69
2022050619 | 6 | 0.76229 | 60983.2 | 0 | 0 | 0.24275 | 8496.25 | 0.55275 | 7738.5 | 40000 | 0 | 8496.25 | 0 | 7738.5 | 0 | 0 | 4748.45 | 0 | 0 | 4748.45
2022050620 | 6 | 0.72958 | 58366.4 | 0 | 0 | 0.25844 | 9045.4 | 0.20067 | 2809.38 | 40000 | 0 | 9045.4 | 0 | 2809.38 | 0 | 0 | 6511.62 | 0 | 0 | 6511.62
2022050621 | 6 | 0.70547 | 56437.6 | 0 | 0 | 0.27587 | 9655.45 | 0.00873 | 122.22 | 40000 | 0 | 9655.45 | 0 | 122.22 | 0 | 0 | 6659.93 | 0 | 0 | 6659.93
2022050622 | 6 | 0.68007 | 54405.6 | 0 | 0 | 0.32484 | 11369.4 | 0 | 0 | 40000 | 0 | 11369.4 | 0 | 0 | 0 | 0 | 3036.2 | 0 | 0 | 3036.2
2022050623 | 6 | 0.64415 | 51532 | 0 | 0 | 0.36836 | 12892.6 | 0 | 0 | 40000 | 0 | 11532 | 1360.6 | 0 | 0 | 1360.6 | 0 | 0 | 0 | 0
2022050624 | 6 | 0.60468 | 48374.4 | 0 | 0 | 0.42392 | 14837.2 | 0 | 0 | 40000 | 0 | 8374.4 | 6462.8 | 0 | 0 | 6462.8 | 0 | 0 | 0 | 0
2022050701 | 7 | 0.56579 | 45263.2 | 0 | 0 | 0.43776 | 15321.6 | 0 | 0 | 40000 | 0 | 5263.2 | 10058.4 | 0 | 0 | 10058.4 | 0 | 0 | 0 | 0
2022050702 | 7 | 0.5373 | 42984 | 0 | 0 | 0.4633 | 16215.5 | 0 | 0 | 40000 | 0 | 2984 | 13231.5 | 0 | 0 | 13231.5 | 0 | 0 | 0 | 0
2022050703 | 7 | 0.5138 | 41104 | 0 | 0 | 0.44661 | 15631.35 | 0 | 0 | 40000 | 0 | 1104 | 14527.35 | 0 | 0 | 14527.35 | 0 | 0 | 0 | 0
2022050704 | 7 | 0.5003 | 40024 | 0 | 0 | 0.42693 | 14942.55 | 0 | 0 | 40000 | 0 | 24 | 14918.55 | 0 | 0 | 14918.55 | 0 | 0 | 0 | 0
2022050705 | 7 | 0.4924 | 39392 | 0 | 0 | 0.42408 | 14842.8 | 0 | 0 | 39392 | 608 | 0 | 14842.8 | 0 | 0 | 15450.8 | 0 | 0 | 0 | 0
2022050706 | 7 | 0.49389 | 39511.2 | 0 | 0 | 0.42374 | 14830.9 | 0 | 0 | 39511.2 | 488.8 | 0 | 14830.9 | 0 | 0 | 15319.7 | 0 | 0 | 0 | 0
2022050707 | 7 | 0.5018 | 40144 | 0 | 0 | 0.4101 | 14353.5 | 0.00074 | 10.36 | 40000 | 0 | 144 | 14209.5 | 0 | 10.36 | 14219.86 | 0 | 0 | 0 | 0
2022050708 | 7 | 0.51073 | 40858.4 | 0 | 0 | 0.38186 | 13365.1 | 0.10684 | 1495.76 | 40000 | 0 | 858.4 | 12506.7 | 0 | 1495.76 | 14002.46 | 0 | 0 | 0 | 0
2022050709 | 7 | 0.53961 | 43168.8 | 0 | 0 | 0.3158 | 11053 | 0.4981 | 6973.4 | 40000 | 0 | 3168.8 | 7884.2 | 0 | 6973.4 | 14857.6 | 0 | 0 | 0 | 0
2022050710 | 7 | 0.57692 | 46153.6 | 0 | 0 | 0.25932 | 9076.2 | 0.67624 | 9467.36 | 40000 | 0 | 6153.6 | 2922.6 | 0 | 9467.36 | 12389.96 | 0 | 0 | 0 | 0
2022050711 | 7 | 0.61909 | 49527.2 | 0 | 0 | 0.23638 | 8273.3 | 0.71674 | 10034.36 | 40000 | 0 | 8273.3 | 0 | 1253.9 | 8780.46 | 8780.46 | 0 | 0 | 0 | 0
2022050712 | 7 | 0.66019 | 52815.2 | 0 | 0 | 0.2226 | 7791 | 0.76088 | 10652.32 | 40000 | 0 | 7791 | 0 | 5024.2 | 5628.12 | 5628.12 | 0 | 0 | 0 | 0
2022050713 | 7 | 0.70067 | 56053.6 | 0 | 0 | 0.24155 | 8454.25 | 0.773 | 10822 | 40000 | 0 | 8454.25 | 0 | 7599.35 | 3222.65 | 3222.65 | 0 | 0 | 0 | 0
2022050714 | 7 | 0.7395 | 59160 | 0 | 0 | 0.29221 | 10227.35 | 0.7758 | 10861.2 | 40000 | 0 | 10227.35 | 0 | 8932.65 | 1928.55 | 1928.55 | 0 | 0 | 0 | 0
2022050715 | 7 | 0.77375 | 61900 | 0 | 0 | 0.36747 | 12861.45 | 0.76099 | 10653.86 | 40000 | 0 | 12861.45 | 0 | 9038.55 | 1615.31 | 1615.31 | 0 | 0 | 0 | 0
2022050716 | 7 | 0.80226 | 64180.8 | 0 | 0 | 0.44139 | 15448.65 | 0.70096 | 9813.44 | 40000 | 0 | 15448.65 | 0 | 8732.15 | 1081.29 | 1081.29 | 0 | 0 | 0 | 0
2022050717 | 7 | 0.81939 | 65551.2 | 0 | 0 | 0.4877 | 17069.5 | 0.65577 | 9180.78 | 40000 | 0 | 17069.5 | 0 | 8481.7 | 699.08 | 699.08 | 0 | 0 | 0 | 0
2022050718 | 7 | 0.82261 | 65808.8 | 0 | 0 | 0.52848 | 18496.8 | 0.56354 | 7889.56 | 40000 | 0 | 18496.8 | 0 | 7312 | 577.56 | 577.56 | 0 | 0 | 0 | 0
2022050719 | 7 | 0.80748 | 64598.4 | 0 | 0 | 0.54551 | 19092.85 | 0.4716 | 6602.4 | 40000 | 0 | 19092.85 | 0 | 5505.55 | 1096.85 | 1096.85 | 0 | 0 | 0 | 0
2022050720 | 7 | 0.77693 | 62154.4 | 0 | 0 | 0.55638 | 19473.3 | 0.23488 | 3288.32 | 40000 | 0 | 19473.3 | 0 | 2681.1 | 607.22 | 607.22 | 0 | 0 | 0 | 0
2022050721 | 7 | 0.75138 | 60110.4 | 0 | 0 | 0.56377 | 19731.95 | 0.0113 | 158.2 | 40000 | 0 | 19731.95 | 0 | 158.2 | 0 | 0 | 220.25 | 0 | 0 | 220.25
2022050722 | 7 | 0.72598 | 58078.4 | 0 | 0 | 0.60109 | 21038.15 | 0 | 0 | 40000 | 0 | 18078.4 | 2959.75 | 0 | 0 | 2959.75 | 0 | 0 | 0 | 0
2022050723 | 7 | 0.69149 | 55319.2 | 0 | 0 | 0.63726 | 22304.1 | 0 | 0 | 40000 | 0 | 15319.2 | 6984.9 | 0 | 0 | 6984.9 | 0 | 0 | 0 | 0
2022050724 | 7 | 0.65414 | 52331.2 | 0 | 0 | 0.67332 | 23566.2 | 0 | 0 | 40000 | 0 | 12331.2 | 11235 | 0 | 0 | 11235 | 0 | 0 | 0 | 0
2022050801 | 1 | 0.61849 | 49479.2 | 0 | 0 | 0.6845 | 23957.5 | 0 | 0 | 40000 | 0 | 9479.2 | 14478.3 | 0 | 0 | 14478.3 | 0 | 0 | 0 | 0
2022050802 | 1 | 0.58801 | 47040.8 | 0 | 0 | 0.68422 | 23947.7 | 0 | 0 | 40000 | 0 | 7040.8 | 16906.9 | 0 | 0 | 16906.9 | 0 | 0 | 0 | 0
2022050803 | 1 | 0.56523 | 45218.4 | 0 | 0 | 0.67312 | 23559.2 | 0 | 0 | 40000 | 0 | 5218.4 | 18340.8 | 0 | 0 | 18340.8 | 0 | 0 | 0 | 0
2022050804 | 1 | 0.55104 | 44083.2 | 0 | 0 | 0.65503 | 22926.05 | 0 | 0 | 40000 | 0 | 4083.2 | 18842.85 | 0 | 0 | 18842.85 | 0 | 0 | 0 | 0
2022050805 | 1 | 0.53571 | 42856.8 | 0 | 0 | 0.64123 | 22443.05 | 0 | 0 | 40000 | 0 | 2856.8 | 19586.25 | 0 | 0 | 19586.25 | 0 | 0 | 0 | 0
2022050806 | 1 | 0.52971 | 42376.8 | 0 | 0 | 0.62582 | 21903.7 | 0 | 0 | 40000 | 0 | 2376.8 | 19526.9 | 0 | 0 | 19526.9 | 0 | 0 | 0 | 0
2022050807 | 1 | 0.52947 | 42357.6 | 0 | 0 | 0.61272 | 21445.2 | 0.00044 | 6.16 | 40000 | 0 | 2357.6 | 19087.6 | 0 | 6.16 | 19093.76 | 0 | 0 | 0 | 0
2022050808 | 1 | 0.53405 | 42724 | 0 | 0 | 0.59816 | 20935.6 | 0.10928 | 1529.92 | 40000 | 0 | 2724 | 18211.6 | 0 | 1529.92 | 19741.52 | 0 | 0 | 0 | 0
2022050809 | 1 | 0.56568 | 45254.4 | 0 | 0 | 0.52538 | 18388.3 | 0.48112 | 6735.68 | 40000 | 0 | 5254.4 | 13133.9 | 0 | 6735.68 | 19869.58 | 0 | 0 | 0 | 0
2022050810 | 1 | 0.61133 | 48906.4 | 0 | 0 | 0.49307 | 17257.45 | 0.70078 | 9810.92 | 40000 | 0 | 8906.4 | 8351.05 | 0 | 9810.92 | 18161.97 | 0 | 0 | 0 | 0
2022050811 | 1 | 0.6568 | 52544 | 0 | 0 | 0.45962 | 16086.7 | 0.76146 | 10660.44 | 40000 | 0 | 12544 | 3542.7 | 0 | 10660.44 | 14203.14 | 0 | 0 | 0 | 0
2022050812 | 1 | 0.69551 | 55640.8 | 0 | 0 | 0.40271 | 14094.85 | 0.78897 | 11045.58 | 40000 | 0 | 14094.85 | 0 | 1545.95 | 9499.63 | 9499.63 | 0 | 0 | 0 | 0
2022050813 | 1 | 0.73494 | 58795.2 | 0 | 0 | 0.36525 | 12783.75 | 0.79454 | 11123.56 | 40000 | 0 | 12783.75 | 0 | 6011.45 | 5112.11 | 5112.11 | 0 | 0 | 0 | 0
2022050814 | 1 | 0.77003 | 61602.4 | 0 | 0 | 0.38748 | 13561.8 | 0.79379 | 11113.06 | 40000 | 0 | 13561.8 | 0 | 8040.6 | 3072.46 | 3072.46 | 0 | 0 | 0 | 0
2022050815 | 1 | 0.80229 | 64183.2 | 0 | 0 | 0.44222 | 15477.7 | 0.78537 | 10995.18 | 40000 | 0 | 15477.7 | 0 | 8705.5 | 2289.68 | 2289.68 | 0 | 0 | 0 | 0
2022050816 | 1 | 0.82674 | 66139.2 | 0 | 0 | 0.49903 | 17466.05 | 0.76772 | 10748.08 | 40000 | 0 | 17466.05 | 0 | 8673.15 | 2074.93 | 2074.93 | 0 | 0 | 0 | 0
2022050817 | 1 | 0.84256 | 67404.8 | 0 | 0 | 0.53681 | 18788.35 | 0.73152 | 10241.28 | 40000 | 0 | 18788.35 | 0 | 8616.45 | 1624.83 | 1624.83 | 0 | 0 | 0 | 0
2022050818 | 1 | 0.84517 | 67613.6 | 0 | 0 | 0.55865 | 19552.75 | 0.66326 | 9285.64 | 40000 | 0 | 19552.75 | 0 | 8060.85 | 1224.79 | 1224.79 | 0 | 0 | 0 | 0
2022050819 | 1 | 0.82863 | 66290.4 | 0 | 0 | 0.57522 | 20132.7 | 0.55133 | 7718.62 | 40000 | 0 | 20132.7 | 0 | 6157.7 | 1560.92 | 1560.92 | 0 | 0 | 0 | 0
2022050820 | 1 | 0.79692 | 63753.6 | 0 | 0 | 0.58443 | 20455.05 | 0.25834 | 3616.76 | 40000 | 0 | 20455.05 | 0 | 3298.55 | 318.21 | 318.21 | 0 | 0 | 0 | 0
2022050821 | 1 | 0.77442 | 61953.6 | 0 | 0 | 0.57769 | 20219.15 | 0.0156 | 218.4 | 40000 | 0 | 20219.15 | 0 | 218.4 | 0 | 0 | 1516.05 | 0 | 0 | 1516.05
2022050822 | 1 | 0.75156 | 60124.8 | 0 | 0 | 0.61896 | 21663.6 | 0 | 0 | 40000 | 0 | 20124.8 | 1538.8 | 0 | 0 | 1538.8 | 0 | 0 | 0 | 0
2022050823 | 1 | 0.70732 | 56585.6 | 0 | 0 | 0.65186 | 22815.1 | 0 | 0 | 40000 | 0 | 16585.6 | 6229.5 | 0 | 0 | 6229.5 | 0 | 0 | 0 | 0
2022050824 | 1 | 0.65973 | 52778.4 | 0 | 0 | 0.65464 | 22912.4 | 0 | 0 | 40000 | 0 | 12778.4 | 10134 | 0 | 0 | 10134 | 0 | 0 | 0 | 0
2022050901 | 2 | 0.61797 | 49437.6 | 0 | 0 | 0.65105 | 22786.75 | 0 | 0 | 40000 | 0 | 9437.6 | 13349.15 | 0 | 0 | 13349.15 | 0 | 0 | 0 | 0
2022050902 | 2 | 0.58835 | 47068 | 0 | 0 | 0.6515 | 22802.5 | 0 | 0 | 40000 | 0 | 7068 | 15734.5 | 0 | 0 | 15734.5 | 0 | 0 | 0 | 0
2022050903 | 2 | 0.56913 | 45530.4 | 0 | 0 | 0.65655 | 22979.25 | 0 | 0 | 40000 | 0 | 5530.4 | 17448.85 | 0 | 0 | 17448.85 | 0 | 0 | 0 | 0
2022050904 | 2 | 0.56021 | 44816.8 | 0 | 0 | 0.65041 | 22764.35 | 0 | 0 | 40000 | 0 | 4816.8 | 17947.55 | 0 | 0 | 17947.55 | 0 | 0 | 0 | 0
2022050905 | 2 | 0.55986 | 44788.8 | 0 | 0 | 0.63458 | 22210.3 | 0 | 0 | 40000 | 0 | 4788.8 | 17421.5 | 0 | 0 | 17421.5 | 0 | 0 | 0 | 0
2022050906 | 2 | 0.57602 | 46081.6 | 0 | 0 | 0.61991 | 21696.85 | 0 | 0 | 40000 | 0 | 6081.6 | 15615.25 | 0 | 0 | 15615.25 | 0 | 0 | 0 | 0
2022050907 | 2 | 0.60409 | 48327.2 | 0 | 0 | 0.61436 | 21502.6 | 0.00035 | 4.9 | 40000 | 0 | 8327.2 | 13175.4 | 0 | 4.9 | 13180.3 | 0 | 0 | 0 | 0
2022050908 | 2 | 0.61902 | 49521.6 | 0 | 0 | 0.58939 | 20628.65 | 0.10012 | 1401.68 | 40000 | 0 | 9521.6 | 11107.05 | 0 | 1401.68 | 12508.73 | 0 | 0 | 0 | 0
2022050909 | 2 | 0.63711 | 50968.8 | 0 | 0 | 0.56768 | 19868.8 | 0.39774 | 5568.36 | 40000 | 0 | 10968.8 | 8900 | 0 | 5568.36 | 14468.36 | 0 | 0 | 0 | 0
2022050910 | 2 | 0.66844 | 53475.2 | 0 | 0 | 0.57437 | 20102.95 | 0.46712 | 6539.68 | 40000 | 0 | 13475.2 | 6627.75 | 0 | 6539.68 | 13167.43 | 0 | 0 | 0 | 0
2022050911 | 2 | 0.70638 | 56510.4 | 0 | 0 | 0.56298 | 19704.3 | 0.59891 | 8384.74 | 40000 | 0 | 16510.4 | 3193.9 | 0 | 8384.74 | 11578.64 | 0 | 0 | 0 | 0
2022050912 | 2 | 0.75153 | 60122.4 | 0 | 0 | 0.55099 | 19284.65 | 0.68296 | 9561.44 | 40000 | 0 | 19284.65 | 0 | 837.75 | 8723.69 | 8723.69 | 0 | 0 | 0 | 0
2022050913 | 2 | 0.79183 | 63346.4 | 0 | 0 | 0.543 | 19005 | 0.73086 | 10232.04 | 40000 | 0 | 19005 | 0 | 4341.4 | 5890.64 | 5890.64 | 0 | 0 | 0 | 0
2022050914 | 2 | 0.82761 | 66208.8 | 0 | 0 | 0.53535 | 18737.25 | 0.73562 | 10298.68 | 40000 | 0 | 18737.25 | 0 | 7471.55 | 2827.13 | 2827.13 | 0 | 0 | 0 | 0
2022050915 | 2 | 0.85795 | 68636 | 0 | 0 | 0.54087 | 18930.45 | 0.71296 | 9981.44 | 40000 | 0 | 18930.45 | 0 | 9705.55 | 275.89 | 275.89 | 0 | 0 | 0 | 0
2022050916 | 2 | 0.87492 | 69993.6 | 0 | 0 | 0.54467 | 19063.45 | 0.69056 | 9667.84 | 40000 | 0 | 19063.45 | 0 | 9667.84 | 0 | 0 | 1262.31 | 0 | 0 | 1262.31
2022050917 | 2 | 0.8859 | 70872 | 0 | 0 | 0.54407 | 19042.45 | 0.66171 | 9263.94 | 40000 | 0 | 19042.45 | 0 | 9263.94 | 0 | 0 | 2565.61 | 0 | 0 | 2565.61
2022050918 | 2 | 0.88257 | 70605.6 | 0 | 0 | 0.56103 | 19636.05 | 0.59706 | 8358.84 | 40000 | 0 | 19636.05 | 0 | 8358.84 | 0 | 0 | 2610.71 | 0 | 0 | 2610.71
2022050919 | 2 | 0.86303 | 69042.4 | 0 | 0 | 0.57515 | 20130.25 | 0.51113 | 7155.82 | 40000 | 0 | 20130.25 | 0 | 7155.82 | 0 | 0 | 1756.33 | 0 | 0 | 1756.33
2022050920 | 2 | 0.82992 | 66393.6 | 0 | 0 | 0.58975 | 20641.25 | 0.25949 | 3632.86 | 40000 | 0 | 20641.25 | 0 | 3632.86 | 0 | 0 | 2119.49 | 0 | 0 | 2119.49
2022050921 | 2 | 0.80894 | 64715.2 | 0 | 0 | 0.59243 | 20735.05 | 0.02076 | 290.64 | 40000 | 0 | 20735.05 | 0 | 290.64 | 0 | 0 | 3689.51 | 0 | 0 | 3689.51
2022050922 | 2 | 0.78177 | 62541.6 | 0 | 0 | 0.62674 | 21935.9 | 0.00042 | 5.88 | 40000 | 0 | 21935.9 | 0 | 5.88 | 0 | 0 | 599.82 | 0 | 0 | 599.82
2022050923 | 2 | 0.7312 | 58496 | 0 | 0 | 0.63398 | 22189.3 | 0 | 0 | 40000 | 0 | 18496 | 3693.3 | 0 | 0 | 3693.3 | 0 | 0 | 0 | 0
2022050924 | 2 | 0.67924 | 54339.2 | 0 | 0 | 0.64204 | 22471.4 | 0 | 0 | 40000 | 0 | 14339.2 | 8132.2 | 0 | 0 | 8132.2 | 0 | 0 | 0 | 0
2022051001 | 3 | 0.63664 | 50931.2 | 0 | 0 | 0.64573 | 22600.55 | 0 | 0 | 40000 | 0 | 10931.2 | 11669.35 | 0 | 0 | 11669.35 | 0 | 0 | 0 | 0
2022051002 | 3 | 0.6105 | 48840 | 0 | 0 | 0.65336 | 22867.6 | 0 | 0 | 40000 | 0 | 8840 | 14027.6 | 0 | 0 | 14027.6 | 0 | 0 | 0 | 0
2022051003 | 3 | 0.58702 | 46961.6 | 0 | 0 | 0.6509 | 22781.5 | 0 | 0 | 40000 | 0 | 6961.6 | 15819.9 | 0 | 0 | 15819.9 | 0 | 0 | 0 | 0
2022051004 | 3 | 0.57157 | 45725.6 | 0 | 0 | 0.62639 | 21923.65 | 0 | 0 | 40000 | 0 | 5725.6 | 16198.05 | 0 | 0 | 16198.05 | 0 | 0 | 0 | 0
2022051005 | 3 | 0.56861 | 45488.8 | 0 | 0 | 0.60291 | 21101.85 | 0 | 0 | 40000 | 0 | 5488.8 | 15613.05 | 0 | 0 | 15613.05 | 0 | 0 | 0 | 0
2022051006 | 3 | 0.58373 | 46698.4 | 0 | 0 | 0.5765 | 20177.5 | 0 | 0 | 40000 | 0 | 6698.4 | 13479.1 | 0 | 0 | 13479.1 | 0 | 0 | 0 | 0
2022051007 | 3 | 0.60596 | 48476.8 | 0 | 0 | 0.53064 | 18572.4 | 0.00046 | 6.44 | 40000 | 0 | 8476.8 | 10095.6 | 0 | 6.44 | 10102.04 | 0 | 0 | 0 | 0
2022051008 | 3 | 0.61903 | 49522.4 | 0 | 0 | 0.52321 | 18312.35 | 0.07727 | 1081.78 | 40000 | 0 | 9522.4 | 8789.95 | 0 | 1081.78 | 9871.73 | 0 | 0 | 0 | 0
2022051009 | 3 | 0.63751 | 51000.8 | 0 | 0 | 0.54265 | 18992.75 | 0.32011 | 4481.54 | 40000 | 0 | 11000.8 | 7991.95 | 0 | 4481.54 | 12473.49 | 0 | 0 | 0 | 0
2022051010 | 3 | 0.66461 | 53168.8 | 0 | 0 | 0.56578 | 19802.3 | 0.44468 | 6225.52 | 40000 | 0 | 13168.8 | 6633.5 | 0 | 6225.52 | 12859.02 | 0 | 0 | 0 | 0
2022051011 | 3 | 0.69557 | 55645.6 | 0 | 0 | 0.55084 | 19279.4 | 0.51652 | 7231.28 | 40000 | 0 | 15645.6 | 3633.8 | 0 | 7231.28 | 10865.08 | 0 | 0 | 0 | 0
2022051012 | 3 | 0.73028 | 58422.4 | 0 | 0 | 0.51238 | 17933.3 | 0.58713 | 8219.82 | 40000 | 0 | 17933.3 | 0 | 489.1 | 7730.72 | 7730.72 | 0 | 0 | 0 | 0
2022051013 | 3 | 0.76178 | 60942.4 | 0 | 0 | 0.48301 | 16905.35 | 0.60494 | 8469.16 | 40000 | 0 | 16905.35 | 0 | 4037.05 | 4432.11 | 4432.11 | 0 | 0 | 0 | 0
2022051014 | 3 | 0.79687 | 63749.6 | 0 | 0 | 0.48582 | 17003.7 | 0.63803 | 8932.42 | 40000 | 0 | 17003.7 | 0 | 6745.9 | 2186.52 | 2186.52 | 0 | 0 | 0 | 0
2022051015 | 3 | 0.82477 | 65981.6 | 0 | 0 | 0.54497 | 19073.95 | 0.65824 | 9215.36 | 40000 | 0 | 19073.95 | 0 | 6907.65 | 2307.71 | 2307.71 | 0 | 0 | 0 | 0
2022051016 | 3 | 0.84769 | 67815.2 | 0 | 0 | 0.59183 | 20714.05 | 0.63832 | 8936.48 | 40000 | 0 | 20714.05 | 0 | 7101.15 | 1835.33 | 1835.33 | 0 | 0 | 0 | 0
2022051017 | 3 | 0.86096 | 68876.8 | 0 | 0 | 0.60396 | 21138.6 | 0.61798 | 8651.72 | 40000 | 0 | 21138.6 | 0 | 7738.2 | 913.52 | 913.52 | 0 | 0 | 0 | 0
2022051018 | 3 | 0.8601 | 68808 | 0 | 0 | 0.65361 | 22876.35 | 0.45058 | 6308.12 | 40000 | 0 | 22876.35 | 0 | 5931.65 | 376.47 | 376.47 | 0 | 0 | 0 | 0
2022051019 | 3 | 0.83865 | 67092 | 0 | 0 | 0.67761 | 23716.35 | 0.26417 | 3698.38 | 40000 | 0 | 23716.35 | 0 | 3375.65 | 322.73 | 322.73 | 0 | 0 | 0 | 0
2022051020 | 3 | 0.8031 | 64248 | 0 | 0 | 0.67302 | 23555.7 | 0.07851 | 1099.14 | 40000 | 0 | 23555.7 | 0 | 692.3 | 406.84 | 406.84 | 0 | 0 | 0 | 0
2022051021 | 3 | 0.77725 | 62180 | 0 | 0 | 0.6435 | 22522.5 | 0.00489 | 68.46 | 40000 | 0 | 22180 | 342.5 | 0 | 68.46 | 410.96 | 0 | 0 | 0 | 0
2022051022 | 3 | 0.74786 | 59828.8 | 0 | 0 | 0.59837 | 20942.95 | 0 | 0 | 40000 | 0 | 19828.8 | 1114.15 | 0 | 0 | 1114.15 | 0 | 0 | 0 | 0
2022051023 | 3 | 0.69453 | 55562.4 | 0 | 0 | 0.57265 | 20042.75 | 0 | 0 | 40000 | 0 | 15562.4 | 4480.35 | 0 | 0 | 4480.35 | 0 | 0 | 0 | 0
2022051024 | 3 | 0.64342 | 51473.6 | 0 | 0 | 0.5605 | 19617.5 | 0 | 0 | 40000 | 0 | 11473.6 | 8143.9 | 0 | 0 | 8143.9 | 0 | 0 | 0 | 0
2022051101 | 4 | 0.60165 | 48132 | 0 | 0 | 0.53955 | 18884.25 | 0 | 0 | 40000 | 0 | 8132 | 10752.25 | 0 | 0 | 10752.25 | 0 | 0 | 0 | 0
2022051102 | 4 | 0.56666 | 45332.8 | 0 | 0 | 0.47052 | 16468.2 | 0 | 0 | 40000 | 0 | 5332.8 | 11135.4 | 0 | 0 | 11135.4 | 0 | 0 | 0 | 0
2022051103 | 4 | 0.54484 | 43587.2 | 0 | 0 | 0.39347 | 13771.45 | 0 | 0 | 40000 | 0 | 3587.2 | 10184.25 | 0 | 0 | 10184.25 | 0 | 0 | 0 | 0
2022051104 | 4 | 0.52986 | 42388.8 | 0 | 0 | 0.34777 | 12171.95 | 0 | 0 | 40000 | 0 | 2388.8 | 9783.15 | 0 | 0 | 9783.15 | 0 | 0 | 0 | 0
2022051105 | 4 | 0.52631 | 42104.8 | 0 | 0 | 0.29146 | 10201.1 | 0 | 0 | 40000 | 0 | 2104.8 | 8096.3 | 0 | 0 | 8096.3 | 0 | 0 | 0 | 0
2022051106 | 4 | 0.53843 | 43074.4 | 0 | 0 | 0.29728 | 10404.8 | 0 | 0 | 40000 | 0 | 3074.4 | 7330.4 | 0 | 0 | 7330.4 | 0 | 0 | 0 | 0
2022051107 | 4 | 0.56201 | 44960.8 | 0 | 0 | 0.31235 | 10932.25 | 0.00099 | 13.86 | 40000 | 0 | 4960.8 | 5971.45 | 0 | 13.86 | 5985.31 | 0 | 0 | 0 | 0
2022051108 | 4 | 0.57702 | 46161.6 | 0 | 0 | 0.32926 | 11524.1 | 0.07288 | 1020.32 | 40000 | 0 | 6161.6 | 5362.5 | 0 | 1020.32 | 6382.82 | 0 | 0 | 0 | 0
2022051109 | 4 | 0.60143 | 48114.4 | 0 | 0 | 0.34332 | 12016.2 | 0.40213 | 5629.82 | 40000 | 0 | 8114.4 | 3901.8 | 0 | 5629.82 | 9531.62 | 0 | 0 | 0 | 0
2022051110 | 4 | 0.6379 | 51032 | 0 | 0 | 0.4288 | 15008 | 0.63157 | 8841.98 | 40000 | 0 | 11032 | 3976 | 0 | 8841.98 | 12817.98 | 0 | 0 | 0 | 0
2022051111 | 4 | 0.67954 | 54363.2 | 0 | 0 | 0.51128 | 17894.8 | 0.55101 | 7714.14 | 40000 | 0 | 14363.2 | 3531.6 | 0 | 7714.14 | 11245.74 | 0 | 0 | 0 | 0
2022051112 | 4 | 0.71398 | 57118.4 | 0 | 0 | 0.56569 | 19799.15 | 0.46209 | 6469.26 | 40000 | 0 | 17118.4 | 2680.75 | 0 | 6469.26 | 9150.01 | 0 | 0 | 0 | 0
2022051113 | 4 | 0.74787 | 59829.6 | 0 | 0 | 0.57711 | 20198.85 | 0.50181 | 7025.34 | 40000 | 0 | 19829.6 | 369.25 | 0 | 7025.34 | 7394.59 | 0 | 0 | 0 | 0
2022051114 | 4 | 0.78695 | 62956 | 0 | 0 | 0.59226 | 20729.1 | 0.51715 | 7240.1 | 40000 | 0 | 20729.1 | 0 | 2226.9 | 5013.2 | 5013.2 | 0 | 0 | 0 | 0
2022051115 | 4 | 0.81566 | 65252.8 | 0 | 0 | 0.596 | 20860 | 0.50243 | 7034.02 | 40000 | 0 | 20860 | 0 | 4392.8 | 2641.22 | 2641.22 | 0 | 0 | 0 | 0
2022051116 | 4 | 0.83734 | 66987.2 | 0 | 0 | 0.61291 | 21451.85 | 0.50789 | 7110.46 | 40000 | 0 | 21451.85 | 0 | 5535.35 | 1575.11 | 1575.11 | 0 | 0 | 0 | 0
2022051117 | 4 | 0.85552 | 68441.6 | 0 | 0 | 0.63492 | 22222.2 | 0.46791 | 6550.74 | 40000 | 0 | 22222.2 | 0 | 6219.4 | 331.34 | 331.34 | 0 | 0 | 0 | 0
2022051118 | 4 | 0.85753 | 68602.4 | 0 | 0 | 0.65383 | 22884.05 | 0.40763 | 5706.82 | 40000 | 0 | 22884.05 | 0 | 5706.82 | 0 | 0 | 11.53 | 0 | 0 | 11.53
2022051119 | 4 | 0.83803 | 67042.4 | 0 | 0 | 0.6656 | 23296 | 0.32876 | 4602.64 | 40000 | 0 | 23296 | 0 | 3746.4 | 856.24 | 856.24 | 0 | 0 | 0 | 0
2022051120 | 4 | 0.80231 | 64184.8 | 0 | 0 | 0.66528 | 23284.8 | 0.13609 | 1905.26 | 40000 | 0 | 23284.8 | 0 | 900 | 1005.26 | 1005.26 | 0 | 0 | 0 | 0
2022051121 | 4 | 0.77191 | 61752.8 | 0 | 0 | 0.65748 | 23011.8 | 0.00624 | 87.36 | 40000 | 0 | 21752.8 | 1259 | 0 | 87.36 | 1346.36 | 0 | 0 | 0 | 0
2022051122 | 4 | 0.7398 | 59184 | 0 | 0 | 0.65026 | 22759.1 | 0 | 0 | 40000 | 0 | 19184 | 3575.1 | 0 | 0 | 3575.1 | 0 | 0 | 0 | 0
2022051123 | 4 | 0.68851 | 55080.8 | 0 | 0 | 0.6539 | 22886.5 | 0 | 0 | 40000 | 0 | 15080.8 | 7805.7 | 0 | 0 | 7805.7 | 0 | 0 | 0 | 0
2022051124 | 4 | 0.63174 | 50539.2 | 0 | 0 | 0.64838 | 22693.3 | 0 | 0 | 40000 | 0 | 10539.2 | 12154.1 | 0 | 0 | 12154.1 | 0 | 0 | 0 | 0
2022051201 | 5 | 0.58622 | 46897.6 | 0 | 0 | 0.627 | 21945 | 0 | 0 | 40000 | 0 | 6897.6 | 15047.4 | 0 | 0 | 15047.4 | 0 | 0 | 0 | 0
2022051202 | 5 | 0.55336 | 44268.8 | 0 | 0 | 0.59973 | 20990.55 | 0 | 0 | 40000 | 0 | 4268.8 | 16721.75 | 0 | 0 | 16721.75 | 0 | 0 | 0 | 0
2022051203 | 5 | 0.52954 | 42363.2 | 0 | 0 | 0.58056 | 20319.6 | 0 | 0 | 40000 | 0 | 2363.2 | 17956.4 | 0 | 0 | 17956.4 | 0 | 0 | 0 | 0
2022051204 | 5 | 0.51534 | 41227.2 | 0 | 0 | 0.56975 | 19941.25 | 0 | 0 | 40000 | 0 | 1227.2 | 18714.05 | 0 | 0 | 18714.05 | 0 | 0 | 0 | 0
2022051205 | 5 | 0.511 | 40880 | 0 | 0 | 0.56278 | 19697.3 | 0 | 0 | 40000 | 0 | 880 | 18817.3 | 0 | 0 | 18817.3 | 0 | 0 | 0 | 0
2022051206 | 5 | 0.52504 | 42003.2 | 0 | 0 | 0.54581 | 19103.35 | 0 | 0 | 40000 | 0 | 2003.2 | 17100.15 | 0 | 0 | 17100.15 | 0 | 0 | 0 | 0
2022051207 | 5 | 0.54656 | 43724.8 | 0 | 0 | 0.5469 | 19141.5 | 0.00172 | 24.08 | 40000 | 0 | 3724.8 | 15416.7 | 0 | 24.08 | 15440.78 | 0 | 0 | 0 | 0
2022051208 | 5 | 0.5602 | 44816 | 0 | 0 | 0.5426 | 18991 | 0.11766 | 1647.24 | 40000 | 0 | 4816 | 14175 | 0 | 1647.24 | 15822.24 | 0 | 0 | 0 | 0
2022051209 | 5 | 0.58519 | 46815.2 | 0 | 0 | 0.52934 | 18526.9 | 0.35733 | 5002.62 | 40000 | 0 | 6815.2 | 11711.7 | 0 | 5002.62 | 16714.32 | 0 | 0 | 0 | 0
2022051210 | 5 | 0.61785 | 49428 | 0 | 0 | 0.55087 | 19280.45 | 0.44026 | 6163.64 | 40000 | 0 | 9428 | 9852.45 | 0 | 6163.64 | 16016.09 | 0 | 0 | 0 | 0
2022051211 | 5 | 0.65739 | 52591.2 | 0 | 0 | 0.54388 | 19035.8 | 0.52139 | 7299.46 | 40000 | 0 | 12591.2 | 6444.6 | 0 | 7299.46 | 13744.06 | 0 | 0 | 0 | 0
2022051212 | 5 | 0.69205 | 55364 | 0 | 0 | 0.51709 | 18098.15 | 0.60727 | 8501.78 | 40000 | 0 | 15364 | 2734.15 | 0 | 8501.78 | 11235.93 | 0 | 0 | 0 | 0
2022051213 | 5 | 0.73157 | 58525.6 | 0 | 0 | 0.51963 | 18187.05 | 0.66013 | 9241.82 | 40000 | 0 | 18187.05 | 0 | 338.55 | 8903.27 | 8903.27 | 0 | 0 | 0 | 0
2022051214 | 5 | 0.77059 | 61647.2 | 0 | 0 | 0.50261 | 17591.35 | 0.65784 | 9209.76 | 40000 | 0 | 17591.35 | 0 | 4055.85 | 5153.91 | 5153.91 | 0 | 0 | 0 | 0
2022051215 | 5 | 0.80266 | 64212.8 | 0 | 0 | 0.46423 | 16248.05 | 0.63128 | 8837.92 | 40000 | 0 | 16248.05 | 0 | 7964.75 | 873.17 | 873.17 | 0 | 0 | 0 | 0
2022051216 | 5 | 0.82881 | 66304.8 | 0 | 0 | 0.42951 | 15032.85 | 0.65394 | 9155.16 | 40000 | 0 | 15032.85 | 0 | 9155.16 | 0 | 0 | 2116.79 | 0 | 0 | 2116.79
2022051217 | 5 | 0.84833 | 67866.4 | 0 | 0 | 0.42887 | 15010.45 | 0.70805 | 9912.7 | 40000 | 0 | 15010.45 | 0 | 9912.7 | 0 | 0 | 2943.25 | 0 | 0 | 2943.25
2022051218 | 5 | 0.84924 | 67939.2 | 0 | 0 | 0.4415 | 15452.5 | 0.6686 | 9360.4 | 40000 | 0 | 15452.5 | 0 | 9360.4 | 0 | 0 | 3126.3 | 0 | 0 | 3126.3
2022051219 | 5 | 0.82817 | 66253.6 | 0 | 0 | 0.46374 | 16230.9 | 0.47352 | 6629.28 | 40000 | 0 | 16230.9 | 0 | 6629.28 | 0 | 0 | 3393.42 | 0 | 0 | 3393.42
2022051220 | 5 | 0.79233 | 63386.4 | 0 | 0 | 0.49871 | 17454.85 | 0.16647 | 2330.58 | 40000 | 0 | 17454.85 | 0 | 2330.58 | 0 | 0 | 3600.97 | 0 | 0 | 3600.97
2022051221 | 5 | 0.76204 | 60963.2 | 0 | 0 | 0.50107 | 17537.45 | 0.0193 | 270.2 | 40000 | 0 | 17537.45 | 0 | 270.2 | 0 | 0 | 3155.55 | 0 | 0 | 3155.55
2022051222 | 5 | 0.73017 | 58413.6 | 0 | 0 | 0.56162 | 19656.7 | 0 | 0 | 40000 | 0 | 18413.6 | 1243.1 | 0 | 0 | 1243.1 | 0 | 0 | 0 | 0
2022051223 | 5 | 0.68301 | 54640.8 | 0 | 0 | 0.62881 | 22008.35 | 0 | 0 | 40000 | 0 | 14640.8 | 7367.55 | 0 | 0 | 7367.55 | 0 | 0 | 0 | 0
2022051224 | 5 | 0.62853 | 50282.4 | 0 | 0 | 0.63756 | 22314.6 | 0 | 0 | 40000 | 0 | 10282.4 | 12032.2 | 0 | 0 | 12032.2 | 0 | 0 | 0 | 0
2022051301 | 6 | 0.58207 | 46565.6 | 0 | 0 | 0.61166 | 21408.1 | 0 | 0 | 40000 | 0 | 6565.6 | 14842.5 | 0 | 0 | 14842.5 | 0 | 0 | 0 | 0
2022051302 | 6 | 0.54902 | 43921.6 | 0 | 0 | 0.58694 | 20542.9 | 0 | 0 | 40000 | 0 | 3921.6 | 16621.3 | 0 | 0 | 16621.3 | 0 | 0 | 0 | 0
2022051303 | 6 | 0.52512 | 42009.6 | 0 | 0 | 0.56598 | 19809.3 | 0 | 0 | 40000 | 0 | 2009.6 | 17799.7 | 0 | 0 | 17799.7 | 0 | 0 | 0 | 0
2022051304 | 6 | 0.50944 | 40755.2 | 0 | 0 | 0.5168 | 18088 | 0 | 0 | 40000 | 0 | 755.2 | 17332.8 | 0 | 0 | 17332.8 | 0 | 0 | 0 | 0
2022051305 | 6 | 0.50541 | 40432.8 | 0 | 0 | 0.48793 | 17077.55 | 0 | 0 | 40000 | 0 | 432.8 | 16644.75 | 0 | 0 | 16644.75 | 0 | 0 | 0 | 0
2022051306 | 6 | 0.51947 | 41557.6 | 0 | 0 | 0.47928 | 16774.8 | 0 | 0 | 40000 | 0 | 1557.6 | 15217.2 | 0 | 0 | 15217.2 | 0 | 0 | 0 | 0
2022051307 | 6 | 0.53963 | 43170.4 | 0 | 0 | 0.46199 | 16169.65 | 0.00228 | 31.92 | 40000 | 0 | 3170.4 | 12999.25 | 0 | 31.92 | 13031.17 | 0 | 0 | 0 | 0
2022051308 | 6 | 0.55682 | 44545.6 | 0 | 0 | 0.45637 | 15972.95 | 0.1548 | 2167.2 | 40000 | 0 | 4545.6 | 11427.35 | 0 | 2167.2 | 13594.55 | 0 | 0 | 0 | 0
2022051309 | 6 | 0.58191 | 46552.8 | 0 | 0 | 0.3879 | 13576.5 | 0.55405 | 7756.7 | 40000 | 0 | 6552.8 | 7023.7 | 0 | 7756.7 | 14780.4 | 0 | 0 | 0 | 0
2022051310 | 6 | 0.61433 | 49146.4 | 0 | 0 | 0.36166 | 12658.1 | 0.70868 | 9921.52 | 40000 | 0 | 9146.4 | 3511.7 | 0 | 9921.52 | 13433.22 | 0 | 0 | 0 | 0
2022051311 | 6 | 0.65187 | 52149.6 | 0 | 0 | 0.27964 | 9787.4 | 0.70311 | 9843.54 | 40000 | 0 | 9787.4 | 0 | 2362.2 | 7481.34 | 7481.34 | 0 | 0 | 0 | 0
2022051312 | 6 | 0.68882 | 55105.6 | 0 | 0 | 0.21556 | 7544.6 | 0.64867 | 9081.38 | 40000 | 0 | 7544.6 | 0 | 7561 | 1520.38 | 1520.38 | 0 | 0 | 0 | 0
2022051313 | 6 | 0.72504 | 58003.2 | 0 | 0 | 0.16404 | 5741.4 | 0.72547 | 10156.58 | 40000 | 0 | 5741.4 | 0 | 10156.58 | 0 | 0 | 2105.22 | 0 | 0 | 2105.22
2022051314 | 6 | 0.76149 | 60919.2 | 0 | 0 | 0.13811 | 4833.85 | 0.74635 | 10448.9 | 40000 | 0 | 4833.85 | 0 | 10448.9 | 0 | 0 | 5636.45 | 0 | 0 | 5636.45
2022051315 | 6 | 0.78305 | 62644 | 0 | 0 | 0.12405 | 4341.75 | 0.7379 | 10330.6 | 40000 | 0 | 4341.75 | 0 | 10330.6 | 0 | 0 | 7971.65 | 0 | 0 | 7971.65
2022051316 | 6 | 0.80469 | 64375.2 | 0 | 0 | 0.13573 | 4750.55 | 0.7336 | 10270.4 | 40000 | 0 | 4750.55 | 0 | 10270.4 | 0 | 0 | 9354.25 | 0 | 0 | 9354.25
2022051317 | 6 | 0.81659 | 65327.2 | 0 | 0 | 0.15714 | 5499.9 | 0.72784 | 10189.76 | 40000 | 0 | 5499.9 | 0 | 10189.76 | 0 | 0 | 9637.54 | 0 | 0 | 9637.54
2022051318 | 6 | 0.81413 | 65130.4 | 0 | 0 | 0.17562 | 6146.7 | 0.65294 | 9141.16 | 40000 | 0 | 6146.7 | 0 | 9141.16 | 0 | 0 | 9842.54 | 0 | 0 | 9842.54
2022051319 | 6 | 0.7973 | 63784 | 0 | 0 | 0.22954 | 8033.9 | 0.53419 | 7478.66 | 40000 | 0 | 8033.9 | 0 | 7478.66 | 0 | 0 | 8271.44 | 0 | 0 | 8271.44
2022051320 | 6 | 0.76568 | 61254.4 | 0 | 0 | 0.29646 | 10376.1 | 0.25795 | 3611.3 | 40000 | 0 | 10376.1 | 0 | 3611.3 | 0 | 0 | 7267 | 0 | 0 | 7267
2022051321 | 6 | 0.73901 | 59120.8 | 0 | 0 | 0.32137 | 11247.95 | 0.01781 | 249.34 | 40000 | 0 | 11247.95 | 0 | 249.34 | 0 | 0 | 7623.51 | 0 | 0 | 7623.51
2022051322 | 6 | 0.71028 | 56822.4 | 0 | 0 | 0.3263 | 11420.5 | 0 | 0 | 40000 | 0 | 11420.5 | 0 | 0 | 0 | 0 | 5401.9 | 0 | 0 | 5401.9
2022051323 | 6 | 0.67175 | 53740 | 0 | 0 | 0.40729 | 14255.15 | 0 | 0 | 40000 | 0 | 13740 | 515.15 | 0 | 0 | 515.15 | 0 | 0 | 0 | 0
2022051324 | 6 | 0.6282 | 50256 | 0 | 0 | 0.45446 | 15906.1 | 0 | 0 | 40000 | 0 | 10256 | 5650.1 | 0 | 0 | 5650.1 | 0 | 0 | 0 | 0
2022051401 | 7 | 0.58914 | 47131.2 | 0 | 0 | 0.44522 | 15582.7 | 0 | 0 | 40000 | 0 | 7131.2 | 8451.5 | 0 | 0 | 8451.5 | 0 | 0 | 0 | 0
2022051402 | 7 | 0.55596 | 44476.8 | 0 | 0 | 0.46896 | 16413.6 | 0 | 0 | 40000 | 0 | 4476.8 | 11936.8 | 0 | 0 | 11936.8 | 0 | 0 | 0 | 0
2022051403 | 7 | 0.5307 | 42456 | 0 | 0 | 0.4793 | 16775.5 | 0 | 0 | 40000 | 0 | 2456 | 14319.5 | 0 | 0 | 14319.5 | 0 | 0 | 0 | 0
2022051404 | 7 | 0.5088 | 40704 | 0 | 0 | 0.45334 | 15866.9 | 0 | 0 | 40000 | 0 | 704 | 15162.9 | 0 | 0 | 15162.9 | 0 | 0 | 0 | 0
2022051405 | 7 | 0.4963 | 39704 | 0 | 0 | 0.41916 | 14670.6 | 0 | 0 | 39704 | 296 | 0 | 14670.6 | 0 | 0 | 14966.6 | 0 | 0 | 0 | 0
2022051406 | 7 | 0.49331 | 39464.8 | 0 | 0 | 0.36225 | 12678.75 | 0 | 0 | 39464.8 | 535.2 | 0 | 12678.75 | 0 | 0 | 13213.95 | 0 | 0 | 0 | 0
2022051407 | 7 | 0.4963 | 39704 | 0 | 0 | 0.30588 | 10705.8 | 0.00183 | 25.62 | 39704 | 296 | 0 | 10705.8 | 0 | 25.62 | 11027.42 | 0 | 0 | 0 | 0
2022051408 | 7 | 0.51043 | 40834.4 | 0 | 0 | 0.27489 | 9621.15 | 0.1396 | 1954.4 | 40000 | 0 | 834.4 | 8786.75 | 0 | 1954.4 | 10741.15 | 0 | 0 | 0 | 0
2022051409 | 7 | 0.54652 | 43721.6 | 0 | 0 | 0.24458 | 8560.3 | 0.55521 | 7772.94 | 40000 | 0 | 3721.6 | 4838.7 | 0 | 7772.94 | 12611.64 | 0 | 0 | 0 | 0
2022051410 | 7 | 0.59412 | 47529.6 | 0 | 0 | 0.29595 | 10358.25 | 0.72534 | 10154.76 | 40000 | 0 | 7529.6 | 2828.65 | 0 | 10154.76 | 12983.41 | 0 | 0 | 0 | 0
2022051411 | 7 | 0.63584 | 50867.2 | 0 | 0 | 0.2666 | 9331 | 0.77635 | 10868.9 | 40000 | 0 | 9331 | 0 | 1536.2 | 9332.7 | 9332.7 | 0 | 0 | 0 | 0
2022051412 | 7 | 0.67715 | 54172 | 0 | 0 | 0.18178 | 6362.3 | 0.80042 | 11205.88 | 40000 | 0 | 6362.3 | 0 | 7809.7 | 3396.18 | 3396.18 | 0 | 0 | 0 | 0
2022051413 | 7 | 0.71748 | 57398.4 | 0 | 0 | 0.114 | 3990 | 0.7934 | 11107.6 | 40000 | 0 | 3990 | 0 | 11107.6 | 0 | 0 | 2300.8 | 0 | 0 | 2300.8
2022051414 | 7 | 0.75186 | 60148.8 | 0 | 0 | 0.09818 | 3436.3 | 0.78859 | 11040.26 | 40000 | 0 | 3436.3 | 0 | 11040.26 | 0 | 0 | 5672.24 | 0 | 0 | 5672.24
2022051415 | 7 | 0.78589 | 62871.2 | 0 | 0 | 0.10856 | 3799.6 | 0.77819 | 10894.66 | 40000 | 0 | 3799.6 | 0 | 10894.66 | 0 | 0 | 8176.94 | 0 | 0 | 8176.94
2022051416 | 7 | 0.81024 | 64819.2 | 0 | 0 | 0.13964 | 4887.4 | 0.74397 | 10415.58 | 40000 | 0 | 4887.4 | 0 | 10415.58 | 0 | 0 | 9516.22 | 0 | 0 | 9516.22
2022051417 | 7 | 0.82576 | 66060.8 | 0 | 0 | 0.19966 | 6988.1 | 0.70101 | 9814.14 | 40000 | 0 | 6988.1 | 0 | 9814.14 | 0 | 0 | 9258.56 | 0 | 0 | 9258.56
2022051418 | 7 | 0.82639 | 66111.2 | 0 | 0 | 0.26496 | 9273.6 | 0.65468 | 9165.52 | 40000 | 0 | 9273.6 | 0 | 9165.52 | 0 | 0 | 7672.08 | 0 | 0 | 7672.08
2022051419 | 7 | 0.80883 | 64706.4 | 0 | 0 | 0.30754 | 10763.9 | 0.5719 | 8006.6 | 40000 | 0 | 10763.9 | 0 | 8006.6 | 0 | 0 | 5935.9 | 0 | 0 | 5935.9
2022051420 | 7 | 0.77408 | 61926.4 | 0 | 0 | 0.34041 | 11914.35 | 0.26937 | 3771.18 | 40000 | 0 | 11914.35 | 0 | 3771.18 | 0 | 0 | 6240.87 | 0 | 0 | 6240.87
2022051421 | 7 | 0.74344 | 59475.2 | 0 | 0 | 0.38464 | 13462.4 | 0.01761 | 246.54 | 40000 | 0 | 13462.4 | 0 | 246.54 | 0 | 0 | 5766.26 | 0 | 0 | 5766.26
2022051422 | 7 | 0.71442 | 57153.6 | 0 | 0 | 0.45366 | 15878.1 | 0 | 0 | 40000 | 0 | 15878.1 | 0 | 0 | 0 | 0 | 1275.5 | 0 | 0 | 1275.5
2022051423 | 7 | 0.67404 | 53923.2 | 0 | 0 | 0.52619 | 18416.65 | 0 | 0 | 40000 | 0 | 13923.2 | 4493.45 | 0 | 0 | 4493.45 | 0 | 0 | 0 | 0
2022051424 | 7 | 0.63312 | 50649.6 | 0 | 0 | 0.57319 | 20061.65 | 0 | 0 | 40000 | 0 | 10649.6 | 9412.05 | 0 | 0 | 9412.05 | 0 | 0 | 0 | 0
2022051501 | 1 | 0.59489 | 47591.2 | 0 | 0 | 0.58689 | 20541.15 | 0 | 0 | 40000 | 0 | 7591.2 | 12949.95 | 0 | 0 | 12949.95 | 0 | 0 | 0 | 0
2022051502 | 1 | 0.56109 | 44887.2 | 0 | 0 | 0.57651 | 20177.85 | 0 | 0 | 40000 | 0 | 4887.2 | 15290.65 | 0 | 0 | 15290.65 | 0 | 0 | 0 | 0
2022051503 | 1 | 0.53269 | 42615.2 | 0 | 0 | 0.52804 | 18481.4 | 0 | 0 | 40000 | 0 | 2615.2 | 15866.2 | 0 | 0 | 15866.2 | 0 | 0 | 0 | 0
2022051504 | 1 | 0.51246 | 40996.8 | 0 | 0 | 0.49048 | 17166.8 | 0 | 0 | 40000 | 0 | 996.8 | 16170 | 0 | 0 | 16170 | 0 | 0 | 0 | 0
2022051505 | 1 | 0.49789 | 39831.2 | 0 | 0 | 0.46581 | 16303.35 | 0 | 0 | 39831.2 | 168.8 | 0 | 16303.35 | 0 | 0 | 16472.15 | 0 | 0 | 0 | 0
2022051506 | 1 | 0.49216 | 39372.8 | 0 | 0 | 0.46146 | 16151.1 | 0 | 0 | 39372.8 | 627.2 | 0 | 16151.1 | 0 | 0 | 16778.3 | 0 | 0 | 0 | 0
2022051507 | 1 | 0.48578 | 38862.4 | 0 | 0 | 0.44496 | 15573.6 | 0.00022 | 3.08 | 38862.4 | 1137.6 | 0 | 15573.6 | 0 | 3.08 | 16714.28 | 0 | 0 | 0 | 0
2022051508 | 1 | 0.49176 | 39340.8 | 0 | 0 | 0.44082 | 15428.7 | 0.06384 | 893.76 | 39340.8 | 659.2 | 0 | 15428.7 | 0 | 893.76 | 16981.66 | 0 | 0 | 0 | 0
2022051509 | 1 | 0.53014 | 42411.2 | 0 | 0 | 0.37638 | 13173.3 | 0.48965 | 6855.1 | 40000 | 0 | 2411.2 | 10762.1 | 0 | 6855.1 | 17617.2 | 0 | 0 | 0 | 0
2022051510 | 1 | 0.5791 | 46328 | 0 | 0 | 0.35983 | 12594.05 | 0.71694 | 10037.16 | 40000 | 0 | 6328 | 6266.05 | 0 | 10037.16 | 16303.21 | 0 | 0 | 0 | 0
2022051511 | 1 | 0.6281 | 50248 | 0 | 0 | 0.35342 | 12369.7 | 0.78042 | 10925.88 | 40000 | 0 | 10248 | 2121.7 | 0 | 10925.88 | 13047.58 | 0 | 0 | 0 | 0
2022051512 | 1 | 0.68121 | 54496.8 | 0 | 0 | 0.35977 | 12591.95 | 0.7967 | 11153.8 | 40000 | 0 | 12591.95 | 0 | 1904.85 | 9248.95 | 9248.95 | 0 | 0 | 0 | 0
2022051513 | 1 | 0.73299 | 58639.2 | 0 | 0 | 0.35119 | 12291.65 | 0.80261 | 11236.54 | 40000 | 0 | 12291.65 | 0 | 6347.55 | 4888.99 | 4888.99 | 0 | 0 | 0 | 0
2022051514 | 1 | 0.77768 | 62214.4 | 0 | 0 | 0.33434 | 11701.9 | 0.80628 | 11287.92 | 40000 | 0 | 11701.9 | 0 | 10512.5 | 775.42 | 775.42 | 0 | 0 | 0 | 0
2022051515 | 1 | 0.80888 | 64710.4 | 0 | 0 | 0.31501 | 11025.35 | 0.79836 | 11177.04 | 40000 | 0 | 11025.35 | 0 | 11177.04 | 0 | 0 | 2508.01 | 0 | 0 | 2508.01
2022051516 | 1 | 0.83445 | 66756 | 0 | 0 | 0.30094 | 10532.9 | 0.77935 | 10910.9 | 40000 | 0 | 10532.9 | 0 | 10910.9 | 0 | 0 | 5312.2 | 0 | 0 | 5312.2
2022051517 | 1 | 0.85305 | 68244 | 0 | 0 | 0.29635 | 10372.25 | 0.75049 | 10506.86 | 40000 | 0 | 10372.25 | 0 | 10506.86 | 0 | 0 | 7364.89 | 0 | 0 | 7364.89
2022051518 | 1 | 0.85896 | 68716.8 | 0 | 0 | 0.32036 | 11212.6 | 0.71331 | 9986.34 | 40000 | 0 | 11212.6 | 0 | 9986.34 | 0 | 0 | 7517.86 | 0 | 0 | 7517.86
2022051519 | 1 | 0.84699 | 67759.2 | 0 | 0 | 0.37409 | 13093.15 | 0.6016 | 8422.4 | 40000 | 0 | 13093.15 | 0 | 8422.4 | 0 | 0 | 6243.65 | 0 | 0 | 6243.65
2022051520 | 1 | 0.8152 | 65216 | 0 | 0 | 0.44175 | 15461.25 | 0.27518 | 3852.52 | 40000 | 0 | 15461.25 | 0 | 3852.52 | 0 | 0 | 5902.23 | 0 | 0 | 5902.23
2022051521 | 1 | 0.78357 | 62685.6 | 0 | 0 | 0.51029 | 17860.15 | 0.01819 | 254.66 | 40000 | 0 | 17860.15 | 0 | 254.66 | 0 | 0 | 4570.79 | 0 | 0 | 4570.79
2022051522 | 1 | 0.75583 | 60466.4 | 0 | 0 | 0.57972 | 20290.2 | 0 | 0 | 40000 | 0 | 20290.2 | 0 | 0 | 0 | 0 | 176.2 | 0 | 0 | 176.2
2022051523 | 1 | 0.70111 | 56088.8 | 0 | 0 | 0.58581 | 20503.35 | 0 | 0 | 40000 | 0 | 16088.8 | 4414.55 | 0 | 0 | 4414.55 | 0 | 0 | 0 | 0
2022051524 | 1 | 0.63956 | 51164.8 | 0 | 0 | 0.59364 | 20777.4 | 0 | 0 | 40000 | 0 | 11164.8 | 9612.6 | 0 | 0 | 9612.6 | 0 | 0 | 0 | 0
2022051601 | 2 | 0.58794 | 47035.2 | 0 | 0 | 0.57072 | 19975.2 | 0 | 0 | 40000 | 0 | 7035.2 | 12940 | 0 | 0 | 12940 | 0 | 0 | 0 | 0
2022051602 | 2 | 0.55197 | 44157.6 | 0 | 0 | 0.494 | 17290 | 0 | 0 | 40000 | 0 | 4157.6 | 13132.4 | 0 | 0 | 13132.4 | 0 | 0 | 0 | 0
2022051603 | 2 | 0.52807 | 42245.6 | 0 | 0 | 0.40929 | 14325.15 | 0 | 0 | 40000 | 0 | 2245.6 | 12079.55 | 0 | 0 | 12079.55 | 0 | 0 | 0 | 0
2022051604 | 2 | 0.51572 | 41257.6 | 0 | 0 | 0.36542 | 12789.7 | 0 | 0 | 40000 | 0 | 1257.6 | 11532.1 | 0 | 0 | 11532.1 | 0 | 0 | 0 | 0
2022051605 | 2 | 0.51334 | 41067.2 | 0 | 0 | 0.35677 | 12486.95 | 0 | 0 | 40000 | 0 | 1067.2 | 11419.75 | 0 | 0 | 11419.75 | 0 | 0 | 0 | 0
2022051606 | 2 | 0.52491 | 41992.8 | 0 | 0 | 0.32249 | 11287.15 | 0 | 0 | 40000 | 0 | 1992.8 | 9294.35 | 0 | 0 | 9294.35 | 0 | 0 | 0 | 0
2022051607 | 2 | 0.55133 | 44106.4 | 0 | 0 | 0.29822 | 10437.7 | 0.00116 | 16.24 | 40000 | 0 | 4106.4 | 6331.3 | 0 | 16.24 | 6347.54 | 0 | 0 | 0 | 0
2022051608 | 2 | 0.56216 | 44972.8 | 0 | 0 | 0.28144 | 9850.4 | 0.11602 | 1624.28 | 40000 | 0 | 4972.8 | 4877.6 | 0 | 1624.28 | 6501.88 | 0 | 0 | 0 | 0
2022051609 | 2 | 0.5878 | 47024 | 0 | 0 | 0.23254 | 8138.9 | 0.49823 | 6975.22 | 40000 | 0 | 7024 | 1114.9 | 0 | 6975.22 | 8090.12 | 0 | 0 | 0 | 0
2022051610 | 2 | 0.62508 | 50006.4 | 0 | 0 | 0.20148 | 7051.8 | 0.7137 | 9991.8 | 40000 | 0 | 7051.8 | 0 | 2954.6 | 7037.2 | 7037.2 | 0 | 0 | 0 | 0
2022051611 | 2 | 0.66372 | 53097.6 | 0 | 0 | 0.16729 | 5855.15 | 0.75289 | 10540.46 | 40000 | 0 | 5855.15 | 0 | 7242.45 | 3298.01 | 3298.01 | 0 | 0 | 0 | 0
2022051612 | 2 | 0.70692 | 56553.6 | 0 | 0 | 0.17008 | 5952.8 | 0.78429 | 10980.06 | 40000 | 0 | 5952.8 | 0 | 10600.8 | 379.26 | 379.26 | 0 | 0 | 0 | 0
2022051613 | 2 | 0.7504 | 60032 | 0 | 0 | 0.18785 | 6574.75 | 0.80143 | 11220.02 | 40000 | 0 | 6574.75 | 0 | 11220.02 | 0 | 0 | 2237.23 | 0 | 0 | 2237.23
2022051614 | 2 | 0.79285 | 63428 | 0 | 0 | 0.19773 | 6920.55 | 0.7871 | 11019.4 | 40000 | 0 | 6920.55 | 0 | 11019.4 | 0 | 0 | 5488.05 | 0 | 0 | 5488.05
2022051615 | 2 | 0.83115 | 66492 | 0 | 0 | 0.24315 | 8510.25 | 0.77038 | 10785.32 | 40000 | 0 | 8510.25 | 0 | 10785.32 | 0 | 0 | 7196.43 | 0 | 0 | 7196.43
2022051616 | 2 | 0.85992 | 68793.6 | 0 | 0 | 0.28672 | 10035.2 | 0.72786 | 10190.04 | 40000 | 0 | 10035.2 | 0 | 10190.04 | 0 | 0 | 8568.36 | 0 | 0 | 8568.36
2022051617 | 2 | 0.8792 | 70336 | 0 | 0 | 0.33713 | 11799.55 | 0.67804 | 9492.56 | 40000 | 0 | 11799.55 | 0 | 9492.56 | 0 | 0 | 9043.89 | 0 | 0 | 9043.89
2022051618 | 2 | 0.88041 | 70432.8 | 0 | 0 | 0.39193 | 13717.55 | 0.58273 | 8158.22 | 40000 | 0 | 13717.55 | 0 | 8158.22 | 0 | 0 | 8557.03 | 0 | 0 | 8557.03
2022051619 | 2 | 0.86091 | 68872.8 | 0 | 0 | 0.44216 | 15475.6 | 0.38484 | 5387.76 | 40000 | 0 | 15475.6 | 0 | 5387.76 | 0 | 0 | 8009.44 | 0 | 0 | 8009.44
2022051620 | 2 | 0.82593 | 66074.4 | 0 | 0 | 0.5052 | 17682 | 0.17014 | 2381.96 | 40000 | 0 | 17682 | 0 | 2381.96 | 0 | 0 | 6010.44 | 0 | 0 | 6010.44
2022051621 | 2 | 0.79438 | 63550.4 | 0 | 0 | 0.53918 | 18871.3 | 0.01 | 140 | 40000 | 0 | 18871.3 | 0 | 140 | 0 | 0 | 4539.1 | 0 | 0 | 4539.1
2022051622 | 2 | 0.76109 | 60887.2 | 0 | 0 | 0.5763 | 20170.5 | 0 | 0 | 40000 | 0 | 20170.5 | 0 | 0 | 0 | 0 | 716.7 | 0 | 0 | 716.7
2022051623 | 2 | 0.70628 | 56502.4 | 0 | 0 | 0.55867 | 19553.45 | 0 | 0 | 40000 | 0 | 16502.4 | 3051.05 | 0 | 0 | 3051.05 | 0 | 0 | 0 | 0
2022051624 | 2 | 0.65179 | 52143.2 | 0 | 0 | 0.55349 | 19372.15 | 0 | 0 | 40000 | 0 | 12143.2 | 7228.95 | 0 | 0 | 7228.95 | 0 | 0 | 0 | 0
2022051701 | 3 | 0.60411 | 48328.8 | 0 | 0 | 0.54472 | 19065.2 | 0 | 0 | 40000 | 0 | 8328.8 | 10736.4 | 0 | 0 | 10736.4 | 0 | 0 | 0 | 0
2022051702 | 3 | 0.56788 | 45430.4 | 0 | 0 | 0.47712 | 16699.2 | 0 | 0 | 40000 | 0 | 5430.4 | 11268.8 | 0 | 0 | 11268.8 | 0 | 0 | 0 | 0
2022051703 | 3 | 0.54224 | 43379.2 | 0 | 0 | 0.4443 | 15550.5 | 0 | 0 | 40000 | 0 | 3379.2 | 12171.3 | 0 | 0 | 12171.3 | 0 | 0 | 0 | 0
2022051704 | 3 | 0.53087 | 42469.6 | 0 | 0 | 0.45512 | 15929.2 | 0 | 0 | 40000 | 0 | 2469.6 | 13459.6 | 0 | 0 | 13459.6 | 0 | 0 | 0 | 0
2022051705 | 3 | 0.53009 | 42407.2 | 0 | 0 | 0.50731 | 17755.85 | 0 | 0 | 40000 | 0 | 2407.2 | 15348.65 | 0 | 0 | 15348.65 | 0 | 0 | 0 | 0
2022051706 | 3 | 0.54697 | 43757.6 | 0 | 0 | 0.51298 | 17954.3 | 0 | 0 | 40000 | 0 | 3757.6 | 14196.7 | 0 | 0 | 14196.7 | 0 | 0 | 0 | 0
2022051707 | 3 | 0.5697 | 45576 | 0 | 0 | 0.50282 | 17598.7 | 0.00109 | 15.26 | 40000 | 0 | 5576 | 12022.7 | 0 | 15.26 | 12037.96 | 0 | 0 | 0 | 0
2022051708 | 3 | 0.58211 | 46568.8 | 0 | 0 | 0.50627 | 17719.45 | 0.07333 | 1026.62 | 40000 | 0 | 6568.8 | 11150.65 | 0 | 1026.62 | 12177.27 | 0 | 0 | 0 | 0
2022051709 | 3 | 0.60636 | 48508.8 | 0 | 0 | 0.52834 | 18491.9 | 0.31403 | 4396.42 | 40000 | 0 | 8508.8 | 9983.1 | 0 | 4396.42 | 14379.52 | 0 | 0 | 0 | 0
2022051710 | 3 | 0.64488 | 51590.4 | 0 | 0 | 0.60472 | 21165.2 | 0.41759 | 5846.26 | 40000 | 0 | 11590.4 | 9574.8 | 0 | 5846.26 | 15421.06 | 0 | 0 | 0 | 0
2022051711 | 3 | 0.68126 | 54500.8 | 0 | 0 | 0.61836 | 21642.6 | 0.42842 | 5997.88 | 40000 | 0 | 14500.8 | 7141.8 | 0 | 5997.88 | 13139.68 | 0 | 0 | 0 | 0
2022051712 | 3 | 0.7272 | 58176 | 0 | 0 | 0.61716 | 21600.6 | 0.48404 | 6776.56 | 40000 | 0 | 18176 | 3424.6 | 0 | 6776.56 | 10201.16 | 0 | 0 | 0 | 0
2022051713 | 3 | 0.76985 | 61588 | 0 | 0 | 0.63628 | 22269.8 | 0.44922 | 6289.08 | 40000 | 0 | 21588 | 681.8 | 0 | 6289.08 | 6970.88 | 0 | 0 | 0 | 0
2022051714 | 3 | 0.80929 | 64743.2 | 0 | 0 | 0.66329 | 23215.15 | 0.43891 | 6144.74 | 40000 | 0 | 23215.15 | 0 | 1528.05 | 4616.69 | 4616.69 | 0 | 0 | 0 | 0
2022051715 | 3 | 0.84191 | 67352.8 | 0 | 0 | 0.67658 | 23680.3 | 0.4554 | 6375.6 | 40000 | 0 | 23680.3 | 0 | 3672.5 | 2703.1 | 2703.1 | 0 | 0 | 0 | 0
2022051716 | 3 | 0.87061 | 69648.8 | 0 | 0 | 0.66552 | 23293.2 | 0.49798 | 6971.72 | 40000 | 0 | 23293.2 | 0 | 6355.6 | 616.12 | 616.12 | 0 | 0 | 0 | 0
2022051717 | 3 | 0.88708 | 70966.4 | 0 | 0 | 0.64638 | 22623.3 | 0.52748 | 7384.72 | 40000 | 0 | 22623.3 | 0 | 7384.72 | 0 | 0 | 958.38 | 0 | 0 | 958.38
2022051718 | 3 | 0.88328 | 70662.4 | 0 | 0 | 0.65387 | 22885.45 | 0.47795 | 6691.3 | 40000 | 0 | 22885.45 | 0 | 6691.3 | 0 | 0 | 1085.65 | 0 | 0 | 1085.65
2022051719 | 3 | 0.86032 | 68825.6 | 0 | 0 | 0.65933 | 23076.55 | 0.40844 | 5718.16 | 40000 | 0 | 23076.55 | 0 | 5718.16 | 0 | 0 | 30.89 | 0 | 0 | 30.89
2022051720 | 3 | 0.82469 | 65975.2 | 0 | 0 | 0.66018 | 23106.3 | 0.23175 | 3244.5 | 40000 | 0 | 23106.3 | 0 | 2868.9 | 375.6 | 375.6 | 0 | 0 | 0 | 0
2022051721 | 3 | 0.79625 | 63700 | 0 | 0 | 0.67027 | 23459.45 | 0.01883 | 263.62 | 40000 | 0 | 23459.45 | 0 | 240.55 | 23.07 | 23.07 | 0 | 0 | 0 | 0
2022051722 | 3 | 0.76601 | 61280.8 | 0 | 0 | 0.675 | 23625 | 0 | 0 | 40000 | 0 | 21280.8 | 2344.2 | 0 | 0 | 2344.2 | 0 | 0 | 0 | 0
2022051723 | 3 | 0.71475 | 57180 | 0 | 0 | 0.67581 | 23653.35 | 0 | 0 | 40000 | 0 | 17180 | 6473.35 | 0 | 0 | 6473.35 | 0 | 0 | 0 | 0
2022051724 | 3 | 0.66082 | 52865.6 | 0 | 0 | 0.68644 | 24025.4 | 0 | 0 | 40000 | 0 | 12865.6 | 11159.8 | 0 | 0 | 11159.8 | 0 | 0 | 0 | 0
2022051801 | 4 | 0.61711 | 49368.8 | 0 | 0 | 0.67974 | 23790.9 | 0 | 0 | 40000 | 0 | 9368.8 | 14422.1 | 0 | 0 | 14422.1 | 0 | 0 | 0 | 0
2022051802 | 4 | 0.58805 | 47044 | 0 | 0 | 0.68352 | 23923.2 | 0 | 0 | 40000 | 0 | 7044 | 16879.2 | 0 | 0 | 16879.2 | 0 | 0 | 0 | 0
2022051803 | 4 | 0.56488 | 45190.4 | 0 | 0 | 0.66876 | 23406.6 | 0 | 0 | 40000 | 0 | 5190.4 | 18216.2 | 0 | 0 | 18216.2 | 0 | 0 | 0 | 0
2022051804 | 4 | 0.55077 | 44061.6 | 0 | 0 | 0.65131 | 22795.85 | 0 | 0 | 40000 | 0 | 4061.6 | 18734.25 | 0 | 0 | 18734.25 | 0 | 0 | 0 | 0
2022051805 | 4 | 0.54718 | 43774.4 | 0 | 0 | 0.61999 | 21699.65 | 0 | 0 | 40000 | 0 | 3774.4 | 17925.25 | 0 | 0 | 17925.25 | 0 | 0 | 0 | 0
2022051806 | 4 | 0.56097 | 44877.6 | 0 | 0 | 0.59734 | 20906.9 | 0 | 0 | 40000 | 0 | 4877.6 | 16029.3 | 0 | 0 | 16029.3 | 0 | 0 | 0 | 0
2022051807 | 4 | 0.58068 | 46454.4 | 0 | 0 | 0.58136 | 20347.6 | 0.00185 | 25.9 | 40000 | 0 | 6454.4 | 13893.2 | 0 | 25.9 | 13919.1 | 0 | 0 | 0 | 0
2022051808 | 4 | 0.59215 | 47372 | 0 | 0 | 0.55873 | 19555.55 | 0.13616 | 1906.24 | 40000 | 0 | 7372 | 12183.55 | 0 | 1906.24 | 14089.79 | 0 | 0 | 0 | 0
2022051809 | 4 | 0.61803 | 49442.4 | 0 | 0 | 0.50103 | 17536.05 | 0.50539 | 7075.46 | 40000 | 0 | 9442.4 | 8093.65 | 0 | 7075.46 | 15169.11 | 0 | 0 | 0 | 0
2022051810 | 4 | 0.64856 | 51884.8 | 0 | 0 | 0.49366 | 17278.1 | 0.6877 | 9627.8 | 40000 | 0 | 11884.8 | 5393.3 | 0 | 9627.8 | 15021.1 | 0 | 0 | 0 | 0
2022051811 | 4 | 0.68275 | 54620 | 0 | 0 | 0.4748 | 16618 | 0.76081 | 10651.34 | 40000 | 0 | 14620 | 1998 | 0 | 10651.34 | 12649.34 | 0 | 0 | 0 | 0
2022051812 | 4 | 0.71984 | 57587.2 | 0 | 0 | 0.43733 | 15306.55 | 0.77848 | 10898.72 | 40000 | 0 | 15306.55 | 0 | 2280.65 | 8618.07 | 8618.07 | 0 | 0 | 0 | 0
2022051813 | 4 | 0.76168 | 60934.4 | 0 | 0 | 0.41349 | 14472.15 | 0.77846 | 10898.44 | 40000 | 0 | 14472.15 | 0 | 6462.25 | 4436.19 | 4436.19 | 0 | 0 | 0 | 0
2022051814 | 4 | 0.798 | 63840 | 0 | 0 | 0.40493 | 14172.55 | 0.76327 | 10685.78 | 40000 | 0 | 14172.55 | 0 | 9667.45 | 1018.33 | 1018.33 | 0 | 0 | 0 | 0
2022051815 | 4 | 0.82768 | 66214.4 | 0 | 0 | 0.38228 | 13379.8 | 0.7494 | 10491.6 | 40000 | 0 | 13379.8 | 0 | 10491.6 | 0 | 0 | 2343 | 0 | 0 | 2343
2022051816 | 4 | 0.85477 | 68381.6 | 0 | 0 | 0.37358 | 13075.3 | 0.7341 | 10277.4 | 40000 | 0 | 13075.3 | 0 | 10277.4 | 0 | 0 | 5028.9 | 0 | 0 | 5028.9
2022051817 | 4 | 0.87604 | 70083.2 | 0 | 0 | 0.37133 | 12996.55 | 0.71918 | 10068.52 | 40000 | 0 | 12996.55 | 0 | 10068.52 | 0 | 0 | 7018.13 | 0 | 0 | 7018.13
2022051818 | 4 | 0.88015 | 70412 | 0 | 0 | 0.36399 | 12739.65 | 0.67547 | 9456.58 | 40000 | 0 | 12739.65 | 0 | 9456.58 | 0 | 0 | 8215.77 | 0 | 0 | 8215.77
2022051819 | 4 | 0.86102 | 68881.6 | 0 | 0 | 0.36637 | 12822.95 | 0.55411 | 7757.54 | 40000 | 0 | 12822.95 | 0 | 7757.54 | 0 | 0 | 8301.11 | 0 | 0 | 8301.11
2022051820 | 4 | 0.82673 | 66138.4 | 0 | 0 | 0.37113 | 12989.55 | 0.24301 | 3402.14 | 40000 | 0 | 12989.55 | 0 | 3402.14 | 0 | 0 | 9746.71 | 0 | 0 | 9746.71
2022051821 | 4 | 0.79588 | 63670.4 | 0 | 0 | 0.40406 | 14142.1 | 0.01361 | 190.54 | 40000 | 0 | 14142.1 | 0 | 190.54 | 0 | 0 | 9337.76 | 0 | 0 | 9337.76
2022051822 | 4 | 0.76703 | 61362.4 | 0 | 0 | 0.47987 | 16795.45 | 0 | 0 | 40000 | 0 | 16795.45 | 0 | 0 | 0 | 0 | 4566.95 | 0 | 0 | 4566.95
2022051823 | 4 | 0.71656 | 57324.8 | 0 | 0 | 0.54965 | 19237.75 | 0 | 0 | 40000 | 0 | 17324.8 | 1912.95 | 0 | 0 | 1912.95 | 0 | 0 | 0 | 0
2022051824 | 4 | 0.66392 | 53113.6 | 0 | 0 | 0.5875 | 20562.5 | 0 | 0 | 40000 | 0 | 13113.6 | 7448.9 | 0 | 0 | 7448.9 | 0 | 0 | 0 | 0
2022051901 | 5 | 0.62167 | 49733.6 | 0 | 0 | 0.58608 | 20512.8 | 0 | 0 | 40000 | 0 | 9733.6 | 10779.2 | 0 | 0 | 10779.2 | 0 | 0 | 0 | 0
2022051902 | 5 | 0.58777 | 47021.6 | 0 | 0 | 0.59898 | 20964.3 | 0 | 0 | 40000 | 0 | 7021.6 | 13942.7 | 0 | 0 | 13942.7 | 0 | 0 | 0 | 0
2022051903 | 5 | 0.56544 | 45235.2 | 0 | 0 | 0.61618 | 21566.3 | 0 | 0 | 40000 | 0 | 5235.2 | 16331.1 | 0 | 0 | 16331.1 | 0 | 0 | 0 | 0
2022051904 | 5 | 0.55279 | 44223.2 | 0 | 0 | 0.61465 | 21512.75 | 0 | 0 | 40000 | 0 | 4223.2 | 17289.55 | 0 | 0 | 17289.55 | 0 | 0 | 0 | 0
2022051905 | 5 | 0.54782 | 43825.6 | 0 | 0 | 0.55047 | 19266.45 | 0 | 0 | 40000 | 0 | 3825.6 | 15440.85 | 0 | 0 | 15440.85 | 0 | 0 | 0 | 0
2022051906 | 5 | 0.56285 | 45028 | 0 | 0 | 0.46987 | 16445.45 | 0 | 0 | 40000 | 0 | 5028 | 11417.45 | 0 | 0 | 11417.45 | 0 | 0 | 0 | 0
2022051907 | 5 | 0.58394 | 46715.2 | 0 | 0 | 0.43393 | 15187.55 | 0.00112 | 15.68 | 40000 | 0 | 6715.2 | 8472.35 | 0 | 15.68 | 8488.03 | 0 | 0 | 0 | 0
2022051908 | 5 | 0.59257 | 47405.6 | 0 | 0 | 0.34605 | 12111.75 | 0.12481 | 1747.34 | 40000 | 0 | 7405.6 | 4706.15 | 0 | 1747.34 | 6453.49 | 0 | 0 | 0 | 0
2022051909 | 5 | 0.61712 | 49369.6 | 0 | 0 | 0.35026 | 12259.1 | 0.4831 | 6763.4 | 40000 | 0 | 9369.6 | 2889.5 | 0 | 6763.4 | 9652.9 | 0 | 0 | 0 | 0
2022051910 | 5 | 0.65505 | 52404 | 0 | 0 | 0.38306 | 13407.1 | 0.69055 | 9667.7 | 40000 | 0 | 12404 | 1003.1 | 0 | 9667.7 | 10670.8 | 0 | 0 | 0 | 0
2022051911 | 5 | 0.69465 | 55572 | 0 | 0 | 0.40526 | 14184.1 | 0.75239 | 10533.46 | 40000 | 0 | 14184.1 | 0 | 1387.9 | 9145.56 | 9145.56 | 0 | 0 | 0 | 0
2022051912 | 5 | 0.73396 | 58716.8 | 0 | 0 | 0.40188 | 14065.8 | 0.77905 | 10906.7 | 40000 | 0 | 14065.8 | 0 | 4651 | 6255.7 | 6255.7 | 0 | 0 | 0 | 0
2022051913 | 5 | 0.77286 | 61828.8 | 0 | 0 | 0.38439 | 13453.65 | 0.80386 | 11254.04 | 40000 | 0 | 13453.65 | 0 | 8375.15 | 2878.89 | 2878.89 | 0 | 0 | 0 | 0
2022051914 | 5 | 0.81182 | 64945.6 | 0 | 0 | 0.41316 | 14460.6 | 0.81441 | 11401.74 | 40000 | 0 | 14460.6 | 0 | 10485 | 916.74 | 916.74 | 0 | 0 | 0 | 0
2022051915 | 5 | 0.84728 | 67782.4 | 0 | 0 | 0.47704 | 16696.4 | 0.79853 | 11179.42 | 40000 | 0 | 16696.4 | 0 | 11086 | 93.42 | 93.42 | 0 | 0 | 0 | 0
2022051916 | 5 | 0.87427 | 69941.6 | 0 | 0 | 0.53284 | 18649.4 | 0.76316 | 10684.24 | 40000 | 0 | 18649.4 | 0 | 10684.24 | 0 | 0 | 607.96 | 0 | 0 | 607.96
2022051917 | 5 | 0.89168 | 71334.4 | 0 | 0 | 0.56379 | 19732.65 | 0.72939 | 10211.46 | 40000 | 0 | 19732.65 | 0 | 10211.46 | 0 | 0 | 1390.29 | 0 | 0 | 1390.29
2022051918 | 5 | 0.88939 | 71151.2 | 0 | 0 | 0.57747 | 20211.45 | 0.69475 | 9726.5 | 40000 | 0 | 20211.45 | 0 | 9726.5 | 0 | 0 | 1213.25 | 0 | 0 | 1213.25
2022051919 | 5 | 0.86257 | 69005.6 | 0 | 0 | 0.57984 | 20294.4 | 0.57801 | 8092.14 | 40000 | 0 | 20294.4 | 0 | 8092.14 | 0 | 0 | 619.06 | 0 | 0 | 619.06
2022051920 | 5 | 0.82616 | 66092.8 | 0 | 0 | 0.57146 | 20001.1 | 0.27816 | 3894.24 | 40000 | 0 | 20001.1 | 0 | 3894.24 | 0 | 0 | 2197.46 | 0 | 0 | 2197.46
2022051921 | 5 | 0.79856 | 63884.8 | 0 | 0 | 0.58718 | 20551.3 | 0.022 | 308 | 40000 | 0 | 20551.3 | 0 | 308 | 0 | 0 | 3025.5 | 0 | 0 | 3025.5
2022051922 | 5 | 0.77213 | 61770.4 | 0 | 0 | 0.65573 | 22950.55 | 0 | 0 | 40000 | 0 | 21770.4 | 1180.15 | 0 | 0 | 1180.15 | 0 | 0 | 0 | 0
2022051923 | 5 | 0.72792 | 58233.6 | 0 | 0 | 0.7058 | 24703 | 0 | 0 | 40000 | 0 | 18233.6 | 6469.4 | 0 | 0 | 6469.4 | 0 | 0 | 0 | 0
2022051924 | 5 | 0.67897 | 54317.6 | 0 | 0 | 0.72929 | 25525.15 | 0 | 0 | 40000 | 0 | 14317.6 | 11207.55 | 0 | 0 | 11207.55 | 0 | 0 | 0 | 0
2022052001 | 6 | 0.63279 | 50623.2 | 0 | 0 | 0.72668 | 25433.8 | 0 | 0 | 40000 | 0 | 10623.2 | 14810.6 | 0 | 0 | 14810.6 | 0 | 0 | 0 | 0
2022052002 | 6 | 0.60365 | 48292 | 0 | 0 | 0.7259 | 25406.5 | 0 | 0 | 40000 | 0 | 8292 | 17114.5 | 0 | 0 | 17114.5 | 0 | 0 | 0 | 0
2022052003 | 6 | 0.58343 | 46674.4 | 0 | 0 | 0.72664 | 25432.4 | 0 | 0 | 40000 | 0 | 6674.4 | 18758 | 0 | 0 | 18758 | 0 | 0 | 0 | 0
2022052004 | 6 | 0.57108 | 45686.4 | 0 | 0 | 0.7186 | 25151 | 0 | 0 | 40000 | 0 | 5686.4 | 19464.6 | 0 | 0 | 19464.6 | 0 | 0 | 0 | 0
2022052005 | 6 | 0.57004 | 45603.2 | 0 | 0 | 0.707 | 24745 | 0 | 0 | 40000 | 0 | 5603.2 | 19141.8 | 0 | 0 | 19141.8 | 0 | 0 | 0 | 0
2022052006 | 6 | 0.58347 | 46677.6 | 0 | 0 | 0.67993 | 23797.55 | 0 | 0 | 40000 | 0 | 6677.6 | 17119.95 | 0 | 0 | 17119.95 | 0 | 0 | 0 | 0
2022052007 | 6 | 0.60776 | 48620.8 | 0 | 0 | 0.66564 | 23297.4 | 0.00109 | 15.26 | 40000 | 0 | 8620.8 | 14676.6 | 0 | 15.26 | 14691.86 | 0 | 0 | 0 | 0
2022052008 | 6 | 0.62332 | 49865.6 | 0 | 0 | 0.64218 | 22476.3 | 0.11949 | 1672.86 | 40000 | 0 | 9865.6 | 12610.7 | 0 | 1672.86 | 14283.56 | 0 | 0 | 0 | 0
2022052009 | 6 | 0.64623 | 51698.4 | 0 | 0 | 0.61326 | 21464.1 | 0.43664 | 6112.96 | 40000 | 0 | 11698.4 | 9765.7 | 0 | 6112.96 | 15878.66 | 0 | 0 | 0 | 0
2022052010 | 6 | 0.68101 | 54480.8 | 0 | 0 | 0.59546 | 20841.1 | 0.57236 | 8013.04 | 40000 | 0 | 14480.8 | 6360.3 | 0 | 8013.04 | 14373.34 | 0 | 0 | 0 | 0
2022052011 | 6 | 0.72171 | 57736.8 | 0 | 0 | 0.55808 | 19532.8 | 0.70859 | 9920.26 | 40000 | 0 | 17736.8 | 1796 | 0 | 9920.26 | 11716.26 | 0 | 0 | 0 | 0
2022052012 | 6 | 0.7608 | 60864 | 0 | 0 | 0.49494 | 17322.9 | 0.74382 | 10413.48 | 40000 | 0 | 17322.9 | 0 | 3541.1 | 6872.38 | 6872.38 | 0 | 0 | 0 | 0
2022052013 | 6 | 0.799 | 63920 | 0 | 0 | 0.42121 | 14742.35 | 0.75797 | 10611.58 | 40000 | 0 | 14742.35 | 0 | 9177.65 | 1433.93 | 1433.93 | 0 | 0 | 0 | 0
2022052014 | 6 | 0.83448 | 66758.4 | 0 | 0 | 0.35719 | 12501.65 | 0.75923 | 10629.22 | 40000 | 0 | 12501.65 | 0 | 10629.22 | 0 | 0 | 3627.53 | 0 | 0 | 3627.53
2022052015 | 6 | 0.8554 | 68432 | 0 | 0 | 0.30029 | 10510.15 | 0.74562 | 10438.68 | 40000 | 0 | 10510.15 | 0 | 10438.68 | 0 | 0 | 7483.17 | 0 | 0 | 7483.17
2022052016 | 6 | 0.86869 | 69495.2 | 0 | 0 | 0.28431 | 9950.85 | 0.7323 | 10252.2 | 40000 | 0 | 9950.85 | 0 | 10252.2 | 0 | 0 | 9292.15 | 0 | 0 | 9292.15
2022052017 | 6 | 0.8742 | 69936 | 0 | 0 | 0.30165 | 10557.75 | 0.7027 | 9837.8 | 40000 | 0 | 10557.75 | 0 | 9837.8 | 0 | 0 | 9540.45 | 0 | 0 | 9540.45
2022052018 | 6 | 0.87141 | 69712.8 | 0 | 0 | 0.35265 | 12342.75 | 0.62905 | 8806.7 | 40000 | 0 | 12342.75 | 0 | 8806.7 | 0 | 0 | 8563.35 | 0 | 0 | 8563.35
2022052019 | 6 | 0.84561 | 67648.8 | 0 | 0 | 0.39796 | 13928.6 | 0.47622 | 6667.08 | 40000 | 0 | 13928.6 | 0 | 6667.08 | 0 | 0 | 7053.12 | 0 | 0 | 7053.12
2022052020 | 6 | 0.81151 | 64920.8 | 0 | 0 | 0.43855 | 15349.25 | 0.244 | 3416 | 40000 | 0 | 15349.25 | 0 | 3416 | 0 | 0 | 6155.55 | 0 | 0 | 6155.55
2022052021 | 6 | 0.78426 | 62740.8 | 0 | 0 | 0.43235 | 15132.25 | 0.02796 | 391.44 | 40000 | 0 | 15132.25 | 0 | 391.44 | 0 | 0 | 7217.11 | 0 | 0 | 7217.11
2022052022 | 6 | 0.76052 | 60841.6 | 0 | 0 | 0.46612 | 16314.2 | 0 | 0 | 40000 | 0 | 16314.2 | 0 | 0 | 0 | 0 | 4527.4 | 0 | 0 | 4527.4
2022052023 | 6 | 0.72545 | 58036 | 0 | 0 | 0.52802 | 18480.7 | 0 | 0 | 40000 | 0 | 18036 | 444.7 | 0 | 0 | 444.7 | 0 | 0 | 0 | 0
2022052024 | 6 | 0.69033 | 55226.4 | 0 | 0 | 0.59068 | 20673.8 | 0 | 0 | 40000 | 0 | 15226.4 | 5447.4 | 0 | 0 | 5447.4 | 0 | 0 | 0 | 0
2022052101 | 7 | 0.65035 | 52028 | 0 | 0 | 0.59402 | 20790.7 | 0 | 0 | 40000 | 0 | 12028 | 8762.7 | 0 | 0 | 8762.7 | 0 | 0 | 0 | 0
2022052102 | 7 | 0.61866 | 49492.8 | 0 | 0 | 0.58433 | 20451.55 | 0 | 0 | 40000 | 0 | 9492.8 | 10958.75 | 0 | 0 | 10958.75 | 0 | 0 | 0 | 0
2022052103 | 7 | 0.59405 | 47524 | 0 | 0 | 0.57809 | 20233.15 | 0 | 0 | 40000 | 0 | 7524 | 12709.15 | 0 | 0 | 12709.15 | 0 | 0 | 0 | 0
2022052104 | 7 | 0.5776 | 46208 | 0 | 0 | 0.57146 | 20001.1 | 0 | 0 | 40000 | 0 | 6208 | 13793.1 | 0 | 0 | 13793.1 | 0 | 0 | 0 | 0
2022052105 | 7 | 0.56836 | 45468.8 | 0 | 0 | 0.57564 | 20147.4 | 0 | 0 | 40000 | 0 | 5468.8 | 14678.6 | 0 | 0 | 14678.6 | 0 | 0 | 0 | 0
2022052106 | 7 | 0.56689 | 45351.2 | 0 | 0 | 0.57078 | 19977.3 | 0 | 0 | 40000 | 0 | 5351.2 | 14626.1 | 0 | 0 | 14626.1 | 0 | 0 | 0 | 0
2022052107 | 7 | 0.57017 | 45613.6 | 0 | 0 | 0.56125 | 19643.75 | 0.00172 | 24.08 | 40000 | 0 | 5613.6 | 14030.15 | 0 | 24.08 | 14054.23 | 0 | 0 | 0 | 0
2022052108 | 7 | 0.58781 | 47024.8 | 0 | 0 | 0.60764 | 21267.4 | 0.12685 | 1775.9 | 40000 | 0 | 7024.8 | 14242.6 | 0 | 1775.9 | 16018.5 | 0 | 0 | 0 | 0
2022052109 | 7 | 0.61811 | 49448.8 | 0 | 0 | 0.62341 | 21819.35 | 0.27523 | 3853.22 | 40000 | 0 | 9448.8 | 12370.55 | 0 | 3853.22 | 16223.77 | 0 | 0 | 0 | 0
2022052110 | 7 | 0.65453 | 52362.4 | 0 | 0 | 0.60654 | 21228.9 | 0.37573 | 5260.22 | 40000 | 0 | 12362.4 | 8866.5 | 0 | 5260.22 | 14126.72 | 0 | 0 | 0 | 0
2022052111 | 7 | 0.69731 | 55784.8 | 0 | 0 | 0.5833 | 20415.5 | 0.53976 | 7556.64 | 40000 | 0 | 15784.8 | 4630.7 | 0 | 7556.64 | 12187.34 | 0 | 0 | 0 | 0
2022052112 | 7 | 0.73835 | 59068 | 0 | 0 | 0.56848 | 19896.8 | 0.57452 | 8043.28 | 40000 | 0 | 19068 | 828.8 | 0 | 8043.28 | 8872.08 | 0 | 0 | 0 | 0
2022052113 | 7 | 0.77591 | 62072.8 | 0 | 0 | 0.53201 | 18620.35 | 0.61398 | 8595.72 | 40000 | 0 | 18620.35 | 0 | 3452.45 | 5143.27 | 5143.27 | 0 | 0 | 0 | 0
2022052114 | 7 | 0.80585 | 64468 | 0 | 0 | 0.49726 | 17404.1 | 0.64108 | 8975.12 | 40000 | 0 | 17404.1 | 0 | 7063.9 | 1911.22 | 1911.22 | 0 | 0 | 0 | 0
2022052115 | 7 | 0.82704 | 66163.2 | 0 | 0 | 0.46906 | 16417.1 | 0.6929 | 9700.6 | 40000 | 0 | 16417.1 | 0 | 9700.6 | 0 | 0 | 45.5 | 0 | 0 | 45.5
2022052116 | 7 | 0.83792 | 67033.6 | 0 | 0 | 0.45231 | 15830.85 | 0.74577 | 10440.78 | 40000 | 0 | 15830.85 | 0 | 10440.78 | 0 | 0 | 761.97 | 0 | 0 | 761.97
2022052117 | 7 | 0.83696 | 66956.8 | 0 | 0 | 0.45759 | 16015.65 | 0.71731 | 10042.34 | 40000 | 0 | 16015.65 | 0 | 10042.34 | 0 | 0 | 898.81 | 0 | 0 | 898.81
2022052118 | 7 | 0.81733 | 65386.4 | 0 | 0 | 0.49874 | 17455.9 | 0.64487 | 9028.18 | 40000 | 0 | 17455.9 | 0 | 7930.5 | 1097.68 | 1097.68 | 0 | 0 | 0 | 0
2022052119 | 7 | 0.77813 | 62250.4 | 0 | 0 | 0.54866 | 19203.1 | 0.46136 | 6459.04 | 40000 | 0 | 19203.1 | 0 | 3047.3 | 3411.74 | 3411.74 | 0 | 0 | 0 | 0
2022052120 | 7 | 0.7396 | 59168 | 0 | 0 | 0.59364 | 20777.4 | 0.23006 | 3220.84 | 40000 | 0 | 19168 | 1609.4 | 0 | 3220.84 | 4830.24 | 0 | 0 | 0 | 0
2022052121 | 7 | 0.71526 | 57220.8 | 0 | 0 | 0.63045 | 22065.75 | 0.02212 | 309.68 | 40000 | 0 | 17220.8 | 4844.95 | 0 | 309.68 | 5154.63 | 0 | 0 | 0 | 0
2022052122 | 7 | 0.69017 | 55213.6 | 0 | 0 | 0.62492 | 21872.2 | 0 | 0 | 40000 | 0 | 15213.6 | 6658.6 | 0 | 0 | 6658.6 | 0 | 0 | 0 | 0
2022052123 | 7 | 0.65478 | 52382.4 | 0 | 0 | 0.66017 | 23105.95 | 0 | 0 | 40000 | 0 | 12382.4 | 10723.55 | 0 | 0 | 10723.55 | 0 | 0 | 0 | 0
2022052124 | 7 | 0.61304 | 49043.2 | 0 | 0 | 0.64984 | 22744.4 | 0 | 0 | 40000 | 0 | 9043.2 | 13701.2 | 0 | 0 | 13701.2 | 0 | 0 | 0 | 0
2022052201 | 1 | 0.57436 | 45948.8 | 0 | 0 | 0.62847 | 21996.45 | 0 | 0 | 40000 | 0 | 5948.8 | 16047.65 | 0 | 0 | 16047.65 | 0 | 0 | 0 | 0
2022052202 | 1 | 0.54086 | 43268.8 | 0 | 0 | 0.61376 | 21481.6 | 0 | 0 | 40000 | 0 | 3268.8 | 18212.8 | 0 | 0 | 18212.8 | 0 | 0 | 0 | 0
2022052203 | 1 | 0.51391 | 41112.8 | 0 | 0 | 0.60291 | 21101.85 | 0 | 0 | 40000 | 0 | 1112.8 | 19989.05 | 0 | 0 | 19989.05 | 0 | 0 | 0 | 0
2022052204 | 1 | 0.49169 | 39335.2 | 0 | 0 | 0.58383 | 20434.05 | 0 | 0 | 39335.2 | 664.8 | 0 | 20434.05 | 0 | 0 | 21098.85 | 0 | 0 | 0 | 0
2022052205 | 1 | 0.47124 | 37699.2 | 0 | 0 | 0.5589 | 19561.5 | 0 | 0 | 37699.2 | 2300.8 | 0 | 19561.5 | 0 | 0 | 21862.3 | 0 | 0 | 0 | 0
2022052206 | 1 | 0.46457 | 37165.6 | 0 | 0 | 0.5369 | 18791.5 | 0 | 0 | 37165.6 | 2834.4 | 0 | 18791.5 | 0 | 0 | 21625.9 | 0 | 0 | 0 | 0
2022052207 | 1 | 0.46217 | 36973.6 | 0 | 0 | 0.52835 | 18492.25 | 0.00017 | 2.38 | 36973.6 | 3026.4 | 0 | 18492.25 | 0 | 2.38 | 21521.03 | 0 | 0 | 0 | 0
2022052208 | 1 | 0.46845 | 37476 | 0 | 0 | 0.51829 | 18140.15 | 0.03226 | 451.64 | 37476 | 2524 | 0 | 18140.15 | 0 | 451.64 | 21115.79 | 0 | 0 | 0 | 0
2022052209 | 1 | 0.48483 | 38786.4 | 0 | 0 | 0.51235 | 17932.25 | 0.11969 | 1675.66 | 38786.4 | 1213.6 | 0 | 17932.25 | 0 | 1675.66 | 20821.51 | 0 | 0 | 0 | 0
2022052210 | 1 | 0.50577 | 40461.6 | 0 | 0 | 0.52415 | 18345.25 | 0.19196 | 2687.44 | 40000 | 0 | 461.6 | 17883.65 | 0 | 2687.44 | 20571.09 | 0 | 0 | 0 | 0
2022052211 | 1 | 0.52148 | 41718.4 | 0 | 0 | 0.4578 | 16023 | 0.34577 | 4840.78 | 40000 | 0 | 1718.4 | 14304.6 | 0 | 4840.78 | 19145.38 | 0 | 0 | 0 | 0
2022052212 | 1 | 0.53699 | 42959.2 | 0 | 0 | 0.33076 | 11576.6 | 0.48642 | 6809.88 | 40000 | 0 | 2959.2 | 8617.4 | 0 | 6809.88 | 15427.28 | 0 | 0 | 0 | 0
2022052213 | 1 | 0.55546 | 44436.8 | 0 | 0 | 0.26128 | 9144.8 | 0.58226 | 8151.64 | 40000 | 0 | 4436.8 | 4708 | 0 | 8151.64 | 12859.64 | 0 | 0 | 0 | 0
2022052214 | 1 | 0.57534 | 46027.2 | 0 | 0 | 0.20219 | 7076.65 | 0.62457 | 8743.98 | 40000 | 0 | 6027.2 | 1049.45 | 0 | 8743.98 | 9793.43 | 0 | 0 | 0 | 0
2022052215 | 1 | 0.59615 | 47692 | 0 | 0 | 0.13657 | 4779.95 | 0.64154 | 8981.56 | 40000 | 0 | 4779.95 | 0 | 2912.05 | 6069.51 | 6069.51 | 0 | 0 | 0 | 0
2022052216 | 1 | 0.61535 | 49228 | 0 | 0 | 0.09887 | 3460.45 | 0.63435 | 8880.9 | 40000 | 0 | 3460.45 | 0 | 5767.55 | 3113.35 | 3113.35 | 0 | 0 | 0 | 0
2022052217 | 1 | 0.63296 | 50636.8 | 0 | 0 | 0.08766 | 3068.1 | 0.58718 | 8220.52 | 40000 | 0 | 3068.1 | 0 | 7568.7 | 651.82 | 651.82 | 0 | 0 | 0 | 0
2022052218 | 1 | 0.6421 | 51368 | 0 | 0 | 0.08586 | 3005.1 | 0.48138 | 6739.32 | 40000 | 0 | 3005.1 | 0 | 6739.32 | 0 | 0 | 1623.58 | 0 | 0 | 1623.58
2022052219 | 1 | 0.63959 | 51167.2 | 0 | 0 | 0.1271 | 4448.5 | 0.32121 | 4496.94 | 40000 | 0 | 4448.5 | 0 | 4496.94 | 0 | 0 | 2221.76 | 0 | 0 | 2221.76
2022052220 | 1 | 0.62451 | 49960.8 | 0 | 0 | 0.16289 | 5701.15 | 0.13178 | 1844.92 | 40000 | 0 | 5701.15 | 0 | 1844.92 | 0 | 0 | 2414.73 | 0 | 0 | 2414.73
2022052221 | 1 | 0.61477 | 49181.6 | 0 | 0 | 0.18189 | 6366.15 | 0.01186 | 166.04 | 40000 | 0 | 6366.15 | 0 | 166.04 | 0 | 0 | 2649.41 | 0 | 0 | 2649.41
2022052222 | 1 | 0.60241 | 48192.8 | 0 | 0 | 0.21661 | 7581.35 | 0.00502 | 70.28 | 40000 | 0 | 7581.35 | 0 | 70.28 | 0 | 0 | 541.17 | 0 | 0 | 541.17
2022052223 | 1 | 0.57054 | 45643.2 | 0 | 0 | 0.25652 | 8978.2 | 0.00502 | 70.28 | 40000 | 0 | 5643.2 | 3335 | 0 | 70.28 | 3405.28 | 0 | 0 | 0 | 0
2022052224 | 1 | 0.52984 | 42387.2 | 0 | 0 | 0.28774 | 10070.9 | 0.00502 | 70.28 | 40000 | 0 | 2387.2 | 7683.7 | 0 | 70.28 | 7753.98 | 0 | 0 | 0 | 0
2022052301 | 2 | 0.49595 | 39676 | 0 | 0 | 0.29495 | 10323.25 | 0.00502 | 70.28 | 39676 | 324 | 0 | 10323.25 | 0 | 70.28 | 10717.53 | 0 | 0 | 0 | 0
2022052302 | 2 | 0.47244 | 37795.2 | 0 | 0 | 0.28687 | 10040.45 | 0.00502 | 70.28 | 37795.2 | 2204.8 | 0 | 10040.45 | 0 | 70.28 | 12315.53 | 0 | 0 | 0 | 0
2022052303 | 2 | 0.4579 | 36632 | 0 | 0 | 0.25742 | 9009.7 | 0.00502 | 70.28 | 36632 | 3368 | 0 | 9009.7 | 0 | 70.28 | 12447.98 | 0 | 0 | 0 | 0
2022052304 | 2 | 0.45461 | 36368.8 | 0 | 0 | 0.23854 | 8348.9 | 0.00502 | 70.28 | 36368.8 | 3631.2 | 0 | 8348.9 | 0 | 70.28 | 12050.38 | 0 | 0 | 0 | 0
2022052305 | 2 | 0.457 | 36560 | 0 | 0 | 0.22907 | 8017.45 | 0.00355 | 49.7 | 36560 | 3440 | 0 | 8017.45 | 0 | 49.7 | 11507.15 | 0 | 0 | 0 | 0
2022052306 | 2 | 0.47765 | 38212 | 0 | 0 | 0.22731 | 7955.85 | 0 | 0 | 38212 | 1788 | 0 | 7955.85 | 0 | 0 | 9743.85 | 0 | 0 | 0 | 0
2022052307 | 2 | 0.50368 | 40294.4 | 0 | 0 | 0.22847 | 7996.45 | 0.00043 | 6.02 | 40000 | 0 | 294.4 | 7702.05 | 0 | 6.02 | 7708.07 | 0 | 0 | 0 | 0
2022052308 | 2 | 0.51806 | 41444.8 | 0 | 0 | 0.22763 | 7967.05 | 0.03736 | 523.04 | 40000 | 0 | 1444.8 | 6522.25 | 0 | 523.04 | 7045.29 | 0 | 0 | 0 | 0
2022052309 | 2 | 0.53048 | 42438.4 | 0 | 0 | 0.229 | 8015 | 0.1419 | 1986.6 | 40000 | 0 | 2438.4 | 5576.6 | 0 | 1986.6 | 7563.2 | 0 | 0 | 0 | 0
2022052310 | 2 | 0.54595 | 43676 | 0 | 0 | 0.23477 | 8216.95 | 0.28127 | 3937.78 | 40000 | 0 | 3676 | 4540.95 | 0 | 3937.78 | 8478.73 | 0 | 0 | 0 | 0
2022052311 | 2 | 0.56583 | 45266.4 | 0 | 0 | 0.23407 | 8192.45 | 0.37663 | 5272.82 | 40000 | 0 | 5266.4 | 2926.05 | 0 | 5272.82 | 8198.87 | 0 | 0 | 0 | 0
2022052312 | 2 | 0.59228 | 47382.4 | 0 | 0 | 0.26439 | 9253.65 | 0.44429 | 6220.06 | 40000 | 0 | 7382.4 | 1871.25 | 0 | 6220.06 | 8091.31 | 0 | 0 | 0 | 0
2022052313 | 2 | 0.61926 | 49540.8 | 0 | 0 | 0.31051 | 10867.85 | 0.50993 | 7139.02 | 40000 | 0 | 9540.8 | 1327.05 | 0 | 7139.02 | 8466.07 | 0 | 0 | 0 | 0
2022052314 | 2 | 0.64873 | 51898.4 | 0 | 0 | 0.34309 | 12008.15 | 0.51896 | 7265.44 | 40000 | 0 | 11898.4 | 109.75 | 0 | 7265.44 | 7375.19 | 0 | 0 | 0 | 0
2022052315 | 2 | 0.67343 | 53874.4 | 0 | 0 | 0.36852 | 12898.2 | 0.47688 | 6676.32 | 40000 | 0 | 12898.2 | 0 | 976.2 | 5700.12 | 5700.12 | 0 | 0 | 0 | 0
2022052316 | 2 | 0.69606 | 55684.8 | 0 | 0 | 0.40385 | 14134.75 | 0.47946 | 6712.44 | 40000 | 0 | 14134.75 | 0 | 1550.05 | 5162.39 | 5162.39 | 0 | 0 | 0 | 0
2022052317 | 2 | 0.70533 | 56426.4 | 0 | 0 | 0.41157 | 14404.95 | 0.52335 | 7326.9 | 40000 | 0 | 14404.95 | 0 | 2021.45 | 5305.45 | 5305.45 | 0 | 0 | 0 | 0
2022052318 | 2 | 0.70245 | 56196 | 0 | 0 | 0.44866 | 15703.1 | 0.53808 | 7533.12 | 40000 | 0 | 15703.1 | 0 | 492.9 | 7040.22 | 7040.22 | 0 | 0 | 0 | 0
2022052319 | 2 | 0.68585 | 54868 | 0 | 0 | 0.49966 | 17488.1 | 0.4096 | 5734.4 | 40000 | 0 | 14868 | 2620.1 | 0 | 5734.4 | 8354.5 | 0 | 0 | 0 | 0
2022052320 | 2 | 0.66299 | 53039.2 | 0 | 0 | 0.53255 | 18639.25 | 0.14009 | 1961.26 | 40000 | 0 | 13039.2 | 5600.05 | 0 | 1961.26 | 7561.31 | 0 | 0 | 0 | 0
2022052321 | 2 | 0.65302 | 52241.6 | 0 | 0 | 0.55802 | 19530.7 | 0.01255 | 175.7 | 40000 | 0 | 12241.6 | 7289.1 | 0 | 175.7 | 7464.8 | 0 | 0 | 0 | 0
2022052322 | 2 | 0.63472 | 50777.6 | 0 | 0 | 0.54249 | 18987.15 | 0 | 0 | 40000 | 0 | 10777.6 | 8209.55 | 0 | 0 | 8209.55 | 0 | 0 | 0 | 0
2022052323 | 2 | 0.59694 | 47755.2 | 0 | 0 | 0.5312 | 18592 | 0 | 0 | 40000 | 0 | 7755.2 | 10836.8 | 0 | 0 | 10836.8 | 0 | 0 | 0 | 0
2022052324 | 2 | 0.55275 | 44220 | 0 | 0 | 0.49932 | 17476.2 | 0 | 0 | 40000 | 0 | 4220 | 13256.2 | 0 | 0 | 13256.2 | 0 | 0 | 0 | 0
2022052401 | 3 | 0.52001 | 41600.8 | 0 | 0 | 0.49852 | 17448.2 | 0 | 0 | 40000 | 0 | 1600.8 | 15847.4 | 0 | 0 | 15847.4 | 0 | 0 | 0 | 0
2022052402 | 3 | 0.49781 | 39824.8 | 0 | 0 | 0.50277 | 17596.95 | 0 | 0 | 39824.8 | 175.2 | 0 | 17596.95 | 0 | 0 | 17772.15 | 0 | 0 | 0 | 0
2022052403 | 3 | 0.48214 | 38571.2 | 0 | 0 | 0.44783 | 15674.05 | 0 | 0 | 38571.2 | 1428.8 | 0 | 15674.05 | 0 | 0 | 17102.85 | 0 | 0 | 0 | 0
2022052404 | 3 | 0.47844 | 38275.2 | 0 | 0 | 0.47874 | 16755.9 | 0 | 0 | 38275.2 | 1724.8 | 0 | 16755.9 | 0 | 0 | 18480.7 | 0 | 0 | 0 | 0
2022052405 | 3 | 0.47819 | 38255.2 | 0 | 0 | 0.47331 | 16565.85 | 0 | 0 | 38255.2 | 1744.8 | 0 | 16565.85 | 0 | 0 | 18310.65 | 0 | 0 | 0 | 0
2022052406 | 3 | 0.49677 | 39741.6 | 0 | 0 | 0.44903 | 15716.05 | 0.00025 | 3.5 | 39741.6 | 258.4 | 0 | 15716.05 | 0 | 3.5 | 15977.95 | 0 | 0 | 0 | 0
2022052407 | 3 | 0.52113 | 41690.4 | 0 | 0 | 0.36709 | 12848.15 | 0.00089 | 12.46 | 40000 | 0 | 1690.4 | 11157.75 | 0 | 12.46 | 11170.21 | 0 | 0 | 0 | 0
2022052408 | 3 | 0.5328 | 42624 | 0 | 0 | 0.27297 | 9553.95 | 0.04029 | 564.06 | 40000 | 0 | 2624 | 6929.95 | 0 | 564.06 | 7494.01 | 0 | 0 | 0 | 0
2022052409 | 3 | 0.54567 | 43653.6 | 0 | 0 | 0.23753 | 8313.55 | 0.15262 | 2136.68 | 40000 | 0 | 3653.6 | 4659.95 | 0 | 2136.68 | 6796.63 | 0 | 0 | 0 | 0
2022052410 | 3 | 0.56082 | 44865.6 | 0 | 0 | 0.20767 | 7268.45 | 0.24849 | 3478.86 | 40000 | 0 | 4865.6 | 2402.85 | 0 | 3478.86 | 5881.71 | 0 | 0 | 0 | 0
2022052411 | 3 | 0.58001 | 46400.8 | 0 | 0 | 0.2017 | 7059.5 | 0.33226 | 4651.64 | 40000 | 0 | 6400.8 | 658.7 | 0 | 4651.64 | 5310.34 | 0 | 0 | 0 | 0
2022052412 | 3 | 0.58683 | 46946.4 | 0 | 0 | 0.17511 | 6128.85 | 0.46062 | 6448.68 | 40000 | 0 | 6128.85 | 0 | 817.55 | 5631.13 | 5631.13 | 0 | 0 | 0 | 0
2022052413 | 3 | 0.5953 | 47624 | 0 | 0 | 0.14559 | 5095.65 | 0.5317 | 7443.8 | 40000 | 0 | 5095.65 | 0 | 2528.35 | 4915.45 | 4915.45 | 0 | 0 | 0 | 0
2022052414 | 3 | 0.61319 | 49055.2 | 0 | 0 | 0.16915 | 5920.25 | 0.53955 | 7553.7 | 40000 | 0 | 5920.25 | 0 | 3134.95 | 4418.75 | 4418.75 | 0 | 0 | 0 | 0
2022052415 | 3 | 0.62814 | 50251.2 | 0 | 0 | 0.23214 | 8124.9 | 0.52108 | 7295.12 | 40000 | 0 | 8124.9 | 0 | 2126.3 | 5168.82 | 5168.82 | 0 | 0 | 0 | 0
2022052416 | 3 | 0.6426 | 51408 | 0 | 0 | 0.29811 | 10433.85 | 0.46 | 6440 | 40000 | 0 | 10433.85 | 0 | 974.15 | 5465.85 | 5465.85 | 0 | 0 | 0 | 0
2022052417 | 3 | 0.66363 | 53090.4 | 0 | 0 | 0.36811 | 12883.85 | 0.36124 | 5057.36 | 40000 | 0 | 12883.85 | 0 | 206.55 | 4850.81 | 4850.81 | 0 | 0 | 0 | 0
2022052418 | 3 | 0.66908 | 53526.4 | 0 | 0 | 0.41506 | 14527.1 | 0.29207 | 4088.98 | 40000 | 0 | 13526.4 | 1000.7 | 0 | 4088.98 | 5089.68 | 0 | 0 | 0 | 0
2022052419 | 3 | 0.65526 | 52420.8 | 0 | 0 | 0.46176 | 16161.6 | 0.14216 | 1990.24 | 40000 | 0 | 12420.8 | 3740.8 | 0 | 1990.24 | 5731.04 | 0 | 0 | 0 | 0
2022052420 | 3 | 0.63625 | 50900 | 0 | 0 | 0.49113 | 17189.55 | 0.04909 | 687.26 | 40000 | 0 | 10900 | 6289.55 | 0 | 687.26 | 6976.81 | 0 | 0 | 0 | 0
2022052421 | 3 | 0.62867 | 50293.6 | 0 | 0 | 0.56826 | 19889.1 | 0.00797 | 111.58 | 40000 | 0 | 10293.6 | 9595.5 | 0 | 111.58 | 9707.08 | 0 | 0 | 0 | 0
2022052422 | 3 | 0.61442 | 49153.6 | 0 | 0 | 0.59581 | 20853.35 | 0 | 0 | 40000 | 0 | 9153.6 | 11699.75 | 0 | 0 | 11699.75 | 0 | 0 | 0 | 0
2022052423 | 3 | 0.57437 | 45949.6 | 0 | 0 | 0.53869 | 18854.15 | 0 | 0 | 40000 | 0 | 5949.6 | 12904.55 | 0 | 0 | 12904.55 | 0 | 0 | 0 | 0
2022052424 | 3 | 0.53191 | 42552.8 | 0 | 0 | 0.48731 | 17055.85 | 0 | 0 | 40000 | 0 | 2552.8 | 14503.05 | 0 | 0 | 14503.05 | 0 | 0 | 0 | 0
2022052501 | 4 | 0.49313 | 39450.4 | 0 | 0 | 0.52386 | 18335.1 | 0 | 0 | 39450.4 | 549.6 | 0 | 18335.1 | 0 | 0 | 18884.7 | 0 | 0 | 0 | 0
2022052502 | 4 | 0.46929 | 37543.2 | 0 | 0 | 0.53986 | 18895.1 | 0 | 0 | 37543.2 | 2456.8 | 0 | 18895.1 | 0 | 0 | 21351.9 | 0 | 0 | 0 | 0
2022052503 | 4 | 0.45282 | 36225.6 | 0 | 0 | 0.48234 | 16881.9 | 0 | 0 | 36225.6 | 3774.4 | 0 | 16881.9 | 0 | 0 | 20656.3 | 0 | 0 | 0 | 0
2022052504 | 4 | 0.43785 | 35028 | 0 | 0 | 0.45278 | 15847.3 | 0 | 0 | 35028 | 4972 | 0 | 15847.3 | 0 | 0 | 20819.3 | 0 | 0 | 0 | 0
2022052505 | 4 | 0.43432 | 34745.6 | 0 | 0 | 0.44565 | 15597.75 | 0 | 0 | 34745.6 | 5254.4 | 0 | 15597.75 | 0 | 0 | 20852.15 | 0 | 0 | 0 | 0
2022052506 | 4 | 0.45102 | 36081.6 | 0 | 0 | 0.45944 | 16080.4 | 0 | 0 | 36081.6 | 3918.4 | 0 | 16080.4 | 0 | 0 | 19998.8 | 0 | 0 | 0 | 0
2022052507 | 4 | 0.47807 | 38245.6 | 0 | 0 | 0.45748 | 16011.8 | 0.00075 | 10.5 | 38245.6 | 1754.4 | 0 | 16011.8 | 0 | 10.5 | 17776.7 | 0 | 0 | 0 | 0
2022052508 | 4 | 0.49115 | 39292 | 0 | 0 | 0.44756 | 15664.6 | 0.08426 | 1179.64 | 39292 | 708 | 0 | 15664.6 | 0 | 1179.64 | 17552.24 | 0 | 0 | 0 | 0
2022052509 | 4 | 0.50436 | 40348.8 | 0 | 0 | 0.43489 | 15221.15 | 0.26212 | 3669.68 | 40000 | 0 | 348.8 | 14872.35 | 0 | 3669.68 | 18542.03 | 0 | 0 | 0 | 0
2022052510 | 4 | 0.5186 | 41488 | 0 | 0 | 0.47278 | 16547.3 | 0.29467 | 4125.38 | 40000 | 0 | 1488 | 15059.3 | 0 | 4125.38 | 19184.68 | 0 | 0 | 0 | 0
2022052511 | 4 | 0.53378 | 42702.4 | 0 | 0 | 0.47557 | 16644.95 | 0.36357 | 5089.98 | 40000 | 0 | 2702.4 | 13942.55 | 0 | 5089.98 | 19032.53 | 0 | 0 | 0 | 0
2022052512 | 4 | 0.54912 | 43929.6 | 0 | 0 | 0.44471 | 15564.85 | 0.47705 | 6678.7 | 40000 | 0 | 3929.6 | 11635.25 | 0 | 6678.7 | 18313.95 | 0 | 0 | 0 | 0
2022052513 | 4 | 0.56655 | 45324 | 0 | 0 | 0.44895 | 15713.25 | 0.48193 | 6747.02 | 40000 | 0 | 5324 | 10389.25 | 0 | 6747.02 | 17136.27 | 0 | 0 | 0 | 0
2022052514 | 4 | 0.58717 | 46973.6 | 0 | 0 | 0.43185 | 15114.75 | 0.52519 | 7352.66 | 40000 | 0 | 6973.6 | 8141.15 | 0 | 7352.66 | 15493.81 | 0 | 0 | 0 | 0
2022052515 | 4 | 0.60658 | 48526.4 | 0 | 0 | 0.42456 | 14859.6 | 0.53298 | 7461.72 | 40000 | 0 | 8526.4 | 6333.2 | 0 | 7461.72 | 13794.92 | 0 | 0 | 0 | 0
2022052516 | 4 | 0.62482 | 49985.6 | 0 | 0 | 0.4346 | 15211 | 0.4814 | 6739.6 | 40000 | 0 | 9985.6 | 5225.4 | 0 | 6739.6 | 11965 | 0 | 0 | 0 | 0
2022052517 | 4 | 0.64009 | 51207.2 | 0 | 0 | 0.42381 | 14833.35 | 0.44852 | 6279.28 | 40000 | 0 | 11207.2 | 3626.15 | 0 | 6279.28 | 9905.43 | 0 | 0 | 0 | 0
2022052518 | 4 | 0.64714 | 51771.2 | 0 | 0 | 0.38151 | 13352.85 | 0.45334 | 6346.76 | 40000 | 0 | 11771.2 | 1581.65 | 0 | 6346.76 | 7928.41 | 0 | 0 | 0 | 0
2022052519 | 4 | 0.6407 | 51256 | 0 | 0 | 0.34085 | 11929.75 | 0.43913 | 6147.82 | 40000 | 0 | 11256 | 673.75 | 0 | 6147.82 | 6821.57 | 0 | 0 | 0 | 0
2022052520 | 4 | 0.62098 | 49678.4 | 0 | 0 | 0.25563 | 8947.05 | 0.29501 | 4130.14 | 40000 | 0 | 8947.05 | 0 | 731.35 | 3398.79 | 3398.79 | 0 | 0 | 0 | 0
2022052521 | 4 | 0.60158 | 48126.4 | 0 | 0 | 0.12388 | 4335.8 | 0.02914 | 407.96 | 40000 | 0 | 4335.8 | 0 | 407.96 | 0 | 0 | 3382.64 | 0 | 0 | 3382.64
2022052522 | 4 | 0.58332 | 46665.6 | 0 | 0 | 0.06178 | 2162.3 | 0 | 0 | 40000 | 0 | 2162.3 | 0 | 0 | 0 | 0 | 4503.3 | 0 | 0 | 4503.3
2022052523 | 4 | 0.54568 | 43654.4 | 0 | 0 | 0.04572 | 1600.2 | 0 | 0 | 40000 | 0 | 1600.2 | 0 | 0 | 0 | 0 | 2054.2 | 0 | 0 | 2054.2
2022052524 | 4 | 0.50365 | 40292 | 0 | 0 | 0.05275 | 1846.25 | 0 | 0 | 40000 | 0 | 292 | 1554.25 | 0 | 0 | 1554.25 | 0 | 0 | 0 | 0
2022052601 | 5 | 0.46921 | 37536.8 | 0 | 0 | 0.07323 | 2563.05 | 0 | 0 | 37536.8 | 2463.2 | 0 | 2563.05 | 0 | 0 | 5026.25 | 0 | 0 | 0 | 0
2022052602 | 5 | 0.44725 | 35780 | 0 | 0 | 0.11586 | 4055.1 | 0 | 0 | 35780 | 4220 | 0 | 4055.1 | 0 | 0 | 8275.1 | 0 | 0 | 0 | 0
2022052603 | 5 | 0.43204 | 34563.2 | 0 | 0 | 0.19509 | 6828.15 | 0 | 0 | 34563.2 | 5436.8 | 0 | 6828.15 | 0 | 0 | 12264.95 | 0 | 0 | 0 | 0
2022052604 | 5 | 0.42602 | 34081.6 | 0 | 0 | 0.25738 | 9008.3 | 0 | 0 | 34081.6 | 5918.4 | 0 | 9008.3 | 0 | 0 | 14926.7 | 0 | 0 | 0 | 0
2022052605 | 5 | 0.43177 | 34541.6 | 0 | 0 | 0.28766 | 10068.1 | 0 | 0 | 34541.6 | 5458.4 | 0 | 10068.1 | 0 | 0 | 15526.5 | 0 | 0 | 0 | 0
2022052606 | 5 | 0.44713 | 35770.4 | 0 | 0 | 0.32169 | 11259.15 | 0 | 0 | 35770.4 | 4229.6 | 0 | 11259.15 | 0 | 0 | 15488.75 | 0 | 0 | 0 | 0
2022052607 | 5 | 0.47198 | 37758.4 | 0 | 0 | 0.35744 | 12510.4 | 0.00391 | 54.74 | 37758.4 | 2241.6 | 0 | 12510.4 | 0 | 54.74 | 14806.74 | 0 | 0 | 0 | 0
2022052608 | 5 | 0.4903 | 39224 | 0 | 0 | 0.34453 | 12058.55 | 0.20444 | 2862.16 | 39224 | 776 | 0 | 12058.55 | 0 | 2862.16 | 15696.71 | 0 | 0 | 0 | 0
2022052609 | 5 | 0.51501 | 41200.8 | 0 | 0 | 0.2523 | 8830.5 | 0.6145 | 8603 | 40000 | 0 | 1200.8 | 7629.7 | 0 | 8603 | 16232.7 | 0 | 0 | 0 | 0
2022052610 | 5 | 0.5414 | 43312 | 0 | 0 | 0.19978 | 6992.3 | 0.7593 | 10630.2 | 40000 | 0 | 3312 | 3680.3 | 0 | 10630.2 | 14310.5 | 0 | 0 | 0 | 0
2022052611 | 5 | 0.57245 | 45796 | 0 | 0 | 0.21931 | 7675.85 | 0.79268 | 11097.52 | 40000 | 0 | 5796 | 1879.85 | 0 | 11097.52 | 12977.37 | 0 | 0 | 0 | 0
2022052612 | 5 | 0.6048 | 48384 | 0 | 0 | 0.16345 | 5720.75 | 0.8133 | 11386.2 | 40000 | 0 | 5720.75 | 0 | 2663.25 | 8722.95 | 8722.95 | 0 | 0 | 0 | 0
2022052613 | 5 | 0.63746 | 50996.8 | 0 | 0 | 0.11982 | 4193.7 | 0.81505 | 11410.7 | 40000 | 0 | 4193.7 | 0 | 6803.1 | 4607.6 | 4607.6 | 0 | 0 | 0 | 0
2022052614 | 5 | 0.67342 | 53873.6 | 0 | 0 | 0.11124 | 3893.4 | 0.81582 | 11421.48 | 40000 | 0 | 3893.4 | 0 | 9980.2 | 1441.28 | 1441.28 | 0 | 0 | 0 | 0
2022052615 | 5 | 0.70859 | 56687.2 | 0 | 0 | 0.10627 | 3719.45 | 0.83254 | 11655.56 | 40000 | 0 | 3719.45 | 0 | 11655.56 | 0 | 0 | 1312.19 | 0 | 0 | 1312.19
2022052616 | 5 | 0.73683 | 58946.4 | 0 | 0 | 0.10156 | 3554.6 | 0.83396 | 11675.44 | 40000 | 0 | 3554.6 | 0 | 11675.44 | 0 | 0 | 3716.36 | 0 | 0 | 3716.36
2022052617 | 5 | 0.75756 | 60604.8 | 0 | 0 | 0.10578 | 3702.3 | 0.81927 | 11469.78 | 40000 | 0 | 3702.3 | 0 | 11469.78 | 0 | 0 | 5432.72 | 0 | 0 | 5432.72
2022052618 | 5 | 0.76964 | 61571.2 | 0 | 0 | 0.10881 | 3808.35 | 0.7941 | 11117.4 | 40000 | 0 | 3808.35 | 0 | 11117.4 | 0 | 0 | 6645.45 | 0 | 0 | 6645.45
2022052619 | 5 | 0.76141 | 60912.8 | 0 | 0 | 0.11166 | 3908.1 | 0.69114 | 9675.96 | 40000 | 0 | 3908.1 | 0 | 9675.96 | 0 | 0 | 7328.74 | 0 | 0 | 7328.74
2022052620 | 5 | 0.73512 | 58809.6 | 0 | 0 | 0.12495 | 4373.25 | 0.36025 | 5043.5 | 40000 | 0 | 4373.25 | 0 | 5043.5 | 0 | 0 | 9392.85 | 0 | 0 | 9392.85
2022052621 | 5 | 0.69969 | 55975.2 | 0 | 0 | 0.16502 | 5775.7 | 0.03554 | 497.56 | 40000 | 0 | 5775.7 | 0 | 497.56 | 0 | 0 | 9701.94 | 0 | 0 | 9701.94
2022052622 | 5 | 0.67161 | 53728.8 | 0 | 0 | 0.22178 | 7762.3 | 0 | 0 | 40000 | 0 | 7762.3 | 0 | 0 | 0 | 0 | 5966.5 | 0 | 0 | 5966.5
2022052623 | 5 | 0.62388 | 49910.4 | 0 | 0 | 0.26232 | 9181.2 | 0 | 0 | 40000 | 0 | 9181.2 | 0 | 0 | 0 | 0 | 729.2 | 0 | 0 | 729.2
2022052624 | 5 | 0.57644 | 46115.2 | 0 | 0 | 0.28955 | 10134.25 | 0 | 0 | 40000 | 0 | 6115.2 | 4019.05 | 0 | 0 | 4019.05 | 0 | 0 | 0 | 0
2022052701 | 6 | 0.53616 | 42892.8 | 0 | 0 | 0.35122 | 12292.7 | 0 | 0 | 40000 | 0 | 2892.8 | 9399.9 | 0 | 0 | 9399.9 | 0 | 0 | 0 | 0
2022052702 | 6 | 0.50525 | 40420 | 0 | 0 | 0.38097 | 13333.95 | 0 | 0 | 40000 | 0 | 420 | 12913.95 | 0 | 0 | 12913.95 | 0 | 0 | 0 | 0
2022052703 | 6 | 0.48866 | 39092.8 | 0 | 0 | 0.38246 | 13386.1 | 0 | 0 | 39092.8 | 907.2 | 0 | 13386.1 | 0 | 0 | 14293.3 | 0 | 0 | 0 | 0
2022052704 | 6 | 0.47487 | 37989.6 | 0 | 0 | 0.36481 | 12768.35 | 0 | 0 | 37989.6 | 2010.4 | 0 | 12768.35 | 0 | 0 | 14778.75 | 0 | 0 | 0 | 0
2022052705 | 6 | 0.47174 | 37739.2 | 0 | 0 | 0.3644 | 12754 | 0 | 0 | 37739.2 | 2260.8 | 0 | 12754 | 0 | 0 | 15014.8 | 0 | 0 | 0 | 0
2022052706 | 6 | 0.4837 | 38696 | 0 | 0 | 0.35035 | 12262.25 | 0 | 0 | 38696 | 1304 | 0 | 12262.25 | 0 | 0 | 13566.25 | 0 | 0 | 0 | 0
2022052707 | 6 | 0.50313 | 40250.4 | 0 | 0 | 0.34257 | 11989.95 | 0.00627 | 87.78 | 40000 | 0 | 250.4 | 11739.55 | 0 | 87.78 | 11827.33 | 0 | 0 | 0 | 0
2022052708 | 6 | 0.52212 | 41769.6 | 0 | 0 | 0.31256 | 10939.6 | 0.20328 | 2845.92 | 40000 | 0 | 1769.6 | 9170 | 0 | 2845.92 | 12015.92 | 0 | 0 | 0 | 0
2022052709 | 6 | 0.55333 | 44266.4 | 0 | 0 | 0.23451 | 8207.85 | 0.59642 | 8349.88 | 40000 | 0 | 4266.4 | 3941.45 | 0 | 8349.88 | 12291.33 | 0 | 0 | 0 | 0
2022052710 | 6 | 0.59089 | 47271.2 | 0 | 0 | 0.25214 | 8824.9 | 0.74541 | 10435.74 | 40000 | 0 | 7271.2 | 1553.7 | 0 | 10435.74 | 11989.44 | 0 | 0 | 0 | 0
2022052711 | 6 | 0.63026 | 50420.8 | 0 | 0 | 0.27304 | 9556.4 | 0.76952 | 10773.28 | 40000 | 0 | 9556.4 | 0 | 864.4 | 9908.88 | 9908.88 | 0 | 0 | 0 | 0
2022052712 | 6 | 0.67542 | 54033.6 | 0 | 0 | 0.26513 | 9279.55 | 0.78331 | 10966.34 | 40000 | 0 | 9279.55 | 0 | 4754.05 | 6212.29 | 6212.29 | 0 | 0 | 0 | 0
2022052713 | 6 | 0.71797 | 57437.6 | 0 | 0 | 0.26538 | 9288.3 | 0.78871 | 11041.94 | 40000 | 0 | 9288.3 | 0 | 8149.3 | 2892.64 | 2892.64 | 0 | 0 | 0 | 0
2022052714 | 6 | 0.75834 | 60667.2 | 0 | 0 | 0.26525 | 9283.75 | 0.78982 | 11057.48 | 40000 | 0 | 9283.75 | 0 | 11057.48 | 0 | 0 | 325.97 | 0 | 0 | 325.97
2022052715 | 6 | 0.79178 | 63342.4 | 0 | 0 | 0.26706 | 9347.1 | 0.77306 | 10822.84 | 40000 | 0 | 9347.1 | 0 | 10822.84 | 0 | 0 | 3172.46 | 0 | 0 | 3172.46
2022052716 | 6 | 0.81829 | 65463.2 | 0 | 0 | 0.28145 | 9850.75 | 0.73992 | 10358.88 | 40000 | 0 | 9850.75 | 0 | 10358.88 | 0 | 0 | 5253.57 | 0 | 0 | 5253.57
2022052717 | 6 | 0.83517 | 66813.6 | 0 | 0 | 0.29826 | 10439.1 | 0.71525 | 10013.5 | 40000 | 0 | 10439.1 | 0 | 10013.5 | 0 | 0 | 6361 | 0 | 0 | 6361
2022052718 | 6 | 0.83741 | 66992.8 | 0 | 0 | 0.32159 | 11255.65 | 0.68862 | 9640.68 | 40000 | 0 | 11255.65 | 0 | 9640.68 | 0 | 0 | 6096.47 | 0 | 0 | 6096.47
2022052719 | 6 | 0.82351 | 65880.8 | 0 | 0 | 0.36866 | 12903.1 | 0.60756 | 8505.84 | 40000 | 0 | 12903.1 | 0 | 8505.84 | 0 | 0 | 4471.86 | 0 | 0 | 4471.86
2022052720 | 6 | 0.79123 | 63298.4 | 0 | 0 | 0.4236 | 14826 | 0.31164 | 4362.96 | 40000 | 0 | 14826 | 0 | 4362.96 | 0 | 0 | 4109.44 | 0 | 0 | 4109.44
2022052721 | 6 | 0.75009 | 60007.2 | 0 | 0 | 0.48754 | 17063.9 | 0.02937 | 411.18 | 40000 | 0 | 17063.9 | 0 | 411.18 | 0 | 0 | 2532.12 | 0 | 0 | 2532.12
2022052722 | 6 | 0.71655 | 57324 | 0 | 0 | 0.5835 | 20422.5 | 0 | 0 | 40000 | 0 | 17324 | 3098.5 | 0 | 0 | 3098.5 | 0 | 0 | 0 | 0
2022052723 | 6 | 0.67197 | 53757.6 | 0 | 0 | 0.64264 | 22492.4 | 0 | 0 | 40000 | 0 | 13757.6 | 8734.8 | 0 | 0 | 8734.8 | 0 | 0 | 0 | 0
2022052724 | 6 | 0.6274 | 50192 | 0 | 0 | 0.64702 | 22645.7 | 0 | 0 | 40000 | 0 | 10192 | 12453.7 | 0 | 0 | 12453.7 | 0 | 0 | 0 | 0
2022052801 | 7 | 0.58084 | 46467.2 | 0 | 0 | 0.6337 | 22179.5 | 0 | 0 | 40000 | 0 | 6467.2 | 15712.3 | 0 | 0 | 15712.3 | 0 | 0 | 0 | 0
2022052802 | 7 | 0.54812 | 43849.6 | 0 | 0 | 0.63428 | 22199.8 | 0 | 0 | 40000 | 0 | 3849.6 | 18350.2 | 0 | 0 | 18350.2 | 0 | 0 | 0 | 0
2022052803 | 7 | 0.52145 | 41716 | 0 | 0 | 0.62744 | 21960.4 | 0 | 0 | 40000 | 0 | 1716 | 20244.4 | 0 | 0 | 20244.4 | 0 | 0 | 0 | 0
2022052804 | 7 | 0.50393 | 40314.4 | 0 | 0 | 0.60756 | 21264.6 | 0 | 0 | 40000 | 0 | 314.4 | 20950.2 | 0 | 0 | 20950.2 | 0 | 0 | 0 | 0
2022052805 | 7 | 0.49169 | 39335.2 | 0 | 0 | 0.59074 | 20675.9 | 0 | 0 | 39335.2 | 664.8 | 0 | 20675.9 | 0 | 0 | 21340.7 | 0 | 0 | 0 | 0
2022052806 | 7 | 0.49278 | 39422.4 | 0 | 0 | 0.58371 | 20429.85 | 0 | 0 | 39422.4 | 577.6 | 0 | 20429.85 | 0 | 0 | 21007.45 | 0 | 0 | 0 | 0
2022052807 | 7 | 0.49126 | 39300.8 | 0 | 0 | 0.57769 | 20219.15 | 0.00231 | 32.34 | 39300.8 | 699.2 | 0 | 20219.15 | 0 | 32.34 | 20950.69 | 0 | 0 | 0 | 0
2022052808 | 7 | 0.50427 | 40341.6 | 0 | 0 | 0.57439 | 20103.65 | 0.0928 | 1299.2 | 40000 | 0 | 341.6 | 19762.05 | 0 | 1299.2 | 21061.25 | 0 | 0 | 0 | 0
2022052809 | 7 | 0.54168 | 43334.4 | 0 | 0 | 0.56222 | 19677.7 | 0.29589 | 4142.46 | 40000 | 0 | 3334.4 | 16343.3 | 0 | 4142.46 | 20485.76 | 0 | 0 | 0 | 0
2022052810 | 7 | 0.58486 | 46788.8 | 0 | 0 | 0.57591 | 20156.85 | 0.3895 | 5453 | 40000 | 0 | 6788.8 | 13368.05 | 0 | 5453 | 18821.05 | 0 | 0 | 0 | 0
2022052811 | 7 | 0.63187 | 50549.6 | 0 | 0 | 0.58666 | 20533.1 | 0.4243 | 5940.2 | 40000 | 0 | 10549.6 | 9983.5 | 0 | 5940.2 | 15923.7 | 0 | 0 | 0 | 0
2022052812 | 7 | 0.68163 | 54530.4 | 0 | 0 | 0.57617 | 20165.95 | 0.45902 | 6426.28 | 40000 | 0 | 14530.4 | 5635.55 | 0 | 6426.28 | 12061.83 | 0 | 0 | 0 | 0
2022052813 | 7 | 0.72477 | 57981.6 | 0 | 0 | 0.56942 | 19929.7 | 0.49504 | 6930.56 | 40000 | 0 | 17981.6 | 1948.1 | 0 | 6930.56 | 8878.66 | 0 | 0 | 0 | 0
2022052814 | 7 | 0.76302 | 61041.6 | 0 | 0 | 0.55453 | 19408.55 | 0.55099 | 7713.86 | 40000 | 0 | 19408.55 | 0 | 1633.05 | 6080.81 | 6080.81 | 0 | 0 | 0 | 0
2022052815 | 7 | 0.79568 | 63654.4 | 0 | 0 | 0.57281 | 20048.35 | 0.57198 | 8007.72 | 40000 | 0 | 20048.35 | 0 | 3606.05 | 4401.67 | 4401.67 | 0 | 0 | 0 | 0
2022052816 | 7 | 0.82142 | 65713.6 | 0 | 0 | 0.58248 | 20386.8 | 0.60274 | 8438.36 | 40000 | 0 | 20386.8 | 0 | 5326.8 | 3111.56 | 3111.56 | 0 | 0 | 0 | 0
2022052817 | 7 | 0.83793 | 67034.4 | 0 | 0 | 0.60067 | 21023.45 | 0.6173 | 8642.2 | 40000 | 0 | 21023.45 | 0 | 6010.95 | 2631.25 | 2631.25 | 0 | 0 | 0 | 0
2022052818 | 7 | 0.84166 | 67332.8 | 0 | 0 | 0.62111 | 21738.85 | 0.56179 | 7865.06 | 40000 | 0 | 21738.85 | 0 | 5593.95 | 2271.11 | 2271.11 | 0 | 0 | 0 | 0
2022052819 | 7 | 0.82686 | 66148.8 | 0 | 0 | 0.64949 | 22732.15 | 0.42808 | 5993.12 | 40000 | 0 | 22732.15 | 0 | 3416.65 | 2576.47 | 2576.47 | 0 | 0 | 0 | 0
2022052820 | 7 | 0.79713 | 63770.4 | 0 | 0 | 0.66475 | 23266.25 | 0.21269 | 2977.66 | 40000 | 0 | 23266.25 | 0 | 504.15 | 2473.51 | 2473.51 | 0 | 0 | 0 | 0
2022052821 | 7 | 0.76243 | 60994.4 | 0 | 0 | 0.67881 | 23758.35 | 0.01775 | 248.5 | 40000 | 0 | 20994.4 | 2763.95 | 0 | 248.5 | 3012.45 | 0 | 0 | 0 | 0
2022052822 | 7 | 0.73601 | 58880.8 | 0 | 0 | 0.69454 | 24308.9 | 0 | 0 | 40000 | 0 | 18880.8 | 5428.1 | 0 | 0 | 5428.1 | 0 | 0 | 0 | 0
2022052823 | 7 | 0.69675 | 55740 | 0 | 0 | 0.69301 | 24255.35 | 0 | 0 | 40000 | 0 | 15740 | 8515.35 | 0 | 0 | 8515.35 | 0 | 0 | 0 | 0
2022052824 | 7 | 0.65475 | 52380 | 0 | 0 | 0.70708 | 24747.8 | 0 | 0 | 40000 | 0 | 12380 | 12367.8 | 0 | 0 | 12367.8 | 0 | 0 | 0 | 0
2022052901 | 1 | 0.61689 | 49351.2 | 0 | 0 | 0.71722 | 25102.7 | 0 | 0 | 40000 | 0 | 9351.2 | 15751.5 | 0 | 0 | 15751.5 | 0 | 0 | 0 | 0
2022052902 | 1 | 0.58486 | 46788.8 | 0 | 0 | 0.72454 | 25358.9 | 0 | 0 | 40000 | 0 | 6788.8 | 18570.1 | 0 | 0 | 18570.1 | 0 | 0 | 0 | 0
2022052903 | 1 | 0.56104 | 44883.2 | 0 | 0 | 0.72139 | 25248.65 | 0 | 0 | 40000 | 0 | 4883.2 | 20365.45 | 0 | 0 | 20365.45 | 0 | 0 | 0 | 0
2022052904 | 1 | 0.5463 | 43704 | 0 | 0 | 0.71127 | 24894.45 | 0 | 0 | 40000 | 0 | 3704 | 21190.45 | 0 | 0 | 21190.45 | 0 | 0 | 0 | 0
2022052905 | 1 | 0.5286 | 42288 | 0 | 0 | 0.68206 | 23872.1 | 0 | 0 | 40000 | 0 | 2288 | 21584.1 | 0 | 0 | 21584.1 | 0 | 0 | 0 | 0
2022052906 | 1 | 0.52201 | 41760.8 | 0 | 0 | 0.67602 | 23660.7 | 0 | 0 | 40000 | 0 | 1760.8 | 21899.9 | 0 | 0 | 21899.9 | 0 | 0 | 0 | 0
2022052907 | 1 | 0.51834 | 41467.2 | 0 | 0 | 0.66873 | 23405.55 | 0.00202 | 28.28 | 40000 | 0 | 1467.2 | 21938.35 | 0 | 28.28 | 21966.63 | 0 | 0 | 0 | 0
2022052908 | 1 | 0.52615 | 42092 | 0 | 0 | 0.65655 | 22979.25 | 0.07386 | 1034.04 | 40000 | 0 | 2092 | 20887.25 | 0 | 1034.04 | 21921.29 | 0 | 0 | 0 | 0
2022052909 | 1 | 0.5617 | 44936 | 0 | 0 | 0.66607 | 23312.45 | 0.25815 | 3614.1 | 40000 | 0 | 4936 | 18376.45 | 0 | 3614.1 | 21990.55 | 0 | 0 | 0 | 0
2022052910 | 1 | 0.60703 | 48562.4 | 0 | 0 | 0.68324 | 23913.4 | 0.37556 | 5257.84 | 40000 | 0 | 8562.4 | 15351 | 0 | 5257.84 | 20608.84 | 0 | 0 | 0 | 0
2022052911 | 1 | 0.64985 | 51988 | 0 | 0 | 0.67334 | 23566.9 | 0.46198 | 6467.72 | 40000 | 0 | 11988 | 11578.9 | 0 | 6467.72 | 18046.62 | 0 | 0 | 0 | 0
2022052912 | 1 | 0.69367 | 55493.6 | 0 | 0 | 0.68 | 23800 | 0.45992 | 6438.88 | 40000 | 0 | 15493.6 | 8306.4 | 0 | 6438.88 | 14745.28 | 0 | 0 | 0 | 0
2022052913 | 1 | 0.73605 | 58884 | 0 | 0 | 0.68718 | 24051.3 | 0.45943 | 6432.02 | 40000 | 0 | 18884 | 5167.3 | 0 | 6432.02 | 11599.32 | 0 | 0 | 0 | 0
2022052914 | 1 | 0.76945 | 61556 | 0 | 0 | 0.66194 | 23167.9 | 0.54616 | 7646.24 | 40000 | 0 | 21556 | 1611.9 | 0 | 7646.24 | 9258.14 | 0 | 0 | 0 | 0
2022052915 | 1 | 0.79583 | 63666.4 | 0 | 0 | 0.67726 | 23704.1 | 0.51275 | 7178.5 | 40000 | 0 | 23666.4 | 37.7 | 0 | 7178.5 | 7216.2 | 0 | 0 | 0 | 0
2022052916 | 1 | 0.8171 | 65368 | 0 | 0 | 0.67606 | 23662.1 | 0.51803 | 7252.42 | 40000 | 0 | 23662.1 | 0 | 1705.9 | 5546.52 | 5546.52 | 0 | 0 | 0 | 0
2022052917 | 1 | 0.83171 | 66536.8 | 0 | 0 | 0.67259 | 23540.65 | 0.52146 | 7300.44 | 40000 | 0 | 23540.65 | 0 | 2996.15 | 4304.29 | 4304.29 | 0 | 0 | 0 | 0
2022052918 | 1 | 0.83211 | 66568.8 | 0 | 0 | 0.67369 | 23579.15 | 0.49076 | 6870.64 | 40000 | 0 | 23579.15 | 0 | 2989.65 | 3880.99 | 3880.99 | 0 | 0 | 0 | 0
2022052919 | 1 | 0.81463 | 65170.4 | 0 | 0 | 0.67311 | 23558.85 | 0.42477 | 5946.78 | 40000 | 0 | 23558.85 | 0 | 1611.55 | 4335.23 | 4335.23 | 0 | 0 | 0 | 0
2022052920 | 1 | 0.78473 | 62778.4 | 0 | 0 | 0.6904 | 24164 | 0.23918 | 3348.52 | 40000 | 0 | 22778.4 | 1385.6 | 0 | 3348.52 | 4734.12 | 0 | 0 | 0 | 0
2022052921 | 1 | 0.7553 | 60424 | 0 | 0 | 0.72784 | 25474.4 | 0.03453 | 483.42 | 40000 | 0 | 20424 | 5050.4 | 0 | 483.42 | 5533.82 | 0 | 0 | 0 | 0
2022052922 | 1 | 0.73305 | 58644 | 0 | 0 | 0.74368 | 26028.8 | 0 | 0 | 40000 | 0 | 18644 | 7384.8 | 0 | 0 | 7384.8 | 0 | 0 | 0 | 0
2022052923 | 1 | 0.69515 | 55612 | 0 | 0 | 0.75385 | 26384.75 | 0 | 0 | 40000 | 0 | 15612 | 10772.75 | 0 | 0 | 10772.75 | 0 | 0 | 0 | 0
2022052924 | 1 | 0.65563 | 52450.4 | 0 | 0 | 0.7533 | 26365.5 | 0 | 0 | 40000 | 0 | 12450.4 | 13915.1 | 0 | 0 | 13915.1 | 0 | 0 | 0 | 0
2022053001 | 2 | 0.62008 | 49606.4 | 0 | 0 | 0.74691 | 26141.85 | 0 | 0 | 40000 | 0 | 9606.4 | 16535.45 | 0 | 0 | 16535.45 | 0 | 0 | 0 | 0
2022053002 | 2 | 0.58906 | 47124.8 | 0 | 0 | 0.74366 | 26028.1 | 0 | 0 | 40000 | 0 | 7124.8 | 18903.3 | 0 | 0 | 18903.3 | 0 | 0 | 0 | 0
2022053003 | 2 | 0.56815 | 45452 | 0 | 0 | 0.73736 | 25807.6 | 0 | 0 | 40000 | 0 | 5452 | 20355.6 | 0 | 0 | 20355.6 | 0 | 0 | 0 | 0
2022053004 | 2 | 0.55548 | 44438.4 | 0 | 0 | 0.73137 | 25597.95 | 0 | 0 | 40000 | 0 | 4438.4 | 21159.55 | 0 | 0 | 21159.55 | 0 | 0 | 0 | 0
2022053005 | 2 | 0.55266 | 44212.8 | 0 | 0 | 0.7257 | 25399.5 | 0 | 0 | 40000 | 0 | 4212.8 | 21186.7 | 0 | 0 | 21186.7 | 0 | 0 | 0 | 0
2022053006 | 2 | 0.5575 | 44600 | 0 | 0 | 0.72589 | 25406.15 | 0 | 0 | 40000 | 0 | 4600 | 20806.15 | 0 | 0 | 20806.15 | 0 | 0 | 0 | 0
2022053007 | 2 | 0.55635 | 44508 | 0 | 0 | 0.71094 | 24882.9 | 0.00402 | 56.28 | 40000 | 0 | 4508 | 20374.9 | 0 | 56.28 | 20431.18 | 0 | 0 | 0 | 0
2022053008 | 2 | 0.56142 | 44913.6 | 0 | 0 | 0.67168 | 23508.8 | 0.14865 | 2081.1 | 40000 | 0 | 4913.6 | 18595.2 | 0 | 2081.1 | 20676.3 | 0 | 0 | 0 | 0
2022053009 | 2 | 0.5921 | 47368 | 0 | 0 | 0.65424 | 22898.4 | 0.36584 | 5121.76 | 40000 | 0 | 7368 | 15530.4 | 0 | 5121.76 | 20652.16 | 0 | 0 | 0 | 0
2022053010 | 2 | 0.63406 | 50724.8 | 0 | 0 | 0.64567 | 22598.45 | 0.43558 | 6098.12 | 40000 | 0 | 10724.8 | 11873.65 | 0 | 6098.12 | 17971.77 | 0 | 0 | 0 | 0
2022053011 | 2 | 0.67951 | 54360.8 | 0 | 0 | 0.60801 | 21280.35 | 0.58761 | 8226.54 | 40000 | 0 | 14360.8 | 6919.55 | 0 | 8226.54 | 15146.09 | 0 | 0 | 0 | 0
2022053012 | 2 | 0.71774 | 57419.2 | 0 | 0 | 0.54815 | 19185.25 | 0.74261 | 10396.54 | 40000 | 0 | 17419.2 | 1766.05 | 0 | 10396.54 | 12162.59 | 0 | 0 | 0 | 0
2022053013 | 2 | 0.74881 | 59904.8 | 0 | 0 | 0.4713 | 16495.5 | 0.75438 | 10561.32 | 40000 | 0 | 16495.5 | 0 | 3409.3 | 7152.02 | 7152.02 | 0 | 0 | 0 | 0
2022053014 | 2 | 0.77871 | 62296.8 | 0 | 0 | 0.44175 | 15461.25 | 0.76247 | 10674.58 | 40000 | 0 | 15461.25 | 0 | 6835.55 | 3839.03 | 3839.03 | 0 | 0 | 0 | 0
2022053015 | 2 | 0.80315 | 64252 | 0 | 0 | 0.47035 | 16462.25 | 0.76234 | 10672.76 | 40000 | 0 | 16462.25 | 0 | 7789.75 | 2883.01 | 2883.01 | 0 | 0 | 0 | 0
2022053016 | 2 | 0.82332 | 65865.6 | 0 | 0 | 0.51709 | 18098.15 | 0.76015 | 10642.1 | 40000 | 0 | 18098.15 | 0 | 7767.45 | 2874.65 | 2874.65 | 0 | 0 | 0 | 0
2022053017 | 2 | 0.83592 | 66873.6 | 0 | 0 | 0.56034 | 19611.9 | 0.72979 | 10217.06 | 40000 | 0 | 19611.9 | 0 | 7261.7 | 2955.36 | 2955.36 | 0 | 0 | 0 | 0
2022053018 | 2 | 0.83896 | 67116.8 | 0 | 0 | 0.60362 | 21126.7 | 0.63436 | 8881.04 | 40000 | 0 | 21126.7 | 0 | 5990.1 | 2890.94 | 2890.94 | 0 | 0 | 0 | 0
2022053019 | 2 | 0.82415 | 65932 | 0 | 0 | 0.64196 | 22468.6 | 0.48313 | 6763.82 | 40000 | 0 | 22468.6 | 0 | 3463.4 | 3300.42 | 3300.42 | 0 | 0 | 0 | 0
2022053020 | 2 | 0.79821 | 63856.8 | 0 | 0 | 0.67604 | 23661.4 | 0.25637 | 3589.18 | 40000 | 0 | 23661.4 | 0 | 195.4 | 3393.78 | 3393.78 | 0 | 0 | 0 | 0
2022053021 | 2 | 0.77164 | 61731.2 | 0 | 0 | 0.6682 | 23387 | 0.03687 | 516.18 | 40000 | 0 | 21731.2 | 1655.8 | 0 | 516.18 | 2171.98 | 0 | 0 | 0 | 0
2022053022 | 2 | 0.75245 | 60196 | 0 | 0 | 0.66587 | 23305.45 | 0 | 0 | 40000 | 0 | 20196 | 3109.45 | 0 | 0 | 3109.45 | 0 | 0 | 0 | 0
2022053023 | 2 | 0.71352 | 57081.6 | 0 | 0 | 0.70109 | 24538.15 | 0 | 0 | 40000 | 0 | 17081.6 | 7456.55 | 0 | 0 | 7456.55 | 0 | 0 | 0 | 0
2022053024 | 2 | 0.67026 | 53620.8 | 0 | 0 | 0.72657 | 25429.95 | 0 | 0 | 40000 | 0 | 13620.8 | 11809.15 | 0 | 0 | 11809.15 | 0 | 0 | 0 | 0
2022053101 | 3 | 0.63226 | 50580.8 | 0 | 0 | 0.73092 | 25582.2 | 0 | 0 | 40000 | 0 | 10580.8 | 15001.4 | 0 | 0 | 15001.4 | 0 | 0 | 0 | 0
2022053102 | 3 | 0.60404 | 48323.2 | 0 | 0 | 0.72094 | 25232.9 | 0 | 0 | 40000 | 0 | 8323.2 | 16909.7 | 0 | 0 | 16909.7 | 0 | 0 | 0 | 0
2022053103 | 3 | 0.58506 | 46804.8 | 0 | 0 | 0.71009 | 24853.15 | 0 | 0 | 40000 | 0 | 6804.8 | 18048.35 | 0 | 0 | 18048.35 | 0 | 0 | 0 | 0
2022053104 | 3 | 0.57436 | 45948.8 | 0 | 0 | 0.6978 | 24423 | 0 | 0 | 40000 | 0 | 5948.8 | 18474.2 | 0 | 0 | 18474.2 | 0 | 0 | 0 | 0
2022053105 | 3 | 0.5719 | 45752 | 0 | 0 | 0.6745 | 23607.5 | 0 | 0 | 40000 | 0 | 5752 | 17855.5 | 0 | 0 | 17855.5 | 0 | 0 | 0 | 0
2022053106 | 3 | 0.583 | 46640 | 0 | 0 | 0.64904 | 22716.4 | 0 | 0 | 40000 | 0 | 6640 | 16076.4 | 0 | 0 | 16076.4 | 0 | 0 | 0 | 0
2022053107 | 3 | 0.59771 | 47816.8 | 0 | 0 | 0.61489 | 21521.15 | 0.0045 | 63 | 40000 | 0 | 7816.8 | 13704.35 | 0 | 63 | 13767.35 | 0 | 0 | 0 | 0
2022053108 | 3 | 0.61469 | 49175.2 | 0 | 0 | 0.58081 | 20328.35 | 0.13609 | 1905.26 | 40000 | 0 | 9175.2 | 11153.15 | 0 | 1905.26 | 13058.41 | 0 | 0 | 0 | 0
2022053109 | 3 | 0.64848 | 51878.4 | 0 | 0 | 0.59911 | 20968.85 | 0.33467 | 4685.38 | 40000 | 0 | 11878.4 | 9090.45 | 0 | 4685.38 | 13775.83 | 0 | 0 | 0 | 0
2022053110 | 3 | 0.68444 | 54755.2 | 0 | 0 | 0.61841 | 21644.35 | 0.36063 | 5048.82 | 40000 | 0 | 14755.2 | 6889.15 | 0 | 5048.82 | 11937.97 | 0 | 0 | 0 | 0
2022053111 | 3 | 0.72675 | 58140 | 0 | 0 | 0.59906 | 20967.1 | 0.45143 | 6320.02 | 40000 | 0 | 18140 | 2827.1 | 0 | 6320.02 | 9147.12 | 0 | 0 | 0 | 0
2022053112 | 3 | 0.77088 | 61670.4 | 0 | 0 | 0.55007 | 19252.45 | 0.60486 | 8468.04 | 40000 | 0 | 19252.45 | 0 | 2417.95 | 6050.09 | 6050.09 | 0 | 0 | 0 | 0
2022053113 | 3 | 0.8087 | 64696 | 0 | 0 | 0.4918 | 17213 | 0.75374 | 10552.36 | 40000 | 0 | 17213 | 0 | 7483 | 3069.36 | 3069.36 | 0 | 0 | 0 | 0
2022053114 | 3 | 0.84176 | 67340.8 | 0 | 0 | 0.4562 | 15967 | 0.76821 | 10754.94 | 40000 | 0 | 15967 | 0 | 10754.94 | 0 | 0 | 618.86 | 0 | 0 | 618.86
2022053115 | 3 | 0.8682 | 69456 | 0 | 0 | 0.4514 | 15799 | 0.76463 | 10704.82 | 40000 | 0 | 15799 | 0 | 10704.82 | 0 | 0 | 2952.18 | 0 | 0 | 2952.18
2022053116 | 3 | 0.88957 | 71165.6 | 0 | 0 | 0.46501 | 16275.35 | 0.72803 | 10192.42 | 40000 | 0 | 16275.35 | 0 | 10192.42 | 0 | 0 | 4697.83 | 0 | 0 | 4697.83
2022053117 | 3 | 0.89813 | 71850.4 | 0 | 0 | 0.49448 | 17306.8 | 0.62236 | 8713.04 | 40000 | 0 | 17306.8 | 0 | 8713.04 | 0 | 0 | 5830.56 | 0 | 0 | 5830.56
2022053118 | 3 | 0.89575 | 71660 | 0 | 0 | 0.55572 | 19450.2 | 0.54938 | 7691.32 | 40000 | 0 | 19450.2 | 0 | 7691.32 | 0 | 0 | 4518.48 | 0 | 0 | 4518.48
2022053119 | 3 | 0.87773 | 70218.4 | 0 | 0 | 0.6219 | 21766.5 | 0.4441 | 6217.4 | 40000 | 0 | 21766.5 | 0 | 6217.4 | 0 | 0 | 2234.5 | 0 | 0 | 2234.5
2022053120 | 3 | 0.84546 | 67636.8 | 0 | 0 | 0.65873 | 23055.55 | 0.21313 | 2983.82 | 40000 | 0 | 23055.55 | 0 | 2983.82 | 0 | 0 | 1597.43 | 0 | 0 | 1597.43
2022053121 | 3 | 0.81143 | 64914.4 | 0 | 0 | 0.66304 | 23206.4 | 0.02701 | 378.14 | 40000 | 0 | 23206.4 | 0 | 378.14 | 0 | 0 | 1329.86 | 0 | 0 | 1329.86
2022053122 | 3 | 0.78516 | 62812.8 | 0 | 0 | 0.6428 | 22498 | 0 | 0 | 40000 | 0 | 22498 | 0 | 0 | 0 | 0 | 314.8 | 0 | 0 | 314.8
2022053123 | 3 | 0.73902 | 59121.6 | 0 | 0 | 0.62915 | 22020.25 | 0 | 0 | 40000 | 0 | 19121.6 | 2898.65 | 0 | 0 | 2898.65 | 0 | 0 | 0 | 0
2022053124 | 3 | 0.68822 | 55057.6 | 0 | 0 | 0.60837 | 21292.95 | 0 | 0 | 40000 | 0 | 15057.6 | 6235.35 | 0 | 0 | 6235.35 | 0 | 0 | 0 | 0
2022060101 | 4 | 0.64347 | 51477.6 | 0 | 0 | 0.55833 | 19541.55 | 0 | 0 | 40000 | 0 | 11477.6 | 8063.95 | 0 | 0 | 8063.95 | 0 | 0 | 0 | 0
2022060102 | 4 | 0.60933 | 48746.4 | 0 | 0 | 0.48148 | 16851.8 | 0 | 0 | 40000 | 0 | 8746.4 | 8105.4 | 0 | 0 | 8105.4 | 0 | 0 | 0 | 0
2022060103 | 4 | 0.58539 | 46831.2 | 0 | 0 | 0.45995 | 16098.25 | 0 | 0 | 40000 | 0 | 6831.2 | 9267.05 | 0 | 0 | 9267.05 | 0 | 0 | 0 | 0
2022060104 | 4 | 0.56838 | 45470.4 | 0 | 0 | 0.42927 | 15024.45 | 0 | 0 | 40000 | 0 | 5470.4 | 9554.05 | 0 | 0 | 9554.05 | 0 | 0 | 0 | 0
2022060105 | 4 | 0.56468 | 45174.4 | 0 | 0 | 0.42684 | 14939.4 | 0 | 0 | 40000 | 0 | 5174.4 | 9765 | 0 | 0 | 9765 | 0 | 0 | 0 | 0
2022060106 | 4 | 0.57378 | 45902.4 | 0 | 0 | 0.41347 | 14471.45 | 0 | 0 | 40000 | 0 | 5902.4 | 8569.05 | 0 | 0 | 8569.05 | 0 | 0 | 0 | 0
2022060107 | 4 | 0.59333 | 47466.4 | 0 | 0 | 0.37956 | 13284.6 | 0.00236 | 33.04 | 40000 | 0 | 7466.4 | 5818.2 | 0 | 33.04 | 5851.24 | 0 | 0 | 0 | 0
2022060108 | 4 | 0.60242 | 48193.6 | 0 | 0 | 0.35756 | 12514.6 | 0.08977 | 1256.78 | 40000 | 0 | 8193.6 | 4321 | 0 | 1256.78 | 5577.78 | 0 | 0 | 0 | 0
2022060109 | 4 | 0.62946 | 50356.8 | 0 | 0 | 0.36702 | 12845.7 | 0.31978 | 4476.92 | 40000 | 0 | 10356.8 | 2488.9 | 0 | 4476.92 | 6965.82 | 0 | 0 | 0 | 0
2022060110 | 4 | 0.66817 | 53453.6 | 0 | 0 | 0.43888 | 15360.8 | 0.48453 | 6783.42 | 40000 | 0 | 13453.6 | 1907.2 | 0 | 6783.42 | 8690.62 | 0 | 0 | 0 | 0
2022060111 | 4 | 0.71194 | 56955.2 | 0 | 0 | 0.43339 | 15168.65 | 0.63931 | 8950.34 | 40000 | 0 | 15168.65 | 0 | 1786.55 | 7163.79 | 7163.79 | 0 | 0 | 0 | 0
2022060112 | 4 | 0.75608 | 60486.4 | 0 | 0 | 0.38625 | 13518.75 | 0.67087 | 9392.18 | 40000 | 0 | 13518.75 | 0 | 6967.65 | 2424.53 | 2424.53 | 0 | 0 | 0 | 0
2022060113 | 4 | 0.79783 | 63826.4 | 0 | 0 | 0.33689 | 11791.15 | 0.68189 | 9546.46 | 40000 | 0 | 11791.15 | 0 | 9546.46 | 0 | 0 | 2488.79 | 0 | 0 | 2488.79
2022060114 | 4 | 0.83473 | 66778.4 | 0 | 0 | 0.31936 | 11177.6 | 0.67393 | 9435.02 | 40000 | 0 | 11177.6 | 0 | 9435.02 | 0 | 0 | 6165.78 | 0 | 0 | 6165.78
2022060115 | 4 | 0.85454 | 68363.2 | 0 | 0 | 0.33192 | 11617.2 | 0.65688 | 9196.32 | 40000 | 0 | 11617.2 | 0 | 9196.32 | 0 | 0 | 7549.68 | 0 | 0 | 7549.68
2022060116 | 4 | 0.85597 | 68477.6 | 0 | 0 | 0.3517 | 12309.5 | 0.59255 | 8295.7 | 40000 | 0 | 12309.5 | 0 | 8295.7 | 0 | 0 | 7872.4 | 0 | 0 | 7872.4
2022060117 | 4 | 0.84538 | 67630.4 | 0 | 0 | 0.39317 | 13760.95 | 0.40589 | 5682.46 | 40000 | 0 | 13760.95 | 0 | 5682.46 | 0 | 0 | 8186.99 | 0 | 0 | 8186.99
2022060118 | 4 | 0.8343 | 66744 | 0 | 0 | 0.45498 | 15924.3 | 0.24665 | 3453.1 | 40000 | 0 | 15924.3 | 0 | 3453.1 | 0 | 0 | 7366.6 | 0 | 0 | 7366.6
2022060119 | 4 | 0.81847 | 65477.6 | 0 | 0 | 0.48517 | 16980.95 | 0.18073 | 2530.22 | 40000 | 0 | 16980.95 | 0 | 2530.22 | 0 | 0 | 5966.43 | 0 | 0 | 5966.43
2022060120 | 4 | 0.78907 | 63125.6 | 0 | 0 | 0.43812 | 15334.2 | 0.05342 | 747.88 | 40000 | 0 | 15334.2 | 0 | 747.88 | 0 | 0 | 7043.52 | 0 | 0 | 7043.52
2022060121 | 4 | 0.75943 | 60754.4 | 0 | 0 | 0.45132 | 15796.2 | 0.00284 | 39.76 | 40000 | 0 | 15796.2 | 0 | 39.76 | 0 | 0 | 4918.44 | 0 | 0 | 4918.44
2022060122 | 4 | 0.73025 | 58420 | 0 | 0 | 0.46145 | 16150.75 | 0 | 0 | 40000 | 0 | 16150.75 | 0 | 0 | 0 | 0 | 2269.25 | 0 | 0 | 2269.25
2022060123 | 4 | 0.68703 | 54962.4 | 0 | 0 | 0.46102 | 16135.7 | 0 | 0 | 40000 | 0 | 14962.4 | 1173.3 | 0 | 0 | 1173.3 | 0 | 0 | 0 | 0
2022060124 | 4 | 0.63834 | 51067.2 | 0 | 0 | 0.47911 | 16768.85 | 0 | 0 | 40000 | 0 | 11067.2 | 5701.65 | 0 | 0 | 5701.65 | 0 | 0 | 0 | 0
2022060201 | 5 | 0.59745 | 47796 | 0 | 0 | 0.42105 | 14736.75 | 0 | 0 | 40000 | 0 | 7796 | 6940.75 | 0 | 0 | 6940.75 | 0 | 0 | 0 | 0
2022060202 | 5 | 0.56868 | 45494.4 | 0 | 0 | 0.37722 | 13202.7 | 0 | 0 | 40000 | 0 | 5494.4 | 7708.3 | 0 | 0 | 7708.3 | 0 | 0 | 0 | 0
2022060203 | 5 | 0.54781 | 43824.8 | 0 | 0 | 0.38931 | 13625.85 | 0 | 0 | 40000 | 0 | 3824.8 | 9801.05 | 0 | 0 | 9801.05 | 0 | 0 | 0 | 0
2022060204 | 5 | 0.53087 | 42469.6 | 0 | 0 | 0.30433 | 10651.55 | 0 | 0 | 40000 | 0 | 2469.6 | 8181.95 | 0 | 0 | 8181.95 | 0 | 0 | 0 | 0
2022060205 | 5 | 0.5279 | 42232 | 0 | 0 | 0.23108 | 8087.8 | 0 | 0 | 40000 | 0 | 2232 | 5855.8 | 0 | 0 | 5855.8 | 0 | 0 | 0 | 0
2022060206 | 5 | 0.52699 | 42159.2 | 0 | 0 | 0.16011 | 5603.85 | 0 | 0 | 40000 | 0 | 2159.2 | 3444.65 | 0 | 0 | 3444.65 | 0 | 0 | 0 | 0
2022060207 | 5 | 0.54282 | 43425.6 | 0 | 0 | 0.15521 | 5432.35 | 0.00072 | 10.08 | 40000 | 0 | 3425.6 | 2006.75 | 0 | 10.08 | 2016.83 | 0 | 0 | 0 | 0
2022060208 | 5 | 0.5553 | 44424 | 0 | 0 | 0.14717 | 5150.95 | 0.04526 | 633.64 | 40000 | 0 | 4424 | 726.95 | 0 | 633.64 | 1360.59 | 0 | 0 | 0 | 0
2022060209 | 5 | 0.57555 | 46044 | 0 | 0 | 0.13557 | 4744.95 | 0.13915 | 1948.1 | 40000 | 0 | 4744.95 | 0 | 1299.05 | 649.05 | 649.05 | 0 | 0 | 0 | 0
2022060210 | 5 | 0.60044 | 48035.2 | 0 | 0 | 0.12638 | 4423.3 | 0.19817 | 2774.38 | 40000 | 0 | 4423.3 | 0 | 2774.38 | 0 | 0 | 837.52 | 0 | 0 | 837.52
2022060211 | 5 | 0.6298 | 50384 | 0 | 0 | 0.10248 | 3586.8 | 0.31228 | 4371.92 | 40000 | 0 | 3586.8 | 0 | 4371.92 | 0 | 0 | 2425.28 | 0 | 0 | 2425.28
2022060212 | 5 | 0.66143 | 52914.4 | 0 | 0 | 0.08494 | 2972.9 | 0.40412 | 5657.68 | 40000 | 0 | 2972.9 | 0 | 5657.68 | 0 | 0 | 4283.82 | 0 | 0 | 4283.82
2022060213 | 5 | 0.69382 | 55505.6 | 0 | 0 | 0.07412 | 2594.2 | 0.45424 | 6359.36 | 40000 | 0 | 2594.2 | 0 | 6359.36 | 0 | 0 | 6552.04 | 0 | 0 | 6552.04
2022060214 | 5 | 0.72616 | 58092.8 | 0 | 0 | 0.07712 | 2699.2 | 0.48784 | 6829.76 | 40000 | 0 | 2699.2 | 0 | 6829.76 | 0 | 0 | 8563.84 | 0 | 0 | 8563.84
2022060215 | 5 | 0.75884 | 60707.2 | 0 | 0 | 0.09355 | 3274.25 | 0.54026 | 7563.64 | 40000 | 0 | 3274.25 | 0 | 7563.64 | 0 | 0 | 9869.31 | 0 | 0 | 9869.31
2022060216 | 5 | 0.78729 | 62983.2 | 0 | 0 | 0.10084 | 3529.4 | 0.56426 | 7899.64 | 40000 | 0 | 3529.4 | 0 | 7899.64 | 0 | 0 | 11554.16 | 0 | 0 | 11554.16
2022060217 | 5 | 0.8051 | 64408 | 0 | 0 | 0.11099 | 3884.65 | 0.57786 | 8090.04 | 40000 | 0 | 3884.65 | 0 | 8090.04 | 0 | 0 | 12433.31 | 0 | 0 | 12433.31
2022060218 | 5 | 0.80958 | 64766.4 | 0 | 0 | 0.12707 | 4447.45 | 0.56042 | 7845.88 | 40000 | 0 | 4447.45 | 0 | 7845.88 | 0 | 0 | 12473.07 | 0 | 0 | 12473.07
2022060219 | 5 | 0.79296 | 63436.8 | 0 | 0 | 0.15306 | 5357.1 | 0.41307 | 5782.98 | 40000 | 0 | 5357.1 | 0 | 5782.98 | 0 | 0 | 12296.72 | 0 | 0 | 12296.72
2022060220 | 5 | 0.76231 | 60984.8 | 0 | 0 | 0.16888 | 5910.8 | 0.16923 | 2369.22 | 40000 | 0 | 5910.8 | 0 | 2369.22 | 0 | 0 | 12704.78 | 0 | 0 | 12704.78
2022060221 | 5 | 0.73216 | 58572.8 | 0 | 0 | 0.17802 | 6230.7 | 0.01619 | 226.66 | 40000 | 0 | 6230.7 | 0 | 226.66 | 0 | 0 | 12115.44 | 0 | 0 | 12115.44
2022060222 | 5 | 0.70492 | 56393.6 | 0 | 0 | 0.20618 | 7216.3 | 0 | 0 | 40000 | 0 | 7216.3 | 0 | 0 | 0 | 0 | 9177.3 | 0 | 0 | 9177.3
2022060223 | 5 | 0.66001 | 52800.8 | 0 | 0 | 0.21891 | 7661.85 | 0 | 0 | 40000 | 0 | 7661.85 | 0 | 0 | 0 | 0 | 5138.95 | 0 | 0 | 5138.95
2022060224 | 5 | 0.61217 | 48973.6 | 0 | 0 | 0.22493 | 7872.55 | 0 | 0 | 40000 | 0 | 7872.55 | 0 | 0 | 0 | 0 | 1101.05 | 0 | 0 | 1101.05
2022060301 | 6 | 0.57027 | 45621.6 | 0 | 0 | 0.25124 | 8793.4 | 0 | 0 | 40000 | 0 | 5621.6 | 3171.8 | 0 | 0 | 3171.8 | 0 | 0 | 0 | 0
2022060302 | 6 | 0.53932 | 43145.6 | 0 | 0 | 0.26132 | 9146.2 | 0 | 0 | 40000 | 0 | 3145.6 | 6000.6 | 0 | 0 | 6000.6 | 0 | 0 | 0 | 0
2022060303 | 6 | 0.51677 | 41341.6 | 0 | 0 | 0.24826 | 8689.1 | 0 | 0 | 40000 | 0 | 1341.6 | 7347.5 | 0 | 0 | 7347.5 | 0 | 0 | 0 | 0
2022060304 | 6 | 0.50456 | 40364.8 | 0 | 0 | 0.24231 | 8480.85 | 0 | 0 | 40000 | 0 | 364.8 | 8116.05 | 0 | 0 | 8116.05 | 0 | 0 | 0 | 0
2022060305 | 6 | 0.49787 | 39829.6 | 0 | 0 | 0.25844 | 9045.4 | 0 | 0 | 39829.6 | 170.4 | 0 | 9045.4 | 0 | 0 | 9215.8 | 0 | 0 | 0 | 0
2022060306 | 6 | 0.51039 | 40831.2 | 0 | 0 | 0.28612 | 10014.2 | 0 | 0 | 40000 | 0 | 831.2 | 9183 | 0 | 0 | 9183 | 0 | 0 | 0 | 0
2022060307 | 6 | 0.52593 | 42074.4 | 0 | 0 | 0.20992 | 7347.2 | 0.00426 | 59.64 | 40000 | 0 | 2074.4 | 5272.8 | 0 | 59.64 | 5332.44 | 0 | 0 | 0 | 0
2022060308 | 6 | 0.54303 | 43442.4 | 0 | 0 | 0.1584 | 5544 | 0.107 | 1498 | 40000 | 0 | 3442.4 | 2101.6 | 0 | 1498 | 3599.6 | 0 | 0 | 0 | 0
2022060309 | 6 | 0.57011 | 45608.8 | 0 | 0 | 0.13033 | 4561.55 | 0.38344 | 5368.16 | 40000 | 0 | 4561.55 | 0 | 1047.25 | 4320.91 | 4320.91 | 0 | 0 | 0 | 0
2022060310 | 6 | 0.6045 | 48360 | 0 | 0 | 0.11458 | 4010.3 | 0.56071 | 7849.94 | 40000 | 0 | 4010.3 | 0 | 4349.7 | 3500.24 | 3500.24 | 0 | 0 | 0 | 0
2022060311 | 6 | 0.64203 | 51362.4 | 0 | 0 | 0.0961 | 3363.5 | 0.63466 | 8885.24 | 40000 | 0 | 3363.5 | 0 | 7998.9 | 886.34 | 886.34 | 0 | 0 | 0 | 0
2022060312 | 6 | 0.67633 | 54106.4 | 0 | 0 | 0.11842 | 4144.7 | 0.65044 | 9106.16 | 40000 | 0 | 4144.7 | 0 | 9106.16 | 0 | 0 | 855.54 | 0 | 0 | 855.54
2022060313 | 6 | 0.70454 | 56363.2 | 0 | 0 | 0.13982 | 4893.7 | 0.64673 | 9054.22 | 40000 | 0 | 4893.7 | 0 | 9054.22 | 0 | 0 | 2415.28 | 0 | 0 | 2415.28
2022060314 | 6 | 0.73532 | 58825.6 | 0 | 0 | 0.13264 | 4642.4 | 0.66051 | 9247.14 | 40000 | 0 | 4642.4 | 0 | 9247.14 | 0 | 0 | 4936.06 | 0 | 0 | 4936.06
2022060315 | 6 | 0.75904 | 60723.2 | 0 | 0 | 0.13907 | 4867.45 | 0.69629 | 9748.06 | 40000 | 0 | 4867.45 | 0 | 9748.06 | 0 | 0 | 6107.69 | 0 | 0 | 6107.69
2022060316 | 6 | 0.77496 | 61996.8 | 0 | 0 | 0.14309 | 5008.15 | 0.70043 | 9806.02 | 40000 | 0 | 5008.15 | 0 | 9806.02 | 0 | 0 | 7182.63 | 0 | 0 | 7182.63
2022060317 | 6 | 0.77956 | 62364.8 | 0 | 0 | 0.16488 | 5770.8 | 0.7082 | 9914.8 | 40000 | 0 | 5770.8 | 0 | 9914.8 | 0 | 0 | 6679.2 | 0 | 0 | 6679.2
2022060318 | 6 | 0.77109 | 61687.2 | 0 | 0 | 0.19021 | 6657.35 | 0.63544 | 8896.16 | 40000 | 0 | 6657.35 | 0 | 8896.16 | 0 | 0 | 6133.69 | 0 | 0 | 6133.69
2022060319 | 6 | 0.74659 | 59727.2 | 0 | 0 | 0.21302 | 7455.7 | 0.48008 | 6721.12 | 40000 | 0 | 7455.7 | 0 | 6721.12 | 0 | 0 | 5550.38 | 0 | 0 | 5550.38
2022060320 | 6 | 0.71812 | 57449.6 | 0 | 0 | 0.24174 | 8460.9 | 0.15813 | 2213.82 | 40000 | 0 | 8460.9 | 0 | 2213.82 | 0 | 0 | 6774.88 | 0 | 0 | 6774.88
2022060321 | 6 | 0.69121 | 55296.8 | 0 | 0 | 0.25202 | 8820.7 | 0.00596 | 83.44 | 40000 | 0 | 8820.7 | 0 | 83.44 | 0 | 0 | 6392.66 | 0 | 0 | 6392.66
2022060322 | 6 | 0.66711 | 53368.8 | 0 | 0 | 0.26162 | 9156.7 | 0 | 0 | 40000 | 0 | 9156.7 | 0 | 0 | 0 | 0 | 4212.1 | 0 | 0 | 4212.1
2022060323 | 6 | 0.62932 | 50345.6 | 0 | 0 | 0.26092 | 9132.2 | 0 | 0 | 40000 | 0 | 9132.2 | 0 | 0 | 0 | 0 | 1213.4 | 0 | 0 | 1213.4
2022060324 | 6 | 0.58813 | 47050.4 | 0 | 0 | 0.27167 | 9508.45 | 0 | 0 | 40000 | 0 | 7050.4 | 2458.05 | 0 | 0 | 2458.05 | 0 | 0 | 0 | 0
2022060401 | 7 | 0.55417 | 44333.6 | 0 | 0 | 0.29563 | 10347.05 | 0 | 0 | 40000 | 0 | 4333.6 | 6013.45 | 0 | 0 | 6013.45 | 0 | 0 | 0 | 0
2022060402 | 7 | 0.52599 | 42079.2 | 0 | 0 | 0.31449 | 11007.15 | 0 | 0 | 40000 | 0 | 2079.2 | 8927.95 | 0 | 0 | 8927.95 | 0 | 0 | 0 | 0
2022060403 | 7 | 0.50351 | 40280.8 | 0 | 0 | 0.29366 | 10278.1 | 0 | 0 | 40000 | 0 | 280.8 | 9997.3 | 0 | 0 | 9997.3 | 0 | 0 | 0 | 0
2022060404 | 7 | 0.49036 | 39228.8 | 0 | 0 | 0.26021 | 9107.35 | 0 | 0 | 39228.8 | 771.2 | 0 | 9107.35 | 0 | 0 | 9878.55 | 0 | 0 | 0 | 0
2022060405 | 7 | 0.48335 | 38668 | 0 | 0 | 0.24303 | 8506.05 | 0 | 0 | 38668 | 1332 | 0 | 8506.05 | 0 | 0 | 9838.05 | 0 | 0 | 0 | 0
2022060406 | 7 | 0.48173 | 38538.4 | 0 | 0 | 0.23291 | 8151.85 | 0 | 0 | 38538.4 | 1461.6 | 0 | 8151.85 | 0 | 0 | 9613.45 | 0 | 0 | 0 | 0
2022060407 | 7 | 0.48244 | 38595.2 | 0 | 0 | 0.1717 | 6009.5 | 0.00376 | 52.64 | 38595.2 | 1404.8 | 0 | 6009.5 | 0 | 52.64 | 7466.94 | 0 | 0 | 0 | 0
2022060408 | 7 | 0.49354 | 39483.2 | 0 | 0 | 0.16564 | 5797.4 | 0.11648 | 1630.72 | 39483.2 | 516.8 | 0 | 5797.4 | 0 | 1630.72 | 7944.92 | 0 | 0 | 0 | 0
2022060409 | 7 | 0.52227 | 41781.6 | 0 | 0 | 0.14022 | 4907.7 | 0.37482 | 5247.48 | 40000 | 0 | 1781.6 | 3126.1 | 0 | 5247.48 | 8373.58 | 0 | 0 | 0 | 0
2022060410 | 7 | 0.5606 | 44848 | 0 | 0 | 0.11982 | 4193.7 | 0.59724 | 8361.36 | 40000 | 0 | 4193.7 | 0 | 654.3 | 7707.06 | 7707.06 | 0 | 0 | 0 | 0
2022060411 | 7 | 0.60139 | 48111.2 | 0 | 0 | 0.11676 | 4086.6 | 0.71217 | 9970.38 | 40000 | 0 | 4086.6 | 0 | 4024.6 | 5945.78 | 5945.78 | 0 | 0 | 0 | 0
2022060412 | 7 | 0.64222 | 51377.6 | 0 | 0 | 0.14927 | 5224.45 | 0.73423 | 10279.22 | 40000 | 0 | 5224.45 | 0 | 6153.15 | 4126.07 | 4126.07 | 0 | 0 | 0 | 0
2022060413 | 7 | 0.67759 | 54207.2 | 0 | 0 | 0.15887 | 5560.45 | 0.74812 | 10473.68 | 40000 | 0 | 5560.45 | 0 | 8646.75 | 1826.93 | 1826.93 | 0 | 0 | 0 | 0
2022060414 | 7 | 0.6966 | 55728 | 0 | 0 | 0.16906 | 5917.1 | 0.72629 | 10168.06 | 40000 | 0 | 5917.1 | 0 | 9810.9 | 357.16 | 357.16 | 0 | 0 | 0 | 0
2022060415 | 7 | 0.73513 | 58810.4 | 0 | 0 | 0.1648 | 5768 | 0.72239 | 10113.46 | 40000 | 0 | 5768 | 0 | 10113.46 | 0 | 0 | 2928.94 | 0 | 0 | 2928.94
2022060416 | 7 | 0.76678 | 61342.4 | 0 | 0 | 0.16746 | 5861.1 | 0.67826 | 9495.64 | 40000 | 0 | 5861.1 | 0 | 9495.64 | 0 | 0 | 5985.66 | 0 | 0 | 5985.66
2022060417 | 7 | 0.7855 | 62840 | 0 | 0 | 0.17531 | 6135.85 | 0.64943 | 9092.02 | 40000 | 0 | 6135.85 | 0 | 9092.02 | 0 | 0 | 7612.13 | 0 | 0 | 7612.13
2022060418 | 7 | 0.78296 | 62636.8 | 0 | 0 | 0.18725 | 6553.75 | 0.62197 | 8707.58 | 40000 | 0 | 6553.75 | 0 | 8707.58 | 0 | 0 | 7375.47 | 0 | 0 | 7375.47
2022060419 | 7 | 0.77338 | 61870.4 | 0 | 0 | 0.22239 | 7783.65 | 0.4953 | 6934.2 | 40000 | 0 | 7783.65 | 0 | 6934.2 | 0 | 0 | 7152.55 | 0 | 0 | 7152.55
2022060420 | 7 | 0.7509 | 60072 | 0 | 0 | 0.28528 | 9984.8 | 0.27468 | 3845.52 | 40000 | 0 | 9984.8 | 0 | 3845.52 | 0 | 0 | 6241.68 | 0 | 0 | 6241.68
2022060421 | 7 | 0.72413 | 57930.4 | 0 | 0 | 0.35246 | 12336.1 | 0.02677 | 374.78 | 40000 | 0 | 12336.1 | 0 | 374.78 | 0 | 0 | 5219.52 | 0 | 0 | 5219.52
2022060422 | 7 | 0.70469 | 56375.2 | 0 | 0 | 0.47227 | 16529.45 | 0 | 0 | 40000 | 0 | 16375.2 | 154.25 | 0 | 0 | 154.25 | 0 | 0 | 0 | 0
2022060423 | 7 | 0.66966 | 53572.8 | 0 | 0 | 0.57202 | 20020.7 | 0 | 0 | 40000 | 0 | 13572.8 | 6447.9 | 0 | 0 | 6447.9 | 0 | 0 | 0 | 0
2022060424 | 7 | 0.63218 | 50574.4 | 0 | 0 | 0.61476 | 21516.6 | 0 | 0 | 40000 | 0 | 10574.4 | 10942.2 | 0 | 0 | 10942.2 | 0 | 0 | 0 | 0
2022060501 | 1 | 0.5949 | 47592 | 0 | 0 | 0.62778 | 21972.3 | 0 | 0 | 40000 | 0 | 7592 | 14380.3 | 0 | 0 | 14380.3 | 0 | 0 | 0 | 0
2022060502 | 1 | 0.56346 | 45076.8 | 0 | 0 | 0.61688 | 21590.8 | 0 | 0 | 40000 | 0 | 5076.8 | 16514 | 0 | 0 | 16514 | 0 | 0 | 0 | 0
2022060503 | 1 | 0.53722 | 42977.6 | 0 | 0 | 0.59293 | 20752.55 | 0 | 0 | 40000 | 0 | 2977.6 | 17774.95 | 0 | 0 | 17774.95 | 0 | 0 | 0 | 0
2022060504 | 1 | 0.51829 | 41463.2 | 0 | 0 | 0.56851 | 19897.85 | 0 | 0 | 40000 | 0 | 1463.2 | 18434.65 | 0 | 0 | 18434.65 | 0 | 0 | 0 | 0
2022060505 | 1 | 0.50934 | 40747.2 | 0 | 0 | 0.56297 | 19703.95 | 0 | 0 | 40000 | 0 | 747.2 | 18956.75 | 0 | 0 | 18956.75 | 0 | 0 | 0 | 0
2022060506 | 1 | 0.50281 | 40224.8 | 0 | 0 | 0.54997 | 19248.95 | 0 | 0 | 40000 | 0 | 224.8 | 19024.15 | 0 | 0 | 19024.15 | 0 | 0 | 0 | 0
2022060507 | 1 | 0.49537 | 39629.6 | 0 | 0 | 0.52719 | 18451.65 | 0.00093 | 13.02 | 39629.6 | 370.4 | 0 | 18451.65 | 0 | 13.02 | 18835.07 | 0 | 0 | 0 | 0
2022060508 | 1 | 0.50615 | 40492 | 0 | 0 | 0.52262 | 18291.7 | 0.06498 | 909.72 | 40000 | 0 | 492 | 17799.7 | 0 | 909.72 | 18709.42 | 0 | 0 | 0 | 0
2022060509 | 1 | 0.54847 | 43877.6 | 0 | 0 | 0.5135 | 17972.5 | 0.39294 | 5501.16 | 40000 | 0 | 3877.6 | 14094.9 | 0 | 5501.16 | 19596.06 | 0 | 0 | 0 | 0
2022060510 | 1 | 0.59981 | 47984.8 | 0 | 0 | 0.49917 | 17470.95 | 0.62844 | 8798.16 | 40000 | 0 | 7984.8 | 9486.15 | 0 | 8798.16 | 18284.31 | 0 | 0 | 0 | 0
2022060511 | 1 | 0.64672 | 51737.6 | 0 | 0 | 0.44834 | 15691.9 | 0.73569 | 10299.66 | 40000 | 0 | 11737.6 | 3954.3 | 0 | 10299.66 | 14253.96 | 0 | 0 | 0 | 0
2022060512 | 1 | 0.69167 | 55333.6 | 0 | 0 | 0.38896 | 13613.6 | 0.78409 | 10977.26 | 40000 | 0 | 13613.6 | 0 | 1720 | 9257.26 | 9257.26 | 0 | 0 | 0 | 0
2022060513 | 1 | 0.73519 | 58815.2 | 0 | 0 | 0.34643 | 12125.05 | 0.78741 | 11023.74 | 40000 | 0 | 12125.05 | 0 | 6690.15 | 4333.59 | 4333.59 | 0 | 0 | 0 | 0
2022060514 | 1 | 0.77695 | 62156 | 0 | 0 | 0.35404 | 12391.4 | 0.77367 | 10831.38 | 40000 | 0 | 12391.4 | 0 | 9764.6 | 1066.78 | 1066.78 | 0 | 0 | 0 | 0
2022060515 | 1 | 0.81258 | 65006.4 | 0 | 0 | 0.38516 | 13480.6 | 0.72712 | 10179.68 | 40000 | 0 | 13480.6 | 0 | 10179.68 | 0 | 0 | 1346.12 | 0 | 0 | 1346.12
2022060516 | 1 | 0.83768 | 67014.4 | 0 | 0 | 0.41882 | 14658.7 | 0.71971 | 10075.94 | 40000 | 0 | 14658.7 | 0 | 10075.94 | 0 | 0 | 2279.76 | 0 | 0 | 2279.76
2022060517 | 1 | 0.85232 | 68185.6 | 0 | 0 | 0.44031 | 15410.85 | 0.70042 | 9805.88 | 40000 | 0 | 15410.85 | 0 | 9805.88 | 0 | 0 | 2968.87 | 0 | 0 | 2968.87
2022060518 | 1 | 0.85173 | 68138.4 | 0 | 0 | 0.46023 | 16108.05 | 0.64774 | 9068.36 | 40000 | 0 | 16108.05 | 0 | 9068.36 | 0 | 0 | 2961.99 | 0 | 0 | 2961.99
2022060519 | 1 | 0.83719 | 66975.2 | 0 | 0 | 0.46523 | 16283.05 | 0.52299 | 7321.86 | 40000 | 0 | 16283.05 | 0 | 7321.86 | 0 | 0 | 3370.29 | 0 | 0 | 3370.29
2022060520 | 1 | 0.80598 | 64478.4 | 0 | 0 | 0.44954 | 15733.9 | 0.25302 | 3542.28 | 40000 | 0 | 15733.9 | 0 | 3542.28 | 0 | 0 | 5202.22 | 0 | 0 | 5202.22
2022060521 | 1 | 0.7746 | 61968 | 0 | 0 | 0.43603 | 15261.05 | 0.0197 | 275.8 | 40000 | 0 | 15261.05 | 0 | 275.8 | 0 | 0 | 6431.15 | 0 | 0 | 6431.15
2022060522 | 1 | 0.74879 | 59903.2 | 0 | 0 | 0.46155 | 16154.25 | 0 | 0 | 40000 | 0 | 16154.25 | 0 | 0 | 0 | 0 | 3748.95 | 0 | 0 | 3748.95
2022060523 | 1 | 0.70566 | 56452.8 | 0 | 0 | 0.49676 | 17386.6 | 0 | 0 | 40000 | 0 | 16452.8 | 933.8 | 0 | 0 | 933.8 | 0 | 0 | 0 | 0
2022060524 | 1 | 0.65812 | 52649.6 | 0 | 0 | 0.53686 | 18790.1 | 0 | 0 | 40000 | 0 | 12649.6 | 6140.5 | 0 | 0 | 6140.5 | 0 | 0 | 0 | 0
2022060601 | 2 | 0.61746 | 49396.8 | 0 | 0 | 0.5806 | 20321 | 0 | 0 | 40000 | 0 | 9396.8 | 10924.2 | 0 | 0 | 10924.2 | 0 | 0 | 0 | 0
2022060602 | 2 | 0.58951 | 47160.8 | 0 | 0 | 0.61596 | 21558.6 | 0 | 0 | 40000 | 0 | 7160.8 | 14397.8 | 0 | 0 | 14397.8 | 0 | 0 | 0 | 0
2022060603 | 2 | 0.57095 | 45676 | 0 | 0 | 0.63695 | 22293.25 | 0 | 0 | 40000 | 0 | 5676 | 16617.25 | 0 | 0 | 16617.25 | 0 | 0 | 0 | 0
2022060604 | 2 | 0.56446 | 45156.8 | 0 | 0 | 0.63145 | 22100.75 | 0 | 0 | 40000 | 0 | 5156.8 | 16943.95 | 0 | 0 | 16943.95 | 0 | 0 | 0 | 0
2022060605 | 2 | 0.56002 | 44801.6 | 0 | 0 | 0.62061 | 21721.35 | 0 | 0 | 40000 | 0 | 4801.6 | 16919.75 | 0 | 0 | 16919.75 | 0 | 0 | 0 | 0
2022060606 | 2 | 0.57095 | 45676 | 0 | 0 | 0.61776 | 21621.6 | 0 | 0 | 40000 | 0 | 5676 | 15945.6 | 0 | 0 | 15945.6 | 0 | 0 | 0 | 0
2022060607 | 2 | 0.58624 | 46899.2 | 0 | 0 | 0.59611 | 20863.85 | 0.00195 | 27.3 | 40000 | 0 | 6899.2 | 13964.65 | 0 | 27.3 | 13991.95 | 0 | 0 | 0 | 0
2022060608 | 2 | 0.60309 | 48247.2 | 0 | 0 | 0.56083 | 19629.05 | 0.17585 | 2461.9 | 40000 | 0 | 8247.2 | 11381.85 | 0 | 2461.9 | 13843.75 | 0 | 0 | 0 | 0
2022060609 | 2 | 0.63569 | 50855.2 | 0 | 0 | 0.51462 | 18011.7 | 0.53396 | 7475.44 | 40000 | 0 | 10855.2 | 7156.5 | 0 | 7475.44 | 14631.94 | 0 | 0 | 0 | 0
2022060610 | 2 | 0.67758 | 54206.4 | 0 | 0 | 0.49355 | 17274.25 | 0.71275 | 9978.5 | 40000 | 0 | 14206.4 | 3067.85 | 0 | 9978.5 | 13046.35 | 0 | 0 | 0 | 0
2022060611 | 2 | 0.72135 | 57708 | 0 | 0 | 0.45361 | 15876.35 | 0.76691 | 10736.74 | 40000 | 0 | 15876.35 | 0 | 1831.65 | 8905.09 | 8905.09 | 0 | 0 | 0 | 0
2022060612 | 2 | 0.76528 | 61222.4 | 0 | 0 | 0.381 | 13335 | 0.80492 | 11268.88 | 40000 | 0 | 13335 | 0 | 7887.4 | 3381.48 | 3381.48 | 0 | 0 | 0 | 0
2022060613 | 2 | 0.807 | 64560 | 0 | 0 | 0.30809 | 10783.15 | 0.80929 | 11330.06 | 40000 | 0 | 10783.15 | 0 | 11330.06 | 0 | 0 | 2446.79 | 0 | 0 | 2446.79
2022060614 | 2 | 0.84832 | 67865.6 | 0 | 0 | 0.26085 | 9129.75 | 0.81138 | 11359.32 | 40000 | 0 | 9129.75 | 0 | 11359.32 | 0 | 0 | 7376.53 | 0 | 0 | 7376.53
2022060615 | 2 | 0.87852 | 70281.6 | 0 | 0 | 0.23921 | 8372.35 | 0.80463 | 11264.82 | 40000 | 0 | 8372.35 | 0 | 11264.82 | 0 | 0 | 10644.43 | 0 | 0 | 10644.43
2022060616 | 2 | 0.89577 | 71661.6 | 0 | 0 | 0.23587 | 8255.45 | 0.78272 | 10958.08 | 40000 | 0 | 8255.45 | 0 | 10958.08 | 0 | 0 | 12448.07 | 0 | 0 | 12448.07
2022060617 | 2 | 0.90663 | 72530.4 | 0 | 0 | 0.24786 | 8675.1 | 0.75316 | 10544.24 | 40000 | 0 | 8675.1 | 0 | 10544.24 | 0 | 0 | 13311.06 | 0 | 0 | 13311.06
2022060618 | 2 | 0.90661 | 72528.8 | 0 | 0 | 0.26455 | 9259.25 | 0.7134 | 9987.6 | 40000 | 0 | 9259.25 | 0 | 9987.6 | 0 | 0 | 13281.95 | 0 | 0 | 13281.95
2022060619 | 2 | 0.89585 | 71668 | 0 | 0 | 0.27181 | 9513.35 | 0.60713 | 8499.82 | 40000 | 0 | 9513.35 | 0 | 8499.82 | 0 | 0 | 13654.83 | 0 | 0 | 13654.83
2022060620 | 2 | 0.87133 | 69706.4 | 0 | 0 | 0.29069 | 10174.15 | 0.34082 | 4771.48 | 40000 | 0 | 10174.15 | 0 | 4771.48 | 0 | 0 | 14760.77 | 0 | 0 | 14760.77
2022060621 | 2 | 0.83863 | 67090.4 | 0 | 0 | 0.33601 | 11760.35 | 0.04127 | 577.78 | 40000 | 0 | 11760.35 | 0 | 577.78 | 0 | 0 | 14752.27 | 0 | 0 | 14752.27
2022060622 | 2 | 0.80825 | 64660 | 0 | 0 | 0.40474 | 14165.9 | 0 | 0 | 40000 | 0 | 14165.9 | 0 | 0 | 0 | 0 | 10494.1 | 0 | 0 | 10494.1
2022060623 | 2 | 0.75744 | 60595.2 | 0 | 0 | 0.46691 | 16341.85 | 0.00011 | 1.54 | 40000 | 0 | 16341.85 | 0 | 1.54 | 0 | 0 | 4251.81 | 0 | 0 | 4251.81
2022060624 | 2 | 0.70062 | 56049.6 | 0 | 0 | 0.48221 | 16877.35 | 0 | 0 | 40000 | 0 | 16049.6 | 827.75 | 0 | 0 | 827.75 | 0 | 0 | 0 | 0
2022060701 | 3 | 0.65452 | 52361.6 | 0 | 0 | 0.50118 | 17541.3 | 0 | 0 | 40000 | 0 | 12361.6 | 5179.7 | 0 | 0 | 5179.7 | 0 | 0 | 0 | 0
2022060702 | 3 | 0.62044 | 49635.2 | 0 | 0 | 0.50315 | 17610.25 | 0 | 0 | 40000 | 0 | 9635.2 | 7975.05 | 0 | 0 | 7975.05 | 0 | 0 | 0 | 0
2022060703 | 3 | 0.59515 | 47612 | 0 | 0 | 0.50087 | 17530.45 | 0 | 0 | 40000 | 0 | 7612 | 9918.45 | 0 | 0 | 9918.45 | 0 | 0 | 0 | 0
2022060704 | 3 | 0.58004 | 46403.2 | 0 | 0 | 0.50163 | 17557.05 | 0 | 0 | 40000 | 0 | 6403.2 | 11153.85 | 0 | 0 | 11153.85 | 0 | 0 | 0 | 0
2022060705 | 3 | 0.57602 | 46081.6 | 0 | 0 | 0.50438 | 17653.3 | 0 | 0 | 40000 | 0 | 6081.6 | 11571.7 | 0 | 0 | 11571.7 | 0 | 0 | 0 | 0
2022060706 | 3 | 0.58289 | 46631.2 | 0 | 0 | 0.48821 | 17087.35 | 0 | 0 | 40000 | 0 | 6631.2 | 10456.15 | 0 | 0 | 10456.15 | 0 | 0 | 0 | 0
2022060707 | 3 | 0.59649 | 47719.2 | 0 | 0 | 0.47646 | 16676.1 | 0.00301 | 42.14 | 40000 | 0 | 7719.2 | 8956.9 | 0 | 42.14 | 8999.04 | 0 | 0 | 0 | 0
2022060708 | 3 | 0.6146 | 49168 | 0 | 0 | 0.47669 | 16684.15 | 0.1876 | 2626.4 | 40000 | 0 | 9168 | 7516.15 | 0 | 2626.4 | 10142.55 | 0 | 0 | 0 | 0
2022060709 | 3 | 0.64974 | 51979.2 | 0 | 0 | 0.46788 | 16375.8 | 0.54289 | 7600.46 | 40000 | 0 | 11979.2 | 4396.6 | 0 | 7600.46 | 11997.06 | 0 | 0 | 0 | 0
2022060710 | 3 | 0.68699 | 54959.2 | 0 | 0 | 0.44866 | 15703.1 | 0.66505 | 9310.7 | 40000 | 0 | 14959.2 | 743.9 | 0 | 9310.7 | 10054.6 | 0 | 0 | 0 | 0
2022060711 | 3 | 0.72619 | 58095.2 | 0 | 0 | 0.37164 | 13007.4 | 0.69176 | 9684.64 | 40000 | 0 | 13007.4 | 0 | 5087.8 | 4596.84 | 4596.84 | 0 | 0 | 0 | 0
2022060712 | 3 | 0.76589 | 61271.2 | 0 | 0 | 0.293 | 10255 | 0.7309 | 10232.6 | 40000 | 0 | 10255 | 0 | 10232.6 | 0 | 0 | 783.6 | 0 | 0 | 783.6
2022060713 | 3 | 0.80935 | 64748 | 0 | 0 | 0.23357 | 8174.95 | 0.75956 | 10633.84 | 40000 | 0 | 8174.95 | 0 | 10633.84 | 0 | 0 | 5939.21 | 0 | 0 | 5939.21
2022060714 | 3 | 0.85126 | 68100.8 | 0 | 0 | 0.20031 | 7010.85 | 0.78494 | 10989.16 | 40000 | 0 | 7010.85 | 0 | 10989.16 | 0 | 0 | 10100.79 | 0 | 0 | 10100.79
2022060715 | 3 | 0.88552 | 70841.6 | 0 | 0 | 0.19335 | 6767.25 | 0.78023 | 10923.22 | 40000 | 0 | 6767.25 | 0 | 10923.22 | 0 | 0 | 13151.13 | 0 | 0 | 13151.13
2022060716 | 3 | 0.90267 | 72213.6 | 0 | 0 | 0.20132 | 7046.2 | 0.77332 | 10826.48 | 40000 | 0 | 7046.2 | 0 | 10826.48 | 0 | 0 | 14340.92 | 0 | 0 | 14340.92
2022060717 | 3 | 0.91147 | 72917.6 | 0 | 0 | 0.22355 | 7824.25 | 0.71537 | 10015.18 | 40000 | 0 | 7824.25 | 0 | 10015.18 | 0 | 0 | 15078.17 | 0 | 0 | 15078.17
2022060718 | 3 | 0.91159 | 72927.2 | 0 | 0 | 0.25816 | 9035.6 | 0.64592 | 9042.88 | 40000 | 0 | 9035.6 | 0 | 9042.88 | 0 | 0 | 14848.72 | 0 | 0 | 14848.72
2022060719 | 3 | 0.90145 | 72116 | 0 | 0 | 0.29922 | 10472.7 | 0.53473 | 7486.22 | 40000 | 0 | 10472.7 | 0 | 7486.22 | 0 | 0 | 14157.08 | 0 | 0 | 14157.08
2022060720 | 3 | 0.87227 | 69781.6 | 0 | 0 | 0.35277 | 12346.95 | 0.27295 | 3821.3 | 40000 | 0 | 12346.95 | 0 | 3821.3 | 0 | 0 | 13613.35 | 0 | 0 | 13613.35
2022060721 | 3 | 0.83969 | 67175.2 | 0 | 0 | 0.38857 | 13599.95 | 0.03123 | 437.22 | 40000 | 0 | 13599.95 | 0 | 437.22 | 0 | 0 | 13138.03 | 0 | 0 | 13138.03
2022060722 | 3 | 0.80911 | 64728.8 | 0 | 0 | 0.40607 | 14212.45 | 0 | 0 | 40000 | 0 | 14212.45 | 0 | 0 | 0 | 0 | 10516.35 | 0 | 0 | 10516.35
2022060723 | 3 | 0.75822 | 60657.6 | 0 | 0 | 0.4254 | 14889 | 0 | 0 | 40000 | 0 | 14889 | 0 | 0 | 0 | 0 | 5768.6 | 0 | 0 | 5768.6
2022060724 | 3 | 0.70557 | 56445.6 | 0 | 0 | 0.44434 | 15551.9 | 0 | 0 | 40000 | 0 | 15551.9 | 0 | 0 | 0 | 0 | 893.7 | 0 | 0 | 893.7
2022060801 | 4 | 0.65794 | 52635.2 | 0 | 0 | 0.44111 | 15438.85 | 0 | 0 | 40000 | 0 | 12635.2 | 2803.65 | 0 | 0 | 2803.65 | 0 | 0 | 0 | 0
2022060802 | 4 | 0.62512 | 50009.6 | 0 | 0 | 0.45886 | 16060.1 | 0 | 0 | 40000 | 0 | 10009.6 | 6050.5 | 0 | 0 | 6050.5 | 0 | 0 | 0 | 0
2022060803 | 4 | 0.60176 | 48140.8 | 0 | 0 | 0.45709 | 15998.15 | 0 | 0 | 40000 | 0 | 8140.8 | 7857.35 | 0 | 0 | 7857.35 | 0 | 0 | 0 | 0
2022060804 | 4 | 0.5857 | 46856 | 0 | 0 | 0.42942 | 15029.7 | 0 | 0 | 40000 | 0 | 6856 | 8173.7 | 0 | 0 | 8173.7 | 0 | 0 | 0 | 0
2022060805 | 4 | 0.58047 | 46437.6 | 0 | 0 | 0.42218 | 14776.3 | 0 | 0 | 40000 | 0 | 6437.6 | 8338.7 | 0 | 0 | 8338.7 | 0 | 0 | 0 | 0
2022060806 | 4 | 0.58823 | 47058.4 | 0 | 0 | 0.42336 | 14817.6 | 0 | 0 | 40000 | 0 | 7058.4 | 7759.2 | 0 | 0 | 7759.2 | 0 | 0 | 0 | 0
2022060807 | 4 | 0.59962 | 47969.6 | 0 | 0 | 0.44158 | 15455.3 | 0.00406 | 56.84 | 40000 | 0 | 7969.6 | 7485.7 | 0 | 56.84 | 7542.54 | 0 | 0 | 0 | 0
2022060808 | 4 | 0.61821 | 49456.8 | 0 | 0 | 0.47786 | 16725.1 | 0.14116 | 1976.24 | 40000 | 0 | 9456.8 | 7268.3 | 0 | 1976.24 | 9244.54 | 0 | 0 | 0 | 0
2022060809 | 4 | 0.65505 | 52404 | 0 | 0 | 0.49726 | 17404.1 | 0.42924 | 6009.36 | 40000 | 0 | 12404 | 5000.1 | 0 | 6009.36 | 11009.46 | 0 | 0 | 0 | 0
2022060810 | 4 | 0.69173 | 55338.4 | 0 | 0 | 0.51645 | 18075.75 | 0.50762 | 7106.68 | 40000 | 0 | 15338.4 | 2737.35 | 0 | 7106.68 | 9844.03 | 0 | 0 | 0 | 0
2022060811 | 4 | 0.73291 | 58632.8 | 0 | 0 | 0.49837 | 17442.95 | 0.58914 | 8247.96 | 40000 | 0 | 17442.95 | 0 | 1189.85 | 7058.11 | 7058.11 | 0 | 0 | 0 | 0
2022060812 | 4 | 0.77029 | 61623.2 | 0 | 0 | 0.50744 | 17760.4 | 0.5721 | 8009.4 | 40000 | 0 | 17760.4 | 0 | 3862.8 | 4146.6 | 4146.6 | 0 | 0 | 0 | 0
2022060813 | 4 | 0.79615 | 63692 | 0 | 0 | 0.5112 | 17892 | 0.48538 | 6795.32 | 40000 | 0 | 17892 | 0 | 5800 | 995.32 | 995.32 | 0 | 0 | 0 | 0
2022060814 | 4 | 0.82187 | 65749.6 | 0 | 0 | 0.48756 | 17064.6 | 0.51362 | 7190.68 | 40000 | 0 | 17064.6 | 0 | 7190.68 | 0 | 0 | 1494.32 | 0 | 0 | 1494.32
2022060815 | 4 | 0.84402 | 67521.6 | 0 | 0 | 0.46462 | 16261.7 | 0.56455 | 7903.7 | 40000 | 0 | 16261.7 | 0 | 7903.7 | 0 | 0 | 3356.2 | 0 | 0 | 3356.2
2022060816 | 4 | 0.8603 | 68824 | 0 | 0 | 0.41622 | 14567.7 | 0.5608 | 7851.2 | 40000 | 0 | 14567.7 | 0 | 7851.2 | 0 | 0 | 6405.1 | 0 | 0 | 6405.1
2022060817 | 4 | 0.87284 | 69827.2 | 0 | 0 | 0.36693 | 12842.55 | 0.44745 | 6264.3 | 40000 | 0 | 12842.55 | 0 | 6264.3 | 0 | 0 | 10720.35 | 0 | 0 | 10720.35
2022060818 | 4 | 0.87324 | 69859.2 | 0 | 0 | 0.372 | 13020 | 0.39635 | 5548.9 | 40000 | 0 | 13020 | 0 | 5548.9 | 0 | 0 | 11290.3 | 0 | 0 | 11290.3
2022060819 | 4 | 0.85568 | 68454.4 | 0 | 0 | 0.36965 | 12937.75 | 0.27503 | 3850.42 | 40000 | 0 | 12937.75 | 0 | 3850.42 | 0 | 0 | 11666.23 | 0 | 0 | 11666.23
2022060820 | 4 | 0.8272 | 66176 | 0 | 0 | 0.36292 | 12702.2 | 0.09847 | 1378.58 | 40000 | 0 | 12702.2 | 0 | 1378.58 | 0 | 0 | 12095.22 | 0 | 0 | 12095.22
2022060821 | 4 | 0.7959 | 63672 | 0 | 0 | 0.33113 | 11589.55 | 0.00696 | 97.44 | 40000 | 0 | 11589.55 | 0 | 97.44 | 0 | 0 | 11985.01 | 0 | 0 | 11985.01
2022060822 | 4 | 0.76815 | 61452 | 0 | 0 | 0.3342 | 11697 | 0 | 0 | 40000 | 0 | 11697 | 0 | 0 | 0 | 0 | 9755 | 0 | 0 | 9755
2022060823 | 4 | 0.72107 | 57685.6 | 0 | 0 | 0.34719 | 12151.65 | 0 | 0 | 40000 | 0 | 12151.65 | 0 | 0 | 0 | 0 | 5533.95 | 0 | 0 | 5533.95
2022060824 | 4 | 0.66825 | 53460 | 0 | 0 | 0.31852 | 11148.2 | 0 | 0 | 40000 | 0 | 11148.2 | 0 | 0 | 0 | 0 | 2311.8 | 0 | 0 | 2311.8
2022060901 | 5 | 0.62242 | 49793.6 | 0 | 0 | 0.28064 | 9822.4 | 0.00115 | 16.1 | 40000 | 0 | 9793.6 | 28.8 | 0 | 16.1 | 44.9 | 0 | 0 | 0 | 0
2022060902 | 5 | 0.58873 | 47098.4 | 0 | 0 | 0.2437 | 8529.5 | 0.00091 | 12.74 | 40000 | 0 | 7098.4 | 1431.1 | 0 | 12.74 | 1443.84 | 0 | 0 | 0 | 0
2022060903 | 5 | 0.56627 | 45301.6 | 0 | 0 | 0.24038 | 8413.3 | 0.00019 | 2.66 | 40000 | 0 | 5301.6 | 3111.7 | 0 | 2.66 | 3114.36 | 0 | 0 | 0 | 0
2022060904 | 5 | 0.55159 | 44127.2 | 0 | 0 | 0.22527 | 7884.45 | 0.0003 | 4.2 | 40000 | 0 | 4127.2 | 3757.25 | 0 | 4.2 | 3761.45 | 0 | 0 | 0 | 0
2022060905 | 5 | 0.54594 | 43675.2 | 0 | 0 | 0.19563 | 6847.05 | 0 | 0 | 40000 | 0 | 3675.2 | 3171.85 | 0 | 0 | 3171.85 | 0 | 0 | 0 | 0
2022060906 | 5 | 0.55488 | 44390.4 | 0 | 0 | 0.18985 | 6644.75 | 0 | 0 | 40000 | 0 | 4390.4 | 2254.35 | 0 | 0 | 2254.35 | 0 | 0 | 0 | 0
2022060907 | 5 | 0.57053 | 45642.4 | 0 | 0 | 0.17027 | 5959.45 | 0.00215 | 30.1 | 40000 | 0 | 5642.4 | 317.05 | 0 | 30.1 | 347.15 | 0 | 0 | 0 | 0
2022060908 | 5 | 0.59026 | 47220.8 | 0 | 0 | 0.15101 | 5285.35 | 0.12692 | 1776.88 | 40000 | 0 | 5285.35 | 0 | 1776.88 | 0 | 0 | 158.57 | 0 | 0 | 158.57
2022060909 | 5 | 0.6182 | 49456 | 0 | 0 | 0.13029 | 4560.15 | 0.47361 | 6630.54 | 40000 | 0 | 4560.15 | 0 | 4895.85 | 1734.69 | 1734.69 | 0 | 0 | 0 | 0
2022060910 | 5 | 0.65645 | 52516 | 0 | 0 | 0.15197 | 5318.95 | 0.62695 | 8777.3 | 40000 | 0 | 5318.95 | 0 | 7197.05 | 1580.25 | 1580.25 | 0 | 0 | 0 | 0
2022060911 | 5 | 0.7037 | 56296 | 0 | 0 | 0.1474 | 5159 | 0.70328 | 9845.92 | 40000 | 0 | 5159 | 0 | 9845.92 | 0 | 0 | 1291.08 | 0 | 0 | 1291.08
2022060912 | 5 | 0.7543 | 60344 | 0 | 0 | 0.15557 | 5444.95 | 0.78836 | 11037.04 | 40000 | 0 | 5444.95 | 0 | 11037.04 | 0 | 0 | 3862.01 | 0 | 0 | 3862.01
2022060913 | 5 | 0.80228 | 64182.4 | 0 | 0 | 0.18013 | 6304.55 | 0.80122 | 11217.08 | 40000 | 0 | 6304.55 | 0 | 11217.08 | 0 | 0 | 6660.77 | 0 | 0 | 6660.77
2022060914 | 5 | 0.8471 | 67768 | 0 | 0 | 0.21189 | 7416.15 | 0.79326 | 11105.64 | 40000 | 0 | 7416.15 | 0 | 11105.64 | 0 | 0 | 9246.21 | 0 | 0 | 9246.21
2022060915 | 5 | 0.88259 | 70607.2 | 0 | 0 | 0.23553 | 8243.55 | 0.78326 | 10965.64 | 40000 | 0 | 8243.55 | 0 | 10965.64 | 0 | 0 | 11398.01 | 0 | 0 | 11398.01
2022060916 | 5 | 0.90085 | 72068 | 0 | 0 | 0.26439 | 9253.65 | 0.75298 | 10541.72 | 40000 | 0 | 9253.65 | 0 | 10541.72 | 0 | 0 | 12272.63 | 0 | 0 | 12272.63
2022060917 | 5 | 0.90942 | 72753.6 | 0 | 0 | 0.31358 | 10975.3 | 0.70626 | 9887.64 | 40000 | 0 | 10975.3 | 0 | 9887.64 | 0 | 0 | 11890.66 | 0 | 0 | 11890.66
2022060918 | 5 | 0.90908 | 72726.4 | 0 | 0 | 0.3468 | 12138 | 0.65486 | 9168.04 | 40000 | 0 | 12138 | 0 | 9168.04 | 0 | 0 | 11420.36 | 0 | 0 | 11420.36
2022060919 | 5 | 0.89975 | 71980 | 0 | 0 | 0.36025 | 12608.75 | 0.55371 | 7751.94 | 40000 | 0 | 12608.75 | 0 | 7751.94 | 0 | 0 | 11619.31 | 0 | 0 | 11619.31
2022060920 | 5 | 0.87132 | 69705.6 | 0 | 0 | 0.38862 | 13601.7 | 0.27274 | 3818.36 | 40000 | 0 | 13601.7 | 0 | 3818.36 | 0 | 0 | 12285.54 | 0 | 0 | 12285.54
2022060921 | 5 | 0.83727 | 66981.6 | 0 | 0 | 0.38026 | 13309.1 | 0.0285 | 399 | 40000 | 0 | 13309.1 | 0 | 399 | 0 | 0 | 13273.5 | 0 | 0 | 13273.5
2022060922 | 5 | 0.80728 | 64582.4 | 0 | 0 | 0.39568 | 13848.8 | 0 | 0 | 40000 | 0 | 13848.8 | 0 | 0 | 0 | 0 | 10733.6 | 0 | 0 | 10733.6
2022060923 | 5 | 0.7603 | 60824 | 0 | 0 | 0.44413 | 15544.55 | 0 | 0 | 40000 | 0 | 15544.55 | 0 | 0 | 0 | 0 | 5279.45 | 0 | 0 | 5279.45
2022060924 | 5 | 0.70778 | 56622.4 | 0 | 0 | 0.44698 | 15644.3 | 0 | 0 | 40000 | 0 | 15644.3 | 0 | 0 | 0 | 0 | 978.1 | 0 | 0 | 978.1
2022061001 | 6 | 0.65914 | 52731.2 | 0 | 0 | 0.43313 | 15159.55 | 0 | 0 | 40000 | 0 | 12731.2 | 2428.35 | 0 | 0 | 2428.35 | 0 | 0 | 0 | 0
2022061002 | 6 | 0.62163 | 49730.4 | 0 | 0 | 0.43641 | 15274.35 | 0 | 0 | 40000 | 0 | 9730.4 | 5543.95 | 0 | 0 | 5543.95 | 0 | 0 | 0 | 0
2022061003 | 6 | 0.59427 | 47541.6 | 0 | 0 | 0.43248 | 15136.8 | 0 | 0 | 40000 | 0 | 7541.6 | 7595.2 | 0 | 0 | 7595.2 | 0 | 0 | 0 | 0
2022061004 | 6 | 0.57692 | 46153.6 | 0 | 0 | 0.35398 | 12389.3 | 0 | 0 | 40000 | 0 | 6153.6 | 6235.7 | 0 | 0 | 6235.7 | 0 | 0 | 0 | 0
2022061005 | 6 | 0.57096 | 45676.8 | 0 | 0 | 0.29246 | 10236.1 | 0 | 0 | 40000 | 0 | 5676.8 | 4559.3 | 0 | 0 | 4559.3 | 0 | 0 | 0 | 0
2022061006 | 6 | 0.57646 | 46116.8 | 0 | 0 | 0.30243 | 10585.05 | 0 | 0 | 40000 | 0 | 6116.8 | 4468.25 | 0 | 0 | 4468.25 | 0 | 0 | 0 | 0
2022061007 | 6 | 0.58931 | 47144.8 | 0 | 0 | 0.30881 | 10808.35 | 0.002 | 28 | 40000 | 0 | 7144.8 | 3663.55 | 0 | 28 | 3691.55 | 0 | 0 | 0 | 0
2022061008 | 6 | 0.60477 | 48381.6 | 0 | 0 | 0.34023 | 11908.05 | 0.14803 | 2072.42 | 40000 | 0 | 8381.6 | 3526.45 | 0 | 2072.42 | 5598.87 | 0 | 0 | 0 | 0
2022061009 | 6 | 0.63386 | 50708.8 | 0 | 0 | 0.3403 | 11910.5 | 0.46683 | 6535.62 | 40000 | 0 | 10708.8 | 1201.7 | 0 | 6535.62 | 7737.32 | 0 | 0 | 0 | 0
2022061010 | 6 | 0.67043 | 53634.4 | 0 | 0 | 0.367 | 12845 | 0.6213 | 8698.2 | 40000 | 0 | 12845 | 0 | 789.4 | 7908.8 | 7908.8 | 0 | 0 | 0 | 0
2022061011 | 6 | 0.71174 | 56939.2 | 0 | 0 | 0.35581 | 12453.35 | 0.70575 | 9880.5 | 40000 | 0 | 12453.35 | 0 | 4485.85 | 5394.65 | 5394.65 | 0 | 0 | 0 | 0
2022061012 | 6 | 0.76018 | 60814.4 | 0 | 0 | 0.31007 | 10852.45 | 0.76892 | 10764.88 | 40000 | 0 | 10852.45 | 0 | 9961.95 | 802.93 | 802.93 | 0 | 0 | 0 | 0
2022061013 | 6 | 0.80616 | 64492.8 | 0 | 0 | 0.2242 | 7847 | 0.78972 | 11056.08 | 40000 | 0 | 7847 | 0 | 11056.08 | 0 | 0 | 5589.72 | 0 | 0 | 5589.72
2022061014 | 6 | 0.85383 | 68306.4 | 0 | 0 | 0.18795 | 6578.25 | 0.79826 | 11175.64 | 40000 | 0 | 6578.25 | 0 | 11175.64 | 0 | 0 | 10552.51 | 0 | 0 | 10552.51
2022061015 | 6 | 0.89329 | 71463.2 | 0 | 0 | 0.19197 | 6718.95 | 0.79352 | 11109.28 | 40000 | 0 | 6718.95 | 0 | 11109.28 | 0 | 0 | 13634.97 | 0 | 0 | 13634.97
2022061016 | 6 | 0.91184 | 72947.2 | 0 | 0 | 0.196 | 6860 | 0.80301 | 11242.14 | 40000 | 0 | 6860 | 0 | 11242.14 | 0 | 0 | 14845.06 | 0 | 0 | 14845.06
2022061017 | 6 | 0.9209 | 73672 | 0 | 0 | 0.20612 | 7214.2 | 0.76352 | 10689.28 | 40000 | 0 | 7214.2 | 0 | 10689.28 | 0 | 0 | 15768.52 | 0 | 0 | 15768.52
2022061018 | 6 | 0.92548 | 74038.4 | 0 | 0 | 0.22445 | 7855.75 | 0.71097 | 9953.58 | 40000 | 0 | 7855.75 | 0 | 9953.58 | 0 | 0 | 16229.07 | 0 | 0 | 16229.07
2022061019 | 6 | 0.92021 | 73616.8 | 0 | 0 | 0.23872 | 8355.2 | 0.6097 | 8535.8 | 40000 | 0 | 8355.2 | 0 | 8535.8 | 0 | 0 | 16725.8 | 0 | 0 | 16725.8
2022061020 | 6 | 0.89505 | 71604 | 0 | 0 | 0.25275 | 8846.25 | 0.33356 | 4669.84 | 40000 | 0 | 8846.25 | 0 | 4669.84 | 0 | 0 | 18087.91 | 0 | 0 | 18087.91
2022061021 | 6 | 0.85693 | 68554.4 | 0 | 0 | 0.29583 | 10354.05 | 0.03616 | 506.24 | 40000 | 0 | 10354.05 | 0 | 506.24 | 0 | 0 | 17694.11 | 0 | 0 | 17694.11
2022061022 | 6 | 0.82564 | 66051.2 | 0 | 0 | 0.37965 | 13287.75 | 0 | 0 | 40000 | 0 | 13287.75 | 0 | 0 | 0 | 0 | 12763.45 | 0 | 0 | 12763.45
2022061023 | 6 | 0.77912 | 62329.6 | 0 | 0 | 0.46433 | 16251.55 | 0 | 0 | 40000 | 0 | 16251.55 | 0 | 0 | 0 | 0 | 6078.05 | 0 | 0 | 6078.05
2022061024 | 6 | 0.73422 | 58737.6 | 0 | 0 | 0.51287 | 17950.45 | 0 | 0 | 40000 | 0 | 17950.45 | 0 | 0 | 0 | 0 | 787.15 | 0 | 0 | 787.15
2022061101 | 7 | 0.68738 | 54990.4 | 0 | 0 | 0.54168 | 18958.8 | 0 | 0 | 40000 | 0 | 14990.4 | 3968.4 | 0 | 0 | 3968.4 | 0 | 0 | 0 | 0
2022061102 | 7 | 0.64963 | 51970.4 | 0 | 0 | 0.55242 | 19334.7 | 0 | 0 | 40000 | 0 | 11970.4 | 7364.3 | 0 | 0 | 7364.3 | 0 | 0 | 0 | 0
2022061103 | 7 | 0.6188 | 49504 | 0 | 0 | 0.56225 | 19678.75 | 0 | 0 | 40000 | 0 | 9504 | 10174.75 | 0 | 0 | 10174.75 | 0 | 0 | 0 | 0
2022061104 | 7 | 0.59805 | 47844 | 0 | 0 | 0.5524 | 19334 | 0 | 0 | 40000 | 0 | 7844 | 11490 | 0 | 0 | 11490 | 0 | 0 | 0 | 0
2022061105 | 7 | 0.581 | 46480 | 0 | 0 | 0.53668 | 18783.8 | 0 | 0 | 40000 | 0 | 6480 | 12303.8 | 0 | 0 | 12303.8 | 0 | 0 | 0 | 0
2022061106 | 7 | 0.57656 | 46124.8 | 0 | 0 | 0.53691 | 18791.85 | 0 | 0 | 40000 | 0 | 6124.8 | 12667.05 | 0 | 0 | 12667.05 | 0 | 0 | 0 | 0
2022061107 | 7 | 0.57638 | 46110.4 | 0 | 0 | 0.51859 | 18150.65 | 0.00386 | 54.04 | 40000 | 0 | 6110.4 | 12040.25 | 0 | 54.04 | 12094.29 | 0 | 0 | 0 | 0
2022061108 | 7 | 0.58525 | 46820 | 0 | 0 | 0.45974 | 16090.9 | 0.19762 | 2766.68 | 40000 | 0 | 6820 | 9270.9 | 0 | 2766.68 | 12037.58 | 0 | 0 | 0 | 0
2022061109 | 7 | 0.62752 | 50201.6 | 0 | 0 | 0.40991 | 14346.85 | 0.56039 | 7845.46 | 40000 | 0 | 10201.6 | 4145.25 | 0 | 7845.46 | 11990.71 | 0 | 0 | 0 | 0
2022061110 | 7 | 0.68311 | 54648.8 | 0 | 0 | 0.44441 | 15554.35 | 0.7302 | 10222.8 | 40000 | 0 | 14648.8 | 905.55 | 0 | 10222.8 | 11128.35 | 0 | 0 | 0 | 0
2022061111 | 7 | 0.73915 | 59132 | 0 | 0 | 0.43838 | 15343.3 | 0.79451 | 11123.14 | 40000 | 0 | 15343.3 | 0 | 3788.7 | 7334.44 | 7334.44 | 0 | 0 | 0 | 0
2022061112 | 7 | 0.79457 | 63565.6 | 0 | 0 | 0.37836 | 13242.6 | 0.8088 | 11323.2 | 40000 | 0 | 13242.6 | 0 | 10323 | 1000.2 | 1000.2 | 0 | 0 | 0 | 0
2022061113 | 7 | 0.8413 | 67304 | 0 | 0 | 0.34743 | 12160.05 | 0.81265 | 11377.1 | 40000 | 0 | 12160.05 | 0 | 11377.1 | 0 | 0 | 3766.85 | 0 | 0 | 3766.85
2022061114 | 7 | 0.88328 | 70662.4 | 0 | 0 | 0.33059 | 11570.65 | 0.7922 | 11090.8 | 40000 | 0 | 11570.65 | 0 | 11090.8 | 0 | 0 | 8000.95 | 0 | 0 | 8000.95
2022061115 | 7 | 0.913 | 73040 | 0 | 0 | 0.30217 | 10575.95 | 0.78341 | 10967.74 | 40000 | 0 | 10575.95 | 0 | 10967.74 | 0 | 0 | 11496.31 | 0 | 0 | 11496.31
2022061116 | 7 | 0.92554 | 74043.2 | 0 | 0 | 0.30594 | 10707.9 | 0.75867 | 10621.38 | 40000 | 0 | 10707.9 | 0 | 10621.38 | 0 | 0 | 12713.92 | 0 | 0 | 12713.92
2022061117 | 7 | 0.93167 | 74533.6 | 0 | 0 | 0.31393 | 10987.55 | 0.73039 | 10225.46 | 40000 | 0 | 10987.55 | 0 | 10225.46 | 0 | 0 | 13320.59 | 0 | 0 | 13320.59
2022061118 | 7 | 0.93112 | 74489.6 | 0 | 0 | 0.34439 | 12053.65 | 0.68559 | 9598.26 | 40000 | 0 | 12053.65 | 0 | 9598.26 | 0 | 0 | 12837.69 | 0 | 0 | 12837.69
2022061119 | 7 | 0.92496 | 73996.8 | 0 | 0 | 0.38139 | 13348.65 | 0.58712 | 8219.68 | 40000 | 0 | 13348.65 | 0 | 8219.68 | 0 | 0 | 12428.47 | 0 | 0 | 12428.47
2022061120 | 7 | 0.90285 | 72228 | 0 | 0 | 0.41895 | 14663.25 | 0.35604 | 4984.56 | 40000 | 0 | 14663.25 | 0 | 4984.56 | 0 | 0 | 12580.19 | 0 | 0 | 12580.19
2022061121 | 7 | 0.86717 | 69373.6 | 0 | 0 | 0.47389 | 16586.15 | 0.04513 | 631.82 | 40000 | 0 | 16586.15 | 0 | 631.82 | 0 | 0 | 12155.63 | 0 | 0 | 12155.63
2022061122 | 7 | 0.83535 | 66828 | 0 | 0 | 0.57853 | 20248.55 | 0 | 0 | 40000 | 0 | 20248.55 | 0 | 0 | 0 | 0 | 6579.45 | 0 | 0 | 6579.45
2022061123 | 7 | 0.79314 | 63451.2 | 0 | 0 | 0.64741 | 22659.35 | 0 | 0 | 40000 | 0 | 22659.35 | 0 | 0 | 0 | 0 | 791.85 | 0 | 0 | 791.85
2022061124 | 7 | 0.74635 | 59708 | 0 | 0 | 0.65795 | 23028.25 | 0 | 0 | 40000 | 0 | 19708 | 3320.25 | 0 | 0 | 3320.25 | 0 | 0 | 0 | 0
2022061201 | 1 | 0.69997 | 55997.6 | 0 | 0 | 0.66467 | 23263.45 | 0 | 0 | 40000 | 0 | 15997.6 | 7265.85 | 0 | 0 | 7265.85 | 0 | 0 | 0 | 0
2022061202 | 1 | 0.6633 | 53064 | 0 | 0 | 0.67214 | 23524.9 | 0 | 0 | 40000 | 0 | 13064 | 10460.9 | 0 | 0 | 10460.9 | 0 | 0 | 0 | 0
2022061203 | 1 | 0.63699 | 50959.2 | 0 | 0 | 0.67212 | 23524.2 | 0 | 0 | 40000 | 0 | 10959.2 | 12565 | 0 | 0 | 12565 | 0 | 0 | 0 | 0
2022061204 | 1 | 0.61334 | 49067.2 | 0 | 0 | 0.66427 | 23249.45 | 0 | 0 | 40000 | 0 | 9067.2 | 14182.25 | 0 | 0 | 14182.25 | 0 | 0 | 0 | 0
2022061205 | 1 | 0.59741 | 47792.8 | 0 | 0 | 0.66021 | 23107.35 | 0 | 0 | 40000 | 0 | 7792.8 | 15314.55 | 0 | 0 | 15314.55 | 0 | 0 | 0 | 0
2022061206 | 1 | 0.59121 | 47296.8 | 0 | 0 | 0.65604 | 22961.4 | 0 | 0 | 40000 | 0 | 7296.8 | 15664.6 | 0 | 0 | 15664.6 | 0 | 0 | 0 | 0
2022061207 | 1 | 0.57816 | 46252.8 | 0 | 0 | 0.63548 | 22241.8 | 0.00427 | 59.78 | 40000 | 0 | 6252.8 | 15989 | 0 | 59.78 | 16048.78 | 0 | 0 | 0 | 0
2022061208 | 1 | 0.58308 | 46646.4 | 0 | 0 | 0.59548 | 20841.8 | 0.19269 | 2697.66 | 40000 | 0 | 6646.4 | 14195.4 | 0 | 2697.66 | 16893.06 | 0 | 0 | 0 | 0
2022061209 | 1 | 0.6253 | 50024 | 0 | 0 | 0.57475 | 20116.25 | 0.51836 | 7257.04 | 40000 | 0 | 10024 | 10092.25 | 0 | 7257.04 | 17349.29 | 0 | 0 | 0 | 0
2022061210 | 1 | 0.67872 | 54297.6 | 0 | 0 | 0.60541 | 21189.35 | 0.56238 | 7873.32 | 40000 | 0 | 14297.6 | 6891.75 | 0 | 7873.32 | 14765.07 | 0 | 0 | 0 | 0
2022061211 | 1 | 0.7339 | 58712 | 0 | 0 | 0.60546 | 21191.1 | 0.58717 | 8220.38 | 40000 | 0 | 18712 | 2479.1 | 0 | 8220.38 | 10699.48 | 0 | 0 | 0 | 0
2022061212 | 1 | 0.78953 | 63162.4 | 0 | 0 | 0.5826 | 20391 | 0.68363 | 9570.82 | 40000 | 0 | 20391 | 0 | 2771.4 | 6799.42 | 6799.42 | 0 | 0 | 0 | 0
2022061213 | 1 | 0.84121 | 67296.8 | 0 | 0 | 0.55729 | 19505.15 | 0.75893 | 10625.02 | 40000 | 0 | 19505.15 | 0 | 7791.65 | 2833.37 | 2833.37 | 0 | 0 | 0 | 0
2022061214 | 1 | 0.88168 | 70534.4 | 0 | 0 | 0.55407 | 19392.45 | 0.76895 | 10765.3 | 40000 | 0 | 19392.45 | 0 | 10765.3 | 0 | 0 | 376.65 | 0 | 0 | 376.65
2022061215 | 1 | 0.91355 | 73084 | 0 | 0 | 0.55073 | 19275.55 | 0.74147 | 10380.58 | 40000 | 0 | 19275.55 | 0 | 10380.58 | 0 | 0 | 3427.87 | 0 | 0 | 3427.87
2022061216 | 1 | 0.9274 | 74192 | 0 | 0 | 0.55173 | 19310.55 | 0.74571 | 10439.94 | 40000 | 0 | 19310.55 | 0 | 10439.94 | 0 | 0 | 4441.51 | 0 | 0 | 4441.51
2022061217 | 1 | 0.93516 | 74812.8 | 0 | 0 | 0.54131 | 18945.85 | 0.74577 | 10440.78 | 40000 | 0 | 18945.85 | 0 | 10440.78 | 0 | 0 | 5426.17 | 0 | 0 | 5426.17
2022061218 | 1 | 0.9384 | 75072 | 0 | 0 | 0.54494 | 19072.9 | 0.70936 | 9931.04 | 40000 | 0 | 19072.9 | 0 | 9931.04 | 0 | 0 | 6068.06 | 0 | 0 | 6068.06
2022061219 | 1 | 0.93206 | 74564.8 | 0 | 0 | 0.54369 | 19029.15 | 0.61714 | 8639.96 | 40000 | 0 | 19029.15 | 0 | 8639.96 | 0 | 0 | 6895.69 | 0 | 0 | 6895.69
2022061220 | 1 | 0.91044 | 72835.2 | 0 | 0 | 0.5449 | 19071.5 | 0.36081 | 5051.34 | 40000 | 0 | 19071.5 | 0 | 5051.34 | 0 | 0 | 8712.36 | 0 | 0 | 8712.36
2022061221 | 1 | 0.87081 | 69664.8 | 0 | 0 | 0.55587 | 19455.45 | 0.04272 | 598.08 | 40000 | 0 | 19455.45 | 0 | 598.08 | 0 | 0 | 9611.27 | 0 | 0 | 9611.27
2022061222 | 1 | 0.8434 | 67472 | 0 | 0 | 0.60703 | 21246.05 | 0 | 0 | 40000 | 0 | 21246.05 | 0 | 0 | 0 | 0 | 6225.95 | 0 | 0 | 6225.95
2022061223 | 1 | 0.79732 | 63785.6 | 0 | 0 | 0.65565 | 22947.75 | 0 | 0 | 40000 | 0 | 22947.75 | 0 | 0 | 0 | 0 | 837.85 | 0 | 0 | 837.85
2022061224 | 1 | 0.74541 | 59632.8 | 0 | 0 | 0.6805 | 23817.5 | 0 | 0 | 40000 | 0 | 19632.8 | 4184.7 | 0 | 0 | 4184.7 | 0 | 0 | 0 | 0
2022061301 | 2 | 0.698 | 55840 | 0 | 0 | 0.69144 | 24200.4 | 0 | 0 | 40000 | 0 | 15840 | 8360.4 | 0 | 0 | 8360.4 | 0 | 0 | 0 | 0
2022061302 | 2 | 0.66406 | 53124.8 | 0 | 0 | 0.69441 | 24304.35 | 0 | 0 | 40000 | 0 | 13124.8 | 11179.55 | 0 | 0 | 11179.55 | 0 | 0 | 0 | 0
2022061303 | 2 | 0.63891 | 51112.8 | 0 | 0 | 0.6997 | 24489.5 | 0 | 0 | 40000 | 0 | 11112.8 | 13376.7 | 0 | 0 | 13376.7 | 0 | 0 | 0 | 0
2022061304 | 2 | 0.62298 | 49838.4 | 0 | 0 | 0.69383 | 24284.05 | 0 | 0 | 40000 | 0 | 9838.4 | 14445.65 | 0 | 0 | 14445.65 | 0 | 0 | 0 | 0
2022061305 | 2 | 0.61564 | 49251.2 | 0 | 0 | 0.6783 | 23740.5 | 0 | 0 | 40000 | 0 | 9251.2 | 14489.3 | 0 | 0 | 14489.3 | 0 | 0 | 0 | 0
2022061306 | 2 | 0.62125 | 49700 | 0 | 0 | 0.65972 | 23090.2 | 0 | 0 | 40000 | 0 | 9700 | 13390.2 | 0 | 0 | 13390.2 | 0 | 0 | 0 | 0
2022061307 | 2 | 0.63061 | 50448.8 | 0 | 0 | 0.64197 | 22468.95 | 0.00516 | 72.24 | 40000 | 0 | 10448.8 | 12020.15 | 0 | 72.24 | 12092.39 | 0 | 0 | 0 | 0
2022061308 | 2 | 0.64748 | 51798.4 | 0 | 0 | 0.62501 | 21875.35 | 0.16896 | 2365.44 | 40000 | 0 | 11798.4 | 10076.95 | 0 | 2365.44 | 12442.39 | 0 | 0 | 0 | 0
2022061309 | 2 | 0.68129 | 54503.2 | 0 | 0 | 0.62615 | 21915.25 | 0.33477 | 4686.78 | 40000 | 0 | 14503.2 | 7412.05 | 0 | 4686.78 | 12098.83 | 0 | 0 | 0 | 0
2022061310 | 2 | 0.72761 | 58208.8 | 0 | 0 | 0.66495 | 23273.25 | 0.40203 | 5628.42 | 40000 | 0 | 18208.8 | 5064.45 | 0 | 5628.42 | 10692.87 | 0 | 0 | 0 | 0
2022061311 | 2 | 0.77683 | 62146.4 | 0 | 0 | 0.68064 | 23822.4 | 0.43255 | 6055.7 | 40000 | 0 | 22146.4 | 1676 | 0 | 6055.7 | 7731.7 | 0 | 0 | 0 | 0
2022061312 | 2 | 0.8262 | 66096 | 0 | 0 | 0.69552 | 24343.2 | 0.43638 | 6109.32 | 40000 | 0 | 24343.2 | 0 | 1752.8 | 4356.52 | 4356.52 | 0 | 0 | 0 | 0
2022061313 | 2 | 0.86721 | 69376.8 | 0 | 0 | 0.69485 | 24319.75 | 0.46342 | 6487.88 | 40000 | 0 | 24319.75 | 0 | 5057.05 | 1430.83 | 1430.83 | 0 | 0 | 0 | 0
2022061314 | 2 | 0.90192 | 72153.6 | 0 | 0 | 0.69084 | 24179.4 | 0.49065 | 6869.1 | 40000 | 0 | 24179.4 | 0 | 6869.1 | 0 | 0 | 1105.1 | 0 | 0 | 1105.1
2022061315 | 2 | 0.92793 | 74234.4 | 0 | 0 | 0.69281 | 24248.35 | 0.49649 | 6950.86 | 40000 | 0 | 24248.35 | 0 | 6950.86 | 0 | 0 | 3035.19 | 0 | 0 | 3035.19
2022061316 | 2 | 0.93047 | 74437.6 | 0 | 0 | 0.6893 | 24125.5 | 0.49217 | 6890.38 | 40000 | 0 | 24125.5 | 0 | 6890.38 | 0 | 0 | 3421.72 | 0 | 0 | 3421.72
2022061317 | 2 | 0.93355 | 74684 | 0 | 0 | 0.67742 | 23709.7 | 0.50965 | 7135.1 | 40000 | 0 | 23709.7 | 0 | 7135.1 | 0 | 0 | 3839.2 | 0 | 0 | 3839.2
2022061318 | 2 | 0.93235 | 74588 | 0 | 0 | 0.67268 | 23543.8 | 0.49077 | 6870.78 | 40000 | 0 | 23543.8 | 0 | 6870.78 | 0 | 0 | 4173.42 | 0 | 0 | 4173.42
2022061319 | 2 | 0.91882 | 73505.6 | 0 | 0 | 0.67221 | 23527.35 | 0.41171 | 5763.94 | 40000 | 0 | 23527.35 | 0 | 5763.94 | 0 | 0 | 4214.31 | 0 | 0 | 4214.31
2022061320 | 2 | 0.89424 | 71539.2 | 0 | 0 | 0.67784 | 23724.4 | 0.26231 | 3672.34 | 40000 | 0 | 23724.4 | 0 | 3672.34 | 0 | 0 | 4142.46 | 0 | 0 | 4142.46
2022061321 | 2 | 0.8559 | 68472 | 0 | 0 | 0.68762 | 24066.7 | 0.04541 | 635.74 | 40000 | 0 | 24066.7 | 0 | 635.74 | 0 | 0 | 3769.56 | 0 | 0 | 3769.56
2022061322 | 2 | 0.83278 | 66622.4 | 0 | 0 | 0.70163 | 24557.05 | 0.007 | 98 | 40000 | 0 | 24557.05 | 0 | 98 | 0 | 0 | 1967.35 | 0 | 0 | 1967.35
2022061323 | 2 | 0.78427 | 62741.6 | 0 | 0 | 0.71906 | 25167.1 | 0 | 0 | 40000 | 0 | 22741.6 | 2425.5 | 0 | 0 | 2425.5 | 0 | 0 | 0 | 0
2022061324 | 2 | 0.73346 | 58676.8 | 0 | 0 | 0.72338 | 25318.3 | 7e-05 | 0.98 | 40000 | 0 | 18676.8 | 6641.5 | 0 | 0.98 | 6642.48 | 0 | 0 | 0 | 0
2022061401 | 3 | 0.68976 | 55180.8 | 0 | 0 | 0.72995 | 25548.25 | 8e-05 | 1.12 | 40000 | 0 | 15180.8 | 10367.45 | 0 | 1.12 | 10368.57 | 0 | 0 | 0 | 0
2022061402 | 3 | 0.658 | 52640 | 0 | 0 | 0.72375 | 25331.25 | 8e-05 | 1.12 | 40000 | 0 | 12640 | 12691.25 | 0 | 1.12 | 12692.37 | 0 | 0 | 0 | 0
2022061403 | 3 | 0.63456 | 50764.8 | 0 | 0 | 0.71508 | 25027.8 | 8e-05 | 1.12 | 40000 | 0 | 10764.8 | 14263 | 0 | 1.12 | 14264.12 | 0 | 0 | 0 | 0
2022061404 | 3 | 0.61866 | 49492.8 | 0 | 0 | 0.70448 | 24656.8 | 8e-05 | 1.12 | 40000 | 0 | 9492.8 | 15164 | 0 | 1.12 | 15165.12 | 0 | 0 | 0 | 0
2022061405 | 3 | 0.61629 | 49303.2 | 0 | 0 | 0.7039 | 24636.5 | 9e-05 | 1.26 | 40000 | 0 | 9303.2 | 15333.3 | 0 | 1.26 | 15334.56 | 0 | 0 | 0 | 0
2022061406 | 3 | 0.62094 | 49675.2 | 0 | 0 | 0.69592 | 24357.2 | 9e-05 | 1.26 | 40000 | 0 | 9675.2 | 14682 | 0 | 1.26 | 14683.26 | 0 | 0 | 0 | 0
2022061407 | 3 | 0.62873 | 50298.4 | 0 | 0 | 0.68749 | 24062.15 | 0.00526 | 73.64 | 40000 | 0 | 10298.4 | 13763.75 | 0 | 73.64 | 13837.39 | 0 | 0 | 0 | 0
2022061408 | 3 | 0.64441 | 51552.8 | 0 | 0 | 0.67534 | 23636.9 | 0.10581 | 1481.34 | 40000 | 0 | 11552.8 | 12084.1 | 0 | 1481.34 | 13565.44 | 0 | 0 | 0 | 0
2022061409 | 3 | 0.67493 | 53994.4 | 0 | 0 | 0.67053 | 23468.55 | 0.26095 | 3653.3 | 40000 | 0 | 13994.4 | 9474.15 | 0 | 3653.3 | 13127.45 | 0 | 0 | 0 | 0
2022061410 | 3 | 0.71574 | 57259.2 | 0 | 0 | 0.68203 | 23871.05 | 0.37241 | 5213.74 | 40000 | 0 | 17259.2 | 6611.85 | 0 | 5213.74 | 11825.59 | 0 | 0 | 0 | 0
2022061411 | 3 | 0.75761 | 60608.8 | 0 | 0 | 0.6779 | 23726.5 | 0.44543 | 6236.02 | 40000 | 0 | 20608.8 | 3117.7 | 0 | 6236.02 | 9353.72 | 0 | 0 | 0 | 0
2022061412 | 3 | 0.79983 | 63986.4 | 0 | 0 | 0.66864 | 23402.4 | 0.50619 | 7086.66 | 40000 | 0 | 23402.4 | 0 | 584 | 6502.66 | 6502.66 | 0 | 0 | 0 | 0
2022061413 | 3 | 0.83955 | 67164 | 0 | 0 | 0.64623 | 22618.05 | 0.58259 | 8156.26 | 40000 | 0 | 22618.05 | 0 | 4545.95 | 3610.31 | 3610.31 | 0 | 0 | 0 | 0
2022061414 | 3 | 0.87226 | 69780.8 | 0 | 0 | 0.59823 | 20938.05 | 0.72279 | 10119.06 | 40000 | 0 | 20938.05 | 0 | 8842.75 | 1276.31 | 1276.31 | 0 | 0 | 0 | 0
2022061415 | 3 | 0.89705 | 71764 | 0 | 0 | 0.57365 | 20077.75 | 0.77779 | 10889.06 | 40000 | 0 | 20077.75 | 0 | 10889.06 | 0 | 0 | 797.19 | 0 | 0 | 797.19
2022061416 | 3 | 0.91219 | 72975.2 | 0 | 0 | 0.57753 | 20213.55 | 0.76518 | 10712.52 | 40000 | 0 | 20213.55 | 0 | 10712.52 | 0 | 0 | 2049.13 | 0 | 0 | 2049.13
2022061417 | 3 | 0.92137 | 73709.6 | 0 | 0 | 0.59997 | 20998.95 | 0.69827 | 9775.78 | 40000 | 0 | 20998.95 | 0 | 9775.78 | 0 | 0 | 2934.87 | 0 | 0 | 2934.87
2022061418 | 3 | 0.91689 | 73351.2 | 0 | 0 | 0.63494 | 22222.9 | 0.55529 | 7774.06 | 40000 | 0 | 22222.9 | 0 | 7774.06 | 0 | 0 | 3354.24 | 0 | 0 | 3354.24
2022061419 | 3 | 0.89447 | 71557.6 | 0 | 0 | 0.67191 | 23516.85 | 0.346 | 4844 | 40000 | 0 | 23516.85 | 0 | 4844 | 0 | 0 | 3196.75 | 0 | 0 | 3196.75
2022061420 | 3 | 0.86091 | 68872.8 | 0 | 0 | 0.70948 | 24831.8 | 0.13582 | 1901.48 | 40000 | 0 | 24831.8 | 0 | 1901.48 | 0 | 0 | 2139.52 | 0 | 0 | 2139.52
2022061421 | 3 | 0.83179 | 66543.2 | 0 | 0 | 0.7142 | 24997 | 0.0153 | 214.2 | 40000 | 0 | 24997 | 0 | 214.2 | 0 | 0 | 1332 | 0 | 0 | 1332
2022061422 | 3 | 0.80652 | 64521.6 | 0 | 0 | 0.68093 | 23832.55 | 0 | 0 | 40000 | 0 | 23832.55 | 0 | 0 | 0 | 0 | 689.05 | 0 | 0 | 689.05
2022061423 | 3 | 0.76232 | 60985.6 | 0 | 0 | 0.67695 | 23693.25 | 0 | 0 | 40000 | 0 | 20985.6 | 2707.65 | 0 | 0 | 2707.65 | 0 | 0 | 0 | 0
2022061424 | 3 | 0.71574 | 57259.2 | 0 | 0 | 0.70144 | 24550.4 | 7e-05 | 0.98 | 40000 | 0 | 17259.2 | 7291.2 | 0 | 0.98 | 7292.18 | 0 | 0 | 0 | 0
2022061501 | 4 | 0.67544 | 54035.2 | 0 | 0 | 0.71874 | 25155.9 | 8e-05 | 1.12 | 40000 | 0 | 14035.2 | 11120.7 | 0 | 1.12 | 11121.82 | 0 | 0 | 0 | 0
2022061502 | 4 | 0.64579 | 51663.2 | 0 | 0 | 0.71608 | 25062.8 | 9e-05 | 1.26 | 40000 | 0 | 11663.2 | 13399.6 | 0 | 1.26 | 13400.86 | 0 | 0 | 0 | 0
2022061503 | 4 | 0.62697 | 50157.6 | 0 | 0 | 0.70698 | 24744.3 | 9e-05 | 1.26 | 40000 | 0 | 10157.6 | 14586.7 | 0 | 1.26 | 14587.96 | 0 | 0 | 0 | 0
2022061504 | 4 | 0.61458 | 49166.4 | 0 | 0 | 0.70357 | 24624.95 | 0.0001 | 1.4 | 40000 | 0 | 9166.4 | 15458.55 | 0 | 1.4 | 15459.95 | 0 | 0 | 0 | 0
2022061505 | 4 | 0.60903 | 48722.4 | 0 | 0 | 0.69293 | 24252.55 | 0.0001 | 1.4 | 40000 | 0 | 8722.4 | 15530.15 | 0 | 1.4 | 15531.55 | 0 | 0 | 0 | 0
2022061506 | 4 | 0.6164 | 49312 | 0 | 0 | 0.67388 | 23585.8 | 0.0001 | 1.4 | 40000 | 0 | 9312 | 14273.8 | 0 | 1.4 | 14275.2 | 0 | 0 | 0 | 0
2022061507 | 4 | 0.63098 | 50478.4 | 0 | 0 | 0.66627 | 23319.45 | 0.00648 | 90.72 | 40000 | 0 | 10478.4 | 12841.05 | 0 | 90.72 | 12931.77 | 0 | 0 | 0 | 0
2022061508 | 4 | 0.64729 | 51783.2 | 0 | 0 | 0.65986 | 23095.1 | 0.10196 | 1427.44 | 40000 | 0 | 11783.2 | 11311.9 | 0 | 1427.44 | 12739.34 | 0 | 0 | 0 | 0
2022061509 | 4 | 0.67376 | 53900.8 | 0 | 0 | 0.64918 | 22721.3 | 0.24789 | 3470.46 | 40000 | 0 | 13900.8 | 8820.5 | 0 | 3470.46 | 12290.96 | 0 | 0 | 0 | 0
2022061510 | 4 | 0.71101 | 56880.8 | 0 | 0 | 0.66879 | 23407.65 | 0.31832 | 4456.48 | 40000 | 0 | 16880.8 | 6526.85 | 0 | 4456.48 | 10983.33 | 0 | 0 | 0 | 0
2022061511 | 4 | 0.75178 | 60142.4 | 0 | 0 | 0.652 | 22820 | 0.41215 | 5770.1 | 40000 | 0 | 20142.4 | 2677.6 | 0 | 5770.1 | 8447.7 | 0 | 0 | 0 | 0
2022061512 | 4 | 0.78879 | 63103.2 | 0 | 0 | 0.64431 | 22550.85 | 0.47136 | 6599.04 | 40000 | 0 | 22550.85 | 0 | 552.35 | 6046.69 | 6046.69 | 0 | 0 | 0 | 0
2022061513 | 4 | 0.82477 | 65981.6 | 0 | 0 | 0.62319 | 21811.65 | 0.53055 | 7427.7 | 40000 | 0 | 21811.65 | 0 | 4169.95 | 3257.75 | 3257.75 | 0 | 0 | 0 | 0
2022061514 | 4 | 0.8583 | 68664 | 0 | 0 | 0.59429 | 20800.15 | 0.60295 | 8441.3 | 40000 | 0 | 20800.15 | 0 | 7863.85 | 577.45 | 577.45 | 0 | 0 | 0 | 0
2022061515 | 4 | 0.88437 | 70749.6 | 0 | 0 | 0.57816 | 20235.6 | 0.66782 | 9349.48 | 40000 | 0 | 20235.6 | 0 | 9349.48 | 0 | 0 | 1164.52 | 0 | 0 | 1164.52
2022061516 | 4 | 0.89887 | 71909.6 | 0 | 0 | 0.57044 | 19965.4 | 0.69777 | 9768.78 | 40000 | 0 | 19965.4 | 0 | 9768.78 | 0 | 0 | 2175.42 | 0 | 0 | 2175.42
2022061517 | 4 | 0.9096 | 72768 | 0 | 0 | 0.55631 | 19470.85 | 0.68206 | 9548.84 | 40000 | 0 | 19470.85 | 0 | 9548.84 | 0 | 0 | 3748.31 | 0 | 0 | 3748.31
2022061518 | 4 | 0.91023 | 72818.4 | 0 | 0 | 0.56591 | 19806.85 | 0.67445 | 9442.3 | 40000 | 0 | 19806.85 | 0 | 9442.3 | 0 | 0 | 3569.25 | 0 | 0 | 3569.25
2022061519 | 4 | 0.89797 | 71837.6 | 0 | 0 | 0.58786 | 20575.1 | 0.58491 | 8188.74 | 40000 | 0 | 20575.1 | 0 | 8188.74 | 0 | 0 | 3073.76 | 0 | 0 | 3073.76
2022061520 | 4 | 0.87021 | 69616.8 | 0 | 0 | 0.60434 | 21151.9 | 0.33002 | 4620.28 | 40000 | 0 | 21151.9 | 0 | 4620.28 | 0 | 0 | 3844.62 | 0 | 0 | 3844.62
2022061521 | 4 | 0.83715 | 66972 | 0 | 0 | 0.61804 | 21631.4 | 0.04842 | 677.88 | 40000 | 0 | 21631.4 | 0 | 677.88 | 0 | 0 | 4662.72 | 0 | 0 | 4662.72
2022061522 | 4 | 0.81248 | 64998.4 | 0 | 0 | 0.62914 | 22019.9 | 0 | 0 | 40000 | 0 | 22019.9 | 0 | 0 | 0 | 0 | 2978.5 | 0 | 0 | 2978.5
2022061523 | 4 | 0.76896 | 61516.8 | 0 | 0 | 0.6574 | 23009 | 5e-05 | 0.7 | 40000 | 0 | 21516.8 | 1492.2 | 0 | 0.7 | 1492.9 | 0 | 0 | 0 | 0
2022061524 | 4 | 0.71976 | 57580.8 | 0 | 0 | 0.66766 | 23368.1 | 6e-05 | 0.84 | 40000 | 0 | 17580.8 | 5787.3 | 0 | 0.84 | 5788.14 | 0 | 0 | 0 | 0
2022061601 | 5 | 0.67557 | 54045.6 | 0 | 0 | 0.65927 | 23074.45 | 6e-05 | 0.84 | 40000 | 0 | 14045.6 | 9028.85 | 0 | 0.84 | 9029.69 | 0 | 0 | 0 | 0
2022061602 | 5 | 0.64291 | 51432.8 | 0 | 0 | 0.63681 | 22288.35 | 6e-05 | 0.84 | 40000 | 0 | 11432.8 | 10855.55 | 0 | 0.84 | 10856.39 | 0 | 0 | 0 | 0
2022061603 | 5 | 0.61808 | 49446.4 | 0 | 0 | 0.60886 | 21310.1 | 6e-05 | 0.84 | 40000 | 0 | 9446.4 | 11863.7 | 0 | 0.84 | 11864.54 | 0 | 0 | 0 | 0
2022061604 | 5 | 0.60212 | 48169.6 | 0 | 0 | 0.58671 | 20534.85 | 0.00027 | 3.78 | 40000 | 0 | 8169.6 | 12365.25 | 0 | 3.78 | 12369.03 | 0 | 0 | 0 | 0
2022061605 | 5 | 0.59578 | 47662.4 | 0 | 0 | 0.55279 | 19347.65 | 6e-05 | 0.84 | 40000 | 0 | 7662.4 | 11685.25 | 0 | 0.84 | 11686.09 | 0 | 0 | 0 | 0
2022061606 | 5 | 0.59924 | 47939.2 | 0 | 0 | 0.50539 | 17688.65 | 6e-05 | 0.84 | 40000 | 0 | 7939.2 | 9749.45 | 0 | 0.84 | 9750.29 | 0 | 0 | 0 | 0
2022061607 | 5 | 0.61098 | 48878.4 | 0 | 0 | 0.47057 | 16469.95 | 0.00821 | 114.94 | 40000 | 0 | 8878.4 | 7591.55 | 0 | 114.94 | 7706.49 | 0 | 0 | 0 | 0
2022061608 | 5 | 0.62357 | 49885.6 | 0 | 0 | 0.41775 | 14621.25 | 0.17749 | 2484.86 | 40000 | 0 | 9885.6 | 4735.65 | 0 | 2484.86 | 7220.51 | 0 | 0 | 0 | 0
2022061609 | 5 | 0.65858 | 52686.4 | 0 | 0 | 0.42224 | 14778.4 | 0.5442 | 7618.8 | 40000 | 0 | 12686.4 | 2092 | 0 | 7618.8 | 9710.8 | 0 | 0 | 0 | 0
2022061610 | 5 | 0.70231 | 56184.8 | 0 | 0 | 0.46762 | 16366.7 | 0.61696 | 8637.44 | 40000 | 0 | 16184.8 | 181.9 | 0 | 8637.44 | 8819.34 | 0 | 0 | 0 | 0
2022061611 | 5 | 0.75183 | 60146.4 | 0 | 0 | 0.43166 | 15108.1 | 0.72032 | 10084.48 | 40000 | 0 | 15108.1 | 0 | 5038.3 | 5046.18 | 5046.18 | 0 | 0 | 0 | 0
2022061612 | 5 | 0.80105 | 64084 | 0 | 0 | 0.4015 | 14052.5 | 0.79695 | 11157.3 | 40000 | 0 | 14052.5 | 0 | 10031.5 | 1125.8 | 1125.8 | 0 | 0 | 0 | 0
2022061613 | 5 | 0.84706 | 67764.8 | 0 | 0 | 0.40675 | 14236.25 | 0.79396 | 11115.44 | 40000 | 0 | 14236.25 | 0 | 11115.44 | 0 | 0 | 2413.11 | 0 | 0 | 2413.11
2022061614 | 5 | 0.89179 | 71343.2 | 0 | 0 | 0.42297 | 14803.95 | 0.79278 | 11098.92 | 40000 | 0 | 14803.95 | 0 | 11098.92 | 0 | 0 | 5440.33 | 0 | 0 | 5440.33
2022061615 | 5 | 0.92365 | 73892 | 0 | 0 | 0.44293 | 15502.55 | 0.79943 | 11192.02 | 40000 | 0 | 15502.55 | 0 | 11192.02 | 0 | 0 | 7197.43 | 0 | 0 | 7197.43
2022061616 | 5 | 0.93717 | 74973.6 | 0 | 0 | 0.47932 | 16776.2 | 0.75698 | 10597.72 | 40000 | 0 | 16776.2 | 0 | 10597.72 | 0 | 0 | 7599.68 | 0 | 0 | 7599.68
2022061617 | 5 | 0.94107 | 75285.6 | 0 | 0 | 0.49811 | 17433.85 | 0.72826 | 10195.64 | 40000 | 0 | 17433.85 | 0 | 10195.64 | 0 | 0 | 7656.11 | 0 | 0 | 7656.11
2022061618 | 5 | 0.93802 | 75041.6 | 0 | 0 | 0.50032 | 17511.2 | 0.70002 | 9800.28 | 40000 | 0 | 17511.2 | 0 | 9800.28 | 0 | 0 | 7730.12 | 0 | 0 | 7730.12
2022061619 | 5 | 0.92927 | 74341.6 | 0 | 0 | 0.49751 | 17412.85 | 0.62001 | 8680.14 | 40000 | 0 | 17412.85 | 0 | 8680.14 | 0 | 0 | 8248.61 | 0 | 0 | 8248.61
2022061620 | 5 | 0.89984 | 71987.2 | 0 | 0 | 0.49352 | 17273.2 | 0.32552 | 4557.28 | 40000 | 0 | 17273.2 | 0 | 4557.28 | 0 | 0 | 10156.72 | 0 | 0 | 10156.72
2022061621 | 5 | 0.8612 | 68896 | 0 | 0 | 0.47394 | 16587.9 | 0.03837 | 537.18 | 40000 | 0 | 16587.9 | 0 | 537.18 | 0 | 0 | 11770.92 | 0 | 0 | 11770.92
2022061622 | 5 | 0.82733 | 66186.4 | 0 | 0 | 0.49895 | 17463.25 | 0 | 0 | 40000 | 0 | 17463.25 | 0 | 0 | 0 | 0 | 8723.15 | 0 | 0 | 8723.15
2022061623 | 5 | 0.77718 | 62174.4 | 0 | 0 | 0.56565 | 19797.75 | 6e-05 | 0.84 | 40000 | 0 | 19797.75 | 0 | 0.84 | 0 | 0 | 2375.81 | 0 | 0 | 2375.81
2022061624 | 5 | 0.72295 | 57836 | 0 | 0 | 0.59138 | 20698.3 | 5e-05 | 0.7 | 40000 | 0 | 17836 | 2862.3 | 0 | 0.7 | 2863 | 0 | 0 | 0 | 0
2022061701 | 6 | 0.67457 | 53965.6 | 0 | 0 | 0.57964 | 20287.4 | 8e-05 | 1.12 | 40000 | 0 | 13965.6 | 6321.8 | 0 | 1.12 | 6322.92 | 0 | 0 | 0 | 0
2022061702 | 6 | 0.63442 | 50753.6 | 0 | 0 | 0.55962 | 19586.7 | 8e-05 | 1.12 | 40000 | 0 | 10753.6 | 8833.1 | 0 | 1.12 | 8834.22 | 0 | 0 | 0 | 0
2022061703 | 6 | 0.60666 | 48532.8 | 0 | 0 | 0.53768 | 18818.8 | 8e-05 | 1.12 | 40000 | 0 | 8532.8 | 10286 | 0 | 1.12 | 10287.12 | 0 | 0 | 0 | 0
2022061704 | 6 | 0.58559 | 46847.2 | 0 | 0 | 0.49762 | 17416.7 | 8e-05 | 1.12 | 40000 | 0 | 6847.2 | 10569.5 | 0 | 1.12 | 10570.62 | 0 | 0 | 0 | 0
2022061705 | 6 | 0.57502 | 46001.6 | 0 | 0 | 0.43863 | 15352.05 | 7e-05 | 0.98 | 40000 | 0 | 6001.6 | 9350.45 | 0 | 0.98 | 9351.43 | 0 | 0 | 0 | 0
2022061706 | 6 | 0.57764 | 46211.2 | 0 | 0 | 0.39999 | 13999.65 | 0.00011 | 1.54 | 40000 | 0 | 6211.2 | 7788.45 | 0 | 1.54 | 7789.99 | 0 | 0 | 0 | 0
2022061707 | 6 | 0.5839 | 46712 | 0 | 0 | 0.35864 | 12552.4 | 0.00458 | 64.12 | 40000 | 0 | 6712 | 5840.4 | 0 | 64.12 | 5904.52 | 0 | 0 | 0 | 0
2022061708 | 6 | 0.59854 | 47883.2 | 0 | 0 | 0.28973 | 10140.55 | 0.189 | 2646 | 40000 | 0 | 7883.2 | 2257.35 | 0 | 2646 | 4903.35 | 0 | 0 | 0 | 0
2022061709 | 6 | 0.63609 | 50887.2 | 0 | 0 | 0.20013 | 7004.55 | 0.57417 | 8038.38 | 40000 | 0 | 7004.55 | 0 | 3882.65 | 4155.73 | 4155.73 | 0 | 0 | 0 | 0
2022061710 | 6 | 0.68637 | 54909.6 | 0 | 0 | 0.22198 | 7769.3 | 0.73817 | 10334.38 | 40000 | 0 | 7769.3 | 0 | 7140.3 | 3194.08 | 3194.08 | 0 | 0 | 0 | 0
2022061711 | 6 | 0.74222 | 59377.6 | 0 | 0 | 0.24129 | 8445.15 | 0.79463 | 11124.82 | 40000 | 0 | 8445.15 | 0 | 10932.45 | 192.37 | 192.37 | 0 | 0 | 0 | 0
2022061712 | 6 | 0.79725 | 63780 | 0 | 0 | 0.21314 | 7459.9 | 0.81143 | 11360.02 | 40000 | 0 | 7459.9 | 0 | 11360.02 | 0 | 0 | 4960.08 | 0 | 0 | 4960.08
2022061713 | 6 | 0.84539 | 67631.2 | 0 | 0 | 0.18952 | 6633.2 | 0.8083 | 11316.2 | 40000 | 0 | 6633.2 | 0 | 11316.2 | 0 | 0 | 9681.8 | 0 | 0 | 9681.8
2022061714 | 6 | 0.88894 | 71115.2 | 0 | 0 | 0.21914 | 7669.9 | 0.78759 | 11026.26 | 40000 | 0 | 7669.9 | 0 | 11026.26 | 0 | 0 | 12419.04 | 0 | 0 | 12419.04
2022061715 | 6 | 0.91981 | 73584.8 | 0 | 0 | 0.26858 | 9400.3 | 0.78628 | 11007.92 | 40000 | 0 | 9400.3 | 0 | 11007.92 | 0 | 0 | 13176.58 | 0 | 0 | 13176.58
2022061716 | 6 | 0.93457 | 74765.6 | 0 | 0 | 0.31668 | 11083.8 | 0.74129 | 10378.06 | 40000 | 0 | 11083.8 | 0 | 10378.06 | 0 | 0 | 13303.74 | 0 | 0 | 13303.74
2022061717 | 6 | 0.93705 | 74964 | 0 | 0 | 0.35726 | 12504.1 | 0.72221 | 10110.94 | 40000 | 0 | 12504.1 | 0 | 10110.94 | 0 | 0 | 12348.96 | 0 | 0 | 12348.96
2022061718 | 6 | 0.93406 | 74724.8 | 0 | 0 | 0.38758 | 13565.3 | 0.7077 | 9907.8 | 40000 | 0 | 13565.3 | 0 | 9907.8 | 0 | 0 | 11251.7 | 0 | 0 | 11251.7
2022061719 | 6 | 0.91584 | 73267.2 | 0 | 0 | 0.4068 | 14238 | 0.61964 | 8674.96 | 40000 | 0 | 14238 | 0 | 8674.96 | 0 | 0 | 10354.24 | 0 | 0 | 10354.24
2022061720 | 6 | 0.88371 | 70696.8 | 0 | 0 | 0.41858 | 14650.3 | 0.34733 | 4862.62 | 40000 | 0 | 14650.3 | 0 | 4862.62 | 0 | 0 | 11183.88 | 0 | 0 | 11183.88
2022061721 | 6 | 0.84584 | 67667.2 | 0 | 0 | 0.409 | 14315 | 0.04352 | 609.28 | 40000 | 0 | 14315 | 0 | 609.28 | 0 | 0 | 12742.92 | 0 | 0 | 12742.92
2022061722 | 6 | 0.81199 | 64959.2 | 0 | 0 | 0.43551 | 15242.85 | 5e-05 | 0.7 | 40000 | 0 | 15242.85 | 0 | 0.7 | 0 | 0 | 9715.65 | 0 | 0 | 9715.65
2022061723 | 6 | 0.76636 | 61308.8 | 0 | 0 | 0.49109 | 17188.15 | 8e-05 | 1.12 | 40000 | 0 | 17188.15 | 0 | 1.12 | 0 | 0 | 4119.53 | 0 | 0 | 4119.53
2022061724 | 6 | 0.71726 | 57380.8 | 0 | 0 | 0.49428 | 17299.8 | 0.00011 | 1.54 | 40000 | 0 | 17299.8 | 0 | 1.54 | 0 | 0 | 79.46 | 0 | 0 | 79.46
2022061801 | 7 | 0.66993 | 53594.4 | 0 | 0 | 0.46747 | 16361.45 | 0.00011 | 1.54 | 40000 | 0 | 13594.4 | 2767.05 | 0 | 1.54 | 2768.59 | 0 | 0 | 0 | 0
2022061802 | 7 | 0.63086 | 50468.8 | 0 | 0 | 0.43402 | 15190.7 | 0.00011 | 1.54 | 40000 | 0 | 10468.8 | 4721.9 | 0 | 1.54 | 4723.44 | 0 | 0 | 0 | 0
2022061803 | 7 | 0.59901 | 47920.8 | 0 | 0 | 0.40609 | 14213.15 | 0.00011 | 1.54 | 40000 | 0 | 7920.8 | 6292.35 | 0 | 1.54 | 6293.89 | 0 | 0 | 0 | 0
2022061804 | 7 | 0.57512 | 46009.6 | 0 | 0 | 0.36305 | 12706.75 | 0.0001 | 1.4 | 40000 | 0 | 6009.6 | 6697.15 | 0 | 1.4 | 6698.55 | 0 | 0 | 0 | 0
2022061805 | 7 | 0.55935 | 44748 | 0 | 0 | 0.32302 | 11305.7 | 0.0001 | 1.4 | 40000 | 0 | 4748 | 6557.7 | 0 | 1.4 | 6559.1 | 0 | 0 | 0 | 0
2022061806 | 7 | 0.55329 | 44263.2 | 0 | 0 | 0.2958 | 10353 | 0.0001 | 1.4 | 40000 | 0 | 4263.2 | 6089.8 | 0 | 1.4 | 6091.2 | 0 | 0 | 0 | 0
2022061807 | 7 | 0.54853 | 43882.4 | 0 | 0 | 0.25711 | 8998.85 | 0.00459 | 64.26 | 40000 | 0 | 3882.4 | 5116.45 | 0 | 64.26 | 5180.71 | 0 | 0 | 0 | 0
2022061808 | 7 | 0.56306 | 45044.8 | 0 | 0 | 0.20758 | 7265.3 | 0.19029 | 2664.06 | 40000 | 0 | 5044.8 | 2220.5 | 0 | 2664.06 | 4884.56 | 0 | 0 | 0 | 0
2022061809 | 7 | 0.60331 | 48264.8 | 0 | 0 | 0.14226 | 4979.1 | 0.58522 | 8193.08 | 40000 | 0 | 4979.1 | 0 | 3285.7 | 4907.38 | 4907.38 | 0 | 0 | 0 | 0
2022061810 | 7 | 0.65074 | 52059.2 | 0 | 0 | 0.15889 | 5561.15 | 0.74445 | 10422.3 | 40000 | 0 | 5561.15 | 0 | 6498.05 | 3924.25 | 3924.25 | 0 | 0 | 0 | 0
2022061811 | 7 | 0.70698 | 56558.4 | 0 | 0 | 0.15368 | 5378.8 | 0.79455 | 11123.7 | 40000 | 0 | 5378.8 | 0 | 11123.7 | 0 | 0 | 55.9 | 0 | 0 | 55.9
2022061812 | 7 | 0.76159 | 60927.2 | 0 | 0 | 0.15549 | 5442.15 | 0.80643 | 11290.02 | 40000 | 0 | 5442.15 | 0 | 11290.02 | 0 | 0 | 4195.03 | 0 | 0 | 4195.03
2022061813 | 7 | 0.80992 | 64793.6 | 0 | 0 | 0.20241 | 7084.35 | 0.79271 | 11097.94 | 40000 | 0 | 7084.35 | 0 | 11097.94 | 0 | 0 | 6611.31 | 0 | 0 | 6611.31
2022061814 | 7 | 0.84767 | 67813.6 | 0 | 0 | 0.24786 | 8675.1 | 0.79057 | 11067.98 | 40000 | 0 | 8675.1 | 0 | 11067.98 | 0 | 0 | 8070.52 | 0 | 0 | 8070.52
2022061815 | 7 | 0.87713 | 70170.4 | 0 | 0 | 0.29406 | 10292.1 | 0.77296 | 10821.44 | 40000 | 0 | 10292.1 | 0 | 10821.44 | 0 | 0 | 9056.86 | 0 | 0 | 9056.86
2022061816 | 7 | 0.89724 | 71779.2 | 0 | 0 | 0.32575 | 11401.25 | 0.76053 | 10647.42 | 40000 | 0 | 11401.25 | 0 | 10647.42 | 0 | 0 | 9730.53 | 0 | 0 | 9730.53
2022061817 | 7 | 0.90777 | 72621.6 | 0 | 0 | 0.36528 | 12784.8 | 0.72952 | 10213.28 | 40000 | 0 | 12784.8 | 0 | 10213.28 | 0 | 0 | 9623.52 | 0 | 0 | 9623.52
2022061818 | 7 | 0.90689 | 72551.2 | 0 | 0 | 0.39985 | 13994.75 | 0.69322 | 9705.08 | 40000 | 0 | 13994.75 | 0 | 9705.08 | 0 | 0 | 8851.37 | 0 | 0 | 8851.37
2022061819 | 7 | 0.89095 | 71276 | 0 | 0 | 0.43224 | 15128.4 | 0.62816 | 8794.24 | 40000 | 0 | 15128.4 | 0 | 8794.24 | 0 | 0 | 7353.36 | 0 | 0 | 7353.36
2022061820 | 7 | 0.86098 | 68878.4 | 0 | 0 | 0.44362 | 15526.7 | 0.36902 | 5166.28 | 40000 | 0 | 15526.7 | 0 | 5166.28 | 0 | 0 | 8185.42 | 0 | 0 | 8185.42
2022061821 | 7 | 0.82316 | 65852.8 | 0 | 0 | 0.43272 | 15145.2 | 0.05988 | 838.32 | 40000 | 0 | 15145.2 | 0 | 838.32 | 0 | 0 | 9869.28 | 0 | 0 | 9869.28
2022061822 | 7 | 0.79669 | 63735.2 | 0 | 0 | 0.44121 | 15442.35 | 0.00892 | 124.88 | 40000 | 0 | 15442.35 | 0 | 124.88 | 0 | 0 | 8167.97 | 0 | 0 | 8167.97
2022061823 | 7 | 0.75567 | 60453.6 | 0 | 0 | 0.49183 | 17214.05 | 0.00113 | 15.82 | 40000 | 0 | 17214.05 | 0 | 15.82 | 0 | 0 | 3223.73 | 0 | 0 | 3223.73
2022061824 | 7 | 0.71222 | 56977.6 | 0 | 0 | 0.52183 | 18264.05 | 0 | 0 | 40000 | 0 | 16977.6 | 1286.45 | 0 | 0 | 1286.45 | 0 | 0 | 0 | 0
2022061901 | 1 | 0.668 | 53440 | 0 | 0 | 0.51264 | 17942.4 | 0 | 0 | 40000 | 0 | 13440 | 4502.4 | 0 | 0 | 4502.4 | 0 | 0 | 0 | 0
2022061902 | 1 | 0.63116 | 50492.8 | 0 | 0 | 0.48828 | 17089.8 | 0 | 0 | 40000 | 0 | 10492.8 | 6597 | 0 | 0 | 6597 | 0 | 0 | 0 | 0
2022061903 | 1 | 0.60021 | 48016.8 | 0 | 0 | 0.44735 | 15657.25 | 0 | 0 | 40000 | 0 | 8016.8 | 7640.45 | 0 | 0 | 7640.45 | 0 | 0 | 0 | 0
2022061904 | 1 | 0.57962 | 46369.6 | 0 | 0 | 0.42373 | 14830.55 | 0 | 0 | 40000 | 0 | 6369.6 | 8460.95 | 0 | 0 | 8460.95 | 0 | 0 | 0 | 0
2022061905 | 1 | 0.56292 | 45033.6 | 0 | 0 | 0.39356 | 13774.6 | 0 | 0 | 40000 | 0 | 5033.6 | 8741 | 0 | 0 | 8741 | 0 | 0 | 0 | 0
2022061906 | 1 | 0.55403 | 44322.4 | 0 | 0 | 0.3674 | 12859 | 0 | 0 | 40000 | 0 | 4322.4 | 8536.6 | 0 | 0 | 8536.6 | 0 | 0 | 0 | 0
2022061907 | 1 | 0.54507 | 43605.6 | 0 | 0 | 0.3341 | 11693.5 | 0.00539 | 75.46 | 40000 | 0 | 3605.6 | 8087.9 | 0 | 75.46 | 8163.36 | 0 | 0 | 0 | 0
2022061908 | 1 | 0.55675 | 44540 | 0 | 0 | 0.25563 | 8947.05 | 0.22201 | 3108.14 | 40000 | 0 | 4540 | 4407.05 | 0 | 3108.14 | 7515.19 | 0 | 0 | 0 | 0
2022061909 | 1 | 0.59932 | 47945.6 | 0 | 0 | 0.20097 | 7033.95 | 0.62323 | 8725.22 | 40000 | 0 | 7033.95 | 0 | 911.65 | 7813.57 | 7813.57 | 0 | 0 | 0 | 0
2022061910 | 1 | 0.65763 | 52610.4 | 0 | 0 | 0.24159 | 8455.65 | 0.76815 | 10754.1 | 40000 | 0 | 8455.65 | 0 | 4154.75 | 6599.35 | 6599.35 | 0 | 0 | 0 | 0
2022061911 | 1 | 0.7165 | 57320 | 0 | 0 | 0.28343 | 9920.05 | 0.81248 | 11374.72 | 40000 | 0 | 9920.05 | 0 | 7399.95 | 3974.77 | 3974.77 | 0 | 0 | 0 | 0
2022061912 | 1 | 0.77425 | 61940 | 0 | 0 | 0.29554 | 10343.9 | 0.81531 | 11414.34 | 40000 | 0 | 10343.9 | 0 | 11414.34 | 0 | 0 | 181.76 | 0 | 0 | 181.76
2022061913 | 1 | 0.82218 | 65774.4 | 0 | 0 | 0.32162 | 11256.7 | 0.80655 | 11291.7 | 40000 | 0 | 11256.7 | 0 | 11291.7 | 0 | 0 | 3226 | 0 | 0 | 3226
2022061914 | 1 | 0.86072 | 68857.6 | 0 | 0 | 0.3572 | 12502 | 0.79495 | 11129.3 | 40000 | 0 | 12502 | 0 | 11129.3 | 0 | 0 | 5226.3 | 0 | 0 | 5226.3
2022061915 | 1 | 0.88819 | 71055.2 | 0 | 0 | 0.39544 | 13840.4 | 0.78809 | 11033.26 | 40000 | 0 | 13840.4 | 0 | 11033.26 | 0 | 0 | 6181.54 | 0 | 0 | 6181.54
2022061916 | 1 | 0.90707 | 72565.6 | 0 | 0 | 0.43454 | 15208.9 | 0.75207 | 10528.98 | 40000 | 0 | 15208.9 | 0 | 10528.98 | 0 | 0 | 6827.72 | 0 | 0 | 6827.72
2022061917 | 1 | 0.9203 | 73624 | 0 | 0 | 0.46768 | 16368.8 | 0.71829 | 10056.06 | 40000 | 0 | 16368.8 | 0 | 10056.06 | 0 | 0 | 7199.14 | 0 | 0 | 7199.14
2022061918 | 1 | 0.92448 | 73958.4 | 0 | 0 | 0.49298 | 17254.3 | 0.63619 | 8906.66 | 40000 | 0 | 17254.3 | 0 | 8906.66 | 0 | 0 | 7797.44 | 0 | 0 | 7797.44
2022061919 | 1 | 0.91113 | 72890.4 | 0 | 0 | 0.52543 | 18390.05 | 0.53903 | 7546.42 | 40000 | 0 | 18390.05 | 0 | 7546.42 | 0 | 0 | 6953.93 | 0 | 0 | 6953.93
2022061920 | 1 | 0.87733 | 70186.4 | 0 | 0 | 0.55004 | 19251.4 | 0.33603 | 4704.42 | 40000 | 0 | 19251.4 | 0 | 4704.42 | 0 | 0 | 6230.58 | 0 | 0 | 6230.58
2022061921 | 1 | 0.83477 | 66781.6 | 0 | 0 | 0.51086 | 17880.1 | 0.04619 | 646.66 | 40000 | 0 | 17880.1 | 0 | 646.66 | 0 | 0 | 8254.84 | 0 | 0 | 8254.84
2022061922 | 1 | 0.80484 | 64387.2 | 0 | 0 | 0.45241 | 15834.35 | 0 | 0 | 40000 | 0 | 15834.35 | 0 | 0 | 0 | 0 | 8552.85 | 0 | 0 | 8552.85
2022061923 | 1 | 0.75804 | 60643.2 | 0 | 0 | 0.45525 | 15933.75 | 7e-05 | 0.98 | 40000 | 0 | 15933.75 | 0 | 0.98 | 0 | 0 | 4708.47 | 0 | 0 | 4708.47
2022061924 | 1 | 0.70565 | 56452 | 0 | 0 | 0.47546 | 16641.1 | 0.0001 | 1.4 | 40000 | 0 | 16452 | 189.1 | 0 | 1.4 | 190.5 | 0 | 0 | 0 | 0
2022062001 | 2 | 0.65968 | 52774.4 | 0 | 0 | 0.49373 | 17280.55 | 0.0001 | 1.4 | 40000 | 0 | 12774.4 | 4506.15 | 0 | 1.4 | 4507.55 | 0 | 0 | 0 | 0
2022062002 | 2 | 0.62409 | 49927.2 | 0 | 0 | 0.50354 | 17623.9 | 0.0001 | 1.4 | 40000 | 0 | 9927.2 | 7696.7 | 0 | 1.4 | 7698.1 | 0 | 0 | 0 | 0
2022062003 | 2 | 0.59719 | 47775.2 | 0 | 0 | 0.49297 | 17253.95 | 0.0001 | 1.4 | 40000 | 0 | 7775.2 | 9478.75 | 0 | 1.4 | 9480.15 | 0 | 0 | 0 | 0
2022062004 | 2 | 0.58226 | 46580.8 | 0 | 0 | 0.47586 | 16655.1 | 0.0001 | 1.4 | 40000 | 0 | 6580.8 | 10074.3 | 0 | 1.4 | 10075.7 | 0 | 0 | 0 | 0
2022062005 | 2 | 0.57298 | 45838.4 | 0 | 0 | 0.42959 | 15035.65 | 0.0001 | 1.4 | 40000 | 0 | 5838.4 | 9197.25 | 0 | 1.4 | 9198.65 | 0 | 0 | 0 | 0
2022062006 | 2 | 0.5747 | 45976 | 0 | 0 | 0.36148 | 12651.8 | 0.0001 | 1.4 | 40000 | 0 | 5976 | 6675.8 | 0 | 1.4 | 6677.2 | 0 | 0 | 0 | 0
2022062007 | 2 | 0.58276 | 46620.8 | 0 | 0 | 0.30575 | 10701.25 | 0.00583 | 81.62 | 40000 | 0 | 6620.8 | 4080.45 | 0 | 81.62 | 4162.07 | 0 | 0 | 0 | 0
2022062008 | 2 | 0.60244 | 48195.2 | 0 | 0 | 0.25078 | 8777.3 | 0.21976 | 3076.64 | 40000 | 0 | 8195.2 | 582.1 | 0 | 3076.64 | 3658.74 | 0 | 0 | 0 | 0
2022062009 | 2 | 0.64451 | 51560.8 | 0 | 0 | 0.21967 | 7688.45 | 0.61794 | 8651.16 | 40000 | 0 | 7688.45 | 0 | 3872.35 | 4778.81 | 4778.81 | 0 | 0 | 0 | 0
2022062010 | 2 | 0.69968 | 55974.4 | 0 | 0 | 0.28223 | 9878.05 | 0.76595 | 10723.3 | 40000 | 0 | 9878.05 | 0 | 6096.35 | 4626.95 | 4626.95 | 0 | 0 | 0 | 0
2022062011 | 2 | 0.76108 | 60886.4 | 0 | 0 | 0.36516 | 12780.6 | 0.79395 | 11115.3 | 40000 | 0 | 12780.6 | 0 | 8105.8 | 3009.5 | 3009.5 | 0 | 0 | 0 | 0
2022062012 | 2 | 0.82184 | 65747.2 | 0 | 0 | 0.42521 | 14882.35 | 0.72768 | 10187.52 | 40000 | 0 | 14882.35 | 0 | 10187.52 | 0 | 0 | 677.33 | 0 | 0 | 677.33
2022062013 | 2 | 0.8728 | 69824 | 0 | 0 | 0.45809 | 16033.15 | 0.69394 | 9715.16 | 40000 | 0 | 16033.15 | 0 | 9715.16 | 0 | 0 | 4075.69 | 0 | 0 | 4075.69
2022062014 | 2 | 0.91765 | 73412 | 0 | 0 | 0.4827 | 16894.5 | 0.70016 | 9802.24 | 40000 | 0 | 16894.5 | 0 | 9802.24 | 0 | 0 | 6715.26 | 0 | 0 | 6715.26
2022062015 | 2 | 0.94447 | 75557.6 | 0 | 0 | 0.48875 | 17106.25 | 0.73073 | 10230.22 | 40000 | 0 | 17106.25 | 0 | 10230.22 | 0 | 0 | 8221.13 | 0 | 0 | 8221.13
2022062016 | 2 | 0.95373 | 76298.4 | 0 | 0 | 0.46766 | 16368.1 | 0.73142 | 10239.88 | 40000 | 0 | 16368.1 | 0 | 10239.88 | 0 | 0 | 9690.42 | 0 | 0 | 9690.42
2022062017 | 2 | 0.95924 | 76739.2 | 0 | 0 | 0.4673 | 16355.5 | 0.6805 | 9527 | 40000 | 0 | 16355.5 | 0 | 9527 | 0 | 0 | 10856.7 | 0 | 0 | 10856.7
2022062018 | 2 | 0.95809 | 76647.2 | 0 | 0 | 0.49063 | 17172.05 | 0.6321 | 8849.4 | 40000 | 0 | 17172.05 | 0 | 8849.4 | 0 | 0 | 10625.75 | 0 | 0 | 10625.75
2022062019 | 2 | 0.94821 | 75856.8 | 0 | 0 | 0.50463 | 17662.05 | 0.50145 | 7020.3 | 40000 | 0 | 17662.05 | 0 | 7020.3 | 0 | 0 | 11174.45 | 0 | 0 | 11174.45
2022062020 | 2 | 0.92089 | 73671.2 | 0 | 0 | 0.49219 | 17226.65 | 0.23399 | 3275.86 | 40000 | 0 | 17226.65 | 0 | 3275.86 | 0 | 0 | 13168.69 | 0 | 0 | 13168.69
2022062021 | 2 | 0.88235 | 70588 | 0 | 0 | 0.4372 | 15302 | 0.01974 | 276.36 | 40000 | 0 | 15302 | 0 | 276.36 | 0 | 0 | 15009.64 | 0 | 0 | 15009.64
2022062022 | 2 | 0.85291 | 68232.8 | 0 | 0 | 0.40702 | 14245.7 | 0 | 0 | 40000 | 0 | 14245.7 | 0 | 0 | 0 | 0 | 13987.1 | 0 | 0 | 13987.1
2022062023 | 2 | 0.80181 | 64144.8 | 0 | 0 | 0.446 | 15610 | 0 | 0 | 40000 | 0 | 15610 | 0 | 0 | 0 | 0 | 8534.8 | 0 | 0 | 8534.8
2022062024 | 2 | 0.7486 | 59888 | 0 | 0 | 0.49212 | 17224.2 | 0 | 0 | 40000 | 0 | 17224.2 | 0 | 0 | 0 | 0 | 2663.8 | 0 | 0 | 2663.8
2022062101 | 3 | 0.69986 | 55988.8 | 0 | 0 | 0.499 | 17465 | 0 | 0 | 40000 | 0 | 15988.8 | 1476.2 | 0 | 0 | 1476.2 | 0 | 0 | 0 | 0
2022062102 | 3 | 0.66214 | 52971.2 | 0 | 0 | 0.48114 | 16839.9 | 0 | 0 | 40000 | 0 | 12971.2 | 3868.7 | 0 | 0 | 3868.7 | 0 | 0 | 0 | 0
2022062103 | 3 | 0.63127 | 50501.6 | 0 | 0 | 0.44222 | 15477.7 | 0 | 0 | 40000 | 0 | 10501.6 | 4976.1 | 0 | 0 | 4976.1 | 0 | 0 | 0 | 0
2022062104 | 3 | 0.61284 | 49027.2 | 0 | 0 | 0.40766 | 14268.1 | 0 | 0 | 40000 | 0 | 9027.2 | 5240.9 | 0 | 0 | 5240.9 | 0 | 0 | 0 | 0
2022062105 | 3 | 0.6037 | 48296 | 0 | 0 | 0.39094 | 13682.9 | 0 | 0 | 40000 | 0 | 8296 | 5386.9 | 0 | 0 | 5386.9 | 0 | 0 | 0 | 0
2022062106 | 3 | 0.60776 | 48620.8 | 0 | 0 | 0.36266 | 12693.1 | 0 | 0 | 40000 | 0 | 8620.8 | 4072.3 | 0 | 0 | 4072.3 | 0 | 0 | 0 | 0
2022062107 | 3 | 0.61805 | 49444 | 0 | 0 | 0.33696 | 11793.6 | 0.00533 | 74.62 | 40000 | 0 | 9444 | 2349.6 | 0 | 74.62 | 2424.22 | 0 | 0 | 0 | 0
2022062108 | 3 | 0.63623 | 50898.4 | 0 | 0 | 0.28626 | 10019.1 | 0.19631 | 2748.34 | 40000 | 0 | 10019.1 | 0 | 879.3 | 1869.04 | 1869.04 | 0 | 0 | 0 | 0
2022062109 | 3 | 0.67577 | 54061.6 | 0 | 0 | 0.24876 | 8706.6 | 0.56253 | 7875.42 | 40000 | 0 | 8706.6 | 0 | 5355 | 2520.42 | 2520.42 | 0 | 0 | 0 | 0
2022062110 | 3 | 0.72327 | 57861.6 | 0 | 0 | 0.32435 | 11352.25 | 0.70239 | 9833.46 | 40000 | 0 | 11352.25 | 0 | 6509.35 | 3324.11 | 3324.11 | 0 | 0 | 0 | 0
2022062111 | 3 | 0.77212 | 61769.6 | 0 | 0 | 0.34374 | 12030.9 | 0.74878 | 10482.92 | 40000 | 0 | 12030.9 | 0 | 9738.7 | 744.22 | 744.22 | 0 | 0 | 0 | 0
2022062112 | 3 | 0.82319 | 65855.2 | 0 | 0 | 0.30603 | 10711.05 | 0.77513 | 10851.82 | 40000 | 0 | 10711.05 | 0 | 10851.82 | 0 | 0 | 4292.33 | 0 | 0 | 4292.33
2022062113 | 3 | 0.86869 | 69495.2 | 0 | 0 | 0.24697 | 8643.95 | 0.75596 | 10583.44 | 40000 | 0 | 8643.95 | 0 | 10583.44 | 0 | 0 | 10267.81 | 0 | 0 | 10267.81
2022062114 | 3 | 0.90666 | 72532.8 | 0 | 0 | 0.22328 | 7814.8 | 0.76238 | 10673.32 | 40000 | 0 | 7814.8 | 0 | 10673.32 | 0 | 0 | 14044.68 | 0 | 0 | 14044.68
2022062115 | 3 | 0.93414 | 74731.2 | 0 | 0 | 0.23238 | 8133.3 | 0.74859 | 10480.26 | 40000 | 0 | 8133.3 | 0 | 10480.26 | 0 | 0 | 16117.64 | 0 | 0 | 16117.64
2022062116 | 3 | 0.94961 | 75968.8 | 0 | 0 | 0.26943 | 9430.05 | 0.75624 | 10587.36 | 40000 | 0 | 9430.05 | 0 | 10587.36 | 0 | 0 | 15951.39 | 0 | 0 | 15951.39
2022062117 | 3 | 0.95273 | 76218.4 | 0 | 0 | 0.31581 | 11053.35 | 0.73976 | 10356.64 | 40000 | 0 | 11053.35 | 0 | 10356.64 | 0 | 0 | 14808.41 | 0 | 0 | 14808.41
2022062118 | 3 | 0.94979 | 75983.2 | 0 | 0 | 0.34324 | 12013.4 | 0.68796 | 9631.44 | 40000 | 0 | 12013.4 | 0 | 9631.44 | 0 | 0 | 14338.36 | 0 | 0 | 14338.36
2022062119 | 3 | 0.93536 | 74828.8 | 0 | 0 | 0.36859 | 12900.65 | 0.5756 | 8058.4 | 40000 | 0 | 12900.65 | 0 | 8058.4 | 0 | 0 | 13869.75 | 0 | 0 | 13869.75
2022062120 | 3 | 0.90484 | 72387.2 | 0 | 0 | 0.3838 | 13433 | 0.29853 | 4179.42 | 40000 | 0 | 13433 | 0 | 4179.42 | 0 | 0 | 14774.78 | 0 | 0 | 14774.78
2022062121 | 3 | 0.86339 | 69071.2 | 0 | 0 | 0.38004 | 13301.4 | 0.02376 | 332.64 | 40000 | 0 | 13301.4 | 0 | 332.64 | 0 | 0 | 15437.16 | 0 | 0 | 15437.16
2022062122 | 3 | 0.83125 | 66500 | 0 | 0 | 0.39072 | 13675.2 | 0 | 0 | 40000 | 0 | 13675.2 | 0 | 0 | 0 | 0 | 12824.8 | 0 | 0 | 12824.8
2022062123 | 3 | 0.78205 | 62564 | 0 | 0 | 0.44059 | 15420.65 | 0 | 0 | 40000 | 0 | 15420.65 | 0 | 0 | 0 | 0 | 7143.35 | 0 | 0 | 7143.35
2022062124 | 3 | 0.72667 | 58133.6 | 0 | 0 | 0.45844 | 16045.4 | 0 | 0 | 40000 | 0 | 16045.4 | 0 | 0 | 0 | 0 | 2088.2 | 0 | 0 | 2088.2
2022062201 | 4 | 0.67756 | 54204.8 | 0 | 0 | 0.43427 | 15199.45 | 0 | 0 | 40000 | 0 | 14204.8 | 994.65 | 0 | 0 | 994.65 | 0 | 0 | 0 | 0
2022062202 | 4 | 0.63986 | 51188.8 | 0 | 0 | 0.42719 | 14951.65 | 0 | 0 | 40000 | 0 | 11188.8 | 3762.85 | 0 | 0 | 3762.85 | 0 | 0 | 0 | 0
2022062203 | 4 | 0.61195 | 48956 | 0 | 0 | 0.40233 | 14081.55 | 0 | 0 | 40000 | 0 | 8956 | 5125.55 | 0 | 0 | 5125.55 | 0 | 0 | 0 | 0
2022062204 | 4 | 0.59279 | 47423.2 | 0 | 0 | 0.35089 | 12281.15 | 0 | 0 | 40000 | 0 | 7423.2 | 4857.95 | 0 | 0 | 4857.95 | 0 | 0 | 0 | 0
2022062205 | 4 | 0.58406 | 46724.8 | 0 | 0 | 0.29327 | 10264.45 | 0 | 0 | 40000 | 0 | 6724.8 | 3539.65 | 0 | 0 | 3539.65 | 0 | 0 | 0 | 0
2022062206 | 4 | 0.58894 | 47115.2 | 0 | 0 | 0.24524 | 8583.4 | 0 | 0 | 40000 | 0 | 7115.2 | 1468.2 | 0 | 0 | 1468.2 | 0 | 0 | 0 | 0
2022062207 | 4 | 0.59918 | 47934.4 | 0 | 0 | 0.22006 | 7702.1 | 0.00533 | 74.62 | 40000 | 0 | 7702.1 | 0 | 74.62 | 0 | 0 | 157.68 | 0 | 0 | 157.68
2022062208 | 4 | 0.61843 | 49474.4 | 0 | 0 | 0.16691 | 5841.85 | 0.2081 | 2913.4 | 40000 | 0 | 5841.85 | 0 | 2913.4 | 0 | 0 | 719.15 | 0 | 0 | 719.15
2022062209 | 4 | 0.6577 | 52616 | 0 | 0 | 0.1085 | 3797.5 | 0.58499 | 8189.86 | 40000 | 0 | 3797.5 | 0 | 8189.86 | 0 | 0 | 628.64 | 0 | 0 | 628.64
2022062210 | 4 | 0.70408 | 56326.4 | 0 | 0 | 0.11122 | 3892.7 | 0.70489 | 9868.46 | 40000 | 0 | 3892.7 | 0 | 9868.46 | 0 | 0 | 2565.24 | 0 | 0 | 2565.24
2022062211 | 4 | 0.75728 | 60582.4 | 0 | 0 | 0.08852 | 3098.2 | 0.74161 | 10382.54 | 40000 | 0 | 3098.2 | 0 | 10382.54 | 0 | 0 | 7101.66 | 0 | 0 | 7101.66
2022062212 | 4 | 0.81185 | 64948 | 0 | 0 | 0.08658 | 3030.3 | 0.78844 | 11038.16 | 40000 | 0 | 3030.3 | 0 | 11038.16 | 0 | 0 | 10879.54 | 0 | 0 | 10879.54
2022062213 | 4 | 0.85911 | 68728.8 | 0 | 0 | 0.10601 | 3710.35 | 0.79125 | 11077.5 | 40000 | 0 | 3710.35 | 0 | 11077.5 | 0 | 0 | 13940.95 | 0 | 0 | 13940.95
2022062214 | 4 | 0.90021 | 72016.8 | 0 | 0 | 0.12589 | 4406.15 | 0.75608 | 10585.12 | 40000 | 0 | 4406.15 | 0 | 10585.12 | 0 | 0 | 17025.53 | 0 | 0 | 17025.53
2022062215 | 4 | 0.92661 | 74128.8 | 0 | 0 | 0.15073 | 5275.55 | 0.70761 | 9906.54 | 40000 | 0 | 5275.55 | 0 | 9906.54 | 0 | 0 | 18946.71 | 0 | 0 | 18946.71
2022062216 | 4 | 0.94304 | 75443.2 | 0 | 0 | 0.17179 | 6012.65 | 0.70546 | 9876.44 | 40000 | 0 | 6012.65 | 0 | 9876.44 | 0 | 0 | 19554.11 | 0 | 0 | 19554.11
2022062217 | 4 | 0.95132 | 76105.6 | 0 | 0 | 0.19442 | 6804.7 | 0.68864 | 9640.96 | 40000 | 0 | 6804.7 | 0 | 9640.96 | 0 | 0 | 19659.94 | 0 | 0 | 19659.94
2022062218 | 4 | 0.94629 | 75703.2 | 0 | 0 | 0.21203 | 7421.05 | 0.64595 | 9043.3 | 40000 | 0 | 7421.05 | 0 | 9043.3 | 0 | 0 | 19238.85 | 0 | 0 | 19238.85
2022062219 | 4 | 0.92852 | 74281.6 | 0 | 0 | 0.23168 | 8108.8 | 0.55119 | 7716.66 | 40000 | 0 | 8108.8 | 0 | 7716.66 | 0 | 0 | 18456.14 | 0 | 0 | 18456.14
2022062220 | 4 | 0.89869 | 71895.2 | 0 | 0 | 0.25309 | 8858.15 | 0.35147 | 4920.58 | 40000 | 0 | 8858.15 | 0 | 4920.58 | 0 | 0 | 18116.47 | 0 | 0 | 18116.47
2022062221 | 4 | 0.86386 | 69108.8 | 0 | 0 | 0.27166 | 9508.1 | 0.05122 | 717.08 | 40000 | 0 | 9508.1 | 0 | 717.08 | 0 | 0 | 18883.62 | 0 | 0 | 18883.62
2022062222 | 4 | 0.83348 | 66678.4 | 0 | 0 | 0.31742 | 11109.7 | 0 | 0 | 40000 | 0 | 11109.7 | 0 | 0 | 0 | 0 | 15568.7 | 0 | 0 | 15568.7
2022062223 | 4 | 0.78394 | 62715.2 | 0 | 0 | 0.36768 | 12868.8 | 0 | 0 | 40000 | 0 | 12868.8 | 0 | 0 | 0 | 0 | 9846.4 | 0 | 0 | 9846.4
2022062224 | 4 | 0.73006 | 58404.8 | 0 | 0 | 0.39378 | 13782.3 | 0 | 0 | 40000 | 0 | 13782.3 | 0 | 0 | 0 | 0 | 4622.5 | 0 | 0 | 4622.5
2022062301 | 5 | 0.68116 | 54492.8 | 0 | 0 | 0.41525 | 14533.75 | 0 | 0 | 40000 | 0 | 14492.8 | 40.95 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0
2022062302 | 5 | 0.64215 | 51372 | 0 | 0 | 0.41144 | 14400.4 | 0 | 0 | 40000 | 0 | 11372 | 3028.4 | 0 | 0 | 3028.4 | 0 | 0 | 0 | 0
2022062303 | 5 | 0.61262 | 49009.6 | 0 | 0 | 0.39787 | 13925.45 | 0 | 0 | 40000 | 0 | 9009.6 | 4915.85 | 0 | 0 | 4915.85 | 0 | 0 | 0 | 0
2022062304 | 5 | 0.59229 | 47383.2 | 0 | 0 | 0.37419 | 13096.65 | 0 | 0 | 40000 | 0 | 7383.2 | 5713.45 | 0 | 0 | 5713.45 | 0 | 0 | 0 | 0
2022062305 | 5 | 0.58554 | 46843.2 | 0 | 0 | 0.35384 | 12384.4 | 0 | 0 | 40000 | 0 | 6843.2 | 5541.2 | 0 | 0 | 5541.2 | 0 | 0 | 0 | 0
2022062306 | 5 | 0.58877 | 47101.6 | 0 | 0 | 0.33817 | 11835.95 | 0 | 0 | 40000 | 0 | 7101.6 | 4734.35 | 0 | 0 | 4734.35 | 0 | 0 | 0 | 0
2022062307 | 5 | 0.59764 | 47811.2 | 0 | 0 | 0.32868 | 11503.8 | 0.00513 | 71.82 | 40000 | 0 | 7811.2 | 3692.6 | 0 | 71.82 | 3764.42 | 0 | 0 | 0 | 0
2022062308 | 5 | 0.61702 | 49361.6 | 0 | 0 | 0.27991 | 9796.85 | 0.1937 | 2711.8 | 40000 | 0 | 9361.6 | 435.25 | 0 | 2711.8 | 3147.05 | 0 | 0 | 0 | 0
2022062309 | 5 | 0.65804 | 52643.2 | 0 | 0 | 0.20486 | 7170.1 | 0.57998 | 8119.72 | 40000 | 0 | 7170.1 | 0 | 5473.1 | 2646.62 | 2646.62 | 0 | 0 | 0 | 0
2022062310 | 5 | 0.71349 | 57079.2 | 0 | 0 | 0.21547 | 7541.45 | 0.76745 | 10744.3 | 40000 | 0 | 7541.45 | 0 | 9537.75 | 1206.55 | 1206.55 | 0 | 0 | 0 | 0
2022062311 | 5 | 0.77457 | 61965.6 | 0 | 0 | 0.18393 | 6437.55 | 0.80766 | 11307.24 | 40000 | 0 | 6437.55 | 0 | 11307.24 | 0 | 0 | 4220.81 | 0 | 0 | 4220.81
2022062312 | 5 | 0.83168 | 66534.4 | 0 | 0 | 0.15963 | 5587.05 | 0.81208 | 11369.12 | 40000 | 0 | 5587.05 | 0 | 11369.12 | 0 | 0 | 9578.23 | 0 | 0 | 9578.23
2022062313 | 5 | 0.87968 | 70374.4 | 0 | 0 | 0.15972 | 5590.2 | 0.78933 | 11050.62 | 40000 | 0 | 5590.2 | 0 | 11050.62 | 0 | 0 | 13733.58 | 0 | 0 | 13733.58
2022062314 | 5 | 0.92227 | 73781.6 | 0 | 0 | 0.17499 | 6124.65 | 0.75025 | 10503.5 | 40000 | 0 | 6124.65 | 0 | 10503.5 | 0 | 0 | 17153.45 | 0 | 0 | 17153.45
2022062315 | 5 | 0.95018 | 76014.4 | 0 | 0 | 0.19549 | 6842.15 | 0.7461 | 10445.4 | 40000 | 0 | 6842.15 | 0 | 10445.4 | 0 | 0 | 18726.85 | 0 | 0 | 18726.85
2022062316 | 5 | 0.95693 | 76554.4 | 0 | 0 | 0.2033 | 7115.5 | 0.71954 | 10073.56 | 40000 | 0 | 7115.5 | 0 | 10073.56 | 0 | 0 | 19365.34 | 0 | 0 | 19365.34
2022062317 | 5 | 0.9595 | 76760 | 0 | 0 | 0.20717 | 7250.95 | 0.68839 | 9637.46 | 40000 | 0 | 7250.95 | 0 | 9637.46 | 0 | 0 | 19871.59 | 0 | 0 | 19871.59
2022062318 | 5 | 0.95751 | 76600.8 | 0 | 0 | 0.21242 | 7434.7 | 0.70698 | 9897.72 | 40000 | 0 | 7434.7 | 0 | 9897.72 | 0 | 0 | 19268.38 | 0 | 0 | 19268.38
2022062319 | 5 | 0.9521 | 76168 | 0 | 0 | 0.2302 | 8057 | 0.61696 | 8637.44 | 40000 | 0 | 8057 | 0 | 8637.44 | 0 | 0 | 19473.56 | 0 | 0 | 19473.56
2022062320 | 5 | 0.92983 | 74386.4 | 0 | 0 | 0.26642 | 9324.7 | 0.35777 | 5008.78 | 40000 | 0 | 9324.7 | 0 | 5008.78 | 0 | 0 | 20052.92 | 0 | 0 | 20052.92
2022062321 | 5 | 0.89247 | 71397.6 | 0 | 0 | 0.30203 | 10571.05 | 0.04867 | 681.38 | 40000 | 0 | 10571.05 | 0 | 681.38 | 0 | 0 | 20145.17 | 0 | 0 | 20145.17
2022062322 | 5 | 0.85863 | 68690.4 | 0 | 0 | 0.36353 | 12723.55 | 0 | 0 | 40000 | 0 | 12723.55 | 0 | 0 | 0 | 0 | 15966.85 | 0 | 0 | 15966.85
2022062323 | 5 | 0.80833 | 64666.4 | 0 | 0 | 0.44118 | 15441.3 | 0 | 0 | 40000 | 0 | 15441.3 | 0 | 0 | 0 | 0 | 9225.1 | 0 | 0 | 9225.1
2022062324 | 5 | 0.75401 | 60320.8 | 0 | 0 | 0.49808 | 17432.8 | 0 | 0 | 40000 | 0 | 17432.8 | 0 | 0 | 0 | 0 | 2888 | 0 | 0 | 2888
2022062401 | 6 | 0.70452 | 56361.6 | 0 | 0 | 0.53385 | 18684.75 | 0 | 0 | 40000 | 0 | 16361.6 | 2323.15 | 0 | 0 | 2323.15 | 0 | 0 | 0 | 0
2022062402 | 6 | 0.66827 | 53461.6 | 0 | 0 | 0.55622 | 19467.7 | 0 | 0 | 40000 | 0 | 13461.6 | 6006.1 | 0 | 0 | 6006.1 | 0 | 0 | 0 | 0
2022062403 | 6 | 0.63477 | 50781.6 | 0 | 0 | 0.55103 | 19286.05 | 0 | 0 | 40000 | 0 | 10781.6 | 8504.45 | 0 | 0 | 8504.45 | 0 | 0 | 0 | 0
2022062404 | 6 | 0.61242 | 48993.6 | 0 | 0 | 0.53266 | 18643.1 | 0 | 0 | 40000 | 0 | 8993.6 | 9649.5 | 0 | 0 | 9649.5 | 0 | 0 | 0 | 0
2022062405 | 6 | 0.60145 | 48116 | 0 | 0 | 0.52148 | 18251.8 | 0 | 0 | 40000 | 0 | 8116 | 10135.8 | 0 | 0 | 10135.8 | 0 | 0 | 0 | 0
2022062406 | 6 | 0.60426 | 48340.8 | 0 | 0 | 0.5148 | 18018 | 0 | 0 | 40000 | 0 | 8340.8 | 9677.2 | 0 | 0 | 9677.2 | 0 | 0 | 0 | 0
2022062407 | 6 | 0.60742 | 48593.6 | 0 | 0 | 0.48482 | 16968.7 | 0.00484 | 67.76 | 40000 | 0 | 8593.6 | 8375.1 | 0 | 67.76 | 8442.86 | 0 | 0 | 0 | 0
2022062408 | 6 | 0.62336 | 49868.8 | 0 | 0 | 0.431 | 15085 | 0.20199 | 2827.86 | 40000 | 0 | 9868.8 | 5216.2 | 0 | 2827.86 | 8044.06 | 0 | 0 | 0 | 0
2022062409 | 6 | 0.6653 | 53224 | 0 | 0 | 0.356 | 12460 | 0.61318 | 8584.52 | 40000 | 0 | 12460 | 0 | 764 | 7820.52 | 7820.52 | 0 | 0 | 0 | 0
2022062410 | 6 | 0.72063 | 57650.4 | 0 | 0 | 0.39609 | 13863.15 | 0.7597 | 10635.8 | 40000 | 0 | 13863.15 | 0 | 3787.25 | 6848.55 | 6848.55 | 0 | 0 | 0 | 0
2022062411 | 6 | 0.78053 | 62442.4 | 0 | 0 | 0.39142 | 13699.7 | 0.79583 | 11141.62 | 40000 | 0 | 13699.7 | 0 | 8742.7 | 2398.92 | 2398.92 | 0 | 0 | 0 | 0
2022062412 | 6 | 0.8344 | 66752 | 0 | 0 | 0.36299 | 12704.65 | 0.79567 | 11139.38 | 40000 | 0 | 12704.65 | 0 | 11139.38 | 0 | 0 | 2907.97 | 0 | 0 | 2907.97
2022062413 | 6 | 0.88226 | 70580.8 | 0 | 0 | 0.34874 | 12205.9 | 0.80085 | 11211.9 | 40000 | 0 | 12205.9 | 0 | 11211.9 | 0 | 0 | 7163 | 0 | 0 | 7163
2022062414 | 6 | 0.92039 | 73631.2 | 0 | 0 | 0.30834 | 10791.9 | 0.81681 | 11435.34 | 40000 | 0 | 10791.9 | 0 | 11435.34 | 0 | 0 | 11403.96 | 0 | 0 | 11403.96
2022062415 | 6 | 0.94649 | 75719.2 | 0 | 0 | 0.28783 | 10074.05 | 0.80863 | 11320.82 | 40000 | 0 | 10074.05 | 0 | 11320.82 | 0 | 0 | 14324.33 | 0 | 0 | 14324.33
2022062416 | 6 | 0.95324 | 76259.2 | 0 | 0 | 0.28128 | 9844.8 | 0.78622 | 11007.08 | 40000 | 0 | 9844.8 | 0 | 11007.08 | 0 | 0 | 15407.32 | 0 | 0 | 15407.32
2022062417 | 6 | 0.95648 | 76518.4 | 0 | 0 | 0.27735 | 9707.25 | 0.77162 | 10802.68 | 40000 | 0 | 9707.25 | 0 | 10802.68 | 0 | 0 | 16008.47 | 0 | 0 | 16008.47
2022062418 | 6 | 0.9557 | 76456 | 0 | 0 | 0.29106 | 10187.1 | 0.73083 | 10231.62 | 40000 | 0 | 10187.1 | 0 | 10231.62 | 0 | 0 | 16037.28 | 0 | 0 | 16037.28
2022062419 | 6 | 0.94869 | 75895.2 | 0 | 0 | 0.32159 | 11255.65 | 0.64173 | 8984.22 | 40000 | 0 | 11255.65 | 0 | 8984.22 | 0 | 0 | 15655.33 | 0 | 0 | 15655.33
2022062420 | 6 | 0.92356 | 73884.8 | 0 | 0 | 0.35083 | 12279.05 | 0.3675 | 5145 | 40000 | 0 | 12279.05 | 0 | 5145 | 0 | 0 | 16460.75 | 0 | 0 | 16460.75
2022062421 | 6 | 0.88433 | 70746.4 | 0 | 0 | 0.37372 | 13080.2 | 0.04818 | 674.52 | 40000 | 0 | 13080.2 | 0 | 674.52 | 0 | 0 | 16991.68 | 0 | 0 | 16991.68
2022062422 | 6 | 0.85167 | 68133.6 | 0 | 0 | 0.44493 | 15572.55 | 0 | 0 | 40000 | 0 | 15572.55 | 0 | 0 | 0 | 0 | 12561.05 | 0 | 0 | 12561.05
2022062423 | 6 | 0.80304 | 64243.2 | 0 | 0 | 0.53719 | 18801.65 | 0 | 0 | 40000 | 0 | 18801.65 | 0 | 0 | 0 | 0 | 5441.55 | 0 | 0 | 5441.55
2022062424 | 6 | 0.75308 | 60246.4 | 0 | 0 | 0.59724 | 20903.4 | 0 | 0 | 40000 | 0 | 20246.4 | 657 | 0 | 0 | 657 | 0 | 0 | 0 | 0
2022062501 | 7 | 0.70418 | 56334.4 | 0 | 0 | 0.63081 | 22078.35 | 6e-05 | 0.84 | 40000 | 0 | 16334.4 | 5743.95 | 0 | 0.84 | 5744.79 | 0 | 0 | 0 | 0
2022062502 | 7 | 0.66449 | 53159.2 | 0 | 0 | 0.61776 | 21621.6 | 5e-05 | 0.7 | 40000 | 0 | 13159.2 | 8462.4 | 0 | 0.7 | 8463.1 | 0 | 0 | 0 | 0
2022062503 | 7 | 0.63183 | 50546.4 | 0 | 0 | 0.59452 | 20808.2 | 0 | 0 | 40000 | 0 | 10546.4 | 10261.8 | 0 | 0 | 10261.8 | 0 | 0 | 0 | 0
2022062504 | 7 | 0.60838 | 48670.4 | 0 | 0 | 0.56691 | 19841.85 | 0 | 0 | 40000 | 0 | 8670.4 | 11171.45 | 0 | 0 | 11171.45 | 0 | 0 | 0 | 0
2022062505 | 7 | 0.59214 | 47371.2 | 0 | 0 | 0.55599 | 19459.65 | 0 | 0 | 40000 | 0 | 7371.2 | 12088.45 | 0 | 0 | 12088.45 | 0 | 0 | 0 | 0
2022062506 | 7 | 0.58432 | 46745.6 | 0 | 0 | 0.54935 | 19227.25 | 0 | 0 | 40000 | 0 | 6745.6 | 12481.65 | 0 | 0 | 12481.65 | 0 | 0 | 0 | 0
2022062507 | 7 | 0.57416 | 45932.8 | 0 | 0 | 0.50735 | 17757.25 | 0.00523 | 73.22 | 40000 | 0 | 5932.8 | 11824.45 | 0 | 73.22 | 11897.67 | 0 | 0 | 0 | 0
2022062508 | 7 | 0.58428 | 46742.4 | 0 | 0 | 0.42944 | 15030.4 | 0.21675 | 3034.5 | 40000 | 0 | 6742.4 | 8288 | 0 | 3034.5 | 11322.5 | 0 | 0 | 0 | 0
2022062509 | 7 | 0.62667 | 50133.6 | 0 | 0 | 0.36072 | 12625.2 | 0.6315 | 8841 | 40000 | 0 | 10133.6 | 2491.6 | 0 | 8841 | 11332.6 | 0 | 0 | 0 | 0
2022062510 | 7 | 0.68205 | 54564 | 0 | 0 | 0.40255 | 14089.25 | 0.77262 | 10816.68 | 40000 | 0 | 14089.25 | 0 | 474.75 | 10341.93 | 10341.93 | 0 | 0 | 0 | 0
2022062511 | 7 | 0.7369 | 58952 | 0 | 0 | 0.34621 | 12117.35 | 0.82499 | 11549.86 | 40000 | 0 | 12117.35 | 0 | 6834.65 | 4715.21 | 4715.21 | 0 | 0 | 0 | 0
2022062512 | 7 | 0.78795 | 63036 | 0 | 0 | 0.24672 | 8635.2 | 0.83716 | 11720.24 | 40000 | 0 | 8635.2 | 0 | 11720.24 | 0 | 0 | 2680.56 | 0 | 0 | 2680.56
2022062513 | 7 | 0.83162 | 66529.6 | 0 | 0 | 0.18867 | 6603.45 | 0.82965 | 11615.1 | 40000 | 0 | 6603.45 | 0 | 11615.1 | 0 | 0 | 8311.05 | 0 | 0 | 8311.05
2022062514 | 7 | 0.86781 | 69424.8 | 0 | 0 | 0.18335 | 6417.25 | 0.82047 | 11486.58 | 40000 | 0 | 6417.25 | 0 | 11486.58 | 0 | 0 | 11520.97 | 0 | 0 | 11520.97
2022062515 | 7 | 0.89793 | 71834.4 | 0 | 0 | 0.19242 | 6734.7 | 0.7956 | 11138.4 | 40000 | 0 | 6734.7 | 0 | 11138.4 | 0 | 0 | 13961.3 | 0 | 0 | 13961.3
2022062516 | 7 | 0.91988 | 73590.4 | 0 | 0 | 0.20358 | 7125.3 | 0.79607 | 11144.98 | 40000 | 0 | 7125.3 | 0 | 11144.98 | 0 | 0 | 15320.12 | 0 | 0 | 15320.12
2022062517 | 7 | 0.93447 | 74757.6 | 0 | 0 | 0.2299 | 8046.5 | 0.77837 | 10897.18 | 40000 | 0 | 8046.5 | 0 | 10897.18 | 0 | 0 | 15813.92 | 0 | 0 | 15813.92
2022062518 | 7 | 0.93907 | 75125.6 | 0 | 0 | 0.26757 | 9364.95 | 0.76002 | 10640.28 | 40000 | 0 | 9364.95 | 0 | 10640.28 | 0 | 0 | 15120.37 | 0 | 0 | 15120.37
2022062519 | 7 | 0.92472 | 73977.6 | 0 | 0 | 0.29724 | 10403.4 | 0.67184 | 9405.76 | 40000 | 0 | 10403.4 | 0 | 9405.76 | 0 | 0 | 14168.44 | 0 | 0 | 14168.44
2022062520 | 7 | 0.89531 | 71624.8 | 0 | 0 | 0.32481 | 11368.35 | 0.39464 | 5524.96 | 40000 | 0 | 11368.35 | 0 | 5524.96 | 0 | 0 | 14731.49 | 0 | 0 | 14731.49
2022062521 | 7 | 0.85396 | 68316.8 | 0 | 0 | 0.35163 | 12307.05 | 0.04634 | 648.76 | 40000 | 0 | 12307.05 | 0 | 648.76 | 0 | 0 | 15360.99 | 0 | 0 | 15360.99
2022062522 | 7 | 0.81753 | 65402.4 | 0 | 0 | 0.39797 | 13928.95 | 0 | 0 | 40000 | 0 | 13928.95 | 0 | 0 | 0 | 0 | 11473.45 | 0 | 0 | 11473.45
2022062523 | 7 | 0.77271 | 61816.8 | 0 | 0 | 0.48529 | 16985.15 | 0 | 0 | 40000 | 0 | 16985.15 | 0 | 0 | 0 | 0 | 4831.65 | 0 | 0 | 4831.65
2022062524 | 7 | 0.725 | 58000 | 0 | 0 | 0.53877 | 18856.95 | 0 | 0 | 40000 | 0 | 18000 | 856.95 | 0 | 0 | 856.95 | 0 | 0 | 0 | 0
2022062601 | 1 | 0.67798 | 54238.4 | 0 | 0 | 0.5394 | 18879 | 0 | 0 | 40000 | 0 | 14238.4 | 4640.6 | 0 | 0 | 4640.6 | 0 | 0 | 0 | 0
2022062602 | 1 | 0.63814 | 51051.2 | 0 | 0 | 0.52114 | 18239.9 | 0 | 0 | 40000 | 0 | 11051.2 | 7188.7 | 0 | 0 | 7188.7 | 0 | 0 | 0 | 0
2022062603 | 1 | 0.60753 | 48602.4 | 0 | 0 | 0.48561 | 16996.35 | 0 | 0 | 40000 | 0 | 8602.4 | 8393.95 | 0 | 0 | 8393.95 | 0 | 0 | 0 | 0
2022062604 | 1 | 0.58413 | 46730.4 | 0 | 0 | 0.44955 | 15734.25 | 0 | 0 | 40000 | 0 | 6730.4 | 9003.85 | 0 | 0 | 9003.85 | 0 | 0 | 0 | 0
2022062605 | 1 | 0.56922 | 45537.6 | 0 | 0 | 0.41512 | 14529.2 | 0 | 0 | 40000 | 0 | 5537.6 | 8991.6 | 0 | 0 | 8991.6 | 0 | 0 | 0 | 0
2022062606 | 1 | 0.55518 | 44414.4 | 0 | 0 | 0.34601 | 12110.35 | 0 | 0 | 40000 | 0 | 4414.4 | 7695.95 | 0 | 0 | 7695.95 | 0 | 0 | 0 | 0
2022062607 | 1 | 0.54338 | 43470.4 | 0 | 0 | 0.28412 | 9944.2 | 0.0054 | 75.6 | 40000 | 0 | 3470.4 | 6473.8 | 0 | 75.6 | 6549.4 | 0 | 0 | 0 | 0
2022062608 | 1 | 0.55489 | 44391.2 | 0 | 0 | 0.23892 | 8362.2 | 0.19029 | 2664.06 | 40000 | 0 | 4391.2 | 3971 | 0 | 2664.06 | 6635.06 | 0 | 0 | 0 | 0
2022062609 | 1 | 0.59902 | 47921.6 | 0 | 0 | 0.25344 | 8870.4 | 0.57444 | 8042.16 | 40000 | 0 | 7921.6 | 948.8 | 0 | 8042.16 | 8990.96 | 0 | 0 | 0 | 0
2022062610 | 1 | 0.6553 | 52424 | 0 | 0 | 0.26976 | 9441.6 | 0.75752 | 10605.28 | 40000 | 0 | 9441.6 | 0 | 2982.4 | 7622.88 | 7622.88 | 0 | 0 | 0 | 0
2022062611 | 1 | 0.71216 | 56972.8 | 0 | 0 | 0.24592 | 8607.2 | 0.81224 | 11371.36 | 40000 | 0 | 8607.2 | 0 | 8365.6 | 3005.76 | 3005.76 | 0 | 0 | 0 | 0
2022062612 | 1 | 0.77064 | 61651.2 | 0 | 0 | 0.22515 | 7880.25 | 0.81578 | 11420.92 | 40000 | 0 | 7880.25 | 0 | 11420.92 | 0 | 0 | 2350.03 | 0 | 0 | 2350.03
2022062613 | 1 | 0.82229 | 65783.2 | 0 | 0 | 0.23213 | 8124.55 | 0.80104 | 11214.56 | 40000 | 0 | 8124.55 | 0 | 11214.56 | 0 | 0 | 6444.09 | 0 | 0 | 6444.09
2022062614 | 1 | 0.86701 | 69360.8 | 0 | 0 | 0.25944 | 9080.4 | 0.76711 | 10739.54 | 40000 | 0 | 9080.4 | 0 | 10739.54 | 0 | 0 | 9540.86 | 0 | 0 | 9540.86
2022062615 | 1 | 0.89981 | 71984.8 | 0 | 0 | 0.28323 | 9913.05 | 0.73994 | 10359.16 | 40000 | 0 | 9913.05 | 0 | 10359.16 | 0 | 0 | 11712.59 | 0 | 0 | 11712.59
2022062616 | 1 | 0.92451 | 73960.8 | 0 | 0 | 0.31994 | 11197.9 | 0.69601 | 9744.14 | 40000 | 0 | 11197.9 | 0 | 9744.14 | 0 | 0 | 13018.76 | 0 | 0 | 13018.76
2022062617 | 1 | 0.94036 | 75228.8 | 0 | 0 | 0.35573 | 12450.55 | 0.68556 | 9597.84 | 40000 | 0 | 12450.55 | 0 | 9597.84 | 0 | 0 | 13180.41 | 0 | 0 | 13180.41
2022062618 | 1 | 0.94429 | 75543.2 | 0 | 0 | 0.39627 | 13869.45 | 0.66336 | 9287.04 | 40000 | 0 | 13869.45 | 0 | 9287.04 | 0 | 0 | 12386.71 | 0 | 0 | 12386.71
2022062619 | 1 | 0.93267 | 74613.6 | 0 | 0 | 0.43778 | 15322.3 | 0.583 | 8162 | 40000 | 0 | 15322.3 | 0 | 8162 | 0 | 0 | 11129.3 | 0 | 0 | 11129.3
2022062620 | 1 | 0.90383 | 72306.4 | 0 | 0 | 0.48489 | 16971.15 | 0.32856 | 4599.84 | 40000 | 0 | 16971.15 | 0 | 4599.84 | 0 | 0 | 10735.41 | 0 | 0 | 10735.41
2022062621 | 1 | 0.86469 | 69175.2 | 0 | 0 | 0.48415 | 16945.25 | 0.03395 | 475.3 | 40000 | 0 | 16945.25 | 0 | 475.3 | 0 | 0 | 11754.65 | 0 | 0 | 11754.65
2022062622 | 1 | 0.83513 | 66810.4 | 0 | 0 | 0.45866 | 16053.1 | 0 | 0 | 40000 | 0 | 16053.1 | 0 | 0 | 0 | 0 | 10757.3 | 0 | 0 | 10757.3
2022062623 | 1 | 0.78505 | 62804 | 0 | 0 | 0.45849 | 16047.15 | 0 | 0 | 40000 | 0 | 16047.15 | 0 | 0 | 0 | 0 | 6756.85 | 0 | 0 | 6756.85
2022062624 | 1 | 0.73007 | 58405.6 | 0 | 0 | 0.45644 | 15975.4 | 0 | 0 | 40000 | 0 | 15975.4 | 0 | 0 | 0 | 0 | 2430.2 | 0 | 0 | 2430.2
2022062701 | 2 | 0.67919 | 54335.2 | 0 | 0 | 0.45487 | 15920.45 | 0 | 0 | 40000 | 0 | 14335.2 | 1585.25 | 0 | 0 | 1585.25 | 0 | 0 | 0 | 0
2022062702 | 2 | 0.63941 | 51152.8 | 0 | 0 | 0.40944 | 14330.4 | 0 | 0 | 40000 | 0 | 11152.8 | 3177.6 | 0 | 0 | 3177.6 | 0 | 0 | 0 | 0
2022062703 | 2 | 0.60822 | 48657.6 | 0 | 0 | 0.35465 | 12412.75 | 0 | 0 | 40000 | 0 | 8657.6 | 3755.15 | 0 | 0 | 3755.15 | 0 | 0 | 0 | 0
2022062704 | 2 | 0.5854 | 46832 | 0 | 0 | 0.30836 | 10792.6 | 0 | 0 | 40000 | 0 | 6832 | 3960.6 | 0 | 0 | 3960.6 | 0 | 0 | 0 | 0
2022062705 | 2 | 0.57768 | 46214.4 | 0 | 0 | 0.28794 | 10077.9 | 0 | 0 | 40000 | 0 | 6214.4 | 3863.5 | 0 | 0 | 3863.5 | 0 | 0 | 0 | 0
2022062706 | 2 | 0.58179 | 46543.2 | 0 | 0 | 0.29249 | 10237.15 | 0 | 0 | 40000 | 0 | 6543.2 | 3693.95 | 0 | 0 | 3693.95 | 0 | 0 | 0 | 0
2022062707 | 2 | 0.59178 | 47342.4 | 0 | 0 | 0.27592 | 9657.2 | 0.00391 | 54.74 | 40000 | 0 | 7342.4 | 2314.8 | 0 | 54.74 | 2369.54 | 0 | 0 | 0 | 0
2022062708 | 2 | 0.60036 | 48028.8 | 0 | 0 | 0.21802 | 7630.7 | 0.12966 | 1815.24 | 40000 | 0 | 7630.7 | 0 | 398.1 | 1417.14 | 1417.14 | 0 | 0 | 0 | 0
2022062709 | 2 | 0.62922 | 50337.6 | 0 | 0 | 0.17285 | 6049.75 | 0.40943 | 5732.02 | 40000 | 0 | 6049.75 | 0 | 4287.85 | 1444.17 | 1444.17 | 0 | 0 | 0 | 0
2022062710 | 2 | 0.67357 | 53885.6 | 0 | 0 | 0.1434 | 5019 | 0.61821 | 8654.94 | 40000 | 0 | 5019 | 0 | 8654.94 | 0 | 0 | 211.66 | 0 | 0 | 211.66
2022062711 | 2 | 0.72778 | 58222.4 | 0 | 0 | 0.11828 | 4139.8 | 0.73153 | 10241.42 | 40000 | 0 | 4139.8 | 0 | 10241.42 | 0 | 0 | 3841.18 | 0 | 0 | 3841.18
2022062712 | 2 | 0.78051 | 62440.8 | 0 | 0 | 0.08448 | 2956.8 | 0.7979 | 11170.6 | 40000 | 0 | 2956.8 | 0 | 11170.6 | 0 | 0 | 8313.4 | 0 | 0 | 8313.4
2022062713 | 2 | 0.83192 | 66553.6 | 0 | 0 | 0.07989 | 2796.15 | 0.82069 | 11489.66 | 40000 | 0 | 2796.15 | 0 | 11489.66 | 0 | 0 | 12267.79 | 0 | 0 | 12267.79
2022062714 | 2 | 0.87722 | 70177.6 | 0 | 0 | 0.08639 | 3023.65 | 0.80756 | 11305.84 | 40000 | 0 | 3023.65 | 0 | 11305.84 | 0 | 0 | 15848.11 | 0 | 0 | 15848.11
2022062715 | 2 | 0.90202 | 72161.6 | 0 | 0 | 0.10592 | 3707.2 | 0.74013 | 10361.82 | 40000 | 0 | 3707.2 | 0 | 10361.82 | 0 | 0 | 18092.58 | 0 | 0 | 18092.58
2022062716 | 2 | 0.89582 | 71665.6 | 0 | 0 | 0.14093 | 4932.55 | 0.67654 | 9471.56 | 40000 | 0 | 4932.55 | 0 | 9471.56 | 0 | 0 | 17261.49 | 0 | 0 | 17261.49
2022062717 | 2 | 0.87923 | 70338.4 | 0 | 0 | 0.17553 | 6143.55 | 0.63329 | 8866.06 | 40000 | 0 | 6143.55 | 0 | 8866.06 | 0 | 0 | 15328.79 | 0 | 0 | 15328.79
2022062718 | 2 | 0.8579 | 68632 | 0 | 0 | 0.23164 | 8107.4 | 0.57657 | 8071.98 | 40000 | 0 | 8107.4 | 0 | 8071.98 | 0 | 0 | 12452.62 | 0 | 0 | 12452.62
2022062719 | 2 | 0.82928 | 66342.4 | 0 | 0 | 0.28158 | 9855.3 | 0.45996 | 6439.44 | 40000 | 0 | 9855.3 | 0 | 6439.44 | 0 | 0 | 10047.66 | 0 | 0 | 10047.66
2022062720 | 2 | 0.79552 | 63641.6 | 0 | 0 | 0.30993 | 10847.55 | 0.23605 | 3304.7 | 40000 | 0 | 10847.55 | 0 | 3304.7 | 0 | 0 | 9489.35 | 0 | 0 | 9489.35
2022062721 | 2 | 0.76807 | 61445.6 | 0 | 0 | 0.30999 | 10849.65 | 0.03165 | 443.1 | 40000 | 0 | 10849.65 | 0 | 443.1 | 0 | 0 | 10152.85 | 0 | 0 | 10152.85
2022062722 | 2 | 0.74171 | 59336.8 | 0 | 0 | 0.29253 | 10238.55 | 0 | 0 | 40000 | 0 | 10238.55 | 0 | 0 | 0 | 0 | 9098.25 | 0 | 0 | 9098.25
2022062723 | 2 | 0.69659 | 55727.2 | 0 | 0 | 0.29966 | 10488.1 | 0 | 0 | 40000 | 0 | 10488.1 | 0 | 0 | 0 | 0 | 5239.1 | 0 | 0 | 5239.1
2022062724 | 2 | 0.64892 | 51913.6 | 0 | 0 | 0.25828 | 9039.8 | 0 | 0 | 40000 | 0 | 9039.8 | 0 | 0 | 0 | 0 | 2873.8 | 0 | 0 | 2873.8
2022062801 | 3 | 0.60889 | 48711.2 | 0 | 0 | 0.21778 | 7622.3 | 0 | 0 | 40000 | 0 | 7622.3 | 0 | 0 | 0 | 0 | 1088.9 | 0 | 0 | 1088.9
2022062802 | 3 | 0.57728 | 46182.4 | 0 | 0 | 0.18502 | 6475.7 | 0 | 0 | 40000 | 0 | 6182.4 | 293.3 | 0 | 0 | 293.3 | 0 | 0 | 0 | 0
2022062803 | 3 | 0.55947 | 44757.6 | 0 | 0 | 0.16333 | 5716.55 | 0 | 0 | 40000 | 0 | 4757.6 | 958.95 | 0 | 0 | 958.95 | 0 | 0 | 0 | 0
2022062804 | 3 | 0.54436 | 43548.8 | 0 | 0 | 0.1287 | 4504.5 | 0 | 0 | 40000 | 0 | 3548.8 | 955.7 | 0 | 0 | 955.7 | 0 | 0 | 0 | 0
2022062805 | 3 | 0.54095 | 43276 | 0 | 0 | 0.1022 | 3577 | 0 | 0 | 40000 | 0 | 3276 | 301 | 0 | 0 | 301 | 0 | 0 | 0 | 0
2022062806 | 3 | 0.55083 | 44066.4 | 0 | 0 | 0.08772 | 3070.2 | 0 | 0 | 40000 | 0 | 3070.2 | 0 | 0 | 0 | 0 | 996.2 | 0 | 0 | 996.2
2022062807 | 3 | 0.56532 | 45225.6 | 0 | 0 | 0.09 | 3150 | 0.00407 | 56.98 | 40000 | 0 | 3150 | 0 | 56.98 | 0 | 0 | 2018.62 | 0 | 0 | 2018.62
2022062808 | 3 | 0.58038 | 46430.4 | 0 | 0 | 0.09155 | 3204.25 | 0.13977 | 1956.78 | 40000 | 0 | 3204.25 | 0 | 1956.78 | 0 | 0 | 1269.37 | 0 | 0 | 1269.37
2022062809 | 3 | 0.60578 | 48462.4 | 0 | 0 | 0.0782 | 2737 | 0.46617 | 6526.38 | 40000 | 0 | 2737 | 0 | 5725.4 | 800.98 | 800.98 | 0 | 0 | 0 | 0
2022062810 | 3 | 0.63992 | 51193.6 | 0 | 0 | 0.07048 | 2466.8 | 0.66456 | 9303.84 | 40000 | 0 | 2466.8 | 0 | 8726.8 | 577.04 | 577.04 | 0 | 0 | 0 | 0
2022062811 | 3 | 0.6807 | 54456 | 0 | 0 | 0.05625 | 1968.75 | 0.75683 | 10595.62 | 40000 | 0 | 1968.75 | 0 | 10595.62 | 0 | 0 | 1891.63 | 0 | 0 | 1891.63
2022062812 | 3 | 0.7224 | 57792 | 0 | 0 | 0.05195 | 1818.25 | 0.76237 | 10673.18 | 40000 | 0 | 1818.25 | 0 | 10673.18 | 0 | 0 | 5300.57 | 0 | 0 | 5300.57
2022062813 | 3 | 0.76371 | 61096.8 | 0 | 0 | 0.05806 | 2032.1 | 0.74336 | 10407.04 | 40000 | 0 | 2032.1 | 0 | 10407.04 | 0 | 0 | 8657.66 | 0 | 0 | 8657.66
2022062814 | 3 | 0.79633 | 63706.4 | 0 | 0 | 0.0802 | 2807 | 0.72071 | 10089.94 | 40000 | 0 | 2807 | 0 | 10089.94 | 0 | 0 | 10809.46 | 0 | 0 | 10809.46
2022062815 | 3 | 0.82061 | 65648.8 | 0 | 0 | 0.11907 | 4167.45 | 0.68949 | 9652.86 | 40000 | 0 | 4167.45 | 0 | 9652.86 | 0 | 0 | 11828.49 | 0 | 0 | 11828.49
2022062816 | 3 | 0.83115 | 66492 | 0 | 0 | 0.15904 | 5566.4 | 0.66399 | 9295.86 | 40000 | 0 | 5566.4 | 0 | 9295.86 | 0 | 0 | 11629.74 | 0 | 0 | 11629.74
2022062817 | 3 | 0.8343 | 66744 | 0 | 0 | 0.18352 | 6423.2 | 0.66065 | 9249.1 | 40000 | 0 | 6423.2 | 0 | 9249.1 | 0 | 0 | 11071.7 | 0 | 0 | 11071.7
2022062818 | 3 | 0.82515 | 66012 | 0 | 0 | 0.23499 | 8224.65 | 0.53388 | 7474.32 | 40000 | 0 | 8224.65 | 0 | 7474.32 | 0 | 0 | 10313.03 | 0 | 0 | 10313.03
2022062819 | 3 | 0.80866 | 64692.8 | 0 | 0 | 0.2667 | 9334.5 | 0.42578 | 5960.92 | 40000 | 0 | 9334.5 | 0 | 5960.92 | 0 | 0 | 9397.38 | 0 | 0 | 9397.38
2022062820 | 3 | 0.78102 | 62481.6 | 0 | 0 | 0.2792 | 9772 | 0.21693 | 3037.02 | 40000 | 0 | 9772 | 0 | 3037.02 | 0 | 0 | 9672.58 | 0 | 0 | 9672.58
2022062821 | 3 | 0.74696 | 59756.8 | 0 | 0 | 0.26213 | 9174.55 | 0.01978 | 276.92 | 40000 | 0 | 9174.55 | 0 | 276.92 | 0 | 0 | 10305.33 | 0 | 0 | 10305.33
2022062822 | 3 | 0.72103 | 57682.4 | 0 | 0 | 0.25873 | 9055.55 | 0 | 0 | 40000 | 0 | 9055.55 | 0 | 0 | 0 | 0 | 8626.85 | 0 | 0 | 8626.85
2022062823 | 3 | 0.67554 | 54043.2 | 0 | 0 | 0.23867 | 8353.45 | 0 | 0 | 40000 | 0 | 8353.45 | 0 | 0 | 0 | 0 | 5689.75 | 0 | 0 | 5689.75
2022062824 | 3 | 0.62648 | 50118.4 | 0 | 0 | 0.20628 | 7219.8 | 0 | 0 | 40000 | 0 | 7219.8 | 0 | 0 | 0 | 0 | 2898.6 | 0 | 0 | 2898.6
2022062901 | 4 | 0.58553 | 46842.4 | 0 | 0 | 0.16331 | 5715.85 | 0 | 0 | 40000 | 0 | 5715.85 | 0 | 0 | 0 | 0 | 1126.55 | 0 | 0 | 1126.55
2022062902 | 4 | 0.55572 | 44457.6 | 0 | 0 | 0.12577 | 4401.95 | 0 | 0 | 40000 | 0 | 4401.95 | 0 | 0 | 0 | 0 | 55.65 | 0 | 0 | 55.65
2022062903 | 4 | 0.53355 | 42684 | 0 | 0 | 0.10552 | 3693.2 | 0 | 0 | 40000 | 0 | 2684 | 1009.2 | 0 | 0 | 1009.2 | 0 | 0 | 0 | 0
2022062904 | 4 | 0.52008 | 41606.4 | 0 | 0 | 0.09865 | 3452.75 | 0 | 0 | 40000 | 0 | 1606.4 | 1846.35 | 0 | 0 | 1846.35 | 0 | 0 | 0 | 0
2022062905 | 4 | 0.5175 | 41400 | 0 | 0 | 0.09118 | 3191.3 | 0 | 0 | 40000 | 0 | 1400 | 1791.3 | 0 | 0 | 1791.3 | 0 | 0 | 0 | 0
2022062906 | 4 | 0.52703 | 42162.4 | 0 | 0 | 0.08448 | 2956.8 | 0 | 0 | 40000 | 0 | 2162.4 | 794.4 | 0 | 0 | 794.4 | 0 | 0 | 0 | 0
2022062907 | 4 | 0.54248 | 43398.4 | 0 | 0 | 0.08124 | 2843.4 | 0.00411 | 57.54 | 40000 | 0 | 2843.4 | 0 | 57.54 | 0 | 0 | 497.46 | 0 | 0 | 497.46
2022062908 | 4 | 0.5558 | 44464 | 0 | 0 | 0.07772 | 2720.2 | 0.12791 | 1790.74 | 40000 | 0 | 2720.2 | 0 | 1743.8 | 46.94 | 46.94 | 0 | 0 | 0 | 0
2022062909 | 4 | 0.58452 | 46761.6 | 0 | 0 | 0.05031 | 1760.85 | 0.47068 | 6589.52 | 40000 | 0 | 1760.85 | 0 | 5000.75 | 1588.77 | 1588.77 | 0 | 0 | 0 | 0
2022062910 | 4 | 0.62924 | 50339.2 | 0 | 0 | 0.05201 | 1820.35 | 0.65005 | 9100.7 | 40000 | 0 | 1820.35 | 0 | 8518.85 | 581.85 | 581.85 | 0 | 0 | 0 | 0
2022062911 | 4 | 0.6775 | 54200 | 0 | 0 | 0.06218 | 2176.3 | 0.72216 | 10110.24 | 40000 | 0 | 2176.3 | 0 | 10110.24 | 0 | 0 | 1913.46 | 0 | 0 | 1913.46
2022062912 | 4 | 0.72716 | 58172.8 | 0 | 0 | 0.05401 | 1890.35 | 0.77458 | 10844.12 | 40000 | 0 | 1890.35 | 0 | 10844.12 | 0 | 0 | 5438.33 | 0 | 0 | 5438.33
2022062913 | 4 | 0.77326 | 61860.8 | 0 | 0 | 0.05685 | 1989.75 | 0.78411 | 10977.54 | 40000 | 0 | 1989.75 | 0 | 10977.54 | 0 | 0 | 8893.51 | 0 | 0 | 8893.51
2022062914 | 4 | 0.81492 | 65193.6 | 0 | 0 | 0.07577 | 2651.95 | 0.76985 | 10777.9 | 40000 | 0 | 2651.95 | 0 | 10777.9 | 0 | 0 | 11763.75 | 0 | 0 | 11763.75
2022062915 | 4 | 0.84525 | 67620 | 0 | 0 | 0.0989 | 3461.5 | 0.75568 | 10579.52 | 40000 | 0 | 3461.5 | 0 | 10579.52 | 0 | 0 | 13578.98 | 0 | 0 | 13578.98
2022062916 | 4 | 0.86621 | 69296.8 | 0 | 0 | 0.12782 | 4473.7 | 0.72282 | 10119.48 | 40000 | 0 | 4473.7 | 0 | 10119.48 | 0 | 0 | 14703.62 | 0 | 0 | 14703.62
2022062917 | 4 | 0.87756 | 70204.8 | 0 | 0 | 0.14665 | 5132.75 | 0.71786 | 10050.04 | 40000 | 0 | 5132.75 | 0 | 10050.04 | 0 | 0 | 15022.01 | 0 | 0 | 15022.01
2022062918 | 4 | 0.87605 | 70084 | 0 | 0 | 0.14615 | 5115.25 | 0.70058 | 9808.12 | 40000 | 0 | 5115.25 | 0 | 9808.12 | 0 | 0 | 15160.63 | 0 | 0 | 15160.63
2022062919 | 4 | 0.85928 | 68742.4 | 0 | 0 | 0.14638 | 5123.3 | 0.57742 | 8083.88 | 40000 | 0 | 5123.3 | 0 | 8083.88 | 0 | 0 | 15535.22 | 0 | 0 | 15535.22
2022062920 | 4 | 0.83069 | 66455.2 | 0 | 0 | 0.16819 | 5886.65 | 0.32133 | 4498.62 | 40000 | 0 | 5886.65 | 0 | 4498.62 | 0 | 0 | 16069.93 | 0 | 0 | 16069.93
2022062921 | 4 | 0.79465 | 63572 | 0 | 0 | 0.18622 | 6517.7 | 0.04596 | 643.44 | 40000 | 0 | 6517.7 | 0 | 643.44 | 0 | 0 | 16410.86 | 0 | 0 | 16410.86
2022062922 | 4 | 0.76542 | 61233.6 | 0 | 0 | 0.25627 | 8969.45 | 0 | 0 | 40000 | 0 | 8969.45 | 0 | 0 | 0 | 0 | 12264.15 | 0 | 0 | 12264.15
2022062923 | 4 | 0.71744 | 57395.2 | 0 | 0 | 0.33199 | 11619.65 | 0 | 0 | 40000 | 0 | 11619.65 | 0 | 0 | 0 | 0 | 5775.55 | 0 | 0 | 5775.55
2022062924 | 4 | 0.66681 | 53344.8 | 0 | 0 | 0.37553 | 13143.55 | 0 | 0 | 40000 | 0 | 13143.55 | 0 | 0 | 0 | 0 | 201.25 | 0 | 0 | 201.25
2022063001 | 5 | 0.62141 | 49712.8 | 0 | 0 | 0.38326 | 13414.1 | 0 | 0 | 40000 | 0 | 9712.8 | 3701.3 | 0 | 0 | 3701.3 | 0 | 0 | 0 | 0
2022063002 | 5 | 0.58678 | 46942.4 | 0 | 0 | 0.39414 | 13794.9 | 0 | 0 | 40000 | 0 | 6942.4 | 6852.5 | 0 | 0 | 6852.5 | 0 | 0 | 0 | 0
2022063003 | 5 | 0.56481 | 45184.8 | 0 | 0 | 0.4011 | 14038.5 | 0 | 0 | 40000 | 0 | 5184.8 | 8853.7 | 0 | 0 | 8853.7 | 0 | 0 | 0 | 0
2022063004 | 5 | 0.54607 | 43685.6 | 0 | 0 | 0.3847 | 13464.5 | 0 | 0 | 40000 | 0 | 3685.6 | 9778.9 | 0 | 0 | 9778.9 | 0 | 0 | 0 | 0
2022063005 | 5 | 0.53996 | 43196.8 | 0 | 0 | 0.37143 | 13000.05 | 0 | 0 | 40000 | 0 | 3196.8 | 9803.25 | 0 | 0 | 9803.25 | 0 | 0 | 0 | 0
2022063006 | 5 | 0.54633 | 43706.4 | 0 | 0 | 0.37552 | 13143.2 | 0 | 0 | 40000 | 0 | 3706.4 | 9436.8 | 0 | 0 | 9436.8 | 0 | 0 | 0 | 0
2022063007 | 5 | 0.55722 | 44577.6 | 0 | 0 | 0.36842 | 12894.7 | 0.00391 | 54.74 | 40000 | 0 | 4577.6 | 8317.1 | 0 | 54.74 | 8371.84 | 0 | 0 | 0 | 0
2022063008 | 5 | 0.5756 | 46048 | 0 | 0 | 0.3221 | 11273.5 | 0.17365 | 2431.1 | 40000 | 0 | 6048 | 5225.5 | 0 | 2431.1 | 7656.6 | 0 | 0 | 0 | 0
2022063009 | 5 | 0.6114 | 48912 | 0 | 0 | 0.21787 | 7625.45 | 0.56603 | 7924.42 | 40000 | 0 | 7625.45 | 0 | 1286.55 | 6637.87 | 6637.87 | 0 | 0 | 0 | 0
2022063010 | 5 | 0.6574 | 52592 | 0 | 0 | 0.22743 | 7960.05 | 0.70272 | 9838.08 | 40000 | 0 | 7960.05 | 0 | 4631.95 | 5206.13 | 5206.13 | 0 | 0 | 0 | 0
2022063011 | 5 | 0.7045 | 56360 | 0 | 0 | 0.21974 | 7690.9 | 0.74304 | 10402.56 | 40000 | 0 | 7690.9 | 0 | 8669.1 | 1733.46 | 1733.46 | 0 | 0 | 0 | 0
2022063012 | 5 | 0.74573 | 59658.4 | 0 | 0 | 0.14957 | 5234.95 | 0.74266 | 10397.24 | 40000 | 0 | 5234.95 | 0 | 10397.24 | 0 | 0 | 4026.21 | 0 | 0 | 4026.21
2022063013 | 5 | 0.78594 | 62875.2 | 0 | 0 | 0.06874 | 2405.9 | 0.71589 | 10022.46 | 40000 | 0 | 2405.9 | 0 | 10022.46 | 0 | 0 | 10446.84 | 0 | 0 | 10446.84
2022063014 | 5 | 0.81678 | 65342.4 | 0 | 0 | 0.05388 | 1885.8 | 0.72739 | 10183.46 | 40000 | 0 | 1885.8 | 0 | 10183.46 | 0 | 0 | 13273.14 | 0 | 0 | 13273.14
2022063015 | 5 | 0.84233 | 67386.4 | 0 | 0 | 0.07254 | 2538.9 | 0.70929 | 9930.06 | 40000 | 0 | 2538.9 | 0 | 9930.06 | 0 | 0 | 14917.44 | 0 | 0 | 14917.44
2022063016 | 5 | 0.8609 | 68872 | 0 | 0 | 0.09851 | 3447.85 | 0.68609 | 9605.26 | 40000 | 0 | 3447.85 | 0 | 9605.26 | 0 | 0 | 15818.89 | 0 | 0 | 15818.89
2022063017 | 5 | 0.8734 | 69872 | 0 | 0 | 0.12128 | 4244.8 | 0.69857 | 9779.98 | 40000 | 0 | 4244.8 | 0 | 9779.98 | 0 | 0 | 15847.22 | 0 | 0 | 15847.22
2022063018 | 5 | 0.87179 | 69743.2 | 0 | 0 | 0.15296 | 5353.6 | 0.6416 | 8982.4 | 40000 | 0 | 5353.6 | 0 | 8982.4 | 0 | 0 | 15407.2 | 0 | 0 | 15407.2
2022063019 | 5 | 0.85663 | 68530.4 | 0 | 0 | 0.17746 | 6211.1 | 0.5738 | 8033.2 | 40000 | 0 | 6211.1 | 0 | 8033.2 | 0 | 0 | 14286.1 | 0 | 0 | 14286.1
2022063020 | 5 | 0.83351 | 66680.8 | 0 | 0 | 0.23738 | 8308.3 | 0.31473 | 4406.22 | 40000 | 0 | 8308.3 | 0 | 4406.22 | 0 | 0 | 13966.28 | 0 | 0 | 13966.28
2022063021 | 5 | 0.80754 | 64603.2 | 0 | 0 | 0.28777 | 10071.95 | 0.0473 | 662.2 | 40000 | 0 | 10071.95 | 0 | 662.2 | 0 | 0 | 13869.05 | 0 | 0 | 13869.05
2022063022 | 5 | 0.78596 | 62876.8 | 0 | 0 | 0.36674 | 12835.9 | 0.00249 | 34.86 | 40000 | 0 | 12835.9 | 0 | 34.86 | 0 | 0 | 10006.04 | 0 | 0 | 10006.04
2022063023 | 5 | 0.74577 | 59661.6 | 0 | 0 | 0.44702 | 15645.7 | 0.00115 | 16.1 | 40000 | 0 | 15645.7 | 0 | 16.1 | 0 | 0 | 3999.8 | 0 | 0 | 3999.8
2022063024 | 5 | 0.69869 | 55895.2 | 0 | 0 | 0.49255 | 17239.25 | 0 | 0 | 40000 | 0 | 15895.2 | 1344.05 | 0 | 0 | 1344.05 | 0 | 0 | 0 | 0
2022070101 | 6 | 0.65476 | 52380.8 | 0 | 0 | 0.50415 | 17645.25 | 0 | 0 | 40000 | 0 | 12380.8 | 5264.45 | 0 | 0 | 5264.45 | 0 | 0 | 0 | 0
2022070102 | 6 | 0.62047 | 49637.6 | 0 | 0 | 0.51688 | 18090.8 | 0 | 0 | 40000 | 0 | 9637.6 | 8453.2 | 0 | 0 | 8453.2 | 0 | 0 | 0 | 0
2022070103 | 6 | 0.5949 | 47592 | 0 | 0 | 0.50269 | 17594.15 | 0 | 0 | 40000 | 0 | 7592 | 10002.15 | 0 | 0 | 10002.15 | 0 | 0 | 0 | 0
2022070104 | 6 | 0.57765 | 46212 | 0 | 0 | 0.48146 | 16851.1 | 0 | 0 | 40000 | 0 | 6212 | 10639.1 | 0 | 0 | 10639.1 | 0 | 0 | 0 | 0
2022070105 | 6 | 0.56904 | 45523.2 | 0 | 0 | 0.44951 | 15732.85 | 0 | 0 | 40000 | 0 | 5523.2 | 10209.65 | 0 | 0 | 10209.65 | 0 | 0 | 0 | 0
2022070106 | 6 | 0.57409 | 45927.2 | 0 | 0 | 0.41023 | 14358.05 | 0 | 0 | 40000 | 0 | 5927.2 | 8430.85 | 0 | 0 | 8430.85 | 0 | 0 | 0 | 0
2022070107 | 6 | 0.57594 | 46075.2 | 0 | 0 | 0.36903 | 12916.05 | 0.00395 | 55.3 | 40000 | 0 | 6075.2 | 6840.85 | 0 | 55.3 | 6896.15 | 0 | 0 | 0 | 0
2022070108 | 6 | 0.58696 | 46956.8 | 0 | 0 | 0.31233 | 10931.55 | 0.17791 | 2490.74 | 40000 | 0 | 6956.8 | 3974.75 | 0 | 2490.74 | 6465.49 | 0 | 0 | 0 | 0
2022070109 | 6 | 0.61743 | 49394.4 | 0 | 0 | 0.26019 | 9106.65 | 0.51416 | 7198.24 | 40000 | 0 | 9106.65 | 0 | 287.75 | 6910.49 | 6910.49 | 0 | 0 | 0 | 0
2022070110 | 6 | 0.65645 | 52516 | 0 | 0 | 0.27632 | 9671.2 | 0.64751 | 9065.14 | 40000 | 0 | 9671.2 | 0 | 2844.8 | 6220.34 | 6220.34 | 0 | 0 | 0 | 0
2022070111 | 6 | 0.70092 | 56073.6 | 0 | 0 | 0.2 | 7000 | 0.69743 | 9764.02 | 40000 | 0 | 7000 | 0 | 9073.6 | 690.42 | 690.42 | 0 | 0 | 0 | 0
2022070112 | 6 | 0.74507 | 59605.6 | 0 | 0 | 0.11278 | 3947.3 | 0.7154 | 10015.6 | 40000 | 0 | 3947.3 | 0 | 10015.6 | 0 | 0 | 5642.7 | 0 | 0 | 5642.7
2022070113 | 6 | 0.78553 | 62842.4 | 0 | 0 | 0.06541 | 2289.35 | 0.69835 | 9776.9 | 40000 | 0 | 2289.35 | 0 | 9776.9 | 0 | 0 | 10776.15 | 0 | 0 | 10776.15
2022070114 | 6 | 0.82041 | 65632.8 | 0 | 0 | 0.06976 | 2441.6 | 0.68539 | 9595.46 | 40000 | 0 | 2441.6 | 0 | 9595.46 | 0 | 0 | 13595.74 | 0 | 0 | 13595.74
2022070115 | 6 | 0.84612 | 67689.6 | 0 | 0 | 0.10181 | 3563.35 | 0.69423 | 9719.22 | 40000 | 0 | 3563.35 | 0 | 9719.22 | 0 | 0 | 14407.03 | 0 | 0 | 14407.03
2022070116 | 6 | 0.86349 | 69079.2 | 0 | 0 | 0.15585 | 5454.75 | 0.69314 | 9703.96 | 40000 | 0 | 5454.75 | 0 | 9703.96 | 0 | 0 | 13920.49 | 0 | 0 | 13920.49
2022070117 | 6 | 0.87807 | 70245.6 | 0 | 0 | 0.21169 | 7409.15 | 0.67155 | 9401.7 | 40000 | 0 | 7409.15 | 0 | 9401.7 | 0 | 0 | 13434.75 | 0 | 0 | 13434.75
2022070118 | 6 | 0.88291 | 70632.8 | 0 | 0 | 0.22724 | 7953.4 | 0.62427 | 8739.78 | 40000 | 0 | 7953.4 | 0 | 8739.78 | 0 | 0 | 13939.62 | 0 | 0 | 13939.62
2022070119 | 6 | 0.87101 | 69680.8 | 0 | 0 | 0.27997 | 9798.95 | 0.57688 | 8076.32 | 40000 | 0 | 9798.95 | 0 | 8076.32 | 0 | 0 | 11805.53 | 0 | 0 | 11805.53
2022070120 | 6 | 0.84695 | 67756 | 0 | 0 | 0.35975 | 12591.25 | 0.34503 | 4830.42 | 40000 | 0 | 12591.25 | 0 | 4830.42 | 0 | 0 | 10334.33 | 0 | 0 | 10334.33
2022070121 | 6 | 0.81584 | 65267.2 | 0 | 0 | 0.40775 | 14271.25 | 0.04942 | 691.88 | 40000 | 0 | 14271.25 | 0 | 691.88 | 0 | 0 | 10304.07 | 0 | 0 | 10304.07
2022070122 | 6 | 0.79021 | 63216.8 | 0 | 0 | 0.45173 | 15810.55 | 0 | 0 | 40000 | 0 | 15810.55 | 0 | 0 | 0 | 0 | 7406.25 | 0 | 0 | 7406.25
2022070123 | 6 | 0.74942 | 59953.6 | 0 | 0 | 0.50164 | 17557.4 | 0 | 0 | 40000 | 0 | 17557.4 | 0 | 0 | 0 | 0 | 2396.2 | 0 | 0 | 2396.2
2022070124 | 6 | 0.70637 | 56509.6 | 0 | 0 | 0.51551 | 18042.85 | 0 | 0 | 40000 | 0 | 16509.6 | 1533.25 | 0 | 0 | 1533.25 | 0 | 0 | 0 | 0
2022070201 | 7 | 0.66491 | 53192.8 | 0 | 0 | 0.51987 | 18195.45 | 0 | 0 | 40000 | 0 | 13192.8 | 5002.65 | 0 | 0 | 5002.65 | 0 | 0 | 0 | 0
2022070202 | 7 | 0.63286 | 50628.8 | 0 | 0 | 0.47943 | 16780.05 | 0 | 0 | 40000 | 0 | 10628.8 | 6151.25 | 0 | 0 | 6151.25 | 0 | 0 | 0 | 0
2022070203 | 7 | 0.60386 | 48308.8 | 0 | 0 | 0.44396 | 15538.6 | 0 | 0 | 40000 | 0 | 8308.8 | 7229.8 | 0 | 0 | 7229.8 | 0 | 0 | 0 | 0
2022070204 | 7 | 0.58237 | 46589.6 | 0 | 0 | 0.42659 | 14930.65 | 0 | 0 | 40000 | 0 | 6589.6 | 8341.05 | 0 | 0 | 8341.05 | 0 | 0 | 0 | 0
2022070205 | 7 | 0.56921 | 45536.8 | 0 | 0 | 0.38449 | 13457.15 | 0 | 0 | 40000 | 0 | 5536.8 | 7920.35 | 0 | 0 | 7920.35 | 0 | 0 | 0 | 0
2022070206 | 7 | 0.56299 | 45039.2 | 0 | 0 | 0.35066 | 12273.1 | 0 | 0 | 40000 | 0 | 5039.2 | 7233.9 | 0 | 0 | 7233.9 | 0 | 0 | 0 | 0
2022070207 | 7 | 0.55883 | 44706.4 | 0 | 0 | 0.31509 | 11028.15 | 0.00418 | 58.52 | 40000 | 0 | 4706.4 | 6321.75 | 0 | 58.52 | 6380.27 | 0 | 0 | 0 | 0
2022070208 | 7 | 0.56868 | 45494.4 | 0 | 0 | 0.25513 | 8929.55 | 0.18295 | 2561.3 | 40000 | 0 | 5494.4 | 3435.15 | 0 | 2561.3 | 5996.45 | 0 | 0 | 0 | 0
2022070209 | 7 | 0.61017 | 48813.6 | 0 | 0 | 0.2125 | 7437.5 | 0.5795 | 8113 | 40000 | 0 | 7437.5 | 0 | 1376.1 | 6736.9 | 6736.9 | 0 | 0 | 0 | 0
2022070210 | 7 | 0.66423 | 53138.4 | 0 | 0 | 0.23039 | 8063.65 | 0.72292 | 10120.88 | 40000 | 0 | 8063.65 | 0 | 5074.75 | 5046.13 | 5046.13 | 0 | 0 | 0 | 0
2022070211 | 7 | 0.72004 | 57603.2 | 0 | 0 | 0.20035 | 7012.25 | 0.77985 | 10917.9 | 40000 | 0 | 7012.25 | 0 | 10590.95 | 326.95 | 326.95 | 0 | 0 | 0 | 0
2022070212 | 7 | 0.77062 | 61649.6 | 0 | 0 | 0.16172 | 5660.2 | 0.74773 | 10468.22 | 40000 | 0 | 5660.2 | 0 | 10468.22 | 0 | 0 | 5521.18 | 0 | 0 | 5521.18
2022070213 | 7 | 0.81154 | 64923.2 | 0 | 0 | 0.14155 | 4954.25 | 0.7233 | 10126.2 | 40000 | 0 | 4954.25 | 0 | 10126.2 | 0 | 0 | 9842.75 | 0 | 0 | 9842.75
2022070214 | 7 | 0.83944 | 67155.2 | 0 | 0 | 0.14412 | 5044.2 | 0.70918 | 9928.52 | 40000 | 0 | 5044.2 | 0 | 9928.52 | 0 | 0 | 12182.48 | 0 | 0 | 12182.48
2022070215 | 7 | 0.86059 | 68847.2 | 0 | 0 | 0.1744 | 6104 | 0.65983 | 9237.62 | 40000 | 0 | 6104 | 0 | 9237.62 | 0 | 0 | 13505.58 | 0 | 0 | 13505.58
2022070216 | 7 | 0.87927 | 70341.6 | 0 | 0 | 0.2376 | 8316 | 0.66104 | 9254.56 | 40000 | 0 | 8316 | 0 | 9254.56 | 0 | 0 | 12771.04 | 0 | 0 | 12771.04
2022070217 | 7 | 0.89218 | 71374.4 | 0 | 0 | 0.29942 | 10479.7 | 0.62115 | 8696.1 | 40000 | 0 | 10479.7 | 0 | 8696.1 | 0 | 0 | 12198.6 | 0 | 0 | 12198.6
2022070218 | 7 | 0.89476 | 71580.8 | 0 | 0 | 0.35644 | 12475.4 | 0.62428 | 8739.92 | 40000 | 0 | 12475.4 | 0 | 8739.92 | 0 | 0 | 10365.48 | 0 | 0 | 10365.48
2022070219 | 7 | 0.88144 | 70515.2 | 0 | 0 | 0.38347 | 13421.45 | 0.56295 | 7881.3 | 40000 | 0 | 13421.45 | 0 | 7881.3 | 0 | 0 | 9212.45 | 0 | 0 | 9212.45
2022070220 | 7 | 0.85382 | 68305.6 | 0 | 0 | 0.41607 | 14562.45 | 0.33207 | 4648.98 | 40000 | 0 | 14562.45 | 0 | 4648.98 | 0 | 0 | 9094.17 | 0 | 0 | 9094.17
2022070221 | 7 | 0.81996 | 65596.8 | 0 | 0 | 0.44569 | 15599.15 | 0.05044 | 706.16 | 40000 | 0 | 15599.15 | 0 | 706.16 | 0 | 0 | 9291.49 | 0 | 0 | 9291.49
2022070222 | 7 | 0.79405 | 63524 | 0 | 0 | 0.43638 | 15273.3 | 0 | 0 | 40000 | 0 | 15273.3 | 0 | 0 | 0 | 0 | 8250.7 | 0 | 0 | 8250.7
2022070223 | 7 | 0.75657 | 60525.6 | 0 | 0 | 0.41284 | 14449.4 | 0 | 0 | 40000 | 0 | 14449.4 | 0 | 0 | 0 | 0 | 6076.2 | 0 | 0 | 6076.2
2022070224 | 7 | 0.7137 | 57096 | 0 | 0 | 0.4024 | 14084 | 0 | 0 | 40000 | 0 | 14084 | 0 | 0 | 0 | 0 | 3012 | 0 | 0 | 3012
2022070301 | 1 | 0.6725 | 53800 | 0 | 0 | 0.39104 | 13686.4 | 0 | 0 | 40000 | 0 | 13686.4 | 0 | 0 | 0 | 0 | 113.6 | 0 | 0 | 113.6
2022070302 | 1 | 0.63894 | 51115.2 | 0 | 0 | 0.37113 | 12989.55 | 0 | 0 | 40000 | 0 | 11115.2 | 1874.35 | 0 | 0 | 1874.35 | 0 | 0 | 0 | 0
2022070303 | 1 | 0.61034 | 48827.2 | 0 | 0 | 0.36489 | 12771.15 | 0 | 0 | 40000 | 0 | 8827.2 | 3943.95 | 0 | 0 | 3943.95 | 0 | 0 | 0 | 0
2022070304 | 1 | 0.58947 | 47157.6 | 0 | 0 | 0.33838 | 11843.3 | 0 | 0 | 40000 | 0 | 7157.6 | 4685.7 | 0 | 0 | 4685.7 | 0 | 0 | 0 | 0
2022070305 | 1 | 0.5742 | 45936 | 0 | 0 | 0.31241 | 10934.35 | 0 | 0 | 40000 | 0 | 5936 | 4998.35 | 0 | 0 | 4998.35 | 0 | 0 | 0 | 0
2022070306 | 1 | 0.56723 | 45378.4 | 0 | 0 | 0.32146 | 11251.1 | 0 | 0 | 40000 | 0 | 5378.4 | 5872.7 | 0 | 0 | 5872.7 | 0 | 0 | 0 | 0
2022070307 | 1 | 0.5604 | 44832 | 0 | 0 | 0.30659 | 10730.65 | 0.00369 | 51.66 | 40000 | 0 | 4832 | 5898.65 | 0 | 51.66 | 5950.31 | 0 | 0 | 0 | 0
2022070308 | 1 | 0.5703 | 45624 | 0 | 0 | 0.28799 | 10079.65 | 0.16555 | 2317.7 | 40000 | 0 | 5624 | 4455.65 | 0 | 2317.7 | 6773.35 | 0 | 0 | 0 | 0
2022070309 | 1 | 0.61066 | 48852.8 | 0 | 0 | 0.27735 | 9707.25 | 0.54025 | 7563.5 | 40000 | 0 | 8852.8 | 854.45 | 0 | 7563.5 | 8417.95 | 0 | 0 | 0 | 0
2022070310 | 1 | 0.66477 | 53181.6 | 0 | 0 | 0.31375 | 10981.25 | 0.69238 | 9693.32 | 40000 | 0 | 10981.25 | 0 | 2200.35 | 7492.97 | 7492.97 | 0 | 0 | 0 | 0
2022070311 | 1 | 0.71684 | 57347.2 | 0 | 0 | 0.28317 | 9910.95 | 0.74938 | 10491.32 | 40000 | 0 | 9910.95 | 0 | 7436.25 | 3055.07 | 3055.07 | 0 | 0 | 0 | 0
2022070312 | 1 | 0.76958 | 61566.4 | 0 | 0 | 0.26982 | 9443.7 | 0.77014 | 10781.96 | 40000 | 0 | 9443.7 | 0 | 10781.96 | 0 | 0 | 1340.74 | 0 | 0 | 1340.74
2022070313 | 1 | 0.81554 | 65243.2 | 0 | 0 | 0.29894 | 10462.9 | 0.77511 | 10851.54 | 40000 | 0 | 10462.9 | 0 | 10851.54 | 0 | 0 | 3928.76 | 0 | 0 | 3928.76
2022070314 | 1 | 0.85243 | 68194.4 | 0 | 0 | 0.33551 | 11742.85 | 0.73067 | 10229.38 | 40000 | 0 | 11742.85 | 0 | 10229.38 | 0 | 0 | 6222.17 | 0 | 0 | 6222.17
2022070315 | 1 | 0.88014 | 70411.2 | 0 | 0 | 0.38457 | 13459.95 | 0.72347 | 10128.58 | 40000 | 0 | 13459.95 | 0 | 10128.58 | 0 | 0 | 6822.67 | 0 | 0 | 6822.67
2022070316 | 1 | 0.89993 | 71994.4 | 0 | 0 | 0.43088 | 15080.8 | 0.67512 | 9451.68 | 40000 | 0 | 15080.8 | 0 | 9451.68 | 0 | 0 | 7461.92 | 0 | 0 | 7461.92
2022070317 | 1 | 0.90634 | 72507.2 | 0 | 0 | 0.46265 | 16192.75 | 0.63889 | 8944.46 | 40000 | 0 | 16192.75 | 0 | 8944.46 | 0 | 0 | 7369.99 | 0 | 0 | 7369.99
2022070318 | 1 | 0.9062 | 72496 | 0 | 0 | 0.51728 | 18104.8 | 0.58205 | 8148.7 | 40000 | 0 | 18104.8 | 0 | 8148.7 | 0 | 0 | 6242.5 | 0 | 0 | 6242.5
2022070319 | 1 | 0.89155 | 71324 | 0 | 0 | 0.54765 | 19167.75 | 0.47771 | 6687.94 | 40000 | 0 | 19167.75 | 0 | 6687.94 | 0 | 0 | 5468.31 | 0 | 0 | 5468.31
2022070320 | 1 | 0.86134 | 68907.2 | 0 | 0 | 0.54148 | 18951.8 | 0.27697 | 3877.58 | 40000 | 0 | 18951.8 | 0 | 3877.58 | 0 | 0 | 6077.82 | 0 | 0 | 6077.82
2022070321 | 1 | 0.82025 | 65620 | 0 | 0 | 0.52573 | 18400.55 | 0.04579 | 641.06 | 40000 | 0 | 18400.55 | 0 | 641.06 | 0 | 0 | 6578.39 | 0 | 0 | 6578.39
2022070322 | 1 | 0.78783 | 63026.4 | 0 | 0 | 0.4574 | 16009 | 0 | 0 | 40000 | 0 | 16009 | 0 | 0 | 0 | 0 | 7017.4 | 0 | 0 | 7017.4
2022070323 | 1 | 0.7474 | 59792 | 0 | 0 | 0.42099 | 14734.65 | 0 | 0 | 40000 | 0 | 14734.65 | 0 | 0 | 0 | 0 | 5057.35 | 0 | 0 | 5057.35
2022070324 | 1 | 0.70644 | 56515.2 | 0 | 0 | 0.39814 | 13934.9 | 0 | 0 | 40000 | 0 | 13934.9 | 0 | 0 | 0 | 0 | 2580.3 | 0 | 0 | 2580.3
2022070401 | 2 | 0.66602 | 53281.6 | 0 | 0 | 0.41031 | 14360.85 | 0 | 0 | 40000 | 0 | 13281.6 | 1079.25 | 0 | 0 | 1079.25 | 0 | 0 | 0 | 0
2022070402 | 2 | 0.63242 | 50593.6 | 0 | 0 | 0.4259 | 14906.5 | 0 | 0 | 40000 | 0 | 10593.6 | 4312.9 | 0 | 0 | 4312.9 | 0 | 0 | 0 | 0
2022070403 | 2 | 0.60905 | 48724 | 0 | 0 | 0.44508 | 15577.8 | 0 | 0 | 40000 | 0 | 8724 | 6853.8 | 0 | 0 | 6853.8 | 0 | 0 | 0 | 0
2022070404 | 2 | 0.59214 | 47371.2 | 0 | 0 | 0.4601 | 16103.5 | 0 | 0 | 40000 | 0 | 7371.2 | 8732.3 | 0 | 0 | 8732.3 | 0 | 0 | 0 | 0
2022070405 | 2 | 0.58278 | 46622.4 | 0 | 0 | 0.4715 | 16502.5 | 0 | 0 | 40000 | 0 | 6622.4 | 9880.1 | 0 | 0 | 9880.1 | 0 | 0 | 0 | 0
2022070406 | 2 | 0.57777 | 46221.6 | 0 | 0 | 0.46717 | 16350.95 | 0 | 0 | 40000 | 0 | 6221.6 | 10129.35 | 0 | 0 | 10129.35 | 0 | 0 | 0 | 0
2022070407 | 2 | 0.56933 | 45546.4 | 0 | 0 | 0.44718 | 15651.3 | 0.00392 | 54.88 | 40000 | 0 | 5546.4 | 10104.9 | 0 | 54.88 | 10159.78 | 0 | 0 | 0 | 0
2022070408 | 2 | 0.57522 | 46017.6 | 0 | 0 | 0.40271 | 14094.85 | 0.17231 | 2412.34 | 40000 | 0 | 6017.6 | 8077.25 | 0 | 2412.34 | 10489.59 | 0 | 0 | 0 | 0
2022070409 | 2 | 0.61514 | 49211.2 | 0 | 0 | 0.4116 | 14406 | 0.54636 | 7649.04 | 40000 | 0 | 9211.2 | 5194.8 | 0 | 7649.04 | 12843.84 | 0 | 0 | 0 | 0
2022070410 | 2 | 0.66982 | 53585.6 | 0 | 0 | 0.4852 | 16982 | 0.71714 | 10039.96 | 40000 | 0 | 13585.6 | 3396.4 | 0 | 10039.96 | 13436.36 | 0 | 0 | 0 | 0
2022070411 | 2 | 0.72472 | 57977.6 | 0 | 0 | 0.46773 | 16370.55 | 0.77393 | 10835.02 | 40000 | 0 | 16370.55 | 0 | 1607.05 | 9227.97 | 9227.97 | 0 | 0 | 0 | 0
2022070412 | 2 | 0.77777 | 62221.6 | 0 | 0 | 0.42975 | 15041.25 | 0.7795 | 10913 | 40000 | 0 | 15041.25 | 0 | 7180.35 | 3732.65 | 3732.65 | 0 | 0 | 0 | 0
2022070413 | 2 | 0.8233 | 65864 | 0 | 0 | 0.40917 | 14320.95 | 0.7783 | 10896.2 | 40000 | 0 | 14320.95 | 0 | 10896.2 | 0 | 0 | 646.85 | 0 | 0 | 646.85
2022070414 | 2 | 0.86155 | 68924 | 0 | 0 | 0.41251 | 14437.85 | 0.75314 | 10543.96 | 40000 | 0 | 14437.85 | 0 | 10543.96 | 0 | 0 | 3942.19 | 0 | 0 | 3942.19
2022070415 | 2 | 0.88939 | 71151.2 | 0 | 0 | 0.41527 | 14534.45 | 0.70756 | 9905.84 | 40000 | 0 | 14534.45 | 0 | 9905.84 | 0 | 0 | 6710.91 | 0 | 0 | 6710.91
2022070416 | 2 | 0.91036 | 72828.8 | 0 | 0 | 0.42682 | 14938.7 | 0.69263 | 9696.82 | 40000 | 0 | 14938.7 | 0 | 9696.82 | 0 | 0 | 8193.28 | 0 | 0 | 8193.28
2022070417 | 2 | 0.9247 | 73976 | 0 | 0 | 0.45855 | 16049.25 | 0.69429 | 9720.06 | 40000 | 0 | 16049.25 | 0 | 9720.06 | 0 | 0 | 8206.69 | 0 | 0 | 8206.69
2022070418 | 2 | 0.92904 | 74323.2 | 0 | 0 | 0.50176 | 17561.6 | 0.65271 | 9137.94 | 40000 | 0 | 17561.6 | 0 | 9137.94 | 0 | 0 | 7623.66 | 0 | 0 | 7623.66
2022070419 | 2 | 0.91511 | 73208.8 | 0 | 0 | 0.54474 | 19065.9 | 0.48793 | 6831.02 | 40000 | 0 | 19065.9 | 0 | 6831.02 | 0 | 0 | 7311.88 | 0 | 0 | 7311.88
2022070420 | 2 | 0.88514 | 70811.2 | 0 | 0 | 0.59739 | 20908.65 | 0.19321 | 2704.94 | 40000 | 0 | 20908.65 | 0 | 2704.94 | 0 | 0 | 7197.61 | 0 | 0 | 7197.61
2022070421 | 2 | 0.84449 | 67559.2 | 0 | 0 | 0.60237 | 21082.95 | 0.03194 | 447.16 | 40000 | 0 | 21082.95 | 0 | 447.16 | 0 | 0 | 6029.09 | 0 | 0 | 6029.09
2022070422 | 2 | 0.80639 | 64511.2 | 0 | 0 | 0.57747 | 20211.45 | 0.0002 | 2.8 | 40000 | 0 | 20211.45 | 0 | 2.8 | 0 | 0 | 4296.95 | 0 | 0 | 4296.95
2022070423 | 2 | 0.76832 | 61465.6 | 0 | 0 | 0.58179 | 20362.65 | 0 | 0 | 40000 | 0 | 20362.65 | 0 | 0 | 0 | 0 | 1102.95 | 0 | 0 | 1102.95
2022070424 | 2 | 0.7269 | 58152 | 0 | 0 | 0.60397 | 21138.95 | 0 | 0 | 40000 | 0 | 18152 | 2986.95 | 0 | 0 | 2986.95 | 0 | 0 | 0 | 0
2022070501 | 3 | 0.68335 | 54668 | 0 | 0 | 0.61303 | 21456.05 | 0 | 0 | 40000 | 0 | 14668 | 6788.05 | 0 | 0 | 6788.05 | 0 | 0 | 0 | 0
2022070502 | 3 | 0.64645 | 51716 | 0 | 0 | 0.57126 | 19994.1 | 0 | 0 | 40000 | 0 | 11716 | 8278.1 | 0 | 0 | 8278.1 | 0 | 0 | 0 | 0
2022070503 | 3 | 0.61716 | 49372.8 | 0 | 0 | 0.53638 | 18773.3 | 0 | 0 | 40000 | 0 | 9372.8 | 9400.5 | 0 | 0 | 9400.5 | 0 | 0 | 0 | 0
2022070504 | 3 | 0.60325 | 48260 | 0 | 0 | 0.5285 | 18497.5 | 0 | 0 | 40000 | 0 | 8260 | 10237.5 | 0 | 0 | 10237.5 | 0 | 0 | 0 | 0
2022070505 | 3 | 0.59483 | 47586.4 | 0 | 0 | 0.53087 | 18580.45 | 0 | 0 | 40000 | 0 | 7586.4 | 10994.05 | 0 | 0 | 10994.05 | 0 | 0 | 0 | 0
2022070506 | 3 | 0.60256 | 48204.8 | 0 | 0 | 0.5197 | 18189.5 | 0 | 0 | 40000 | 0 | 8204.8 | 9984.7 | 0 | 0 | 9984.7 | 0 | 0 | 0 | 0
2022070507 | 3 | 0.61171 | 48936.8 | 0 | 0 | 0.52152 | 18253.2 | 0.00384 | 53.76 | 40000 | 0 | 8936.8 | 9316.4 | 0 | 53.76 | 9370.16 | 0 | 0 | 0 | 0
2022070508 | 3 | 0.62922 | 50337.6 | 0 | 0 | 0.48407 | 16942.45 | 0.16011 | 2241.54 | 40000 | 0 | 10337.6 | 6604.85 | 0 | 2241.54 | 8846.39 | 0 | 0 | 0 | 0
2022070509 | 3 | 0.66951 | 53560.8 | 0 | 0 | 0.50557 | 17694.95 | 0.46078 | 6450.92 | 40000 | 0 | 13560.8 | 4134.15 | 0 | 6450.92 | 10585.07 | 0 | 0 | 0 | 0
2022070510 | 3 | 0.71808 | 57446.4 | 0 | 0 | 0.55598 | 19459.3 | 0.58569 | 8199.66 | 40000 | 0 | 17446.4 | 2012.9 | 0 | 8199.66 | 10212.56 | 0 | 0 | 0 | 0
2022070511 | 3 | 0.76903 | 61522.4 | 0 | 0 | 0.50663 | 17732.05 | 0.67767 | 9487.38 | 40000 | 0 | 17732.05 | 0 | 3790.35 | 5697.03 | 5697.03 | 0 | 0 | 0 | 0
2022070512 | 3 | 0.81994 | 65595.2 | 0 | 0 | 0.4233 | 14815.5 | 0.7578 | 10609.2 | 40000 | 0 | 14815.5 | 0 | 10609.2 | 0 | 0 | 170.5 | 0 | 0 | 170.5
2022070513 | 3 | 0.86382 | 69105.6 | 0 | 0 | 0.35037 | 12262.95 | 0.75506 | 10570.84 | 40000 | 0 | 12262.95 | 0 | 10570.84 | 0 | 0 | 6271.81 | 0 | 0 | 6271.81
2022070514 | 3 | 0.90618 | 72494.4 | 0 | 0 | 0.31601 | 11060.35 | 0.76369 | 10691.66 | 40000 | 0 | 11060.35 | 0 | 10691.66 | 0 | 0 | 10742.39 | 0 | 0 | 10742.39
2022070515 | 3 | 0.93618 | 74894.4 | 0 | 0 | 0.32092 | 11232.2 | 0.77218 | 10810.52 | 40000 | 0 | 11232.2 | 0 | 10810.52 | 0 | 0 | 12851.68 | 0 | 0 | 12851.68
2022070516 | 3 | 0.9572 | 76576 | 0 | 0 | 0.35538 | 12438.3 | 0.72058 | 10088.12 | 40000 | 0 | 12438.3 | 0 | 10088.12 | 0 | 0 | 14049.58 | 0 | 0 | 14049.58
2022070517 | 3 | 0.97053 | 77642.4 | 0 | 0 | 0.38648 | 13526.8 | 0.67321 | 9424.94 | 40000 | 0 | 13526.8 | 0 | 9424.94 | 0 | 0 | 14690.66 | 0 | 0 | 14690.66
2022070518 | 3 | 0.96737 | 77389.6 | 0 | 0 | 0.4083 | 14290.5 | 0.53431 | 7480.34 | 40000 | 0 | 14290.5 | 0 | 7480.34 | 0 | 0 | 15618.76 | 0 | 0 | 15618.76
2022070519 | 3 | 0.95251 | 76200.8 | 0 | 0 | 0.44433 | 15551.55 | 0.37185 | 5205.9 | 40000 | 0 | 15551.55 | 0 | 5205.9 | 0 | 0 | 15443.35 | 0 | 0 | 15443.35
2022070520 | 3 | 0.92724 | 74179.2 | 0 | 0 | 0.49213 | 17224.55 | 0.20668 | 2893.52 | 40000 | 0 | 17224.55 | 0 | 2893.52 | 0 | 0 | 14061.13 | 0 | 0 | 14061.13
2022070521 | 3 | 0.88702 | 70961.6 | 0 | 0 | 0.47915 | 16770.25 | 0.0212 | 296.8 | 40000 | 0 | 16770.25 | 0 | 296.8 | 0 | 0 | 13894.55 | 0 | 0 | 13894.55
2022070522 | 3 | 0.85444 | 68355.2 | 0 | 0 | 0.47365 | 16577.75 | 0 | 0 | 40000 | 0 | 16577.75 | 0 | 0 | 0 | 0 | 11777.45 | 0 | 0 | 11777.45
2022070523 | 3 | 0.80104 | 64083.2 | 0 | 0 | 0.45066 | 15773.1 | 0 | 0 | 40000 | 0 | 15773.1 | 0 | 0 | 0 | 0 | 8310.1 | 0 | 0 | 8310.1
2022070524 | 3 | 0.74587 | 59669.6 | 0 | 0 | 0.44359 | 15525.65 | 0 | 0 | 40000 | 0 | 15525.65 | 0 | 0 | 0 | 0 | 4143.95 | 0 | 0 | 4143.95
2022070601 | 4 | 0.69676 | 55740.8 | 0 | 0 | 0.4649 | 16271.5 | 0 | 0 | 40000 | 0 | 15740.8 | 530.7 | 0 | 0 | 530.7 | 0 | 0 | 0 | 0
2022070602 | 4 | 0.65897 | 52717.6 | 0 | 0 | 0.50324 | 17613.4 | 0 | 0 | 40000 | 0 | 12717.6 | 4895.8 | 0 | 0 | 4895.8 | 0 | 0 | 0 | 0
2022070603 | 4 | 0.62933 | 50346.4 | 0 | 0 | 0.49791 | 17426.85 | 0 | 0 | 40000 | 0 | 10346.4 | 7080.45 | 0 | 0 | 7080.45 | 0 | 0 | 0 | 0
2022070604 | 4 | 0.61124 | 48899.2 | 0 | 0 | 0.50134 | 17546.9 | 0 | 0 | 40000 | 0 | 8899.2 | 8647.7 | 0 | 0 | 8647.7 | 0 | 0 | 0 | 0
2022070605 | 4 | 0.60467 | 48373.6 | 0 | 0 | 0.50536 | 17687.6 | 0 | 0 | 40000 | 0 | 8373.6 | 9314 | 0 | 0 | 9314 | 0 | 0 | 0 | 0
2022070606 | 4 | 0.61008 | 48806.4 | 0 | 0 | 0.50579 | 17702.65 | 0 | 0 | 40000 | 0 | 8806.4 | 8896.25 | 0 | 0 | 8896.25 | 0 | 0 | 0 | 0
2022070607 | 4 | 0.6221 | 49768 | 0 | 0 | 0.46902 | 16415.7 | 0.00303 | 42.42 | 40000 | 0 | 9768 | 6647.7 | 0 | 42.42 | 6690.12 | 0 | 0 | 0 | 0
2022070608 | 4 | 0.63221 | 50576.8 | 0 | 0 | 0.42237 | 14782.95 | 0.15871 | 2221.94 | 40000 | 0 | 10576.8 | 4206.15 | 0 | 2221.94 | 6428.09 | 0 | 0 | 0 | 0
2022070609 | 4 | 0.66919 | 53535.2 | 0 | 0 | 0.41782 | 14623.7 | 0.44188 | 6186.32 | 40000 | 0 | 13535.2 | 1088.5 | 0 | 6186.32 | 7274.82 | 0 | 0 | 0 | 0
2022070610 | 4 | 0.72153 | 57722.4 | 0 | 0 | 0.47718 | 16701.3 | 0.61049 | 8546.86 | 40000 | 0 | 16701.3 | 0 | 1021.1 | 7525.76 | 7525.76 | 0 | 0 | 0 | 0
2022070611 | 4 | 0.77514 | 62011.2 | 0 | 0 | 0.41138 | 14398.3 | 0.73125 | 10237.5 | 40000 | 0 | 14398.3 | 0 | 7612.9 | 2624.6 | 2624.6 | 0 | 0 | 0 | 0
2022070612 | 4 | 0.82394 | 65915.2 | 0 | 0 | 0.31651 | 11077.85 | 0.74435 | 10420.9 | 40000 | 0 | 11077.85 | 0 | 10420.9 | 0 | 0 | 4416.45 | 0 | 0 | 4416.45
2022070613 | 4 | 0.87202 | 69761.6 | 0 | 0 | 0.25186 | 8815.1 | 0.73279 | 10259.06 | 40000 | 0 | 8815.1 | 0 | 10259.06 | 0 | 0 | 10687.44 | 0 | 0 | 10687.44
2022070614 | 4 | 0.91515 | 73212 | 0 | 0 | 0.2383 | 8340.5 | 0.77014 | 10781.96 | 40000 | 0 | 8340.5 | 0 | 10781.96 | 0 | 0 | 14089.54 | 0 | 0 | 14089.54
2022070615 | 4 | 0.94538 | 75630.4 | 0 | 0 | 0.26801 | 9380.35 | 0.76885 | 10763.9 | 40000 | 0 | 9380.35 | 0 | 10763.9 | 0 | 0 | 15486.15 | 0 | 0 | 15486.15
2022070616 | 4 | 0.96066 | 76852.8 | 0 | 0 | 0.30124 | 10543.4 | 0.75216 | 10530.24 | 40000 | 0 | 10543.4 | 0 | 10530.24 | 0 | 0 | 15779.16 | 0 | 0 | 15779.16
2022070617 | 4 | 0.96538 | 77230.4 | 0 | 0 | 0.32892 | 11512.2 | 0.70794 | 9911.16 | 40000 | 0 | 11512.2 | 0 | 9911.16 | 0 | 0 | 15807.04 | 0 | 0 | 15807.04
2022070618 | 4 | 0.96191 | 76952.8 | 0 | 0 | 0.35223 | 12328.05 | 0.67745 | 9484.3 | 40000 | 0 | 12328.05 | 0 | 9484.3 | 0 | 0 | 15140.45 | 0 | 0 | 15140.45
2022070619 | 4 | 0.94751 | 75800.8 | 0 | 0 | 0.3646 | 12761 | 0.5782 | 8094.8 | 40000 | 0 | 12761 | 0 | 8094.8 | 0 | 0 | 14945 | 0 | 0 | 14945
2022070620 | 4 | 0.92105 | 73684 | 0 | 0 | 0.36949 | 12932.15 | 0.33405 | 4676.7 | 40000 | 0 | 12932.15 | 0 | 4676.7 | 0 | 0 | 16075.15 | 0 | 0 | 16075.15
2022070621 | 4 | 0.88553 | 70842.4 | 0 | 0 | 0.37787 | 13225.45 | 0.04011 | 561.54 | 40000 | 0 | 13225.45 | 0 | 561.54 | 0 | 0 | 17055.41 | 0 | 0 | 17055.41
2022070622 | 4 | 0.85246 | 68196.8 | 0 | 0 | 0.41923 | 14673.05 | 0 | 0 | 40000 | 0 | 14673.05 | 0 | 0 | 0 | 0 | 13523.75 | 0 | 0 | 13523.75
2022070623 | 4 | 0.80392 | 64313.6 | 0 | 0 | 0.49047 | 17166.45 | 0 | 0 | 40000 | 0 | 17166.45 | 0 | 0 | 0 | 0 | 7147.15 | 0 | 0 | 7147.15
2022070624 | 4 | 0.75072 | 60057.6 | 0 | 0 | 0.53156 | 18604.6 | 0 | 0 | 40000 | 0 | 18604.6 | 0 | 0 | 0 | 0 | 1453 | 0 | 0 | 1453
2022070701 | 5 | 0.7038 | 56304 | 0 | 0 | 0.5194 | 18179 | 0 | 0 | 40000 | 0 | 16304 | 1875 | 0 | 0 | 1875 | 0 | 0 | 0 | 0
2022070702 | 5 | 0.66677 | 53341.6 | 0 | 0 | 0.51486 | 18020.1 | 0 | 0 | 40000 | 0 | 13341.6 | 4678.5 | 0 | 0 | 4678.5 | 0 | 0 | 0 | 0
2022070703 | 5 | 0.64212 | 51369.6 | 0 | 0 | 0.52139 | 18248.65 | 0 | 0 | 40000 | 0 | 11369.6 | 6879.05 | 0 | 0 | 6879.05 | 0 | 0 | 0 | 0
2022070704 | 5 | 0.62531 | 50024.8 | 0 | 0 | 0.50642 | 17724.7 | 0 | 0 | 40000 | 0 | 10024.8 | 7699.9 | 0 | 0 | 7699.9 | 0 | 0 | 0 | 0
2022070705 | 5 | 0.61578 | 49262.4 | 0 | 0 | 0.49937 | 17477.95 | 0 | 0 | 40000 | 0 | 9262.4 | 8215.55 | 0 | 0 | 8215.55 | 0 | 0 | 0 | 0
2022070706 | 5 | 0.61729 | 49383.2 | 0 | 0 | 0.47599 | 16659.65 | 0 | 0 | 40000 | 0 | 9383.2 | 7276.45 | 0 | 0 | 7276.45 | 0 | 0 | 0 | 0
2022070707 | 5 | 0.62342 | 49873.6 | 0 | 0 | 0.44554 | 15593.9 | 0.00332 | 46.48 | 40000 | 0 | 9873.6 | 5720.3 | 0 | 46.48 | 5766.78 | 0 | 0 | 0 | 0
2022070708 | 5 | 0.63821 | 51056.8 | 0 | 0 | 0.40126 | 14044.1 | 0.17925 | 2509.5 | 40000 | 0 | 11056.8 | 2987.3 | 0 | 2509.5 | 5496.8 | 0 | 0 | 0 | 0
2022070709 | 5 | 0.67767 | 54213.6 | 0 | 0 | 0.3502 | 12257 | 0.56677 | 7934.78 | 40000 | 0 | 12257 | 0 | 1956.6 | 5978.18 | 5978.18 | 0 | 0 | 0 | 0
2022070710 | 5 | 0.72584 | 58067.2 | 0 | 0 | 0.37102 | 12985.7 | 0.74891 | 10484.74 | 40000 | 0 | 12985.7 | 0 | 5081.5 | 5403.24 | 5403.24 | 0 | 0 | 0 | 0
2022070711 | 5 | 0.77751 | 62200.8 | 0 | 0 | 0.30743 | 10760.05 | 0.78752 | 11025.28 | 40000 | 0 | 10760.05 | 0 | 11025.28 | 0 | 0 | 415.47 | 0 | 0 | 415.47
2022070712 | 5 | 0.8295 | 66360 | 0 | 0 | 0.225 | 7875 | 0.78921 | 11048.94 | 40000 | 0 | 7875 | 0 | 11048.94 | 0 | 0 | 7436.06 | 0 | 0 | 7436.06
2022070713 | 5 | 0.87826 | 70260.8 | 0 | 0 | 0.18832 | 6591.2 | 0.78813 | 11033.82 | 40000 | 0 | 6591.2 | 0 | 11033.82 | 0 | 0 | 12635.78 | 0 | 0 | 12635.78
2022070714 | 5 | 0.91842 | 73473.6 | 0 | 0 | 0.18222 | 6377.7 | 0.77497 | 10849.58 | 40000 | 0 | 6377.7 | 0 | 10849.58 | 0 | 0 | 16246.32 | 0 | 0 | 16246.32
2022070715 | 5 | 0.94791 | 75832.8 | 0 | 0 | 0.17392 | 6087.2 | 0.76365 | 10691.1 | 40000 | 0 | 6087.2 | 0 | 10691.1 | 0 | 0 | 19054.5 | 0 | 0 | 19054.5
2022070716 | 5 | 0.96245 | 76996 | 0 | 0 | 0.18917 | 6620.95 | 0.74197 | 10387.58 | 40000 | 0 | 6620.95 | 0 | 10387.58 | 0 | 0 | 19987.47 | 0 | 0 | 19987.47
2022070717 | 5 | 0.96663 | 77330.4 | 0 | 0 | 0.2144 | 7504 | 0.7319 | 10246.6 | 40000 | 0 | 7504 | 0 | 10246.6 | 0 | 0 | 19579.8 | 0 | 0 | 19579.8
2022070718 | 5 | 0.96091 | 76872.8 | 0 | 0 | 0.25655 | 8979.25 | 0.69819 | 9774.66 | 40000 | 0 | 8979.25 | 0 | 9774.66 | 0 | 0 | 18118.89 | 0 | 0 | 18118.89
2022070719 | 5 | 0.94772 | 75817.6 | 0 | 0 | 0.29378 | 10282.3 | 0.59639 | 8349.46 | 40000 | 0 | 10282.3 | 0 | 8349.46 | 0 | 0 | 17185.84 | 0 | 0 | 17185.84
2022070720 | 5 | 0.92127 | 73701.6 | 0 | 0 | 0.31118 | 10891.3 | 0.34052 | 4767.28 | 40000 | 0 | 10891.3 | 0 | 4767.28 | 0 | 0 | 18043.02 | 0 | 0 | 18043.02
2022070721 | 5 | 0.88715 | 70972 | 0 | 0 | 0.31 | 10850 | 0.03385 | 473.9 | 40000 | 0 | 10850 | 0 | 473.9 | 0 | 0 | 19648.1 | 0 | 0 | 19648.1
2022070722 | 5 | 0.85438 | 68350.4 | 0 | 0 | 0.36572 | 12800.2 | 0 | 0 | 40000 | 0 | 12800.2 | 0 | 0 | 0 | 0 | 15550.2 | 0 | 0 | 15550.2
2022070723 | 5 | 0.80444 | 64355.2 | 0 | 0 | 0.43936 | 15377.6 | 0 | 0 | 40000 | 0 | 15377.6 | 0 | 0 | 0 | 0 | 8977.6 | 0 | 0 | 8977.6
2022070724 | 5 | 0.75104 | 60083.2 | 0 | 0 | 0.46688 | 16340.8 | 0 | 0 | 40000 | 0 | 16340.8 | 0 | 0 | 0 | 0 | 3742.4 | 0 | 0 | 3742.4
2022070801 | 6 | 0.70287 | 56229.6 | 0 | 0 | 0.48337 | 16917.95 | 0 | 0 | 40000 | 0 | 16229.6 | 688.35 | 0 | 0 | 688.35 | 0 | 0 | 0 | 0
2022070802 | 6 | 0.66428 | 53142.4 | 0 | 0 | 0.47252 | 16538.2 | 0 | 0 | 40000 | 0 | 13142.4 | 3395.8 | 0 | 0 | 3395.8 | 0 | 0 | 0 | 0
2022070803 | 6 | 0.63647 | 50917.6 | 0 | 0 | 0.42474 | 14865.9 | 0 | 0 | 40000 | 0 | 10917.6 | 3948.3 | 0 | 0 | 3948.3 | 0 | 0 | 0 | 0
2022070804 | 6 | 0.62035 | 49628 | 0 | 0 | 0.3838 | 13433 | 0 | 0 | 40000 | 0 | 9628 | 3805 | 0 | 0 | 3805 | 0 | 0 | 0 | 0
2022070805 | 6 | 0.61237 | 48989.6 | 0 | 0 | 0.36618 | 12816.3 | 0 | 0 | 40000 | 0 | 8989.6 | 3826.7 | 0 | 0 | 3826.7 | 0 | 0 | 0 | 0
2022070806 | 6 | 0.61812 | 49449.6 | 0 | 0 | 0.38169 | 13359.15 | 0 | 0 | 40000 | 0 | 9449.6 | 3909.55 | 0 | 0 | 3909.55 | 0 | 0 | 0 | 0
2022070807 | 6 | 0.61994 | 49595.2 | 0 | 0 | 0.37557 | 13144.95 | 0.00334 | 46.76 | 40000 | 0 | 9595.2 | 3549.75 | 0 | 46.76 | 3596.51 | 0 | 0 | 0 | 0
2022070808 | 6 | 0.63559 | 50847.2 | 0 | 0 | 0.32751 | 11462.85 | 0.16474 | 2306.36 | 40000 | 0 | 10847.2 | 615.65 | 0 | 2306.36 | 2922.01 | 0 | 0 | 0 | 0
2022070809 | 6 | 0.67677 | 54141.6 | 0 | 0 | 0.27585 | 9654.75 | 0.54854 | 7679.56 | 40000 | 0 | 9654.75 | 0 | 4486.85 | 3192.71 | 3192.71 | 0 | 0 | 0 | 0
2022070810 | 6 | 0.72895 | 58316 | 0 | 0 | 0.27214 | 9524.9 | 0.7503 | 10504.2 | 40000 | 0 | 9524.9 | 0 | 8791.1 | 1713.1 | 1713.1 | 0 | 0 | 0 | 0
2022070811 | 6 | 0.78441 | 62752.8 | 0 | 0 | 0.18843 | 6595.05 | 0.77418 | 10838.52 | 40000 | 0 | 6595.05 | 0 | 10838.52 | 0 | 0 | 5319.23 | 0 | 0 | 5319.23
2022070812 | 6 | 0.84059 | 67247.2 | 0 | 0 | 0.1047 | 3664.5 | 0.7739 | 10834.6 | 40000 | 0 | 3664.5 | 0 | 10834.6 | 0 | 0 | 12748.1 | 0 | 0 | 12748.1
2022070813 | 6 | 0.8896 | 71168 | 0 | 0 | 0.06747 | 2361.45 | 0.76019 | 10642.66 | 40000 | 0 | 2361.45 | 0 | 10642.66 | 0 | 0 | 18163.89 | 0 | 0 | 18163.89
2022070814 | 6 | 0.92929 | 74343.2 | 0 | 0 | 0.07267 | 2543.45 | 0.76418 | 10698.52 | 40000 | 0 | 2543.45 | 0 | 10698.52 | 0 | 0 | 21101.23 | 0 | 0 | 21101.23
2022070815 | 6 | 0.95826 | 76660.8 | 0 | 0 | 0.09388 | 3285.8 | 0.74286 | 10400.04 | 40000 | 0 | 3285.8 | 0 | 10400.04 | 0 | 0 | 22974.96 | 0 | 0 | 22974.96
2022070816 | 6 | 0.97319 | 77855.2 | 0 | 0 | 0.11815 | 4135.25 | 0.71107 | 9954.98 | 40000 | 0 | 4135.25 | 0 | 9954.98 | 0 | 0 | 23764.97 | 0 | 0 | 23764.97
2022070817 | 6 | 0.97975 | 78380 | 0 | 0 | 0.13813 | 4834.55 | 0.70758 | 9906.12 | 40000 | 0 | 4834.55 | 0 | 9906.12 | 0 | 0 | 23639.33 | 0 | 0 | 23639.33
2022070818 | 6 | 0.97942 | 78353.6 | 0 | 0 | 0.14373 | 5030.55 | 0.7052 | 9872.8 | 40000 | 0 | 5030.55 | 0 | 9872.8 | 0 | 0 | 23450.25 | 0 | 0 | 23450.25
2022070819 | 6 | 0.97392 | 77913.6 | 0 | 0 | 0.18754 | 6563.9 | 0.63542 | 8895.88 | 40000 | 0 | 6563.9 | 0 | 8895.88 | 0 | 0 | 22453.82 | 0 | 0 | 22453.82
2022070820 | 6 | 0.95248 | 76198.4 | 0 | 0 | 0.24242 | 8484.7 | 0.35706 | 4998.84 | 40000 | 0 | 8484.7 | 0 | 4998.84 | 0 | 0 | 22714.86 | 0 | 0 | 22714.86
2022070821 | 6 | 0.91421 | 73136.8 | 0 | 0 | 0.26836 | 9392.6 | 0.04447 | 622.58 | 40000 | 0 | 9392.6 | 0 | 622.58 | 0 | 0 | 23121.62 | 0 | 0 | 23121.62
2022070822 | 6 | 0.88028 | 70422.4 | 0 | 0 | 0.322 | 11270 | 0 | 0 | 40000 | 0 | 11270 | 0 | 0 | 0 | 0 | 19152.4 | 0 | 0 | 19152.4
2022070823 | 6 | 0.82847 | 66277.6 | 0 | 0 | 0.38258 | 13390.3 | 0 | 0 | 40000 | 0 | 13390.3 | 0 | 0 | 0 | 0 | 12887.3 | 0 | 0 | 12887.3
2022070824 | 6 | 0.7779 | 62232 | 0 | 0 | 0.4245 | 14857.5 | 0 | 0 | 40000 | 0 | 14857.5 | 0 | 0 | 0 | 0 | 7374.5 | 0 | 0 | 7374.5
2022070901 | 7 | 0.73019 | 58415.2 | 0 | 0 | 0.4294 | 15029 | 0 | 0 | 40000 | 0 | 15029 | 0 | 0 | 0 | 0 | 3386.2 | 0 | 0 | 3386.2
2022070902 | 7 | 0.68753 | 55002.4 | 0 | 0 | 0.38161 | 13356.35 | 0 | 0 | 40000 | 0 | 13356.35 | 0 | 0 | 0 | 0 | 1646.05 | 0 | 0 | 1646.05
2022070903 | 7 | 0.65193 | 52154.4 | 0 | 0 | 0.28883 | 10109.05 | 0 | 0 | 40000 | 0 | 10109.05 | 0 | 0 | 0 | 0 | 2045.35 | 0 | 0 | 2045.35
2022070904 | 7 | 0.62702 | 50161.6 | 0 | 0 | 0.21564 | 7547.4 | 0 | 0 | 40000 | 0 | 7547.4 | 0 | 0 | 0 | 0 | 2614.2 | 0 | 0 | 2614.2
2022070905 | 7 | 0.61204 | 48963.2 | 0 | 0 | 0.15574 | 5450.9 | 0 | 0 | 40000 | 0 | 5450.9 | 0 | 0 | 0 | 0 | 3512.3 | 0 | 0 | 3512.3
2022070906 | 7 | 0.60342 | 48273.6 | 0 | 0 | 0.1411 | 4938.5 | 0 | 0 | 40000 | 0 | 4938.5 | 0 | 0 | 0 | 0 | 3335.1 | 0 | 0 | 3335.1
2022070907 | 7 | 0.59627 | 47701.6 | 0 | 0 | 0.146 | 5110 | 0.00263 | 36.82 | 40000 | 0 | 5110 | 0 | 36.82 | 0 | 0 | 2554.78 | 0 | 0 | 2554.78
2022070908 | 7 | 0.60554 | 48443.2 | 0 | 0 | 0.14429 | 5050.15 | 0.14955 | 2093.7 | 40000 | 0 | 5050.15 | 0 | 2093.7 | 0 | 0 | 1299.35 | 0 | 0 | 1299.35
2022070909 | 7 | 0.64493 | 51594.4 | 0 | 0 | 0.10552 | 3693.2 | 0.52178 | 7304.92 | 40000 | 0 | 3693.2 | 0 | 7304.92 | 0 | 0 | 596.28 | 0 | 0 | 596.28
2022070910 | 7 | 0.7022 | 56176 | 0 | 0 | 0.09694 | 3392.9 | 0.67181 | 9405.34 | 40000 | 0 | 3392.9 | 0 | 9405.34 | 0 | 0 | 3377.76 | 0 | 0 | 3377.76
2022070911 | 7 | 0.76284 | 61027.2 | 0 | 0 | 0.06297 | 2203.95 | 0.72843 | 10198.02 | 40000 | 0 | 2203.95 | 0 | 10198.02 | 0 | 0 | 8625.23 | 0 | 0 | 8625.23
2022070912 | 7 | 0.82207 | 65765.6 | 0 | 0 | 0.04581 | 1603.35 | 0.72115 | 10096.1 | 40000 | 0 | 1603.35 | 0 | 10096.1 | 0 | 0 | 14066.15 | 0 | 0 | 14066.15
2022070913 | 7 | 0.87246 | 69796.8 | 0 | 0 | 0.04737 | 1657.95 | 0.71286 | 9980.04 | 40000 | 0 | 1657.95 | 0 | 9980.04 | 0 | 0 | 18158.81 | 0 | 0 | 18158.81
2022070914 | 7 | 0.91594 | 73275.2 | 0 | 0 | 0.07529 | 2635.15 | 0.73646 | 10310.44 | 40000 | 0 | 2635.15 | 0 | 10310.44 | 0 | 0 | 20329.61 | 0 | 0 | 20329.61
2022070915 | 7 | 0.94621 | 75696.8 | 0 | 0 | 0.11807 | 4132.45 | 0.67194 | 9407.16 | 40000 | 0 | 4132.45 | 0 | 9407.16 | 0 | 0 | 22157.19 | 0 | 0 | 22157.19
2022070916 | 7 | 0.95858 | 76686.4 | 0 | 0 | 0.13749 | 4812.15 | 0.58432 | 8180.48 | 40000 | 0 | 4812.15 | 0 | 8180.48 | 0 | 0 | 23693.77 | 0 | 0 | 23693.77
2022070917 | 7 | 0.96773 | 77418.4 | 0 | 0 | 0.15548 | 5441.8 | 0.52693 | 7377.02 | 40000 | 0 | 5441.8 | 0 | 7377.02 | 0 | 0 | 24599.58 | 0 | 0 | 24599.58
2022070918 | 7 | 0.96894 | 77515.2 | 0 | 0 | 0.18738 | 6558.3 | 0.50111 | 7015.54 | 40000 | 0 | 6558.3 | 0 | 7015.54 | 0 | 0 | 23941.36 | 0 | 0 | 23941.36
2022070919 | 7 | 0.95664 | 76531.2 | 0 | 0 | 0.19065 | 6672.75 | 0.44086 | 6172.04 | 40000 | 0 | 6672.75 | 0 | 6172.04 | 0 | 0 | 23686.41 | 0 | 0 | 23686.41
2022070920 | 7 | 0.93566 | 74852.8 | 0 | 0 | 0.21484 | 7519.4 | 0.27865 | 3901.1 | 40000 | 0 | 7519.4 | 0 | 3901.1 | 0 | 0 | 23432.3 | 0 | 0 | 23432.3
2022070921 | 7 | 0.89541 | 71632.8 | 0 | 0 | 0.19503 | 6826.05 | 0.02889 | 404.46 | 40000 | 0 | 6826.05 | 0 | 404.46 | 0 | 0 | 24402.29 | 0 | 0 | 24402.29
2022070922 | 7 | 0.86395 | 69116 | 0 | 0 | 0.20218 | 7076.3 | 0 | 0 | 40000 | 0 | 7076.3 | 0 | 0 | 0 | 0 | 22039.7 | 0 | 0 | 22039.7
2022070923 | 7 | 0.81966 | 65572.8 | 0 | 0 | 0.20294 | 7102.9 | 0 | 0 | 40000 | 0 | 7102.9 | 0 | 0 | 0 | 0 | 18469.9 | 0 | 0 | 18469.9
2022070924 | 7 | 0.77168 | 61734.4 | 0 | 0 | 0.1816 | 6356 | 0 | 0 | 40000 | 0 | 6356 | 0 | 0 | 0 | 0 | 15378.4 | 0 | 0 | 15378.4
2022071001 | 1 | 0.72462 | 57969.6 | 0 | 0 | 0.17553 | 6143.55 | 0 | 0 | 40000 | 0 | 6143.55 | 0 | 0 | 0 | 0 | 11826.05 | 0 | 0 | 11826.05
2022071002 | 1 | 0.68334 | 54667.2 | 0 | 0 | 0.16876 | 5906.6 | 0 | 0 | 40000 | 0 | 5906.6 | 0 | 0 | 0 | 0 | 8760.6 | 0 | 0 | 8760.6
2022071003 | 1 | 0.65134 | 52107.2 | 0 | 0 | 0.15 | 5250 | 0 | 0 | 40000 | 0 | 5250 | 0 | 0 | 0 | 0 | 6857.2 | 0 | 0 | 6857.2
2022071004 | 1 | 0.62828 | 50262.4 | 0 | 0 | 0.14161 | 4956.35 | 0 | 0 | 40000 | 0 | 4956.35 | 0 | 0 | 0 | 0 | 5306.05 | 0 | 0 | 5306.05
2022071005 | 1 | 0.61077 | 48861.6 | 0 | 0 | 0.13225 | 4628.75 | 0 | 0 | 40000 | 0 | 4628.75 | 0 | 0 | 0 | 0 | 4232.85 | 0 | 0 | 4232.85
2022071006 | 1 | 0.5973 | 47784 | 0 | 0 | 0.11121 | 3892.35 | 0 | 0 | 40000 | 0 | 3892.35 | 0 | 0 | 0 | 0 | 3891.65 | 0 | 0 | 3891.65
2022071007 | 1 | 0.58795 | 47036 | 0 | 0 | 0.10228 | 3579.8 | 0.00297 | 41.58 | 40000 | 0 | 3579.8 | 0 | 41.58 | 0 | 0 | 3414.62 | 0 | 0 | 3414.62
2022071008 | 1 | 0.59058 | 47246.4 | 0 | 0 | 0.07837 | 2742.95 | 0.15365 | 2151.1 | 40000 | 0 | 2742.95 | 0 | 2151.1 | 0 | 0 | 2352.35 | 0 | 0 | 2352.35
2022071009 | 1 | 0.63027 | 50421.6 | 0 | 0 | 0.04956 | 1734.6 | 0.51121 | 7156.94 | 40000 | 0 | 1734.6 | 0 | 7156.94 | 0 | 0 | 1530.06 | 0 | 0 | 1530.06
2022071010 | 1 | 0.68868 | 55094.4 | 0 | 0 | 0.04711 | 1648.85 | 0.74565 | 10439.1 | 40000 | 0 | 1648.85 | 0 | 10439.1 | 0 | 0 | 3006.45 | 0 | 0 | 3006.45
2022071011 | 1 | 0.74924 | 59939.2 | 0 | 0 | 0.03091 | 1081.85 | 0.80382 | 11253.48 | 40000 | 0 | 1081.85 | 0 | 11253.48 | 0 | 0 | 7603.87 | 0 | 0 | 7603.87
2022071012 | 1 | 0.80945 | 64756 | 0 | 0 | 0.02256 | 789.6 | 0.80728 | 11301.92 | 40000 | 0 | 789.6 | 0 | 11301.92 | 0 | 0 | 12664.48 | 0 | 0 | 12664.48
2022071013 | 1 | 0.86553 | 69242.4 | 0 | 0 | 0.02686 | 940.1 | 0.78532 | 10994.48 | 40000 | 0 | 940.1 | 0 | 10994.48 | 0 | 0 | 17307.82 | 0 | 0 | 17307.82
2022071014 | 1 | 0.91012 | 72809.6 | 0 | 0 | 0.04021 | 1407.35 | 0.76176 | 10664.64 | 40000 | 0 | 1407.35 | 0 | 10664.64 | 0 | 0 | 20737.61 | 0 | 0 | 20737.61
2022071015 | 1 | 0.93707 | 74965.6 | 0 | 0 | 0.06071 | 2124.85 | 0.72954 | 10213.56 | 40000 | 0 | 2124.85 | 0 | 10213.56 | 0 | 0 | 22627.19 | 0 | 0 | 22627.19
2022071016 | 1 | 0.95456 | 76364.8 | 0 | 0 | 0.09042 | 3164.7 | 0.73217 | 10250.38 | 40000 | 0 | 3164.7 | 0 | 10250.38 | 0 | 0 | 22949.72 | 0 | 0 | 22949.72
2022071017 | 1 | 0.96695 | 77356 | 0 | 0 | 0.11124 | 3893.4 | 0.70548 | 9876.72 | 40000 | 0 | 3893.4 | 0 | 9876.72 | 0 | 0 | 23585.88 | 0 | 0 | 23585.88
2022071018 | 1 | 0.96811 | 77448.8 | 0 | 0 | 0.13401 | 4690.35 | 0.65883 | 9223.62 | 40000 | 0 | 4690.35 | 0 | 9223.62 | 0 | 0 | 23534.83 | 0 | 0 | 23534.83
2022071019 | 1 | 0.96014 | 76811.2 | 0 | 0 | 0.15982 | 5593.7 | 0.50718 | 7100.52 | 40000 | 0 | 5593.7 | 0 | 7100.52 | 0 | 0 | 24116.98 | 0 | 0 | 24116.98
2022071020 | 1 | 0.93783 | 75026.4 | 0 | 0 | 0.18203 | 6371.05 | 0.26338 | 3687.32 | 40000 | 0 | 6371.05 | 0 | 3687.32 | 0 | 0 | 24968.03 | 0 | 0 | 24968.03
2022071021 | 1 | 0.9025 | 72200 | 0 | 0 | 0.21483 | 7519.05 | 0.033 | 462 | 40000 | 0 | 7519.05 | 0 | 462 | 0 | 0 | 24218.95 | 0 | 0 | 24218.95
2022071022 | 1 | 0.87127 | 69701.6 | 0 | 0 | 0.25899 | 9064.65 | 0 | 0 | 40000 | 0 | 9064.65 | 0 | 0 | 0 | 0 | 20636.95 | 0 | 0 | 20636.95
2022071023 | 1 | 0.82373 | 65898.4 | 0 | 0 | 0.31695 | 11093.25 | 0 | 0 | 40000 | 0 | 11093.25 | 0 | 0 | 0 | 0 | 14805.15 | 0 | 0 | 14805.15
2022071024 | 1 | 0.77023 | 61618.4 | 0 | 0 | 0.3363 | 11770.5 | 0 | 0 | 40000 | 0 | 11770.5 | 0 | 0 | 0 | 0 | 9847.9 | 0 | 0 | 9847.9
2022071101 | 2 | 0.72377 | 57901.6 | 0 | 0 | 0.33218 | 11626.3 | 0 | 0 | 40000 | 0 | 11626.3 | 0 | 0 | 0 | 0 | 6275.3 | 0 | 0 | 6275.3
2022071102 | 2 | 0.68808 | 55046.4 | 0 | 0 | 0.31257 | 10939.95 | 0 | 0 | 40000 | 0 | 10939.95 | 0 | 0 | 0 | 0 | 4106.45 | 0 | 0 | 4106.45
2022071103 | 2 | 0.65932 | 52745.6 | 0 | 0 | 0.27409 | 9593.15 | 0 | 0 | 40000 | 0 | 9593.15 | 0 | 0 | 0 | 0 | 3152.45 | 0 | 0 | 3152.45
2022071104 | 2 | 0.64396 | 51516.8 | 0 | 0 | 0.21917 | 7670.95 | 0 | 0 | 40000 | 0 | 7670.95 | 0 | 0 | 0 | 0 | 3845.85 | 0 | 0 | 3845.85
2022071105 | 2 | 0.63528 | 50822.4 | 0 | 0 | 0.19097 | 6683.95 | 0 | 0 | 40000 | 0 | 6683.95 | 0 | 0 | 0 | 0 | 4138.45 | 0 | 0 | 4138.45
2022071106 | 2 | 0.63772 | 51017.6 | 0 | 0 | 0.16866 | 5903.1 | 0 | 0 | 40000 | 0 | 5903.1 | 0 | 0 | 0 | 0 | 5114.5 | 0 | 0 | 5114.5
2022071107 | 2 | 0.64199 | 51359.2 | 0 | 0 | 0.13827 | 4839.45 | 0.00202 | 28.28 | 40000 | 0 | 4839.45 | 0 | 28.28 | 0 | 0 | 6491.47 | 0 | 0 | 6491.47
2022071108 | 2 | 0.65304 | 52243.2 | 0 | 0 | 0.10387 | 3635.45 | 0.13877 | 1942.78 | 40000 | 0 | 3635.45 | 0 | 1942.78 | 0 | 0 | 6664.97 | 0 | 0 | 6664.97
2022071109 | 2 | 0.68532 | 54825.6 | 0 | 0 | 0.07091 | 2481.85 | 0.49658 | 6952.12 | 40000 | 0 | 2481.85 | 0 | 6952.12 | 0 | 0 | 5391.63 | 0 | 0 | 5391.63
2022071110 | 2 | 0.73465 | 58772 | 0 | 0 | 0.07458 | 2610.3 | 0.70121 | 9816.94 | 40000 | 0 | 2610.3 | 0 | 9816.94 | 0 | 0 | 6344.76 | 0 | 0 | 6344.76
2022071111 | 2 | 0.79548 | 63638.4 | 0 | 0 | 0.05393 | 1887.55 | 0.77295 | 10821.3 | 40000 | 0 | 1887.55 | 0 | 10821.3 | 0 | 0 | 10929.55 | 0 | 0 | 10929.55
2022071112 | 2 | 0.8569 | 68552 | 0 | 0 | 0.02984 | 1044.4 | 0.79148 | 11080.72 | 40000 | 0 | 1044.4 | 0 | 11080.72 | 0 | 0 | 16426.88 | 0 | 0 | 16426.88
2022071113 | 2 | 0.90616 | 72492.8 | 0 | 0 | 0.02095 | 733.25 | 0.78803 | 11032.42 | 40000 | 0 | 733.25 | 0 | 11032.42 | 0 | 0 | 20727.13 | 0 | 0 | 20727.13
2022071114 | 2 | 0.94187 | 75349.6 | 0 | 0 | 0.04292 | 1502.2 | 0.76712 | 10739.68 | 40000 | 0 | 1502.2 | 0 | 10739.68 | 0 | 0 | 23107.72 | 0 | 0 | 23107.72
2022071115 | 2 | 0.96724 | 77379.2 | 0 | 0 | 0.08581 | 3003.35 | 0.77612 | 10865.68 | 40000 | 0 | 3003.35 | 0 | 10865.68 | 0 | 0 | 23510.17 | 0 | 0 | 23510.17
2022071116 | 2 | 0.97704 | 78163.2 | 0 | 0 | 0.13466 | 4713.1 | 0.75392 | 10554.88 | 40000 | 0 | 4713.1 | 0 | 10554.88 | 0 | 0 | 22895.22 | 0 | 0 | 22895.22
2022071117 | 2 | 0.9804 | 78432 | 0 | 0 | 0.17614 | 6164.9 | 0.7237 | 10131.8 | 40000 | 0 | 6164.9 | 0 | 10131.8 | 0 | 0 | 22135.3 | 0 | 0 | 22135.3
2022071118 | 2 | 0.97731 | 78184.8 | 0 | 0 | 0.20447 | 7156.45 | 0.68586 | 9602.04 | 40000 | 0 | 7156.45 | 0 | 9602.04 | 0 | 0 | 21426.31 | 0 | 0 | 21426.31
2022071119 | 2 | 0.97124 | 77699.2 | 0 | 0 | 0.23879 | 8357.65 | 0.61291 | 8580.74 | 40000 | 0 | 8357.65 | 0 | 8580.74 | 0 | 0 | 20760.81 | 0 | 0 | 20760.81
2022071120 | 2 | 0.94954 | 75963.2 | 0 | 0 | 0.28286 | 9900.1 | 0.36462 | 5104.68 | 40000 | 0 | 9900.1 | 0 | 5104.68 | 0 | 0 | 20958.42 | 0 | 0 | 20958.42
2022071121 | 2 | 0.91257 | 73005.6 | 0 | 0 | 0.28847 | 10096.45 | 0.05129 | 718.06 | 40000 | 0 | 10096.45 | 0 | 718.06 | 0 | 0 | 22191.09 | 0 | 0 | 22191.09
2022071122 | 2 | 0.87918 | 70334.4 | 0 | 0 | 0.33509 | 11728.15 | 0 | 0 | 40000 | 0 | 11728.15 | 0 | 0 | 0 | 0 | 18606.25 | 0 | 0 | 18606.25
2022071123 | 2 | 0.82939 | 66351.2 | 0 | 0 | 0.39258 | 13740.3 | 0 | 0 | 40000 | 0 | 13740.3 | 0 | 0 | 0 | 0 | 12610.9 | 0 | 0 | 12610.9
2022071124 | 2 | 0.77389 | 61911.2 | 0 | 0 | 0.40698 | 14244.3 | 0 | 0 | 40000 | 0 | 14244.3 | 0 | 0 | 0 | 0 | 7666.9 | 0 | 0 | 7666.9
2022071201 | 3 | 0.72646 | 58116.8 | 0 | 0 | 0.40404 | 14141.4 | 0 | 0 | 40000 | 0 | 14141.4 | 0 | 0 | 0 | 0 | 3975.4 | 0 | 0 | 3975.4
2022071202 | 3 | 0.68586 | 54868.8 | 0 | 0 | 0.37837 | 13242.95 | 0 | 0 | 40000 | 0 | 13242.95 | 0 | 0 | 0 | 0 | 1625.85 | 0 | 0 | 1625.85
2022071203 | 3 | 0.65539 | 52431.2 | 0 | 0 | 0.34369 | 12029.15 | 0 | 0 | 40000 | 0 | 12029.15 | 0 | 0 | 0 | 0 | 402.05 | 0 | 0 | 402.05
2022071204 | 3 | 0.63564 | 50851.2 | 0 | 0 | 0.30103 | 10536.05 | 0 | 0 | 40000 | 0 | 10536.05 | 0 | 0 | 0 | 0 | 315.15 | 0 | 0 | 315.15
2022071205 | 3 | 0.62567 | 50053.6 | 0 | 0 | 0.26332 | 9216.2 | 0 | 0 | 40000 | 0 | 9216.2 | 0 | 0 | 0 | 0 | 837.4 | 0 | 0 | 837.4
2022071206 | 3 | 0.62714 | 50171.2 | 0 | 0 | 0.25155 | 8804.25 | 0 | 0 | 40000 | 0 | 8804.25 | 0 | 0 | 0 | 0 | 1366.95 | 0 | 0 | 1366.95
2022071207 | 3 | 0.63311 | 50648.8 | 0 | 0 | 0.22488 | 7870.8 | 0.00246 | 34.44 | 40000 | 0 | 7870.8 | 0 | 34.44 | 0 | 0 | 2743.56 | 0 | 0 | 2743.56
2022071208 | 3 | 0.64536 | 51628.8 | 0 | 0 | 0.20768 | 7268.8 | 0.12432 | 1740.48 | 40000 | 0 | 7268.8 | 0 | 1740.48 | 0 | 0 | 2619.52 | 0 | 0 | 2619.52
2022071209 | 3 | 0.67991 | 54392.8 | 0 | 0 | 0.19833 | 6941.55 | 0.45294 | 6341.16 | 40000 | 0 | 6941.55 | 0 | 6341.16 | 0 | 0 | 1110.09 | 0 | 0 | 1110.09
2022071210 | 3 | 0.73195 | 58556 | 0 | 0 | 0.19232 | 6731.2 | 0.68346 | 9568.44 | 40000 | 0 | 6731.2 | 0 | 9568.44 | 0 | 0 | 2256.36 | 0 | 0 | 2256.36
2022071211 | 3 | 0.79326 | 63460.8 | 0 | 0 | 0.17351 | 6072.85 | 0.73555 | 10297.7 | 40000 | 0 | 6072.85 | 0 | 10297.7 | 0 | 0 | 7090.25 | 0 | 0 | 7090.25
2022071212 | 3 | 0.85197 | 68157.6 | 0 | 0 | 0.20826 | 7289.1 | 0.77608 | 10865.12 | 40000 | 0 | 7289.1 | 0 | 10865.12 | 0 | 0 | 10003.38 | 0 | 0 | 10003.38
2022071213 | 3 | 0.90358 | 72286.4 | 0 | 0 | 0.24574 | 8600.9 | 0.75216 | 10530.24 | 40000 | 0 | 8600.9 | 0 | 10530.24 | 0 | 0 | 13155.26 | 0 | 0 | 13155.26
2022071214 | 3 | 0.94866 | 75892.8 | 0 | 0 | 0.24724 | 8653.4 | 0.72748 | 10184.72 | 40000 | 0 | 8653.4 | 0 | 10184.72 | 0 | 0 | 17054.68 | 0 | 0 | 17054.68
2022071215 | 3 | 0.97171 | 77736.8 | 0 | 0 | 0.22807 | 7982.45 | 0.71397 | 9995.58 | 40000 | 0 | 7982.45 | 0 | 9995.58 | 0 | 0 | 19758.77 | 0 | 0 | 19758.77
2022071216 | 3 | 0.9799 | 78392 | 0 | 0 | 0.23734 | 8306.9 | 0.66096 | 9253.44 | 40000 | 0 | 8306.9 | 0 | 9253.44 | 0 | 0 | 20831.66 | 0 | 0 | 20831.66
2022071217 | 3 | 0.98212 | 78569.6 | 0 | 0 | 0.26055 | 9119.25 | 0.63181 | 8845.34 | 40000 | 0 | 9119.25 | 0 | 8845.34 | 0 | 0 | 20605.01 | 0 | 0 | 20605.01
2022071218 | 3 | 0.97269 | 77815.2 | 0 | 0 | 0.28776 | 10071.6 | 0.55667 | 7793.38 | 40000 | 0 | 10071.6 | 0 | 7793.38 | 0 | 0 | 19950.22 | 0 | 0 | 19950.22
2022071219 | 3 | 0.95595 | 76476 | 0 | 0 | 0.32427 | 11349.45 | 0.45069 | 6309.66 | 40000 | 0 | 11349.45 | 0 | 6309.66 | 0 | 0 | 18816.89 | 0 | 0 | 18816.89
2022071220 | 3 | 0.92855 | 74284 | 0 | 0 | 0.32516 | 11380.6 | 0.27929 | 3910.06 | 40000 | 0 | 11380.6 | 0 | 3910.06 | 0 | 0 | 18993.34 | 0 | 0 | 18993.34
2022071221 | 3 | 0.89328 | 71462.4 | 0 | 0 | 0.29194 | 10217.9 | 0.04931 | 690.34 | 40000 | 0 | 10217.9 | 0 | 690.34 | 0 | 0 | 20554.16 | 0 | 0 | 20554.16
2022071222 | 3 | 0.86245 | 68996 | 0 | 0 | 0.26681 | 9338.35 | 0.00428 | 59.92 | 40000 | 0 | 9338.35 | 0 | 59.92 | 0 | 0 | 19597.73 | 0 | 0 | 19597.73
2022071223 | 3 | 0.81059 | 64847.2 | 0 | 0 | 0.27147 | 9501.45 | 0 | 0 | 40000 | 0 | 9501.45 | 0 | 0 | 0 | 0 | 15345.75 | 0 | 0 | 15345.75
2022071224 | 3 | 0.75644 | 60515.2 | 0 | 0 | 0.25147 | 8801.45 | 0 | 0 | 40000 | 0 | 8801.45 | 0 | 0 | 0 | 0 | 11713.75 | 0 | 0 | 11713.75
2022071301 | 4 | 0.70591 | 56472.8 | 0 | 0 | 0.23276 | 8146.6 | 0 | 0 | 40000 | 0 | 8146.6 | 0 | 0 | 0 | 0 | 8326.2 | 0 | 0 | 8326.2
2022071302 | 4 | 0.66603 | 53282.4 | 0 | 0 | 0.19553 | 6843.55 | 0 | 0 | 40000 | 0 | 6843.55 | 0 | 0 | 0 | 0 | 6438.85 | 0 | 0 | 6438.85
2022071303 | 4 | 0.63529 | 50823.2 | 0 | 0 | 0.17294 | 6052.9 | 0 | 0 | 40000 | 0 | 6052.9 | 0 | 0 | 0 | 0 | 4770.3 | 0 | 0 | 4770.3
2022071304 | 4 | 0.61588 | 49270.4 | 0 | 0 | 0.1436 | 5026 | 0 | 0 | 40000 | 0 | 5026 | 0 | 0 | 0 | 0 | 4244.4 | 0 | 0 | 4244.4
2022071305 | 4 | 0.60781 | 48624.8 | 0 | 0 | 0.11862 | 4151.7 | 0 | 0 | 40000 | 0 | 4151.7 | 0 | 0 | 0 | 0 | 4473.1 | 0 | 0 | 4473.1
2022071306 | 4 | 0.61028 | 48822.4 | 0 | 0 | 0.10882 | 3808.7 | 0 | 0 | 40000 | 0 | 3808.7 | 0 | 0 | 0 | 0 | 5013.7 | 0 | 0 | 5013.7
2022071307 | 4 | 0.62341 | 49872.8 | 0 | 0 | 0.09618 | 3366.3 | 0.00207 | 28.98 | 40000 | 0 | 3366.3 | 0 | 28.98 | 0 | 0 | 6477.52 | 0 | 0 | 6477.52
2022071308 | 4 | 0.63327 | 50661.6 | 0 | 0 | 0.07341 | 2569.35 | 0.1214 | 1699.6 | 40000 | 0 | 2569.35 | 0 | 1699.6 | 0 | 0 | 6392.65 | 0 | 0 | 6392.65
2022071309 | 4 | 0.67024 | 53619.2 | 0 | 0 | 0.0449 | 1571.5 | 0.4647 | 6505.8 | 40000 | 0 | 1571.5 | 0 | 6505.8 | 0 | 0 | 5541.9 | 0 | 0 | 5541.9
2022071310 | 4 | 0.72112 | 57689.6 | 0 | 0 | 0.03761 | 1316.35 | 0.66964 | 9374.96 | 40000 | 0 | 1316.35 | 0 | 9374.96 | 0 | 0 | 6998.29 | 0 | 0 | 6998.29
2022071311 | 4 | 0.78458 | 62766.4 | 0 | 0 | 0.02866 | 1003.1 | 0.75817 | 10614.38 | 40000 | 0 | 1003.1 | 0 | 10614.38 | 0 | 0 | 11148.92 | 0 | 0 | 11148.92
2022071312 | 4 | 0.84643 | 67714.4 | 0 | 0 | 0.01957 | 684.95 | 0.77103 | 10794.42 | 40000 | 0 | 684.95 | 0 | 10794.42 | 0 | 0 | 16235.03 | 0 | 0 | 16235.03
2022071313 | 4 | 0.89715 | 71772 | 0 | 0 | 0.01978 | 692.3 | 0.76037 | 10645.18 | 40000 | 0 | 692.3 | 0 | 10645.18 | 0 | 0 | 20434.52 | 0 | 0 | 20434.52
2022071314 | 4 | 0.93759 | 75007.2 | 0 | 0 | 0.05657 | 1979.95 | 0.74919 | 10488.66 | 40000 | 0 | 1979.95 | 0 | 10488.66 | 0 | 0 | 22538.59 | 0 | 0 | 22538.59
2022071315 | 4 | 0.96656 | 77324.8 | 0 | 0 | 0.11114 | 3889.9 | 0.68035 | 9524.9 | 40000 | 0 | 3889.9 | 0 | 9524.9 | 0 | 0 | 23910 | 0 | 0 | 23910
2022071316 | 4 | 0.97714 | 78171.2 | 0 | 0 | 0.15085 | 5279.75 | 0.57508 | 8051.12 | 40000 | 0 | 5279.75 | 0 | 8051.12 | 0 | 0 | 24840.33 | 0 | 0 | 24840.33
2022071317 | 4 | 0.98074 | 78459.2 | 0 | 0 | 0.18962 | 6636.7 | 0.51932 | 7270.48 | 40000 | 0 | 6636.7 | 0 | 7270.48 | 0 | 0 | 24552.02 | 0 | 0 | 24552.02
2022071318 | 4 | 0.97347 | 77877.6 | 0 | 0 | 0.21638 | 7573.3 | 0.40999 | 5739.86 | 40000 | 0 | 7573.3 | 0 | 5739.86 | 0 | 0 | 24564.44 | 0 | 0 | 24564.44
2022071319 | 4 | 0.95556 | 76444.8 | 0 | 0 | 0.2241 | 7843.5 | 0.30974 | 4336.36 | 40000 | 0 | 7843.5 | 0 | 4336.36 | 0 | 0 | 24264.94 | 0 | 0 | 24264.94
2022071320 | 4 | 0.93276 | 74620.8 | 0 | 0 | 0.25436 | 8902.6 | 0.16207 | 2268.98 | 40000 | 0 | 8902.6 | 0 | 2268.98 | 0 | 0 | 23449.22 | 0 | 0 | 23449.22
2022071321 | 4 | 0.90176 | 72140.8 | 0 | 0 | 0.23959 | 8385.65 | 0.01996 | 279.44 | 40000 | 0 | 8385.65 | 0 | 279.44 | 0 | 0 | 23475.71 | 0 | 0 | 23475.71
2022071322 | 4 | 0.87426 | 69940.8 | 0 | 0 | 0.26226 | 9179.1 | 0 | 0 | 40000 | 0 | 9179.1 | 0 | 0 | 0 | 0 | 20761.7 | 0 | 0 | 20761.7
2022071323 | 4 | 0.82621 | 66096.8 | 0 | 0 | 0.31602 | 11060.7 | 0 | 0 | 40000 | 0 | 11060.7 | 0 | 0 | 0 | 0 | 15036.1 | 0 | 0 | 15036.1
2022071324 | 4 | 0.77279 | 61823.2 | 0 | 0 | 0.30399 | 10639.65 | 0 | 0 | 40000 | 0 | 10639.65 | 0 | 0 | 0 | 0 | 11183.55 | 0 | 0 | 11183.55
2022071401 | 5 | 0.72478 | 57982.4 | 0 | 0 | 0.28766 | 10068.1 | 0 | 0 | 40000 | 0 | 10068.1 | 0 | 0 | 0 | 0 | 7914.3 | 0 | 0 | 7914.3
2022071402 | 5 | 0.6857 | 54856 | 0 | 0 | 0.23207 | 8122.45 | 0 | 0 | 40000 | 0 | 8122.45 | 0 | 0 | 0 | 0 | 6733.55 | 0 | 0 | 6733.55
2022071403 | 5 | 0.65491 | 52392.8 | 0 | 0 | 0.20879 | 7307.65 | 0 | 0 | 40000 | 0 | 7307.65 | 0 | 0 | 0 | 0 | 5085.15 | 0 | 0 | 5085.15
2022071404 | 5 | 0.63614 | 50891.2 | 0 | 0 | 0.20884 | 7309.4 | 0 | 0 | 40000 | 0 | 7309.4 | 0 | 0 | 0 | 0 | 3581.8 | 0 | 0 | 3581.8
2022071405 | 5 | 0.62413 | 49930.4 | 0 | 0 | 0.21144 | 7400.4 | 0 | 0 | 40000 | 0 | 7400.4 | 0 | 0 | 0 | 0 | 2530 | 0 | 0 | 2530
2022071406 | 5 | 0.62562 | 50049.6 | 0 | 0 | 0.19378 | 6782.3 | 0 | 0 | 40000 | 0 | 6782.3 | 0 | 0 | 0 | 0 | 3267.3 | 0 | 0 | 3267.3
2022071407 | 5 | 0.63324 | 50659.2 | 0 | 0 | 0.20284 | 7099.4 | 0.00095 | 13.3 | 40000 | 0 | 7099.4 | 0 | 13.3 | 0 | 0 | 3546.5 | 0 | 0 | 3546.5
2022071408 | 5 | 0.64274 | 51419.2 | 0 | 0 | 0.19356 | 6774.6 | 0.09902 | 1386.28 | 40000 | 0 | 6774.6 | 0 | 1386.28 | 0 | 0 | 3258.32 | 0 | 0 | 3258.32
2022071409 | 5 | 0.67299 | 53839.2 | 0 | 0 | 0.12827 | 4489.45 | 0.48381 | 6773.34 | 40000 | 0 | 4489.45 | 0 | 6773.34 | 0 | 0 | 2576.41 | 0 | 0 | 2576.41
2022071410 | 5 | 0.7186 | 57488 | 0 | 0 | 0.10833 | 3791.55 | 0.69757 | 9765.98 | 40000 | 0 | 3791.55 | 0 | 9765.98 | 0 | 0 | 3930.47 | 0 | 0 | 3930.47
2022071411 | 5 | 0.76865 | 61492 | 0 | 0 | 0.09088 | 3180.8 | 0.75234 | 10532.76 | 40000 | 0 | 3180.8 | 0 | 10532.76 | 0 | 0 | 7778.44 | 0 | 0 | 7778.44
2022071412 | 5 | 0.81106 | 64884.8 | 0 | 0 | 0.06885 | 2409.75 | 0.74071 | 10369.94 | 40000 | 0 | 2409.75 | 0 | 10369.94 | 0 | 0 | 12105.11 | 0 | 0 | 12105.11
2022071413 | 5 | 0.84283 | 67426.4 | 0 | 0 | 0.08286 | 2900.1 | 0.73038 | 10225.32 | 40000 | 0 | 2900.1 | 0 | 10225.32 | 0 | 0 | 14300.98 | 0 | 0 | 14300.98
2022071414 | 5 | 0.86022 | 68817.6 | 0 | 0 | 0.1098 | 3843 | 0.70842 | 9917.88 | 40000 | 0 | 3843 | 0 | 9917.88 | 0 | 0 | 15056.72 | 0 | 0 | 15056.72
2022071415 | 5 | 0.86837 | 69469.6 | 0 | 0 | 0.17533 | 6136.55 | 0.64849 | 9078.86 | 40000 | 0 | 6136.55 | 0 | 9078.86 | 0 | 0 | 14254.19 | 0 | 0 | 14254.19
2022071416 | 5 | 0.87392 | 69913.6 | 0 | 0 | 0.24914 | 8719.9 | 0.61463 | 8604.82 | 40000 | 0 | 8719.9 | 0 | 8604.82 | 0 | 0 | 12588.88 | 0 | 0 | 12588.88
2022071417 | 5 | 0.87971 | 70376.8 | 0 | 0 | 0.33551 | 11742.85 | 0.57725 | 8081.5 | 40000 | 0 | 11742.85 | 0 | 8081.5 | 0 | 0 | 10552.45 | 0 | 0 | 10552.45
2022071418 | 5 | 0.8684 | 69472 | 0 | 0 | 0.40263 | 14092.05 | 0.57424 | 8039.36 | 40000 | 0 | 14092.05 | 0 | 8039.36 | 0 | 0 | 7340.59 | 0 | 0 | 7340.59
2022071419 | 5 | 0.84254 | 67403.2 | 0 | 0 | 0.4256 | 14896 | 0.43748 | 6124.72 | 40000 | 0 | 14896 | 0 | 6124.72 | 0 | 0 | 6382.48 | 0 | 0 | 6382.48
2022071420 | 5 | 0.80672 | 64537.6 | 0 | 0 | 0.41142 | 14399.7 | 0.18752 | 2625.28 | 40000 | 0 | 14399.7 | 0 | 2625.28 | 0 | 0 | 7512.62 | 0 | 0 | 7512.62
2022071421 | 5 | 0.77647 | 62117.6 | 0 | 0 | 0.41149 | 14402.15 | 0.03248 | 454.72 | 40000 | 0 | 14402.15 | 0 | 454.72 | 0 | 0 | 7260.73 | 0 | 0 | 7260.73
2022071422 | 5 | 0.75307 | 60245.6 | 0 | 0 | 0.42933 | 15026.55 | 0 | 0 | 40000 | 0 | 15026.55 | 0 | 0 | 0 | 0 | 5219.05 | 0 | 0 | 5219.05
2022071423 | 5 | 0.70986 | 56788.8 | 0 | 0 | 0.4109 | 14381.5 | 0 | 0 | 40000 | 0 | 14381.5 | 0 | 0 | 0 | 0 | 2407.3 | 0 | 0 | 2407.3
2022071424 | 5 | 0.66233 | 52986.4 | 0 | 0 | 0.34464 | 12062.4 | 0 | 0 | 40000 | 0 | 12062.4 | 0 | 0 | 0 | 0 | 924 | 0 | 0 | 924
2022071501 | 6 | 0.61949 | 49559.2 | 0 | 0 | 0.26629 | 9320.15 | 0 | 0 | 40000 | 0 | 9320.15 | 0 | 0 | 0 | 0 | 239.05 | 0 | 0 | 239.05
2022071502 | 6 | 0.58742 | 46993.6 | 0 | 0 | 0.203 | 7105 | 0 | 0 | 40000 | 0 | 6993.6 | 111.4 | 0 | 0 | 111.4 | 0 | 0 | 0 | 0
2022071503 | 6 | 0.56427 | 45141.6 | 0 | 0 | 0.16754 | 5863.9 | 0 | 0 | 40000 | 0 | 5141.6 | 722.3 | 0 | 0 | 722.3 | 0 | 0 | 0 | 0
2022071504 | 6 | 0.54885 | 43908 | 0 | 0 | 0.17341 | 6069.35 | 0 | 0 | 40000 | 0 | 3908 | 2161.35 | 0 | 0 | 2161.35 | 0 | 0 | 0 | 0
2022071505 | 6 | 0.54436 | 43548.8 | 0 | 0 | 0.15846 | 5546.1 | 0 | 0 | 40000 | 0 | 3548.8 | 1997.3 | 0 | 0 | 1997.3 | 0 | 0 | 0 | 0
2022071506 | 6 | 0.55117 | 44093.6 | 0 | 0 | 0.16131 | 5645.85 | 0 | 0 | 40000 | 0 | 4093.6 | 1552.25 | 0 | 0 | 1552.25 | 0 | 0 | 0 | 0
2022071507 | 6 | 0.56232 | 44985.6 | 0 | 0 | 0.13648 | 4776.8 | 0.00221 | 30.94 | 40000 | 0 | 4776.8 | 0 | 30.94 | 0 | 0 | 177.86 | 0 | 0 | 177.86
2022071508 | 6 | 0.57909 | 46327.2 | 0 | 0 | 0.10672 | 3735.2 | 0.15624 | 2187.36 | 40000 | 0 | 3735.2 | 0 | 2187.36 | 0 | 0 | 404.64 | 0 | 0 | 404.64
2022071509 | 6 | 0.61738 | 49390.4 | 0 | 0 | 0.05883 | 2059.05 | 0.57058 | 7988.12 | 40000 | 0 | 2059.05 | 0 | 7331.35 | 656.77 | 656.77 | 0 | 0 | 0 | 0
2022071510 | 6 | 0.66493 | 53194.4 | 0 | 0 | 0.05839 | 2043.65 | 0.74331 | 10406.34 | 40000 | 0 | 2043.65 | 0 | 10406.34 | 0 | 0 | 744.41 | 0 | 0 | 744.41
2022071511 | 6 | 0.71835 | 57468 | 0 | 0 | 0.0738 | 2583 | 0.76437 | 10701.18 | 40000 | 0 | 2583 | 0 | 10701.18 | 0 | 0 | 4183.82 | 0 | 0 | 4183.82
2022071512 | 6 | 0.77216 | 61772.8 | 0 | 0 | 0.08055 | 2819.25 | 0.76179 | 10665.06 | 40000 | 0 | 2819.25 | 0 | 10665.06 | 0 | 0 | 8288.49 | 0 | 0 | 8288.49
2022071513 | 6 | 0.81736 | 65388.8 | 0 | 0 | 0.08659 | 3030.65 | 0.76881 | 10763.34 | 40000 | 0 | 3030.65 | 0 | 10763.34 | 0 | 0 | 11594.81 | 0 | 0 | 11594.81
2022071514 | 6 | 0.84968 | 67974.4 | 0 | 0 | 0.08919 | 3121.65 | 0.76585 | 10721.9 | 40000 | 0 | 3121.65 | 0 | 10721.9 | 0 | 0 | 14130.85 | 0 | 0 | 14130.85
2022071515 | 6 | 0.86873 | 69498.4 | 0 | 0 | 0.1008 | 3528 | 0.77388 | 10834.32 | 40000 | 0 | 3528 | 0 | 10834.32 | 0 | 0 | 15136.08 | 0 | 0 | 15136.08
2022071516 | 6 | 0.87262 | 69809.6 | 0 | 0 | 0.11365 | 3977.75 | 0.73744 | 10324.16 | 40000 | 0 | 3977.75 | 0 | 10324.16 | 0 | 0 | 15507.69 | 0 | 0 | 15507.69
2022071517 | 6 | 0.87695 | 70156 | 0 | 0 | 0.1287 | 4504.5 | 0.69926 | 9789.64 | 40000 | 0 | 4504.5 | 0 | 9789.64 | 0 | 0 | 15861.86 | 0 | 0 | 15861.86
2022071518 | 6 | 0.87482 | 69985.6 | 0 | 0 | 0.13846 | 4846.1 | 0.70057 | 9807.98 | 40000 | 0 | 4846.1 | 0 | 9807.98 | 0 | 0 | 15331.52 | 0 | 0 | 15331.52
2022071519 | 6 | 0.85655 | 68524 | 0 | 0 | 0.17182 | 6013.7 | 0.65328 | 9145.92 | 40000 | 0 | 6013.7 | 0 | 9145.92 | 0 | 0 | 13364.38 | 0 | 0 | 13364.38
2022071520 | 6 | 0.83177 | 66541.6 | 0 | 0 | 0.22836 | 7992.6 | 0.38122 | 5337.08 | 40000 | 0 | 7992.6 | 0 | 5337.08 | 0 | 0 | 13211.92 | 0 | 0 | 13211.92
2022071521 | 6 | 0.80147 | 64117.6 | 0 | 0 | 0.27026 | 9459.1 | 0.05197 | 727.58 | 40000 | 0 | 9459.1 | 0 | 727.58 | 0 | 0 | 13930.92 | 0 | 0 | 13930.92
2022071522 | 6 | 0.77548 | 62038.4 | 0 | 0 | 0.33748 | 11811.8 | 0 | 0 | 40000 | 0 | 11811.8 | 0 | 0 | 0 | 0 | 10226.6 | 0 | 0 | 10226.6
2022071523 | 6 | 0.73298 | 58638.4 | 0 | 0 | 0.42876 | 15006.6 | 0 | 0 | 40000 | 0 | 15006.6 | 0 | 0 | 0 | 0 | 3631.8 | 0 | 0 | 3631.8
2022071524 | 6 | 0.68923 | 55138.4 | 0 | 0 | 0.47262 | 16541.7 | 0 | 0 | 40000 | 0 | 15138.4 | 1403.3 | 0 | 0 | 1403.3 | 0 | 0 | 0 | 0
2022071601 | 7 | 0.64898 | 51918.4 | 0 | 0 | 0.48275 | 16896.25 | 0 | 0 | 40000 | 0 | 11918.4 | 4977.85 | 0 | 0 | 4977.85 | 0 | 0 | 0 | 0
2022071602 | 7 | 0.61596 | 49276.8 | 0 | 0 | 0.46894 | 16412.9 | 0 | 0 | 40000 | 0 | 9276.8 | 7136.1 | 0 | 0 | 7136.1 | 0 | 0 | 0 | 0
2022071603 | 7 | 0.59022 | 47217.6 | 0 | 0 | 0.45099 | 15784.65 | 0 | 0 | 40000 | 0 | 7217.6 | 8567.05 | 0 | 0 | 8567.05 | 0 | 0 | 0 | 0
2022071604 | 7 | 0.57556 | 46044.8 | 0 | 0 | 0.42173 | 14760.55 | 0 | 0 | 40000 | 0 | 6044.8 | 8715.75 | 0 | 0 | 8715.75 | 0 | 0 | 0 | 0
2022071605 | 7 | 0.56095 | 44876 | 0 | 0 | 0.37336 | 13067.6 | 0 | 0 | 40000 | 0 | 4876 | 8191.6 | 0 | 0 | 8191.6 | 0 | 0 | 0 | 0
2022071606 | 7 | 0.55645 | 44516 | 0 | 0 | 0.33194 | 11617.9 | 0 | 0 | 40000 | 0 | 4516 | 7101.9 | 0 | 0 | 7101.9 | 0 | 0 | 0 | 0
2022071607 | 7 | 0.55462 | 44369.6 | 0 | 0 | 0.2961 | 10363.5 | 0.00219 | 30.66 | 40000 | 0 | 4369.6 | 5993.9 | 0 | 30.66 | 6024.56 | 0 | 0 | 0 | 0
2022071608 | 7 | 0.56422 | 45137.6 | 0 | 0 | 0.25039 | 8763.65 | 0.15309 | 2143.26 | 40000 | 0 | 5137.6 | 3626.05 | 0 | 2143.26 | 5769.31 | 0 | 0 | 0 | 0
2022071609 | 7 | 0.60463 | 48370.4 | 0 | 0 | 0.16186 | 5665.1 | 0.5772 | 8080.8 | 40000 | 0 | 5665.1 | 0 | 2705.3 | 5375.5 | 5375.5 | 0 | 0 | 0 | 0
2022071610 | 7 | 0.65659 | 52527.2 | 0 | 0 | 0.16061 | 5621.35 | 0.75947 | 10632.58 | 40000 | 0 | 5621.35 | 0 | 6905.85 | 3726.73 | 3726.73 | 0 | 0 | 0 | 0
2022071611 | 7 | 0.71234 | 56987.2 | 0 | 0 | 0.14035 | 4912.25 | 0.79972 | 11196.08 | 40000 | 0 | 4912.25 | 0 | 11196.08 | 0 | 0 | 878.87 | 0 | 0 | 878.87
2022071612 | 7 | 0.76775 | 61420 | 0 | 0 | 0.10242 | 3584.7 | 0.80127 | 11217.78 | 40000 | 0 | 3584.7 | 0 | 11217.78 | 0 | 0 | 6617.52 | 0 | 0 | 6617.52
2022071613 | 7 | 0.81273 | 65018.4 | 0 | 0 | 0.09757 | 3414.95 | 0.79408 | 11117.12 | 40000 | 0 | 3414.95 | 0 | 11117.12 | 0 | 0 | 10486.33 | 0 | 0 | 10486.33
2022071614 | 7 | 0.85135 | 68108 | 0 | 0 | 0.13413 | 4694.55 | 0.8002 | 11202.8 | 40000 | 0 | 4694.55 | 0 | 11202.8 | 0 | 0 | 12210.65 | 0 | 0 | 12210.65
2022071615 | 7 | 0.88302 | 70641.6 | 0 | 0 | 0.16932 | 5926.2 | 0.78568 | 10999.52 | 40000 | 0 | 5926.2 | 0 | 10999.52 | 0 | 0 | 13715.88 | 0 | 0 | 13715.88
2022071616 | 7 | 0.90527 | 72421.6 | 0 | 0 | 0.20269 | 7094.15 | 0.76934 | 10770.76 | 40000 | 0 | 7094.15 | 0 | 10770.76 | 0 | 0 | 14556.69 | 0 | 0 | 14556.69
2022071617 | 7 | 0.92074 | 73659.2 | 0 | 0 | 0.23112 | 8089.2 | 0.74196 | 10387.44 | 40000 | 0 | 8089.2 | 0 | 10387.44 | 0 | 0 | 15182.56 | 0 | 0 | 15182.56
2022071618 | 7 | 0.92214 | 73771.2 | 0 | 0 | 0.24684 | 8639.4 | 0.70647 | 9890.58 | 40000 | 0 | 8639.4 | 0 | 9890.58 | 0 | 0 | 15241.22 | 0 | 0 | 15241.22
2022071619 | 7 | 0.90938 | 72750.4 | 0 | 0 | 0.2564 | 8974 | 0.60932 | 8530.48 | 40000 | 0 | 8974 | 0 | 8530.48 | 0 | 0 | 15245.92 | 0 | 0 | 15245.92
2022071620 | 7 | 0.88093 | 70474.4 | 0 | 0 | 0.26654 | 9328.9 | 0.3715 | 5201 | 40000 | 0 | 9328.9 | 0 | 5201 | 0 | 0 | 15944.5 | 0 | 0 | 15944.5
2022071621 | 7 | 0.84587 | 67669.6 | 0 | 0 | 0.27032 | 9461.2 | 0.05117 | 716.38 | 40000 | 0 | 9461.2 | 0 | 716.38 | 0 | 0 | 17492.02 | 0 | 0 | 17492.02
2022071622 | 7 | 0.81798 | 65438.4 | 0 | 0 | 0.32827 | 11489.45 | 0 | 0 | 40000 | 0 | 11489.45 | 0 | 0 | 0 | 0 | 13948.95 | 0 | 0 | 13948.95
2022071623 | 7 | 0.77568 | 62054.4 | 0 | 0 | 0.39593 | 13857.55 | 0 | 0 | 40000 | 0 | 13857.55 | 0 | 0 | 0 | 0 | 8196.85 | 0 | 0 | 8196.85
2022071624 | 7 | 0.72925 | 58340 | 0 | 0 | 0.43851 | 15347.85 | 0 | 0 | 40000 | 0 | 15347.85 | 0 | 0 | 0 | 0 | 2992.15 | 0 | 0 | 2992.15
2022071701 | 1 | 0.68653 | 54922.4 | 0 | 0 | 0.46063 | 16122.05 | 0 | 0 | 40000 | 0 | 14922.4 | 1199.65 | 0 | 0 | 1199.65 | 0 | 0 | 0 | 0
2022071702 | 1 | 0.65011 | 52008.8 | 0 | 0 | 0.47328 | 16564.8 | 0 | 0 | 40000 | 0 | 12008.8 | 4556 | 0 | 0 | 4556 | 0 | 0 | 0 | 0
2022071703 | 1 | 0.62174 | 49739.2 | 0 | 0 | 0.45048 | 15766.8 | 0 | 0 | 40000 | 0 | 9739.2 | 6027.6 | 0 | 0 | 6027.6 | 0 | 0 | 0 | 0
2022071704 | 1 | 0.59999 | 47999.2 | 0 | 0 | 0.43727 | 15304.45 | 0 | 0 | 40000 | 0 | 7999.2 | 7305.25 | 0 | 0 | 7305.25 | 0 | 0 | 0 | 0
2022071705 | 1 | 0.58319 | 46655.2 | 0 | 0 | 0.44434 | 15551.9 | 0 | 0 | 40000 | 0 | 6655.2 | 8896.7 | 0 | 0 | 8896.7 | 0 | 0 | 0 | 0
2022071706 | 1 | 0.57286 | 45828.8 | 0 | 0 | 0.42217 | 14775.95 | 0 | 0 | 40000 | 0 | 5828.8 | 8947.15 | 0 | 0 | 8947.15 | 0 | 0 | 0 | 0
2022071707 | 1 | 0.56301 | 45040.8 | 0 | 0 | 0.39662 | 13881.7 | 0.00088 | 12.32 | 40000 | 0 | 5040.8 | 8840.9 | 0 | 12.32 | 8853.22 | 0 | 0 | 0 | 0
2022071708 | 1 | 0.56408 | 45126.4 | 0 | 0 | 0.34333 | 12016.55 | 0.10018 | 1402.52 | 40000 | 0 | 5126.4 | 6890.15 | 0 | 1402.52 | 8292.67 | 0 | 0 | 0 | 0
2022071709 | 1 | 0.59921 | 47936.8 | 0 | 0 | 0.27539 | 9638.65 | 0.47384 | 6633.76 | 40000 | 0 | 7936.8 | 1701.85 | 0 | 6633.76 | 8335.61 | 0 | 0 | 0 | 0
2022071710 | 1 | 0.65059 | 52047.2 | 0 | 0 | 0.2852 | 9982 | 0.69495 | 9729.3 | 40000 | 0 | 9982 | 0 | 2065.2 | 7664.1 | 7664.1 | 0 | 0 | 0 | 0
2022071711 | 1 | 0.7079 | 56632 | 0 | 0 | 0.25762 | 9016.7 | 0.77005 | 10780.7 | 40000 | 0 | 9016.7 | 0 | 7615.3 | 3165.4 | 3165.4 | 0 | 0 | 0 | 0
2022071712 | 1 | 0.7656 | 61248 | 0 | 0 | 0.20848 | 7296.8 | 0.78484 | 10987.76 | 40000 | 0 | 7296.8 | 0 | 10987.76 | 0 | 0 | 2963.44 | 0 | 0 | 2963.44
2022071713 | 1 | 0.81978 | 65582.4 | 0 | 0 | 0.15491 | 5421.85 | 0.79356 | 11109.84 | 40000 | 0 | 5421.85 | 0 | 11109.84 | 0 | 0 | 9050.71 | 0 | 0 | 9050.71
2022071714 | 1 | 0.86771 | 69416.8 | 0 | 0 | 0.13786 | 4825.1 | 0.75738 | 10603.32 | 40000 | 0 | 4825.1 | 0 | 10603.32 | 0 | 0 | 13988.38 | 0 | 0 | 13988.38
2022071715 | 1 | 0.90349 | 72279.2 | 0 | 0 | 0.14832 | 5191.2 | 0.7315 | 10241 | 40000 | 0 | 5191.2 | 0 | 10241 | 0 | 0 | 16847 | 0 | 0 | 16847
2022071716 | 1 | 0.92693 | 74154.4 | 0 | 0 | 0.15706 | 5497.1 | 0.73219 | 10250.66 | 40000 | 0 | 5497.1 | 0 | 10250.66 | 0 | 0 | 18406.64 | 0 | 0 | 18406.64
2022071717 | 1 | 0.9435 | 75480 | 0 | 0 | 0.16571 | 5799.85 | 0.70597 | 9883.58 | 40000 | 0 | 5799.85 | 0 | 9883.58 | 0 | 0 | 19796.57 | 0 | 0 | 19796.57
2022071718 | 1 | 0.94282 | 75425.6 | 0 | 0 | 0.16708 | 5847.8 | 0.61625 | 8627.5 | 40000 | 0 | 5847.8 | 0 | 8627.5 | 0 | 0 | 20950.3 | 0 | 0 | 20950.3
2022071719 | 1 | 0.92718 | 74174.4 | 0 | 0 | 0.17826 | 6239.1 | 0.44409 | 6217.26 | 40000 | 0 | 6239.1 | 0 | 6217.26 | 0 | 0 | 21718.04 | 0 | 0 | 21718.04
2022071720 | 1 | 0.8985 | 71880 | 0 | 0 | 0.20043 | 7015.05 | 0.22179 | 3105.06 | 40000 | 0 | 7015.05 | 0 | 3105.06 | 0 | 0 | 21759.89 | 0 | 0 | 21759.89
2022071721 | 1 | 0.87022 | 69617.6 | 0 | 0 | 0.2562 | 8967 | 0.02832 | 396.48 | 40000 | 0 | 8967 | 0 | 396.48 | 0 | 0 | 20254.12 | 0 | 0 | 20254.12
2022071722 | 1 | 0.84678 | 67742.4 | 0 | 0 | 0.33628 | 11769.8 | 0 | 0 | 40000 | 0 | 11769.8 | 0 | 0 | 0 | 0 | 15972.6 | 0 | 0 | 15972.6
2022071723 | 1 | 0.80154 | 64123.2 | 0 | 0 | 0.43122 | 15092.7 | 0 | 0 | 40000 | 0 | 15092.7 | 0 | 0 | 0 | 0 | 9030.5 | 0 | 0 | 9030.5
2022071724 | 1 | 0.75105 | 60084 | 0 | 0 | 0.4857 | 16999.5 | 0 | 0 | 40000 | 0 | 16999.5 | 0 | 0 | 0 | 0 | 3084.5 | 0 | 0 | 3084.5
2022071801 | 2 | 0.70442 | 56353.6 | 0 | 0 | 0.50475 | 17666.25 | 0 | 0 | 40000 | 0 | 16353.6 | 1312.65 | 0 | 0 | 1312.65 | 0 | 0 | 0 | 0
2022071802 | 2 | 0.66696 | 53356.8 | 0 | 0 | 0.50445 | 17655.75 | 0 | 0 | 40000 | 0 | 13356.8 | 4298.95 | 0 | 0 | 4298.95 | 0 | 0 | 0 | 0
2022071803 | 2 | 0.63886 | 51108.8 | 0 | 0 | 0.48159 | 16855.65 | 0 | 0 | 40000 | 0 | 11108.8 | 5746.85 | 0 | 0 | 5746.85 | 0 | 0 | 0 | 0
2022071804 | 2 | 0.61933 | 49546.4 | 0 | 0 | 0.44299 | 15504.65 | 0 | 0 | 40000 | 0 | 9546.4 | 5958.25 | 0 | 0 | 5958.25 | 0 | 0 | 0 | 0
2022071805 | 2 | 0.60896 | 48716.8 | 0 | 0 | 0.40253 | 14088.55 | 0 | 0 | 40000 | 0 | 8716.8 | 5371.75 | 0 | 0 | 5371.75 | 0 | 0 | 0 | 0
2022071806 | 2 | 0.61326 | 49060.8 | 0 | 0 | 0.38044 | 13315.4 | 0 | 0 | 40000 | 0 | 9060.8 | 4254.6 | 0 | 0 | 4254.6 | 0 | 0 | 0 | 0
2022071807 | 2 | 0.61995 | 49596 | 0 | 0 | 0.34794 | 12177.9 | 0.00052 | 7.28 | 40000 | 0 | 9596 | 2581.9 | 0 | 7.28 | 2589.18 | 0 | 0 | 0 | 0
2022071808 | 2 | 0.63005 | 50404 | 0 | 0 | 0.31073 | 10875.55 | 0.10112 | 1415.68 | 40000 | 0 | 10404 | 471.55 | 0 | 1415.68 | 1887.23 | 0 | 0 | 0 | 0
2022071809 | 2 | 0.66497 | 53197.6 | 0 | 0 | 0.23453 | 8208.55 | 0.47567 | 6659.38 | 40000 | 0 | 8208.55 | 0 | 4989.05 | 1670.33 | 1670.33 | 0 | 0 | 0 | 0
2022071810 | 2 | 0.7145 | 57160 | 0 | 0 | 0.21967 | 7688.45 | 0.6809 | 9532.6 | 40000 | 0 | 7688.45 | 0 | 9471.55 | 61.05 | 61.05 | 0 | 0 | 0 | 0
2022071811 | 2 | 0.77062 | 61649.6 | 0 | 0 | 0.19376 | 6781.6 | 0.765 | 10710 | 40000 | 0 | 6781.6 | 0 | 10710 | 0 | 0 | 4158 | 0 | 0 | 4158
2022071812 | 2 | 0.82709 | 66167.2 | 0 | 0 | 0.14862 | 5201.7 | 0.79075 | 11070.5 | 40000 | 0 | 5201.7 | 0 | 11070.5 | 0 | 0 | 9895 | 0 | 0 | 9895
2022071813 | 2 | 0.88169 | 70535.2 | 0 | 0 | 0.10886 | 3810.1 | 0.79508 | 11131.12 | 40000 | 0 | 3810.1 | 0 | 11131.12 | 0 | 0 | 15593.98 | 0 | 0 | 15593.98
2022071814 | 2 | 0.9268 | 74144 | 0 | 0 | 0.10713 | 3749.55 | 0.7975 | 11165 | 40000 | 0 | 3749.55 | 0 | 11165 | 0 | 0 | 19229.45 | 0 | 0 | 19229.45
2022071815 | 2 | 0.96303 | 77042.4 | 0 | 0 | 0.12348 | 4321.8 | 0.79318 | 11104.52 | 40000 | 0 | 4321.8 | 0 | 11104.52 | 0 | 0 | 21616.08 | 0 | 0 | 21616.08
2022071816 | 2 | 0.98251 | 78600.8 | 0 | 0 | 0.13521 | 4732.35 | 0.78082 | 10931.48 | 40000 | 0 | 4732.35 | 0 | 10931.48 | 0 | 0 | 22936.97 | 0 | 0 | 22936.97
2022071817 | 2 | 0.98974 | 79179.2 | 0 | 0 | 0.14686 | 5140.1 | 0.76291 | 10680.74 | 40000 | 0 | 5140.1 | 0 | 10680.74 | 0 | 0 | 23358.36 | 0 | 0 | 23358.36
2022071818 | 2 | 0.98995 | 79196 | 0 | 0 | 0.15885 | 5559.75 | 0.72864 | 10200.96 | 40000 | 0 | 5559.75 | 0 | 10200.96 | 0 | 0 | 23435.29 | 0 | 0 | 23435.29
2022071819 | 2 | 0.97631 | 78104.8 | 0 | 0 | 0.17173 | 6010.55 | 0.61089 | 8552.46 | 40000 | 0 | 6010.55 | 0 | 8552.46 | 0 | 0 | 23541.79 | 0 | 0 | 23541.79
2022071820 | 2 | 0.94439 | 75551.2 | 0 | 0 | 0.20383 | 7134.05 | 0.3068 | 4295.2 | 40000 | 0 | 7134.05 | 0 | 4295.2 | 0 | 0 | 24121.95 | 0 | 0 | 24121.95
2022071821 | 2 | 0.91135 | 72908 | 0 | 0 | 0.26679 | 9337.65 | 0.03487 | 488.18 | 40000 | 0 | 9337.65 | 0 | 488.18 | 0 | 0 | 23082.17 | 0 | 0 | 23082.17
2022071822 | 2 | 0.88478 | 70782.4 | 0 | 0 | 0.36957 | 12934.95 | 0 | 0 | 40000 | 0 | 12934.95 | 0 | 0 | 0 | 0 | 17847.45 | 0 | 0 | 17847.45
2022071823 | 2 | 0.83508 | 66806.4 | 0 | 0 | 0.45841 | 16044.35 | 0 | 0 | 40000 | 0 | 16044.35 | 0 | 0 | 0 | 0 | 10762.05 | 0 | 0 | 10762.05
2022071824 | 2 | 0.77923 | 62338.4 | 0 | 0 | 0.51266 | 17943.1 | 4e-05 | 0.56 | 40000 | 0 | 17943.1 | 0 | 0.56 | 0 | 0 | 4394.74 | 0 | 0 | 4394.74
2022071901 | 3 | 0.73301 | 58640.8 | 0 | 0 | 0.54572 | 19100.2 | 5e-05 | 0.7 | 40000 | 0 | 18640.8 | 459.4 | 0 | 0.7 | 460.1 | 0 | 0 | 0 | 0
2022071902 | 3 | 0.696 | 55680 | 0 | 0 | 0.56349 | 19722.15 | 5e-05 | 0.7 | 40000 | 0 | 15680 | 4042.15 | 0 | 0.7 | 4042.85 | 0 | 0 | 0 | 0
2022071903 | 3 | 0.66688 | 53350.4 | 0 | 0 | 0.5573 | 19505.5 | 5e-05 | 0.7 | 40000 | 0 | 13350.4 | 6155.1 | 0 | 0.7 | 6155.8 | 0 | 0 | 0 | 0
2022071904 | 3 | 0.64777 | 51821.6 | 0 | 0 | 0.53823 | 18838.05 | 4e-05 | 0.56 | 40000 | 0 | 11821.6 | 7016.45 | 0 | 0.56 | 7017.01 | 0 | 0 | 0 | 0
2022071905 | 3 | 0.63964 | 51171.2 | 0 | 0 | 0.54626 | 19119.1 | 0 | 0 | 40000 | 0 | 11171.2 | 7947.9 | 0 | 0 | 7947.9 | 0 | 0 | 0 | 0
2022071906 | 3 | 0.64114 | 51291.2 | 0 | 0 | 0.54641 | 19124.35 | 4e-05 | 0.56 | 40000 | 0 | 11291.2 | 7833.15 | 0 | 0.56 | 7833.71 | 0 | 0 | 0 | 0
2022071907 | 3 | 0.64802 | 51841.6 | 0 | 0 | 0.54199 | 18969.65 | 0.00126 | 17.64 | 40000 | 0 | 11841.6 | 7128.05 | 0 | 17.64 | 7145.69 | 0 | 0 | 0 | 0
2022071908 | 3 | 0.65782 | 52625.6 | 0 | 0 | 0.51659 | 18080.65 | 0.12871 | 1801.94 | 40000 | 0 | 12625.6 | 5455.05 | 0 | 1801.94 | 7256.99 | 0 | 0 | 0 | 0
2022071909 | 3 | 0.69198 | 55358.4 | 0 | 0 | 0.45476 | 15916.6 | 0.51153 | 7161.42 | 40000 | 0 | 15358.4 | 558.2 | 0 | 7161.42 | 7719.62 | 0 | 0 | 0 | 0
2022071910 | 3 | 0.7426 | 59408 | 0 | 0 | 0.4871 | 17048.5 | 0.69661 | 9752.54 | 40000 | 0 | 17048.5 | 0 | 2359.5 | 7393.04 | 7393.04 | 0 | 0 | 0 | 0
2022071911 | 3 | 0.79665 | 63732 | 0 | 0 | 0.44295 | 15503.25 | 0.77246 | 10814.44 | 40000 | 0 | 15503.25 | 0 | 8228.75 | 2585.69 | 2585.69 | 0 | 0 | 0 | 0
2022071912 | 3 | 0.85105 | 68084 | 0 | 0 | 0.39299 | 13754.65 | 0.7666 | 10732.4 | 40000 | 0 | 13754.65 | 0 | 10732.4 | 0 | 0 | 3596.95 | 0 | 0 | 3596.95
2022071913 | 3 | 0.90469 | 72375.2 | 0 | 0 | 0.39038 | 13663.3 | 0.77518 | 10852.52 | 40000 | 0 | 13663.3 | 0 | 10852.52 | 0 | 0 | 7859.38 | 0 | 0 | 7859.38
2022071914 | 3 | 0.95252 | 76201.6 | 0 | 0 | 0.38046 | 13316.1 | 0.75708 | 10599.12 | 40000 | 0 | 13316.1 | 0 | 10599.12 | 0 | 0 | 12286.38 | 0 | 0 | 12286.38
2022071915 | 3 | 0.98603 | 78882.4 | 0 | 0 | 0.35695 | 12493.25 | 0.76198 | 10667.72 | 40000 | 0 | 12493.25 | 0 | 10667.72 | 0 | 0 | 15721.43 | 0 | 0 | 15721.43
2022071916 | 3 | 0.99287 | 79429.6 | 0 | 0 | 0.33151 | 11602.85 | 0.77138 | 10799.32 | 40000 | 0 | 11602.85 | 0 | 10799.32 | 0 | 0 | 17027.43 | 0 | 0 | 17027.43
2022071917 | 3 | 0.99743 | 79794.4 | 0 | 0 | 0.31132 | 10896.2 | 0.75859 | 10620.26 | 40000 | 0 | 10896.2 | 0 | 10620.26 | 0 | 0 | 18277.94 | 0 | 0 | 18277.94
2022071918 | 3 | 0.99468 | 79574.4 | 0 | 0 | 0.30376 | 10631.6 | 0.71807 | 10052.98 | 40000 | 0 | 10631.6 | 0 | 10052.98 | 0 | 0 | 18889.82 | 0 | 0 | 18889.82
2022071919 | 3 | 0.98411 | 78728.8 | 0 | 0 | 0.30959 | 10835.65 | 0.55989 | 7838.46 | 40000 | 0 | 10835.65 | 0 | 7838.46 | 0 | 0 | 20054.69 | 0 | 0 | 20054.69
2022071920 | 3 | 0.95944 | 76755.2 | 0 | 0 | 0.34933 | 12226.55 | 0.25556 | 3577.84 | 40000 | 0 | 12226.55 | 0 | 3577.84 | 0 | 0 | 20950.81 | 0 | 0 | 20950.81
2022071921 | 3 | 0.92617 | 74093.6 | 0 | 0 | 0.40988 | 14345.8 | 0.03286 | 460.04 | 40000 | 0 | 14345.8 | 0 | 460.04 | 0 | 0 | 19287.76 | 0 | 0 | 19287.76
2022071922 | 3 | 0.89557 | 71645.6 | 0 | 0 | 0.53007 | 18552.45 | 0 | 0 | 40000 | 0 | 18552.45 | 0 | 0 | 0 | 0 | 13093.15 | 0 | 0 | 13093.15
2022071923 | 3 | 0.84725 | 67780 | 0 | 0 | 0.60559 | 21195.65 | 0 | 0 | 40000 | 0 | 21195.65 | 0 | 0 | 0 | 0 | 6584.35 | 0 | 0 | 6584.35
2022071924 | 3 | 0.79392 | 63513.6 | 0 | 0 | 0.63059 | 22070.65 | 0 | 0 | 40000 | 0 | 22070.65 | 0 | 0 | 0 | 0 | 1442.95 | 0 | 0 | 1442.95
2022072001 | 4 | 0.74817 | 59853.6 | 0 | 0 | 0.6478 | 22673 | 0 | 0 | 40000 | 0 | 19853.6 | 2819.4 | 0 | 0 | 2819.4 | 0 | 0 | 0 | 0
2022072002 | 4 | 0.71181 | 56944.8 | 0 | 0 | 0.6509 | 22781.5 | 0 | 0 | 40000 | 0 | 16944.8 | 5836.7 | 0 | 0 | 5836.7 | 0 | 0 | 0 | 0
2022072003 | 4 | 0.68455 | 54764 | 0 | 0 | 0.65184 | 22814.4 | 0 | 0 | 40000 | 0 | 14764 | 8050.4 | 0 | 0 | 8050.4 | 0 | 0 | 0 | 0
2022072004 | 4 | 0.66413 | 53130.4 | 0 | 0 | 0.62827 | 21989.45 | 0 | 0 | 40000 | 0 | 13130.4 | 8859.05 | 0 | 0 | 8859.05 | 0 | 0 | 0 | 0
2022072005 | 4 | 0.65103 | 52082.4 | 0 | 0 | 0.57785 | 20224.75 | 0 | 0 | 40000 | 0 | 12082.4 | 8142.35 | 0 | 0 | 8142.35 | 0 | 0 | 0 | 0
2022072006 | 4 | 0.64996 | 51996.8 | 0 | 0 | 0.50586 | 17705.1 | 0 | 0 | 40000 | 0 | 11996.8 | 5708.3 | 0 | 0 | 5708.3 | 0 | 0 | 0 | 0
2022072007 | 4 | 0.65548 | 52438.4 | 0 | 0 | 0.44394 | 15537.9 | 0.00106 | 14.84 | 40000 | 0 | 12438.4 | 3099.5 | 0 | 14.84 | 3114.34 | 0 | 0 | 0 | 0
2022072008 | 4 | 0.66527 | 53221.6 | 0 | 0 | 0.3804 | 13314 | 0.09378 | 1312.92 | 40000 | 0 | 13221.6 | 92.4 | 0 | 1312.92 | 1405.32 | 0 | 0 | 0 | 0
2022072009 | 4 | 0.69661 | 55728.8 | 0 | 0 | 0.34088 | 11930.8 | 0.34552 | 4837.28 | 40000 | 0 | 11930.8 | 0 | 3798 | 1039.28 | 1039.28 | 0 | 0 | 0 | 0
2022072010 | 4 | 0.74234 | 59387.2 | 0 | 0 | 0.30772 | 10770.2 | 0.45596 | 6383.44 | 40000 | 0 | 10770.2 | 0 | 6383.44 | 0 | 0 | 2233.56 | 0 | 0 | 2233.56
2022072011 | 4 | 0.79884 | 63907.2 | 0 | 0 | 0.26792 | 9377.2 | 0.56843 | 7958.02 | 40000 | 0 | 9377.2 | 0 | 7958.02 | 0 | 0 | 6571.98 | 0 | 0 | 6571.98
2022072012 | 4 | 0.85805 | 68644 | 0 | 0 | 0.24716 | 8650.6 | 0.65739 | 9203.46 | 40000 | 0 | 8650.6 | 0 | 9203.46 | 0 | 0 | 10789.94 | 0 | 0 | 10789.94
2022072013 | 4 | 0.90972 | 72777.6 | 0 | 0 | 0.23287 | 8150.45 | 0.71016 | 9942.24 | 40000 | 0 | 8150.45 | 0 | 9942.24 | 0 | 0 | 14684.91 | 0 | 0 | 14684.91
2022072014 | 4 | 0.95366 | 76292.8 | 0 | 0 | 0.22169 | 7759.15 | 0.68182 | 9545.48 | 40000 | 0 | 7759.15 | 0 | 9545.48 | 0 | 0 | 18988.17 | 0 | 0 | 18988.17
2022072015 | 4 | 0.98242 | 78593.6 | 0 | 0 | 0.2036 | 7126 | 0.69322 | 9705.08 | 40000 | 0 | 7126 | 0 | 9705.08 | 0 | 0 | 21762.52 | 0 | 0 | 21762.52
2022072016 | 4 | 0.9946 | 79568 | 0 | 0 | 0.18729 | 6555.15 | 0.68421 | 9578.94 | 40000 | 0 | 6555.15 | 0 | 9578.94 | 0 | 0 | 23433.91 | 0 | 0 | 23433.91
2022072017 | 4 | 1 | 80000 | 0 | 0 | 0.20721 | 7252.35 | 0.66851 | 9359.14 | 40000 | 0 | 7252.35 | 0 | 9359.14 | 0 | 0 | 23388.51 | 0 | 0 | 23388.51
2022072018 | 4 | 0.99809 | 79847.2 | 0 | 0 | 0.24004 | 8401.4 | 0.60091 | 8412.74 | 40000 | 0 | 8401.4 | 0 | 8412.74 | 0 | 0 | 23033.06 | 0 | 0 | 23033.06
2022072019 | 4 | 0.98344 | 78675.2 | 0 | 0 | 0.28165 | 9857.75 | 0.55071 | 7709.94 | 40000 | 0 | 9857.75 | 0 | 7709.94 | 0 | 0 | 21107.51 | 0 | 0 | 21107.51
2022072020 | 4 | 0.95124 | 76099.2 | 0 | 0 | 0.30909 | 10818.15 | 0.29556 | 4137.84 | 40000 | 0 | 10818.15 | 0 | 4137.84 | 0 | 0 | 21143.21 | 0 | 0 | 21143.21
2022072021 | 4 | 0.91899 | 73519.2 | 0 | 0 | 0.31692 | 11092.2 | 0.0338 | 473.2 | 40000 | 0 | 11092.2 | 0 | 473.2 | 0 | 0 | 21953.8 | 0 | 0 | 21953.8
2022072022 | 4 | 0.88759 | 71007.2 | 0 | 0 | 0.33336 | 11667.6 | 0 | 0 | 40000 | 0 | 11667.6 | 0 | 0 | 0 | 0 | 19339.6 | 0 | 0 | 19339.6
2022072023 | 4 | 0.8417 | 67336 | 0 | 0 | 0.37362 | 13076.7 | 0 | 0 | 40000 | 0 | 13076.7 | 0 | 0 | 0 | 0 | 14259.3 | 0 | 0 | 14259.3
2022072024 | 4 | 0.79092 | 63273.6 | 0 | 0 | 0.45163 | 15807.05 | 0 | 0 | 40000 | 0 | 15807.05 | 0 | 0 | 0 | 0 | 7466.55 | 0 | 0 | 7466.55
2022072101 | 5 | 0.74167 | 59333.6 | 0 | 0 | 0.46803 | 16381.05 | 0 | 0 | 40000 | 0 | 16381.05 | 0 | 0 | 0 | 0 | 2952.55 | 0 | 0 | 2952.55
2022072102 | 5 | 0.70578 | 56462.4 | 0 | 0 | 0.47417 | 16595.95 | 0 | 0 | 40000 | 0 | 16462.4 | 133.55 | 0 | 0 | 133.55 | 0 | 0 | 0 | 0
2022072103 | 5 | 0.67788 | 54230.4 | 0 | 0 | 0.42224 | 14778.4 | 0 | 0 | 40000 | 0 | 14230.4 | 548 | 0 | 0 | 548 | 0 | 0 | 0 | 0
2022072104 | 5 | 0.66129 | 52903.2 | 0 | 0 | 0.34872 | 12205.2 | 0 | 0 | 40000 | 0 | 12205.2 | 0 | 0 | 0 | 0 | 698 | 0 | 0 | 698
2022072105 | 5 | 0.65043 | 52034.4 | 0 | 0 | 0.31125 | 10893.75 | 0 | 0 | 40000 | 0 | 10893.75 | 0 | 0 | 0 | 0 | 1140.65 | 0 | 0 | 1140.65
2022072106 | 5 | 0.65346 | 52276.8 | 0 | 0 | 0.26198 | 9169.3 | 0 | 0 | 40000 | 0 | 9169.3 | 0 | 0 | 0 | 0 | 3107.5 | 0 | 0 | 3107.5
2022072107 | 5 | 0.66135 | 52908 | 0 | 0 | 0.25727 | 9004.45 | 0.00062 | 8.68 | 40000 | 0 | 9004.45 | 0 | 8.68 | 0 | 0 | 3894.87 | 0 | 0 | 3894.87
2022072108 | 5 | 0.66566 | 53252.8 | 0 | 0 | 0.2381 | 8333.5 | 0.07076 | 990.64 | 40000 | 0 | 8333.5 | 0 | 990.64 | 0 | 0 | 3928.66 | 0 | 0 | 3928.66
2022072109 | 5 | 0.69346 | 55476.8 | 0 | 0 | 0.2249 | 7871.5 | 0.26515 | 3712.1 | 40000 | 0 | 7871.5 | 0 | 3712.1 | 0 | 0 | 3893.2 | 0 | 0 | 3893.2
2022072110 | 5 | 0.72992 | 58393.6 | 0 | 0 | 0.22244 | 7785.4 | 0.34653 | 4851.42 | 40000 | 0 | 7785.4 | 0 | 4851.42 | 0 | 0 | 5756.78 | 0 | 0 | 5756.78
2022072111 | 5 | 0.7729 | 61832 | 0 | 0 | 0.18566 | 6498.1 | 0.42363 | 5930.82 | 40000 | 0 | 6498.1 | 0 | 5930.82 | 0 | 0 | 9403.08 | 0 | 0 | 9403.08
2022072112 | 5 | 0.82113 | 65690.4 | 0 | 0 | 0.18851 | 6597.85 | 0.46981 | 6577.34 | 40000 | 0 | 6597.85 | 0 | 6577.34 | 0 | 0 | 12515.21 | 0 | 0 | 12515.21
2022072113 | 5 | 0.86437 | 69149.6 | 0 | 0 | 0.19452 | 6808.2 | 0.5206 | 7288.4 | 40000 | 0 | 6808.2 | 0 | 7288.4 | 0 | 0 | 15053 | 0 | 0 | 15053
2022072114 | 5 | 0.90428 | 72342.4 | 0 | 0 | 0.20571 | 7199.85 | 0.57256 | 8015.84 | 40000 | 0 | 7199.85 | 0 | 8015.84 | 0 | 0 | 17126.71 | 0 | 0 | 17126.71
2022072115 | 5 | 0.93635 | 74908 | 0 | 0 | 0.23843 | 8345.05 | 0.56261 | 7876.54 | 40000 | 0 | 8345.05 | 0 | 7876.54 | 0 | 0 | 18686.41 | 0 | 0 | 18686.41
2022072116 | 5 | 0.96065 | 76852 | 0 | 0 | 0.29025 | 10158.75 | 0.56347 | 7888.58 | 40000 | 0 | 10158.75 | 0 | 7888.58 | 0 | 0 | 18804.67 | 0 | 0 | 18804.67
2022072117 | 5 | 0.97453 | 77962.4 | 0 | 0 | 0.34821 | 12187.35 | 0.61123 | 8557.22 | 40000 | 0 | 12187.35 | 0 | 8557.22 | 0 | 0 | 17217.83 | 0 | 0 | 17217.83
2022072118 | 5 | 0.97192 | 77753.6 | 0 | 0 | 0.38655 | 13529.25 | 0.58502 | 8190.28 | 40000 | 0 | 13529.25 | 0 | 8190.28 | 0 | 0 | 16034.07 | 0 | 0 | 16034.07
2022072119 | 5 | 0.954 | 76320 | 0 | 0 | 0.41899 | 14664.65 | 0.45672 | 6394.08 | 40000 | 0 | 14664.65 | 0 | 6394.08 | 0 | 0 | 15261.27 | 0 | 0 | 15261.27
2022072120 | 5 | 0.91924 | 73539.2 | 0 | 0 | 0.4484 | 15694 | 0.27051 | 3787.14 | 40000 | 0 | 15694 | 0 | 3787.14 | 0 | 0 | 14058.06 | 0 | 0 | 14058.06
2022072121 | 5 | 0.88262 | 70609.6 | 0 | 0 | 0.39533 | 13836.55 | 0.0212 | 296.8 | 40000 | 0 | 13836.55 | 0 | 296.8 | 0 | 0 | 16476.25 | 0 | 0 | 16476.25
2022072122 | 5 | 0.85312 | 68249.6 | 0 | 0 | 0.35057 | 12269.95 | 0 | 0 | 40000 | 0 | 12269.95 | 0 | 0 | 0 | 0 | 15979.65 | 0 | 0 | 15979.65
2022072123 | 5 | 0.80492 | 64393.6 | 0 | 0 | 0.36414 | 12744.9 | 0 | 0 | 40000 | 0 | 12744.9 | 0 | 0 | 0 | 0 | 11648.7 | 0 | 0 | 11648.7
2022072124 | 5 | 0.75322 | 60257.6 | 0 | 0 | 0.38778 | 13572.3 | 0 | 0 | 40000 | 0 | 13572.3 | 0 | 0 | 0 | 0 | 6685.3 | 0 | 0 | 6685.3
2022072201 | 6 | 0.7054 | 56432 | 0 | 0 | 0.39205 | 13721.75 | 0 | 0 | 40000 | 0 | 13721.75 | 0 | 0 | 0 | 0 | 2710.25 | 0 | 0 | 2710.25
2022072202 | 6 | 0.66637 | 53309.6 | 0 | 0 | 0.3909 | 13681.5 | 0 | 0 | 40000 | 0 | 13309.6 | 371.9 | 0 | 0 | 371.9 | 0 | 0 | 0 | 0
2022072203 | 6 | 0.63914 | 51131.2 | 0 | 0 | 0.38759 | 13565.65 | 0 | 0 | 40000 | 0 | 11131.2 | 2434.45 | 0 | 0 | 2434.45 | 0 | 0 | 0 | 0
2022072204 | 6 | 0.62404 | 49923.2 | 0 | 0 | 0.3873 | 13555.5 | 0 | 0 | 40000 | 0 | 9923.2 | 3632.3 | 0 | 0 | 3632.3 | 0 | 0 | 0 | 0
2022072205 | 6 | 0.61587 | 49269.6 | 0 | 0 | 0.35575 | 12451.25 | 0 | 0 | 40000 | 0 | 9269.6 | 3181.65 | 0 | 0 | 3181.65 | 0 | 0 | 0 | 0
2022072206 | 6 | 0.61893 | 49514.4 | 0 | 0 | 0.32755 | 11464.25 | 0 | 0 | 40000 | 0 | 9514.4 | 1949.85 | 0 | 0 | 1949.85 | 0 | 0 | 0 | 0
2022072207 | 6 | 0.62885 | 50308 | 0 | 0 | 0.33715 | 11800.25 | 0.00034 | 4.76 | 40000 | 0 | 10308 | 1492.25 | 0 | 4.76 | 1497.01 | 0 | 0 | 0 | 0
2022072208 | 6 | 0.6373 | 50984 | 0 | 0 | 0.33791 | 11826.85 | 0.06045 | 846.3 | 40000 | 0 | 10984 | 842.85 | 0 | 846.3 | 1689.15 | 0 | 0 | 0 | 0
2022072209 | 6 | 0.66598 | 53278.4 | 0 | 0 | 0.29751 | 10412.85 | 0.26425 | 3699.5 | 40000 | 0 | 10412.85 | 0 | 2865.55 | 833.95 | 833.95 | 0 | 0 | 0 | 0
2022072210 | 6 | 0.71141 | 56912.8 | 0 | 0 | 0.31648 | 11076.8 | 0.46658 | 6532.12 | 40000 | 0 | 11076.8 | 0 | 5836 | 696.12 | 696.12 | 0 | 0 | 0 | 0
2022072211 | 6 | 0.76215 | 60972 | 0 | 0 | 0.29889 | 10461.15 | 0.64904 | 9086.56 | 40000 | 0 | 10461.15 | 0 | 9086.56 | 0 | 0 | 1424.29 | 0 | 0 | 1424.29
2022072212 | 6 | 0.81356 | 65084.8 | 0 | 0 | 0.27006 | 9452.1 | 0.69853 | 9779.42 | 40000 | 0 | 9452.1 | 0 | 9779.42 | 0 | 0 | 5853.28 | 0 | 0 | 5853.28
2022072213 | 6 | 0.85876 | 68700.8 | 0 | 0 | 0.25393 | 8887.55 | 0.70837 | 9917.18 | 40000 | 0 | 8887.55 | 0 | 9917.18 | 0 | 0 | 9896.07 | 0 | 0 | 9896.07
2022072214 | 6 | 0.89392 | 71513.6 | 0 | 0 | 0.25519 | 8931.65 | 0.71201 | 9968.14 | 40000 | 0 | 8931.65 | 0 | 9968.14 | 0 | 0 | 12613.81 | 0 | 0 | 12613.81
2022072215 | 6 | 0.90762 | 72609.6 | 0 | 0 | 0.27682 | 9688.7 | 0.70863 | 9920.82 | 40000 | 0 | 9688.7 | 0 | 9920.82 | 0 | 0 | 13000.08 | 0 | 0 | 13000.08
2022072216 | 6 | 0.9066 | 72528 | 0 | 0 | 0.31733 | 11106.55 | 0.69463 | 9724.82 | 40000 | 0 | 11106.55 | 0 | 9724.82 | 0 | 0 | 11696.63 | 0 | 0 | 11696.63
2022072217 | 6 | 0.90654 | 72523.2 | 0 | 0 | 0.35476 | 12416.6 | 0.65018 | 9102.52 | 40000 | 0 | 12416.6 | 0 | 9102.52 | 0 | 0 | 11004.08 | 0 | 0 | 11004.08
2022072218 | 6 | 0.90399 | 72319.2 | 0 | 0 | 0.38534 | 13486.9 | 0.59628 | 8347.92 | 40000 | 0 | 13486.9 | 0 | 8347.92 | 0 | 0 | 10484.38 | 0 | 0 | 10484.38
2022072219 | 6 | 0.88768 | 71014.4 | 0 | 0 | 0.42216 | 14775.6 | 0.48029 | 6724.06 | 40000 | 0 | 14775.6 | 0 | 6724.06 | 0 | 0 | 9514.74 | 0 | 0 | 9514.74
2022072220 | 6 | 0.86154 | 68923.2 | 0 | 0 | 0.44438 | 15553.3 | 0.24492 | 3428.88 | 40000 | 0 | 15553.3 | 0 | 3428.88 | 0 | 0 | 9941.02 | 0 | 0 | 9941.02
2022072221 | 6 | 0.83035 | 66428 | 0 | 0 | 0.43186 | 15115.1 | 0.01846 | 258.44 | 40000 | 0 | 15115.1 | 0 | 258.44 | 0 | 0 | 11054.46 | 0 | 0 | 11054.46
2022072222 | 6 | 0.80511 | 64408.8 | 0 | 0 | 0.43625 | 15268.75 | 0 | 0 | 40000 | 0 | 15268.75 | 0 | 0 | 0 | 0 | 9140.05 | 0 | 0 | 9140.05
2022072223 | 6 | 0.76162 | 60929.6 | 0 | 0 | 0.48377 | 16931.95 | 0 | 0 | 40000 | 0 | 16931.95 | 0 | 0 | 0 | 0 | 3997.65 | 0 | 0 | 3997.65
2022072224 | 6 | 0.71893 | 57514.4 | 0 | 0 | 0.50745 | 17760.75 | 0 | 0 | 40000 | 0 | 17514.4 | 246.35 | 0 | 0 | 246.35 | 0 | 0 | 0 | 0
2022072301 | 7 | 0.67651 | 54120.8 | 0 | 0 | 0.52193 | 18267.55 | 0 | 0 | 40000 | 0 | 14120.8 | 4146.75 | 0 | 0 | 4146.75 | 0 | 0 | 0 | 0
2022072302 | 7 | 0.64144 | 51315.2 | 0 | 0 | 0.51691 | 18091.85 | 0 | 0 | 40000 | 0 | 11315.2 | 6776.65 | 0 | 0 | 6776.65 | 0 | 0 | 0 | 0
2022072303 | 7 | 0.61561 | 49248.8 | 0 | 0 | 0.52273 | 18295.55 | 0 | 0 | 40000 | 0 | 9248.8 | 9046.75 | 0 | 0 | 9046.75 | 0 | 0 | 0 | 0
2022072304 | 7 | 0.59769 | 47815.2 | 0 | 0 | 0.52526 | 18384.1 | 0 | 0 | 40000 | 0 | 7815.2 | 10568.9 | 0 | 0 | 10568.9 | 0 | 0 | 0 | 0
2022072305 | 7 | 0.58541 | 46832.8 | 0 | 0 | 0.50131 | 17545.85 | 0 | 0 | 40000 | 0 | 6832.8 | 10713.05 | 0 | 0 | 10713.05 | 0 | 0 | 0 | 0
2022072306 | 7 | 0.58008 | 46406.4 | 0 | 0 | 0.48061 | 16821.35 | 0 | 0 | 40000 | 0 | 6406.4 | 10414.95 | 0 | 0 | 10414.95 | 0 | 0 | 0 | 0
2022072307 | 7 | 0.5793 | 46344 | 0 | 0 | 0.46303 | 16206.05 | 0.00113 | 15.82 | 40000 | 0 | 6344 | 9862.05 | 0 | 15.82 | 9877.87 | 0 | 0 | 0 | 0
2022072308 | 7 | 0.58653 | 46922.4 | 0 | 0 | 0.4232 | 14812 | 0.09551 | 1337.14 | 40000 | 0 | 6922.4 | 7889.6 | 0 | 1337.14 | 9226.74 | 0 | 0 | 0 | 0
2022072309 | 7 | 0.62775 | 50220 | 0 | 0 | 0.39621 | 13867.35 | 0.43398 | 6075.72 | 40000 | 0 | 10220 | 3647.35 | 0 | 6075.72 | 9723.07 | 0 | 0 | 0 | 0
2022072310 | 7 | 0.68529 | 54823.2 | 0 | 0 | 0.46843 | 16395.05 | 0.68303 | 9562.42 | 40000 | 0 | 14823.2 | 1571.85 | 0 | 9562.42 | 11134.27 | 0 | 0 | 0 | 0
2022072311 | 7 | 0.74014 | 59211.2 | 0 | 0 | 0.45336 | 15867.6 | 0.75558 | 10578.12 | 40000 | 0 | 15867.6 | 0 | 3343.6 | 7234.52 | 7234.52 | 0 | 0 | 0 | 0
2022072312 | 7 | 0.78931 | 63144.8 | 0 | 0 | 0.41171 | 14409.85 | 0.75521 | 10572.94 | 40000 | 0 | 14409.85 | 0 | 8734.95 | 1837.99 | 1837.99 | 0 | 0 | 0 | 0
2022072313 | 7 | 0.8286 | 66288 | 0 | 0 | 0.36865 | 12902.75 | 0.73684 | 10315.76 | 40000 | 0 | 12902.75 | 0 | 10315.76 | 0 | 0 | 3069.49 | 0 | 0 | 3069.49
2022072314 | 7 | 0.85839 | 68671.2 | 0 | 0 | 0.33956 | 11884.6 | 0.75936 | 10631.04 | 40000 | 0 | 11884.6 | 0 | 10631.04 | 0 | 0 | 6155.56 | 0 | 0 | 6155.56
2022072315 | 7 | 0.8867 | 70936 | 0 | 0 | 0.3499 | 12246.5 | 0.76401 | 10696.14 | 40000 | 0 | 12246.5 | 0 | 10696.14 | 0 | 0 | 7993.36 | 0 | 0 | 7993.36
2022072316 | 7 | 0.91056 | 72844.8 | 0 | 0 | 0.37806 | 13232.1 | 0.73141 | 10239.74 | 40000 | 0 | 13232.1 | 0 | 10239.74 | 0 | 0 | 9372.96 | 0 | 0 | 9372.96
2022072317 | 7 | 0.92678 | 74142.4 | 0 | 0 | 0.39603 | 13861.05 | 0.71507 | 10010.98 | 40000 | 0 | 13861.05 | 0 | 10010.98 | 0 | 0 | 10270.37 | 0 | 0 | 10270.37
2022072318 | 7 | 0.9265 | 74120 | 0 | 0 | 0.41116 | 14390.6 | 0.69676 | 9754.64 | 40000 | 0 | 14390.6 | 0 | 9754.64 | 0 | 0 | 9974.76 | 0 | 0 | 9974.76
2022072319 | 7 | 0.91139 | 72911.2 | 0 | 0 | 0.44417 | 15545.95 | 0.5902 | 8262.8 | 40000 | 0 | 15545.95 | 0 | 8262.8 | 0 | 0 | 9102.45 | 0 | 0 | 9102.45
2022072320 | 7 | 0.88439 | 70751.2 | 0 | 0 | 0.48232 | 16881.2 | 0.33912 | 4747.68 | 40000 | 0 | 16881.2 | 0 | 4747.68 | 0 | 0 | 9122.32 | 0 | 0 | 9122.32
2022072321 | 7 | 0.84874 | 67899.2 | 0 | 0 | 0.48791 | 17076.85 | 0.03869 | 541.66 | 40000 | 0 | 17076.85 | 0 | 541.66 | 0 | 0 | 10280.69 | 0 | 0 | 10280.69
2022072322 | 7 | 0.82196 | 65756.8 | 0 | 0 | 0.50343 | 17620.05 | 0 | 0 | 40000 | 0 | 17620.05 | 0 | 0 | 0 | 0 | 8136.75 | 0 | 0 | 8136.75
2022072323 | 7 | 0.78133 | 62506.4 | 0 | 0 | 0.56214 | 19674.9 | 0 | 0 | 40000 | 0 | 19674.9 | 0 | 0 | 0 | 0 | 2831.5 | 0 | 0 | 2831.5
2022072324 | 7 | 0.73876 | 59100.8 | 0 | 0 | 0.62152 | 21753.2 | 5e-05 | 0.7 | 40000 | 0 | 19100.8 | 2652.4 | 0 | 0.7 | 2653.1 | 0 | 0 | 0 | 0
2022072401 | 1 | 0.69903 | 55922.4 | 0 | 0 | 0.63485 | 22219.75 | 5e-05 | 0.7 | 40000 | 0 | 15922.4 | 6297.35 | 0 | 0.7 | 6298.05 | 0 | 0 | 0 | 0
2022072402 | 1 | 0.66803 | 53442.4 | 0 | 0 | 0.61545 | 21540.75 | 5e-05 | 0.7 | 40000 | 0 | 13442.4 | 8098.35 | 0 | 0.7 | 8099.05 | 0 | 0 | 0 | 0
2022072403 | 1 | 0.64221 | 51376.8 | 0 | 0 | 0.59841 | 20944.35 | 5e-05 | 0.7 | 40000 | 0 | 11376.8 | 9567.55 | 0 | 0.7 | 9568.25 | 0 | 0 | 0 | 0
2022072404 | 1 | 0.62033 | 49626.4 | 0 | 0 | 0.57389 | 20086.15 | 0 | 0 | 40000 | 0 | 9626.4 | 10459.75 | 0 | 0 | 10459.75 | 0 | 0 | 0 | 0
2022072405 | 1 | 0.60521 | 48416.8 | 0 | 0 | 0.54167 | 18958.45 | 0 | 0 | 40000 | 0 | 8416.8 | 10541.65 | 0 | 0 | 10541.65 | 0 | 0 | 0 | 0
2022072406 | 1 | 0.59621 | 47696.8 | 0 | 0 | 0.50682 | 17738.7 | 0 | 0 | 40000 | 0 | 7696.8 | 10041.9 | 0 | 0 | 10041.9 | 0 | 0 | 0 | 0
2022072407 | 1 | 0.58618 | 46894.4 | 0 | 0 | 0.46713 | 16349.55 | 0.00107 | 14.98 | 40000 | 0 | 6894.4 | 9455.15 | 0 | 14.98 | 9470.13 | 0 | 0 | 0 | 0
2022072408 | 1 | 0.58854 | 47083.2 | 0 | 0 | 0.43018 | 15056.3 | 0.12284 | 1719.76 | 40000 | 0 | 7083.2 | 7973.1 | 0 | 1719.76 | 9692.86 | 0 | 0 | 0 | 0
2022072409 | 1 | 0.63009 | 50407.2 | 0 | 0 | 0.4205 | 14717.5 | 0.50555 | 7077.7 | 40000 | 0 | 10407.2 | 4310.3 | 0 | 7077.7 | 11388 | 0 | 0 | 0 | 0
2022072410 | 1 | 0.68467 | 54773.6 | 0 | 0 | 0.46335 | 16217.25 | 0.70126 | 9817.64 | 40000 | 0 | 14773.6 | 1443.65 | 0 | 9817.64 | 11261.29 | 0 | 0 | 0 | 0
2022072411 | 1 | 0.73814 | 59051.2 | 0 | 0 | 0.3863 | 13520.5 | 0.7567 | 10593.8 | 40000 | 0 | 13520.5 | 0 | 5530.7 | 5063.1 | 5063.1 | 0 | 0 | 0 | 0
2022072412 | 1 | 0.7866 | 62928 | 0 | 0 | 0.3208 | 11228 | 0.77484 | 10847.76 | 40000 | 0 | 11228 | 0 | 10847.76 | 0 | 0 | 852.24 | 0 | 0 | 852.24
2022072413 | 1 | 0.83414 | 66731.2 | 0 | 0 | 0.27208 | 9522.8 | 0.76813 | 10753.82 | 40000 | 0 | 9522.8 | 0 | 10753.82 | 0 | 0 | 6454.58 | 0 | 0 | 6454.58
2022072414 | 1 | 0.87282 | 69825.6 | 0 | 0 | 0.24498 | 8574.3 | 0.71736 | 10043.04 | 40000 | 0 | 8574.3 | 0 | 10043.04 | 0 | 0 | 11208.26 | 0 | 0 | 11208.26
2022072415 | 1 | 0.90325 | 72260 | 0 | 0 | 0.25741 | 9009.35 | 0.70302 | 9842.28 | 40000 | 0 | 9009.35 | 0 | 9842.28 | 0 | 0 | 13408.37 | 0 | 0 | 13408.37
2022072416 | 1 | 0.92542 | 74033.6 | 0 | 0 | 0.2681 | 9383.5 | 0.68045 | 9526.3 | 40000 | 0 | 9383.5 | 0 | 9526.3 | 0 | 0 | 15123.8 | 0 | 0 | 15123.8
2022072417 | 1 | 0.93865 | 75092 | 0 | 0 | 0.29217 | 10225.95 | 0.6713 | 9398.2 | 40000 | 0 | 10225.95 | 0 | 9398.2 | 0 | 0 | 15467.85 | 0 | 0 | 15467.85
2022072418 | 1 | 0.94364 | 75491.2 | 0 | 0 | 0.32155 | 11254.25 | 0.63783 | 8929.62 | 40000 | 0 | 11254.25 | 0 | 8929.62 | 0 | 0 | 15307.33 | 0 | 0 | 15307.33
2022072419 | 1 | 0.93258 | 74606.4 | 0 | 0 | 0.34706 | 12147.1 | 0.57331 | 8026.34 | 40000 | 0 | 12147.1 | 0 | 8026.34 | 0 | 0 | 14432.96 | 0 | 0 | 14432.96
2022072420 | 1 | 0.90886 | 72708.8 | 0 | 0 | 0.39537 | 13837.95 | 0.32063 | 4488.82 | 40000 | 0 | 13837.95 | 0 | 4488.82 | 0 | 0 | 14382.03 | 0 | 0 | 14382.03
2022072421 | 1 | 0.87565 | 70052 | 0 | 0 | 0.42841 | 14994.35 | 0.03317 | 464.38 | 40000 | 0 | 14994.35 | 0 | 464.38 | 0 | 0 | 14593.27 | 0 | 0 | 14593.27
2022072422 | 1 | 0.8469 | 67752 | 0 | 0 | 0.46511 | 16278.85 | 0 | 0 | 40000 | 0 | 16278.85 | 0 | 0 | 0 | 0 | 11473.15 | 0 | 0 | 11473.15
2022072423 | 1 | 0.79908 | 63926.4 | 0 | 0 | 0.53312 | 18659.2 | 0 | 0 | 40000 | 0 | 18659.2 | 0 | 0 | 0 | 0 | 5267.2 | 0 | 0 | 5267.2
2022072424 | 1 | 0.74898 | 59918.4 | 0 | 0 | 0.56512 | 19779.2 | 0 | 0 | 40000 | 0 | 19779.2 | 0 | 0 | 0 | 0 | 139.2 | 0 | 0 | 139.2
2022072501 | 2 | 0.70252 | 56201.6 | 0 | 0 | 0.57453 | 20108.55 | 0 | 0 | 40000 | 0 | 16201.6 | 3906.95 | 0 | 0 | 3906.95 | 0 | 0 | 0 | 0
2022072502 | 2 | 0.67115 | 53692 | 0 | 0 | 0.56765 | 19867.75 | 0 | 0 | 40000 | 0 | 13692 | 6175.75 | 0 | 0 | 6175.75 | 0 | 0 | 0 | 0
2022072503 | 2 | 0.6458 | 51664 | 0 | 0 | 0.5466 | 19131 | 0 | 0 | 40000 | 0 | 11664 | 7467 | 0 | 0 | 7467 | 0 | 0 | 0 | 0
2022072504 | 2 | 0.63042 | 50433.6 | 0 | 0 | 0.52355 | 18324.25 | 0 | 0 | 40000 | 0 | 10433.6 | 7890.65 | 0 | 0 | 7890.65 | 0 | 0 | 0 | 0
2022072505 | 2 | 0.62549 | 50039.2 | 0 | 0 | 0.51023 | 17858.05 | 0 | 0 | 40000 | 0 | 10039.2 | 7818.85 | 0 | 0 | 7818.85 | 0 | 0 | 0 | 0
2022072506 | 2 | 0.6271 | 50168 | 0 | 0 | 0.49399 | 17289.65 | 0 | 0 | 40000 | 0 | 10168 | 7121.65 | 0 | 0 | 7121.65 | 0 | 0 | 0 | 0
2022072507 | 2 | 0.63282 | 50625.6 | 0 | 0 | 0.45983 | 16094.05 | 0.00096 | 13.44 | 40000 | 0 | 10625.6 | 5468.45 | 0 | 13.44 | 5481.89 | 0 | 0 | 0 | 0
2022072508 | 2 | 0.64173 | 51338.4 | 0 | 0 | 0.39732 | 13906.2 | 0.12267 | 1717.38 | 40000 | 0 | 11338.4 | 2567.8 | 0 | 1717.38 | 4285.18 | 0 | 0 | 0 | 0
2022072509 | 2 | 0.67884 | 54307.2 | 0 | 0 | 0.36825 | 12888.75 | 0.50165 | 7023.1 | 40000 | 0 | 12888.75 | 0 | 1418.45 | 5604.65 | 5604.65 | 0 | 0 | 0 | 0
2022072510 | 2 | 0.73104 | 58483.2 | 0 | 0 | 0.43727 | 15304.45 | 0.71858 | 10060.12 | 40000 | 0 | 15304.45 | 0 | 3178.75 | 6881.37 | 6881.37 | 0 | 0 | 0 | 0
2022072511 | 2 | 0.78441 | 62752.8 | 0 | 0 | 0.40601 | 14210.35 | 0.78212 | 10949.68 | 40000 | 0 | 14210.35 | 0 | 8542.45 | 2407.23 | 2407.23 | 0 | 0 | 0 | 0
2022072512 | 2 | 0.8379 | 67032 | 0 | 0 | 0.34438 | 12053.3 | 0.78997 | 11059.58 | 40000 | 0 | 12053.3 | 0 | 11059.58 | 0 | 0 | 3919.12 | 0 | 0 | 3919.12
2022072513 | 2 | 0.89023 | 71218.4 | 0 | 0 | 0.29705 | 10396.75 | 0.78919 | 11048.66 | 40000 | 0 | 10396.75 | 0 | 11048.66 | 0 | 0 | 9772.99 | 0 | 0 | 9772.99
2022072514 | 2 | 0.93294 | 74635.2 | 0 | 0 | 0.31482 | 11018.7 | 0.76776 | 10748.64 | 40000 | 0 | 11018.7 | 0 | 10748.64 | 0 | 0 | 12867.86 | 0 | 0 | 12867.86
2022072515 | 2 | 0.96432 | 77145.6 | 0 | 0 | 0.34599 | 12109.65 | 0.7427 | 10397.8 | 40000 | 0 | 12109.65 | 0 | 10397.8 | 0 | 0 | 14638.15 | 0 | 0 | 14638.15
2022072516 | 2 | 0.97906 | 78324.8 | 0 | 0 | 0.36533 | 12786.55 | 0.70725 | 9901.5 | 40000 | 0 | 12786.55 | 0 | 9901.5 | 0 | 0 | 15636.75 | 0 | 0 | 15636.75
2022072517 | 2 | 0.9866 | 78928 | 0 | 0 | 0.37143 | 13000.05 | 0.69248 | 9694.72 | 40000 | 0 | 13000.05 | 0 | 9694.72 | 0 | 0 | 16233.23 | 0 | 0 | 16233.23
2022072518 | 2 | 0.9846 | 78768 | 0 | 0 | 0.3795 | 13282.5 | 0.6776 | 9486.4 | 40000 | 0 | 13282.5 | 0 | 9486.4 | 0 | 0 | 15999.1 | 0 | 0 | 15999.1
2022072519 | 2 | 0.96855 | 77484 | 0 | 0 | 0.40615 | 14215.25 | 0.58543 | 8196.02 | 40000 | 0 | 14215.25 | 0 | 8196.02 | 0 | 0 | 15072.73 | 0 | 0 | 15072.73
2022072520 | 2 | 0.93647 | 74917.6 | 0 | 0 | 0.43974 | 15390.9 | 0.30062 | 4208.68 | 40000 | 0 | 15390.9 | 0 | 4208.68 | 0 | 0 | 15318.02 | 0 | 0 | 15318.02
2022072521 | 2 | 0.89681 | 71744.8 | 0 | 0 | 0.45425 | 15898.75 | 0.02569 | 359.66 | 40000 | 0 | 15898.75 | 0 | 359.66 | 0 | 0 | 15486.39 | 0 | 0 | 15486.39
2022072522 | 2 | 0.86404 | 69123.2 | 0 | 0 | 0.48222 | 16877.7 | 0 | 0 | 40000 | 0 | 16877.7 | 0 | 0 | 0 | 0 | 12245.5 | 0 | 0 | 12245.5
2022072523 | 2 | 0.81358 | 65086.4 | 0 | 0 | 0.55181 | 19313.35 | 0 | 0 | 40000 | 0 | 19313.35 | 0 | 0 | 0 | 0 | 5773.05 | 0 | 0 | 5773.05
2022072524 | 2 | 0.75937 | 60749.6 | 0 | 0 | 0.59377 | 20781.95 | 0 | 0 | 40000 | 0 | 20749.6 | 32.35 | 0 | 0 | 32.35 | 0 | 0 | 0 | 0
2022072601 | 3 | 0.71125 | 56900 | 0 | 0 | 0.59875 | 20956.25 | 0 | 0 | 40000 | 0 | 16900 | 4056.25 | 0 | 0 | 4056.25 | 0 | 0 | 0 | 0
2022072602 | 3 | 0.67479 | 53983.2 | 0 | 0 | 0.58309 | 20408.15 | 0 | 0 | 40000 | 0 | 13983.2 | 6424.95 | 0 | 0 | 6424.95 | 0 | 0 | 0 | 0
2022072603 | 3 | 0.64765 | 51812 | 0 | 0 | 0.56945 | 19930.75 | 0 | 0 | 40000 | 0 | 11812 | 8118.75 | 0 | 0 | 8118.75 | 0 | 0 | 0 | 0
2022072604 | 3 | 0.62944 | 50355.2 | 0 | 0 | 0.55869 | 19554.15 | 0 | 0 | 40000 | 0 | 10355.2 | 9198.95 | 0 | 0 | 9198.95 | 0 | 0 | 0 | 0
2022072605 | 3 | 0.62071 | 49656.8 | 0 | 0 | 0.53594 | 18757.9 | 0 | 0 | 40000 | 0 | 9656.8 | 9101.1 | 0 | 0 | 9101.1 | 0 | 0 | 0 | 0
2022072606 | 3 | 0.623 | 49840 | 0 | 0 | 0.49827 | 17439.45 | 0 | 0 | 40000 | 0 | 9840 | 7599.45 | 0 | 0 | 7599.45 | 0 | 0 | 0 | 0
2022072607 | 3 | 0.63105 | 50484 | 0 | 0 | 0.46218 | 16176.3 | 0.00085 | 11.9 | 40000 | 0 | 10484 | 5692.3 | 0 | 11.9 | 5704.2 | 0 | 0 | 0 | 0
2022072608 | 3 | 0.6368 | 50944 | 0 | 0 | 0.41932 | 14676.2 | 0.12449 | 1742.86 | 40000 | 0 | 10944 | 3732.2 | 0 | 1742.86 | 5475.06 | 0 | 0 | 0 | 0
2022072609 | 3 | 0.67349 | 53879.2 | 0 | 0 | 0.38883 | 13609.05 | 0.51521 | 7212.94 | 40000 | 0 | 13609.05 | 0 | 270.15 | 6942.79 | 6942.79 | 0 | 0 | 0 | 0
2022072610 | 3 | 0.7202 | 57616 | 0 | 0 | 0.44411 | 15543.85 | 0.63984 | 8957.76 | 40000 | 0 | 15543.85 | 0 | 2072.15 | 6885.61 | 6885.61 | 0 | 0 | 0 | 0
2022072611 | 3 | 0.77182 | 61745.6 | 0 | 0 | 0.41128 | 14394.8 | 0.75929 | 10630.06 | 40000 | 0 | 14394.8 | 0 | 7350.8 | 3279.26 | 3279.26 | 0 | 0 | 0 | 0
2022072612 | 3 | 0.82905 | 66324 | 0 | 0 | 0.36091 | 12631.85 | 0.78919 | 11048.66 | 40000 | 0 | 12631.85 | 0 | 11048.66 | 0 | 0 | 2643.49 | 0 | 0 | 2643.49
2022072613 | 3 | 0.87766 | 70212.8 | 0 | 0 | 0.30967 | 10838.45 | 0.77365 | 10831.1 | 40000 | 0 | 10838.45 | 0 | 10831.1 | 0 | 0 | 8543.25 | 0 | 0 | 8543.25
2022072614 | 3 | 0.91833 | 73466.4 | 0 | 0 | 0.29784 | 10424.4 | 0.75245 | 10534.3 | 40000 | 0 | 10424.4 | 0 | 10534.3 | 0 | 0 | 12507.7 | 0 | 0 | 12507.7
2022072615 | 3 | 0.94977 | 75981.6 | 0 | 0 | 0.29816 | 10435.6 | 0.7269 | 10176.6 | 40000 | 0 | 10435.6 | 0 | 10176.6 | 0 | 0 | 15369.4 | 0 | 0 | 15369.4
2022072616 | 3 | 0.9704 | 77632 | 0 | 0 | 0.31081 | 10878.35 | 0.71016 | 9942.24 | 40000 | 0 | 10878.35 | 0 | 9942.24 | 0 | 0 | 16811.41 | 0 | 0 | 16811.41
2022072617 | 3 | 0.98376 | 78700.8 | 0 | 0 | 0.32479 | 11367.65 | 0.70467 | 9865.38 | 40000 | 0 | 11367.65 | 0 | 9865.38 | 0 | 0 | 17467.77 | 0 | 0 | 17467.77
2022072618 | 3 | 0.9843 | 78744 | 0 | 0 | 0.33786 | 11825.1 | 0.7065 | 9891 | 40000 | 0 | 11825.1 | 0 | 9891 | 0 | 0 | 17027.9 | 0 | 0 | 17027.9
2022072619 | 3 | 0.96769 | 77415.2 | 0 | 0 | 0.36182 | 12663.7 | 0.6074 | 8503.6 | 40000 | 0 | 12663.7 | 0 | 8503.6 | 0 | 0 | 16247.9 | 0 | 0 | 16247.9
2022072620 | 3 | 0.93527 | 74821.6 | 0 | 0 | 0.39054 | 13668.9 | 0.30672 | 4294.08 | 40000 | 0 | 13668.9 | 0 | 4294.08 | 0 | 0 | 16858.62 | 0 | 0 | 16858.62
2022072621 | 3 | 0.89787 | 71829.6 | 0 | 0 | 0.4037 | 14129.5 | 0.02731 | 382.34 | 40000 | 0 | 14129.5 | 0 | 382.34 | 0 | 0 | 17317.76 | 0 | 0 | 17317.76
2022072622 | 3 | 0.86833 | 69466.4 | 0 | 0 | 0.43167 | 15108.45 | 0 | 0 | 40000 | 0 | 15108.45 | 0 | 0 | 0 | 0 | 14357.95 | 0 | 0 | 14357.95
2022072623 | 3 | 0.82106 | 65684.8 | 0 | 0 | 0.50578 | 17702.3 | 0 | 0 | 40000 | 0 | 17702.3 | 0 | 0 | 0 | 0 | 7982.5 | 0 | 0 | 7982.5
2022072624 | 3 | 0.77003 | 61602.4 | 0 | 0 | 0.55295 | 19353.25 | 0 | 0 | 40000 | 0 | 19353.25 | 0 | 0 | 0 | 0 | 2249.15 | 0 | 0 | 2249.15
2022072701 | 4 | 0.72315 | 57852 | 0 | 0 | 0.57182 | 20013.7 | 0 | 0 | 40000 | 0 | 17852 | 2161.7 | 0 | 0 | 2161.7 | 0 | 0 | 0 | 0
2022072702 | 4 | 0.68739 | 54991.2 | 0 | 0 | 0.55759 | 19515.65 | 0 | 0 | 40000 | 0 | 14991.2 | 4524.45 | 0 | 0 | 4524.45 | 0 | 0 | 0 | 0
2022072703 | 4 | 0.66254 | 53003.2 | 0 | 0 | 0.53987 | 18895.45 | 0 | 0 | 40000 | 0 | 13003.2 | 5892.25 | 0 | 0 | 5892.25 | 0 | 0 | 0 | 0
2022072704 | 4 | 0.64537 | 51629.6 | 0 | 0 | 0.51545 | 18040.75 | 0 | 0 | 40000 | 0 | 11629.6 | 6411.15 | 0 | 0 | 6411.15 | 0 | 0 | 0 | 0
2022072705 | 4 | 0.63369 | 50695.2 | 0 | 0 | 0.50437 | 17652.95 | 0 | 0 | 40000 | 0 | 10695.2 | 6957.75 | 0 | 0 | 6957.75 | 0 | 0 | 0 | 0
2022072706 | 4 | 0.63566 | 50852.8 | 0 | 0 | 0.48166 | 16858.1 | 0 | 0 | 40000 | 0 | 10852.8 | 6005.3 | 0 | 0 | 6005.3 | 0 | 0 | 0 | 0
2022072707 | 4 | 0.64558 | 51646.4 | 0 | 0 | 0.44781 | 15673.35 | 0.00062 | 8.68 | 40000 | 0 | 11646.4 | 4026.95 | 0 | 8.68 | 4035.63 | 0 | 0 | 0 | 0
2022072708 | 4 | 0.65109 | 52087.2 | 0 | 0 | 0.39066 | 13673.1 | 0.11483 | 1607.62 | 40000 | 0 | 12087.2 | 1585.9 | 0 | 1607.62 | 3193.52 | 0 | 0 | 0 | 0
2022072709 | 4 | 0.68424 | 54739.2 | 0 | 0 | 0.33228 | 11629.8 | 0.5005 | 7007 | 40000 | 0 | 11629.8 | 0 | 3109.4 | 3897.6 | 3897.6 | 0 | 0 | 0 | 0
2022072710 | 4 | 0.73103 | 58482.4 | 0 | 0 | 0.347 | 12145 | 0.70362 | 9850.68 | 40000 | 0 | 12145 | 0 | 6337.4 | 3513.28 | 3513.28 | 0 | 0 | 0 | 0
2022072711 | 4 | 0.7825 | 62600 | 0 | 0 | 0.29407 | 10292.45 | 0.7526 | 10536.4 | 40000 | 0 | 10292.45 | 0 | 10536.4 | 0 | 0 | 1771.15 | 0 | 0 | 1771.15
2022072712 | 4 | 0.83304 | 66643.2 | 0 | 0 | 0.21104 | 7386.4 | 0.75105 | 10514.7 | 40000 | 0 | 7386.4 | 0 | 10514.7 | 0 | 0 | 8742.1 | 0 | 0 | 8742.1
2022072713 | 4 | 0.87631 | 70104.8 | 0 | 0 | 0.19068 | 6673.8 | 0.7688 | 10763.2 | 40000 | 0 | 6673.8 | 0 | 10763.2 | 0 | 0 | 12667.8 | 0 | 0 | 12667.8
2022072714 | 4 | 0.91462 | 73169.6 | 0 | 0 | 0.19808 | 6932.8 | 0.72979 | 10217.06 | 40000 | 0 | 6932.8 | 0 | 10217.06 | 0 | 0 | 16019.74 | 0 | 0 | 16019.74
2022072715 | 4 | 0.93616 | 74892.8 | 0 | 0 | 0.23249 | 8137.15 | 0.72422 | 10139.08 | 40000 | 0 | 8137.15 | 0 | 10139.08 | 0 | 0 | 16616.57 | 0 | 0 | 16616.57
2022072716 | 4 | 0.94887 | 75909.6 | 0 | 0 | 0.23664 | 8282.4 | 0.69636 | 9749.04 | 40000 | 0 | 8282.4 | 0 | 9749.04 | 0 | 0 | 17878.16 | 0 | 0 | 17878.16
2022072717 | 4 | 0.95417 | 76333.6 | 0 | 0 | 0.26994 | 9447.9 | 0.65497 | 9169.58 | 40000 | 0 | 9447.9 | 0 | 9169.58 | 0 | 0 | 17716.12 | 0 | 0 | 17716.12
2022072718 | 4 | 0.94851 | 75880.8 | 0 | 0 | 0.30755 | 10764.25 | 0.63141 | 8839.74 | 40000 | 0 | 10764.25 | 0 | 8839.74 | 0 | 0 | 16276.81 | 0 | 0 | 16276.81
2022072719 | 4 | 0.93045 | 74436 | 0 | 0 | 0.34632 | 12121.2 | 0.56342 | 7887.88 | 40000 | 0 | 12121.2 | 0 | 7887.88 | 0 | 0 | 14426.92 | 0 | 0 | 14426.92
2022072720 | 4 | 0.90533 | 72426.4 | 0 | 0 | 0.37704 | 13196.4 | 0.2806 | 3928.4 | 40000 | 0 | 13196.4 | 0 | 3928.4 | 0 | 0 | 15301.6 | 0 | 0 | 15301.6
2022072721 | 4 | 0.87221 | 69776.8 | 0 | 0 | 0.39645 | 13875.75 | 0.01539 | 215.46 | 40000 | 0 | 13875.75 | 0 | 215.46 | 0 | 0 | 15685.59 | 0 | 0 | 15685.59
2022072722 | 4 | 0.84022 | 67217.6 | 0 | 0 | 0.43363 | 15177.05 | 0 | 0 | 40000 | 0 | 15177.05 | 0 | 0 | 0 | 0 | 12040.55 | 0 | 0 | 12040.55
2022072723 | 4 | 0.79339 | 63471.2 | 0 | 0 | 0.48376 | 16931.6 | 0 | 0 | 40000 | 0 | 16931.6 | 0 | 0 | 0 | 0 | 6539.6 | 0 | 0 | 6539.6
2022072724 | 4 | 0.74334 | 59467.2 | 0 | 0 | 0.52198 | 18269.3 | 0 | 0 | 40000 | 0 | 18269.3 | 0 | 0 | 0 | 0 | 1197.9 | 0 | 0 | 1197.9
2022072801 | 5 | 0.70185 | 56148 | 0 | 0 | 0.52869 | 18504.15 | 0 | 0 | 40000 | 0 | 16148 | 2356.15 | 0 | 0 | 2356.15 | 0 | 0 | 0 | 0
2022072802 | 5 | 0.66536 | 53228.8 | 0 | 0 | 0.50668 | 17733.8 | 0 | 0 | 40000 | 0 | 13228.8 | 4505 | 0 | 0 | 4505 | 0 | 0 | 0 | 0
2022072803 | 5 | 0.64248 | 51398.4 | 0 | 0 | 0.4924 | 17234 | 0 | 0 | 40000 | 0 | 11398.4 | 5835.6 | 0 | 0 | 5835.6 | 0 | 0 | 0 | 0
2022072804 | 5 | 0.62268 | 49814.4 | 0 | 0 | 0.47066 | 16473.1 | 0 | 0 | 40000 | 0 | 9814.4 | 6658.7 | 0 | 0 | 6658.7 | 0 | 0 | 0 | 0
2022072805 | 5 | 0.61395 | 49116 | 0 | 0 | 0.44048 | 15416.8 | 0 | 0 | 40000 | 0 | 9116 | 6300.8 | 0 | 0 | 6300.8 | 0 | 0 | 0 | 0
2022072806 | 5 | 0.61925 | 49540 | 0 | 0 | 0.38611 | 13513.85 | 0 | 0 | 40000 | 0 | 9540 | 3973.85 | 0 | 0 | 3973.85 | 0 | 0 | 0 | 0
2022072807 | 5 | 0.62984 | 50387.2 | 0 | 0 | 0.34972 | 12240.2 | 0.00058 | 8.12 | 40000 | 0 | 10387.2 | 1853 | 0 | 8.12 | 1861.12 | 0 | 0 | 0 | 0
2022072808 | 5 | 0.64017 | 51213.6 | 0 | 0 | 0.31956 | 11184.6 | 0.1178 | 1649.2 | 40000 | 0 | 11184.6 | 0 | 29 | 1620.2 | 1620.2 | 0 | 0 | 0 | 0
2022072809 | 5 | 0.67648 | 54118.4 | 0 | 0 | 0.28839 | 10093.65 | 0.49875 | 6982.5 | 40000 | 0 | 10093.65 | 0 | 4024.75 | 2957.75 | 2957.75 | 0 | 0 | 0 | 0
2022072810 | 5 | 0.72759 | 58207.2 | 0 | 0 | 0.32563 | 11397.05 | 0.73584 | 10301.76 | 40000 | 0 | 11397.05 | 0 | 6810.15 | 3491.61 | 3491.61 | 0 | 0 | 0 | 0
2022072811 | 5 | 0.78222 | 62577.6 | 0 | 0 | 0.28192 | 9867.2 | 0.77736 | 10883.04 | 40000 | 0 | 9867.2 | 0 | 10883.04 | 0 | 0 | 1827.36 | 0 | 0 | 1827.36
2022072812 | 5 | 0.83289 | 66631.2 | 0 | 0 | 0.22242 | 7784.7 | 0.77838 | 10897.32 | 40000 | 0 | 7784.7 | 0 | 10897.32 | 0 | 0 | 7949.18 | 0 | 0 | 7949.18
2022072813 | 5 | 0.88066 | 70452.8 | 0 | 0 | 0.17288 | 6050.8 | 0.76904 | 10766.56 | 40000 | 0 | 6050.8 | 0 | 10766.56 | 0 | 0 | 13635.44 | 0 | 0 | 13635.44
2022072814 | 5 | 0.9193 | 73544 | 0 | 0 | 0.1697 | 5939.5 | 0.75563 | 10578.82 | 40000 | 0 | 5939.5 | 0 | 10578.82 | 0 | 0 | 17025.68 | 0 | 0 | 17025.68
2022072815 | 5 | 0.94287 | 75429.6 | 0 | 0 | 0.19677 | 6886.95 | 0.73231 | 10252.34 | 40000 | 0 | 6886.95 | 0 | 10252.34 | 0 | 0 | 18290.31 | 0 | 0 | 18290.31
2022072816 | 5 | 0.9549 | 76392 | 0 | 0 | 0.22171 | 7759.85 | 0.71767 | 10047.38 | 40000 | 0 | 7759.85 | 0 | 10047.38 | 0 | 0 | 18584.77 | 0 | 0 | 18584.77
2022072817 | 5 | 0.95276 | 76220.8 | 0 | 0 | 0.25987 | 9095.45 | 0.69756 | 9765.84 | 40000 | 0 | 9095.45 | 0 | 9765.84 | 0 | 0 | 17359.51 | 0 | 0 | 17359.51
2022072818 | 5 | 0.94449 | 75559.2 | 0 | 0 | 0.30458 | 10660.3 | 0.68088 | 9532.32 | 40000 | 0 | 10660.3 | 0 | 9532.32 | 0 | 0 | 15366.58 | 0 | 0 | 15366.58
2022072819 | 5 | 0.93002 | 74401.6 | 0 | 0 | 0.35067 | 12273.45 | 0.59425 | 8319.5 | 40000 | 0 | 12273.45 | 0 | 8319.5 | 0 | 0 | 13808.65 | 0 | 0 | 13808.65
2022072820 | 5 | 0.9016 | 72128 | 0 | 0 | 0.40381 | 14133.35 | 0.32251 | 4515.14 | 40000 | 0 | 14133.35 | 0 | 4515.14 | 0 | 0 | 13479.51 | 0 | 0 | 13479.51
2022072821 | 5 | 0.87107 | 69685.6 | 0 | 0 | 0.41615 | 14565.25 | 0.03151 | 441.14 | 40000 | 0 | 14565.25 | 0 | 441.14 | 0 | 0 | 14679.21 | 0 | 0 | 14679.21
2022072822 | 5 | 0.84288 | 67430.4 | 0 | 0 | 0.39705 | 13896.75 | 0 | 0 | 40000 | 0 | 13896.75 | 0 | 0 | 0 | 0 | 13533.65 | 0 | 0 | 13533.65
2022072823 | 5 | 0.79647 | 63717.6 | 0 | 0 | 0.43426 | 15199.1 | 0 | 0 | 40000 | 0 | 15199.1 | 0 | 0 | 0 | 0 | 8518.5 | 0 | 0 | 8518.5
2022072824 | 5 | 0.74625 | 59700 | 0 | 0 | 0.48775 | 17071.25 | 0 | 0 | 40000 | 0 | 17071.25 | 0 | 0 | 0 | 0 | 2628.75 | 0 | 0 | 2628.75
2022072901 | 6 | 0.70222 | 56177.6 | 0 | 0 | 0.50495 | 17673.25 | 0 | 0 | 40000 | 0 | 16177.6 | 1495.65 | 0 | 0 | 1495.65 | 0 | 0 | 0 | 0
2022072902 | 6 | 0.66612 | 53289.6 | 0 | 0 | 0.4775 | 16712.5 | 0 | 0 | 40000 | 0 | 13289.6 | 3422.9 | 0 | 0 | 3422.9 | 0 | 0 | 0 | 0
2022072903 | 6 | 0.63986 | 51188.8 | 0 | 0 | 0.43143 | 15100.05 | 0 | 0 | 40000 | 0 | 11188.8 | 3911.25 | 0 | 0 | 3911.25 | 0 | 0 | 0 | 0
2022072904 | 6 | 0.62499 | 49999.2 | 0 | 0 | 0.39011 | 13653.85 | 0 | 0 | 40000 | 0 | 9999.2 | 3654.65 | 0 | 0 | 3654.65 | 0 | 0 | 0 | 0
2022072905 | 6 | 0.61439 | 49151.2 | 0 | 0 | 0.37208 | 13022.8 | 0 | 0 | 40000 | 0 | 9151.2 | 3871.6 | 0 | 0 | 3871.6 | 0 | 0 | 0 | 0
2022072906 | 6 | 0.61876 | 49500.8 | 0 | 0 | 0.33756 | 11814.6 | 0 | 0 | 40000 | 0 | 9500.8 | 2313.8 | 0 | 0 | 2313.8 | 0 | 0 | 0 | 0
2022072907 | 6 | 0.62703 | 50162.4 | 0 | 0 | 0.28339 | 9918.65 | 0.00038 | 5.32 | 40000 | 0 | 9918.65 | 0 | 5.32 | 0 | 0 | 238.43 | 0 | 0 | 238.43
2022072908 | 6 | 0.63595 | 50876 | 0 | 0 | 0.24489 | 8571.15 | 0.11226 | 1571.64 | 40000 | 0 | 8571.15 | 0 | 1571.64 | 0 | 0 | 733.21 | 0 | 0 | 733.21
2022072909 | 6 | 0.67435 | 53948 | 0 | 0 | 0.21829 | 7640.15 | 0.5091 | 7127.4 | 40000 | 0 | 7640.15 | 0 | 6307.85 | 819.55 | 819.55 | 0 | 0 | 0 | 0
2022072910 | 6 | 0.72644 | 58115.2 | 0 | 0 | 0.23379 | 8182.65 | 0.69722 | 9761.08 | 40000 | 0 | 8182.65 | 0 | 9761.08 | 0 | 0 | 171.47 | 0 | 0 | 171.47
2022072911 | 6 | 0.78068 | 62454.4 | 0 | 0 | 0.20275 | 7096.25 | 0.7437 | 10411.8 | 40000 | 0 | 7096.25 | 0 | 10411.8 | 0 | 0 | 4946.35 | 0 | 0 | 4946.35
2022072912 | 6 | 0.83872 | 67097.6 | 0 | 0 | 0.17206 | 6022.1 | 0.74687 | 10456.18 | 40000 | 0 | 6022.1 | 0 | 10456.18 | 0 | 0 | 10619.32 | 0 | 0 | 10619.32
2022072913 | 6 | 0.88474 | 70779.2 | 0 | 0 | 0.17263 | 6042.05 | 0.73352 | 10269.28 | 40000 | 0 | 6042.05 | 0 | 10269.28 | 0 | 0 | 14467.87 | 0 | 0 | 14467.87
2022072914 | 6 | 0.91964 | 73571.2 | 0 | 0 | 0.20667 | 7233.45 | 0.70721 | 9900.94 | 40000 | 0 | 7233.45 | 0 | 9900.94 | 0 | 0 | 16436.81 | 0 | 0 | 16436.81
2022072915 | 6 | 0.93822 | 75057.6 | 0 | 0 | 0.24643 | 8625.05 | 0.68262 | 9556.68 | 40000 | 0 | 8625.05 | 0 | 9556.68 | 0 | 0 | 16875.87 | 0 | 0 | 16875.87
2022072916 | 6 | 0.95017 | 76013.6 | 0 | 0 | 0.29627 | 10369.45 | 0.63662 | 8912.68 | 40000 | 0 | 10369.45 | 0 | 8912.68 | 0 | 0 | 16731.47 | 0 | 0 | 16731.47
2022072917 | 6 | 0.95931 | 76744.8 | 0 | 0 | 0.33995 | 11898.25 | 0.61213 | 8569.82 | 40000 | 0 | 11898.25 | 0 | 8569.82 | 0 | 0 | 16276.73 | 0 | 0 | 16276.73
2022072918 | 6 | 0.95097 | 76077.6 | 0 | 0 | 0.3813 | 13345.5 | 0.56416 | 7898.24 | 40000 | 0 | 13345.5 | 0 | 7898.24 | 0 | 0 | 14833.86 | 0 | 0 | 14833.86
2022072919 | 6 | 0.91982 | 73585.6 | 0 | 0 | 0.4363 | 15270.5 | 0.53531 | 7494.34 | 40000 | 0 | 15270.5 | 0 | 7494.34 | 0 | 0 | 10820.76 | 0 | 0 | 10820.76
2022072920 | 6 | 0.88259 | 70607.2 | 0 | 0 | 0.42733 | 14956.55 | 0.30073 | 4210.22 | 40000 | 0 | 14956.55 | 0 | 4210.22 | 0 | 0 | 11440.43 | 0 | 0 | 11440.43
2022072921 | 6 | 0.85085 | 68068 | 0 | 0 | 0.37515 | 13130.25 | 0.02625 | 367.5 | 40000 | 0 | 13130.25 | 0 | 367.5 | 0 | 0 | 14570.25 | 0 | 0 | 14570.25
2022072922 | 6 | 0.82344 | 65875.2 | 0 | 0 | 0.38568 | 13498.8 | 0 | 0 | 40000 | 0 | 13498.8 | 0 | 0 | 0 | 0 | 12376.4 | 0 | 0 | 12376.4
2022072923 | 6 | 0.78222 | 62577.6 | 0 | 0 | 0.3693 | 12925.5 | 0 | 0 | 40000 | 0 | 12925.5 | 0 | 0 | 0 | 0 | 9652.1 | 0 | 0 | 9652.1
2022072924 | 6 | 0.73706 | 58964.8 | 0 | 0 | 0.37272 | 13045.2 | 0 | 0 | 40000 | 0 | 13045.2 | 0 | 0 | 0 | 0 | 5919.6 | 0 | 0 | 5919.6
2022073001 | 7 | 0.69487 | 55589.6 | 0 | 0 | 0.37373 | 13080.55 | 0 | 0 | 40000 | 0 | 13080.55 | 0 | 0 | 0 | 0 | 2509.05 | 0 | 0 | 2509.05
2022073002 | 7 | 0.66224 | 52979.2 | 0 | 0 | 0.36814 | 12884.9 | 0 | 0 | 40000 | 0 | 12884.9 | 0 | 0 | 0 | 0 | 94.3 | 0 | 0 | 94.3
2022073003 | 7 | 0.63699 | 50959.2 | 0 | 0 | 0.37021 | 12957.35 | 0 | 0 | 40000 | 0 | 10959.2 | 1998.15 | 0 | 0 | 1998.15 | 0 | 0 | 0 | 0
2022073004 | 7 | 0.61482 | 49185.6 | 0 | 0 | 0.35363 | 12377.05 | 0 | 0 | 40000 | 0 | 9185.6 | 3191.45 | 0 | 0 | 3191.45 | 0 | 0 | 0 | 0
2022073005 | 7 | 0.60324 | 48259.2 | 0 | 0 | 0.35913 | 12569.55 | 0 | 0 | 40000 | 0 | 8259.2 | 4310.35 | 0 | 0 | 4310.35 | 0 | 0 | 0 | 0
2022073006 | 7 | 0.59699 | 47759.2 | 0 | 0 | 0.32938 | 11528.3 | 0 | 0 | 40000 | 0 | 7759.2 | 3769.1 | 0 | 0 | 3769.1 | 0 | 0 | 0 | 0
2022073007 | 7 | 0.59412 | 47529.6 | 0 | 0 | 0.2833 | 9915.5 | 0.00037 | 5.18 | 40000 | 0 | 7529.6 | 2385.9 | 0 | 5.18 | 2391.08 | 0 | 0 | 0 | 0
2022073008 | 7 | 0.5968 | 47744 | 0 | 0 | 0.23731 | 8305.85 | 0.08195 | 1147.3 | 40000 | 0 | 7744 | 561.85 | 0 | 1147.3 | 1709.15 | 0 | 0 | 0 | 0
2022073009 | 7 | 0.63655 | 50924 | 0 | 0 | 0.20658 | 7230.3 | 0.43373 | 6072.22 | 40000 | 0 | 7230.3 | 0 | 3693.7 | 2378.52 | 2378.52 | 0 | 0 | 0 | 0
2022073010 | 7 | 0.68907 | 55125.6 | 0 | 0 | 0.21859 | 7650.65 | 0.65239 | 9133.46 | 40000 | 0 | 7650.65 | 0 | 7474.95 | 1658.51 | 1658.51 | 0 | 0 | 0 | 0
2022073011 | 7 | 0.74051 | 59240.8 | 0 | 0 | 0.20009 | 7003.15 | 0.74931 | 10490.34 | 40000 | 0 | 7003.15 | 0 | 10490.34 | 0 | 0 | 1747.31 | 0 | 0 | 1747.31
2022073012 | 7 | 0.79348 | 63478.4 | 0 | 0 | 0.19506 | 6827.1 | 0.75685 | 10595.9 | 40000 | 0 | 6827.1 | 0 | 10595.9 | 0 | 0 | 6055.4 | 0 | 0 | 6055.4
2022073013 | 7 | 0.84355 | 67484 | 0 | 0 | 0.18933 | 6626.55 | 0.71496 | 10009.44 | 40000 | 0 | 6626.55 | 0 | 10009.44 | 0 | 0 | 10848.01 | 0 | 0 | 10848.01
2022073014 | 7 | 0.88018 | 70414.4 | 0 | 0 | 0.20221 | 7077.35 | 0.71998 | 10079.72 | 40000 | 0 | 7077.35 | 0 | 10079.72 | 0 | 0 | 13257.33 | 0 | 0 | 13257.33
2022073015 | 7 | 0.90603 | 72482.4 | 0 | 0 | 0.22442 | 7854.7 | 0.69878 | 9782.92 | 40000 | 0 | 7854.7 | 0 | 9782.92 | 0 | 0 | 14844.78 | 0 | 0 | 14844.78
2022073016 | 7 | 0.9195 | 73560 | 0 | 0 | 0.24184 | 8464.4 | 0.71104 | 9954.56 | 40000 | 0 | 8464.4 | 0 | 9954.56 | 0 | 0 | 15141.04 | 0 | 0 | 15141.04
2022073017 | 7 | 0.92848 | 74278.4 | 0 | 0 | 0.26208 | 9172.8 | 0.68216 | 9550.24 | 40000 | 0 | 9172.8 | 0 | 9550.24 | 0 | 0 | 15555.36 | 0 | 0 | 15555.36
2022073018 | 7 | 0.92364 | 73891.2 | 0 | 0 | 0.28554 | 9993.9 | 0.65172 | 9124.08 | 40000 | 0 | 9993.9 | 0 | 9124.08 | 0 | 0 | 14773.22 | 0 | 0 | 14773.22
2022073019 | 7 | 0.90179 | 72143.2 | 0 | 0 | 0.29367 | 10278.45 | 0.55671 | 7793.94 | 40000 | 0 | 10278.45 | 0 | 7793.94 | 0 | 0 | 14070.81 | 0 | 0 | 14070.81
2022073020 | 7 | 0.86886 | 69508.8 | 0 | 0 | 0.29477 | 10316.95 | 0.29471 | 4125.94 | 40000 | 0 | 10316.95 | 0 | 4125.94 | 0 | 0 | 15065.91 | 0 | 0 | 15065.91
2022073021 | 7 | 0.83835 | 67068 | 0 | 0 | 0.31716 | 11100.6 | 0.03069 | 429.66 | 40000 | 0 | 11100.6 | 0 | 429.66 | 0 | 0 | 15537.74 | 0 | 0 | 15537.74
2022073022 | 7 | 0.81196 | 64956.8 | 0 | 0 | 0.36187 | 12665.45 | 0 | 0 | 40000 | 0 | 12665.45 | 0 | 0 | 0 | 0 | 12291.35 | 0 | 0 | 12291.35
2022073023 | 7 | 0.77547 | 62037.6 | 0 | 0 | 0.4337 | 15179.5 | 0 | 0 | 40000 | 0 | 15179.5 | 0 | 0 | 0 | 0 | 6858.1 | 0 | 0 | 6858.1
2022073024 | 7 | 0.73415 | 58732 | 0 | 0 | 0.47309 | 16558.15 | 0 | 0 | 40000 | 0 | 16558.15 | 0 | 0 | 0 | 0 | 2173.85 | 0 | 0 | 2173.85
2022073101 | 1 | 0.69492 | 55593.6 | 0 | 0 | 0.50105 | 17536.75 | 0 | 0 | 40000 | 0 | 15593.6 | 1943.15 | 0 | 0 | 1943.15 | 0 | 0 | 0 | 0
2022073102 | 1 | 0.6623 | 52984 | 0 | 0 | 0.51555 | 18044.25 | 0 | 0 | 40000 | 0 | 12984 | 5060.25 | 0 | 0 | 5060.25 | 0 | 0 | 0 | 0
2022073103 | 1 | 0.6358 | 50864 | 0 | 0 | 0.52433 | 18351.55 | 0 | 0 | 40000 | 0 | 10864 | 7487.55 | 0 | 0 | 7487.55 | 0 | 0 | 0 | 0
2022073104 | 1 | 0.6168 | 49344 | 0 | 0 | 0.52679 | 18437.65 | 0 | 0 | 40000 | 0 | 9344 | 9093.65 | 0 | 0 | 9093.65 | 0 | 0 | 0 | 0
2022073105 | 1 | 0.60109 | 48087.2 | 0 | 0 | 0.52283 | 18299.05 | 0 | 0 | 40000 | 0 | 8087.2 | 10211.85 | 0 | 0 | 10211.85 | 0 | 0 | 0 | 0
2022073106 | 1 | 0.59094 | 47275.2 | 0 | 0 | 0.50512 | 17679.2 | 0 | 0 | 40000 | 0 | 7275.2 | 10404 | 0 | 0 | 10404 | 0 | 0 | 0 | 0
2022073107 | 1 | 0.58259 | 46607.2 | 0 | 0 | 0.49001 | 17150.35 | 0.00024 | 3.36 | 40000 | 0 | 6607.2 | 10543.15 | 0 | 3.36 | 10546.51 | 0 | 0 | 0 | 0
2022073108 | 1 | 0.58149 | 46519.2 | 0 | 0 | 0.46795 | 16378.25 | 0.06787 | 950.18 | 40000 | 0 | 6519.2 | 9859.05 | 0 | 950.18 | 10809.23 | 0 | 0 | 0 | 0
2022073109 | 1 | 0.61651 | 49320.8 | 0 | 0 | 0.42124 | 14743.4 | 0.38584 | 5401.76 | 40000 | 0 | 9320.8 | 5422.6 | 0 | 5401.76 | 10824.36 | 0 | 0 | 0 | 0
2022073110 | 1 | 0.66791 | 53432.8 | 0 | 0 | 0.40599 | 14209.65 | 0.61342 | 8587.88 | 40000 | 0 | 13432.8 | 776.85 | 0 | 8587.88 | 9364.73 | 0 | 0 | 0 | 0
2022073111 | 1 | 0.7201 | 57608 | 0 | 0 | 0.37202 | 13020.7 | 0.7251 | 10151.4 | 40000 | 0 | 13020.7 | 0 | 4587.3 | 5564.1 | 5564.1 | 0 | 0 | 0 | 0
2022073112 | 1 | 0.77333 | 61866.4 | 0 | 0 | 0.33344 | 11670.4 | 0.72892 | 10204.88 | 40000 | 0 | 11670.4 | 0 | 10196 | 8.88 | 8.88 | 0 | 0 | 0 | 0
2022073113 | 1 | 0.8215 | 65720 | 0 | 0 | 0.30687 | 10740.45 | 0.72489 | 10148.46 | 40000 | 0 | 10740.45 | 0 | 10148.46 | 0 | 0 | 4831.09 | 0 | 0 | 4831.09
2022073114 | 1 | 0.86337 | 69069.6 | 0 | 0 | 0.28951 | 10132.85 | 0.74492 | 10428.88 | 40000 | 0 | 10132.85 | 0 | 10428.88 | 0 | 0 | 8507.87 | 0 | 0 | 8507.87
2022073115 | 1 | 0.89916 | 71932.8 | 0 | 0 | 0.27736 | 9707.6 | 0.75987 | 10638.18 | 40000 | 0 | 9707.6 | 0 | 10638.18 | 0 | 0 | 11587.02 | 0 | 0 | 11587.02
2022073116 | 1 | 0.92225 | 73780 | 0 | 0 | 0.25681 | 8988.35 | 0.75004 | 10500.56 | 40000 | 0 | 8988.35 | 0 | 10500.56 | 0 | 0 | 14291.09 | 0 | 0 | 14291.09
2022073117 | 1 | 0.9377 | 75016 | 0 | 0 | 0.25935 | 9077.25 | 0.71438 | 10001.32 | 40000 | 0 | 9077.25 | 0 | 10001.32 | 0 | 0 | 15937.43 | 0 | 0 | 15937.43
2022073118 | 1 | 0.9441 | 75528 | 0 | 0 | 0.26701 | 9345.35 | 0.66653 | 9331.42 | 40000 | 0 | 9345.35 | 0 | 9331.42 | 0 | 0 | 16851.23 | 0 | 0 | 16851.23
2022073119 | 1 | 0.93167 | 74533.6 | 0 | 0 | 0.28991 | 10146.85 | 0.55864 | 7820.96 | 40000 | 0 | 10146.85 | 0 | 7820.96 | 0 | 0 | 16565.79 | 0 | 0 | 16565.79
2022073120 | 1 | 0.90197 | 72157.6 | 0 | 0 | 0.32284 | 11299.4 | 0.27035 | 3784.9 | 40000 | 0 | 11299.4 | 0 | 3784.9 | 0 | 0 | 17073.3 | 0 | 0 | 17073.3
2022073121 | 1 | 0.86785 | 69428 | 0 | 0 | 0.35446 | 12406.1 | 0.02129 | 298.06 | 40000 | 0 | 12406.1 | 0 | 298.06 | 0 | 0 | 16723.84 | 0 | 0 | 16723.84
2022073122 | 1 | 0.83806 | 67044.8 | 0 | 0 | 0.41478 | 14517.3 | 0 | 0 | 40000 | 0 | 14517.3 | 0 | 0 | 0 | 0 | 12527.5 | 0 | 0 | 12527.5
2022073123 | 1 | 0.79076 | 63260.8 | 0 | 0 | 0.48769 | 17069.15 | 0 | 0 | 40000 | 0 | 17069.15 | 0 | 0 | 0 | 0 | 6191.65 | 0 | 0 | 6191.65
2022073124 | 1 | 0.74041 | 59232.8 | 0 | 0 | 0.52614 | 18414.9 | 0 | 0 | 40000 | 0 | 18414.9 | 0 | 0 | 0 | 0 | 817.9 | 0 | 0 | 817.9
2022080101 | 2 | 0.69492 | 55593.6 | 0 | 0 | 0.53508 | 18727.8 | 0 | 0 | 40000 | 0 | 15593.6 | 3134.2 | 0 | 0 | 3134.2 | 0 | 0 | 0 | 0
2022080102 | 2 | 0.65983 | 52786.4 | 0 | 0 | 0.5365 | 18777.5 | 0 | 0 | 40000 | 0 | 12786.4 | 5991.1 | 0 | 0 | 5991.1 | 0 | 0 | 0 | 0
2022080103 | 2 | 0.63715 | 50972 | 0 | 0 | 0.53597 | 18758.95 | 0 | 0 | 40000 | 0 | 10972 | 7786.95 | 0 | 0 | 7786.95 | 0 | 0 | 0 | 0
2022080104 | 2 | 0.62334 | 49867.2 | 0 | 0 | 0.5379 | 18826.5 | 0 | 0 | 40000 | 0 | 9867.2 | 8959.3 | 0 | 0 | 8959.3 | 0 | 0 | 0 | 0
2022080105 | 2 | 0.61563 | 49250.4 | 0 | 0 | 0.52235 | 18282.25 | 0 | 0 | 40000 | 0 | 9250.4 | 9031.85 | 0 | 0 | 9031.85 | 0 | 0 | 0 | 0
2022080106 | 2 | 0.62236 | 49788.8 | 0 | 0 | 0.51402 | 17990.7 | 0 | 0 | 40000 | 0 | 9788.8 | 8201.9 | 0 | 0 | 8201.9 | 0 | 0 | 0 | 0
2022080107 | 2 | 0.63265 | 50612 | 0 | 0 | 0.48672 | 17035.2 | 0.0002 | 2.8 | 40000 | 0 | 10612 | 6423.2 | 0 | 2.8 | 6426 | 0 | 0 | 0 | 0
2022080108 | 2 | 0.63827 | 51061.6 | 0 | 0 | 0.42334 | 14816.9 | 0.08201 | 1148.14 | 40000 | 0 | 11061.6 | 3755.3 | 0 | 1148.14 | 4903.44 | 0 | 0 | 0 | 0
2022080109 | 2 | 0.67199 | 53759.2 | 0 | 0 | 0.3656 | 12796 | 0.45238 | 6333.32 | 40000 | 0 | 12796 | 0 | 963.2 | 5370.12 | 5370.12 | 0 | 0 | 0 | 0
2022080110 | 2 | 0.71677 | 57341.6 | 0 | 0 | 0.38378 | 13432.3 | 0.63184 | 8845.76 | 40000 | 0 | 13432.3 | 0 | 3909.3 | 4936.46 | 4936.46 | 0 | 0 | 0 | 0
2022080111 | 2 | 0.76322 | 61057.6 | 0 | 0 | 0.34624 | 12118.4 | 0.69601 | 9744.14 | 40000 | 0 | 12118.4 | 0 | 8939.2 | 804.94 | 804.94 | 0 | 0 | 0 | 0
2022080112 | 2 | 0.80993 | 64794.4 | 0 | 0 | 0.25115 | 8790.25 | 0.68811 | 9633.54 | 40000 | 0 | 8790.25 | 0 | 9633.54 | 0 | 0 | 6370.61 | 0 | 0 | 6370.61
2022080113 | 2 | 0.85201 | 68160.8 | 0 | 0 | 0.20576 | 7201.6 | 0.71394 | 9995.16 | 40000 | 0 | 7201.6 | 0 | 9995.16 | 0 | 0 | 10964.04 | 0 | 0 | 10964.04
2022080114 | 2 | 0.89183 | 71346.4 | 0 | 0 | 0.19931 | 6975.85 | 0.73012 | 10221.68 | 40000 | 0 | 6975.85 | 0 | 10221.68 | 0 | 0 | 14148.87 | 0 | 0 | 14148.87
2022080115 | 2 | 0.92183 | 73746.4 | 0 | 0 | 0.21441 | 7504.35 | 0.73411 | 10277.54 | 40000 | 0 | 7504.35 | 0 | 10277.54 | 0 | 0 | 15964.51 | 0 | 0 | 15964.51
2022080116 | 2 | 0.94656 | 75724.8 | 0 | 0 | 0.26835 | 9392.25 | 0.72411 | 10137.54 | 40000 | 0 | 9392.25 | 0 | 10137.54 | 0 | 0 | 16195.01 | 0 | 0 | 16195.01
2022080117 | 2 | 0.95315 | 76252 | 0 | 0 | 0.31209 | 10923.15 | 0.69461 | 9724.54 | 40000 | 0 | 10923.15 | 0 | 9724.54 | 0 | 0 | 15604.31 | 0 | 0 | 15604.31
2022080118 | 2 | 0.94956 | 75964.8 | 0 | 0 | 0.33971 | 11889.85 | 0.6594 | 9231.6 | 40000 | 0 | 11889.85 | 0 | 9231.6 | 0 | 0 | 14843.35 | 0 | 0 | 14843.35
2022080119 | 2 | 0.93927 | 75141.6 | 0 | 0 | 0.37966 | 13288.1 | 0.55902 | 7826.28 | 40000 | 0 | 13288.1 | 0 | 7826.28 | 0 | 0 | 14027.22 | 0 | 0 | 14027.22
2022080120 | 2 | 0.91105 | 72884 | 0 | 0 | 0.42116 | 14740.6 | 0.27091 | 3792.74 | 40000 | 0 | 14740.6 | 0 | 3792.74 | 0 | 0 | 14350.66 | 0 | 0 | 14350.66
2022080121 | 2 | 0.87951 | 70360.8 | 0 | 0 | 0.43721 | 15302.35 | 0.02645 | 370.3 | 40000 | 0 | 15302.35 | 0 | 370.3 | 0 | 0 | 14688.15 | 0 | 0 | 14688.15
2022080122 | 2 | 0.84869 | 67895.2 | 0 | 0 | 0.48116 | 16840.6 | 0 | 0 | 40000 | 0 | 16840.6 | 0 | 0 | 0 | 0 | 11054.6 | 0 | 0 | 11054.6
2022080123 | 2 | 0.79868 | 63894.4 | 0 | 0 | 0.52243 | 18285.05 | 0 | 0 | 40000 | 0 | 18285.05 | 0 | 0 | 0 | 0 | 5609.35 | 0 | 0 | 5609.35
2022080124 | 2 | 0.74537 | 59629.6 | 0 | 0 | 0.5329 | 18651.5 | 0 | 0 | 40000 | 0 | 18651.5 | 0 | 0 | 0 | 0 | 978.1 | 0 | 0 | 978.1
2022080201 | 3 | 0.69925 | 55940 | 0 | 0 | 0.55195 | 19318.25 | 0 | 0 | 40000 | 0 | 15940 | 3378.25 | 0 | 0 | 3378.25 | 0 | 0 | 0 | 0
2022080202 | 3 | 0.66568 | 53254.4 | 0 | 0 | 0.55998 | 19599.3 | 0 | 0 | 40000 | 0 | 13254.4 | 6344.9 | 0 | 0 | 6344.9 | 0 | 0 | 0 | 0
2022080203 | 3 | 0.64351 | 51480.8 | 0 | 0 | 0.56335 | 19717.25 | 0 | 0 | 40000 | 0 | 11480.8 | 8236.45 | 0 | 0 | 8236.45 | 0 | 0 | 0 | 0
2022080204 | 3 | 0.63011 | 50408.8 | 0 | 0 | 0.56257 | 19689.95 | 0 | 0 | 40000 | 0 | 10408.8 | 9281.15 | 0 | 0 | 9281.15 | 0 | 0 | 0 | 0
2022080205 | 3 | 0.62359 | 49887.2 | 0 | 0 | 0.55065 | 19272.75 | 0 | 0 | 40000 | 0 | 9887.2 | 9385.55 | 0 | 0 | 9385.55 | 0 | 0 | 0 | 0
2022080206 | 3 | 0.63041 | 50432.8 | 0 | 0 | 0.51815 | 18135.25 | 0 | 0 | 40000 | 0 | 10432.8 | 7702.45 | 0 | 0 | 7702.45 | 0 | 0 | 0 | 0
2022080207 | 3 | 0.64383 | 51506.4 | 0 | 0 | 0.51236 | 17932.6 | 0.00016 | 2.24 | 40000 | 0 | 11506.4 | 6426.2 | 0 | 2.24 | 6428.44 | 0 | 0 | 0 | 0
2022080208 | 3 | 0.65053 | 52042.4 | 0 | 0 | 0.48279 | 16897.65 | 0.08425 | 1179.5 | 40000 | 0 | 12042.4 | 4855.25 | 0 | 1179.5 | 6034.75 | 0 | 0 | 0 | 0
2022080209 | 3 | 0.68561 | 54848.8 | 0 | 0 | 0.47384 | 16584.4 | 0.42856 | 5999.84 | 40000 | 0 | 14848.8 | 1735.6 | 0 | 5999.84 | 7735.44 | 0 | 0 | 0 | 0
2022080210 | 3 | 0.73708 | 58966.4 | 0 | 0 | 0.55746 | 19511.1 | 0.55843 | 7818.02 | 40000 | 0 | 18966.4 | 544.7 | 0 | 7818.02 | 8362.72 | 0 | 0 | 0 | 0
2022080211 | 3 | 0.7893 | 63144 | 0 | 0 | 0.55426 | 19399.1 | 0.63541 | 8895.74 | 40000 | 0 | 19399.1 | 0 | 3744.9 | 5150.84 | 5150.84 | 0 | 0 | 0 | 0
2022080212 | 3 | 0.8421 | 67368 | 0 | 0 | 0.51534 | 18036.9 | 0.75445 | 10562.3 | 40000 | 0 | 18036.9 | 0 | 9331.1 | 1231.2 | 1231.2 | 0 | 0 | 0 | 0
2022080213 | 3 | 0.88953 | 71162.4 | 0 | 0 | 0.47796 | 16728.6 | 0.78159 | 10942.26 | 40000 | 0 | 16728.6 | 0 | 10942.26 | 0 | 0 | 3491.54 | 0 | 0 | 3491.54
2022080214 | 3 | 0.93413 | 74730.4 | 0 | 0 | 0.45109 | 15788.15 | 0.77554 | 10857.56 | 40000 | 0 | 15788.15 | 0 | 10857.56 | 0 | 0 | 8084.69 | 0 | 0 | 8084.69
2022080215 | 3 | 0.96304 | 77043.2 | 0 | 0 | 0.44793 | 15677.55 | 0.77883 | 10903.62 | 40000 | 0 | 15677.55 | 0 | 10903.62 | 0 | 0 | 10462.03 | 0 | 0 | 10462.03
2022080216 | 3 | 0.97477 | 77981.6 | 0 | 0 | 0.43933 | 15376.55 | 0.76051 | 10647.14 | 40000 | 0 | 15376.55 | 0 | 10647.14 | 0 | 0 | 11957.91 | 0 | 0 | 11957.91
2022080217 | 3 | 0.98173 | 78538.4 | 0 | 0 | 0.43361 | 15176.35 | 0.75719 | 10600.66 | 40000 | 0 | 15176.35 | 0 | 10600.66 | 0 | 0 | 12761.39 | 0 | 0 | 12761.39
2022080218 | 3 | 0.9815 | 78520 | 0 | 0 | 0.42808 | 14982.8 | 0.73547 | 10296.58 | 40000 | 0 | 14982.8 | 0 | 10296.58 | 0 | 0 | 13240.62 | 0 | 0 | 13240.62
2022080219 | 3 | 0.9739 | 77912 | 0 | 0 | 0.43236 | 15132.6 | 0.63368 | 8871.52 | 40000 | 0 | 15132.6 | 0 | 8871.52 | 0 | 0 | 13907.88 | 0 | 0 | 13907.88
2022080220 | 3 | 0.94562 | 75649.6 | 0 | 0 | 0.4653 | 16285.5 | 0.30985 | 4337.9 | 40000 | 0 | 16285.5 | 0 | 4337.9 | 0 | 0 | 15026.2 | 0 | 0 | 15026.2
2022080221 | 3 | 0.90945 | 72756 | 0 | 0 | 0.4784 | 16744 | 0.02838 | 397.32 | 40000 | 0 | 16744 | 0 | 397.32 | 0 | 0 | 15614.68 | 0 | 0 | 15614.68
2022080222 | 3 | 0.8789 | 70312 | 0 | 0 | 0.53091 | 18581.85 | 0 | 0 | 40000 | 0 | 18581.85 | 0 | 0 | 0 | 0 | 11730.15 | 0 | 0 | 11730.15
2022080223 | 3 | 0.8305 | 66440 | 0 | 0 | 0.60249 | 21087.15 | 0 | 0 | 40000 | 0 | 21087.15 | 0 | 0 | 0 | 0 | 5352.85 | 0 | 0 | 5352.85
2022080224 | 3 | 0.77697 | 62157.6 | 0 | 0 | 0.64955 | 22734.25 | 0 | 0 | 40000 | 0 | 22157.6 | 576.65 | 0 | 0 | 576.65 | 0 | 0 | 0 | 0
2022080301 | 4 | 0.73032 | 58425.6 | 0 | 0 | 0.68286 | 23900.1 | 0 | 0 | 40000 | 0 | 18425.6 | 5474.5 | 0 | 0 | 5474.5 | 0 | 0 | 0 | 0
2022080302 | 4 | 0.69382 | 55505.6 | 0 | 0 | 0.69021 | 24157.35 | 0 | 0 | 40000 | 0 | 15505.6 | 8651.75 | 0 | 0 | 8651.75 | 0 | 0 | 0 | 0
2022080303 | 4 | 0.66843 | 53474.4 | 0 | 0 | 0.69687 | 24390.45 | 0 | 0 | 40000 | 0 | 13474.4 | 10916.05 | 0 | 0 | 10916.05 | 0 | 0 | 0 | 0
2022080304 | 4 | 0.65294 | 52235.2 | 0 | 0 | 0.68675 | 24036.25 | 0 | 0 | 40000 | 0 | 12235.2 | 11801.05 | 0 | 0 | 11801.05 | 0 | 0 | 0 | 0
2022080305 | 4 | 0.64781 | 51824.8 | 0 | 0 | 0.67884 | 23759.4 | 0 | 0 | 40000 | 0 | 11824.8 | 11934.6 | 0 | 0 | 11934.6 | 0 | 0 | 0 | 0
2022080306 | 4 | 0.64986 | 51988.8 | 0 | 0 | 0.66322 | 23212.7 | 0 | 0 | 40000 | 0 | 11988.8 | 11223.9 | 0 | 0 | 11223.9 | 0 | 0 | 0 | 0
2022080307 | 4 | 0.65914 | 52731.2 | 0 | 0 | 0.64216 | 22475.6 | 0.00029 | 4.06 | 40000 | 0 | 12731.2 | 9744.4 | 0 | 4.06 | 9748.46 | 0 | 0 | 0 | 0
2022080308 | 4 | 0.66402 | 53121.6 | 0 | 0 | 0.61344 | 21470.4 | 0.09281 | 1299.34 | 40000 | 0 | 13121.6 | 8348.8 | 0 | 1299.34 | 9648.14 | 0 | 0 | 0 | 0
2022080309 | 4 | 0.69488 | 55590.4 | 0 | 0 | 0.59803 | 20931.05 | 0.40965 | 5735.1 | 40000 | 0 | 15590.4 | 5340.65 | 0 | 5735.1 | 11075.75 | 0 | 0 | 0 | 0
2022080310 | 4 | 0.74298 | 59438.4 | 0 | 0 | 0.64248 | 22486.8 | 0.44386 | 6214.04 | 40000 | 0 | 19438.4 | 3048.4 | 0 | 6214.04 | 9262.44 | 0 | 0 | 0 | 0
2022080311 | 4 | 0.79667 | 63733.6 | 0 | 0 | 0.59576 | 20851.6 | 0.61615 | 8626.1 | 40000 | 0 | 20851.6 | 0 | 2882 | 5744.1 | 5744.1 | 0 | 0 | 0 | 0
2022080312 | 4 | 0.85035 | 68028 | 0 | 0 | 0.52533 | 18386.55 | 0.74684 | 10455.76 | 40000 | 0 | 18386.55 | 0 | 9641.45 | 814.31 | 814.31 | 0 | 0 | 0 | 0
2022080313 | 4 | 0.89603 | 71682.4 | 0 | 0 | 0.45841 | 16044.35 | 0.76856 | 10759.84 | 40000 | 0 | 16044.35 | 0 | 10759.84 | 0 | 0 | 4878.21 | 0 | 0 | 4878.21
2022080314 | 4 | 0.9378 | 75024 | 0 | 0 | 0.38581 | 13503.35 | 0.75029 | 10504.06 | 40000 | 0 | 13503.35 | 0 | 10504.06 | 0 | 0 | 11016.59 | 0 | 0 | 11016.59
2022080315 | 4 | 0.96763 | 77410.4 | 0 | 0 | 0.35456 | 12409.6 | 0.74978 | 10496.92 | 40000 | 0 | 12409.6 | 0 | 10496.92 | 0 | 0 | 14503.88 | 0 | 0 | 14503.88
2022080316 | 4 | 0.97796 | 78236.8 | 0 | 0 | 0.33 | 11550 | 0.71798 | 10051.72 | 40000 | 0 | 11550 | 0 | 10051.72 | 0 | 0 | 16635.08 | 0 | 0 | 16635.08
2022080317 | 4 | 0.97945 | 78356 | 0 | 0 | 0.30876 | 10806.6 | 0.71799 | 10051.86 | 40000 | 0 | 10806.6 | 0 | 10051.86 | 0 | 0 | 17497.54 | 0 | 0 | 17497.54
2022080318 | 4 | 0.97588 | 78070.4 | 0 | 0 | 0.29369 | 10279.15 | 0.67937 | 9511.18 | 40000 | 0 | 10279.15 | 0 | 9511.18 | 0 | 0 | 18280.07 | 0 | 0 | 18280.07
2022080319 | 4 | 0.96154 | 76923.2 | 0 | 0 | 0.29927 | 10474.45 | 0.55367 | 7751.38 | 40000 | 0 | 10474.45 | 0 | 7751.38 | 0 | 0 | 18697.37 | 0 | 0 | 18697.37
2022080320 | 4 | 0.93218 | 74574.4 | 0 | 0 | 0.32194 | 11267.9 | 0.27135 | 3798.9 | 40000 | 0 | 11267.9 | 0 | 3798.9 | 0 | 0 | 19507.6 | 0 | 0 | 19507.6
2022080321 | 4 | 0.90146 | 72116.8 | 0 | 0 | 0.36477 | 12766.95 | 0.01691 | 236.74 | 40000 | 0 | 12766.95 | 0 | 236.74 | 0 | 0 | 19113.11 | 0 | 0 | 19113.11
2022080322 | 4 | 0.87369 | 69895.2 | 0 | 0 | 0.44511 | 15578.85 | 0 | 0 | 40000 | 0 | 15578.85 | 0 | 0 | 0 | 0 | 14316.35 | 0 | 0 | 14316.35
2022080323 | 4 | 0.82467 | 65973.6 | 0 | 0 | 0.53479 | 18717.65 | 0 | 0 | 40000 | 0 | 18717.65 | 0 | 0 | 0 | 0 | 7255.95 | 0 | 0 | 7255.95
2022080324 | 4 | 0.77234 | 61787.2 | 0 | 0 | 0.58315 | 20410.25 | 0 | 0 | 40000 | 0 | 20410.25 | 0 | 0 | 0 | 0 | 1376.95 | 0 | 0 | 1376.95
2022080401 | 5 | 0.72765 | 58212 | 0 | 0 | 0.5951 | 20828.5 | 0 | 0 | 40000 | 0 | 18212 | 2616.5 | 0 | 0 | 2616.5 | 0 | 0 | 0 | 0
2022080402 | 5 | 0.69257 | 55405.6 | 0 | 0 | 0.58622 | 20517.7 | 0 | 0 | 40000 | 0 | 15405.6 | 5112.1 | 0 | 0 | 5112.1 | 0 | 0 | 0 | 0
2022080403 | 5 | 0.66558 | 53246.4 | 0 | 0 | 0.56468 | 19763.8 | 0 | 0 | 40000 | 0 | 13246.4 | 6517.4 | 0 | 0 | 6517.4 | 0 | 0 | 0 | 0
2022080404 | 5 | 0.64744 | 51795.2 | 0 | 0 | 0.54042 | 18914.7 | 0 | 0 | 40000 | 0 | 11795.2 | 7119.5 | 0 | 0 | 7119.5 | 0 | 0 | 0 | 0
2022080405 | 5 | 0.63767 | 51013.6 | 0 | 0 | 0.53913 | 18869.55 | 0 | 0 | 40000 | 0 | 11013.6 | 7855.95 | 0 | 0 | 7855.95 | 0 | 0 | 0 | 0
2022080406 | 5 | 0.64318 | 51454.4 | 0 | 0 | 0.5104 | 17864 | 0 | 0 | 40000 | 0 | 11454.4 | 6409.6 | 0 | 0 | 6409.6 | 0 | 0 | 0 | 0
2022080407 | 5 | 0.65196 | 52156.8 | 0 | 0 | 0.45849 | 16047.15 | 0.00013 | 1.82 | 40000 | 0 | 12156.8 | 3890.35 | 0 | 1.82 | 3892.17 | 0 | 0 | 0 | 0
2022080408 | 5 | 0.65545 | 52436 | 0 | 0 | 0.40021 | 14007.35 | 0.07071 | 989.94 | 40000 | 0 | 12436 | 1571.35 | 0 | 989.94 | 2561.29 | 0 | 0 | 0 | 0
2022080409 | 5 | 0.69085 | 55268 | 0 | 0 | 0.36733 | 12856.55 | 0.41718 | 5840.52 | 40000 | 0 | 12856.55 | 0 | 2411.45 | 3429.07 | 3429.07 | 0 | 0 | 0 | 0
2022080410 | 5 | 0.7348 | 58784 | 0 | 0 | 0.3676 | 12866 | 0.65888 | 9224.32 | 40000 | 0 | 12866 | 0 | 5918 | 3306.32 | 3306.32 | 0 | 0 | 0 | 0
2022080411 | 5 | 0.78736 | 62988.8 | 0 | 0 | 0.31268 | 10943.8 | 0.72311 | 10123.54 | 40000 | 0 | 10943.8 | 0 | 10123.54 | 0 | 0 | 1921.46 | 0 | 0 | 1921.46
2022080412 | 5 | 0.84108 | 67286.4 | 0 | 0 | 0.26095 | 9133.25 | 0.75392 | 10554.88 | 40000 | 0 | 9133.25 | 0 | 10554.88 | 0 | 0 | 7598.27 | 0 | 0 | 7598.27
2022080413 | 5 | 0.89311 | 71448.8 | 0 | 0 | 0.21911 | 7668.85 | 0.76185 | 10665.9 | 40000 | 0 | 7668.85 | 0 | 10665.9 | 0 | 0 | 13114.05 | 0 | 0 | 13114.05
2022080414 | 5 | 0.93768 | 75014.4 | 0 | 0 | 0.21002 | 7350.7 | 0.751 | 10514 | 40000 | 0 | 7350.7 | 0 | 10514 | 0 | 0 | 17149.7 | 0 | 0 | 17149.7
2022080415 | 5 | 0.96905 | 77524 | 0 | 0 | 0.21241 | 7434.35 | 0.73114 | 10235.96 | 40000 | 0 | 7434.35 | 0 | 10235.96 | 0 | 0 | 19853.69 | 0 | 0 | 19853.69
2022080416 | 5 | 0.97743 | 78194.4 | 0 | 0 | 0.21405 | 7491.75 | 0.70991 | 9938.74 | 40000 | 0 | 7491.75 | 0 | 9938.74 | 0 | 0 | 20763.91 | 0 | 0 | 20763.91
2022080417 | 5 | 0.97596 | 78076.8 | 0 | 0 | 0.23796 | 8328.6 | 0.68307 | 9562.98 | 40000 | 0 | 8328.6 | 0 | 9562.98 | 0 | 0 | 20185.22 | 0 | 0 | 20185.22
2022080418 | 5 | 0.96886 | 77508.8 | 0 | 0 | 0.30062 | 10521.7 | 0.65572 | 9180.08 | 40000 | 0 | 10521.7 | 0 | 9180.08 | 0 | 0 | 17807.02 | 0 | 0 | 17807.02
2022080419 | 5 | 0.9503 | 76024 | 0 | 0 | 0.3544 | 12404 | 0.49753 | 6965.42 | 40000 | 0 | 12404 | 0 | 6965.42 | 0 | 0 | 16654.58 | 0 | 0 | 16654.58
2022080420 | 5 | 0.92168 | 73734.4 | 0 | 0 | 0.372 | 13020 | 0.22295 | 3121.3 | 40000 | 0 | 13020 | 0 | 3121.3 | 0 | 0 | 17593.1 | 0 | 0 | 17593.1
2022080421 | 5 | 0.88933 | 71146.4 | 0 | 0 | 0.36171 | 12659.85 | 0.01448 | 202.72 | 40000 | 0 | 12659.85 | 0 | 202.72 | 0 | 0 | 18283.83 | 0 | 0 | 18283.83
2022080422 | 5 | 0.85429 | 68343.2 | 0 | 0 | 0.39414 | 13794.9 | 0 | 0 | 40000 | 0 | 13794.9 | 0 | 0 | 0 | 0 | 14548.3 | 0 | 0 | 14548.3
2022080423 | 5 | 0.804 | 64320 | 0 | 0 | 0.41874 | 14655.9 | 0 | 0 | 40000 | 0 | 14655.9 | 0 | 0 | 0 | 0 | 9664.1 | 0 | 0 | 9664.1
2022080424 | 5 | 0.75162 | 60129.6 | 0 | 0 | 0.4475 | 15662.5 | 0 | 0 | 40000 | 0 | 15662.5 | 0 | 0 | 0 | 0 | 4467.1 | 0 | 0 | 4467.1
2022080501 | 6 | 0.70681 | 56544.8 | 0 | 0 | 0.42151 | 14752.85 | 0 | 0 | 40000 | 0 | 14752.85 | 0 | 0 | 0 | 0 | 1791.95 | 0 | 0 | 1791.95
2022080502 | 6 | 0.67288 | 53830.4 | 0 | 0 | 0.37827 | 13239.45 | 0 | 0 | 40000 | 0 | 13239.45 | 0 | 0 | 0 | 0 | 590.95 | 0 | 0 | 590.95
2022080503 | 6 | 0.648 | 51840 | 0 | 0 | 0.35726 | 12504.1 | 0 | 0 | 40000 | 0 | 11840 | 664.1 | 0 | 0 | 664.1 | 0 | 0 | 0 | 0
2022080504 | 6 | 0.63033 | 50426.4 | 0 | 0 | 0.35721 | 12502.35 | 0 | 0 | 40000 | 0 | 10426.4 | 2075.95 | 0 | 0 | 2075.95 | 0 | 0 | 0 | 0
2022080505 | 6 | 0.6229 | 49832 | 0 | 0 | 0.35983 | 12594.05 | 0 | 0 | 40000 | 0 | 9832 | 2762.05 | 0 | 0 | 2762.05 | 0 | 0 | 0 | 0
2022080506 | 6 | 0.6267 | 50136 | 0 | 0 | 0.34408 | 12042.8 | 0 | 0 | 40000 | 0 | 10136 | 1906.8 | 0 | 0 | 1906.8 | 0 | 0 | 0 | 0
2022080507 | 6 | 0.63803 | 51042.4 | 0 | 0 | 0.32512 | 11379.2 | 0.00016 | 2.24 | 40000 | 0 | 11042.4 | 336.8 | 0 | 2.24 | 339.04 | 0 | 0 | 0 | 0
2022080508 | 6 | 0.64352 | 51481.6 | 0 | 0 | 0.29504 | 10326.4 | 0.06684 | 935.76 | 40000 | 0 | 10326.4 | 0 | 935.76 | 0 | 0 | 219.44 | 0 | 0 | 219.44
2022080509 | 6 | 0.67602 | 54081.6 | 0 | 0 | 0.24631 | 8620.85 | 0.36676 | 5134.64 | 40000 | 0 | 8620.85 | 0 | 5134.64 | 0 | 0 | 326.11 | 0 | 0 | 326.11
2022080510 | 6 | 0.72307 | 57845.6 | 0 | 0 | 0.27533 | 9636.55 | 0.61355 | 8589.7 | 40000 | 0 | 9636.55 | 0 | 8209.05 | 380.65 | 380.65 | 0 | 0 | 0 | 0
2022080511 | 6 | 0.77617 | 62093.6 | 0 | 0 | 0.23715 | 8300.25 | 0.73496 | 10289.44 | 40000 | 0 | 8300.25 | 0 | 10289.44 | 0 | 0 | 3503.91 | 0 | 0 | 3503.91
2022080512 | 6 | 0.82742 | 66193.6 | 0 | 0 | 0.15614 | 5464.9 | 0.75432 | 10560.48 | 40000 | 0 | 5464.9 | 0 | 10560.48 | 0 | 0 | 10168.22 | 0 | 0 | 10168.22
2022080513 | 6 | 0.86531 | 69224.8 | 0 | 0 | 0.09647 | 3376.45 | 0.73592 | 10302.88 | 40000 | 0 | 3376.45 | 0 | 10302.88 | 0 | 0 | 15545.47 | 0 | 0 | 15545.47
2022080514 | 6 | 0.8941 | 71528 | 0 | 0 | 0.10065 | 3522.75 | 0.73461 | 10284.54 | 40000 | 0 | 3522.75 | 0 | 10284.54 | 0 | 0 | 17720.71 | 0 | 0 | 17720.71
2022080515 | 6 | 0.91236 | 72988.8 | 0 | 0 | 0.14704 | 5146.4 | 0.71214 | 9969.96 | 40000 | 0 | 5146.4 | 0 | 9969.96 | 0 | 0 | 17872.44 | 0 | 0 | 17872.44
2022080516 | 6 | 0.92731 | 74184.8 | 0 | 0 | 0.19745 | 6910.75 | 0.66926 | 9369.64 | 40000 | 0 | 6910.75 | 0 | 9369.64 | 0 | 0 | 17904.41 | 0 | 0 | 17904.41
2022080517 | 6 | 0.92982 | 74385.6 | 0 | 0 | 0.23471 | 8214.85 | 0.65498 | 9169.72 | 40000 | 0 | 8214.85 | 0 | 9169.72 | 0 | 0 | 17001.03 | 0 | 0 | 17001.03
2022080518 | 6 | 0.92097 | 73677.6 | 0 | 0 | 0.27537 | 9637.95 | 0.59264 | 8296.96 | 40000 | 0 | 9637.95 | 0 | 8296.96 | 0 | 0 | 15742.69 | 0 | 0 | 15742.69
2022080519 | 6 | 0.89898 | 71918.4 | 0 | 0 | 0.33545 | 11740.75 | 0.50058 | 7008.12 | 40000 | 0 | 11740.75 | 0 | 7008.12 | 0 | 0 | 13169.53 | 0 | 0 | 13169.53
2022080520 | 6 | 0.87017 | 69613.6 | 0 | 0 | 0.38839 | 13593.65 | 0.24281 | 3399.34 | 40000 | 0 | 13593.65 | 0 | 3399.34 | 0 | 0 | 12620.61 | 0 | 0 | 12620.61
2022080521 | 6 | 0.84214 | 67371.2 | 0 | 0 | 0.41432 | 14501.2 | 0.02139 | 299.46 | 40000 | 0 | 14501.2 | 0 | 299.46 | 0 | 0 | 12570.54 | 0 | 0 | 12570.54
2022080522 | 6 | 0.81365 | 65092 | 0 | 0 | 0.43883 | 15359.05 | 0.00468 | 65.52 | 40000 | 0 | 15359.05 | 0 | 65.52 | 0 | 0 | 9667.43 | 0 | 0 | 9667.43
2022080523 | 6 | 0.77164 | 61731.2 | 0 | 0 | 0.48823 | 17088.05 | 0.00468 | 65.52 | 40000 | 0 | 17088.05 | 0 | 65.52 | 0 | 0 | 4577.63 | 0 | 0 | 4577.63
2022080524 | 6 | 0.72467 | 57973.6 | 0 | 0 | 0.551 | 19285 | 0.00468 | 65.52 | 40000 | 0 | 17973.6 | 1311.4 | 0 | 65.52 | 1376.92 | 0 | 0 | 0 | 0
2022080601 | 7 | 0.68506 | 54804.8 | 0 | 0 | 0.55304 | 19356.4 | 0.00468 | 65.52 | 40000 | 0 | 14804.8 | 4551.6 | 0 | 65.52 | 4617.12 | 0 | 0 | 0 | 0
2022080602 | 7 | 0.64863 | 51890.4 | 0 | 0 | 0.52734 | 18456.9 | 0.00361 | 50.54 | 40000 | 0 | 11890.4 | 6566.5 | 0 | 50.54 | 6617.04 | 0 | 0 | 0 | 0
2022080603 | 7 | 0.62475 | 49980 | 0 | 0 | 0.49727 | 17404.45 | 0 | 0 | 40000 | 0 | 9980 | 7424.45 | 0 | 0 | 7424.45 | 0 | 0 | 0 | 0
2022080604 | 7 | 0.60354 | 48283.2 | 0 | 0 | 0.48692 | 17042.2 | 0 | 0 | 40000 | 0 | 8283.2 | 8759 | 0 | 0 | 8759 | 0 | 0 | 0 | 0
2022080605 | 7 | 0.58963 | 47170.4 | 0 | 0 | 0.47169 | 16509.15 | 0 | 0 | 40000 | 0 | 7170.4 | 9338.75 | 0 | 0 | 9338.75 | 0 | 0 | 0 | 0
2022080606 | 7 | 0.58559 | 46847.2 | 0 | 0 | 0.44278 | 15497.3 | 0 | 0 | 40000 | 0 | 6847.2 | 8650.1 | 0 | 0 | 8650.1 | 0 | 0 | 0 | 0
2022080607 | 7 | 0.58491 | 46792.8 | 0 | 0 | 0.4126 | 14441 | 0.00016 | 2.24 | 40000 | 0 | 6792.8 | 7648.2 | 0 | 2.24 | 7650.44 | 0 | 0 | 0 | 0
2022080608 | 7 | 0.58811 | 47048.8 | 0 | 0 | 0.37011 | 12953.85 | 0.07666 | 1073.24 | 40000 | 0 | 7048.8 | 5905.05 | 0 | 1073.24 | 6978.29 | 0 | 0 | 0 | 0
2022080609 | 7 | 0.61646 | 49316.8 | 0 | 0 | 0.27564 | 9647.4 | 0.41497 | 5809.58 | 40000 | 0 | 9316.8 | 330.6 | 0 | 5809.58 | 6140.18 | 0 | 0 | 0 | 0
2022080610 | 7 | 0.6555 | 52440 | 0 | 0 | 0.28088 | 9830.8 | 0.63246 | 8854.44 | 40000 | 0 | 9830.8 | 0 | 2609.2 | 6245.24 | 6245.24 | 0 | 0 | 0 | 0
2022080611 | 7 | 0.69836 | 55868.8 | 0 | 0 | 0.26408 | 9242.8 | 0.72177 | 10104.78 | 40000 | 0 | 9242.8 | 0 | 6626 | 3478.78 | 3478.78 | 0 | 0 | 0 | 0
2022080612 | 7 | 0.74377 | 59501.6 | 0 | 0 | 0.20912 | 7319.2 | 0.72519 | 10152.66 | 40000 | 0 | 7319.2 | 0 | 10152.66 | 0 | 0 | 2029.74 | 0 | 0 | 2029.74
2022080613 | 7 | 0.78605 | 62884 | 0 | 0 | 0.2028 | 7098 | 0.73039 | 10225.46 | 40000 | 0 | 7098 | 0 | 10225.46 | 0 | 0 | 5560.54 | 0 | 0 | 5560.54
2022080614 | 7 | 0.82689 | 66151.2 | 0 | 0 | 0.23223 | 8128.05 | 0.73684 | 10315.76 | 40000 | 0 | 8128.05 | 0 | 10315.76 | 0 | 0 | 7707.39 | 0 | 0 | 7707.39
2022080615 | 7 | 0.85633 | 68506.4 | 0 | 0 | 0.23177 | 8111.95 | 0.71074 | 9950.36 | 40000 | 0 | 8111.95 | 0 | 9950.36 | 0 | 0 | 10444.09 | 0 | 0 | 10444.09
2022080616 | 7 | 0.86869 | 69495.2 | 0 | 0 | 0.23416 | 8195.6 | 0.65913 | 9227.82 | 40000 | 0 | 8195.6 | 0 | 9227.82 | 0 | 0 | 12071.78 | 0 | 0 | 12071.78
2022080617 | 7 | 0.87396 | 69916.8 | 0 | 0 | 0.26425 | 9248.75 | 0.60698 | 8497.72 | 40000 | 0 | 9248.75 | 0 | 8497.72 | 0 | 0 | 12170.33 | 0 | 0 | 12170.33
2022080618 | 7 | 0.87253 | 69802.4 | 0 | 0 | 0.30908 | 10817.8 | 0.57201 | 8008.14 | 40000 | 0 | 10817.8 | 0 | 8008.14 | 0 | 0 | 10976.46 | 0 | 0 | 10976.46
2022080619 | 7 | 0.85684 | 68547.2 | 0 | 0 | 0.37175 | 13011.25 | 0.47652 | 6671.28 | 40000 | 0 | 13011.25 | 0 | 6671.28 | 0 | 0 | 8864.67 | 0 | 0 | 8864.67
2022080620 | 7 | 0.82839 | 66271.2 | 0 | 0 | 0.44219 | 15476.65 | 0.19863 | 2780.82 | 40000 | 0 | 15476.65 | 0 | 2780.82 | 0 | 0 | 8013.73 | 0 | 0 | 8013.73
2022080621 | 7 | 0.803 | 64240 | 0 | 0 | 0.48126 | 16844.1 | 0.01472 | 206.08 | 40000 | 0 | 16844.1 | 0 | 206.08 | 0 | 0 | 7189.82 | 0 | 0 | 7189.82
2022080622 | 7 | 0.77931 | 62344.8 | 0 | 0 | 0.49843 | 17445.05 | 0 | 0 | 40000 | 0 | 17445.05 | 0 | 0 | 0 | 0 | 4899.75 | 0 | 0 | 4899.75
2022080623 | 7 | 0.74212 | 59369.6 | 0 | 0 | 0.5068 | 17738 | 0 | 0 | 40000 | 0 | 17738 | 0 | 0 | 0 | 0 | 1631.6 | 0 | 0 | 1631.6
2022080624 | 7 | 0.70336 | 56268.8 | 0 | 0 | 0.4944 | 17304 | 0 | 0 | 40000 | 0 | 16268.8 | 1035.2 | 0 | 0 | 1035.2 | 0 | 0 | 0 | 0
2022080701 | 1 | 0.66439 | 53151.2 | 0 | 0 | 0.46626 | 16319.1 | 0 | 0 | 40000 | 0 | 13151.2 | 3167.9 | 0 | 0 | 3167.9 | 0 | 0 | 0 | 0
2022080702 | 1 | 0.63318 | 50654.4 | 0 | 0 | 0.45767 | 16018.45 | 0 | 0 | 40000 | 0 | 10654.4 | 5364.05 | 0 | 0 | 5364.05 | 0 | 0 | 0 | 0
2022080703 | 1 | 0.61121 | 48896.8 | 0 | 0 | 0.46181 | 16163.35 | 0 | 0 | 40000 | 0 | 8896.8 | 7266.55 | 0 | 0 | 7266.55 | 0 | 0 | 0 | 0
2022080704 | 1 | 0.59111 | 47288.8 | 0 | 0 | 0.44195 | 15468.25 | 0 | 0 | 40000 | 0 | 7288.8 | 8179.45 | 0 | 0 | 8179.45 | 0 | 0 | 0 | 0
2022080705 | 1 | 0.57684 | 46147.2 | 0 | 0 | 0.40924 | 14323.4 | 0 | 0 | 40000 | 0 | 6147.2 | 8176.2 | 0 | 0 | 8176.2 | 0 | 0 | 0 | 0
2022080706 | 1 | 0.56951 | 45560.8 | 0 | 0 | 0.38046 | 13316.1 | 0 | 0 | 40000 | 0 | 5560.8 | 7755.3 | 0 | 0 | 7755.3 | 0 | 0 | 0 | 0
2022080707 | 1 | 0.56503 | 45202.4 | 0 | 0 | 0.35551 | 12442.85 | 0.00013 | 1.82 | 40000 | 0 | 5202.4 | 7240.45 | 0 | 1.82 | 7242.27 | 0 | 0 | 0 | 0
2022080708 | 1 | 0.5665 | 45320 | 0 | 0 | 0.31967 | 11188.45 | 0.08698 | 1217.72 | 40000 | 0 | 5320 | 5868.45 | 0 | 1217.72 | 7086.17 | 0 | 0 | 0 | 0
2022080709 | 1 | 0.60579 | 48463.2 | 0 | 0 | 0.2803 | 9810.5 | 0.46871 | 6561.94 | 40000 | 0 | 8463.2 | 1347.3 | 0 | 6561.94 | 7909.24 | 0 | 0 | 0 | 0
2022080710 | 1 | 0.66117 | 52893.6 | 0 | 0 | 0.34291 | 12001.85 | 0.72714 | 10179.96 | 40000 | 0 | 12001.85 | 0 | 891.75 | 9288.21 | 9288.21 | 0 | 0 | 0 | 0
2022080711 | 1 | 0.71554 | 57243.2 | 0 | 0 | 0.32494 | 11372.9 | 0.78282 | 10959.48 | 40000 | 0 | 11372.9 | 0 | 5870.3 | 5089.18 | 5089.18 | 0 | 0 | 0 | 0
2022080712 | 1 | 0.76835 | 61468 | 0 | 0 | 0.28438 | 9953.3 | 0.77642 | 10869.88 | 40000 | 0 | 9953.3 | 0 | 10869.88 | 0 | 0 | 644.82 | 0 | 0 | 644.82
2022080713 | 1 | 0.81305 | 65044 | 0 | 0 | 0.24483 | 8569.05 | 0.76843 | 10758.02 | 40000 | 0 | 8569.05 | 0 | 10758.02 | 0 | 0 | 5716.93 | 0 | 0 | 5716.93
2022080714 | 1 | 0.85227 | 68181.6 | 0 | 0 | 0.24603 | 8611.05 | 0.72103 | 10094.42 | 40000 | 0 | 8611.05 | 0 | 10094.42 | 0 | 0 | 9476.13 | 0 | 0 | 9476.13
2022080715 | 1 | 0.88177 | 70541.6 | 0 | 0 | 0.26201 | 9170.35 | 0.69471 | 9725.94 | 40000 | 0 | 9170.35 | 0 | 9725.94 | 0 | 0 | 11645.31 | 0 | 0 | 11645.31
2022080716 | 1 | 0.90283 | 72226.4 | 0 | 0 | 0.28717 | 10050.95 | 0.66101 | 9254.14 | 40000 | 0 | 10050.95 | 0 | 9254.14 | 0 | 0 | 12921.31 | 0 | 0 | 12921.31
2022080717 | 1 | 0.91747 | 73397.6 | 0 | 0 | 0.31348 | 10971.8 | 0.65844 | 9218.16 | 40000 | 0 | 10971.8 | 0 | 9218.16 | 0 | 0 | 13207.64 | 0 | 0 | 13207.64
2022080718 | 1 | 0.9199 | 73592 | 0 | 0 | 0.33835 | 11842.25 | 0.622 | 8708 | 40000 | 0 | 11842.25 | 0 | 8708 | 0 | 0 | 13041.75 | 0 | 0 | 13041.75
2022080719 | 1 | 0.9047 | 72376 | 0 | 0 | 0.35621 | 12467.35 | 0.53122 | 7437.08 | 40000 | 0 | 12467.35 | 0 | 7437.08 | 0 | 0 | 12471.57 | 0 | 0 | 12471.57
2022080720 | 1 | 0.87351 | 69880.8 | 0 | 0 | 0.371 | 12985 | 0.25666 | 3593.24 | 40000 | 0 | 12985 | 0 | 3593.24 | 0 | 0 | 13302.56 | 0 | 0 | 13302.56
2022080721 | 1 | 0.84327 | 67461.6 | 0 | 0 | 0.35259 | 12340.65 | 0.01632 | 228.48 | 40000 | 0 | 12340.65 | 0 | 228.48 | 0 | 0 | 14892.47 | 0 | 0 | 14892.47
2022080722 | 1 | 0.81616 | 65292.8 | 0 | 0 | 0.34668 | 12133.8 | 0 | 0 | 40000 | 0 | 12133.8 | 0 | 0 | 0 | 0 | 13159 | 0 | 0 | 13159
2022080723 | 1 | 0.77005 | 61604 | 0 | 0 | 0.37587 | 13155.45 | 0 | 0 | 40000 | 0 | 13155.45 | 0 | 0 | 0 | 0 | 8448.55 | 0 | 0 | 8448.55
2022080724 | 1 | 0.71867 | 57493.6 | 0 | 0 | 0.4009 | 14031.5 | 0 | 0 | 40000 | 0 | 14031.5 | 0 | 0 | 0 | 0 | 3462.1 | 0 | 0 | 3462.1
2022080801 | 2 | 0.67658 | 54126.4 | 0 | 0 | 0.42369 | 14829.15 | 0 | 0 | 40000 | 0 | 14126.4 | 702.75 | 0 | 0 | 702.75 | 0 | 0 | 0 | 0
2022080802 | 2 | 0.64911 | 51928.8 | 0 | 0 | 0.43158 | 15105.3 | 0 | 0 | 40000 | 0 | 11928.8 | 3176.5 | 0 | 0 | 3176.5 | 0 | 0 | 0 | 0
2022080803 | 2 | 0.62438 | 49950.4 | 0 | 0 | 0.43074 | 15075.9 | 0 | 0 | 40000 | 0 | 9950.4 | 5125.5 | 0 | 0 | 5125.5 | 0 | 0 | 0 | 0
2022080804 | 2 | 0.60811 | 48648.8 | 0 | 0 | 0.4048 | 14168 | 0 | 0 | 40000 | 0 | 8648.8 | 5519.2 | 0 | 0 | 5519.2 | 0 | 0 | 0 | 0
2022080805 | 2 | 0.60259 | 48207.2 | 0 | 0 | 0.36285 | 12699.75 | 0 | 0 | 40000 | 0 | 8207.2 | 4492.55 | 0 | 0 | 4492.55 | 0 | 0 | 0 | 0
2022080806 | 2 | 0.60961 | 48768.8 | 0 | 0 | 0.32748 | 11461.8 | 0 | 0 | 40000 | 0 | 8768.8 | 2693 | 0 | 0 | 2693 | 0 | 0 | 0 | 0
2022080807 | 2 | 0.62599 | 50079.2 | 0 | 0 | 0.29926 | 10474.1 | 0.0001 | 1.4 | 40000 | 0 | 10079.2 | 394.9 | 0 | 1.4 | 396.3 | 0 | 0 | 0 | 0
2022080808 | 2 | 0.63362 | 50689.6 | 0 | 0 | 0.27049 | 9467.15 | 0.07829 | 1096.06 | 40000 | 0 | 9467.15 | 0 | 1096.06 | 0 | 0 | 126.39 | 0 | 0 | 126.39
2022080809 | 2 | 0.66681 | 53344.8 | 0 | 0 | 0.2347 | 8214.5 | 0.43701 | 6118.14 | 40000 | 0 | 8214.5 | 0 | 5130.3 | 987.84 | 987.84 | 0 | 0 | 0 | 0
2022080810 | 2 | 0.71417 | 57133.6 | 0 | 0 | 0.24856 | 8699.6 | 0.7212 | 10096.8 | 40000 | 0 | 8699.6 | 0 | 8434 | 1662.8 | 1662.8 | 0 | 0 | 0 | 0
2022080811 | 2 | 0.76573 | 61258.4 | 0 | 0 | 0.18117 | 6340.95 | 0.78668 | 11013.52 | 40000 | 0 | 6340.95 | 0 | 11013.52 | 0 | 0 | 3903.93 | 0 | 0 | 3903.93
2022080812 | 2 | 0.81818 | 65454.4 | 0 | 0 | 0.12027 | 4209.45 | 0.78861 | 11040.54 | 40000 | 0 | 4209.45 | 0 | 11040.54 | 0 | 0 | 10204.41 | 0 | 0 | 10204.41
2022080813 | 2 | 0.86921 | 69536.8 | 0 | 0 | 0.10082 | 3528.7 | 0.76745 | 10744.3 | 40000 | 0 | 3528.7 | 0 | 10744.3 | 0 | 0 | 15263.8 | 0 | 0 | 15263.8
2022080814 | 2 | 0.91109 | 72887.2 | 0 | 0 | 0.11165 | 3907.75 | 0.73265 | 10257.1 | 40000 | 0 | 3907.75 | 0 | 10257.1 | 0 | 0 | 18722.35 | 0 | 0 | 18722.35
2022080815 | 2 | 0.93645 | 74916 | 0 | 0 | 0.12594 | 4407.9 | 0.69811 | 9773.54 | 40000 | 0 | 4407.9 | 0 | 9773.54 | 0 | 0 | 20734.56 | 0 | 0 | 20734.56
2022080816 | 2 | 0.95401 | 76320.8 | 0 | 0 | 0.15728 | 5504.8 | 0.68162 | 9542.68 | 40000 | 0 | 5504.8 | 0 | 9542.68 | 0 | 0 | 21273.32 | 0 | 0 | 21273.32
2022080817 | 2 | 0.96068 | 76854.4 | 0 | 0 | 0.19887 | 6960.45 | 0.65717 | 9200.38 | 40000 | 0 | 6960.45 | 0 | 9200.38 | 0 | 0 | 20693.57 | 0 | 0 | 20693.57
2022080818 | 2 | 0.9543 | 76344 | 0 | 0 | 0.20093 | 7032.55 | 0.60739 | 8503.46 | 40000 | 0 | 7032.55 | 0 | 8503.46 | 0 | 0 | 20807.99 | 0 | 0 | 20807.99
2022080819 | 2 | 0.9325 | 74600 | 0 | 0 | 0.19587 | 6855.45 | 0.49966 | 6995.24 | 40000 | 0 | 6855.45 | 0 | 6995.24 | 0 | 0 | 20749.31 | 0 | 0 | 20749.31
2022080820 | 2 | 0.8954 | 71632 | 0 | 0 | 0.18282 | 6398.7 | 0.22751 | 3185.14 | 40000 | 0 | 6398.7 | 0 | 3185.14 | 0 | 0 | 22048.16 | 0 | 0 | 22048.16
2022080821 | 2 | 0.86355 | 69084 | 0 | 0 | 0.19571 | 6849.85 | 0.01198 | 167.72 | 40000 | 0 | 6849.85 | 0 | 167.72 | 0 | 0 | 22066.43 | 0 | 0 | 22066.43
2022080822 | 2 | 0.83579 | 66863.2 | 0 | 0 | 0.22675 | 7936.25 | 0 | 0 | 40000 | 0 | 7936.25 | 0 | 0 | 0 | 0 | 18926.95 | 0 | 0 | 18926.95
2022080823 | 2 | 0.78762 | 63009.6 | 0 | 0 | 0.25525 | 8933.75 | 0 | 0 | 40000 | 0 | 8933.75 | 0 | 0 | 0 | 0 | 14075.85 | 0 | 0 | 14075.85
2022080824 | 2 | 0.73442 | 58753.6 | 0 | 0 | 0.2822 | 9877 | 0 | 0 | 40000 | 0 | 9877 | 0 | 0 | 0 | 0 | 8876.6 | 0 | 0 | 8876.6
2022080901 | 3 | 0.68792 | 55033.6 | 0 | 0 | 0.30917 | 10820.95 | 0 | 0 | 40000 | 0 | 10820.95 | 0 | 0 | 0 | 0 | 4212.65 | 0 | 0 | 4212.65
2022080902 | 3 | 0.65293 | 52234.4 | 0 | 0 | 0.32102 | 11235.7 | 0 | 0 | 40000 | 0 | 11235.7 | 0 | 0 | 0 | 0 | 998.7 | 0 | 0 | 998.7
2022080903 | 3 | 0.62908 | 50326.4 | 0 | 0 | 0.30989 | 10846.15 | 0 | 0 | 40000 | 0 | 10326.4 | 519.75 | 0 | 0 | 519.75 | 0 | 0 | 0 | 0
2022080904 | 3 | 0.61608 | 49286.4 | 0 | 0 | 0.30029 | 10510.15 | 0 | 0 | 40000 | 0 | 9286.4 | 1223.75 | 0 | 0 | 1223.75 | 0 | 0 | 0 | 0
2022080905 | 3 | 0.60982 | 48785.6 | 0 | 0 | 0.28906 | 10117.1 | 0 | 0 | 40000 | 0 | 8785.6 | 1331.5 | 0 | 0 | 1331.5 | 0 | 0 | 0 | 0
2022080906 | 3 | 0.61481 | 49184.8 | 0 | 0 | 0.24026 | 8409.1 | 0 | 0 | 40000 | 0 | 8409.1 | 0 | 0 | 0 | 0 | 775.7 | 0 | 0 | 775.7
2022080907 | 3 | 0.62839 | 50271.2 | 0 | 0 | 0.213 | 7455 | 9e-05 | 1.26 | 40000 | 0 | 7455 | 0 | 1.26 | 0 | 0 | 2814.94 | 0 | 0 | 2814.94
2022080908 | 3 | 0.63618 | 50894.4 | 0 | 0 | 0.1526 | 5341 | 0.06453 | 903.42 | 40000 | 0 | 5341 | 0 | 903.42 | 0 | 0 | 4649.98 | 0 | 0 | 4649.98
2022080909 | 3 | 0.66716 | 53372.8 | 0 | 0 | 0.09542 | 3339.7 | 0.41902 | 5866.28 | 40000 | 0 | 3339.7 | 0 | 5866.28 | 0 | 0 | 4166.82 | 0 | 0 | 4166.82
2022080910 | 3 | 0.71483 | 57186.4 | 0 | 0 | 0.07635 | 2672.25 | 0.63911 | 8947.54 | 40000 | 0 | 2672.25 | 0 | 8947.54 | 0 | 0 | 5566.61 | 0 | 0 | 5566.61
2022080911 | 3 | 0.76944 | 61555.2 | 0 | 0 | 0.0608 | 2128 | 0.66808 | 9353.12 | 40000 | 0 | 2128 | 0 | 9353.12 | 0 | 0 | 10074.08 | 0 | 0 | 10074.08
2022080912 | 3 | 0.8239 | 65912 | 0 | 0 | 0.04013 | 1404.55 | 0.69776 | 9768.64 | 40000 | 0 | 1404.55 | 0 | 9768.64 | 0 | 0 | 14738.81 | 0 | 0 | 14738.81
2022080913 | 3 | 0.87038 | 69630.4 | 0 | 0 | 0.03851 | 1347.85 | 0.68157 | 9541.98 | 40000 | 0 | 1347.85 | 0 | 9541.98 | 0 | 0 | 18740.57 | 0 | 0 | 18740.57
2022080914 | 3 | 0.9068 | 72544 | 0 | 0 | 0.05654 | 1978.9 | 0.6718 | 9405.2 | 40000 | 0 | 1978.9 | 0 | 9405.2 | 0 | 0 | 21159.9 | 0 | 0 | 21159.9
2022080915 | 3 | 0.92359 | 73887.2 | 0 | 0 | 0.08118 | 2841.3 | 0.62011 | 8681.54 | 40000 | 0 | 2841.3 | 0 | 8681.54 | 0 | 0 | 22364.36 | 0 | 0 | 22364.36
2022080916 | 3 | 0.92458 | 73966.4 | 0 | 0 | 0.13134 | 4596.9 | 0.55004 | 7700.56 | 40000 | 0 | 4596.9 | 0 | 7700.56 | 0 | 0 | 21668.94 | 0 | 0 | 21668.94
2022080917 | 3 | 0.91614 | 73291.2 | 0 | 0 | 0.17422 | 6097.7 | 0.51032 | 7144.48 | 40000 | 0 | 6097.7 | 0 | 7144.48 | 0 | 0 | 20049.02 | 0 | 0 | 20049.02
2022080918 | 3 | 0.8942 | 71536 | 0 | 0 | 0.19918 | 6971.3 | 0.48953 | 6853.42 | 40000 | 0 | 6971.3 | 0 | 6853.42 | 0 | 0 | 17711.28 | 0 | 0 | 17711.28
2022080919 | 3 | 0.86967 | 69573.6 | 0 | 0 | 0.24444 | 8555.4 | 0.3844 | 5381.6 | 40000 | 0 | 8555.4 | 0 | 5381.6 | 0 | 0 | 15636.6 | 0 | 0 | 15636.6
2022080920 | 3 | 0.84124 | 67299.2 | 0 | 0 | 0.27623 | 9668.05 | 0.1816 | 2542.4 | 40000 | 0 | 9668.05 | 0 | 2542.4 | 0 | 0 | 15088.75 | 0 | 0 | 15088.75
2022080921 | 3 | 0.82073 | 65658.4 | 0 | 0 | 0.24037 | 8412.95 | 0.0087 | 121.8 | 40000 | 0 | 8412.95 | 0 | 121.8 | 0 | 0 | 17123.65 | 0 | 0 | 17123.65
2022080922 | 3 | 0.795 | 63600 | 0 | 0 | 0.2283 | 7990.5 | 0 | 0 | 40000 | 0 | 7990.5 | 0 | 0 | 0 | 0 | 15609.5 | 0 | 0 | 15609.5
2022080923 | 3 | 0.75061 | 60048.8 | 0 | 0 | 0.21498 | 7524.3 | 0 | 0 | 40000 | 0 | 7524.3 | 0 | 0 | 0 | 0 | 12524.5 | 0 | 0 | 12524.5
2022080924 | 3 | 0.70147 | 56117.6 | 0 | 0 | 0.19022 | 6657.7 | 0 | 0 | 40000 | 0 | 6657.7 | 0 | 0 | 0 | 0 | 9459.9 | 0 | 0 | 9459.9
2022081001 | 4 | 0.65783 | 52626.4 | 0 | 0 | 0.18162 | 6356.7 | 0 | 0 | 40000 | 0 | 6356.7 | 0 | 0 | 0 | 0 | 6269.7 | 0 | 0 | 6269.7
2022081002 | 4 | 0.62528 | 50022.4 | 0 | 0 | 0.17226 | 6029.1 | 0 | 0 | 40000 | 0 | 6029.1 | 0 | 0 | 0 | 0 | 3993.3 | 0 | 0 | 3993.3
2022081003 | 4 | 0.60317 | 48253.6 | 0 | 0 | 0.16965 | 5937.75 | 0 | 0 | 40000 | 0 | 5937.75 | 0 | 0 | 0 | 0 | 2315.85 | 0 | 0 | 2315.85
2022081004 | 4 | 0.58905 | 47124 | 0 | 0 | 0.17215 | 6025.25 | 0 | 0 | 40000 | 0 | 6025.25 | 0 | 0 | 0 | 0 | 1098.75 | 0 | 0 | 1098.75
2022081005 | 4 | 0.58552 | 46841.6 | 0 | 0 | 0.16455 | 5759.25 | 0 | 0 | 40000 | 0 | 5759.25 | 0 | 0 | 0 | 0 | 1082.35 | 0 | 0 | 1082.35
2022081006 | 4 | 0.5954 | 47632 | 0 | 0 | 0.1476 | 5166 | 0 | 0 | 40000 | 0 | 5166 | 0 | 0 | 0 | 0 | 2466 | 0 | 0 | 2466
2022081007 | 4 | 0.61317 | 49053.6 | 0 | 0 | 0.13789 | 4826.15 | 7e-05 | 0.98 | 40000 | 0 | 4826.15 | 0 | 0.98 | 0 | 0 | 4226.47 | 0 | 0 | 4226.47
2022081008 | 4 | 0.62138 | 49710.4 | 0 | 0 | 0.12258 | 4290.3 | 0.05285 | 739.9 | 40000 | 0 | 4290.3 | 0 | 739.9 | 0 | 0 | 4680.2 | 0 | 0 | 4680.2
2022081009 | 4 | 0.65435 | 52348 | 0 | 0 | 0.09412 | 3294.2 | 0.30239 | 4233.46 | 40000 | 0 | 3294.2 | 0 | 4233.46 | 0 | 0 | 4820.34 | 0 | 0 | 4820.34
2022081010 | 4 | 0.7013 | 56104 | 0 | 0 | 0.07394 | 2587.9 | 0.53446 | 7482.44 | 40000 | 0 | 2587.9 | 0 | 7482.44 | 0 | 0 | 6033.66 | 0 | 0 | 6033.66
2022081011 | 4 | 0.75699 | 60559.2 | 0 | 0 | 0.04959 | 1735.65 | 0.63375 | 8872.5 | 40000 | 0 | 1735.65 | 0 | 8872.5 | 0 | 0 | 9951.05 | 0 | 0 | 9951.05
2022081012 | 4 | 0.81487 | 65189.6 | 0 | 0 | 0.0402 | 1407 | 0.65468 | 9165.52 | 40000 | 0 | 1407 | 0 | 9165.52 | 0 | 0 | 14617.08 | 0 | 0 | 14617.08
2022081013 | 4 | 0.86556 | 69244.8 | 0 | 0 | 0.07433 | 2601.55 | 0.64481 | 9027.34 | 40000 | 0 | 2601.55 | 0 | 9027.34 | 0 | 0 | 17615.91 | 0 | 0 | 17615.91
2022081014 | 4 | 0.90619 | 72495.2 | 0 | 0 | 0.11222 | 3927.7 | 0.63501 | 8890.14 | 40000 | 0 | 3927.7 | 0 | 8890.14 | 0 | 0 | 19677.36 | 0 | 0 | 19677.36
2022081015 | 4 | 0.93059 | 74447.2 | 0 | 0 | 0.14755 | 5164.25 | 0.56893 | 7965.02 | 40000 | 0 | 5164.25 | 0 | 7965.02 | 0 | 0 | 21317.93 | 0 | 0 | 21317.93
2022081016 | 4 | 0.94028 | 75222.4 | 0 | 0 | 0.19546 | 6841.1 | 0.52332 | 7326.48 | 40000 | 0 | 6841.1 | 0 | 7326.48 | 0 | 0 | 21054.82 | 0 | 0 | 21054.82
2022081017 | 4 | 0.92885 | 74308 | 0 | 0 | 0.18741 | 6559.35 | 0.48981 | 6857.34 | 40000 | 0 | 6559.35 | 0 | 6857.34 | 0 | 0 | 20891.31 | 0 | 0 | 20891.31
2022081018 | 4 | 0.89796 | 71836.8 | 0 | 0 | 0.178 | 6230 | 0.44323 | 6205.22 | 40000 | 0 | 6230 | 0 | 6205.22 | 0 | 0 | 19401.58 | 0 | 0 | 19401.58
2022081019 | 4 | 0.85333 | 68266.4 | 0 | 0 | 0.18733 | 6556.55 | 0.33111 | 4635.54 | 40000 | 0 | 6556.55 | 0 | 4635.54 | 0 | 0 | 17074.31 | 0 | 0 | 17074.31
2022081020 | 4 | 0.79491 | 63592.8 | 0 | 0 | 0.19028 | 6659.8 | 0.17194 | 2407.16 | 40000 | 0 | 6659.8 | 0 | 2407.16 | 0 | 0 | 14525.84 | 0 | 0 | 14525.84
2022081021 | 4 | 0.76779 | 61423.2 | 0 | 0 | 0.18259 | 6390.65 | 0.01027 | 143.78 | 40000 | 0 | 6390.65 | 0 | 143.78 | 0 | 0 | 14888.77 | 0 | 0 | 14888.77
2022081022 | 4 | 0.74164 | 59331.2 | 0 | 0 | 0.15961 | 5586.35 | 0 | 0 | 40000 | 0 | 5586.35 | 0 | 0 | 0 | 0 | 13744.85 | 0 | 0 | 13744.85
2022081023 | 4 | 0.69977 | 55981.6 | 0 | 0 | 0.14576 | 5101.6 | 0 | 0 | 40000 | 0 | 5101.6 | 0 | 0 | 0 | 0 | 10880 | 0 | 0 | 10880
2022081024 | 4 | 0.65498 | 52398.4 | 0 | 0 | 0.13444 | 4705.4 | 0 | 0 | 40000 | 0 | 4705.4 | 0 | 0 | 0 | 0 | 7693 | 0 | 0 | 7693
2022081101 | 5 | 0.61645 | 49316 | 0 | 0 | 0.12515 | 4380.25 | 0 | 0 | 40000 | 0 | 4380.25 | 0 | 0 | 0 | 0 | 4935.75 | 0 | 0 | 4935.75
2022081102 | 5 | 0.58734 | 46987.2 | 0 | 0 | 0.10001 | 3500.35 | 0 | 0 | 40000 | 0 | 3500.35 | 0 | 0 | 0 | 0 | 3486.85 | 0 | 0 | 3486.85
2022081103 | 5 | 0.56949 | 45559.2 | 0 | 0 | 0.09135 | 3197.25 | 0 | 0 | 40000 | 0 | 3197.25 | 0 | 0 | 0 | 0 | 2361.95 | 0 | 0 | 2361.95
2022081104 | 5 | 0.5586 | 44688 | 0 | 0 | 0.07043 | 2465.05 | 0 | 0 | 40000 | 0 | 2465.05 | 0 | 0 | 0 | 0 | 2222.95 | 0 | 0 | 2222.95
2022081105 | 5 | 0.55593 | 44474.4 | 0 | 0 | 0.06337 | 2217.95 | 0 | 0 | 40000 | 0 | 2217.95 | 0 | 0 | 0 | 0 | 2256.45 | 0 | 0 | 2256.45
2022081106 | 5 | 0.56831 | 45464.8 | 0 | 0 | 0.04396 | 1538.6 | 0 | 0 | 40000 | 0 | 1538.6 | 0 | 0 | 0 | 0 | 3926.2 | 0 | 0 | 3926.2
2022081107 | 5 | 0.59013 | 47210.4 | 0 | 0 | 0.0304 | 1064 | 0 | 0 | 40000 | 0 | 1064 | 0 | 0 | 0 | 0 | 6146.4 | 0 | 0 | 6146.4
2022081108 | 5 | 0.59984 | 47987.2 | 0 | 0 | 0.02297 | 803.95 | 0.0543 | 760.2 | 40000 | 0 | 803.95 | 0 | 760.2 | 0 | 0 | 6423.05 | 0 | 0 | 6423.05
2022081109 | 5 | 0.62549 | 50039.2 | 0 | 0 | 0.0128 | 448 | 0.36436 | 5101.04 | 40000 | 0 | 448 | 0 | 5101.04 | 0 | 0 | 4490.16 | 0 | 0 | 4490.16
2022081110 | 5 | 0.66784 | 53427.2 | 0 | 0 | 0.01076 | 376.6 | 0.54718 | 7660.52 | 40000 | 0 | 376.6 | 0 | 7660.52 | 0 | 0 | 5390.08 | 0 | 0 | 5390.08
2022081111 | 5 | 0.72269 | 57815.2 | 0 | 0 | 0.01128 | 394.8 | 0.60359 | 8450.26 | 40000 | 0 | 394.8 | 0 | 8450.26 | 0 | 0 | 8970.14 | 0 | 0 | 8970.14
2022081112 | 5 | 0.77841 | 62272.8 | 0 | 0 | 0.01716 | 600.6 | 0.63582 | 8901.48 | 40000 | 0 | 600.6 | 0 | 8901.48 | 0 | 0 | 12770.72 | 0 | 0 | 12770.72
2022081113 | 5 | 0.83053 | 66442.4 | 0 | 0 | 0.0242 | 847 | 0.64019 | 8962.66 | 40000 | 0 | 847 | 0 | 8962.66 | 0 | 0 | 16632.74 | 0 | 0 | 16632.74
2022081114 | 5 | 0.87346 | 69876.8 | 0 | 0 | 0.04531 | 1585.85 | 0.67465 | 9445.1 | 40000 | 0 | 1585.85 | 0 | 9445.1 | 0 | 0 | 18845.85 | 0 | 0 | 18845.85
2022081115 | 5 | 0.90087 | 72069.6 | 0 | 0 | 0.07846 | 2746.1 | 0.67651 | 9471.14 | 40000 | 0 | 2746.1 | 0 | 9471.14 | 0 | 0 | 19852.36 | 0 | 0 | 19852.36
2022081116 | 5 | 0.92221 | 73776.8 | 0 | 0 | 0.12028 | 4209.8 | 0.65777 | 9208.78 | 40000 | 0 | 4209.8 | 0 | 9208.78 | 0 | 0 | 20358.22 | 0 | 0 | 20358.22
2022081117 | 5 | 0.92898 | 74318.4 | 0 | 0 | 0.15393 | 5387.55 | 0.58681 | 8215.34 | 40000 | 0 | 5387.55 | 0 | 8215.34 | 0 | 0 | 20715.51 | 0 | 0 | 20715.51
2022081118 | 5 | 0.92039 | 73631.2 | 0 | 0 | 0.18713 | 6549.55 | 0.48773 | 6828.22 | 40000 | 0 | 6549.55 | 0 | 6828.22 | 0 | 0 | 20253.43 | 0 | 0 | 20253.43
2022081119 | 5 | 0.89375 | 71500 | 0 | 0 | 0.21216 | 7425.6 | 0.29842 | 4177.88 | 40000 | 0 | 7425.6 | 0 | 4177.88 | 0 | 0 | 19896.52 | 0 | 0 | 19896.52
2022081120 | 5 | 0.86054 | 68843.2 | 0 | 0 | 0.23413 | 8194.55 | 0.09113 | 1275.82 | 40000 | 0 | 8194.55 | 0 | 1275.82 | 0 | 0 | 19372.83 | 0 | 0 | 19372.83
2022081121 | 5 | 0.83022 | 66417.6 | 0 | 0 | 0.22015 | 7705.25 | 0.00392 | 54.88 | 40000 | 0 | 7705.25 | 0 | 54.88 | 0 | 0 | 18657.47 | 0 | 0 | 18657.47
2022081122 | 5 | 0.79768 | 63814.4 | 0 | 0 | 0.23307 | 8157.45 | 0 | 0 | 40000 | 0 | 8157.45 | 0 | 0 | 0 | 0 | 15656.95 | 0 | 0 | 15656.95
2022081123 | 5 | 0.75143 | 60114.4 | 0 | 0 | 0.2463 | 8620.5 | 0 | 0 | 40000 | 0 | 8620.5 | 0 | 0 | 0 | 0 | 11493.9 | 0 | 0 | 11493.9
2022081124 | 5 | 0.70314 | 56251.2 | 0 | 0 | 0.25878 | 9057.3 | 0 | 0 | 40000 | 0 | 9057.3 | 0 | 0 | 0 | 0 | 7193.9 | 0 | 0 | 7193.9
2022081201 | 6 | 0.66044 | 52835.2 | 0 | 0 | 0.24035 | 8412.25 | 0 | 0 | 40000 | 0 | 8412.25 | 0 | 0 | 0 | 0 | 4422.95 | 0 | 0 | 4422.95
2022081202 | 6 | 0.62725 | 50180 | 0 | 0 | 0.22417 | 7845.95 | 0 | 0 | 40000 | 0 | 7845.95 | 0 | 0 | 0 | 0 | 2334.05 | 0 | 0 | 2334.05
2022081203 | 6 | 0.60269 | 48215.2 | 0 | 0 | 0.1926 | 6741 | 0 | 0 | 40000 | 0 | 6741 | 0 | 0 | 0 | 0 | 1474.2 | 0 | 0 | 1474.2
2022081204 | 6 | 0.59047 | 47237.6 | 0 | 0 | 0.15439 | 5403.65 | 0 | 0 | 40000 | 0 | 5403.65 | 0 | 0 | 0 | 0 | 1833.95 | 0 | 0 | 1833.95
2022081205 | 6 | 0.58561 | 46848.8 | 0 | 0 | 0.1254 | 4389 | 0 | 0 | 40000 | 0 | 4389 | 0 | 0 | 0 | 0 | 2459.8 | 0 | 0 | 2459.8
2022081206 | 6 | 0.59229 | 47383.2 | 0 | 0 | 0.10822 | 3787.7 | 0 | 0 | 40000 | 0 | 3787.7 | 0 | 0 | 0 | 0 | 3595.5 | 0 | 0 | 3595.5
2022081207 | 6 | 0.60922 | 48737.6 | 0 | 0 | 0.08339 | 2918.65 | 5e-05 | 0.7 | 40000 | 0 | 2918.65 | 0 | 0.7 | 0 | 0 | 5818.25 | 0 | 0 | 5818.25
2022081208 | 6 | 0.61674 | 49339.2 | 0 | 0 | 0.05949 | 2082.15 | 0.05684 | 795.76 | 40000 | 0 | 2082.15 | 0 | 795.76 | 0 | 0 | 6461.29 | 0 | 0 | 6461.29
2022081209 | 6 | 0.64602 | 51681.6 | 0 | 0 | 0.034 | 1190 | 0.39862 | 5580.68 | 40000 | 0 | 1190 | 0 | 5580.68 | 0 | 0 | 4910.92 | 0 | 0 | 4910.92
2022081210 | 6 | 0.69116 | 55292.8 | 0 | 0 | 0.02733 | 956.55 | 0.64174 | 8984.36 | 40000 | 0 | 956.55 | 0 | 8984.36 | 0 | 0 | 5351.89 | 0 | 0 | 5351.89
2022081211 | 6 | 0.74657 | 59725.6 | 0 | 0 | 0.0496 | 1736 | 0.70904 | 9926.56 | 40000 | 0 | 1736 | 0 | 9926.56 | 0 | 0 | 8063.04 | 0 | 0 | 8063.04
2022081212 | 6 | 0.80057 | 64045.6 | 0 | 0 | 0.05413 | 1894.55 | 0.74523 | 10433.22 | 40000 | 0 | 1894.55 | 0 | 10433.22 | 0 | 0 | 11717.83 | 0 | 0 | 11717.83
2022081213 | 6 | 0.84438 | 67550.4 | 0 | 0 | 0.05366 | 1878.1 | 0.6914 | 9679.6 | 40000 | 0 | 1878.1 | 0 | 9679.6 | 0 | 0 | 15992.7 | 0 | 0 | 15992.7
2022081214 | 6 | 0.87193 | 69754.4 | 0 | 0 | 0.07751 | 2712.85 | 0.64961 | 9094.54 | 40000 | 0 | 2712.85 | 0 | 9094.54 | 0 | 0 | 17947.01 | 0 | 0 | 17947.01
2022081215 | 6 | 0.89652 | 71721.6 | 0 | 0 | 0.11164 | 3907.4 | 0.61683 | 8635.62 | 40000 | 0 | 3907.4 | 0 | 8635.62 | 0 | 0 | 19178.58 | 0 | 0 | 19178.58
2022081216 | 6 | 0.90926 | 72740.8 | 0 | 0 | 0.13492 | 4722.2 | 0.63887 | 8944.18 | 40000 | 0 | 4722.2 | 0 | 8944.18 | 0 | 0 | 19074.42 | 0 | 0 | 19074.42
2022081217 | 6 | 0.91048 | 72838.4 | 0 | 0 | 0.17188 | 6015.8 | 0.64513 | 9031.82 | 40000 | 0 | 6015.8 | 0 | 9031.82 | 0 | 0 | 17790.78 | 0 | 0 | 17790.78
2022081218 | 6 | 0.89798 | 71838.4 | 0 | 0 | 0.18202 | 6370.7 | 0.60066 | 8409.24 | 40000 | 0 | 6370.7 | 0 | 8409.24 | 0 | 0 | 17058.46 | 0 | 0 | 17058.46
2022081219 | 6 | 0.871 | 69680 | 0 | 0 | 0.1748 | 6118 | 0.51132 | 7158.48 | 40000 | 0 | 6118 | 0 | 7158.48 | 0 | 0 | 16403.52 | 0 | 0 | 16403.52
2022081220 | 6 | 0.84243 | 67394.4 | 0 | 0 | 0.18264 | 6392.4 | 0.23031 | 3224.34 | 40000 | 0 | 6392.4 | 0 | 3224.34 | 0 | 0 | 17777.66 | 0 | 0 | 17777.66
2022081221 | 6 | 0.81085 | 64868 | 0 | 0 | 0.17556 | 6144.6 | 0.01182 | 165.48 | 40000 | 0 | 6144.6 | 0 | 165.48 | 0 | 0 | 18557.92 | 0 | 0 | 18557.92
2022081222 | 6 | 0.78642 | 62913.6 | 0 | 0 | 0.20682 | 7238.7 | 0 | 0 | 40000 | 0 | 7238.7 | 0 | 0 | 0 | 0 | 15674.9 | 0 | 0 | 15674.9
2022081223 | 6 | 0.74759 | 59807.2 | 0 | 0 | 0.24358 | 8525.3 | 0 | 0 | 40000 | 0 | 8525.3 | 0 | 0 | 0 | 0 | 11281.9 | 0 | 0 | 11281.9
2022081224 | 6 | 0.70459 | 56367.2 | 0 | 0 | 0.2551 | 8928.5 | 0 | 0 | 40000 | 0 | 8928.5 | 0 | 0 | 0 | 0 | 7438.7 | 0 | 0 | 7438.7
2022081301 | 7 | 0.66379 | 53103.2 | 0 | 0 | 0.25722 | 9002.7 | 0 | 0 | 40000 | 0 | 9002.7 | 0 | 0 | 0 | 0 | 4100.5 | 0 | 0 | 4100.5
2022081302 | 7 | 0.63302 | 50641.6 | 0 | 0 | 0.23411 | 8193.85 | 0 | 0 | 40000 | 0 | 8193.85 | 0 | 0 | 0 | 0 | 2447.75 | 0 | 0 | 2447.75
2022081303 | 7 | 0.61117 | 48893.6 | 0 | 0 | 0.2097 | 7339.5 | 0 | 0 | 40000 | 0 | 7339.5 | 0 | 0 | 0 | 0 | 1554.1 | 0 | 0 | 1554.1
2022081304 | 7 | 0.59105 | 47284 | 0 | 0 | 0.1849 | 6471.5 | 0 | 0 | 40000 | 0 | 6471.5 | 0 | 0 | 0 | 0 | 812.5 | 0 | 0 | 812.5
2022081305 | 7 | 0.57981 | 46384.8 | 0 | 0 | 0.1624 | 5684 | 0 | 0 | 40000 | 0 | 5684 | 0 | 0 | 0 | 0 | 700.8 | 0 | 0 | 700.8
2022081306 | 7 | 0.57768 | 46214.4 | 0 | 0 | 0.1372 | 4802 | 0 | 0 | 40000 | 0 | 4802 | 0 | 0 | 0 | 0 | 1412.4 | 0 | 0 | 1412.4
2022081307 | 7 | 0.57737 | 46189.6 | 0 | 0 | 0.12113 | 4239.55 | 0 | 0 | 40000 | 0 | 4239.55 | 0 | 0 | 0 | 0 | 1950.05 | 0 | 0 | 1950.05
2022081308 | 7 | 0.5819 | 46552 | 0 | 0 | 0.11071 | 3874.85 | 0.07182 | 1005.48 | 40000 | 0 | 3874.85 | 0 | 1005.48 | 0 | 0 | 1671.67 | 0 | 0 | 1671.67
2022081309 | 7 | 0.6185 | 49480 | 0 | 0 | 0.06496 | 2273.6 | 0.45865 | 6421.1 | 40000 | 0 | 2273.6 | 0 | 6421.1 | 0 | 0 | 785.3 | 0 | 0 | 785.3
2022081310 | 7 | 0.66918 | 53534.4 | 0 | 0 | 0.04561 | 1596.35 | 0.68256 | 9555.84 | 40000 | 0 | 1596.35 | 0 | 9555.84 | 0 | 0 | 2382.21 | 0 | 0 | 2382.21
2022081311 | 7 | 0.72518 | 58014.4 | 0 | 0 | 0.0433 | 1515.5 | 0.74791 | 10470.74 | 40000 | 0 | 1515.5 | 0 | 10470.74 | 0 | 0 | 6028.16 | 0 | 0 | 6028.16
2022081312 | 7 | 0.77359 | 61887.2 | 0 | 0 | 0.03115 | 1090.25 | 0.69159 | 9682.26 | 40000 | 0 | 1090.25 | 0 | 9682.26 | 0 | 0 | 11114.69 | 0 | 0 | 11114.69
2022081313 | 7 | 0.81266 | 65012.8 | 0 | 0 | 0.03436 | 1202.6 | 0.6362 | 8906.8 | 40000 | 0 | 1202.6 | 0 | 8906.8 | 0 | 0 | 14903.4 | 0 | 0 | 14903.4
2022081314 | 7 | 0.84746 | 67796.8 | 0 | 0 | 0.03923 | 1373.05 | 0.67268 | 9417.52 | 40000 | 0 | 1373.05 | 0 | 9417.52 | 0 | 0 | 17006.23 | 0 | 0 | 17006.23
2022081315 | 7 | 0.86928 | 69542.4 | 0 | 0 | 0.05398 | 1889.3 | 0.62646 | 8770.44 | 40000 | 0 | 1889.3 | 0 | 8770.44 | 0 | 0 | 18882.66 | 0 | 0 | 18882.66
2022081316 | 7 | 0.87927 | 70341.6 | 0 | 0 | 0.06343 | 2220.05 | 0.59691 | 8356.74 | 40000 | 0 | 2220.05 | 0 | 8356.74 | 0 | 0 | 19764.81 | 0 | 0 | 19764.81
2022081317 | 7 | 0.88449 | 70759.2 | 0 | 0 | 0.08515 | 2980.25 | 0.58647 | 8210.58 | 40000 | 0 | 2980.25 | 0 | 8210.58 | 0 | 0 | 19568.37 | 0 | 0 | 19568.37
2022081318 | 7 | 0.88106 | 70484.8 | 0 | 0 | 0.08901 | 3115.35 | 0.56917 | 7968.38 | 40000 | 0 | 3115.35 | 0 | 7968.38 | 0 | 0 | 19401.07 | 0 | 0 | 19401.07
2022081319 | 7 | 0.86506 | 69204.8 | 0 | 0 | 0.09876 | 3456.6 | 0.49361 | 6910.54 | 40000 | 0 | 3456.6 | 0 | 6910.54 | 0 | 0 | 18837.66 | 0 | 0 | 18837.66
2022081320 | 7 | 0.83461 | 66768.8 | 0 | 0 | 0.11748 | 4111.8 | 0.20827 | 2915.78 | 40000 | 0 | 4111.8 | 0 | 2915.78 | 0 | 0 | 19741.22 | 0 | 0 | 19741.22
2022081321 | 7 | 0.80744 | 64595.2 | 0 | 0 | 0.15729 | 5505.15 | 0.00929 | 130.06 | 40000 | 0 | 5505.15 | 0 | 130.06 | 0 | 0 | 18959.99 | 0 | 0 | 18959.99
2022081322 | 7 | 0.78095 | 62476 | 0 | 0 | 0.19985 | 6994.75 | 0.00081 | 11.34 | 40000 | 0 | 6994.75 | 0 | 11.34 | 0 | 0 | 15469.91 | 0 | 0 | 15469.91
2022081323 | 7 | 0.73942 | 59153.6 | 0 | 0 | 0.24774 | 8670.9 | 0.00081 | 11.34 | 40000 | 0 | 8670.9 | 0 | 11.34 | 0 | 0 | 10471.36 | 0 | 0 | 10471.36
2022081324 | 7 | 0.69635 | 55708 | 0 | 0 | 0.26568 | 9298.8 | 0.00081 | 11.34 | 40000 | 0 | 9298.8 | 0 | 11.34 | 0 | 0 | 6397.86 | 0 | 0 | 6397.86
2022081401 | 1 | 0.65692 | 52553.6 | 0 | 0 | 0.27997 | 9798.95 | 0.00081 | 11.34 | 40000 | 0 | 9798.95 | 0 | 11.34 | 0 | 0 | 2743.31 | 0 | 0 | 2743.31
2022081402 | 1 | 0.62435 | 49948 | 0 | 0 | 0.27983 | 9794.05 | 0.00082 | 11.48 | 40000 | 0 | 9794.05 | 0 | 11.48 | 0 | 0 | 142.47 | 0 | 0 | 142.47
2022081403 | 1 | 0.6013 | 48104 | 0 | 0 | 0.27924 | 9773.4 | 0.00082 | 11.48 | 40000 | 0 | 8104 | 1669.4 | 0 | 11.48 | 1680.88 | 0 | 0 | 0 | 0
2022081404 | 1 | 0.58186 | 46548.8 | 0 | 0 | 0.26785 | 9374.75 | 0.00082 | 11.48 | 40000 | 0 | 6548.8 | 2825.95 | 0 | 11.48 | 2837.43 | 0 | 0 | 0 | 0
2022081405 | 1 | 0.56426 | 45140.8 | 0 | 0 | 0.25395 | 8888.25 | 0.00082 | 11.48 | 40000 | 0 | 5140.8 | 3747.45 | 0 | 11.48 | 3758.93 | 0 | 0 | 0 | 0
2022081406 | 1 | 0.55526 | 44420.8 | 0 | 0 | 0.24918 | 8721.3 | 9e-05 | 1.26 | 40000 | 0 | 4420.8 | 4300.5 | 0 | 1.26 | 4301.76 | 0 | 0 | 0 | 0
2022081407 | 1 | 0.55093 | 44074.4 | 0 | 0 | 0.22061 | 7721.35 | 7e-05 | 0.98 | 40000 | 0 | 4074.4 | 3646.95 | 0 | 0.98 | 3647.93 | 0 | 0 | 0 | 0
2022081408 | 1 | 0.55252 | 44201.6 | 0 | 0 | 0.1913 | 6695.5 | 0.05845 | 818.3 | 40000 | 0 | 4201.6 | 2493.9 | 0 | 818.3 | 3312.2 | 0 | 0 | 0 | 0
2022081409 | 1 | 0.58506 | 46804.8 | 0 | 0 | 0.13977 | 4891.95 | 0.39925 | 5589.5 | 40000 | 0 | 4891.95 | 0 | 1912.85 | 3676.65 | 3676.65 | 0 | 0 | 0 | 0
2022081410 | 1 | 0.63126 | 50500.8 | 0 | 0 | 0.11061 | 3871.35 | 0.64002 | 8960.28 | 40000 | 0 | 3871.35 | 0 | 6629.45 | 2330.83 | 2330.83 | 0 | 0 | 0 | 0
2022081411 | 1 | 0.68388 | 54710.4 | 0 | 0 | 0.10886 | 3810.1 | 0.69735 | 9762.9 | 40000 | 0 | 3810.1 | 0 | 9762.9 | 0 | 0 | 1137.4 | 0 | 0 | 1137.4
2022081412 | 1 | 0.73272 | 58617.6 | 0 | 0 | 0.0944 | 3304 | 0.69524 | 9733.36 | 40000 | 0 | 3304 | 0 | 9733.36 | 0 | 0 | 5580.24 | 0 | 0 | 5580.24
2022081413 | 1 | 0.77019 | 61615.2 | 0 | 0 | 0.11349 | 3972.15 | 0.64753 | 9065.42 | 40000 | 0 | 3972.15 | 0 | 9065.42 | 0 | 0 | 8577.63 | 0 | 0 | 8577.63
2022081414 | 1 | 0.80087 | 64069.6 | 0 | 0 | 0.13437 | 4702.95 | 0.65028 | 9103.92 | 40000 | 0 | 4702.95 | 0 | 9103.92 | 0 | 0 | 10262.73 | 0 | 0 | 10262.73
2022081415 | 1 | 0.82876 | 66300.8 | 0 | 0 | 0.14553 | 5093.55 | 0.65092 | 9112.88 | 40000 | 0 | 5093.55 | 0 | 9112.88 | 0 | 0 | 12094.37 | 0 | 0 | 12094.37
2022081416 | 1 | 0.84983 | 67986.4 | 0 | 0 | 0.15141 | 5299.35 | 0.65023 | 9103.22 | 40000 | 0 | 5299.35 | 0 | 9103.22 | 0 | 0 | 13583.83 | 0 | 0 | 13583.83
2022081417 | 1 | 0.86137 | 68909.6 | 0 | 0 | 0.14894 | 5212.9 | 0.63548 | 8896.72 | 40000 | 0 | 5212.9 | 0 | 8896.72 | 0 | 0 | 14799.98 | 0 | 0 | 14799.98
2022081418 | 1 | 0.8641 | 69128 | 0 | 0 | 0.16334 | 5716.9 | 0.61288 | 8580.32 | 40000 | 0 | 5716.9 | 0 | 8580.32 | 0 | 0 | 14830.78 | 0 | 0 | 14830.78
2022081419 | 1 | 0.85238 | 68190.4 | 0 | 0 | 0.18555 | 6494.25 | 0.49541 | 6935.74 | 40000 | 0 | 6494.25 | 0 | 6935.74 | 0 | 0 | 14760.41 | 0 | 0 | 14760.41
2022081420 | 1 | 0.82797 | 66237.6 | 0 | 0 | 0.22202 | 7770.7 | 0.21015 | 2942.1 | 40000 | 0 | 7770.7 | 0 | 2942.1 | 0 | 0 | 15524.8 | 0 | 0 | 15524.8
2022081421 | 1 | 0.80803 | 64642.4 | 0 | 0 | 0.29416 | 10295.6 | 0.01061 | 148.54 | 40000 | 0 | 10295.6 | 0 | 148.54 | 0 | 0 | 14198.26 | 0 | 0 | 14198.26
2022081422 | 1 | 0.78017 | 62413.6 | 0 | 0 | 0.37296 | 13053.6 | 0 | 0 | 40000 | 0 | 13053.6 | 0 | 0 | 0 | 0 | 9360 | 0 | 0 | 9360
2022081423 | 1 | 0.73387 | 58709.6 | 0 | 0 | 0.43749 | 15312.15 | 0 | 0 | 40000 | 0 | 15312.15 | 0 | 0 | 0 | 0 | 3397.45 | 0 | 0 | 3397.45
2022081424 | 1 | 0.68756 | 55004.8 | 0 | 0 | 0.48151 | 16852.85 | 0 | 0 | 40000 | 0 | 15004.8 | 1848.05 | 0 | 0 | 1848.05 | 0 | 0 | 0 | 0
2022081501 | 2 | 0.64828 | 51862.4 | 0 | 0 | 0.46394 | 16237.9 | 0 | 0 | 40000 | 0 | 11862.4 | 4375.5 | 0 | 0 | 4375.5 | 0 | 0 | 0 | 0
2022081502 | 2 | 0.61792 | 49433.6 | 0 | 0 | 0.44063 | 15422.05 | 0 | 0 | 40000 | 0 | 9433.6 | 5988.45 | 0 | 0 | 5988.45 | 0 | 0 | 0 | 0
2022081503 | 2 | 0.59955 | 47964 | 0 | 0 | 0.39754 | 13913.9 | 0 | 0 | 40000 | 0 | 7964 | 5949.9 | 0 | 0 | 5949.9 | 0 | 0 | 0 | 0
2022081504 | 2 | 0.58574 | 46859.2 | 0 | 0 | 0.35295 | 12353.25 | 0 | 0 | 40000 | 0 | 6859.2 | 5494.05 | 0 | 0 | 5494.05 | 0 | 0 | 0 | 0
2022081505 | 2 | 0.58179 | 46543.2 | 0 | 0 | 0.32777 | 11471.95 | 0 | 0 | 40000 | 0 | 6543.2 | 4928.75 | 0 | 0 | 4928.75 | 0 | 0 | 0 | 0
2022081506 | 2 | 0.59255 | 47404 | 0 | 0 | 0.30517 | 10680.95 | 0 | 0 | 40000 | 0 | 7404 | 3276.95 | 0 | 0 | 3276.95 | 0 | 0 | 0 | 0
2022081507 | 2 | 0.61062 | 48849.6 | 0 | 0 | 0.30944 | 10830.4 | 0.00012 | 1.68 | 40000 | 0 | 8849.6 | 1980.8 | 0 | 1.68 | 1982.48 | 0 | 0 | 0 | 0
2022081508 | 2 | 0.62039 | 49631.2 | 0 | 0 | 0.30233 | 10581.55 | 0.05945 | 832.3 | 40000 | 0 | 9631.2 | 950.35 | 0 | 832.3 | 1782.65 | 0 | 0 | 0 | 0
2022081509 | 2 | 0.64611 | 51688.8 | 0 | 0 | 0.24237 | 8482.95 | 0.40032 | 5604.48 | 40000 | 0 | 8482.95 | 0 | 3205.85 | 2398.63 | 2398.63 | 0 | 0 | 0 | 0
2022081510 | 2 | 0.68698 | 54958.4 | 0 | 0 | 0.25765 | 9017.75 | 0.61959 | 8674.26 | 40000 | 0 | 9017.75 | 0 | 5940.65 | 2733.61 | 2733.61 | 0 | 0 | 0 | 0
2022081511 | 2 | 0.73642 | 58913.6 | 0 | 0 | 0.26627 | 9319.45 | 0.67154 | 9401.56 | 40000 | 0 | 9319.45 | 0 | 9401.56 | 0 | 0 | 192.59 | 0 | 0 | 192.59
2022081512 | 2 | 0.78626 | 62900.8 | 0 | 0 | 0.27839 | 9743.65 | 0.69151 | 9681.14 | 40000 | 0 | 9743.65 | 0 | 9681.14 | 0 | 0 | 3476.01 | 0 | 0 | 3476.01
2022081513 | 2 | 0.83183 | 66546.4 | 0 | 0 | 0.29064 | 10172.4 | 0.67453 | 9443.42 | 40000 | 0 | 10172.4 | 0 | 9443.42 | 0 | 0 | 6930.58 | 0 | 0 | 6930.58
2022081514 | 2 | 0.87257 | 69805.6 | 0 | 0 | 0.30991 | 10846.85 | 0.66481 | 9307.34 | 40000 | 0 | 10846.85 | 0 | 9307.34 | 0 | 0 | 9651.41 | 0 | 0 | 9651.41
2022081515 | 2 | 0.90493 | 72394.4 | 0 | 0 | 0.33151 | 11602.85 | 0.6655 | 9317 | 40000 | 0 | 11602.85 | 0 | 9317 | 0 | 0 | 11474.55 | 0 | 0 | 11474.55
2022081516 | 2 | 0.92353 | 73882.4 | 0 | 0 | 0.34834 | 12191.9 | 0.63612 | 8905.68 | 40000 | 0 | 12191.9 | 0 | 8905.68 | 0 | 0 | 12784.82 | 0 | 0 | 12784.82
2022081517 | 2 | 0.93111 | 74488.8 | 0 | 0 | 0.36294 | 12702.9 | 0.5706 | 7988.4 | 40000 | 0 | 12702.9 | 0 | 7988.4 | 0 | 0 | 13797.5 | 0 | 0 | 13797.5
2022081518 | 2 | 0.92428 | 73942.4 | 0 | 0 | 0.37903 | 13266.05 | 0.53547 | 7496.58 | 40000 | 0 | 13266.05 | 0 | 7496.58 | 0 | 0 | 13179.77 | 0 | 0 | 13179.77
2022081519 | 2 | 0.90275 | 72220 | 0 | 0 | 0.38703 | 13546.05 | 0.41547 | 5816.58 | 40000 | 0 | 13546.05 | 0 | 5816.58 | 0 | 0 | 12857.37 | 0 | 0 | 12857.37
2022081520 | 2 | 0.86723 | 69378.4 | 0 | 0 | 0.37479 | 13117.65 | 0.16299 | 2281.86 | 40000 | 0 | 13117.65 | 0 | 2281.86 | 0 | 0 | 13978.89 | 0 | 0 | 13978.89
2022081521 | 2 | 0.84009 | 67207.2 | 0 | 0 | 0.34262 | 11991.7 | 0.00901 | 126.14 | 40000 | 0 | 11991.7 | 0 | 126.14 | 0 | 0 | 15089.36 | 0 | 0 | 15089.36
2022081522 | 2 | 0.80493 | 64394.4 | 0 | 0 | 0.35314 | 12359.9 | 0 | 0 | 40000 | 0 | 12359.9 | 0 | 0 | 0 | 0 | 12034.5 | 0 | 0 | 12034.5
2022081523 | 2 | 0.75249 | 60199.2 | 0 | 0 | 0.36472 | 12765.2 | 0 | 0 | 40000 | 0 | 12765.2 | 0 | 0 | 0 | 0 | 7434 | 0 | 0 | 7434
2022081524 | 2 | 0.70033 | 56026.4 | 0 | 0 | 0.37578 | 13152.3 | 0 | 0 | 40000 | 0 | 13152.3 | 0 | 0 | 0 | 0 | 2874.1 | 0 | 0 | 2874.1
2022081601 | 3 | 0.65703 | 52562.4 | 0 | 0 | 0.36422 | 12747.7 | 0 | 0 | 40000 | 0 | 12562.4 | 185.3 | 0 | 0 | 185.3 | 0 | 0 | 0 | 0
2022081602 | 3 | 0.62607 | 50085.6 | 0 | 0 | 0.3531 | 12358.5 | 0 | 0 | 40000 | 0 | 10085.6 | 2272.9 | 0 | 0 | 2272.9 | 0 | 0 | 0 | 0
2022081603 | 3 | 0.60376 | 48300.8 | 0 | 0 | 0.3204 | 11214 | 0 | 0 | 40000 | 0 | 8300.8 | 2913.2 | 0 | 0 | 2913.2 | 0 | 0 | 0 | 0
2022081604 | 3 | 0.59307 | 47445.6 | 0 | 0 | 0.28916 | 10120.6 | 0 | 0 | 40000 | 0 | 7445.6 | 2675 | 0 | 0 | 2675 | 0 | 0 | 0 | 0
2022081605 | 3 | 0.58718 | 46974.4 | 0 | 0 | 0.26462 | 9261.7 | 0 | 0 | 40000 | 0 | 6974.4 | 2287.3 | 0 | 0 | 2287.3 | 0 | 0 | 0 | 0
2022081606 | 3 | 0.59741 | 47792.8 | 0 | 0 | 0.22955 | 8034.25 | 0 | 0 | 40000 | 0 | 7792.8 | 241.45 | 0 | 0 | 241.45 | 0 | 0 | 0 | 0
2022081607 | 3 | 0.61641 | 49312.8 | 0 | 0 | 0.19908 | 6967.8 | 7e-05 | 0.98 | 40000 | 0 | 6967.8 | 0 | 0.98 | 0 | 0 | 2344.02 | 0 | 0 | 2344.02
2022081608 | 3 | 0.62492 | 49993.6 | 0 | 0 | 0.18205 | 6371.75 | 0.05145 | 720.3 | 40000 | 0 | 6371.75 | 0 | 720.3 | 0 | 0 | 2901.55 | 0 | 0 | 2901.55
2022081609 | 3 | 0.6531 | 52248 | 0 | 0 | 0.13572 | 4750.2 | 0.25018 | 3502.52 | 40000 | 0 | 4750.2 | 0 | 3502.52 | 0 | 0 | 3995.28 | 0 | 0 | 3995.28
2022081610 | 3 | 0.69742 | 55793.6 | 0 | 0 | 0.1345 | 4707.5 | 0.39605 | 5544.7 | 40000 | 0 | 4707.5 | 0 | 5544.7 | 0 | 0 | 5541.4 | 0 | 0 | 5541.4
2022081611 | 3 | 0.7438 | 59504 | 0 | 0 | 0.14017 | 4905.95 | 0.46025 | 6443.5 | 40000 | 0 | 4905.95 | 0 | 6443.5 | 0 | 0 | 8154.55 | 0 | 0 | 8154.55
2022081612 | 3 | 0.79783 | 63826.4 | 0 | 0 | 0.13757 | 4814.95 | 0.52792 | 7390.88 | 40000 | 0 | 4814.95 | 0 | 7390.88 | 0 | 0 | 11620.57 | 0 | 0 | 11620.57
2022081613 | 3 | 0.84727 | 67781.6 | 0 | 0 | 0.14022 | 4907.7 | 0.55177 | 7724.78 | 40000 | 0 | 4907.7 | 0 | 7724.78 | 0 | 0 | 15149.12 | 0 | 0 | 15149.12
2022081614 | 3 | 0.89115 | 71292 | 0 | 0 | 0.16086 | 5630.1 | 0.58551 | 8197.14 | 40000 | 0 | 5630.1 | 0 | 8197.14 | 0 | 0 | 17464.76 | 0 | 0 | 17464.76
2022081615 | 3 | 0.92176 | 73740.8 | 0 | 0 | 0.1829 | 6401.5 | 0.54273 | 7598.22 | 40000 | 0 | 6401.5 | 0 | 7598.22 | 0 | 0 | 19741.08 | 0 | 0 | 19741.08
2022081616 | 3 | 0.93966 | 75172.8 | 0 | 0 | 0.20118 | 7041.3 | 0.48148 | 6740.72 | 40000 | 0 | 7041.3 | 0 | 6740.72 | 0 | 0 | 21390.78 | 0 | 0 | 21390.78
2022081617 | 3 | 0.94538 | 75630.4 | 0 | 0 | 0.21569 | 7549.15 | 0.41593 | 5823.02 | 40000 | 0 | 7549.15 | 0 | 5823.02 | 0 | 0 | 22258.23 | 0 | 0 | 22258.23
2022081618 | 3 | 0.94661 | 75728.8 | 0 | 0 | 0.22294 | 7802.9 | 0.40819 | 5714.66 | 40000 | 0 | 7802.9 | 0 | 5714.66 | 0 | 0 | 22211.24 | 0 | 0 | 22211.24
2022081619 | 3 | 0.92856 | 74284.8 | 0 | 0 | 0.23066 | 8073.1 | 0.29657 | 4151.98 | 40000 | 0 | 8073.1 | 0 | 4151.98 | 0 | 0 | 22059.72 | 0 | 0 | 22059.72
2022081620 | 3 | 0.89425 | 71540 | 0 | 0 | 0.22442 | 7854.7 | 0.07816 | 1094.24 | 40000 | 0 | 7854.7 | 0 | 1094.24 | 0 | 0 | 22591.06 | 0 | 0 | 22591.06
2022081621 | 3 | 0.86259 | 69007.2 | 0 | 0 | 0.20529 | 7185.15 | 0.00193 | 27.02 | 40000 | 0 | 7185.15 | 0 | 27.02 | 0 | 0 | 21795.03 | 0 | 0 | 21795.03
2022081622 | 3 | 0.82523 | 66018.4 | 0 | 0 | 0.21414 | 7494.9 | 0 | 0 | 40000 | 0 | 7494.9 | 0 | 0 | 0 | 0 | 18523.5 | 0 | 0 | 18523.5
2022081623 | 3 | 0.77338 | 61870.4 | 0 | 0 | 0.22703 | 7946.05 | 0 | 0 | 40000 | 0 | 7946.05 | 0 | 0 | 0 | 0 | 13924.35 | 0 | 0 | 13924.35
2022081624 | 3 | 0.71849 | 57479.2 | 0 | 0 | 0.22744 | 7960.4 | 0 | 0 | 40000 | 0 | 7960.4 | 0 | 0 | 0 | 0 | 9518.8 | 0 | 0 | 9518.8
2022081701 | 4 | 0.67386 | 53908.8 | 0 | 0 | 0.23419 | 8196.65 | 0 | 0 | 40000 | 0 | 8196.65 | 0 | 0 | 0 | 0 | 5712.15 | 0 | 0 | 5712.15
2022081702 | 4 | 0.64018 | 51214.4 | 0 | 0 | 0.24602 | 8610.7 | 0 | 0 | 40000 | 0 | 8610.7 | 0 | 0 | 0 | 0 | 2603.7 | 0 | 0 | 2603.7
2022081703 | 4 | 0.6173 | 49384 | 0 | 0 | 0.27543 | 9640.05 | 0 | 0 | 40000 | 0 | 9384 | 256.05 | 0 | 0 | 256.05 | 0 | 0 | 0 | 0
2022081704 | 4 | 0.60385 | 48308 | 0 | 0 | 0.27057 | 9469.95 | 0 | 0 | 40000 | 0 | 8308 | 1161.95 | 0 | 0 | 1161.95 | 0 | 0 | 0 | 0
2022081705 | 4 | 0.59887 | 47909.6 | 0 | 0 | 0.2556 | 8946 | 0 | 0 | 40000 | 0 | 7909.6 | 1036.4 | 0 | 0 | 1036.4 | 0 | 0 | 0 | 0
2022081706 | 4 | 0.60795 | 48636 | 0 | 0 | 0.25257 | 8839.95 | 0 | 0 | 40000 | 0 | 8636 | 203.95 | 0 | 0 | 203.95 | 0 | 0 | 0 | 0
2022081707 | 4 | 0.62949 | 50359.2 | 0 | 0 | 0.23554 | 8243.9 | 0 | 0 | 40000 | 0 | 8243.9 | 0 | 0 | 0 | 0 | 2115.3 | 0 | 0 | 2115.3
2022081708 | 4 | 0.63492 | 50793.6 | 0 | 0 | 0.20993 | 7347.55 | 0.05315 | 744.1 | 40000 | 0 | 7347.55 | 0 | 744.1 | 0 | 0 | 2701.95 | 0 | 0 | 2701.95
2022081709 | 4 | 0.6607 | 52856 | 0 | 0 | 0.13334 | 4666.9 | 0.34134 | 4778.76 | 40000 | 0 | 4666.9 | 0 | 4778.76 | 0 | 0 | 3410.34 | 0 | 0 | 3410.34
2022081710 | 4 | 0.70631 | 56504.8 | 0 | 0 | 0.098 | 3430 | 0.54594 | 7643.16 | 40000 | 0 | 3430 | 0 | 7643.16 | 0 | 0 | 5431.64 | 0 | 0 | 5431.64
2022081711 | 4 | 0.76246 | 60996.8 | 0 | 0 | 0.08501 | 2975.35 | 0.67572 | 9460.08 | 40000 | 0 | 2975.35 | 0 | 9460.08 | 0 | 0 | 8561.37 | 0 | 0 | 8561.37
2022081712 | 4 | 0.81817 | 65453.6 | 0 | 0 | 0.0713 | 2495.5 | 0.69859 | 9780.26 | 40000 | 0 | 2495.5 | 0 | 9780.26 | 0 | 0 | 13177.84 | 0 | 0 | 13177.84
2022081713 | 4 | 0.86921 | 69536.8 | 0 | 0 | 0.06473 | 2265.55 | 0.68917 | 9648.38 | 40000 | 0 | 2265.55 | 0 | 9648.38 | 0 | 0 | 17622.87 | 0 | 0 | 17622.87
2022081714 | 4 | 0.91354 | 73083.2 | 0 | 0 | 0.07991 | 2796.85 | 0.67712 | 9479.68 | 40000 | 0 | 2796.85 | 0 | 9479.68 | 0 | 0 | 20806.67 | 0 | 0 | 20806.67
2022081715 | 4 | 0.9479 | 75832 | 0 | 0 | 0.10639 | 3723.65 | 0.63689 | 8916.46 | 40000 | 0 | 3723.65 | 0 | 8916.46 | 0 | 0 | 23191.89 | 0 | 0 | 23191.89
2022081716 | 4 | 0.96115 | 76892 | 0 | 0 | 0.1235 | 4322.5 | 0.59167 | 8283.38 | 40000 | 0 | 4322.5 | 0 | 8283.38 | 0 | 0 | 24286.12 | 0 | 0 | 24286.12
2022081717 | 4 | 0.97228 | 77782.4 | 0 | 0 | 0.15603 | 5461.05 | 0.5738 | 8033.2 | 40000 | 0 | 5461.05 | 0 | 8033.2 | 0 | 0 | 24288.15 | 0 | 0 | 24288.15
2022081718 | 4 | 0.97166 | 77732.8 | 0 | 0 | 0.19855 | 6949.25 | 0.55332 | 7746.48 | 40000 | 0 | 6949.25 | 0 | 7746.48 | 0 | 0 | 23037.07 | 0 | 0 | 23037.07
2022081719 | 4 | 0.95114 | 76091.2 | 0 | 0 | 0.25486 | 8920.1 | 0.37251 | 5215.14 | 40000 | 0 | 8920.1 | 0 | 5215.14 | 0 | 0 | 21955.96 | 0 | 0 | 21955.96
2022081720 | 4 | 0.91618 | 73294.4 | 0 | 0 | 0.30744 | 10760.4 | 0.11387 | 1594.18 | 40000 | 0 | 10760.4 | 0 | 1594.18 | 0 | 0 | 20939.82 | 0 | 0 | 20939.82
2022081721 | 4 | 0.88523 | 70818.4 | 0 | 0 | 0.33337 | 11667.95 | 0.00209 | 29.26 | 40000 | 0 | 11667.95 | 0 | 29.26 | 0 | 0 | 19121.19 | 0 | 0 | 19121.19
2022081722 | 4 | 0.84015 | 67212 | 0 | 0 | 0.34357 | 12024.95 | 0 | 0 | 40000 | 0 | 12024.95 | 0 | 0 | 0 | 0 | 15187.05 | 0 | 0 | 15187.05
2022081723 | 4 | 0.7738 | 61904 | 0 | 0 | 0.3276 | 11466 | 0 | 0 | 40000 | 0 | 11466 | 0 | 0 | 0 | 0 | 10438 | 0 | 0 | 10438
2022081724 | 4 | 0.71409 | 57127.2 | 0 | 0 | 0.31787 | 11125.45 | 0 | 0 | 40000 | 0 | 11125.45 | 0 | 0 | 0 | 0 | 6001.75 | 0 | 0 | 6001.75
2022081801 | 5 | 0.6665 | 53320 | 0 | 0 | 0.28877 | 10106.95 | 0 | 0 | 40000 | 0 | 10106.95 | 0 | 0 | 0 | 0 | 3213.05 | 0 | 0 | 3213.05
2022081802 | 5 | 0.63168 | 50534.4 | 0 | 0 | 0.22875 | 8006.25 | 0 | 0 | 40000 | 0 | 8006.25 | 0 | 0 | 0 | 0 | 2528.15 | 0 | 0 | 2528.15
2022081803 | 5 | 0.60655 | 48524 | 0 | 0 | 0.16194 | 5667.9 | 0 | 0 | 40000 | 0 | 5667.9 | 0 | 0 | 0 | 0 | 2856.1 | 0 | 0 | 2856.1
2022081804 | 5 | 0.58878 | 47102.4 | 0 | 0 | 0.11952 | 4183.2 | 0 | 0 | 40000 | 0 | 4183.2 | 0 | 0 | 0 | 0 | 2919.2 | 0 | 0 | 2919.2
2022081805 | 5 | 0.58409 | 46727.2 | 0 | 0 | 0.09958 | 3485.3 | 0 | 0 | 40000 | 0 | 3485.3 | 0 | 0 | 0 | 0 | 3241.9 | 0 | 0 | 3241.9
2022081806 | 5 | 0.5942 | 47536 | 0 | 0 | 0.10111 | 3538.85 | 0 | 0 | 40000 | 0 | 3538.85 | 0 | 0 | 0 | 0 | 3997.15 | 0 | 0 | 3997.15
2022081807 | 5 | 0.61932 | 49545.6 | 0 | 0 | 0.09955 | 3484.25 | 0 | 0 | 40000 | 0 | 3484.25 | 0 | 0 | 0 | 0 | 6061.35 | 0 | 0 | 6061.35
2022081808 | 5 | 0.62246 | 49796.8 | 0 | 0 | 0.12893 | 4512.55 | 0.02756 | 385.84 | 40000 | 0 | 4512.55 | 0 | 385.84 | 0 | 0 | 4898.41 | 0 | 0 | 4898.41
2022081809 | 5 | 0.64228 | 51382.4 | 0 | 0 | 0.15821 | 5537.35 | 0.2086 | 2920.4 | 40000 | 0 | 5537.35 | 0 | 2920.4 | 0 | 0 | 2924.65 | 0 | 0 | 2924.65
2022081810 | 5 | 0.67858 | 54286.4 | 0 | 0 | 0.16495 | 5773.25 | 0.38716 | 5420.24 | 40000 | 0 | 5773.25 | 0 | 5420.24 | 0 | 0 | 3092.91 | 0 | 0 | 3092.91
2022081811 | 5 | 0.71926 | 57540.8 | 0 | 0 | 0.13951 | 4882.85 | 0.50833 | 7116.62 | 40000 | 0 | 4882.85 | 0 | 7116.62 | 0 | 0 | 5541.33 | 0 | 0 | 5541.33
2022081812 | 5 | 0.75964 | 60771.2 | 0 | 0 | 0.1071 | 3748.5 | 0.58604 | 8204.56 | 40000 | 0 | 3748.5 | 0 | 8204.56 | 0 | 0 | 8818.14 | 0 | 0 | 8818.14
2022081813 | 5 | 0.79494 | 63595.2 | 0 | 0 | 0.07575 | 2651.25 | 0.63918 | 8948.52 | 40000 | 0 | 2651.25 | 0 | 8948.52 | 0 | 0 | 11995.43 | 0 | 0 | 11995.43
2022081814 | 5 | 0.81988 | 65590.4 | 0 | 0 | 0.07231 | 2530.85 | 0.58409 | 8177.26 | 40000 | 0 | 2530.85 | 0 | 8177.26 | 0 | 0 | 14882.29 | 0 | 0 | 14882.29
2022081815 | 5 | 0.83369 | 66695.2 | 0 | 0 | 0.09535 | 3337.25 | 0.55321 | 7744.94 | 40000 | 0 | 3337.25 | 0 | 7744.94 | 0 | 0 | 15613.01 | 0 | 0 | 15613.01
2022081816 | 5 | 0.84029 | 67223.2 | 0 | 0 | 0.11342 | 3969.7 | 0.56693 | 7937.02 | 40000 | 0 | 3969.7 | 0 | 7937.02 | 0 | 0 | 15316.48 | 0 | 0 | 15316.48
2022081817 | 5 | 0.8335 | 66680 | 0 | 0 | 0.14002 | 4900.7 | 0.55472 | 7766.08 | 40000 | 0 | 4900.7 | 0 | 7766.08 | 0 | 0 | 14013.22 | 0 | 0 | 14013.22
2022081818 | 5 | 0.80241 | 64192.8 | 0 | 0 | 0.18722 | 6552.7 | 0.49957 | 6993.98 | 40000 | 0 | 6552.7 | 0 | 6993.98 | 0 | 0 | 10646.12 | 0 | 0 | 10646.12
2022081819 | 5 | 0.77345 | 61876 | 0 | 0 | 0.2297 | 8039.5 | 0.36562 | 5118.68 | 40000 | 0 | 8039.5 | 0 | 5118.68 | 0 | 0 | 8717.82 | 0 | 0 | 8717.82
2022081820 | 5 | 0.75072 | 60057.6 | 0 | 0 | 0.24492 | 8572.2 | 0.13987 | 1958.18 | 40000 | 0 | 8572.2 | 0 | 1958.18 | 0 | 0 | 9527.22 | 0 | 0 | 9527.22
2022081821 | 5 | 0.73399 | 58719.2 | 0 | 0 | 0.21555 | 7544.25 | 0.00448 | 62.72 | 40000 | 0 | 7544.25 | 0 | 62.72 | 0 | 0 | 11112.23 | 0 | 0 | 11112.23
2022081822 | 5 | 0.70907 | 56725.6 | 0 | 0 | 0.17351 | 6072.85 | 0 | 0 | 40000 | 0 | 6072.85 | 0 | 0 | 0 | 0 | 10652.75 | 0 | 0 | 10652.75
2022081823 | 5 | 0.67002 | 53601.6 | 0 | 0 | 0.16106 | 5637.1 | 0 | 0 | 40000 | 0 | 5637.1 | 0 | 0 | 0 | 0 | 7964.5 | 0 | 0 | 7964.5
2022081824 | 5 | 0.62438 | 49950.4 | 0 | 0 | 0.1656 | 5796 | 0 | 0 | 40000 | 0 | 5796 | 0 | 0 | 0 | 0 | 4154.4 | 0 | 0 | 4154.4
2022081901 | 6 | 0.58777 | 47021.6 | 0 | 0 | 0.17162 | 6006.7 | 0 | 0 | 40000 | 0 | 6006.7 | 0 | 0 | 0 | 0 | 1014.9 | 0 | 0 | 1014.9
2022081902 | 6 | 0.56278 | 45022.4 | 0 | 0 | 0.16459 | 5760.65 | 0 | 0 | 40000 | 0 | 5022.4 | 738.25 | 0 | 0 | 738.25 | 0 | 0 | 0 | 0
2022081903 | 6 | 0.54668 | 43734.4 | 0 | 0 | 0.15485 | 5419.75 | 0 | 0 | 40000 | 0 | 3734.4 | 1685.35 | 0 | 0 | 1685.35 | 0 | 0 | 0 | 0
2022081904 | 6 | 0.53978 | 43182.4 | 0 | 0 | 0.13298 | 4654.3 | 0 | 0 | 40000 | 0 | 3182.4 | 1471.9 | 0 | 0 | 1471.9 | 0 | 0 | 0 | 0
2022081905 | 6 | 0.53865 | 43092 | 0 | 0 | 0.1014 | 3549 | 0 | 0 | 40000 | 0 | 3092 | 457 | 0 | 0 | 457 | 0 | 0 | 0 | 0
2022081906 | 6 | 0.55244 | 44195.2 | 0 | 0 | 0.08273 | 2895.55 | 0 | 0 | 40000 | 0 | 2895.55 | 0 | 0 | 0 | 0 | 1299.65 | 0 | 0 | 1299.65
2022081907 | 6 | 0.58087 | 46469.6 | 0 | 0 | 0.08293 | 2902.55 | 0 | 0 | 40000 | 0 | 2902.55 | 0 | 0 | 0 | 0 | 3567.05 | 0 | 0 | 3567.05
2022081908 | 6 | 0.59006 | 47204.8 | 0 | 0 | 0.08111 | 2838.85 | 0.02556 | 357.84 | 40000 | 0 | 2838.85 | 0 | 357.84 | 0 | 0 | 4008.11 | 0 | 0 | 4008.11
2022081909 | 6 | 0.60578 | 48462.4 | 0 | 0 | 0.0619 | 2166.5 | 0.26207 | 3668.98 | 40000 | 0 | 2166.5 | 0 | 3668.98 | 0 | 0 | 2626.92 | 0 | 0 | 2626.92
2022081910 | 6 | 0.63088 | 50470.4 | 0 | 0 | 0.07379 | 2582.65 | 0.43607 | 6104.98 | 40000 | 0 | 2582.65 | 0 | 6104.98 | 0 | 0 | 1782.77 | 0 | 0 | 1782.77
2022081911 | 6 | 0.66514 | 53211.2 | 0 | 0 | 0.07163 | 2507.05 | 0.48107 | 6734.98 | 40000 | 0 | 2507.05 | 0 | 6734.98 | 0 | 0 | 3969.17 | 0 | 0 | 3969.17
2022081912 | 6 | 0.70226 | 56180.8 | 0 | 0 | 0.06024 | 2108.4 | 0.58994 | 8259.16 | 40000 | 0 | 2108.4 | 0 | 8259.16 | 0 | 0 | 5813.24 | 0 | 0 | 5813.24
2022081913 | 6 | 0.73786 | 59028.8 | 0 | 0 | 0.04996 | 1748.6 | 0.6144 | 8601.6 | 40000 | 0 | 1748.6 | 0 | 8601.6 | 0 | 0 | 8678.6 | 0 | 0 | 8678.6
2022081914 | 6 | 0.76852 | 61481.6 | 0 | 0 | 0.06521 | 2282.35 | 0.58742 | 8223.88 | 40000 | 0 | 2282.35 | 0 | 8223.88 | 0 | 0 | 10975.37 | 0 | 0 | 10975.37
2022081915 | 6 | 0.78548 | 62838.4 | 0 | 0 | 0.1012 | 3542 | 0.53682 | 7515.48 | 40000 | 0 | 3542 | 0 | 7515.48 | 0 | 0 | 11780.92 | 0 | 0 | 11780.92
2022081916 | 6 | 0.79116 | 63292.8 | 0 | 0 | 0.15536 | 5437.6 | 0.47319 | 6624.66 | 40000 | 0 | 5437.6 | 0 | 6624.66 | 0 | 0 | 11230.54 | 0 | 0 | 11230.54
2022081917 | 6 | 0.79387 | 63509.6 | 0 | 0 | 0.20787 | 7275.45 | 0.40302 | 5642.28 | 40000 | 0 | 7275.45 | 0 | 5642.28 | 0 | 0 | 10591.87 | 0 | 0 | 10591.87
2022081918 | 6 | 0.78667 | 62933.6 | 0 | 0 | 0.24772 | 8670.2 | 0.35999 | 5039.86 | 40000 | 0 | 8670.2 | 0 | 5039.86 | 0 | 0 | 9223.54 | 0 | 0 | 9223.54
2022081919 | 6 | 0.76899 | 61519.2 | 0 | 0 | 0.27384 | 9584.4 | 0.26057 | 3647.98 | 40000 | 0 | 9584.4 | 0 | 3647.98 | 0 | 0 | 8286.82 | 0 | 0 | 8286.82
2022081920 | 6 | 0.74586 | 59668.8 | 0 | 0 | 0.28186 | 9865.1 | 0.07087 | 992.18 | 40000 | 0 | 9865.1 | 0 | 992.18 | 0 | 0 | 8811.52 | 0 | 0 | 8811.52
2022081921 | 6 | 0.72824 | 58259.2 | 0 | 0 | 0.3161 | 11063.5 | 0.00042 | 5.88 | 40000 | 0 | 11063.5 | 0 | 5.88 | 0 | 0 | 7189.82 | 0 | 0 | 7189.82
2022081922 | 6 | 0.70493 | 56394.4 | 0 | 0 | 0.33709 | 11798.15 | 0 | 0 | 40000 | 0 | 11798.15 | 0 | 0 | 0 | 0 | 4596.25 | 0 | 0 | 4596.25
2022081923 | 6 | 0.67344 | 53875.2 | 0 | 0 | 0.35513 | 12429.55 | 0 | 0 | 40000 | 0 | 12429.55 | 0 | 0 | 0 | 0 | 1445.65 | 0 | 0 | 1445.65
2022081924 | 6 | 0.63608 | 50886.4 | 0 | 0 | 0.36008 | 12602.8 | 0 | 0 | 40000 | 0 | 10886.4 | 1716.4 | 0 | 0 | 1716.4 | 0 | 0 | 0 | 0
2022082001 | 7 | 0.60144 | 48115.2 | 0 | 0 | 0.3294 | 11529 | 0 | 0 | 40000 | 0 | 8115.2 | 3413.8 | 0 | 0 | 3413.8 | 0 | 0 | 0 | 0
2022082002 | 7 | 0.57681 | 46144.8 | 0 | 0 | 0.28241 | 9884.35 | 0 | 0 | 40000 | 0 | 6144.8 | 3739.55 | 0 | 0 | 3739.55 | 0 | 0 | 0 | 0
2022082003 | 7 | 0.55718 | 44574.4 | 0 | 0 | 0.27135 | 9497.25 | 0 | 0 | 40000 | 0 | 4574.4 | 4922.85 | 0 | 0 | 4922.85 | 0 | 0 | 0 | 0
2022082004 | 7 | 0.54543 | 43634.4 | 0 | 0 | 0.27328 | 9564.8 | 0 | 0 | 40000 | 0 | 3634.4 | 5930.4 | 0 | 0 | 5930.4 | 0 | 0 | 0 | 0
2022082005 | 7 | 0.53719 | 42975.2 | 0 | 0 | 0.26581 | 9303.35 | 0 | 0 | 40000 | 0 | 2975.2 | 6328.15 | 0 | 0 | 6328.15 | 0 | 0 | 0 | 0
2022082006 | 7 | 0.5377 | 43016 | 0 | 0 | 0.26637 | 9322.95 | 0 | 0 | 40000 | 0 | 3016 | 6306.95 | 0 | 0 | 6306.95 | 0 | 0 | 0 | 0
2022082007 | 7 | 0.54537 | 43629.6 | 0 | 0 | 0.26303 | 9206.05 | 0 | 0 | 40000 | 0 | 3629.6 | 5576.45 | 0 | 0 | 5576.45 | 0 | 0 | 0 | 0
2022082008 | 7 | 0.55437 | 44349.6 | 0 | 0 | 0.24034 | 8411.9 | 0.03291 | 460.74 | 40000 | 0 | 4349.6 | 4062.3 | 0 | 460.74 | 4523.04 | 0 | 0 | 0 | 0
2022082009 | 7 | 0.58534 | 46827.2 | 0 | 0 | 0.20411 | 7143.85 | 0.20469 | 2865.66 | 40000 | 0 | 6827.2 | 316.65 | 0 | 2865.66 | 3182.31 | 0 | 0 | 0 | 0
2022082010 | 7 | 0.63039 | 50431.2 | 0 | 0 | 0.2285 | 7997.5 | 0.37583 | 5261.62 | 40000 | 0 | 7997.5 | 0 | 2433.7 | 2827.92 | 2827.92 | 0 | 0 | 0 | 0
2022082011 | 7 | 0.68188 | 54550.4 | 0 | 0 | 0.23871 | 8354.85 | 0.4197 | 5875.8 | 40000 | 0 | 8354.85 | 0 | 5875.8 | 0 | 0 | 319.75 | 0 | 0 | 319.75
2022082012 | 7 | 0.72848 | 58278.4 | 0 | 0 | 0.22286 | 7800.1 | 0.47839 | 6697.46 | 40000 | 0 | 7800.1 | 0 | 6697.46 | 0 | 0 | 3780.84 | 0 | 0 | 3780.84
2022082013 | 7 | 0.76317 | 61053.6 | 0 | 0 | 0.22561 | 7896.35 | 0.49641 | 6949.74 | 40000 | 0 | 7896.35 | 0 | 6949.74 | 0 | 0 | 6207.51 | 0 | 0 | 6207.51
2022082014 | 7 | 0.79057 | 63245.6 | 0 | 0 | 0.23548 | 8241.8 | 0.47203 | 6608.42 | 40000 | 0 | 8241.8 | 0 | 6608.42 | 0 | 0 | 8395.38 | 0 | 0 | 8395.38
2022082015 | 7 | 0.80611 | 64488.8 | 0 | 0 | 0.27715 | 9700.25 | 0.48902 | 6846.28 | 40000 | 0 | 9700.25 | 0 | 6846.28 | 0 | 0 | 7942.27 | 0 | 0 | 7942.27
2022082016 | 7 | 0.81234 | 64987.2 | 0 | 0 | 0.35682 | 12488.7 | 0.50983 | 7137.62 | 40000 | 0 | 12488.7 | 0 | 7137.62 | 0 | 0 | 5360.88 | 0 | 0 | 5360.88
2022082017 | 7 | 0.82138 | 65710.4 | 0 | 0 | 0.39348 | 13771.8 | 0.46587 | 6522.18 | 40000 | 0 | 13771.8 | 0 | 6522.18 | 0 | 0 | 5416.42 | 0 | 0 | 5416.42
2022082018 | 7 | 0.82071 | 65656.8 | 0 | 0 | 0.3781 | 13233.5 | 0.36807 | 5152.98 | 40000 | 0 | 13233.5 | 0 | 5152.98 | 0 | 0 | 7270.32 | 0 | 0 | 7270.32
2022082019 | 7 | 0.79847 | 63877.6 | 0 | 0 | 0.3779 | 13226.5 | 0.21209 | 2969.26 | 40000 | 0 | 13226.5 | 0 | 2969.26 | 0 | 0 | 7681.84 | 0 | 0 | 7681.84
2022082020 | 7 | 0.77139 | 61711.2 | 0 | 0 | 0.35509 | 12428.15 | 0.03766 | 527.24 | 40000 | 0 | 12428.15 | 0 | 527.24 | 0 | 0 | 8755.81 | 0 | 0 | 8755.81
2022082021 | 7 | 0.75279 | 60223.2 | 0 | 0 | 0.33666 | 11783.1 | 0.0003 | 4.2 | 40000 | 0 | 11783.1 | 0 | 4.2 | 0 | 0 | 8435.9 | 0 | 0 | 8435.9
2022082022 | 7 | 0.72587 | 58069.6 | 0 | 0 | 0.33723 | 11803.05 | 0 | 0 | 40000 | 0 | 11803.05 | 0 | 0 | 0 | 0 | 6266.55 | 0 | 0 | 6266.55
2022082023 | 7 | 0.68885 | 55108 | 0 | 0 | 0.3533 | 12365.5 | 0 | 0 | 40000 | 0 | 12365.5 | 0 | 0 | 0 | 0 | 2742.5 | 0 | 0 | 2742.5
2022082024 | 7 | 0.653 | 52240 | 0 | 0 | 0.30886 | 10810.1 | 0 | 0 | 40000 | 0 | 10810.1 | 0 | 0 | 0 | 0 | 1429.9 | 0 | 0 | 1429.9
2022082101 | 1 | 0.619 | 49520 | 0 | 0 | 0.25635 | 8972.25 | 0 | 0 | 40000 | 0 | 8972.25 | 0 | 0 | 0 | 0 | 547.75 | 0 | 0 | 547.75
2022082102 | 1 | 0.59137 | 47309.6 | 0 | 0 | 0.23173 | 8110.55 | 0 | 0 | 40000 | 0 | 7309.6 | 800.95 | 0 | 0 | 800.95 | 0 | 0 | 0 | 0
2022082103 | 1 | 0.57242 | 45793.6 | 0 | 0 | 0.24113 | 8439.55 | 0 | 0 | 40000 | 0 | 5793.6 | 2645.95 | 0 | 0 | 2645.95 | 0 | 0 | 0 | 0
2022082104 | 1 | 0.55927 | 44741.6 | 0 | 0 | 0.25155 | 8804.25 | 0 | 0 | 40000 | 0 | 4741.6 | 4062.65 | 0 | 0 | 4062.65 | 0 | 0 | 0 | 0
2022082105 | 1 | 0.55168 | 44134.4 | 0 | 0 | 0.25032 | 8761.2 | 0 | 0 | 40000 | 0 | 4134.4 | 4626.8 | 0 | 0 | 4626.8 | 0 | 0 | 0 | 0
2022082106 | 1 | 0.54899 | 43919.2 | 0 | 0 | 0.24117 | 8440.95 | 0 | 0 | 40000 | 0 | 3919.2 | 4521.75 | 0 | 0 | 4521.75 | 0 | 0 | 0 | 0
2022082107 | 1 | 0.54635 | 43708 | 0 | 0 | 0.22566 | 7898.1 | 0 | 0 | 40000 | 0 | 3708 | 4190.1 | 0 | 0 | 4190.1 | 0 | 0 | 0 | 0
2022082108 | 1 | 0.54947 | 43957.6 | 0 | 0 | 0.21035 | 7362.25 | 0.01623 | 227.22 | 40000 | 0 | 3957.6 | 3404.65 | 0 | 227.22 | 3631.87 | 0 | 0 | 0 | 0
2022082109 | 1 | 0.57587 | 46069.6 | 0 | 0 | 0.19777 | 6921.95 | 0.13044 | 1826.16 | 40000 | 0 | 6069.6 | 852.35 | 0 | 1826.16 | 2678.51 | 0 | 0 | 0 | 0
2022082110 | 1 | 0.6179 | 49432 | 0 | 0 | 0.19464 | 6812.4 | 0.28029 | 3924.06 | 40000 | 0 | 6812.4 | 0 | 2619.6 | 1304.46 | 1304.46 | 0 | 0 | 0 | 0
2022082111 | 1 | 0.65608 | 52486.4 | 0 | 0 | 0.18603 | 6511.05 | 0.34962 | 4894.68 | 40000 | 0 | 6511.05 | 0 | 4894.68 | 0 | 0 | 1080.67 | 0 | 0 | 1080.67
2022082112 | 1 | 0.68581 | 54864.8 | 0 | 0 | 0.18852 | 6598.2 | 0.42133 | 5898.62 | 40000 | 0 | 6598.2 | 0 | 5898.62 | 0 | 0 | 2367.98 | 0 | 0 | 2367.98
2022082113 | 1 | 0.71225 | 56980 | 0 | 0 | 0.19089 | 6681.15 | 0.49254 | 6895.56 | 40000 | 0 | 6681.15 | 0 | 6895.56 | 0 | 0 | 3403.29 | 0 | 0 | 3403.29
2022082114 | 1 | 0.74085 | 59268 | 0 | 0 | 0.18628 | 6519.8 | 0.52557 | 7357.98 | 40000 | 0 | 6519.8 | 0 | 7357.98 | 0 | 0 | 5390.22 | 0 | 0 | 5390.22
2022082115 | 1 | 0.76704 | 61363.2 | 0 | 0 | 0.17989 | 6296.15 | 0.55868 | 7821.52 | 40000 | 0 | 6296.15 | 0 | 7821.52 | 0 | 0 | 7245.53 | 0 | 0 | 7245.53
2022082116 | 1 | 0.779 | 62320 | 0 | 0 | 0.19306 | 6757.1 | 0.51276 | 7178.64 | 40000 | 0 | 6757.1 | 0 | 7178.64 | 0 | 0 | 8384.26 | 0 | 0 | 8384.26
2022082117 | 1 | 0.78263 | 62610.4 | 0 | 0 | 0.20297 | 7103.95 | 0.44471 | 6225.94 | 40000 | 0 | 7103.95 | 0 | 6225.94 | 0 | 0 | 9280.51 | 0 | 0 | 9280.51
2022082118 | 1 | 0.78425 | 62740 | 0 | 0 | 0.21897 | 7663.95 | 0.38724 | 5421.36 | 40000 | 0 | 7663.95 | 0 | 5421.36 | 0 | 0 | 9654.69 | 0 | 0 | 9654.69
2022082119 | 1 | 0.77452 | 61961.6 | 0 | 0 | 0.24184 | 8464.4 | 0.30472 | 4266.08 | 40000 | 0 | 8464.4 | 0 | 4266.08 | 0 | 0 | 9231.12 | 0 | 0 | 9231.12
2022082120 | 1 | 0.75789 | 60631.2 | 0 | 0 | 0.25237 | 8832.95 | 0.1048 | 1467.2 | 40000 | 0 | 8832.95 | 0 | 1467.2 | 0 | 0 | 10331.05 | 0 | 0 | 10331.05
2022082121 | 1 | 0.74816 | 59852.8 | 0 | 0 | 0.25081 | 8778.35 | 0.00182 | 25.48 | 40000 | 0 | 8778.35 | 0 | 25.48 | 0 | 0 | 11048.97 | 0 | 0 | 11048.97
2022082122 | 1 | 0.72377 | 57901.6 | 0 | 0 | 0.23155 | 8104.25 | 0 | 0 | 40000 | 0 | 8104.25 | 0 | 0 | 0 | 0 | 9797.35 | 0 | 0 | 9797.35
2022082123 | 1 | 0.68339 | 54671.2 | 0 | 0 | 0.21075 | 7376.25 | 0 | 0 | 40000 | 0 | 7376.25 | 0 | 0 | 0 | 0 | 7294.95 | 0 | 0 | 7294.95
2022082124 | 1 | 0.63915 | 51132 | 0 | 0 | 0.20485 | 7169.75 | 0 | 0 | 40000 | 0 | 7169.75 | 0 | 0 | 0 | 0 | 3962.25 | 0 | 0 | 3962.25
2022082201 | 2 | 0.60583 | 48466.4 | 0 | 0 | 0.21143 | 7400.05 | 0 | 0 | 40000 | 0 | 7400.05 | 0 | 0 | 0 | 0 | 1066.35 | 0 | 0 | 1066.35
2022082202 | 2 | 0.58148 | 46518.4 | 0 | 0 | 0.21256 | 7439.6 | 0 | 0 | 40000 | 0 | 6518.4 | 921.2 | 0 | 0 | 921.2 | 0 | 0 | 0 | 0
2022082203 | 2 | 0.56754 | 45403.2 | 0 | 0 | 0.22567 | 7898.45 | 0 | 0 | 40000 | 0 | 5403.2 | 2495.25 | 0 | 0 | 2495.25 | 0 | 0 | 0 | 0
2022082204 | 2 | 0.56341 | 45072.8 | 0 | 0 | 0.22924 | 8023.4 | 0 | 0 | 40000 | 0 | 5072.8 | 2950.6 | 0 | 0 | 2950.6 | 0 | 0 | 0 | 0
2022082205 | 2 | 0.5636 | 45088 | 0 | 0 | 0.21775 | 7621.25 | 0 | 0 | 40000 | 0 | 5088 | 2533.25 | 0 | 0 | 2533.25 | 0 | 0 | 0 | 0
2022082206 | 2 | 0.58001 | 46400.8 | 0 | 0 | 0.21547 | 7541.45 | 0 | 0 | 40000 | 0 | 6400.8 | 1140.65 | 0 | 0 | 1140.65 | 0 | 0 | 0 | 0
2022082207 | 2 | 0.60776 | 48620.8 | 0 | 0 | 0.2313 | 8095.5 | 0 | 0 | 40000 | 0 | 8095.5 | 0 | 0 | 0 | 0 | 525.3 | 0 | 0 | 525.3
2022082208 | 2 | 0.61617 | 49293.6 | 0 | 0 | 0.23687 | 8290.45 | 0.01245 | 174.3 | 40000 | 0 | 8290.45 | 0 | 174.3 | 0 | 0 | 828.85 | 0 | 0 | 828.85
2022082209 | 2 | 0.63046 | 50436.8 | 0 | 0 | 0.25157 | 8804.95 | 0.09839 | 1377.46 | 40000 | 0 | 8804.95 | 0 | 1377.46 | 0 | 0 | 254.39 | 0 | 0 | 254.39
2022082210 | 2 | 0.65707 | 52565.6 | 0 | 0 | 0.29449 | 10307.15 | 0.1975 | 2765 | 40000 | 0 | 10307.15 | 0 | 2258.45 | 506.55 | 506.55 | 0 | 0 | 0 | 0
2022082211 | 2 | 0.68712 | 54969.6 | 0 | 0 | 0.30438 | 10653.3 | 0.29326 | 4105.64 | 40000 | 0 | 10653.3 | 0 | 4105.64 | 0 | 0 | 210.66 | 0 | 0 | 210.66
2022082212 | 2 | 0.71312 | 57049.6 | 0 | 0 | 0.28385 | 9934.75 | 0.39853 | 5579.42 | 40000 | 0 | 9934.75 | 0 | 5579.42 | 0 | 0 | 1535.43 | 0 | 0 | 1535.43
2022082213 | 2 | 0.73599 | 58879.2 | 0 | 0 | 0.26122 | 9142.7 | 0.42899 | 6005.86 | 40000 | 0 | 9142.7 | 0 | 6005.86 | 0 | 0 | 3730.64 | 0 | 0 | 3730.64
2022082214 | 2 | 0.75445 | 60356 | 0 | 0 | 0.24208 | 8472.8 | 0.44577 | 6240.78 | 40000 | 0 | 8472.8 | 0 | 6240.78 | 0 | 0 | 5642.42 | 0 | 0 | 5642.42
2022082215 | 2 | 0.76664 | 61331.2 | 0 | 0 | 0.25545 | 8940.75 | 0.44065 | 6169.1 | 40000 | 0 | 8940.75 | 0 | 6169.1 | 0 | 0 | 6221.35 | 0 | 0 | 6221.35
2022082216 | 2 | 0.77374 | 61899.2 | 0 | 0 | 0.26454 | 9258.9 | 0.43699 | 6117.86 | 40000 | 0 | 9258.9 | 0 | 6117.86 | 0 | 0 | 6522.44 | 0 | 0 | 6522.44
2022082217 | 2 | 0.77591 | 62072.8 | 0 | 0 | 0.26587 | 9305.45 | 0.37547 | 5256.58 | 40000 | 0 | 9305.45 | 0 | 5256.58 | 0 | 0 | 7510.77 | 0 | 0 | 7510.77
2022082218 | 2 | 0.76975 | 61580 | 0 | 0 | 0.25955 | 9084.25 | 0.29567 | 4139.38 | 40000 | 0 | 9084.25 | 0 | 4139.38 | 0 | 0 | 8356.37 | 0 | 0 | 8356.37
2022082219 | 2 | 0.74849 | 59879.2 | 0 | 0 | 0.24325 | 8513.75 | 0.20344 | 2848.16 | 40000 | 0 | 8513.75 | 0 | 2848.16 | 0 | 0 | 8517.29 | 0 | 0 | 8517.29
2022082220 | 2 | 0.72372 | 57897.6 | 0 | 0 | 0.2164 | 7574 | 0.06314 | 883.96 | 40000 | 0 | 7574 | 0 | 883.96 | 0 | 0 | 9439.64 | 0 | 0 | 9439.64
2022082221 | 2 | 0.71129 | 56903.2 | 0 | 0 | 0.18885 | 6609.75 | 0.00194 | 27.16 | 40000 | 0 | 6609.75 | 0 | 27.16 | 0 | 0 | 10266.29 | 0 | 0 | 10266.29
2022082222 | 2 | 0.69144 | 55315.2 | 0 | 0 | 0.17623 | 6168.05 | 0 | 0 | 40000 | 0 | 6168.05 | 0 | 0 | 0 | 0 | 9147.15 | 0 | 0 | 9147.15
2022082223 | 2 | 0.65593 | 52474.4 | 0 | 0 | 0.17178 | 6012.3 | 0 | 0 | 40000 | 0 | 6012.3 | 0 | 0 | 0 | 0 | 6462.1 | 0 | 0 | 6462.1
2022082224 | 2 | 0.61389 | 49111.2 | 0 | 0 | 0.13812 | 4834.2 | 0 | 0 | 40000 | 0 | 4834.2 | 0 | 0 | 0 | 0 | 4277 | 0 | 0 | 4277
2022082301 | 3 | 0.57872 | 46297.6 | 0 | 0 | 0.10788 | 3775.8 | 0 | 0 | 40000 | 0 | 3775.8 | 0 | 0 | 0 | 0 | 2521.8 | 0 | 0 | 2521.8
2022082302 | 3 | 0.55693 | 44554.4 | 0 | 0 | 0.09594 | 3357.9 | 0 | 0 | 40000 | 0 | 3357.9 | 0 | 0 | 0 | 0 | 1196.5 | 0 | 0 | 1196.5
2022082303 | 3 | 0.54223 | 43378.4 | 0 | 0 | 0.07591 | 2656.85 | 0 | 0 | 40000 | 0 | 2656.85 | 0 | 0 | 0 | 0 | 721.55 | 0 | 0 | 721.55
2022082304 | 3 | 0.5353 | 42824 | 0 | 0 | 0.0691 | 2418.5 | 0 | 0 | 40000 | 0 | 2418.5 | 0 | 0 | 0 | 0 | 405.5 | 0 | 0 | 405.5
2022082305 | 3 | 0.53566 | 42852.8 | 0 | 0 | 0.05489 | 1921.15 | 0 | 0 | 40000 | 0 | 1921.15 | 0 | 0 | 0 | 0 | 931.65 | 0 | 0 | 931.65
2022082306 | 3 | 0.55302 | 44241.6 | 0 | 0 | 0.05339 | 1868.65 | 0 | 0 | 40000 | 0 | 1868.65 | 0 | 0 | 0 | 0 | 2372.95 | 0 | 0 | 2372.95
2022082307 | 3 | 0.57936 | 46348.8 | 0 | 0 | 0.05182 | 1813.7 | 0 | 0 | 40000 | 0 | 1813.7 | 0 | 0 | 0 | 0 | 4535.1 | 0 | 0 | 4535.1
2022082308 | 3 | 0.59036 | 47228.8 | 0 | 0 | 0.05398 | 1889.3 | 0.01074 | 150.36 | 40000 | 0 | 1889.3 | 0 | 150.36 | 0 | 0 | 5189.14 | 0 | 0 | 5189.14
2022082309 | 3 | 0.59805 | 47844 | 0 | 0 | 0.04548 | 1591.8 | 0.12478 | 1746.92 | 40000 | 0 | 1591.8 | 0 | 1746.92 | 0 | 0 | 4505.28 | 0 | 0 | 4505.28
2022082310 | 3 | 0.6184 | 49472 | 0 | 0 | 0.04891 | 1711.85 | 0.26021 | 3642.94 | 40000 | 0 | 1711.85 | 0 | 3642.94 | 0 | 0 | 4117.21 | 0 | 0 | 4117.21
2022082311 | 3 | 0.64305 | 51444 | 0 | 0 | 0.0665 | 2327.5 | 0.33117 | 4636.38 | 40000 | 0 | 2327.5 | 0 | 4636.38 | 0 | 0 | 4480.12 | 0 | 0 | 4480.12
2022082312 | 3 | 0.66818 | 53454.4 | 0 | 0 | 0.07206 | 2522.1 | 0.38823 | 5435.22 | 40000 | 0 | 2522.1 | 0 | 5435.22 | 0 | 0 | 5497.08 | 0 | 0 | 5497.08
2022082313 | 3 | 0.69111 | 55288.8 | 0 | 0 | 0.06791 | 2376.85 | 0.46417 | 6498.38 | 40000 | 0 | 2376.85 | 0 | 6498.38 | 0 | 0 | 6413.57 | 0 | 0 | 6413.57
2022082314 | 3 | 0.71556 | 57244.8 | 0 | 0 | 0.06885 | 2409.75 | 0.49067 | 6869.38 | 40000 | 0 | 2409.75 | 0 | 6869.38 | 0 | 0 | 7965.67 | 0 | 0 | 7965.67
2022082315 | 3 | 0.73749 | 58999.2 | 0 | 0 | 0.07908 | 2767.8 | 0.49321 | 6904.94 | 40000 | 0 | 2767.8 | 0 | 6904.94 | 0 | 0 | 9326.46 | 0 | 0 | 9326.46
2022082316 | 3 | 0.7599 | 60792 | 0 | 0 | 0.08533 | 2986.55 | 0.50431 | 7060.34 | 40000 | 0 | 2986.55 | 0 | 7060.34 | 0 | 0 | 10745.11 | 0 | 0 | 10745.11
2022082317 | 3 | 0.78004 | 62403.2 | 0 | 0 | 0.10811 | 3783.85 | 0.51581 | 7221.34 | 40000 | 0 | 3783.85 | 0 | 7221.34 | 0 | 0 | 11398.01 | 0 | 0 | 11398.01
2022082318 | 3 | 0.7899 | 63192 | 0 | 0 | 0.1397 | 4889.5 | 0.45881 | 6423.34 | 40000 | 0 | 4889.5 | 0 | 6423.34 | 0 | 0 | 11879.16 | 0 | 0 | 11879.16
2022082319 | 3 | 0.77769 | 62215.2 | 0 | 0 | 0.17708 | 6197.8 | 0.35525 | 4973.5 | 40000 | 0 | 6197.8 | 0 | 4973.5 | 0 | 0 | 11043.9 | 0 | 0 | 11043.9
2022082320 | 3 | 0.75524 | 60419.2 | 0 | 0 | 0.16116 | 5640.6 | 0.10679 | 1495.06 | 40000 | 0 | 5640.6 | 0 | 1495.06 | 0 | 0 | 13283.54 | 0 | 0 | 13283.54
2022082321 | 3 | 0.73954 | 59163.2 | 0 | 0 | 0.13929 | 4875.15 | 0.00184 | 25.76 | 40000 | 0 | 4875.15 | 0 | 25.76 | 0 | 0 | 14262.29 | 0 | 0 | 14262.29
2022082322 | 3 | 0.71781 | 57424.8 | 0 | 0 | 0.13756 | 4814.6 | 0 | 0 | 40000 | 0 | 4814.6 | 0 | 0 | 0 | 0 | 12610.2 | 0 | 0 | 12610.2
2022082323 | 3 | 0.67865 | 54292 | 0 | 0 | 0.14426 | 5049.1 | 0 | 0 | 40000 | 0 | 5049.1 | 0 | 0 | 0 | 0 | 9242.9 | 0 | 0 | 9242.9
2022082324 | 3 | 0.63175 | 50540 | 0 | 0 | 0.13882 | 4858.7 | 0 | 0 | 40000 | 0 | 4858.7 | 0 | 0 | 0 | 0 | 5681.3 | 0 | 0 | 5681.3
2022082401 | 4 | 0.59625 | 47700 | 0 | 0 | 0.11684 | 4089.4 | 0 | 0 | 40000 | 0 | 4089.4 | 0 | 0 | 0 | 0 | 3610.6 | 0 | 0 | 3610.6
2022082402 | 4 | 0.57522 | 46017.6 | 0 | 0 | 0.10797 | 3778.95 | 0 | 0 | 40000 | 0 | 3778.95 | 0 | 0 | 0 | 0 | 2238.65 | 0 | 0 | 2238.65
2022082403 | 4 | 0.55994 | 44795.2 | 0 | 0 | 0.09535 | 3337.25 | 0 | 0 | 40000 | 0 | 3337.25 | 0 | 0 | 0 | 0 | 1457.95 | 0 | 0 | 1457.95
2022082404 | 4 | 0.55265 | 44212 | 0 | 0 | 0.08258 | 2890.3 | 0 | 0 | 40000 | 0 | 2890.3 | 0 | 0 | 0 | 0 | 1321.7 | 0 | 0 | 1321.7
2022082405 | 4 | 0.55108 | 44086.4 | 0 | 0 | 0.06878 | 2407.3 | 0 | 0 | 40000 | 0 | 2407.3 | 0 | 0 | 0 | 0 | 1679.1 | 0 | 0 | 1679.1
2022082406 | 4 | 0.56325 | 45060 | 0 | 0 | 0.05553 | 1943.55 | 0 | 0 | 40000 | 0 | 1943.55 | 0 | 0 | 0 | 0 | 3116.45 | 0 | 0 | 3116.45
2022082407 | 4 | 0.58888 | 47110.4 | 0 | 0 | 0.04769 | 1669.15 | 0 | 0 | 40000 | 0 | 1669.15 | 0 | 0 | 0 | 0 | 5441.25 | 0 | 0 | 5441.25
2022082408 | 4 | 0.59605 | 47684 | 0 | 0 | 0.03817 | 1335.95 | 0.02382 | 333.48 | 40000 | 0 | 1335.95 | 0 | 333.48 | 0 | 0 | 6014.57 | 0 | 0 | 6014.57
2022082409 | 4 | 0.60905 | 48724 | 0 | 0 | 0.02358 | 825.3 | 0.22815 | 3194.1 | 40000 | 0 | 825.3 | 0 | 3194.1 | 0 | 0 | 4704.6 | 0 | 0 | 4704.6
2022082410 | 4 | 0.63072 | 50457.6 | 0 | 0 | 0.01538 | 538.3 | 0.41958 | 5874.12 | 40000 | 0 | 538.3 | 0 | 5874.12 | 0 | 0 | 4045.18 | 0 | 0 | 4045.18
2022082411 | 4 | 0.65803 | 52642.4 | 0 | 0 | 0.02836 | 992.6 | 0.49944 | 6992.16 | 40000 | 0 | 992.6 | 0 | 6992.16 | 0 | 0 | 4657.64 | 0 | 0 | 4657.64
2022082412 | 4 | 0.6862 | 54896 | 0 | 0 | 0.03815 | 1335.25 | 0.57031 | 7984.34 | 40000 | 0 | 1335.25 | 0 | 7984.34 | 0 | 0 | 5576.41 | 0 | 0 | 5576.41
2022082413 | 4 | 0.71764 | 57411.2 | 0 | 0 | 0.03656 | 1279.6 | 0.57076 | 7990.64 | 40000 | 0 | 1279.6 | 0 | 7990.64 | 0 | 0 | 8140.96 | 0 | 0 | 8140.96
2022082414 | 4 | 0.74863 | 59890.4 | 0 | 0 | 0.04546 | 1591.1 | 0.56619 | 7926.66 | 40000 | 0 | 1591.1 | 0 | 7926.66 | 0 | 0 | 10372.64 | 0 | 0 | 10372.64
2022082415 | 4 | 0.76695 | 61356 | 0 | 0 | 0.06454 | 2258.9 | 0.57474 | 8046.36 | 40000 | 0 | 2258.9 | 0 | 8046.36 | 0 | 0 | 11050.74 | 0 | 0 | 11050.74
2022082416 | 4 | 0.77784 | 62227.2 | 0 | 0 | 0.10651 | 3727.85 | 0.55773 | 7808.22 | 40000 | 0 | 3727.85 | 0 | 7808.22 | 0 | 0 | 10691.13 | 0 | 0 | 10691.13
2022082417 | 4 | 0.78532 | 62825.6 | 0 | 0 | 0.13649 | 4777.15 | 0.44669 | 6253.66 | 40000 | 0 | 4777.15 | 0 | 6253.66 | 0 | 0 | 11794.79 | 0 | 0 | 11794.79
2022082418 | 4 | 0.78839 | 63071.2 | 0 | 0 | 0.14701 | 5145.35 | 0.42385 | 5933.9 | 40000 | 0 | 5145.35 | 0 | 5933.9 | 0 | 0 | 11991.95 | 0 | 0 | 11991.95
2022082419 | 4 | 0.77571 | 62056.8 | 0 | 0 | 0.16379 | 5732.65 | 0.30162 | 4222.68 | 40000 | 0 | 5732.65 | 0 | 4222.68 | 0 | 0 | 12101.47 | 0 | 0 | 12101.47
2022082420 | 4 | 0.75471 | 60376.8 | 0 | 0 | 0.17238 | 6033.3 | 0.09371 | 1311.94 | 40000 | 0 | 6033.3 | 0 | 1311.94 | 0 | 0 | 13031.56 | 0 | 0 | 13031.56
2022082421 | 4 | 0.74099 | 59279.2 | 0 | 0 | 0.16432 | 5751.2 | 0.01416 | 198.24 | 40000 | 0 | 5751.2 | 0 | 198.24 | 0 | 0 | 13329.76 | 0 | 0 | 13329.76
2022082422 | 4 | 0.71387 | 57109.6 | 0 | 0 | 0.15569 | 5449.15 | 0.01195 | 167.3 | 40000 | 0 | 5449.15 | 0 | 167.3 | 0 | 0 | 11493.15 | 0 | 0 | 11493.15
2022082423 | 4 | 0.66683 | 53346.4 | 0 | 0 | 0.13926 | 4874.1 | 0.00328 | 45.92 | 40000 | 0 | 4874.1 | 0 | 45.92 | 0 | 0 | 8426.38 | 0 | 0 | 8426.38
2022082424 | 4 | 0.61905 | 49524 | 0 | 0 | 0.11831 | 4140.85 | 0 | 0 | 40000 | 0 | 4140.85 | 0 | 0 | 0 | 0 | 5383.15 | 0 | 0 | 5383.15
2022082501 | 5 | 0.58243 | 46594.4 | 0 | 0 | 0.09759 | 3415.65 | 0 | 0 | 40000 | 0 | 3415.65 | 0 | 0 | 0 | 0 | 3178.75 | 0 | 0 | 3178.75
2022082502 | 5 | 0.55801 | 44640.8 | 0 | 0 | 0.08364 | 2927.4 | 0 | 0 | 40000 | 0 | 2927.4 | 0 | 0 | 0 | 0 | 1713.4 | 0 | 0 | 1713.4
2022082503 | 5 | 0.54239 | 43391.2 | 0 | 0 | 0.06654 | 2328.9 | 0 | 0 | 40000 | 0 | 2328.9 | 0 | 0 | 0 | 0 | 1062.3 | 0 | 0 | 1062.3
2022082504 | 5 | 0.53116 | 42492.8 | 0 | 0 | 0.05832 | 2041.2 | 0 | 0 | 40000 | 0 | 2041.2 | 0 | 0 | 0 | 0 | 451.6 | 0 | 0 | 451.6
2022082505 | 5 | 0.53126 | 42500.8 | 0 | 0 | 0.04684 | 1639.4 | 0 | 0 | 40000 | 0 | 1639.4 | 0 | 0 | 0 | 0 | 861.4 | 0 | 0 | 861.4
2022082506 | 5 | 0.54613 | 43690.4 | 0 | 0 | 0.0397 | 1389.5 | 0 | 0 | 40000 | 0 | 1389.5 | 0 | 0 | 0 | 0 | 2300.9 | 0 | 0 | 2300.9
2022082507 | 5 | 0.5742 | 45936 | 0 | 0 | 0.03676 | 1286.6 | 0 | 0 | 40000 | 0 | 1286.6 | 0 | 0 | 0 | 0 | 4649.4 | 0 | 0 | 4649.4
2022082508 | 5 | 0.5819 | 46552 | 0 | 0 | 0.03468 | 1213.8 | 0.03171 | 443.94 | 40000 | 0 | 1213.8 | 0 | 443.94 | 0 | 0 | 4894.26 | 0 | 0 | 4894.26
2022082509 | 5 | 0.60119 | 48095.2 | 0 | 0 | 0.02066 | 723.1 | 0.27899 | 3905.86 | 40000 | 0 | 723.1 | 0 | 3905.86 | 0 | 0 | 3466.24 | 0 | 0 | 3466.24
2022082510 | 5 | 0.63406 | 50724.8 | 0 | 0 | 0.01472 | 515.2 | 0.45322 | 6345.08 | 40000 | 0 | 515.2 | 0 | 6345.08 | 0 | 0 | 3864.52 | 0 | 0 | 3864.52
2022082511 | 5 | 0.67763 | 54210.4 | 0 | 0 | 0.02359 | 825.65 | 0.5337 | 7471.8 | 40000 | 0 | 825.65 | 0 | 7471.8 | 0 | 0 | 5912.95 | 0 | 0 | 5912.95
2022082512 | 5 | 0.71824 | 57459.2 | 0 | 0 | 0.02849 | 997.15 | 0.56926 | 7969.64 | 40000 | 0 | 997.15 | 0 | 7969.64 | 0 | 0 | 8492.41 | 0 | 0 | 8492.41
2022082513 | 5 | 0.75342 | 60273.6 | 0 | 0 | 0.02196 | 768.6 | 0.57282 | 8019.48 | 40000 | 0 | 768.6 | 0 | 8019.48 | 0 | 0 | 11485.52 | 0 | 0 | 11485.52
2022082514 | 5 | 0.78741 | 62992.8 | 0 | 0 | 0.02955 | 1034.25 | 0.57833 | 8096.62 | 40000 | 0 | 1034.25 | 0 | 8096.62 | 0 | 0 | 13861.93 | 0 | 0 | 13861.93
2022082515 | 5 | 0.81263 | 65010.4 | 0 | 0 | 0.06176 | 2161.6 | 0.57664 | 8072.96 | 40000 | 0 | 2161.6 | 0 | 8072.96 | 0 | 0 | 14775.84 | 0 | 0 | 14775.84
2022082516 | 5 | 0.83416 | 66732.8 | 0 | 0 | 0.08425 | 2948.75 | 0.5003 | 7004.2 | 40000 | 0 | 2948.75 | 0 | 7004.2 | 0 | 0 | 16779.85 | 0 | 0 | 16779.85
2022082517 | 5 | 0.84785 | 67828 | 0 | 0 | 0.0805 | 2817.5 | 0.50239 | 7033.46 | 40000 | 0 | 2817.5 | 0 | 7033.46 | 0 | 0 | 17977.04 | 0 | 0 | 17977.04
2022082518 | 5 | 0.84547 | 67637.6 | 0 | 0 | 0.06785 | 2374.75 | 0.49246 | 6894.44 | 40000 | 0 | 2374.75 | 0 | 6894.44 | 0 | 0 | 18368.41 | 0 | 0 | 18368.41
2022082519 | 5 | 0.82924 | 66339.2 | 0 | 0 | 0.06703 | 2346.05 | 0.39579 | 5541.06 | 40000 | 0 | 2346.05 | 0 | 5541.06 | 0 | 0 | 18452.09 | 0 | 0 | 18452.09
2022082520 | 5 | 0.79844 | 63875.2 | 0 | 0 | 0.07685 | 2689.75 | 0.13788 | 1930.32 | 40000 | 0 | 2689.75 | 0 | 1930.32 | 0 | 0 | 19255.13 | 0 | 0 | 19255.13
2022082521 | 5 | 0.77582 | 62065.6 | 0 | 0 | 0.08737 | 3057.95 | 0.0021 | 29.4 | 40000 | 0 | 3057.95 | 0 | 29.4 | 0 | 0 | 18978.25 | 0 | 0 | 18978.25
2022082522 | 5 | 0.74869 | 59895.2 | 0 | 0 | 0.10919 | 3821.65 | 0 | 0 | 40000 | 0 | 3821.65 | 0 | 0 | 0 | 0 | 16073.55 | 0 | 0 | 16073.55
2022082523 | 5 | 0.70232 | 56185.6 | 0 | 0 | 0.13267 | 4643.45 | 0 | 0 | 40000 | 0 | 4643.45 | 0 | 0 | 0 | 0 | 11542.15 | 0 | 0 | 11542.15
2022082524 | 5 | 0.6524 | 52192 | 0 | 0 | 0.1407 | 4924.5 | 0 | 0 | 40000 | 0 | 4924.5 | 0 | 0 | 0 | 0 | 7267.5 | 0 | 0 | 7267.5
2022082601 | 6 | 0.60918 | 48734.4 | 0 | 0 | 0.15169 | 5309.15 | 0 | 0 | 40000 | 0 | 5309.15 | 0 | 0 | 0 | 0 | 3425.25 | 0 | 0 | 3425.25
2022082602 | 6 | 0.58088 | 46470.4 | 0 | 0 | 0.15163 | 5307.05 | 0 | 0 | 40000 | 0 | 5307.05 | 0 | 0 | 0 | 0 | 1163.35 | 0 | 0 | 1163.35
2022082603 | 6 | 0.56296 | 45036.8 | 0 | 0 | 0.14743 | 5160.05 | 0 | 0 | 40000 | 0 | 5036.8 | 123.25 | 0 | 0 | 123.25 | 0 | 0 | 0 | 0
2022082604 | 6 | 0.54909 | 43927.2 | 0 | 0 | 0.12863 | 4502.05 | 0 | 0 | 40000 | 0 | 3927.2 | 574.85 | 0 | 0 | 574.85 | 0 | 0 | 0 | 0
2022082605 | 6 | 0.54546 | 43636.8 | 0 | 0 | 0.10741 | 3759.35 | 0 | 0 | 40000 | 0 | 3636.8 | 122.55 | 0 | 0 | 122.55 | 0 | 0 | 0 | 0
2022082606 | 6 | 0.55906 | 44724.8 | 0 | 0 | 0.09769 | 3419.15 | 0 | 0 | 40000 | 0 | 3419.15 | 0 | 0 | 0 | 0 | 1305.65 | 0 | 0 | 1305.65
2022082607 | 6 | 0.58498 | 46798.4 | 0 | 0 | 0.07908 | 2767.8 | 0 | 0 | 40000 | 0 | 2767.8 | 0 | 0 | 0 | 0 | 4030.6 | 0 | 0 | 4030.6
2022082608 | 6 | 0.59257 | 47405.6 | 0 | 0 | 0.06416 | 2245.6 | 0.03703 | 518.42 | 40000 | 0 | 2245.6 | 0 | 518.42 | 0 | 0 | 4641.58 | 0 | 0 | 4641.58
2022082609 | 6 | 0.61329 | 49063.2 | 0 | 0 | 0.03787 | 1325.45 | 0.3436 | 4810.4 | 40000 | 0 | 1325.45 | 0 | 4810.4 | 0 | 0 | 2927.35 | 0 | 0 | 2927.35
2022082610 | 6 | 0.655 | 52400 | 0 | 0 | 0.02209 | 773.15 | 0.61307 | 8582.98 | 40000 | 0 | 773.15 | 0 | 8582.98 | 0 | 0 | 3043.87 | 0 | 0 | 3043.87
2022082611 | 6 | 0.70126 | 56100.8 | 0 | 0 | 0.02633 | 921.55 | 0.69405 | 9716.7 | 40000 | 0 | 921.55 | 0 | 9716.7 | 0 | 0 | 5462.55 | 0 | 0 | 5462.55
2022082612 | 6 | 0.74735 | 59788 | 0 | 0 | 0.02418 | 846.3 | 0.69865 | 9781.1 | 40000 | 0 | 846.3 | 0 | 9781.1 | 0 | 0 | 9160.6 | 0 | 0 | 9160.6
2022082613 | 6 | 0.78858 | 63086.4 | 0 | 0 | 0.01962 | 686.7 | 0.65646 | 9190.44 | 40000 | 0 | 686.7 | 0 | 9190.44 | 0 | 0 | 13209.26 | 0 | 0 | 13209.26
2022082614 | 6 | 0.81956 | 65564.8 | 0 | 0 | 0.03044 | 1065.4 | 0.60953 | 8533.42 | 40000 | 0 | 1065.4 | 0 | 8533.42 | 0 | 0 | 15965.98 | 0 | 0 | 15965.98
2022082615 | 6 | 0.83969 | 67175.2 | 0 | 0 | 0.05678 | 1987.3 | 0.53159 | 7442.26 | 40000 | 0 | 1987.3 | 0 | 7442.26 | 0 | 0 | 17745.64 | 0 | 0 | 17745.64
2022082616 | 6 | 0.84855 | 67884 | 0 | 0 | 0.06305 | 2206.75 | 0.53304 | 7462.56 | 40000 | 0 | 2206.75 | 0 | 7462.56 | 0 | 0 | 18214.69 | 0 | 0 | 18214.69
2022082617 | 6 | 0.85572 | 68457.6 | 0 | 0 | 0.07578 | 2652.3 | 0.56823 | 7955.22 | 40000 | 0 | 2652.3 | 0 | 7955.22 | 0 | 0 | 17850.08 | 0 | 0 | 17850.08
2022082618 | 6 | 0.85168 | 68134.4 | 0 | 0 | 0.07697 | 2693.95 | 0.53611 | 7505.54 | 40000 | 0 | 2693.95 | 0 | 7505.54 | 0 | 0 | 17934.91 | 0 | 0 | 17934.91
2022082619 | 6 | 0.83014 | 66411.2 | 0 | 0 | 0.08678 | 3037.3 | 0.43043 | 6026.02 | 40000 | 0 | 3037.3 | 0 | 6026.02 | 0 | 0 | 17347.88 | 0 | 0 | 17347.88
2022082620 | 6 | 0.79676 | 63740.8 | 0 | 0 | 0.1122 | 3927 | 0.13023 | 1823.22 | 40000 | 0 | 3927 | 0 | 1823.22 | 0 | 0 | 17990.58 | 0 | 0 | 17990.58
2022082621 | 6 | 0.77212 | 61769.6 | 0 | 0 | 0.1509 | 5281.5 | 0.00265 | 37.1 | 40000 | 0 | 5281.5 | 0 | 37.1 | 0 | 0 | 16451 | 0 | 0 | 16451
2022082622 | 6 | 0.74261 | 59408.8 | 0 | 0 | 0.22308 | 7807.8 | 0 | 0 | 40000 | 0 | 7807.8 | 0 | 0 | 0 | 0 | 11601 | 0 | 0 | 11601
2022082623 | 6 | 0.70398 | 56318.4 | 0 | 0 | 0.29152 | 10203.2 | 0 | 0 | 40000 | 0 | 10203.2 | 0 | 0 | 0 | 0 | 6115.2 | 0 | 0 | 6115.2
2022082624 | 6 | 0.66422 | 53137.6 | 0 | 0 | 0.33839 | 11843.65 | 0 | 0 | 40000 | 0 | 11843.65 | 0 | 0 | 0 | 0 | 1293.95 | 0 | 0 | 1293.95
2022082701 | 7 | 0.62648 | 50118.4 | 0 | 0 | 0.3619 | 12666.5 | 0 | 0 | 40000 | 0 | 10118.4 | 2548.1 | 0 | 0 | 2548.1 | 0 | 0 | 0 | 0
2022082702 | 7 | 0.59585 | 47668 | 0 | 0 | 0.34596 | 12108.6 | 0 | 0 | 40000 | 0 | 7668 | 4440.6 | 0 | 0 | 4440.6 | 0 | 0 | 0 | 0
2022082703 | 7 | 0.57527 | 46021.6 | 0 | 0 | 0.34036 | 11912.6 | 0 | 0 | 40000 | 0 | 6021.6 | 5891 | 0 | 0 | 5891 | 0 | 0 | 0 | 0
2022082704 | 7 | 0.55895 | 44716 | 0 | 0 | 0.33245 | 11635.75 | 0 | 0 | 40000 | 0 | 4716 | 6919.75 | 0 | 0 | 6919.75 | 0 | 0 | 0 | 0
2022082705 | 7 | 0.54705 | 43764 | 0 | 0 | 0.29198 | 10219.3 | 0 | 0 | 40000 | 0 | 3764 | 6455.3 | 0 | 0 | 6455.3 | 0 | 0 | 0 | 0
2022082706 | 7 | 0.54587 | 43669.6 | 0 | 0 | 0.25949 | 9082.15 | 0 | 0 | 40000 | 0 | 3669.6 | 5412.55 | 0 | 0 | 5412.55 | 0 | 0 | 0 | 0
2022082707 | 7 | 0.54915 | 43932 | 0 | 0 | 0.25542 | 8939.7 | 0 | 0 | 40000 | 0 | 3932 | 5007.7 | 0 | 0 | 5007.7 | 0 | 0 | 0 | 0
2022082708 | 7 | 0.55432 | 44345.6 | 0 | 0 | 0.23363 | 8177.05 | 0.03637 | 509.18 | 40000 | 0 | 4345.6 | 3831.45 | 0 | 509.18 | 4340.63 | 0 | 0 | 0 | 0
2022082709 | 7 | 0.58846 | 47076.8 | 0 | 0 | 0.17085 | 5979.75 | 0.34396 | 4815.44 | 40000 | 0 | 5979.75 | 0 | 1097.05 | 3718.39 | 3718.39 | 0 | 0 | 0 | 0
2022082710 | 7 | 0.63842 | 51073.6 | 0 | 0 | 0.14477 | 5066.95 | 0.612 | 8568 | 40000 | 0 | 5066.95 | 0 | 6006.65 | 2561.35 | 2561.35 | 0 | 0 | 0 | 0
2022082711 | 7 | 0.69256 | 55404.8 | 0 | 0 | 0.1714 | 5999 | 0.7272 | 10180.8 | 40000 | 0 | 5999 | 0 | 9405.8 | 775 | 775 | 0 | 0 | 0 | 0
2022082712 | 7 | 0.74082 | 59265.6 | 0 | 0 | 0.17606 | 6162.1 | 0.74362 | 10410.68 | 40000 | 0 | 6162.1 | 0 | 10410.68 | 0 | 0 | 2692.82 | 0 | 0 | 2692.82
2022082713 | 7 | 0.78116 | 62492.8 | 0 | 0 | 0.1763 | 6170.5 | 0.74567 | 10439.38 | 40000 | 0 | 6170.5 | 0 | 10439.38 | 0 | 0 | 5882.92 | 0 | 0 | 5882.92
2022082714 | 7 | 0.81306 | 65044.8 | 0 | 0 | 0.19138 | 6698.3 | 0.74223 | 10391.22 | 40000 | 0 | 6698.3 | 0 | 10391.22 | 0 | 0 | 7955.28 | 0 | 0 | 7955.28
2022082715 | 7 | 0.83548 | 66838.4 | 0 | 0 | 0.19521 | 6832.35 | 0.68911 | 9647.54 | 40000 | 0 | 6832.35 | 0 | 9647.54 | 0 | 0 | 10358.51 | 0 | 0 | 10358.51
2022082716 | 7 | 0.84997 | 67997.6 | 0 | 0 | 0.20958 | 7335.3 | 0.65561 | 9178.54 | 40000 | 0 | 7335.3 | 0 | 9178.54 | 0 | 0 | 11483.76 | 0 | 0 | 11483.76
2022082717 | 7 | 0.86027 | 68821.6 | 0 | 0 | 0.22886 | 8010.1 | 0.64428 | 9019.92 | 40000 | 0 | 8010.1 | 0 | 9019.92 | 0 | 0 | 11791.58 | 0 | 0 | 11791.58
2022082718 | 7 | 0.86549 | 69239.2 | 0 | 0 | 0.26249 | 9187.15 | 0.63211 | 8849.54 | 40000 | 0 | 9187.15 | 0 | 8849.54 | 0 | 0 | 11202.51 | 0 | 0 | 11202.51
2022082719 | 7 | 0.84818 | 67854.4 | 0 | 0 | 0.31215 | 10925.25 | 0.49936 | 6991.04 | 40000 | 0 | 10925.25 | 0 | 6991.04 | 0 | 0 | 9938.11 | 0 | 0 | 9938.11
2022082720 | 7 | 0.81359 | 65087.2 | 0 | 0 | 0.31777 | 11121.95 | 0.14071 | 1969.94 | 40000 | 0 | 11121.95 | 0 | 1969.94 | 0 | 0 | 11995.31 | 0 | 0 | 11995.31
2022082721 | 7 | 0.78706 | 62964.8 | 0 | 0 | 0.34423 | 12048.05 | 0.0006 | 8.4 | 40000 | 0 | 12048.05 | 0 | 8.4 | 0 | 0 | 10908.35 | 0 | 0 | 10908.35
2022082722 | 7 | 0.75771 | 60616.8 | 0 | 0 | 0.39487 | 13820.45 | 0 | 0 | 40000 | 0 | 13820.45 | 0 | 0 | 0 | 0 | 6796.35 | 0 | 0 | 6796.35
2022082723 | 7 | 0.72025 | 57620 | 0 | 0 | 0.4343 | 15200.5 | 0 | 0 | 40000 | 0 | 15200.5 | 0 | 0 | 0 | 0 | 2419.5 | 0 | 0 | 2419.5
2022082724 | 7 | 0.68177 | 54541.6 | 0 | 0 | 0.48321 | 16912.35 | 0 | 0 | 40000 | 0 | 14541.6 | 2370.75 | 0 | 0 | 2370.75 | 0 | 0 | 0 | 0
2022082801 | 1 | 0.64461 | 51568.8 | 0 | 0 | 0.48461 | 16961.35 | 0 | 0 | 40000 | 0 | 11568.8 | 5392.55 | 0 | 0 | 5392.55 | 0 | 0 | 0 | 0
2022082802 | 1 | 0.61514 | 49211.2 | 0 | 0 | 0.50231 | 17580.85 | 0 | 0 | 40000 | 0 | 9211.2 | 8369.65 | 0 | 0 | 8369.65 | 0 | 0 | 0 | 0
2022082803 | 1 | 0.59358 | 47486.4 | 0 | 0 | 0.51094 | 17882.9 | 0 | 0 | 40000 | 0 | 7486.4 | 10396.5 | 0 | 0 | 10396.5 | 0 | 0 | 0 | 0
2022082804 | 1 | 0.57496 | 45996.8 | 0 | 0 | 0.48307 | 16907.45 | 0 | 0 | 40000 | 0 | 5996.8 | 10910.65 | 0 | 0 | 10910.65 | 0 | 0 | 0 | 0
2022082805 | 1 | 0.56177 | 44941.6 | 0 | 0 | 0.43294 | 15152.9 | 0 | 0 | 40000 | 0 | 4941.6 | 10211.3 | 0 | 0 | 10211.3 | 0 | 0 | 0 | 0
2022082806 | 1 | 0.55646 | 44516.8 | 0 | 0 | 0.40255 | 14089.25 | 0 | 0 | 40000 | 0 | 4516.8 | 9572.45 | 0 | 0 | 9572.45 | 0 | 0 | 0 | 0
2022082807 | 1 | 0.55596 | 44476.8 | 0 | 0 | 0.39579 | 13852.65 | 0 | 0 | 40000 | 0 | 4476.8 | 9375.85 | 0 | 0 | 9375.85 | 0 | 0 | 0 | 0
2022082808 | 1 | 0.55867 | 44693.6 | 0 | 0 | 0.39274 | 13745.9 | 0.04705 | 658.7 | 40000 | 0 | 4693.6 | 9052.3 | 0 | 658.7 | 9711 | 0 | 0 | 0 | 0
2022082809 | 1 | 0.59446 | 47556.8 | 0 | 0 | 0.34354 | 12023.9 | 0.40848 | 5718.72 | 40000 | 0 | 7556.8 | 4467.1 | 0 | 5718.72 | 10185.82 | 0 | 0 | 0 | 0
2022082810 | 1 | 0.65038 | 52030.4 | 0 | 0 | 0.34626 | 12119.1 | 0.68917 | 9648.38 | 40000 | 0 | 12030.4 | 88.7 | 0 | 9648.38 | 9737.08 | 0 | 0 | 0 | 0
2022082811 | 1 | 0.70297 | 56237.6 | 0 | 0 | 0.30056 | 10519.6 | 0.76329 | 10686.06 | 40000 | 0 | 10519.6 | 0 | 5718 | 4968.06 | 4968.06 | 0 | 0 | 0 | 0
2022082812 | 1 | 0.7532 | 60256 | 0 | 0 | 0.23827 | 8339.45 | 0.78705 | 11018.7 | 40000 | 0 | 8339.45 | 0 | 11018.7 | 0 | 0 | 897.85 | 0 | 0 | 897.85
2022082813 | 1 | 0.79943 | 63954.4 | 0 | 0 | 0.21922 | 7672.7 | 0.78015 | 10922.1 | 40000 | 0 | 7672.7 | 0 | 10922.1 | 0 | 0 | 5359.6 | 0 | 0 | 5359.6
2022082814 | 1 | 0.83739 | 66991.2 | 0 | 0 | 0.20616 | 7215.6 | 0.75003 | 10500.42 | 40000 | 0 | 7215.6 | 0 | 10500.42 | 0 | 0 | 9275.18 | 0 | 0 | 9275.18
2022082815 | 1 | 0.8648 | 69184 | 0 | 0 | 0.20435 | 7152.25 | 0.72002 | 10080.28 | 40000 | 0 | 7152.25 | 0 | 10080.28 | 0 | 0 | 11951.47 | 0 | 0 | 11951.47
2022082816 | 1 | 0.88112 | 70489.6 | 0 | 0 | 0.2192 | 7672 | 0.67637 | 9469.18 | 40000 | 0 | 7672 | 0 | 9469.18 | 0 | 0 | 13348.42 | 0 | 0 | 13348.42
2022082817 | 1 | 0.88903 | 71122.4 | 0 | 0 | 0.25587 | 8955.45 | 0.51349 | 7188.86 | 40000 | 0 | 8955.45 | 0 | 7188.86 | 0 | 0 | 14978.09 | 0 | 0 | 14978.09
2022082818 | 1 | 0.89105 | 71284 | 0 | 0 | 0.32177 | 11261.95 | 0.47273 | 6618.22 | 40000 | 0 | 11261.95 | 0 | 6618.22 | 0 | 0 | 13403.83 | 0 | 0 | 13403.83
2022082819 | 1 | 0.87383 | 69906.4 | 0 | 0 | 0.43819 | 15336.65 | 0.38125 | 5337.5 | 40000 | 0 | 15336.65 | 0 | 5337.5 | 0 | 0 | 9232.25 | 0 | 0 | 9232.25
2022082820 | 1 | 0.84347 | 67477.6 | 0 | 0 | 0.49224 | 17228.4 | 0.11039 | 1545.46 | 40000 | 0 | 17228.4 | 0 | 1545.46 | 0 | 0 | 8703.74 | 0 | 0 | 8703.74
2022082821 | 1 | 0.81994 | 65595.2 | 0 | 0 | 0.4499 | 15746.5 | 0.00119 | 16.66 | 40000 | 0 | 15746.5 | 0 | 16.66 | 0 | 0 | 9832.04 | 0 | 0 | 9832.04
2022082822 | 1 | 0.78855 | 63084 | 0 | 0 | 0.4762 | 16667 | 0 | 0 | 40000 | 0 | 16667 | 0 | 0 | 0 | 0 | 6417 | 0 | 0 | 6417
2022082823 | 1 | 0.73773 | 59018.4 | 0 | 0 | 0.45515 | 15930.25 | 0 | 0 | 40000 | 0 | 15930.25 | 0 | 0 | 0 | 0 | 3088.15 | 0 | 0 | 3088.15
2022082824 | 1 | 0.68537 | 54829.6 | 0 | 0 | 0.40684 | 14239.4 | 0 | 0 | 40000 | 0 | 14239.4 | 0 | 0 | 0 | 0 | 590.2 | 0 | 0 | 590.2
2022082901 | 2 | 0.63824 | 51059.2 | 0 | 0 | 0.38642 | 13524.7 | 0 | 0 | 40000 | 0 | 11059.2 | 2465.5 | 0 | 0 | 2465.5 | 0 | 0 | 0 | 0
2022082902 | 2 | 0.60795 | 48636 | 0 | 0 | 0.34466 | 12063.1 | 0 | 0 | 40000 | 0 | 8636 | 3427.1 | 0 | 0 | 3427.1 | 0 | 0 | 0 | 0
2022082903 | 2 | 0.58959 | 47167.2 | 0 | 0 | 0.31155 | 10904.25 | 0 | 0 | 40000 | 0 | 7167.2 | 3737.05 | 0 | 0 | 3737.05 | 0 | 0 | 0 | 0
2022082904 | 2 | 0.57968 | 46374.4 | 0 | 0 | 0.28077 | 9826.95 | 0 | 0 | 40000 | 0 | 6374.4 | 3452.55 | 0 | 0 | 3452.55 | 0 | 0 | 0 | 0
2022082905 | 2 | 0.57905 | 46324 | 0 | 0 | 0.2645 | 9257.5 | 0 | 0 | 40000 | 0 | 6324 | 2933.5 | 0 | 0 | 2933.5 | 0 | 0 | 0 | 0
2022082906 | 2 | 0.59123 | 47298.4 | 0 | 0 | 0.24279 | 8497.65 | 0 | 0 | 40000 | 0 | 7298.4 | 1199.25 | 0 | 0 | 1199.25 | 0 | 0 | 0 | 0
2022082907 | 2 | 0.62079 | 49663.2 | 0 | 0 | 0.24997 | 8748.95 | 0 | 0 | 40000 | 0 | 8748.95 | 0 | 0 | 0 | 0 | 914.25 | 0 | 0 | 914.25
2022082908 | 2 | 0.62636 | 50108.8 | 0 | 0 | 0.24085 | 8429.75 | 0.03155 | 441.7 | 40000 | 0 | 8429.75 | 0 | 441.7 | 0 | 0 | 1237.35 | 0 | 0 | 1237.35
2022082909 | 2 | 0.63956 | 51164.8 | 0 | 0 | 0.20965 | 7337.75 | 0.29236 | 4093.04 | 40000 | 0 | 7337.75 | 0 | 3827.05 | 265.99 | 265.99 | 0 | 0 | 0 | 0
2022082910 | 2 | 0.67283 | 53826.4 | 0 | 0 | 0.23321 | 8162.35 | 0.52996 | 7419.44 | 40000 | 0 | 8162.35 | 0 | 5664.05 | 1755.39 | 1755.39 | 0 | 0 | 0 | 0
2022082911 | 2 | 0.71928 | 57542.4 | 0 | 0 | 0.22733 | 7956.55 | 0.64482 | 9027.48 | 40000 | 0 | 7956.55 | 0 | 9027.48 | 0 | 0 | 558.37 | 0 | 0 | 558.37
2022082912 | 2 | 0.75663 | 60530.4 | 0 | 0 | 0.1941 | 6793.5 | 0.68394 | 9575.16 | 40000 | 0 | 6793.5 | 0 | 9575.16 | 0 | 0 | 4161.74 | 0 | 0 | 4161.74
2022082913 | 2 | 0.79723 | 63778.4 | 0 | 0 | 0.17104 | 5986.4 | 0.69225 | 9691.5 | 40000 | 0 | 5986.4 | 0 | 9691.5 | 0 | 0 | 8100.5 | 0 | 0 | 8100.5
2022082914 | 2 | 0.83025 | 66420 | 0 | 0 | 0.17188 | 6015.8 | 0.65346 | 9148.44 | 40000 | 0 | 6015.8 | 0 | 9148.44 | 0 | 0 | 11255.76 | 0 | 0 | 11255.76
2022082915 | 2 | 0.84895 | 67916 | 0 | 0 | 0.19402 | 6790.7 | 0.62458 | 8744.12 | 40000 | 0 | 6790.7 | 0 | 8744.12 | 0 | 0 | 12381.18 | 0 | 0 | 12381.18
2022082916 | 2 | 0.85719 | 68575.2 | 0 | 0 | 0.22702 | 7945.7 | 0.57552 | 8057.28 | 40000 | 0 | 7945.7 | 0 | 8057.28 | 0 | 0 | 12572.22 | 0 | 0 | 12572.22
2022082917 | 2 | 0.86067 | 68853.6 | 0 | 0 | 0.28186 | 9865.1 | 0.51655 | 7231.7 | 40000 | 0 | 9865.1 | 0 | 7231.7 | 0 | 0 | 11756.8 | 0 | 0 | 11756.8
2022082918 | 2 | 0.85455 | 68364 | 0 | 0 | 0.3059 | 10706.5 | 0.42485 | 5947.9 | 40000 | 0 | 10706.5 | 0 | 5947.9 | 0 | 0 | 11709.6 | 0 | 0 | 11709.6
2022082919 | 2 | 0.83469 | 66775.2 | 0 | 0 | 0.3257 | 11399.5 | 0.21087 | 2952.18 | 40000 | 0 | 11399.5 | 0 | 2952.18 | 0 | 0 | 12423.52 | 0 | 0 | 12423.52
2022082920 | 2 | 0.80424 | 64339.2 | 0 | 0 | 0.33506 | 11727.1 | 0.04412 | 617.68 | 40000 | 0 | 11727.1 | 0 | 617.68 | 0 | 0 | 11994.42 | 0 | 0 | 11994.42
2022082921 | 2 | 0.78156 | 62524.8 | 0 | 0 | 0.37018 | 12956.3 | 0.00072 | 10.08 | 40000 | 0 | 12956.3 | 0 | 10.08 | 0 | 0 | 9558.42 | 0 | 0 | 9558.42
2022082922 | 2 | 0.7451 | 59608 | 0 | 0 | 0.42137 | 14747.95 | 0 | 0 | 40000 | 0 | 14747.95 | 0 | 0 | 0 | 0 | 4860.05 | 0 | 0 | 4860.05
2022082923 | 2 | 0.68943 | 55154.4 | 0 | 0 | 0.45034 | 15761.9 | 0 | 0 | 40000 | 0 | 15154.4 | 607.5 | 0 | 0 | 607.5 | 0 | 0 | 0 | 0
2022082924 | 2 | 0.6391 | 51128 | 0 | 0 | 0.36746 | 12861.1 | 0 | 0 | 40000 | 0 | 11128 | 1733.1 | 0 | 0 | 1733.1 | 0 | 0 | 0 | 0
2022083001 | 3 | 0.60409 | 48327.2 | 0 | 0 | 0.28652 | 10028.2 | 0 | 0 | 40000 | 0 | 8327.2 | 1701 | 0 | 0 | 1701 | 0 | 0 | 0 | 0
2022083002 | 3 | 0.57919 | 46335.2 | 0 | 0 | 0.21648 | 7576.8 | 0 | 0 | 40000 | 0 | 6335.2 | 1241.6 | 0 | 0 | 1241.6 | 0 | 0 | 0 | 0
2022083003 | 3 | 0.56631 | 45304.8 | 0 | 0 | 0.17922 | 6272.7 | 0 | 0 | 40000 | 0 | 5304.8 | 967.9 | 0 | 0 | 967.9 | 0 | 0 | 0 | 0
2022083004 | 3 | 0.56077 | 44861.6 | 0 | 0 | 0.15737 | 5507.95 | 0 | 0 | 40000 | 0 | 4861.6 | 646.35 | 0 | 0 | 646.35 | 0 | 0 | 0 | 0
2022083005 | 3 | 0.56214 | 44971.2 | 0 | 0 | 0.13628 | 4769.8 | 0 | 0 | 40000 | 0 | 4769.8 | 0 | 0 | 0 | 0 | 201.4 | 0 | 0 | 201.4
2022083006 | 3 | 0.58016 | 46412.8 | 0 | 0 | 0.12235 | 4282.25 | 0 | 0 | 40000 | 0 | 4282.25 | 0 | 0 | 0 | 0 | 2130.55 | 0 | 0 | 2130.55
2022083007 | 3 | 0.61029 | 48823.2 | 0 | 0 | 0.11158 | 3905.3 | 0 | 0 | 40000 | 0 | 3905.3 | 0 | 0 | 0 | 0 | 4917.9 | 0 | 0 | 4917.9
2022083008 | 3 | 0.61648 | 49318.4 | 0 | 0 | 0.13121 | 4592.35 | 0.00852 | 119.28 | 40000 | 0 | 4592.35 | 0 | 119.28 | 0 | 0 | 4606.77 | 0 | 0 | 4606.77
2022083009 | 3 | 0.63012 | 50409.6 | 0 | 0 | 0.1256 | 4396 | 0.1314 | 1839.6 | 40000 | 0 | 4396 | 0 | 1839.6 | 0 | 0 | 4174 | 0 | 0 | 4174
2022083010 | 3 | 0.65495 | 52396 | 0 | 0 | 0.12694 | 4442.9 | 0.32352 | 4529.28 | 40000 | 0 | 4442.9 | 0 | 4529.28 | 0 | 0 | 3423.82 | 0 | 0 | 3423.82
2022083011 | 3 | 0.68551 | 54840.8 | 0 | 0 | 0.13138 | 4598.3 | 0.36139 | 5059.46 | 40000 | 0 | 4598.3 | 0 | 5059.46 | 0 | 0 | 5183.04 | 0 | 0 | 5183.04
2022083012 | 3 | 0.71061 | 56848.8 | 0 | 0 | 0.11956 | 4184.6 | 0.41949 | 5872.86 | 40000 | 0 | 4184.6 | 0 | 5872.86 | 0 | 0 | 6791.34 | 0 | 0 | 6791.34
2022083013 | 3 | 0.72939 | 58351.2 | 0 | 0 | 0.11477 | 4016.95 | 0.4396 | 6154.4 | 40000 | 0 | 4016.95 | 0 | 6154.4 | 0 | 0 | 8179.85 | 0 | 0 | 8179.85
2022083014 | 3 | 0.74732 | 59785.6 | 0 | 0 | 0.1204 | 4214 | 0.45379 | 6353.06 | 40000 | 0 | 4214 | 0 | 6353.06 | 0 | 0 | 9218.54 | 0 | 0 | 9218.54
2022083015 | 3 | 0.75295 | 60236 | 0 | 0 | 0.1213 | 4245.5 | 0.42665 | 5973.1 | 40000 | 0 | 4245.5 | 0 | 5973.1 | 0 | 0 | 10017.4 | 0 | 0 | 10017.4
2022083016 | 3 | 0.75163 | 60130.4 | 0 | 0 | 0.1455 | 5092.5 | 0.40941 | 5731.74 | 40000 | 0 | 5092.5 | 0 | 5731.74 | 0 | 0 | 9306.16 | 0 | 0 | 9306.16
2022083017 | 3 | 0.7459 | 59672 | 0 | 0 | 0.18068 | 6323.8 | 0.317 | 4438 | 40000 | 0 | 6323.8 | 0 | 4438 | 0 | 0 | 8910.2 | 0 | 0 | 8910.2
2022083018 | 3 | 0.73014 | 58411.2 | 0 | 0 | 0.16524 | 5783.4 | 0.23441 | 3281.74 | 40000 | 0 | 5783.4 | 0 | 3281.74 | 0 | 0 | 9346.06 | 0 | 0 | 9346.06
2022083019 | 3 | 0.70962 | 56769.6 | 0 | 0 | 0.15447 | 5406.45 | 0.13901 | 1946.14 | 40000 | 0 | 5406.45 | 0 | 1946.14 | 0 | 0 | 9417.01 | 0 | 0 | 9417.01
2022083020 | 3 | 0.69365 | 55492 | 0 | 0 | 0.12353 | 4323.55 | 0.04596 | 643.44 | 40000 | 0 | 4323.55 | 0 | 643.44 | 0 | 0 | 10525.01 | 0 | 0 | 10525.01
2022083021 | 3 | 0.69296 | 55436.8 | 0 | 0 | 0.10814 | 3784.9 | 0.00146 | 20.44 | 40000 | 0 | 3784.9 | 0 | 20.44 | 0 | 0 | 11631.46 | 0 | 0 | 11631.46
2022083022 | 3 | 0.67244 | 53795.2 | 0 | 0 | 0.08749 | 3062.15 | 0 | 0 | 40000 | 0 | 3062.15 | 0 | 0 | 0 | 0 | 10733.05 | 0 | 0 | 10733.05
2022083023 | 3 | 0.63671 | 50936.8 | 0 | 0 | 0.07858 | 2750.3 | 0 | 0 | 40000 | 0 | 2750.3 | 0 | 0 | 0 | 0 | 8186.5 | 0 | 0 | 8186.5
2022083024 | 3 | 0.59907 | 47925.6 | 0 | 0 | 0.07102 | 2485.7 | 0 | 0 | 40000 | 0 | 2485.7 | 0 | 0 | 0 | 0 | 5439.9 | 0 | 0 | 5439.9
2022083101 | 4 | 0.56972 | 45577.6 | 0 | 0 | 0.06357 | 2224.95 | 0 | 0 | 40000 | 0 | 2224.95 | 0 | 0 | 0 | 0 | 3352.65 | 0 | 0 | 3352.65
2022083102 | 4 | 0.54844 | 43875.2 | 0 | 0 | 0.0511 | 1788.5 | 0 | 0 | 40000 | 0 | 1788.5 | 0 | 0 | 0 | 0 | 2086.7 | 0 | 0 | 2086.7
2022083103 | 4 | 0.53587 | 42869.6 | 0 | 0 | 0.04904 | 1716.4 | 0 | 0 | 40000 | 0 | 1716.4 | 0 | 0 | 0 | 0 | 1153.2 | 0 | 0 | 1153.2
2022083104 | 4 | 0.52864 | 42291.2 | 0 | 0 | 0.04043 | 1415.05 | 0 | 0 | 40000 | 0 | 1415.05 | 0 | 0 | 0 | 0 | 876.15 | 0 | 0 | 876.15
2022083105 | 4 | 0.5332 | 42656 | 0 | 0 | 0.03022 | 1057.7 | 0 | 0 | 40000 | 0 | 1057.7 | 0 | 0 | 0 | 0 | 1598.3 | 0 | 0 | 1598.3
2022083106 | 4 | 0.55128 | 44102.4 | 0 | 0 | 0.02705 | 946.75 | 0 | 0 | 40000 | 0 | 946.75 | 0 | 0 | 0 | 0 | 3155.65 | 0 | 0 | 3155.65
2022083107 | 4 | 0.58132 | 46505.6 | 0 | 0 | 0.02933 | 1026.55 | 0 | 0 | 40000 | 0 | 1026.55 | 0 | 0 | 0 | 0 | 5479.05 | 0 | 0 | 5479.05
2022083108 | 4 | 0.5885 | 47080 | 0 | 0 | 0.03718 | 1301.3 | 0.01794 | 251.16 | 40000 | 0 | 1301.3 | 0 | 251.16 | 0 | 0 | 5527.54 | 0 | 0 | 5527.54
2022083109 | 4 | 0.604 | 48320 | 0 | 0 | 0.0358 | 1253 | 0.13787 | 1930.18 | 40000 | 0 | 1253 | 0 | 1930.18 | 0 | 0 | 5136.82 | 0 | 0 | 5136.82
2022083110 | 4 | 0.63492 | 50793.6 | 0 | 0 | 0.03122 | 1092.7 | 0.243 | 3402 | 40000 | 0 | 1092.7 | 0 | 3402 | 0 | 0 | 6298.9 | 0 | 0 | 6298.9
2022083111 | 4 | 0.67475 | 53980 | 0 | 0 | 0.0481 | 1683.5 | 0.31005 | 4340.7 | 40000 | 0 | 1683.5 | 0 | 4340.7 | 0 | 0 | 7955.8 | 0 | 0 | 7955.8
2022083112 | 4 | 0.71638 | 57310.4 | 0 | 0 | 0.07097 | 2483.95 | 0.35103 | 4914.42 | 40000 | 0 | 2483.95 | 0 | 4914.42 | 0 | 0 | 9912.03 | 0 | 0 | 9912.03
2022083113 | 4 | 0.75107 | 60085.6 | 0 | 0 | 0.08334 | 2916.9 | 0.38365 | 5371.1 | 40000 | 0 | 2916.9 | 0 | 5371.1 | 0 | 0 | 11797.6 | 0 | 0 | 11797.6
2022083114 | 4 | 0.78252 | 62601.6 | 0 | 0 | 0.10575 | 3701.25 | 0.40452 | 5663.28 | 40000 | 0 | 3701.25 | 0 | 5663.28 | 0 | 0 | 13237.07 | 0 | 0 | 13237.07
2022083115 | 4 | 0.80244 | 64195.2 | 0 | 0 | 0.08644 | 3025.4 | 0.43334 | 6066.76 | 40000 | 0 | 3025.4 | 0 | 6066.76 | 0 | 0 | 15103.04 | 0 | 0 | 15103.04
2022083116 | 4 | 0.80779 | 64623.2 | 0 | 0 | 0.10249 | 3587.15 | 0.3928 | 5499.2 | 40000 | 0 | 3587.15 | 0 | 5499.2 | 0 | 0 | 15536.85 | 0 | 0 | 15536.85
2022083117 | 4 | 0.79852 | 63881.6 | 0 | 0 | 0.11447 | 4006.45 | 0.30433 | 4260.62 | 40000 | 0 | 4006.45 | 0 | 4260.62 | 0 | 0 | 15614.53 | 0 | 0 | 15614.53
2022083118 | 4 | 0.783 | 62640 | 0 | 0 | 0.13116 | 4590.6 | 0.19836 | 2777.04 | 40000 | 0 | 4590.6 | 0 | 2777.04 | 0 | 0 | 15272.36 | 0 | 0 | 15272.36
2022083119 | 4 | 0.76059 | 60847.2 | 0 | 0 | 0.13439 | 4703.65 | 0.12331 | 1726.34 | 40000 | 0 | 4703.65 | 0 | 1726.34 | 0 | 0 | 14417.21 | 0 | 0 | 14417.21
2022083120 | 4 | 0.73867 | 59093.6 | 0 | 0 | 0.11386 | 3985.1 | 0.02825 | 395.5 | 40000 | 0 | 3985.1 | 0 | 395.5 | 0 | 0 | 14713 | 0 | 0 | 14713
2022083121 | 4 | 0.72489 | 57991.2 | 0 | 0 | 0.09351 | 3272.85 | 6e-05 | 0.84 | 40000 | 0 | 3272.85 | 0 | 0.84 | 0 | 0 | 14717.51 | 0 | 0 | 14717.51
2022083122 | 4 | 0.69549 | 55639.2 | 0 | 0 | 0.08958 | 3135.3 | 0 | 0 | 40000 | 0 | 3135.3 | 0 | 0 | 0 | 0 | 12503.9 | 0 | 0 | 12503.9
2022083123 | 4 | 0.65145 | 52116 | 0 | 0 | 0.0857 | 2999.5 | 0 | 0 | 40000 | 0 | 2999.5 | 0 | 0 | 0 | 0 | 9116.5 | 0 | 0 | 9116.5
2022083124 | 4 | 0.60617 | 48493.6 | 0 | 0 | 0.09177 | 3211.95 | 0 | 0 | 40000 | 0 | 3211.95 | 0 | 0 | 0 | 0 | 5281.65 | 0 | 0 | 5281.65
2022090101 | 5 | 0.57241 | 45792.8 | 0 | 0 | 0.10358 | 3625.3 | 0 | 0 | 40000 | 0 | 3625.3 | 0 | 0 | 0 | 0 | 2167.5 | 0 | 0 | 2167.5
2022090102 | 5 | 0.54933 | 43946.4 | 0 | 0 | 0.08552 | 2993.2 | 0 | 0 | 40000 | 0 | 2993.2 | 0 | 0 | 0 | 0 | 953.2 | 0 | 0 | 953.2
2022090103 | 5 | 0.53219 | 42575.2 | 0 | 0 | 0.06626 | 2319.1 | 0 | 0 | 40000 | 0 | 2319.1 | 0 | 0 | 0 | 0 | 256.1 | 0 | 0 | 256.1
2022090104 | 5 | 0.52351 | 41880.8 | 0 | 0 | 0.04325 | 1513.75 | 0 | 0 | 40000 | 0 | 1513.75 | 0 | 0 | 0 | 0 | 367.05 | 0 | 0 | 367.05
2022090105 | 5 | 0.5242 | 41936 | 0 | 0 | 0.02252 | 788.2 | 0 | 0 | 40000 | 0 | 788.2 | 0 | 0 | 0 | 0 | 1147.8 | 0 | 0 | 1147.8
2022090106 | 5 | 0.53788 | 43030.4 | 0 | 0 | 0.01499 | 524.65 | 0 | 0 | 40000 | 0 | 524.65 | 0 | 0 | 0 | 0 | 2505.75 | 0 | 0 | 2505.75
2022090107 | 5 | 0.56602 | 45281.6 | 0 | 0 | 0.01833 | 641.55 | 0 | 0 | 40000 | 0 | 641.55 | 0 | 0 | 0 | 0 | 4640.05 | 0 | 0 | 4640.05
2022090108 | 5 | 0.57728 | 46182.4 | 0 | 0 | 0.0195 | 682.5 | 0.02064 | 288.96 | 40000 | 0 | 682.5 | 0 | 288.96 | 0 | 0 | 5210.94 | 0 | 0 | 5210.94
2022090109 | 5 | 0.5971 | 47768 | 0 | 0 | 0.0204 | 714 | 0.12866 | 1801.24 | 40000 | 0 | 714 | 0 | 1801.24 | 0 | 0 | 5252.76 | 0 | 0 | 5252.76
2022090110 | 5 | 0.63031 | 50424.8 | 0 | 0 | 0.02983 | 1044.05 | 0.24889 | 3484.46 | 40000 | 0 | 1044.05 | 0 | 3484.46 | 0 | 0 | 5896.29 | 0 | 0 | 5896.29
2022090111 | 5 | 0.67294 | 53835.2 | 0 | 0 | 0.03913 | 1369.55 | 0.32349 | 4528.86 | 40000 | 0 | 1369.55 | 0 | 4528.86 | 0 | 0 | 7936.79 | 0 | 0 | 7936.79
2022090112 | 5 | 0.71319 | 57055.2 | 0 | 0 | 0.06256 | 2189.6 | 0.36737 | 5143.18 | 40000 | 0 | 2189.6 | 0 | 5143.18 | 0 | 0 | 9722.42 | 0 | 0 | 9722.42
2022090113 | 5 | 0.74338 | 59470.4 | 0 | 0 | 0.09083 | 3179.05 | 0.39577 | 5540.78 | 40000 | 0 | 3179.05 | 0 | 5540.78 | 0 | 0 | 10750.57 | 0 | 0 | 10750.57
2022090114 | 5 | 0.77074 | 61659.2 | 0 | 0 | 0.09746 | 3411.1 | 0.39828 | 5575.92 | 40000 | 0 | 3411.1 | 0 | 5575.92 | 0 | 0 | 12672.18 | 0 | 0 | 12672.18
2022090115 | 5 | 0.7759 | 62072 | 0 | 0 | 0.10174 | 3560.9 | 0.38288 | 5360.32 | 40000 | 0 | 3560.9 | 0 | 5360.32 | 0 | 0 | 13150.78 | 0 | 0 | 13150.78
2022090116 | 5 | 0.7634 | 61072 | 0 | 0 | 0.11976 | 4191.6 | 0.33414 | 4677.96 | 40000 | 0 | 4191.6 | 0 | 4677.96 | 0 | 0 | 12202.44 | 0 | 0 | 12202.44
2022090117 | 5 | 0.75448 | 60358.4 | 0 | 0 | 0.14717 | 5150.95 | 0.30917 | 4328.38 | 40000 | 0 | 5150.95 | 0 | 4328.38 | 0 | 0 | 10879.07 | 0 | 0 | 10879.07
2022090118 | 5 | 0.7534 | 60272 | 0 | 0 | 0.16741 | 5859.35 | 0.23315 | 3264.1 | 40000 | 0 | 5859.35 | 0 | 3264.1 | 0 | 0 | 11148.55 | 0 | 0 | 11148.55
2022090119 | 5 | 0.7405 | 59240 | 0 | 0 | 0.15774 | 5520.9 | 0.13824 | 1935.36 | 40000 | 0 | 5520.9 | 0 | 1935.36 | 0 | 0 | 11783.74 | 0 | 0 | 11783.74
2022090120 | 5 | 0.72442 | 57953.6 | 0 | 0 | 0.15244 | 5335.4 | 0.0233 | 326.2 | 40000 | 0 | 5335.4 | 0 | 326.2 | 0 | 0 | 12292 | 0 | 0 | 12292
2022090121 | 5 | 0.71592 | 57273.6 | 0 | 0 | 0.16176 | 5661.6 | 0.00048 | 6.72 | 40000 | 0 | 5661.6 | 0 | 6.72 | 0 | 0 | 11605.28 | 0 | 0 | 11605.28
2022090122 | 5 | 0.68905 | 55124 | 0 | 0 | 0.18873 | 6605.55 | 8e-05 | 1.12 | 40000 | 0 | 6605.55 | 0 | 1.12 | 0 | 0 | 8517.33 | 0 | 0 | 8517.33
2022090123 | 5 | 0.64728 | 51782.4 | 0 | 0 | 0.17946 | 6281.1 | 8e-05 | 1.12 | 40000 | 0 | 6281.1 | 0 | 1.12 | 0 | 0 | 5500.18 | 0 | 0 | 5500.18
2022090124 | 5 | 0.60415 | 48332 | 0 | 0 | 0.17254 | 6038.9 | 9e-05 | 1.26 | 40000 | 0 | 6038.9 | 0 | 1.26 | 0 | 0 | 2291.84 | 0 | 0 | 2291.84
2022090201 | 6 | 0.57071 | 45656.8 | 0 | 0 | 0.16681 | 5838.35 | 9e-05 | 1.26 | 40000 | 0 | 5656.8 | 181.55 | 0 | 1.26 | 182.81 | 0 | 0 | 0 | 0
2022090202 | 6 | 0.54444 | 43555.2 | 0 | 0 | 0.17587 | 6155.45 | 0 | 0 | 40000 | 0 | 3555.2 | 2600.25 | 0 | 0 | 2600.25 | 0 | 0 | 0 | 0
2022090203 | 6 | 0.52792 | 42233.6 | 0 | 0 | 0.17452 | 6108.2 | 0 | 0 | 40000 | 0 | 2233.6 | 3874.6 | 0 | 0 | 3874.6 | 0 | 0 | 0 | 0
2022090204 | 6 | 0.51906 | 41524.8 | 0 | 0 | 0.16978 | 5942.3 | 0 | 0 | 40000 | 0 | 1524.8 | 4417.5 | 0 | 0 | 4417.5 | 0 | 0 | 0 | 0
2022090205 | 6 | 0.51925 | 41540 | 0 | 0 | 0.16124 | 5643.4 | 0 | 0 | 40000 | 0 | 1540 | 4103.4 | 0 | 0 | 4103.4 | 0 | 0 | 0 | 0
2022090206 | 6 | 0.53804 | 43043.2 | 0 | 0 | 0.1463 | 5120.5 | 0 | 0 | 40000 | 0 | 3043.2 | 2077.3 | 0 | 0 | 2077.3 | 0 | 0 | 0 | 0
2022090207 | 6 | 0.5632 | 45056 | 0 | 0 | 0.13905 | 4866.75 | 0 | 0 | 40000 | 0 | 4866.75 | 0 | 0 | 0 | 0 | 189.25 | 0 | 0 | 189.25
2022090208 | 6 | 0.57257 | 45805.6 | 0 | 0 | 0.1259 | 4406.5 | 0.01622 | 227.08 | 40000 | 0 | 4406.5 | 0 | 227.08 | 0 | 0 | 1172.02 | 0 | 0 | 1172.02
2022090209 | 6 | 0.58875 | 47100 | 0 | 0 | 0.08938 | 3128.3 | 0.15928 | 2229.92 | 40000 | 0 | 3128.3 | 0 | 2229.92 | 0 | 0 | 1741.78 | 0 | 0 | 1741.78
2022090210 | 6 | 0.61998 | 49598.4 | 0 | 0 | 0.05943 | 2080.05 | 0.30083 | 4211.62 | 40000 | 0 | 2080.05 | 0 | 4211.62 | 0 | 0 | 3306.73 | 0 | 0 | 3306.73
2022090211 | 6 | 0.65695 | 52556 | 0 | 0 | 0.06947 | 2431.45 | 0.37473 | 5246.22 | 40000 | 0 | 2431.45 | 0 | 5246.22 | 0 | 0 | 4878.33 | 0 | 0 | 4878.33
2022090212 | 6 | 0.69186 | 55348.8 | 0 | 0 | 0.08276 | 2896.6 | 0.47101 | 6594.14 | 40000 | 0 | 2896.6 | 0 | 6594.14 | 0 | 0 | 5858.06 | 0 | 0 | 5858.06
2022090213 | 6 | 0.72565 | 58052 | 0 | 0 | 0.07727 | 2704.45 | 0.57175 | 8004.5 | 40000 | 0 | 2704.45 | 0 | 8004.5 | 0 | 0 | 7343.05 | 0 | 0 | 7343.05
2022090214 | 6 | 0.75444 | 60355.2 | 0 | 0 | 0.08517 | 2980.95 | 0.57236 | 8013.04 | 40000 | 0 | 2980.95 | 0 | 8013.04 | 0 | 0 | 9361.21 | 0 | 0 | 9361.21
2022090215 | 6 | 0.7686 | 61488 | 0 | 0 | 0.08849 | 3097.15 | 0.51958 | 7274.12 | 40000 | 0 | 3097.15 | 0 | 7274.12 | 0 | 0 | 11116.73 | 0 | 0 | 11116.73
2022090216 | 6 | 0.76711 | 61368.8 | 0 | 0 | 0.09722 | 3402.7 | 0.41499 | 5809.86 | 40000 | 0 | 3402.7 | 0 | 5809.86 | 0 | 0 | 12156.24 | 0 | 0 | 12156.24
2022090217 | 6 | 0.76537 | 61229.6 | 0 | 0 | 0.13116 | 4590.6 | 0.37047 | 5186.58 | 40000 | 0 | 4590.6 | 0 | 5186.58 | 0 | 0 | 11452.42 | 0 | 0 | 11452.42
2022090218 | 6 | 0.7639 | 61112 | 0 | 0 | 0.17024 | 5958.4 | 0.36006 | 5040.84 | 40000 | 0 | 5958.4 | 0 | 5040.84 | 0 | 0 | 10112.76 | 0 | 0 | 10112.76
2022090219 | 6 | 0.74753 | 59802.4 | 0 | 0 | 0.20518 | 7181.3 | 0.22193 | 3107.02 | 40000 | 0 | 7181.3 | 0 | 3107.02 | 0 | 0 | 9514.08 | 0 | 0 | 9514.08
2022090220 | 6 | 0.72287 | 57829.6 | 0 | 0 | 0.20117 | 7040.95 | 0.04235 | 592.9 | 40000 | 0 | 7040.95 | 0 | 592.9 | 0 | 0 | 10195.75 | 0 | 0 | 10195.75
2022090221 | 6 | 0.70564 | 56451.2 | 0 | 0 | 0.19437 | 6802.95 | 0.0004 | 5.6 | 40000 | 0 | 6802.95 | 0 | 5.6 | 0 | 0 | 9642.65 | 0 | 0 | 9642.65
2022090222 | 6 | 0.67963 | 54370.4 | 0 | 0 | 0.2039 | 7136.5 | 0 | 0 | 40000 | 0 | 7136.5 | 0 | 0 | 0 | 0 | 7233.9 | 0 | 0 | 7233.9
2022090223 | 6 | 0.64757 | 51805.6 | 0 | 0 | 0.20709 | 7248.15 | 0 | 0 | 40000 | 0 | 7248.15 | 0 | 0 | 0 | 0 | 4557.45 | 0 | 0 | 4557.45
2022090224 | 6 | 0.61072 | 48857.6 | 0 | 0 | 0.21486 | 7520.1 | 0 | 0 | 40000 | 0 | 7520.1 | 0 | 0 | 0 | 0 | 1337.5 | 0 | 0 | 1337.5
2022090301 | 7 | 0.57815 | 46252 | 0 | 0 | 0.17861 | 6251.35 | 0 | 0 | 40000 | 0 | 6251.35 | 0 | 0 | 0 | 0 | 0.65 | 0 | 0 | 0.65
2022090302 | 7 | 0.55395 | 44316 | 0 | 0 | 0.13891 | 4861.85 | 0 | 0 | 40000 | 0 | 4316 | 545.85 | 0 | 0 | 545.85 | 0 | 0 | 0 | 0
2022090303 | 7 | 0.53501 | 42800.8 | 0 | 0 | 0.12485 | 4369.75 | 0 | 0 | 40000 | 0 | 2800.8 | 1568.95 | 0 | 0 | 1568.95 | 0 | 0 | 0 | 0
2022090304 | 7 | 0.52344 | 41875.2 | 0 | 0 | 0.09762 | 3416.7 | 0 | 0 | 40000 | 0 | 1875.2 | 1541.5 | 0 | 0 | 1541.5 | 0 | 0 | 0 | 0
2022090305 | 7 | 0.51869 | 41495.2 | 0 | 0 | 0.06795 | 2378.25 | 0 | 0 | 40000 | 0 | 1495.2 | 883.05 | 0 | 0 | 883.05 | 0 | 0 | 0 | 0
2022090306 | 7 | 0.51648 | 41318.4 | 0 | 0 | 0.05843 | 2045.05 | 0 | 0 | 40000 | 0 | 1318.4 | 726.65 | 0 | 0 | 726.65 | 0 | 0 | 0 | 0
2022090307 | 7 | 0.52061 | 41648.8 | 0 | 0 | 0.0597 | 2089.5 | 0 | 0 | 40000 | 0 | 1648.8 | 440.7 | 0 | 0 | 440.7 | 0 | 0 | 0 | 0
2022090308 | 7 | 0.52644 | 42115.2 | 0 | 0 | 0.05546 | 1941.1 | 0.01921 | 268.94 | 40000 | 0 | 1941.1 | 0 | 174.1 | 94.84 | 94.84 | 0 | 0 | 0 | 0
2022090309 | 7 | 0.55653 | 44522.4 | 0 | 0 | 0.0629 | 2201.5 | 0.19244 | 2694.16 | 40000 | 0 | 2201.5 | 0 | 2320.9 | 373.26 | 373.26 | 0 | 0 | 0 | 0
2022090310 | 7 | 0.59524 | 47619.2 | 0 | 0 | 0.04876 | 1706.6 | 0.39507 | 5530.98 | 40000 | 0 | 1706.6 | 0 | 5530.98 | 0 | 0 | 381.62 | 0 | 0 | 381.62
2022090311 | 7 | 0.64232 | 51385.6 | 0 | 0 | 0.0542 | 1897 | 0.5099 | 7138.6 | 40000 | 0 | 1897 | 0 | 7138.6 | 0 | 0 | 2350 | 0 | 0 | 2350
2022090312 | 7 | 0.68624 | 54899.2 | 0 | 0 | 0.05826 | 2039.1 | 0.63373 | 8872.22 | 40000 | 0 | 2039.1 | 0 | 8872.22 | 0 | 0 | 3987.88 | 0 | 0 | 3987.88
2022090313 | 7 | 0.71966 | 57572.8 | 0 | 0 | 0.06148 | 2151.8 | 0.63094 | 8833.16 | 40000 | 0 | 2151.8 | 0 | 8833.16 | 0 | 0 | 6587.84 | 0 | 0 | 6587.84
2022090314 | 7 | 0.74486 | 59588.8 | 0 | 0 | 0.07975 | 2791.25 | 0.62519 | 8752.66 | 40000 | 0 | 2791.25 | 0 | 8752.66 | 0 | 0 | 8044.89 | 0 | 0 | 8044.89
2022090315 | 7 | 0.75481 | 60384.8 | 0 | 0 | 0.09757 | 3414.95 | 0.59751 | 8365.14 | 40000 | 0 | 3414.95 | 0 | 8365.14 | 0 | 0 | 8604.71 | 0 | 0 | 8604.71
2022090316 | 7 | 0.75721 | 60576.8 | 0 | 0 | 0.10724 | 3753.4 | 0.5546 | 7764.4 | 40000 | 0 | 3753.4 | 0 | 7764.4 | 0 | 0 | 9059 | 0 | 0 | 9059
2022090317 | 7 | 0.75072 | 60057.6 | 0 | 0 | 0.11309 | 3958.15 | 0.50095 | 7013.3 | 40000 | 0 | 3958.15 | 0 | 7013.3 | 0 | 0 | 9086.15 | 0 | 0 | 9086.15
2022090318 | 7 | 0.72873 | 58298.4 | 0 | 0 | 0.1199 | 4196.5 | 0.41002 | 5740.28 | 40000 | 0 | 4196.5 | 0 | 5740.28 | 0 | 0 | 8361.62 | 0 | 0 | 8361.62
2022090319 | 7 | 0.69989 | 55991.2 | 0 | 0 | 0.11827 | 4139.45 | 0.26288 | 3680.32 | 40000 | 0 | 4139.45 | 0 | 3680.32 | 0 | 0 | 8171.43 | 0 | 0 | 8171.43
2022090320 | 7 | 0.67787 | 54229.6 | 0 | 0 | 0.08251 | 2887.85 | 0.06515 | 912.1 | 40000 | 0 | 2887.85 | 0 | 912.1 | 0 | 0 | 10429.65 | 0 | 0 | 10429.65
2022090321 | 7 | 0.6617 | 52936 | 0 | 0 | 0.07366 | 2578.1 | 0.00014 | 1.96 | 40000 | 0 | 2578.1 | 0 | 1.96 | 0 | 0 | 10355.94 | 0 | 0 | 10355.94
2022090322 | 7 | 0.63938 | 51150.4 | 0 | 0 | 0.09239 | 3233.65 | 0 | 0 | 40000 | 0 | 3233.65 | 0 | 0 | 0 | 0 | 7916.75 | 0 | 0 | 7916.75
2022090323 | 7 | 0.6097 | 48776 | 0 | 0 | 0.10117 | 3540.95 | 0 | 0 | 40000 | 0 | 3540.95 | 0 | 0 | 0 | 0 | 5235.05 | 0 | 0 | 5235.05
2022090324 | 7 | 0.57712 | 46169.6 | 0 | 0 | 0.09756 | 3414.6 | 0 | 0 | 40000 | 0 | 3414.6 | 0 | 0 | 0 | 0 | 2755 | 0 | 0 | 2755
2022090401 | 1 | 0.54685 | 43748 | 0 | 0 | 0.10442 | 3654.7 | 0 | 0 | 40000 | 0 | 3654.7 | 0 | 0 | 0 | 0 | 93.3 | 0 | 0 | 93.3
2022090402 | 1 | 0.52442 | 41953.6 | 0 | 0 | 0.11682 | 4088.7 | 0 | 0 | 40000 | 0 | 1953.6 | 2135.1 | 0 | 0 | 2135.1 | 0 | 0 | 0 | 0
2022090403 | 1 | 0.50641 | 40512.8 | 0 | 0 | 0.13725 | 4803.75 | 0 | 0 | 40000 | 0 | 512.8 | 4290.95 | 0 | 0 | 4290.95 | 0 | 0 | 0 | 0
2022090404 | 1 | 0.49385 | 39508 | 0 | 0 | 0.1222 | 4277 | 0 | 0 | 39508 | 492 | 0 | 4277 | 0 | 0 | 4769 | 0 | 0 | 0 | 0
2022090405 | 1 | 0.487 | 38960 | 0 | 0 | 0.09141 | 3199.35 | 0 | 0 | 38960 | 1040 | 0 | 3199.35 | 0 | 0 | 4239.35 | 0 | 0 | 0 | 0
2022090406 | 1 | 0.48655 | 38924 | 0 | 0 | 0.0833 | 2915.5 | 0 | 0 | 38924 | 1076 | 0 | 2915.5 | 0 | 0 | 3991.5 | 0 | 0 | 0 | 0
2022090407 | 1 | 0.48841 | 39072.8 | 0 | 0 | 0.08424 | 2948.4 | 0 | 0 | 39072.8 | 927.2 | 0 | 2948.4 | 0 | 0 | 3875.6 | 0 | 0 | 0 | 0
2022090408 | 1 | 0.49187 | 39349.6 | 0 | 0 | 0.08099 | 2834.65 | 0.02452 | 343.28 | 39349.6 | 650.4 | 0 | 2834.65 | 0 | 343.28 | 3828.33 | 0 | 0 | 0 | 0
2022090409 | 1 | 0.51427 | 41141.6 | 0 | 0 | 0.05799 | 2029.65 | 0.30457 | 4263.98 | 40000 | 0 | 1141.6 | 888.05 | 0 | 4263.98 | 5152.03 | 0 | 0 | 0 | 0
2022090410 | 1 | 0.5509 | 44072 | 0 | 0 | 0.02739 | 958.65 | 0.57071 | 7989.94 | 40000 | 0 | 958.65 | 0 | 3113.35 | 4876.59 | 4876.59 | 0 | 0 | 0 | 0
2022090411 | 1 | 0.58917 | 47133.6 | 0 | 0 | 0.0168 | 588 | 0.64973 | 9096.22 | 40000 | 0 | 588 | 0 | 6545.6 | 2550.62 | 2550.62 | 0 | 0 | 0 | 0
2022090412 | 1 | 0.62912 | 50329.6 | 0 | 0 | 0.01583 | 554.05 | 0.67847 | 9498.58 | 40000 | 0 | 554.05 | 0 | 9498.58 | 0 | 0 | 276.97 | 0 | 0 | 276.97
2022090413 | 1 | 0.67096 | 53676.8 | 0 | 0 | 0.02619 | 916.65 | 0.64468 | 9025.52 | 40000 | 0 | 916.65 | 0 | 9025.52 | 0 | 0 | 3734.63 | 0 | 0 | 3734.63
2022090414 | 1 | 0.70287 | 56229.6 | 0 | 0 | 0.03361 | 1176.35 | 0.62627 | 8767.78 | 40000 | 0 | 1176.35 | 0 | 8767.78 | 0 | 0 | 6285.47 | 0 | 0 | 6285.47
2022090415 | 1 | 0.71687 | 57349.6 | 0 | 0 | 0.03736 | 1307.6 | 0.5974 | 8363.6 | 40000 | 0 | 1307.6 | 0 | 8363.6 | 0 | 0 | 7678.4 | 0 | 0 | 7678.4
2022090416 | 1 | 0.69652 | 55721.6 | 0 | 0 | 0.062 | 2170 | 0.59058 | 8268.12 | 40000 | 0 | 2170 | 0 | 8268.12 | 0 | 0 | 5283.48 | 0 | 0 | 5283.48
2022090417 | 1 | 0.68182 | 54545.6 | 0 | 0 | 0.07816 | 2735.6 | 0.52055 | 7287.7 | 40000 | 0 | 2735.6 | 0 | 7287.7 | 0 | 0 | 4522.3 | 0 | 0 | 4522.3
2022090418 | 1 | 0.6727 | 53816 | 0 | 0 | 0.11215 | 3925.25 | 0.47481 | 6647.34 | 40000 | 0 | 3925.25 | 0 | 6647.34 | 0 | 0 | 3243.41 | 0 | 0 | 3243.41
2022090419 | 1 | 0.65652 | 52521.6 | 0 | 0 | 0.15639 | 5473.65 | 0.34551 | 4837.14 | 40000 | 0 | 5473.65 | 0 | 4837.14 | 0 | 0 | 2210.81 | 0 | 0 | 2210.81
2022090420 | 1 | 0.64251 | 51400.8 | 0 | 0 | 0.16682 | 5838.7 | 0.08824 | 1235.36 | 40000 | 0 | 5838.7 | 0 | 1235.36 | 0 | 0 | 4326.74 | 0 | 0 | 4326.74
2022090421 | 1 | 0.63194 | 50555.2 | 0 | 0 | 0.18213 | 6374.55 | 0.00031 | 4.34 | 40000 | 0 | 6374.55 | 0 | 4.34 | 0 | 0 | 4176.31 | 0 | 0 | 4176.31
2022090422 | 1 | 0.61047 | 48837.6 | 0 | 0 | 0.16667 | 5833.45 | 0 | 0 | 40000 | 0 | 5833.45 | 0 | 0 | 0 | 0 | 3004.15 | 0 | 0 | 3004.15
2022090423 | 1 | 0.58326 | 46660.8 | 0 | 0 | 0.18074 | 6325.9 | 0 | 0 | 40000 | 0 | 6325.9 | 0 | 0 | 0 | 0 | 334.9 | 0 | 0 | 334.9
2022090424 | 1 | 0.55194 | 44155.2 | 0 | 0 | 0.22706 | 7947.1 | 0 | 0 | 40000 | 0 | 4155.2 | 3791.9 | 0 | 0 | 3791.9 | 0 | 0 | 0 | 0
2022090501 | 2 | 0.52357 | 41885.6 | 0 | 0 | 0.2541 | 8893.5 | 0 | 0 | 40000 | 0 | 1885.6 | 7007.9 | 0 | 0 | 7007.9 | 0 | 0 | 0 | 0
2022090502 | 2 | 0.50117 | 40093.6 | 0 | 0 | 0.24512 | 8579.2 | 0 | 0 | 40000 | 0 | 93.6 | 8485.6 | 0 | 0 | 8485.6 | 0 | 0 | 0 | 0
2022090503 | 2 | 0.48515 | 38812 | 0 | 0 | 0.23799 | 8329.65 | 0 | 0 | 38812 | 1188 | 0 | 8329.65 | 0 | 0 | 9517.65 | 0 | 0 | 0 | 0
2022090504 | 2 | 0.47564 | 38051.2 | 0 | 0 | 0.22438 | 7853.3 | 0 | 0 | 38051.2 | 1948.8 | 0 | 7853.3 | 0 | 0 | 9802.1 | 0 | 0 | 0 | 0
2022090505 | 2 | 0.47364 | 37891.2 | 0 | 0 | 0.20465 | 7162.75 | 0 | 0 | 37891.2 | 2108.8 | 0 | 7162.75 | 0 | 0 | 9271.55 | 0 | 0 | 0 | 0
2022090506 | 2 | 0.48005 | 38404 | 0 | 0 | 0.18578 | 6502.3 | 0 | 0 | 38404 | 1596 | 0 | 6502.3 | 0 | 0 | 8098.3 | 0 | 0 | 0 | 0
2022090507 | 2 | 0.48285 | 38628 | 0 | 0 | 0.16475 | 5766.25 | 0 | 0 | 38628 | 1372 | 0 | 5766.25 | 0 | 0 | 7138.25 | 0 | 0 | 0 | 0
2022090508 | 2 | 0.48286 | 38628.8 | 0 | 0 | 0.13589 | 4756.15 | 0.02346 | 328.44 | 38628.8 | 1371.2 | 0 | 4756.15 | 0 | 328.44 | 6455.79 | 0 | 0 | 0 | 0
2022090509 | 2 | 0.50327 | 40261.6 | 0 | 0 | 0.10549 | 3692.15 | 0.30458 | 4264.12 | 40000 | 0 | 261.6 | 3430.55 | 0 | 4264.12 | 7694.67 | 0 | 0 | 0 | 0
2022090510 | 2 | 0.54072 | 43257.6 | 0 | 0 | 0.05155 | 1804.25 | 0.58302 | 8162.28 | 40000 | 0 | 1804.25 | 0 | 1453.35 | 6708.93 | 6708.93 | 0 | 0 | 0 | 0
2022090511 | 2 | 0.58345 | 46676 | 0 | 0 | 0.05124 | 1793.4 | 0.67375 | 9432.5 | 40000 | 0 | 1793.4 | 0 | 4882.6 | 4549.9 | 4549.9 | 0 | 0 | 0 | 0
2022090512 | 2 | 0.62773 | 50218.4 | 0 | 0 | 0.04522 | 1582.7 | 0.7007 | 9809.8 | 40000 | 0 | 1582.7 | 0 | 8635.7 | 1174.1 | 1174.1 | 0 | 0 | 0 | 0
2022090513 | 2 | 0.67348 | 53878.4 | 0 | 0 | 0.03538 | 1238.3 | 0.7011 | 9815.4 | 40000 | 0 | 1238.3 | 0 | 9815.4 | 0 | 0 | 2824.7 | 0 | 0 | 2824.7
2022090514 | 2 | 0.71446 | 57156.8 | 0 | 0 | 0.03622 | 1267.7 | 0.70092 | 9812.88 | 40000 | 0 | 1267.7 | 0 | 9812.88 | 0 | 0 | 6076.22 | 0 | 0 | 6076.22
2022090515 | 2 | 0.74785 | 59828 | 0 | 0 | 0.04235 | 1482.25 | 0.67485 | 9447.9 | 40000 | 0 | 1482.25 | 0 | 9447.9 | 0 | 0 | 8897.85 | 0 | 0 | 8897.85
2022090516 | 2 | 0.77185 | 61748 | 0 | 0 | 0.07319 | 2561.65 | 0.64458 | 9024.12 | 40000 | 0 | 2561.65 | 0 | 9024.12 | 0 | 0 | 10162.23 | 0 | 0 | 10162.23
2022090517 | 2 | 0.7863 | 62904 | 0 | 0 | 0.1091 | 3818.5 | 0.56929 | 7970.06 | 40000 | 0 | 3818.5 | 0 | 7970.06 | 0 | 0 | 11115.44 | 0 | 0 | 11115.44
2022090518 | 2 | 0.78764 | 63011.2 | 0 | 0 | 0.12083 | 4229.05 | 0.56247 | 7874.58 | 40000 | 0 | 4229.05 | 0 | 7874.58 | 0 | 0 | 10907.57 | 0 | 0 | 10907.57
2022090519 | 2 | 0.77215 | 61772 | 0 | 0 | 0.14097 | 4933.95 | 0.40882 | 5723.48 | 40000 | 0 | 4933.95 | 0 | 5723.48 | 0 | 0 | 11114.57 | 0 | 0 | 11114.57
2022090520 | 2 | 0.74169 | 59335.2 | 0 | 0 | 0.14602 | 5110.7 | 0.09706 | 1358.84 | 40000 | 0 | 5110.7 | 0 | 1358.84 | 0 | 0 | 12865.66 | 0 | 0 | 12865.66
2022090521 | 2 | 0.72035 | 57628 | 0 | 0 | 0.17155 | 6004.25 | 0.00028 | 3.92 | 40000 | 0 | 6004.25 | 0 | 3.92 | 0 | 0 | 11619.83 | 0 | 0 | 11619.83
2022090522 | 2 | 0.68678 | 54942.4 | 0 | 0 | 0.1934 | 6769 | 0 | 0 | 40000 | 0 | 6769 | 0 | 0 | 0 | 0 | 8173.4 | 0 | 0 | 8173.4
2022090523 | 2 | 0.63735 | 50988 | 0 | 0 | 0.22151 | 7752.85 | 0 | 0 | 40000 | 0 | 7752.85 | 0 | 0 | 0 | 0 | 3235.15 | 0 | 0 | 3235.15
2022090524 | 2 | 0.58989 | 47191.2 | 0 | 0 | 0.23318 | 8161.3 | 0 | 0 | 40000 | 0 | 7191.2 | 970.1 | 0 | 0 | 970.1 | 0 | 0 | 0 | 0
2022090601 | 3 | 0.55235 | 44188 | 0 | 0 | 0.23282 | 8148.7 | 0 | 0 | 40000 | 0 | 4188 | 3960.7 | 0 | 0 | 3960.7 | 0 | 0 | 0 | 0
2022090602 | 3 | 0.52735 | 42188 | 0 | 0 | 0.21604 | 7561.4 | 0 | 0 | 40000 | 0 | 2188 | 5373.4 | 0 | 0 | 5373.4 | 0 | 0 | 0 | 0
2022090603 | 3 | 0.51043 | 40834.4 | 0 | 0 | 0.22174 | 7760.9 | 0 | 0 | 40000 | 0 | 834.4 | 6926.5 | 0 | 0 | 6926.5 | 0 | 0 | 0 | 0
2022090604 | 3 | 0.50239 | 40191.2 | 0 | 0 | 0.20055 | 7019.25 | 0 | 0 | 40000 | 0 | 191.2 | 6828.05 | 0 | 0 | 6828.05 | 0 | 0 | 0 | 0
2022090605 | 3 | 0.50454 | 40363.2 | 0 | 0 | 0.18249 | 6387.15 | 0 | 0 | 40000 | 0 | 363.2 | 6023.95 | 0 | 0 | 6023.95 | 0 | 0 | 0 | 0
2022090606 | 3 | 0.52291 | 41832.8 | 0 | 0 | 0.16083 | 5629.05 | 0 | 0 | 40000 | 0 | 1832.8 | 3796.25 | 0 | 0 | 3796.25 | 0 | 0 | 0 | 0
2022090607 | 3 | 0.54994 | 43995.2 | 0 | 0 | 0.15141 | 5299.35 | 0 | 0 | 40000 | 0 | 3995.2 | 1304.15 | 0 | 0 | 1304.15 | 0 | 0 | 0 | 0
2022090608 | 3 | 0.56111 | 44888.8 | 0 | 0 | 0.13244 | 4635.4 | 0.02727 | 381.78 | 40000 | 0 | 4635.4 | 0 | 253.4 | 128.38 | 128.38 | 0 | 0 | 0 | 0
2022090609 | 3 | 0.58165 | 46532 | 0 | 0 | 0.09477 | 3316.95 | 0.34884 | 4883.76 | 40000 | 0 | 3316.95 | 0 | 3215.05 | 1668.71 | 1668.71 | 0 | 0 | 0 | 0
2022090610 | 3 | 0.61644 | 49315.2 | 0 | 0 | 0.05462 | 1911.7 | 0.62698 | 8777.72 | 40000 | 0 | 1911.7 | 0 | 7403.5 | 1374.22 | 1374.22 | 0 | 0 | 0 | 0
2022090611 | 3 | 0.65648 | 52518.4 | 0 | 0 | 0.04615 | 1615.25 | 0.67039 | 9385.46 | 40000 | 0 | 1615.25 | 0 | 9385.46 | 0 | 0 | 1517.69 | 0 | 0 | 1517.69
2022090612 | 3 | 0.70003 | 56002.4 | 0 | 0 | 0.03692 | 1292.2 | 0.6917 | 9683.8 | 40000 | 0 | 1292.2 | 0 | 9683.8 | 0 | 0 | 5026.4 | 0 | 0 | 5026.4
2022090613 | 3 | 0.74754 | 59803.2 | 0 | 0 | 0.02768 | 968.8 | 0.71918 | 10068.52 | 40000 | 0 | 968.8 | 0 | 10068.52 | 0 | 0 | 8765.88 | 0 | 0 | 8765.88
2022090614 | 3 | 0.78768 | 63014.4 | 0 | 0 | 0.02606 | 912.1 | 0.71616 | 10026.24 | 40000 | 0 | 912.1 | 0 | 10026.24 | 0 | 0 | 12076.06 | 0 | 0 | 12076.06
2022090615 | 3 | 0.81583 | 65266.4 | 0 | 0 | 0.04401 | 1540.35 | 0.68886 | 9644.04 | 40000 | 0 | 1540.35 | 0 | 9644.04 | 0 | 0 | 14082.01 | 0 | 0 | 14082.01
2022090616 | 3 | 0.8292 | 66336 | 0 | 0 | 0.06061 | 2121.35 | 0.66021 | 9242.94 | 40000 | 0 | 2121.35 | 0 | 9242.94 | 0 | 0 | 14971.71 | 0 | 0 | 14971.71
2022090617 | 3 | 0.83625 | 66900 | 0 | 0 | 0.07245 | 2535.75 | 0.65068 | 9109.52 | 40000 | 0 | 2535.75 | 0 | 9109.52 | 0 | 0 | 15254.73 | 0 | 0 | 15254.73
2022090618 | 3 | 0.83361 | 66688.8 | 0 | 0 | 0.09184 | 3214.4 | 0.59056 | 8267.84 | 40000 | 0 | 3214.4 | 0 | 8267.84 | 0 | 0 | 15206.56 | 0 | 0 | 15206.56
2022090619 | 3 | 0.81641 | 65312.8 | 0 | 0 | 0.10331 | 3615.85 | 0.38952 | 5453.28 | 40000 | 0 | 3615.85 | 0 | 5453.28 | 0 | 0 | 16243.67 | 0 | 0 | 16243.67
2022090620 | 3 | 0.78146 | 62516.8 | 0 | 0 | 0.10556 | 3694.6 | 0.08495 | 1189.3 | 40000 | 0 | 3694.6 | 0 | 1189.3 | 0 | 0 | 17632.9 | 0 | 0 | 17632.9
2022090621 | 3 | 0.76347 | 61077.6 | 0 | 0 | 0.12343 | 4320.05 | 0.00016 | 2.24 | 40000 | 0 | 4320.05 | 0 | 2.24 | 0 | 0 | 16755.31 | 0 | 0 | 16755.31
2022090622 | 3 | 0.72862 | 58289.6 | 0 | 0 | 0.15352 | 5373.2 | 0 | 0 | 40000 | 0 | 5373.2 | 0 | 0 | 0 | 0 | 12916.4 | 0 | 0 | 12916.4
2022090623 | 3 | 0.67836 | 54268.8 | 0 | 0 | 0.1898 | 6643 | 0 | 0 | 40000 | 0 | 6643 | 0 | 0 | 0 | 0 | 7625.8 | 0 | 0 | 7625.8
2022090624 | 3 | 0.62634 | 50107.2 | 0 | 0 | 0.182 | 6370 | 0 | 0 | 40000 | 0 | 6370 | 0 | 0 | 0 | 0 | 3737.2 | 0 | 0 | 3737.2
2022090701 | 4 | 0.58441 | 46752.8 | 0 | 0 | 0.16465 | 5762.75 | 0 | 0 | 40000 | 0 | 5762.75 | 0 | 0 | 0 | 0 | 990.05 | 0 | 0 | 990.05
2022090702 | 4 | 0.55638 | 44510.4 | 0 | 0 | 0.15133 | 5296.55 | 0 | 0 | 40000 | 0 | 4510.4 | 786.15 | 0 | 0 | 786.15 | 0 | 0 | 0 | 0
2022090703 | 4 | 0.53786 | 43028.8 | 0 | 0 | 0.11822 | 4137.7 | 0 | 0 | 40000 | 0 | 3028.8 | 1108.9 | 0 | 0 | 1108.9 | 0 | 0 | 0 | 0
2022090704 | 4 | 0.52678 | 42142.4 | 0 | 0 | 0.09112 | 3189.2 | 0 | 0 | 40000 | 0 | 2142.4 | 1046.8 | 0 | 0 | 1046.8 | 0 | 0 | 0 | 0
2022090705 | 4 | 0.52491 | 41992.8 | 0 | 0 | 0.07893 | 2762.55 | 0 | 0 | 40000 | 0 | 1992.8 | 769.75 | 0 | 0 | 769.75 | 0 | 0 | 0 | 0
2022090706 | 4 | 0.54023 | 43218.4 | 0 | 0 | 0.07096 | 2483.6 | 0 | 0 | 40000 | 0 | 2483.6 | 0 | 0 | 0 | 0 | 734.8 | 0 | 0 | 734.8
2022090707 | 4 | 0.56446 | 45156.8 | 0 | 0 | 0.07197 | 2518.95 | 0 | 0 | 40000 | 0 | 2518.95 | 0 | 0 | 0 | 0 | 2637.85 | 0 | 0 | 2637.85
2022090708 | 4 | 0.57162 | 45729.6 | 0 | 0 | 0.0779 | 2726.5 | 0.0261 | 365.4 | 40000 | 0 | 2726.5 | 0 | 365.4 | 0 | 0 | 2637.7 | 0 | 0 | 2637.7
2022090709 | 4 | 0.58866 | 47092.8 | 0 | 0 | 0.07012 | 2454.2 | 0.31184 | 4365.76 | 40000 | 0 | 2454.2 | 0 | 4365.76 | 0 | 0 | 272.84 | 0 | 0 | 272.84
2022090710 | 4 | 0.62476 | 49980.8 | 0 | 0 | 0.0396 | 1386 | 0.61855 | 8659.7 | 40000 | 0 | 1386 | 0 | 8594.8 | 64.9 | 64.9 | 0 | 0 | 0 | 0
2022090711 | 4 | 0.67136 | 53708.8 | 0 | 0 | 0.05212 | 1824.2 | 0.71123 | 9957.22 | 40000 | 0 | 1824.2 | 0 | 9957.22 | 0 | 0 | 1927.38 | 0 | 0 | 1927.38
2022090712 | 4 | 0.72403 | 57922.4 | 0 | 0 | 0.11875 | 4156.25 | 0.75193 | 10527.02 | 40000 | 0 | 4156.25 | 0 | 10527.02 | 0 | 0 | 3239.13 | 0 | 0 | 3239.13
2022090713 | 4 | 0.77474 | 61979.2 | 0 | 0 | 0.15605 | 5461.75 | 0.73917 | 10348.38 | 40000 | 0 | 5461.75 | 0 | 10348.38 | 0 | 0 | 6169.07 | 0 | 0 | 6169.07
2022090714 | 4 | 0.81614 | 65291.2 | 0 | 0 | 0.16288 | 5700.8 | 0.72915 | 10208.1 | 40000 | 0 | 5700.8 | 0 | 10208.1 | 0 | 0 | 9382.3 | 0 | 0 | 9382.3
2022090715 | 4 | 0.83564 | 66851.2 | 0 | 0 | 0.16888 | 5910.8 | 0.73758 | 10326.12 | 40000 | 0 | 5910.8 | 0 | 10326.12 | 0 | 0 | 10614.28 | 0 | 0 | 10614.28
2022090716 | 4 | 0.83914 | 67131.2 | 0 | 0 | 0.17846 | 6246.1 | 0.70279 | 9839.06 | 40000 | 0 | 6246.1 | 0 | 9839.06 | 0 | 0 | 11046.04 | 0 | 0 | 11046.04
2022090717 | 4 | 0.83383 | 66706.4 | 0 | 0 | 0.18015 | 6305.25 | 0.66576 | 9320.64 | 40000 | 0 | 6305.25 | 0 | 9320.64 | 0 | 0 | 11080.51 | 0 | 0 | 11080.51
2022090718 | 4 | 0.81762 | 65409.6 | 0 | 0 | 0.17822 | 6237.7 | 0.56777 | 7948.78 | 40000 | 0 | 6237.7 | 0 | 7948.78 | 0 | 0 | 11223.12 | 0 | 0 | 11223.12
2022090719 | 4 | 0.79875 | 63900 | 0 | 0 | 0.16475 | 5766.25 | 0.31634 | 4428.76 | 40000 | 0 | 5766.25 | 0 | 4428.76 | 0 | 0 | 13704.99 | 0 | 0 | 13704.99
2022090720 | 4 | 0.76775 | 61420 | 0 | 0 | 0.14411 | 5043.85 | 0.04905 | 686.7 | 40000 | 0 | 5043.85 | 0 | 686.7 | 0 | 0 | 15689.45 | 0 | 0 | 15689.45
2022090721 | 4 | 0.74429 | 59543.2 | 0 | 0 | 0.15258 | 5340.3 | 0 | 0 | 40000 | 0 | 5340.3 | 0 | 0 | 0 | 0 | 14202.9 | 0 | 0 | 14202.9
2022090722 | 4 | 0.70741 | 56592.8 | 0 | 0 | 0.18355 | 6424.25 | 0 | 0 | 40000 | 0 | 6424.25 | 0 | 0 | 0 | 0 | 10168.55 | 0 | 0 | 10168.55
2022090723 | 4 | 0.65647 | 52517.6 | 0 | 0 | 0.21077 | 7376.95 | 0 | 0 | 40000 | 0 | 7376.95 | 0 | 0 | 0 | 0 | 5140.65 | 0 | 0 | 5140.65
2022090724 | 4 | 0.60771 | 48616.8 | 0 | 0 | 0.19929 | 6975.15 | 0 | 0 | 40000 | 0 | 6975.15 | 0 | 0 | 0 | 0 | 1641.65 | 0 | 0 | 1641.65
2022090801 | 5 | 0.57021 | 45616.8 | 0 | 0 | 0.16109 | 5638.15 | 0 | 0 | 40000 | 0 | 5616.8 | 21.35 | 0 | 0 | 21.35 | 0 | 0 | 0 | 0
2022090802 | 5 | 0.54278 | 43422.4 | 0 | 0 | 0.12616 | 4415.6 | 0 | 0 | 40000 | 0 | 3422.4 | 993.2 | 0 | 0 | 993.2 | 0 | 0 | 0 | 0
2022090803 | 5 | 0.52413 | 41930.4 | 0 | 0 | 0.0971 | 3398.5 | 0 | 0 | 40000 | 0 | 1930.4 | 1468.1 | 0 | 0 | 1468.1 | 0 | 0 | 0 | 0
2022090804 | 5 | 0.51385 | 41108 | 0 | 0 | 0.07631 | 2670.85 | 0 | 0 | 40000 | 0 | 1108 | 1562.85 | 0 | 0 | 1562.85 | 0 | 0 | 0 | 0
2022090805 | 5 | 0.51332 | 41065.6 | 0 | 0 | 0.05857 | 2049.95 | 0 | 0 | 40000 | 0 | 1065.6 | 984.35 | 0 | 0 | 984.35 | 0 | 0 | 0 | 0
2022090806 | 5 | 0.5302 | 42416 | 0 | 0 | 0.0458 | 1603 | 0 | 0 | 40000 | 0 | 1603 | 0 | 0 | 0 | 0 | 813 | 0 | 0 | 813
2022090807 | 5 | 0.55737 | 44589.6 | 0 | 0 | 0.04421 | 1547.35 | 0 | 0 | 40000 | 0 | 1547.35 | 0 | 0 | 0 | 0 | 3042.25 | 0 | 0 | 3042.25
2022090808 | 5 | 0.5653 | 45224 | 0 | 0 | 0.04543 | 1590.05 | 0.02736 | 383.04 | 40000 | 0 | 1590.05 | 0 | 383.04 | 0 | 0 | 3250.91 | 0 | 0 | 3250.91
2022090809 | 5 | 0.58021 | 46416.8 | 0 | 0 | 0.03915 | 1370.25 | 0.34774 | 4868.36 | 40000 | 0 | 1370.25 | 0 | 4868.36 | 0 | 0 | 178.19 | 0 | 0 | 178.19
2022090810 | 5 | 0.61245 | 48996 | 0 | 0 | 0.01935 | 677.25 | 0.69895 | 9785.3 | 40000 | 0 | 677.25 | 0 | 8318.75 | 1466.55 | 1466.55 | 0 | 0 | 0 | 0
2022090811 | 5 | 0.65865 | 52692 | 0 | 0 | 0.02289 | 801.15 | 0.77031 | 10784.34 | 40000 | 0 | 801.15 | 0 | 10784.34 | 0 | 0 | 1106.51 | 0 | 0 | 1106.51
2022090812 | 5 | 0.70681 | 56544.8 | 0 | 0 | 0.03677 | 1286.95 | 0.77716 | 10880.24 | 40000 | 0 | 1286.95 | 0 | 10880.24 | 0 | 0 | 4377.61 | 0 | 0 | 4377.61
2022090813 | 5 | 0.75121 | 60096.8 | 0 | 0 | 0.03844 | 1345.4 | 0.74582 | 10441.48 | 40000 | 0 | 1345.4 | 0 | 10441.48 | 0 | 0 | 8309.92 | 0 | 0 | 8309.92
2022090814 | 5 | 0.78793 | 63034.4 | 0 | 0 | 0.03051 | 1067.85 | 0.73733 | 10322.62 | 40000 | 0 | 1067.85 | 0 | 10322.62 | 0 | 0 | 11643.93 | 0 | 0 | 11643.93
2022090815 | 5 | 0.80792 | 64633.6 | 0 | 0 | 0.02663 | 932.05 | 0.74161 | 10382.54 | 40000 | 0 | 932.05 | 0 | 10382.54 | 0 | 0 | 13319.01 | 0 | 0 | 13319.01
2022090816 | 5 | 0.82035 | 65628 | 0 | 0 | 0.02479 | 867.65 | 0.74595 | 10443.3 | 40000 | 0 | 867.65 | 0 | 10443.3 | 0 | 0 | 14317.05 | 0 | 0 | 14317.05
2022090817 | 5 | 0.82494 | 65995.2 | 0 | 0 | 0.03058 | 1070.3 | 0.70081 | 9811.34 | 40000 | 0 | 1070.3 | 0 | 9811.34 | 0 | 0 | 15113.56 | 0 | 0 | 15113.56
2022090818 | 5 | 0.82266 | 65812.8 | 0 | 0 | 0.04242 | 1484.7 | 0.6029 | 8440.6 | 40000 | 0 | 1484.7 | 0 | 8440.6 | 0 | 0 | 15887.5 | 0 | 0 | 15887.5
2022090819 | 5 | 0.80185 | 64148 | 0 | 0 | 0.06176 | 2161.6 | 0.37254 | 5215.56 | 40000 | 0 | 2161.6 | 0 | 5215.56 | 0 | 0 | 16770.84 | 0 | 0 | 16770.84
2022090820 | 5 | 0.7721 | 61768 | 0 | 0 | 0.08872 | 3105.2 | 0.05525 | 773.5 | 40000 | 0 | 3105.2 | 0 | 773.5 | 0 | 0 | 17889.3 | 0 | 0 | 17889.3
2022090821 | 5 | 0.74775 | 59820 | 0 | 0 | 0.12378 | 4332.3 | 0.00348 | 48.72 | 40000 | 0 | 4332.3 | 0 | 48.72 | 0 | 0 | 15438.98 | 0 | 0 | 15438.98
2022090822 | 5 | 0.70926 | 56740.8 | 0 | 0 | 0.15278 | 5347.3 | 0.00345 | 48.3 | 40000 | 0 | 5347.3 | 0 | 48.3 | 0 | 0 | 11345.2 | 0 | 0 | 11345.2
2022090823 | 5 | 0.66046 | 52836.8 | 0 | 0 | 0.20112 | 7039.2 | 0.00044 | 6.16 | 40000 | 0 | 7039.2 | 0 | 6.16 | 0 | 0 | 5791.44 | 0 | 0 | 5791.44
2022090824 | 5 | 0.60811 | 48648.8 | 0 | 0 | 0.25477 | 8916.95 | 0 | 0 | 40000 | 0 | 8648.8 | 268.15 | 0 | 0 | 268.15 | 0 | 0 | 0 | 0
2022090901 | 6 | 0.56777 | 45421.6 | 0 | 0 | 0.28476 | 9966.6 | 0 | 0 | 40000 | 0 | 5421.6 | 4545 | 0 | 0 | 4545 | 0 | 0 | 0 | 0
2022090902 | 6 | 0.53748 | 42998.4 | 0 | 0 | 0.30329 | 10615.15 | 0 | 0 | 40000 | 0 | 2998.4 | 7616.75 | 0 | 0 | 7616.75 | 0 | 0 | 0 | 0
2022090903 | 6 | 0.51678 | 41342.4 | 0 | 0 | 0.31165 | 10907.75 | 0 | 0 | 40000 | 0 | 1342.4 | 9565.35 | 0 | 0 | 9565.35 | 0 | 0 | 0 | 0
2022090904 | 6 | 0.50566 | 40452.8 | 0 | 0 | 0.31162 | 10906.7 | 0 | 0 | 40000 | 0 | 452.8 | 10453.9 | 0 | 0 | 10453.9 | 0 | 0 | 0 | 0
2022090905 | 6 | 0.50369 | 40295.2 | 0 | 0 | 0.29165 | 10207.75 | 0 | 0 | 40000 | 0 | 295.2 | 9912.55 | 0 | 0 | 9912.55 | 0 | 0 | 0 | 0
2022090906 | 6 | 0.52048 | 41638.4 | 0 | 0 | 0.25438 | 8903.3 | 0 | 0 | 40000 | 0 | 1638.4 | 7264.9 | 0 | 0 | 7264.9 | 0 | 0 | 0 | 0
2022090907 | 6 | 0.54709 | 43767.2 | 0 | 0 | 0.21544 | 7540.4 | 0 | 0 | 40000 | 0 | 3767.2 | 3773.2 | 0 | 0 | 3773.2 | 0 | 0 | 0 | 0
2022090908 | 6 | 0.55803 | 44642.4 | 0 | 0 | 0.19412 | 6794.2 | 0.03073 | 430.22 | 40000 | 0 | 4642.4 | 2151.8 | 0 | 430.22 | 2582.02 | 0 | 0 | 0 | 0
2022090909 | 6 | 0.57624 | 46099.2 | 0 | 0 | 0.1408 | 4928 | 0.32768 | 4587.52 | 40000 | 0 | 4928 | 0 | 1171.2 | 3416.32 | 3416.32 | 0 | 0 | 0 | 0
2022090910 | 6 | 0.61188 | 48950.4 | 0 | 0 | 0.07421 | 2597.35 | 0.60692 | 8496.88 | 40000 | 0 | 2597.35 | 0 | 6353.05 | 2143.83 | 2143.83 | 0 | 0 | 0 | 0
2022090911 | 6 | 0.65852 | 52681.6 | 0 | 0 | 0.0656 | 2296 | 0.7069 | 9896.6 | 40000 | 0 | 2296 | 0 | 9896.6 | 0 | 0 | 489 | 0 | 0 | 489
2022090912 | 6 | 0.70043 | 56034.4 | 0 | 0 | 0.05148 | 1801.8 | 0.76691 | 10736.74 | 40000 | 0 | 1801.8 | 0 | 10736.74 | 0 | 0 | 3495.86 | 0 | 0 | 3495.86
2022090913 | 6 | 0.74441 | 59552.8 | 0 | 0 | 0.0377 | 1319.5 | 0.75745 | 10604.3 | 40000 | 0 | 1319.5 | 0 | 10604.3 | 0 | 0 | 7629 | 0 | 0 | 7629
2022090914 | 6 | 0.77686 | 62148.8 | 0 | 0 | 0.03672 | 1285.2 | 0.76542 | 10715.88 | 40000 | 0 | 1285.2 | 0 | 10715.88 | 0 | 0 | 10147.72 | 0 | 0 | 10147.72
2022090915 | 6 | 0.80227 | 64181.6 | 0 | 0 | 0.0462 | 1617 | 0.74895 | 10485.3 | 40000 | 0 | 1617 | 0 | 10485.3 | 0 | 0 | 12079.3 | 0 | 0 | 12079.3
2022090916 | 6 | 0.81891 | 65512.8 | 0 | 0 | 0.07842 | 2744.7 | 0.73046 | 10226.44 | 40000 | 0 | 2744.7 | 0 | 10226.44 | 0 | 0 | 12541.66 | 0 | 0 | 12541.66
2022090917 | 6 | 0.82701 | 66160.8 | 0 | 0 | 0.10351 | 3622.85 | 0.71045 | 9946.3 | 40000 | 0 | 3622.85 | 0 | 9946.3 | 0 | 0 | 12591.65 | 0 | 0 | 12591.65
2022090918 | 6 | 0.81757 | 65405.6 | 0 | 0 | 0.09888 | 3460.8 | 0.6448 | 9027.2 | 40000 | 0 | 3460.8 | 0 | 9027.2 | 0 | 0 | 12917.6 | 0 | 0 | 12917.6
2022090919 | 6 | 0.78988 | 63190.4 | 0 | 0 | 0.1186 | 4151 | 0.41111 | 5755.54 | 40000 | 0 | 4151 | 0 | 5755.54 | 0 | 0 | 13283.86 | 0 | 0 | 13283.86
2022090920 | 6 | 0.75059 | 60047.2 | 0 | 0 | 0.1624 | 5684 | 0.07125 | 997.5 | 40000 | 0 | 5684 | 0 | 997.5 | 0 | 0 | 13365.7 | 0 | 0 | 13365.7
2022090921 | 6 | 0.72137 | 57709.6 | 0 | 0 | 0.25135 | 8797.25 | 0 | 0 | 40000 | 0 | 8797.25 | 0 | 0 | 0 | 0 | 8912.35 | 0 | 0 | 8912.35
2022090922 | 6 | 0.6881 | 55048 | 0 | 0 | 0.34151 | 11952.85 | 0 | 0 | 40000 | 0 | 11952.85 | 0 | 0 | 0 | 0 | 3095.15 | 0 | 0 | 3095.15
2022090923 | 6 | 0.65211 | 52168.8 | 0 | 0 | 0.41663 | 14582.05 | 0 | 0 | 40000 | 0 | 12168.8 | 2413.25 | 0 | 0 | 2413.25 | 0 | 0 | 0 | 0
2022090924 | 6 | 0.61092 | 48873.6 | 0 | 0 | 0.45512 | 15929.2 | 0 | 0 | 40000 | 0 | 8873.6 | 7055.6 | 0 | 0 | 7055.6 | 0 | 0 | 0 | 0
2022091001 | 7 | 0.57298 | 45838.4 | 0 | 0 | 0.4472 | 15652 | 0 | 0 | 40000 | 0 | 5838.4 | 9813.6 | 0 | 0 | 9813.6 | 0 | 0 | 0 | 0
2022091002 | 7 | 0.5428 | 43424 | 0 | 0 | 0.41311 | 14458.85 | 0 | 0 | 40000 | 0 | 3424 | 11034.85 | 0 | 0 | 11034.85 | 0 | 0 | 0 | 0
2022091003 | 7 | 0.51878 | 41502.4 | 0 | 0 | 0.36086 | 12630.1 | 0 | 0 | 40000 | 0 | 1502.4 | 11127.7 | 0 | 0 | 11127.7 | 0 | 0 | 0 | 0
2022091004 | 7 | 0.5029 | 40232 | 0 | 0 | 0.31096 | 10883.6 | 0 | 0 | 40000 | 0 | 232 | 10651.6 | 0 | 0 | 10651.6 | 0 | 0 | 0 | 0
2022091005 | 7 | 0.49366 | 39492.8 | 0 | 0 | 0.25752 | 9013.2 | 0 | 0 | 39492.8 | 507.2 | 0 | 9013.2 | 0 | 0 | 9520.4 | 0 | 0 | 0 | 0
2022091006 | 7 | 0.49273 | 39418.4 | 0 | 0 | 0.22633 | 7921.55 | 0 | 0 | 39418.4 | 581.6 | 0 | 7921.55 | 0 | 0 | 8503.15 | 0 | 0 | 0 | 0
2022091007 | 7 | 0.49724 | 39779.2 | 0 | 0 | 0.18856 | 6599.6 | 0 | 0 | 39779.2 | 220.8 | 0 | 6599.6 | 0 | 0 | 6820.4 | 0 | 0 | 0 | 0
2022091008 | 7 | 0.50453 | 40362.4 | 0 | 0 | 0.15804 | 5531.4 | 0.02642 | 369.88 | 40000 | 0 | 362.4 | 5169 | 0 | 369.88 | 5538.88 | 0 | 0 | 0 | 0
2022091009 | 7 | 0.53183 | 42546.4 | 0 | 0 | 0.11419 | 3996.65 | 0.34231 | 4792.34 | 40000 | 0 | 2546.4 | 1450.25 | 0 | 4792.34 | 6242.59 | 0 | 0 | 0 | 0
2022091010 | 7 | 0.57649 | 46119.2 | 0 | 0 | 0.07837 | 2742.95 | 0.65194 | 9127.16 | 40000 | 0 | 2742.95 | 0 | 3376.25 | 5750.91 | 5750.91 | 0 | 0 | 0 | 0
2022091011 | 7 | 0.62973 | 50378.4 | 0 | 0 | 0.07946 | 2781.1 | 0.75651 | 10591.14 | 40000 | 0 | 2781.1 | 0 | 7597.3 | 2993.84 | 2993.84 | 0 | 0 | 0 | 0
2022091012 | 7 | 0.67774 | 54219.2 | 0 | 0 | 0.06402 | 2240.7 | 0.7892 | 11048.8 | 40000 | 0 | 2240.7 | 0 | 11048.8 | 0 | 0 | 929.7 | 0 | 0 | 929.7
2022091013 | 7 | 0.72024 | 57619.2 | 0 | 0 | 0.0507 | 1774.5 | 0.76101 | 10654.14 | 40000 | 0 | 1774.5 | 0 | 10654.14 | 0 | 0 | 5190.56 | 0 | 0 | 5190.56
2022091014 | 7 | 0.75319 | 60255.2 | 0 | 0 | 0.05541 | 1939.35 | 0.72404 | 10136.56 | 40000 | 0 | 1939.35 | 0 | 10136.56 | 0 | 0 | 8179.29 | 0 | 0 | 8179.29
2022091015 | 7 | 0.77926 | 62340.8 | 0 | 0 | 0.06776 | 2371.6 | 0.71776 | 10048.64 | 40000 | 0 | 2371.6 | 0 | 10048.64 | 0 | 0 | 9920.56 | 0 | 0 | 9920.56
2022091016 | 7 | 0.80049 | 64039.2 | 0 | 0 | 0.10178 | 3562.3 | 0.72394 | 10135.16 | 40000 | 0 | 3562.3 | 0 | 10135.16 | 0 | 0 | 10341.74 | 0 | 0 | 10341.74
2022091017 | 7 | 0.81102 | 64881.6 | 0 | 0 | 0.13758 | 4815.3 | 0.70257 | 9835.98 | 40000 | 0 | 4815.3 | 0 | 9835.98 | 0 | 0 | 10230.32 | 0 | 0 | 10230.32
2022091018 | 7 | 0.80683 | 64546.4 | 0 | 0 | 0.16257 | 5689.95 | 0.62217 | 8710.38 | 40000 | 0 | 5689.95 | 0 | 8710.38 | 0 | 0 | 10146.07 | 0 | 0 | 10146.07
2022091019 | 7 | 0.78561 | 62848.8 | 0 | 0 | 0.21984 | 7694.4 | 0.38152 | 5341.28 | 40000 | 0 | 7694.4 | 0 | 5341.28 | 0 | 0 | 9813.12 | 0 | 0 | 9813.12
2022091020 | 7 | 0.75384 | 60307.2 | 0 | 0 | 0.27947 | 9781.45 | 0.05942 | 831.88 | 40000 | 0 | 9781.45 | 0 | 831.88 | 0 | 0 | 9693.87 | 0 | 0 | 9693.87
2022091021 | 7 | 0.72559 | 58047.2 | 0 | 0 | 0.33805 | 11831.75 | 0 | 0 | 40000 | 0 | 11831.75 | 0 | 0 | 0 | 0 | 6215.45 | 0 | 0 | 6215.45
2022091022 | 7 | 0.68826 | 55060.8 | 0 | 0 | 0.39155 | 13704.25 | 0 | 0 | 40000 | 0 | 13704.25 | 0 | 0 | 0 | 0 | 1356.55 | 0 | 0 | 1356.55
2022091023 | 7 | 0.64988 | 51990.4 | 0 | 0 | 0.40721 | 14252.35 | 0 | 0 | 40000 | 0 | 11990.4 | 2261.95 | 0 | 0 | 2261.95 | 0 | 0 | 0 | 0
2022091024 | 7 | 0.6115 | 48920 | 0 | 0 | 0.41667 | 14583.45 | 0 | 0 | 40000 | 0 | 8920 | 5663.45 | 0 | 0 | 5663.45 | 0 | 0 | 0 | 0
2022091101 | 1 | 0.57672 | 46137.6 | 0 | 0 | 0.39886 | 13960.1 | 0 | 0 | 40000 | 0 | 6137.6 | 7822.5 | 0 | 0 | 7822.5 | 0 | 0 | 0 | 0
2022091102 | 1 | 0.55004 | 44003.2 | 0 | 0 | 0.36029 | 12610.15 | 0 | 0 | 40000 | 0 | 4003.2 | 8606.95 | 0 | 0 | 8606.95 | 0 | 0 | 0 | 0
2022091103 | 1 | 0.52772 | 42217.6 | 0 | 0 | 0.34974 | 12240.9 | 0 | 0 | 40000 | 0 | 2217.6 | 10023.3 | 0 | 0 | 10023.3 | 0 | 0 | 0 | 0
2022091104 | 1 | 0.51193 | 40954.4 | 0 | 0 | 0.33477 | 11716.95 | 0 | 0 | 40000 | 0 | 954.4 | 10762.55 | 0 | 0 | 10762.55 | 0 | 0 | 0 | 0
2022091105 | 1 | 0.4986 | 39888 | 0 | 0 | 0.31806 | 11132.1 | 0 | 0 | 39888 | 112 | 0 | 11132.1 | 0 | 0 | 11244.1 | 0 | 0 | 0 | 0
2022091106 | 1 | 0.49638 | 39710.4 | 0 | 0 | 0.30978 | 10842.3 | 0 | 0 | 39710.4 | 289.6 | 0 | 10842.3 | 0 | 0 | 11131.9 | 0 | 0 | 0 | 0
2022091107 | 1 | 0.49265 | 39412 | 0 | 0 | 0.30739 | 10758.65 | 0 | 0 | 39412 | 588 | 0 | 10758.65 | 0 | 0 | 11346.65 | 0 | 0 | 0 | 0
2022091108 | 1 | 0.4935 | 39480 | 0 | 0 | 0.32539 | 11388.65 | 0.01985 | 277.9 | 39480 | 520 | 0 | 11388.65 | 0 | 277.9 | 12186.55 | 0 | 0 | 0 | 0
2022091109 | 1 | 0.51684 | 41347.2 | 0 | 0 | 0.33541 | 11739.35 | 0.18309 | 2563.26 | 40000 | 0 | 1347.2 | 10392.15 | 0 | 2563.26 | 12955.41 | 0 | 0 | 0 | 0
2022091110 | 1 | 0.55827 | 44661.6 | 0 | 0 | 0.32838 | 11493.3 | 0.3496 | 4894.4 | 40000 | 0 | 4661.6 | 6831.7 | 0 | 4894.4 | 11726.1 | 0 | 0 | 0 | 0
2022091111 | 1 | 0.59949 | 47959.2 | 0 | 0 | 0.26349 | 9222.15 | 0.48151 | 6741.14 | 40000 | 0 | 7959.2 | 1262.95 | 0 | 6741.14 | 8004.09 | 0 | 0 | 0 | 0
2022091112 | 1 | 0.64155 | 51324 | 0 | 0 | 0.2014 | 7049 | 0.57054 | 7987.56 | 40000 | 0 | 7049 | 0 | 4275 | 3712.56 | 3712.56 | 0 | 0 | 0 | 0
2022091113 | 1 | 0.68084 | 54467.2 | 0 | 0 | 0.13448 | 4706.8 | 0.65396 | 9155.44 | 40000 | 0 | 4706.8 | 0 | 9155.44 | 0 | 0 | 604.96 | 0 | 0 | 604.96
2022091114 | 1 | 0.71464 | 57171.2 | 0 | 0 | 0.09526 | 3334.1 | 0.68455 | 9583.7 | 40000 | 0 | 3334.1 | 0 | 9583.7 | 0 | 0 | 4253.4 | 0 | 0 | 4253.4
2022091115 | 1 | 0.742 | 59360 | 0 | 0 | 0.07851 | 2747.85 | 0.68995 | 9659.3 | 40000 | 0 | 2747.85 | 0 | 9659.3 | 0 | 0 | 6952.85 | 0 | 0 | 6952.85
2022091116 | 1 | 0.76522 | 61217.6 | 0 | 0 | 0.07283 | 2549.05 | 0.71234 | 9972.76 | 40000 | 0 | 2549.05 | 0 | 9972.76 | 0 | 0 | 8695.79 | 0 | 0 | 8695.79
2022091117 | 1 | 0.77562 | 62049.6 | 0 | 0 | 0.06462 | 2261.7 | 0.64572 | 9040.08 | 40000 | 0 | 2261.7 | 0 | 9040.08 | 0 | 0 | 10747.82 | 0 | 0 | 10747.82
2022091118 | 1 | 0.77543 | 62034.4 | 0 | 0 | 0.06361 | 2226.35 | 0.56398 | 7895.72 | 40000 | 0 | 2226.35 | 0 | 7895.72 | 0 | 0 | 11912.33 | 0 | 0 | 11912.33
2022091119 | 1 | 0.75647 | 60517.6 | 0 | 0 | 0.05626 | 1969.1 | 0.35244 | 4934.16 | 40000 | 0 | 1969.1 | 0 | 4934.16 | 0 | 0 | 13614.34 | 0 | 0 | 13614.34
2022091120 | 1 | 0.72544 | 58035.2 | 0 | 0 | 0.05209 | 1823.15 | 0.05176 | 724.64 | 40000 | 0 | 1823.15 | 0 | 724.64 | 0 | 0 | 15487.41 | 0 | 0 | 15487.41
2022091121 | 1 | 0.70981 | 56784.8 | 0 | 0 | 0.07209 | 2523.15 | 0 | 0 | 40000 | 0 | 2523.15 | 0 | 0 | 0 | 0 | 14261.65 | 0 | 0 | 14261.65
2022091122 | 1 | 0.67644 | 54115.2 | 0 | 0 | 0.09542 | 3339.7 | 0 | 0 | 40000 | 0 | 3339.7 | 0 | 0 | 0 | 0 | 10775.5 | 0 | 0 | 10775.5
2022091123 | 1 | 0.62973 | 50378.4 | 0 | 0 | 0.08892 | 3112.2 | 0 | 0 | 40000 | 0 | 3112.2 | 0 | 0 | 0 | 0 | 7266.2 | 0 | 0 | 7266.2
2022091124 | 1 | 0.58266 | 46612.8 | 0 | 0 | 0.08308 | 2907.8 | 0 | 0 | 40000 | 0 | 2907.8 | 0 | 0 | 0 | 0 | 3705 | 0 | 0 | 3705
2022091201 | 2 | 0.54331 | 43464.8 | 0 | 0 | 0.09033 | 3161.55 | 0 | 0 | 40000 | 0 | 3161.55 | 0 | 0 | 0 | 0 | 303.25 | 0 | 0 | 303.25
2022091202 | 2 | 0.51537 | 41229.6 | 0 | 0 | 0.09576 | 3351.6 | 0 | 0 | 40000 | 0 | 1229.6 | 2122 | 0 | 0 | 2122 | 0 | 0 | 0 | 0
2022091203 | 2 | 0.49844 | 39875.2 | 0 | 0 | 0.10048 | 3516.8 | 0 | 0 | 39875.2 | 124.8 | 0 | 3516.8 | 0 | 0 | 3641.6 | 0 | 0 | 0 | 0
2022091204 | 2 | 0.48837 | 39069.6 | 0 | 0 | 0.11204 | 3921.4 | 0 | 0 | 39069.6 | 930.4 | 0 | 3921.4 | 0 | 0 | 4851.8 | 0 | 0 | 0 | 0
2022091205 | 2 | 0.49064 | 39251.2 | 0 | 0 | 0.11764 | 4117.4 | 0 | 0 | 39251.2 | 748.8 | 0 | 4117.4 | 0 | 0 | 4866.2 | 0 | 0 | 0 | 0
2022091206 | 2 | 0.50676 | 40540.8 | 0 | 0 | 0.1128 | 3948 | 0 | 0 | 40000 | 0 | 540.8 | 3407.2 | 0 | 0 | 3407.2 | 0 | 0 | 0 | 0
2022091207 | 2 | 0.53376 | 42700.8 | 0 | 0 | 0.11946 | 4181.1 | 0 | 0 | 40000 | 0 | 2700.8 | 1480.3 | 0 | 0 | 1480.3 | 0 | 0 | 0 | 0
2022091208 | 2 | 0.54015 | 43212 | 0 | 0 | 0.12009 | 4203.15 | 0.02425 | 339.5 | 40000 | 0 | 3212 | 991.15 | 0 | 339.5 | 1330.65 | 0 | 0 | 0 | 0
2022091209 | 2 | 0.55497 | 44397.6 | 0 | 0 | 0.10245 | 3585.75 | 0.28371 | 3971.94 | 40000 | 0 | 3585.75 | 0 | 811.85 | 3160.09 | 3160.09 | 0 | 0 | 0 | 0
2022091210 | 2 | 0.58193 | 46554.4 | 0 | 0 | 0.07781 | 2723.35 | 0.57696 | 8077.44 | 40000 | 0 | 2723.35 | 0 | 3831.05 | 4246.39 | 4246.39 | 0 | 0 | 0 | 0
2022091211 | 2 | 0.62022 | 49617.6 | 0 | 0 | 0.09992 | 3497.2 | 0.66697 | 9337.58 | 40000 | 0 | 3497.2 | 0 | 6120.4 | 3217.18 | 3217.18 | 0 | 0 | 0 | 0
2022091212 | 2 | 0.66097 | 52877.6 | 0 | 0 | 0.09875 | 3456.25 | 0.75815 | 10614.1 | 40000 | 0 | 3456.25 | 0 | 9421.35 | 1192.75 | 1192.75 | 0 | 0 | 0 | 0
2022091213 | 2 | 0.70156 | 56124.8 | 0 | 0 | 0.08559 | 2995.65 | 0.77026 | 10783.64 | 40000 | 0 | 2995.65 | 0 | 10783.64 | 0 | 0 | 2345.51 | 0 | 0 | 2345.51
2022091214 | 2 | 0.74033 | 59226.4 | 0 | 0 | 0.07711 | 2698.85 | 0.76982 | 10777.48 | 40000 | 0 | 2698.85 | 0 | 10777.48 | 0 | 0 | 5750.07 | 0 | 0 | 5750.07
2022091215 | 2 | 0.77305 | 61844 | 0 | 0 | 0.06951 | 2432.85 | 0.76 | 10640 | 40000 | 0 | 2432.85 | 0 | 10640 | 0 | 0 | 8771.15 | 0 | 0 | 8771.15
2022091216 | 2 | 0.79767 | 63813.6 | 0 | 0 | 0.06204 | 2171.4 | 0.75279 | 10539.06 | 40000 | 0 | 2171.4 | 0 | 10539.06 | 0 | 0 | 11103.14 | 0 | 0 | 11103.14
2022091217 | 2 | 0.81503 | 65202.4 | 0 | 0 | 0.05884 | 2059.4 | 0.71941 | 10071.74 | 40000 | 0 | 2059.4 | 0 | 10071.74 | 0 | 0 | 13071.26 | 0 | 0 | 13071.26
2022091218 | 2 | 0.81436 | 65148.8 | 0 | 0 | 0.05662 | 1981.7 | 0.65397 | 9155.58 | 40000 | 0 | 1981.7 | 0 | 9155.58 | 0 | 0 | 14011.52 | 0 | 0 | 14011.52
2022091219 | 2 | 0.78937 | 63149.6 | 0 | 0 | 0.06574 | 2300.9 | 0.41701 | 5838.14 | 40000 | 0 | 2300.9 | 0 | 5838.14 | 0 | 0 | 15010.56 | 0 | 0 | 15010.56
2022091220 | 2 | 0.75591 | 60472.8 | 0 | 0 | 0.09571 | 3349.85 | 0.05869 | 821.66 | 40000 | 0 | 3349.85 | 0 | 821.66 | 0 | 0 | 16301.29 | 0 | 0 | 16301.29
2022091221 | 2 | 0.73454 | 58763.2 | 0 | 0 | 0.1663 | 5820.5 | 0 | 0 | 40000 | 0 | 5820.5 | 0 | 0 | 0 | 0 | 12942.7 | 0 | 0 | 12942.7
2022091222 | 2 | 0.69441 | 55552.8 | 0 | 0 | 0.27424 | 9598.4 | 0 | 0 | 40000 | 0 | 9598.4 | 0 | 0 | 0 | 0 | 5954.4 | 0 | 0 | 5954.4
2022091223 | 2 | 0.63961 | 51168.8 | 0 | 0 | 0.34598 | 12109.3 | 0 | 0 | 40000 | 0 | 11168.8 | 940.5 | 0 | 0 | 940.5 | 0 | 0 | 0 | 0
2022091224 | 2 | 0.58852 | 47081.6 | 0 | 0 | 0.36006 | 12602.1 | 0 | 0 | 40000 | 0 | 7081.6 | 5520.5 | 0 | 0 | 5520.5 | 0 | 0 | 0 | 0
2022091301 | 3 | 0.5499 | 43992 | 0 | 0 | 0.36985 | 12944.75 | 0 | 0 | 40000 | 0 | 3992 | 8952.75 | 0 | 0 | 8952.75 | 0 | 0 | 0 | 0
2022091302 | 3 | 0.52183 | 41746.4 | 0 | 0 | 0.37973 | 13290.55 | 0 | 0 | 40000 | 0 | 1746.4 | 11544.15 | 0 | 0 | 11544.15 | 0 | 0 | 0 | 0
2022091303 | 3 | 0.50489 | 40391.2 | 0 | 0 | 0.38086 | 13330.1 | 0 | 0 | 40000 | 0 | 391.2 | 12938.9 | 0 | 0 | 12938.9 | 0 | 0 | 0 | 0
2022091304 | 3 | 0.49538 | 39630.4 | 0 | 0 | 0.37155 | 13004.25 | 0 | 0 | 39630.4 | 369.6 | 0 | 13004.25 | 0 | 0 | 13373.85 | 0 | 0 | 0 | 0
2022091305 | 3 | 0.4925 | 39400 | 0 | 0 | 0.34077 | 11926.95 | 0 | 0 | 39400 | 600 | 0 | 11926.95 | 0 | 0 | 12526.95 | 0 | 0 | 0 | 0
2022091306 | 3 | 0.50873 | 40698.4 | 0 | 0 | 0.30586 | 10705.1 | 0 | 0 | 40000 | 0 | 698.4 | 10006.7 | 0 | 0 | 10006.7 | 0 | 0 | 0 | 0
2022091307 | 3 | 0.53662 | 42929.6 | 0 | 0 | 0.28252 | 9888.2 | 0 | 0 | 40000 | 0 | 2929.6 | 6958.6 | 0 | 0 | 6958.6 | 0 | 0 | 0 | 0
2022091308 | 3 | 0.54241 | 43392.8 | 0 | 0 | 0.27247 | 9536.45 | 0.02311 | 323.54 | 40000 | 0 | 3392.8 | 6143.65 | 0 | 323.54 | 6467.19 | 0 | 0 | 0 | 0
2022091309 | 3 | 0.55691 | 44552.8 | 0 | 0 | 0.22247 | 7786.45 | 0.33375 | 4672.5 | 40000 | 0 | 4552.8 | 3233.65 | 0 | 4672.5 | 7906.15 | 0 | 0 | 0 | 0
2022091310 | 3 | 0.58638 | 46910.4 | 0 | 0 | 0.1621 | 5673.5 | 0.67529 | 9454.06 | 40000 | 0 | 5673.5 | 0 | 1236.9 | 8217.16 | 8217.16 | 0 | 0 | 0 | 0
2022091311 | 3 | 0.62903 | 50322.4 | 0 | 0 | 0.16267 | 5693.45 | 0.76639 | 10729.46 | 40000 | 0 | 5693.45 | 0 | 4628.95 | 6100.51 | 6100.51 | 0 | 0 | 0 | 0
2022091312 | 3 | 0.6722 | 53776 | 0 | 0 | 0.13102 | 4585.7 | 0.77241 | 10813.74 | 40000 | 0 | 4585.7 | 0 | 9190.3 | 1623.44 | 1623.44 | 0 | 0 | 0 | 0
2022091313 | 3 | 0.71683 | 57346.4 | 0 | 0 | 0.11939 | 4178.65 | 0.77204 | 10808.56 | 40000 | 0 | 4178.65 | 0 | 10808.56 | 0 | 0 | 2359.19 | 0 | 0 | 2359.19
2022091314 | 3 | 0.75881 | 60704.8 | 0 | 0 | 0.13105 | 4586.75 | 0.76279 | 10679.06 | 40000 | 0 | 4586.75 | 0 | 10679.06 | 0 | 0 | 5438.99 | 0 | 0 | 5438.99
2022091315 | 3 | 0.78901 | 63120.8 | 0 | 0 | 0.15106 | 5287.1 | 0.73611 | 10305.54 | 40000 | 0 | 5287.1 | 0 | 10305.54 | 0 | 0 | 7528.16 | 0 | 0 | 7528.16
2022091316 | 3 | 0.81428 | 65142.4 | 0 | 0 | 0.17196 | 6018.6 | 0.72078 | 10090.92 | 40000 | 0 | 6018.6 | 0 | 10090.92 | 0 | 0 | 9032.88 | 0 | 0 | 9032.88
2022091317 | 3 | 0.82995 | 66396 | 0 | 0 | 0.20043 | 7015.05 | 0.68122 | 9537.08 | 40000 | 0 | 7015.05 | 0 | 9537.08 | 0 | 0 | 9843.87 | 0 | 0 | 9843.87
2022091318 | 3 | 0.82853 | 66282.4 | 0 | 0 | 0.23213 | 8124.55 | 0.59651 | 8351.14 | 40000 | 0 | 8124.55 | 0 | 8351.14 | 0 | 0 | 9806.71 | 0 | 0 | 9806.71
2022091319 | 3 | 0.80499 | 64399.2 | 0 | 0 | 0.28281 | 9898.35 | 0.34769 | 4867.66 | 40000 | 0 | 9898.35 | 0 | 4867.66 | 0 | 0 | 9633.19 | 0 | 0 | 9633.19
2022091320 | 3 | 0.77135 | 61708 | 0 | 0 | 0.31019 | 10856.65 | 0.03709 | 519.26 | 40000 | 0 | 10856.65 | 0 | 519.26 | 0 | 0 | 10332.09 | 0 | 0 | 10332.09
2022091321 | 3 | 0.74571 | 59656.8 | 0 | 0 | 0.35619 | 12466.65 | 0 | 0 | 40000 | 0 | 12466.65 | 0 | 0 | 0 | 0 | 7190.15 | 0 | 0 | 7190.15
2022091322 | 3 | 0.7073 | 56584 | 0 | 0 | 0.412 | 14420 | 0 | 0 | 40000 | 0 | 14420 | 0 | 0 | 0 | 0 | 2164 | 0 | 0 | 2164
2022091323 | 3 | 0.65384 | 52307.2 | 0 | 0 | 0.45851 | 16047.85 | 0 | 0 | 40000 | 0 | 12307.2 | 3740.65 | 0 | 0 | 3740.65 | 0 | 0 | 0 | 0
2022091324 | 3 | 0.60132 | 48105.6 | 0 | 0 | 0.47124 | 16493.4 | 0 | 0 | 40000 | 0 | 8105.6 | 8387.8 | 0 | 0 | 8387.8 | 0 | 0 | 0 | 0
2022091401 | 4 | 0.55864 | 44691.2 | 0 | 0 | 0.46116 | 16140.6 | 0 | 0 | 40000 | 0 | 4691.2 | 11449.4 | 0 | 0 | 11449.4 | 0 | 0 | 0 | 0
2022091402 | 4 | 0.52911 | 42328.8 | 0 | 0 | 0.44202 | 15470.7 | 0 | 0 | 40000 | 0 | 2328.8 | 13141.9 | 0 | 0 | 13141.9 | 0 | 0 | 0 | 0
2022091403 | 4 | 0.50864 | 40691.2 | 0 | 0 | 0.42741 | 14959.35 | 0 | 0 | 40000 | 0 | 691.2 | 14268.15 | 0 | 0 | 14268.15 | 0 | 0 | 0 | 0
2022091404 | 4 | 0.49527 | 39621.6 | 0 | 0 | 0.40969 | 14339.15 | 0 | 0 | 39621.6 | 378.4 | 0 | 14339.15 | 0 | 0 | 14717.55 | 0 | 0 | 0 | 0
2022091405 | 4 | 0.49287 | 39429.6 | 0 | 0 | 0.39201 | 13720.35 | 0 | 0 | 39429.6 | 570.4 | 0 | 13720.35 | 0 | 0 | 14290.75 | 0 | 0 | 0 | 0
2022091406 | 4 | 0.50819 | 40655.2 | 0 | 0 | 0.35984 | 12594.4 | 0 | 0 | 40000 | 0 | 655.2 | 11939.2 | 0 | 0 | 11939.2 | 0 | 0 | 0 | 0
2022091407 | 4 | 0.5355 | 42840 | 0 | 0 | 0.33512 | 11729.2 | 0 | 0 | 40000 | 0 | 2840 | 8889.2 | 0 | 0 | 8889.2 | 0 | 0 | 0 | 0
2022091408 | 4 | 0.54315 | 43452 | 0 | 0 | 0.32156 | 11254.6 | 0.02576 | 360.64 | 40000 | 0 | 3452 | 7802.6 | 0 | 360.64 | 8163.24 | 0 | 0 | 0 | 0
2022091409 | 4 | 0.55718 | 44574.4 | 0 | 0 | 0.2618 | 9163 | 0.2926 | 4096.4 | 40000 | 0 | 4574.4 | 4588.6 | 0 | 4096.4 | 8685 | 0 | 0 | 0 | 0
2022091410 | 4 | 0.59019 | 47215.2 | 0 | 0 | 0.24562 | 8596.7 | 0.5952 | 8332.8 | 40000 | 0 | 7215.2 | 1381.5 | 0 | 8332.8 | 9714.3 | 0 | 0 | 0 | 0
2022091411 | 4 | 0.63005 | 50404 | 0 | 0 | 0.2796 | 9786 | 0.70581 | 9881.34 | 40000 | 0 | 9786 | 0 | 618 | 9263.34 | 9263.34 | 0 | 0 | 0 | 0
2022091412 | 4 | 0.66965 | 53572 | 0 | 0 | 0.28687 | 10040.45 | 0.74126 | 10377.64 | 40000 | 0 | 10040.45 | 0 | 3531.55 | 6846.09 | 6846.09 | 0 | 0 | 0 | 0
2022091413 | 4 | 0.7093 | 56744 | 0 | 0 | 0.3096 | 10836 | 0.75154 | 10521.56 | 40000 | 0 | 10836 | 0 | 5908 | 4613.56 | 4613.56 | 0 | 0 | 0 | 0
2022091414 | 4 | 0.74817 | 59853.6 | 0 | 0 | 0.33403 | 11691.05 | 0.72814 | 10193.96 | 40000 | 0 | 11691.05 | 0 | 8162.55 | 2031.41 | 2031.41 | 0 | 0 | 0 | 0
2022091415 | 4 | 0.77953 | 62362.4 | 0 | 0 | 0.35543 | 12440.05 | 0.71637 | 10029.18 | 40000 | 0 | 12440.05 | 0 | 9922.35 | 106.83 | 106.83 | 0 | 0 | 0 | 0
2022091416 | 4 | 0.80209 | 64167.2 | 0 | 0 | 0.3698 | 12943 | 0.65659 | 9192.26 | 40000 | 0 | 12943 | 0 | 9192.26 | 0 | 0 | 2031.94 | 0 | 0 | 2031.94
2022091417 | 4 | 0.81561 | 65248.8 | 0 | 0 | 0.39661 | 13881.35 | 0.59242 | 8293.88 | 40000 | 0 | 13881.35 | 0 | 8293.88 | 0 | 0 | 3073.57 | 0 | 0 | 3073.57
2022091418 | 4 | 0.81086 | 64868.8 | 0 | 0 | 0.40292 | 14102.2 | 0.4538 | 6353.2 | 40000 | 0 | 14102.2 | 0 | 6353.2 | 0 | 0 | 4413.4 | 0 | 0 | 4413.4
2022091419 | 4 | 0.78211 | 62568.8 | 0 | 0 | 0.40607 | 14212.45 | 0.25505 | 3570.7 | 40000 | 0 | 14212.45 | 0 | 3570.7 | 0 | 0 | 4785.65 | 0 | 0 | 4785.65
2022091420 | 4 | 0.74708 | 59766.4 | 0 | 0 | 0.3751 | 13128.5 | 0.03694 | 517.16 | 40000 | 0 | 13128.5 | 0 | 517.16 | 0 | 0 | 6120.74 | 0 | 0 | 6120.74
2022091421 | 4 | 0.72514 | 58011.2 | 0 | 0 | 0.39126 | 13694.1 | 0 | 0 | 40000 | 0 | 13694.1 | 0 | 0 | 0 | 0 | 4317.1 | 0 | 0 | 4317.1
2022091422 | 4 | 0.68581 | 54864.8 | 0 | 0 | 0.43501 | 15225.35 | 0 | 0 | 40000 | 0 | 14864.8 | 360.55 | 0 | 0 | 360.55 | 0 | 0 | 0 | 0
2022091423 | 4 | 0.63701 | 50960.8 | 0 | 0 | 0.44074 | 15425.9 | 0 | 0 | 40000 | 0 | 10960.8 | 4465.1 | 0 | 0 | 4465.1 | 0 | 0 | 0 | 0
2022091424 | 4 | 0.58608 | 46886.4 | 0 | 0 | 0.43625 | 15268.75 | 0 | 0 | 40000 | 0 | 6886.4 | 8382.35 | 0 | 0 | 8382.35 | 0 | 0 | 0 | 0
2022091501 | 5 | 0.54659 | 43727.2 | 0 | 0 | 0.42229 | 14780.15 | 0 | 0 | 40000 | 0 | 3727.2 | 11052.95 | 0 | 0 | 11052.95 | 0 | 0 | 0 | 0
2022091502 | 5 | 0.51817 | 41453.6 | 0 | 0 | 0.40875 | 14306.25 | 0 | 0 | 40000 | 0 | 1453.6 | 12852.65 | 0 | 0 | 12852.65 | 0 | 0 | 0 | 0
2022091503 | 5 | 0.49907 | 39925.6 | 0 | 0 | 0.39639 | 13873.65 | 0 | 0 | 39925.6 | 74.4 | 0 | 13873.65 | 0 | 0 | 13948.05 | 0 | 0 | 0 | 0
2022091504 | 5 | 0.48826 | 39060.8 | 0 | 0 | 0.39366 | 13778.1 | 0 | 0 | 39060.8 | 939.2 | 0 | 13778.1 | 0 | 0 | 14717.3 | 0 | 0 | 0 | 0
2022091505 | 5 | 0.48351 | 38680.8 | 0 | 0 | 0.38211 | 13373.85 | 0 | 0 | 38680.8 | 1319.2 | 0 | 13373.85 | 0 | 0 | 14693.05 | 0 | 0 | 0 | 0
2022091506 | 5 | 0.49827 | 39861.6 | 0 | 0 | 0.3613 | 12645.5 | 0 | 0 | 39861.6 | 138.4 | 0 | 12645.5 | 0 | 0 | 12783.9 | 0 | 0 | 0 | 0
2022091507 | 5 | 0.52588 | 42070.4 | 0 | 0 | 0.34854 | 12198.9 | 0 | 0 | 40000 | 0 | 2070.4 | 10128.5 | 0 | 0 | 10128.5 | 0 | 0 | 0 | 0
2022091508 | 5 | 0.53395 | 42716 | 0 | 0 | 0.3562 | 12467 | 0.02535 | 354.9 | 40000 | 0 | 2716 | 9751 | 0 | 354.9 | 10105.9 | 0 | 0 | 0 | 0
2022091509 | 5 | 0.55014 | 44011.2 | 0 | 0 | 0.31331 | 10965.85 | 0.32409 | 4537.26 | 40000 | 0 | 4011.2 | 6954.65 | 0 | 4537.26 | 11491.91 | 0 | 0 | 0 | 0
2022091510 | 5 | 0.58255 | 46604 | 0 | 0 | 0.31564 | 11047.4 | 0.65486 | 9168.04 | 40000 | 0 | 6604 | 4443.4 | 0 | 9168.04 | 13611.44 | 0 | 0 | 0 | 0
2022091511 | 5 | 0.62217 | 49773.6 | 0 | 0 | 0.34571 | 12099.85 | 0.70533 | 9874.62 | 40000 | 0 | 9773.6 | 2326.25 | 0 | 9874.62 | 12200.87 | 0 | 0 | 0 | 0
2022091512 | 5 | 0.66372 | 53097.6 | 0 | 0 | 0.31052 | 10868.2 | 0.72637 | 10169.18 | 40000 | 0 | 10868.2 | 0 | 2229.4 | 7939.78 | 7939.78 | 0 | 0 | 0 | 0
2022091513 | 5 | 0.70353 | 56282.4 | 0 | 0 | 0.27434 | 9601.9 | 0.71398 | 9995.72 | 40000 | 0 | 9601.9 | 0 | 6680.5 | 3315.22 | 3315.22 | 0 | 0 | 0 | 0
2022091514 | 5 | 0.74233 | 59386.4 | 0 | 0 | 0.2657 | 9299.5 | 0.74359 | 10410.26 | 40000 | 0 | 9299.5 | 0 | 10086.9 | 323.36 | 323.36 | 0 | 0 | 0 | 0
2022091515 | 5 | 0.77206 | 61764.8 | 0 | 0 | 0.24694 | 8642.9 | 0.74755 | 10465.7 | 40000 | 0 | 8642.9 | 0 | 10465.7 | 0 | 0 | 2656.2 | 0 | 0 | 2656.2
2022091516 | 5 | 0.796 | 63680 | 0 | 0 | 0.25199 | 8819.65 | 0.74178 | 10384.92 | 40000 | 0 | 8819.65 | 0 | 10384.92 | 0 | 0 | 4475.43 | 0 | 0 | 4475.43
2022091517 | 5 | 0.81194 | 64955.2 | 0 | 0 | 0.2833 | 9915.5 | 0.71926 | 10069.64 | 40000 | 0 | 9915.5 | 0 | 10069.64 | 0 | 0 | 4970.06 | 0 | 0 | 4970.06
2022091518 | 5 | 0.80965 | 64772 | 0 | 0 | 0.33912 | 11869.2 | 0.66683 | 9335.62 | 40000 | 0 | 11869.2 | 0 | 9335.62 | 0 | 0 | 3567.18 | 0 | 0 | 3567.18
2022091519 | 5 | 0.78422 | 62737.6 | 0 | 0 | 0.37603 | 13161.05 | 0.42008 | 5881.12 | 40000 | 0 | 13161.05 | 0 | 5881.12 | 0 | 0 | 3695.43 | 0 | 0 | 3695.43
2022091520 | 5 | 0.7518 | 60144 | 0 | 0 | 0.37445 | 13105.75 | 0.05023 | 703.22 | 40000 | 0 | 13105.75 | 0 | 703.22 | 0 | 0 | 6335.03 | 0 | 0 | 6335.03
2022091521 | 5 | 0.73343 | 58674.4 | 0 | 0 | 0.39503 | 13826.05 | 0 | 0 | 40000 | 0 | 13826.05 | 0 | 0 | 0 | 0 | 4848.35 | 0 | 0 | 4848.35
2022091522 | 5 | 0.70035 | 56028 | 0 | 0 | 0.45476 | 15916.6 | 0 | 0 | 40000 | 0 | 15916.6 | 0 | 0 | 0 | 0 | 111.4 | 0 | 0 | 111.4
2022091523 | 5 | 0.65774 | 52619.2 | 0 | 0 | 0.50119 | 17541.65 | 0 | 0 | 40000 | 0 | 12619.2 | 4922.45 | 0 | 0 | 4922.45 | 0 | 0 | 0 | 0
2022091524 | 5 | 0.61222 | 48977.6 | 0 | 0 | 0.51701 | 18095.35 | 0 | 0 | 40000 | 0 | 8977.6 | 9117.75 | 0 | 0 | 9117.75 | 0 | 0 | 0 | 0
2022091601 | 6 | 0.57524 | 46019.2 | 0 | 0 | 0.51545 | 18040.75 | 0 | 0 | 40000 | 0 | 6019.2 | 12021.55 | 0 | 0 | 12021.55 | 0 | 0 | 0 | 0
2022091602 | 6 | 0.54707 | 43765.6 | 0 | 0 | 0.50417 | 17645.95 | 0 | 0 | 40000 | 0 | 3765.6 | 13880.35 | 0 | 0 | 13880.35 | 0 | 0 | 0 | 0
2022091603 | 6 | 0.52942 | 42353.6 | 0 | 0 | 0.49221 | 17227.35 | 0 | 0 | 40000 | 0 | 2353.6 | 14873.75 | 0 | 0 | 14873.75 | 0 | 0 | 0 | 0
2022091604 | 6 | 0.52025 | 41620 | 0 | 0 | 0.49349 | 17272.15 | 0 | 0 | 40000 | 0 | 1620 | 15652.15 | 0 | 0 | 15652.15 | 0 | 0 | 0 | 0
2022091605 | 6 | 0.51964 | 41571.2 | 0 | 0 | 0.47669 | 16684.15 | 0 | 0 | 40000 | 0 | 1571.2 | 15112.95 | 0 | 0 | 15112.95 | 0 | 0 | 0 | 0
2022091606 | 6 | 0.53608 | 42886.4 | 0 | 0 | 0.44592 | 15607.2 | 0 | 0 | 40000 | 0 | 2886.4 | 12720.8 | 0 | 0 | 12720.8 | 0 | 0 | 0 | 0
2022091607 | 6 | 0.5627 | 45016 | 0 | 0 | 0.41223 | 14428.05 | 0 | 0 | 40000 | 0 | 5016 | 9412.05 | 0 | 0 | 9412.05 | 0 | 0 | 0 | 0
2022091608 | 6 | 0.57266 | 45812.8 | 0 | 0 | 0.39569 | 13849.15 | 0.02111 | 295.54 | 40000 | 0 | 5812.8 | 8036.35 | 0 | 295.54 | 8331.89 | 0 | 0 | 0 | 0
2022091609 | 6 | 0.58926 | 47140.8 | 0 | 0 | 0.3204 | 11214 | 0.33659 | 4712.26 | 40000 | 0 | 7140.8 | 4073.2 | 0 | 4712.26 | 8785.46 | 0 | 0 | 0 | 0
2022091610 | 6 | 0.62688 | 50150.4 | 0 | 0 | 0.32351 | 11322.85 | 0.67059 | 9388.26 | 40000 | 0 | 10150.4 | 1172.45 | 0 | 9388.26 | 10560.71 | 0 | 0 | 0 | 0
2022091611 | 6 | 0.67391 | 53912.8 | 0 | 0 | 0.37972 | 13290.2 | 0.68652 | 9611.28 | 40000 | 0 | 13290.2 | 0 | 622.6 | 8988.68 | 8988.68 | 0 | 0 | 0 | 0
2022091612 | 6 | 0.71747 | 57397.6 | 0 | 0 | 0.34305 | 12006.75 | 0.73282 | 10259.48 | 40000 | 0 | 12006.75 | 0 | 5390.85 | 4868.63 | 4868.63 | 0 | 0 | 0 | 0
2022091613 | 6 | 0.757 | 60560 | 0 | 0 | 0.30933 | 10826.55 | 0.72674 | 10174.36 | 40000 | 0 | 10826.55 | 0 | 9733.45 | 440.91 | 440.91 | 0 | 0 | 0 | 0
2022091614 | 6 | 0.79571 | 63656.8 | 0 | 0 | 0.29195 | 10218.25 | 0.71546 | 10016.44 | 40000 | 0 | 10218.25 | 0 | 10016.44 | 0 | 0 | 3422.11 | 0 | 0 | 3422.11
2022091615 | 6 | 0.82013 | 65610.4 | 0 | 0 | 0.28665 | 10032.75 | 0.72417 | 10138.38 | 40000 | 0 | 10032.75 | 0 | 10138.38 | 0 | 0 | 5439.27 | 0 | 0 | 5439.27
2022091616 | 6 | 0.82963 | 66370.4 | 0 | 0 | 0.28558 | 9995.3 | 0.71444 | 10002.16 | 40000 | 0 | 9995.3 | 0 | 10002.16 | 0 | 0 | 6372.94 | 0 | 0 | 6372.94
2022091617 | 6 | 0.83502 | 66801.6 | 0 | 0 | 0.29398 | 10289.3 | 0.67882 | 9503.48 | 40000 | 0 | 10289.3 | 0 | 9503.48 | 0 | 0 | 7008.82 | 0 | 0 | 7008.82
2022091618 | 6 | 0.83284 | 66627.2 | 0 | 0 | 0.33072 | 11575.2 | 0.62345 | 8728.3 | 40000 | 0 | 11575.2 | 0 | 8728.3 | 0 | 0 | 6323.7 | 0 | 0 | 6323.7
2022091619 | 6 | 0.81032 | 64825.6 | 0 | 0 | 0.38093 | 13332.55 | 0.40543 | 5676.02 | 40000 | 0 | 13332.55 | 0 | 5676.02 | 0 | 0 | 5817.03 | 0 | 0 | 5817.03
2022091620 | 6 | 0.77774 | 62219.2 | 0 | 0 | 0.4064 | 14224 | 0.05422 | 759.08 | 40000 | 0 | 14224 | 0 | 759.08 | 0 | 0 | 7236.12 | 0 | 0 | 7236.12
2022091621 | 6 | 0.75537 | 60429.6 | 0 | 0 | 0.46411 | 16243.85 | 0 | 0 | 40000 | 0 | 16243.85 | 0 | 0 | 0 | 0 | 4185.75 | 0 | 0 | 4185.75
2022091622 | 6 | 0.72589 | 58071.2 | 0 | 0 | 0.52748 | 18461.8 | 0 | 0 | 40000 | 0 | 18071.2 | 390.6 | 0 | 0 | 390.6 | 0 | 0 | 0 | 0
2022091623 | 6 | 0.68898 | 55118.4 | 0 | 0 | 0.55567 | 19448.45 | 0 | 0 | 40000 | 0 | 15118.4 | 4330.05 | 0 | 0 | 4330.05 | 0 | 0 | 0 | 0
2022091624 | 6 | 0.65078 | 52062.4 | 0 | 0 | 0.56721 | 19852.35 | 0 | 0 | 40000 | 0 | 12062.4 | 7789.95 | 0 | 0 | 7789.95 | 0 | 0 | 0 | 0
2022091701 | 7 | 0.61426 | 49140.8 | 0 | 0 | 0.56215 | 19675.25 | 0 | 0 | 40000 | 0 | 9140.8 | 10534.45 | 0 | 0 | 10534.45 | 0 | 0 | 0 | 0
2022091702 | 7 | 0.58568 | 46854.4 | 0 | 0 | 0.55371 | 19379.85 | 0 | 0 | 40000 | 0 | 6854.4 | 12525.45 | 0 | 0 | 12525.45 | 0 | 0 | 0 | 0
2022091703 | 7 | 0.56459 | 45167.2 | 0 | 0 | 0.54844 | 19195.4 | 0 | 0 | 40000 | 0 | 5167.2 | 14028.2 | 0 | 0 | 14028.2 | 0 | 0 | 0 | 0
2022091704 | 7 | 0.54984 | 43987.2 | 0 | 0 | 0.52749 | 18462.15 | 0 | 0 | 40000 | 0 | 3987.2 | 14474.95 | 0 | 0 | 14474.95 | 0 | 0 | 0 | 0
2022091705 | 7 | 0.54098 | 43278.4 | 0 | 0 | 0.50673 | 17735.55 | 0 | 0 | 40000 | 0 | 3278.4 | 14457.15 | 0 | 0 | 14457.15 | 0 | 0 | 0 | 0
2022091706 | 7 | 0.54284 | 43427.2 | 0 | 0 | 0.48153 | 16853.55 | 0 | 0 | 40000 | 0 | 3427.2 | 13426.35 | 0 | 0 | 13426.35 | 0 | 0 | 0 | 0
2022091707 | 7 | 0.54677 | 43741.6 | 0 | 0 | 0.45788 | 16025.8 | 0 | 0 | 40000 | 0 | 3741.6 | 12284.2 | 0 | 0 | 12284.2 | 0 | 0 | 0 | 0
2022091708 | 7 | 0.55393 | 44314.4 | 0 | 0 | 0.43491 | 15221.85 | 0.01637 | 229.18 | 40000 | 0 | 4314.4 | 10907.45 | 0 | 229.18 | 11136.63 | 0 | 0 | 0 | 0
2022091709 | 7 | 0.58358 | 46686.4 | 0 | 0 | 0.3874 | 13559 | 0.30145 | 4220.3 | 40000 | 0 | 6686.4 | 6872.6 | 0 | 4220.3 | 11092.9 | 0 | 0 | 0 | 0
2022091710 | 7 | 0.63222 | 50577.6 | 0 | 0 | 0.42207 | 14772.45 | 0.53448 | 7482.72 | 40000 | 0 | 10577.6 | 4194.85 | 0 | 7482.72 | 11677.57 | 0 | 0 | 0 | 0
2022091711 | 7 | 0.67897 | 54317.6 | 0 | 0 | 0.48606 | 17012.1 | 0.4388 | 6143.2 | 40000 | 0 | 14317.6 | 2694.5 | 0 | 6143.2 | 8837.7 | 0 | 0 | 0 | 0
2022091712 | 7 | 0.72531 | 58024.8 | 0 | 0 | 0.47826 | 16739.1 | 0.49382 | 6913.48 | 40000 | 0 | 16739.1 | 0 | 1285.7 | 5627.78 | 5627.78 | 0 | 0 | 0 | 0
2022091713 | 7 | 0.76905 | 61524 | 0 | 0 | 0.44543 | 15590.05 | 0.60272 | 8438.08 | 40000 | 0 | 15590.05 | 0 | 5933.95 | 2504.13 | 2504.13 | 0 | 0 | 0 | 0
2022091714 | 7 | 0.80369 | 64295.2 | 0 | 0 | 0.42836 | 14992.6 | 0.67224 | 9411.36 | 40000 | 0 | 14992.6 | 0 | 9302.6 | 108.76 | 108.76 | 0 | 0 | 0 | 0
2022091715 | 7 | 0.82809 | 66247.2 | 0 | 0 | 0.42369 | 14829.15 | 0.69452 | 9723.28 | 40000 | 0 | 14829.15 | 0 | 9723.28 | 0 | 0 | 1694.77 | 0 | 0 | 1694.77
2022091716 | 7 | 0.84239 | 67391.2 | 0 | 0 | 0.41997 | 14698.95 | 0.70234 | 9832.76 | 40000 | 0 | 14698.95 | 0 | 9832.76 | 0 | 0 | 2859.49 | 0 | 0 | 2859.49
2022091717 | 7 | 0.84664 | 67731.2 | 0 | 0 | 0.41611 | 14563.85 | 0.70706 | 9898.84 | 40000 | 0 | 14563.85 | 0 | 9898.84 | 0 | 0 | 3268.51 | 0 | 0 | 3268.51
2022091718 | 7 | 0.84051 | 67240.8 | 0 | 0 | 0.42678 | 14937.3 | 0.66135 | 9258.9 | 40000 | 0 | 14937.3 | 0 | 9258.9 | 0 | 0 | 3044.6 | 0 | 0 | 3044.6
2022091719 | 7 | 0.81927 | 65541.6 | 0 | 0 | 0.44426 | 15549.1 | 0.41057 | 5747.98 | 40000 | 0 | 15549.1 | 0 | 5747.98 | 0 | 0 | 4244.52 | 0 | 0 | 4244.52
2022091720 | 7 | 0.78387 | 62709.6 | 0 | 0 | 0.43036 | 15062.6 | 0.05294 | 741.16 | 40000 | 0 | 15062.6 | 0 | 741.16 | 0 | 0 | 6905.84 | 0 | 0 | 6905.84
2022091721 | 7 | 0.75928 | 60742.4 | 0 | 0 | 0.4304 | 15064 | 0 | 0 | 40000 | 0 | 15064 | 0 | 0 | 0 | 0 | 5678.4 | 0 | 0 | 5678.4
2022091722 | 7 | 0.72705 | 58164 | 0 | 0 | 0.47766 | 16718.1 | 0 | 0 | 40000 | 0 | 16718.1 | 0 | 0 | 0 | 0 | 1445.9 | 0 | 0 | 1445.9
2022091723 | 7 | 0.68987 | 55189.6 | 0 | 0 | 0.49892 | 17462.2 | 0 | 0 | 40000 | 0 | 15189.6 | 2272.6 | 0 | 0 | 2272.6 | 0 | 0 | 0 | 0
2022091724 | 7 | 0.65137 | 52109.6 | 0 | 0 | 0.49885 | 17459.75 | 0 | 0 | 40000 | 0 | 12109.6 | 5350.15 | 0 | 0 | 5350.15 | 0 | 0 | 0 | 0
2022091801 | 1 | 0.61604 | 49283.2 | 0 | 0 | 0.49758 | 17415.3 | 0 | 0 | 40000 | 0 | 9283.2 | 8132.1 | 0 | 0 | 8132.1 | 0 | 0 | 0 | 0
2022091802 | 1 | 0.58639 | 46911.2 | 0 | 0 | 0.48582 | 17003.7 | 0 | 0 | 40000 | 0 | 6911.2 | 10092.5 | 0 | 0 | 10092.5 | 0 | 0 | 0 | 0
2022091803 | 1 | 0.56047 | 44837.6 | 0 | 0 | 0.46443 | 16255.05 | 0 | 0 | 40000 | 0 | 4837.6 | 11417.45 | 0 | 0 | 11417.45 | 0 | 0 | 0 | 0
2022091804 | 1 | 0.54445 | 43556 | 0 | 0 | 0.45386 | 15885.1 | 0 | 0 | 40000 | 0 | 3556 | 12329.1 | 0 | 0 | 12329.1 | 0 | 0 | 0 | 0
2022091805 | 1 | 0.53441 | 42752.8 | 0 | 0 | 0.44405 | 15541.75 | 0 | 0 | 40000 | 0 | 2752.8 | 12788.95 | 0 | 0 | 12788.95 | 0 | 0 | 0 | 0
2022091806 | 1 | 0.53288 | 42630.4 | 0 | 0 | 0.44009 | 15403.15 | 0 | 0 | 40000 | 0 | 2630.4 | 12772.75 | 0 | 0 | 12772.75 | 0 | 0 | 0 | 0
2022091807 | 1 | 0.53054 | 42443.2 | 0 | 0 | 0.43655 | 15279.25 | 0 | 0 | 40000 | 0 | 2443.2 | 12836.05 | 0 | 0 | 12836.05 | 0 | 0 | 0 | 0
2022091808 | 1 | 0.53294 | 42635.2 | 0 | 0 | 0.41394 | 14487.9 | 0.02207 | 308.98 | 40000 | 0 | 2635.2 | 11852.7 | 0 | 308.98 | 12161.68 | 0 | 0 | 0 | 0
2022091809 | 1 | 0.5636 | 45088 | 0 | 0 | 0.36084 | 12629.4 | 0.32649 | 4570.86 | 40000 | 0 | 5088 | 7541.4 | 0 | 4570.86 | 12112.26 | 0 | 0 | 0 | 0
2022091810 | 1 | 0.6183 | 49464 | 0 | 0 | 0.38577 | 13501.95 | 0.50614 | 7085.96 | 40000 | 0 | 9464 | 4037.95 | 0 | 7085.96 | 11123.91 | 0 | 0 | 0 | 0
2022091811 | 1 | 0.66793 | 53434.4 | 0 | 0 | 0.39194 | 13717.9 | 0.46264 | 6476.96 | 40000 | 0 | 13434.4 | 283.5 | 0 | 6476.96 | 6760.46 | 0 | 0 | 0 | 0
2022091812 | 1 | 0.71731 | 57384.8 | 0 | 0 | 0.35183 | 12314.05 | 0.57065 | 7989.1 | 40000 | 0 | 12314.05 | 0 | 5070.75 | 2918.35 | 2918.35 | 0 | 0 | 0 | 0
2022091813 | 1 | 0.76543 | 61234.4 | 0 | 0 | 0.31409 | 10993.15 | 0.65695 | 9197.3 | 40000 | 0 | 10993.15 | 0 | 9197.3 | 0 | 0 | 1043.95 | 0 | 0 | 1043.95
2022091814 | 1 | 0.80511 | 64408.8 | 0 | 0 | 0.28499 | 9974.65 | 0.72837 | 10197.18 | 40000 | 0 | 9974.65 | 0 | 10197.18 | 0 | 0 | 4236.97 | 0 | 0 | 4236.97
2022091815 | 1 | 0.83555 | 66844 | 0 | 0 | 0.26609 | 9313.15 | 0.73661 | 10312.54 | 40000 | 0 | 9313.15 | 0 | 10312.54 | 0 | 0 | 7218.31 | 0 | 0 | 7218.31
2022091816 | 1 | 0.8501 | 68008 | 0 | 0 | 0.25801 | 9030.35 | 0.74578 | 10440.92 | 40000 | 0 | 9030.35 | 0 | 10440.92 | 0 | 0 | 8536.73 | 0 | 0 | 8536.73
2022091817 | 1 | 0.85981 | 68784.8 | 0 | 0 | 0.27796 | 9728.6 | 0.72568 | 10159.52 | 40000 | 0 | 9728.6 | 0 | 10159.52 | 0 | 0 | 8896.68 | 0 | 0 | 8896.68
2022091818 | 1 | 0.85875 | 68700 | 0 | 0 | 0.30981 | 10843.35 | 0.65756 | 9205.84 | 40000 | 0 | 10843.35 | 0 | 9205.84 | 0 | 0 | 8650.81 | 0 | 0 | 8650.81
2022091819 | 1 | 0.84255 | 67404 | 0 | 0 | 0.35027 | 12259.45 | 0.40969 | 5735.66 | 40000 | 0 | 12259.45 | 0 | 5735.66 | 0 | 0 | 9408.89 | 0 | 0 | 9408.89
2022091820 | 1 | 0.81438 | 65150.4 | 0 | 0 | 0.38549 | 13492.15 | 0.04351 | 609.14 | 40000 | 0 | 13492.15 | 0 | 609.14 | 0 | 0 | 11049.11 | 0 | 0 | 11049.11
2022091821 | 1 | 0.79119 | 63295.2 | 0 | 0 | 0.41999 | 14699.65 | 0 | 0 | 40000 | 0 | 14699.65 | 0 | 0 | 0 | 0 | 8595.55 | 0 | 0 | 8595.55
2022091822 | 1 | 0.75593 | 60474.4 | 0 | 0 | 0.46252 | 16188.2 | 0 | 0 | 40000 | 0 | 16188.2 | 0 | 0 | 0 | 0 | 4286.2 | 0 | 0 | 4286.2
2022091823 | 1 | 0.70708 | 56566.4 | 0 | 0 | 0.47205 | 16521.75 | 0 | 0 | 40000 | 0 | 16521.75 | 0 | 0 | 0 | 0 | 44.65 | 0 | 0 | 44.65
2022091824 | 1 | 0.65637 | 52509.6 | 0 | 0 | 0.46431 | 16250.85 | 0 | 0 | 40000 | 0 | 12509.6 | 3741.25 | 0 | 0 | 3741.25 | 0 | 0 | 0 | 0
2022091901 | 2 | 0.61254 | 49003.2 | 0 | 0 | 0.44487 | 15570.45 | 0 | 0 | 40000 | 0 | 9003.2 | 6567.25 | 0 | 0 | 6567.25 | 0 | 0 | 0 | 0
2022091902 | 2 | 0.58164 | 46531.2 | 0 | 0 | 0.4313 | 15095.5 | 0 | 0 | 40000 | 0 | 6531.2 | 8564.3 | 0 | 0 | 8564.3 | 0 | 0 | 0 | 0
2022091903 | 2 | 0.5609 | 44872 | 0 | 0 | 0.41832 | 14641.2 | 0 | 0 | 40000 | 0 | 4872 | 9769.2 | 0 | 0 | 9769.2 | 0 | 0 | 0 | 0
2022091904 | 2 | 0.55069 | 44055.2 | 0 | 0 | 0.41369 | 14479.15 | 0 | 0 | 40000 | 0 | 4055.2 | 10423.95 | 0 | 0 | 10423.95 | 0 | 0 | 0 | 0
2022091905 | 2 | 0.5495 | 43960 | 0 | 0 | 0.38679 | 13537.65 | 0 | 0 | 40000 | 0 | 3960 | 9577.65 | 0 | 0 | 9577.65 | 0 | 0 | 0 | 0
2022091906 | 2 | 0.56584 | 45267.2 | 0 | 0 | 0.33944 | 11880.4 | 0 | 0 | 40000 | 0 | 5267.2 | 6613.2 | 0 | 0 | 6613.2 | 0 | 0 | 0 | 0
2022091907 | 2 | 0.58957 | 47165.6 | 0 | 0 | 0.30128 | 10544.8 | 0 | 0 | 40000 | 0 | 7165.6 | 3379.2 | 0 | 0 | 3379.2 | 0 | 0 | 0 | 0
2022091908 | 2 | 0.59716 | 47772.8 | 0 | 0 | 0.26218 | 9176.3 | 0.02023 | 283.22 | 40000 | 0 | 7772.8 | 1403.5 | 0 | 283.22 | 1686.72 | 0 | 0 | 0 | 0
2022091909 | 2 | 0.61773 | 49418.4 | 0 | 0 | 0.20368 | 7128.8 | 0.29056 | 4067.84 | 40000 | 0 | 7128.8 | 0 | 2289.6 | 1778.24 | 1778.24 | 0 | 0 | 0 | 0
2022091910 | 2 | 0.66215 | 52972 | 0 | 0 | 0.19853 | 6948.55 | 0.56385 | 7893.9 | 40000 | 0 | 6948.55 | 0 | 6023.45 | 1870.45 | 1870.45 | 0 | 0 | 0 | 0
2022091911 | 2 | 0.71406 | 57124.8 | 0 | 0 | 0.22714 | 7949.9 | 0.65886 | 9224.04 | 40000 | 0 | 7949.9 | 0 | 9174.9 | 49.14 | 49.14 | 0 | 0 | 0 | 0
2022091912 | 2 | 0.76437 | 61149.6 | 0 | 0 | 0.20348 | 7121.8 | 0.69857 | 9779.98 | 40000 | 0 | 7121.8 | 0 | 9779.98 | 0 | 0 | 4247.82 | 0 | 0 | 4247.82
2022091913 | 2 | 0.80651 | 64520.8 | 0 | 0 | 0.19971 | 6989.85 | 0.68234 | 9552.76 | 40000 | 0 | 6989.85 | 0 | 9552.76 | 0 | 0 | 7978.19 | 0 | 0 | 7978.19
2022091914 | 2 | 0.85013 | 68010.4 | 0 | 0 | 0.21786 | 7625.1 | 0.66046 | 9246.44 | 40000 | 0 | 7625.1 | 0 | 9246.44 | 0 | 0 | 11138.86 | 0 | 0 | 11138.86
2022091915 | 2 | 0.86745 | 69396 | 0 | 0 | 0.22468 | 7863.8 | 0.67849 | 9498.86 | 40000 | 0 | 7863.8 | 0 | 9498.86 | 0 | 0 | 12033.34 | 0 | 0 | 12033.34
2022091916 | 2 | 0.8736 | 69888 | 0 | 0 | 0.23116 | 8090.6 | 0.66657 | 9331.98 | 40000 | 0 | 8090.6 | 0 | 9331.98 | 0 | 0 | 12465.42 | 0 | 0 | 12465.42
2022091917 | 2 | 0.87918 | 70334.4 | 0 | 0 | 0.24396 | 8538.6 | 0.65375 | 9152.5 | 40000 | 0 | 8538.6 | 0 | 9152.5 | 0 | 0 | 12643.3 | 0 | 0 | 12643.3
2022091918 | 2 | 0.87492 | 69993.6 | 0 | 0 | 0.27019 | 9456.65 | 0.61254 | 8575.56 | 40000 | 0 | 9456.65 | 0 | 8575.56 | 0 | 0 | 11961.39 | 0 | 0 | 11961.39
2022091919 | 2 | 0.86163 | 68930.4 | 0 | 0 | 0.27995 | 9798.25 | 0.35782 | 5009.48 | 40000 | 0 | 9798.25 | 0 | 5009.48 | 0 | 0 | 14122.67 | 0 | 0 | 14122.67
2022091920 | 2 | 0.83345 | 66676 | 0 | 0 | 0.25973 | 9090.55 | 0.03477 | 486.78 | 40000 | 0 | 9090.55 | 0 | 486.78 | 0 | 0 | 17098.67 | 0 | 0 | 17098.67
2022091921 | 2 | 0.81098 | 64878.4 | 0 | 0 | 0.29835 | 10442.25 | 0 | 0 | 40000 | 0 | 10442.25 | 0 | 0 | 0 | 0 | 14436.15 | 0 | 0 | 14436.15
2022091922 | 2 | 0.76998 | 61598.4 | 0 | 0 | 0.36228 | 12679.8 | 0 | 0 | 40000 | 0 | 12679.8 | 0 | 0 | 0 | 0 | 8918.6 | 0 | 0 | 8918.6
2022091923 | 2 | 0.71692 | 57353.6 | 0 | 0 | 0.40801 | 14280.35 | 0 | 0 | 40000 | 0 | 14280.35 | 0 | 0 | 0 | 0 | 3073.25 | 0 | 0 | 3073.25
2022091924 | 2 | 0.66543 | 53234.4 | 0 | 0 | 0.42435 | 14852.25 | 0 | 0 | 40000 | 0 | 13234.4 | 1617.85 | 0 | 0 | 1617.85 | 0 | 0 | 0 | 0
2022092001 | 3 | 0.62346 | 49876.8 | 0 | 0 | 0.42115 | 14740.25 | 0 | 0 | 40000 | 0 | 9876.8 | 4863.45 | 0 | 0 | 4863.45 | 0 | 0 | 0 | 0
2022092002 | 3 | 0.5927 | 47416 | 0 | 0 | 0.40698 | 14244.3 | 0 | 0 | 40000 | 0 | 7416 | 6828.3 | 0 | 0 | 6828.3 | 0 | 0 | 0 | 0
2022092003 | 3 | 0.57089 | 45671.2 | 0 | 0 | 0.37308 | 13057.8 | 0 | 0 | 40000 | 0 | 5671.2 | 7386.6 | 0 | 0 | 7386.6 | 0 | 0 | 0 | 0
2022092004 | 3 | 0.55762 | 44609.6 | 0 | 0 | 0.35117 | 12290.95 | 0 | 0 | 40000 | 0 | 4609.6 | 7681.35 | 0 | 0 | 7681.35 | 0 | 0 | 0 | 0
2022092005 | 3 | 0.55575 | 44460 | 0 | 0 | 0.33172 | 11610.2 | 0 | 0 | 40000 | 0 | 4460 | 7150.2 | 0 | 0 | 7150.2 | 0 | 0 | 0 | 0
2022092006 | 3 | 0.57263 | 45810.4 | 0 | 0 | 0.31414 | 10994.9 | 0 | 0 | 40000 | 0 | 5810.4 | 5184.5 | 0 | 0 | 5184.5 | 0 | 0 | 0 | 0
2022092007 | 3 | 0.59762 | 47809.6 | 0 | 0 | 0.31313 | 10959.55 | 0 | 0 | 40000 | 0 | 7809.6 | 3149.95 | 0 | 0 | 3149.95 | 0 | 0 | 0 | 0
2022092008 | 3 | 0.60439 | 48351.2 | 0 | 0 | 0.29885 | 10459.75 | 0.01997 | 279.58 | 40000 | 0 | 8351.2 | 2108.55 | 0 | 279.58 | 2388.13 | 0 | 0 | 0 | 0
2022092009 | 3 | 0.62324 | 49859.2 | 0 | 0 | 0.24236 | 8482.6 | 0.32875 | 4602.5 | 40000 | 0 | 8482.6 | 0 | 1376.6 | 3225.9 | 3225.9 | 0 | 0 | 0 | 0
2022092010 | 3 | 0.66987 | 53589.6 | 0 | 0 | 0.21777 | 7621.95 | 0.67384 | 9433.76 | 40000 | 0 | 7621.95 | 0 | 5967.65 | 3466.11 | 3466.11 | 0 | 0 | 0 | 0
2022092011 | 3 | 0.72294 | 57835.2 | 0 | 0 | 0.22404 | 7841.4 | 0.73583 | 10301.62 | 40000 | 0 | 7841.4 | 0 | 9993.8 | 307.82 | 307.82 | 0 | 0 | 0 | 0
2022092012 | 3 | 0.76868 | 61494.4 | 0 | 0 | 0.2093 | 7325.5 | 0.74888 | 10484.32 | 40000 | 0 | 7325.5 | 0 | 10484.32 | 0 | 0 | 3684.58 | 0 | 0 | 3684.58
2022092013 | 3 | 0.81432 | 65145.6 | 0 | 0 | 0.20885 | 7309.75 | 0.71916 | 10068.24 | 40000 | 0 | 7309.75 | 0 | 10068.24 | 0 | 0 | 7767.61 | 0 | 0 | 7767.61
2022092014 | 3 | 0.8557 | 68456 | 0 | 0 | 0.19947 | 6981.45 | 0.70956 | 9933.84 | 40000 | 0 | 6981.45 | 0 | 9933.84 | 0 | 0 | 11540.71 | 0 | 0 | 11540.71
2022092015 | 3 | 0.87852 | 70281.6 | 0 | 0 | 0.20028 | 7009.8 | 0.70381 | 9853.34 | 40000 | 0 | 7009.8 | 0 | 9853.34 | 0 | 0 | 13418.46 | 0 | 0 | 13418.46
2022092016 | 3 | 0.88301 | 70640.8 | 0 | 0 | 0.21026 | 7359.1 | 0.68795 | 9631.3 | 40000 | 0 | 7359.1 | 0 | 9631.3 | 0 | 0 | 13650.4 | 0 | 0 | 13650.4
2022092017 | 3 | 0.88924 | 71139.2 | 0 | 0 | 0.22331 | 7815.85 | 0.67081 | 9391.34 | 40000 | 0 | 7815.85 | 0 | 9391.34 | 0 | 0 | 13932.01 | 0 | 0 | 13932.01
2022092018 | 3 | 0.88522 | 70817.6 | 0 | 0 | 0.24146 | 8451.1 | 0.62352 | 8729.28 | 40000 | 0 | 8451.1 | 0 | 8729.28 | 0 | 0 | 13637.22 | 0 | 0 | 13637.22
2022092019 | 3 | 0.86916 | 69532.8 | 0 | 0 | 0.24954 | 8733.9 | 0.35996 | 5039.44 | 40000 | 0 | 8733.9 | 0 | 5039.44 | 0 | 0 | 15759.46 | 0 | 0 | 15759.46
2022092020 | 3 | 0.83843 | 67074.4 | 0 | 0 | 0.2455 | 8592.5 | 0.04025 | 563.5 | 40000 | 0 | 8592.5 | 0 | 563.5 | 0 | 0 | 17918.4 | 0 | 0 | 17918.4
2022092021 | 3 | 0.81095 | 64876 | 0 | 0 | 0.28818 | 10086.3 | 0 | 0 | 40000 | 0 | 10086.3 | 0 | 0 | 0 | 0 | 14789.7 | 0 | 0 | 14789.7
2022092022 | 3 | 0.76823 | 61458.4 | 0 | 0 | 0.36196 | 12668.6 | 0 | 0 | 40000 | 0 | 12668.6 | 0 | 0 | 0 | 0 | 8789.8 | 0 | 0 | 8789.8
2022092023 | 3 | 0.71354 | 57083.2 | 0 | 0 | 0.40256 | 14089.6 | 0 | 0 | 40000 | 0 | 14089.6 | 0 | 0 | 0 | 0 | 2993.6 | 0 | 0 | 2993.6
2022092024 | 3 | 0.66228 | 52982.4 | 0 | 0 | 0.41117 | 14390.95 | 0 | 0 | 40000 | 0 | 12982.4 | 1408.55 | 0 | 0 | 1408.55 | 0 | 0 | 0 | 0
2022092101 | 4 | 0.61625 | 49300 | 0 | 0 | 0.39845 | 13945.75 | 0 | 0 | 40000 | 0 | 9300 | 4645.75 | 0 | 0 | 4645.75 | 0 | 0 | 0 | 0
2022092102 | 4 | 0.58319 | 46655.2 | 0 | 0 | 0.38063 | 13322.05 | 0 | 0 | 40000 | 0 | 6655.2 | 6666.85 | 0 | 0 | 6666.85 | 0 | 0 | 0 | 0
2022092103 | 4 | 0.56289 | 45031.2 | 0 | 0 | 0.36386 | 12735.1 | 0 | 0 | 40000 | 0 | 5031.2 | 7703.9 | 0 | 0 | 7703.9 | 0 | 0 | 0 | 0
2022092104 | 4 | 0.5485 | 43880 | 0 | 0 | 0.35955 | 12584.25 | 0 | 0 | 40000 | 0 | 3880 | 8704.25 | 0 | 0 | 8704.25 | 0 | 0 | 0 | 0
2022092105 | 4 | 0.54532 | 43625.6 | 0 | 0 | 0.36319 | 12711.65 | 0 | 0 | 40000 | 0 | 3625.6 | 9086.05 | 0 | 0 | 9086.05 | 0 | 0 | 0 | 0
2022092106 | 4 | 0.55669 | 44535.2 | 0 | 0 | 0.34828 | 12189.8 | 0 | 0 | 40000 | 0 | 4535.2 | 7654.6 | 0 | 0 | 7654.6 | 0 | 0 | 0 | 0
2022092107 | 4 | 0.57979 | 46383.2 | 0 | 0 | 0.32045 | 11215.75 | 0 | 0 | 40000 | 0 | 6383.2 | 4832.55 | 0 | 0 | 4832.55 | 0 | 0 | 0 | 0
2022092108 | 4 | 0.58519 | 46815.2 | 0 | 0 | 0.28673 | 10035.55 | 0.02085 | 291.9 | 40000 | 0 | 6815.2 | 3220.35 | 0 | 291.9 | 3512.25 | 0 | 0 | 0 | 0
2022092109 | 4 | 0.60398 | 48318.4 | 0 | 0 | 0.21882 | 7658.7 | 0.36153 | 5061.42 | 40000 | 0 | 7658.7 | 0 | 659.7 | 4401.72 | 4401.72 | 0 | 0 | 0 | 0
2022092110 | 4 | 0.64718 | 51774.4 | 0 | 0 | 0.17594 | 6157.9 | 0.72185 | 10105.9 | 40000 | 0 | 6157.9 | 0 | 5616.5 | 4489.4 | 4489.4 | 0 | 0 | 0 | 0
2022092111 | 4 | 0.7003 | 56024 | 0 | 0 | 0.19727 | 6904.45 | 0.78187 | 10946.18 | 40000 | 0 | 6904.45 | 0 | 9119.55 | 1826.63 | 1826.63 | 0 | 0 | 0 | 0
2022092112 | 4 | 0.75275 | 60220 | 0 | 0 | 0.17528 | 6134.8 | 0.77933 | 10910.62 | 40000 | 0 | 6134.8 | 0 | 10910.62 | 0 | 0 | 3174.58 | 0 | 0 | 3174.58
2022092113 | 4 | 0.8007 | 64056 | 0 | 0 | 0.16906 | 5917.1 | 0.75545 | 10576.3 | 40000 | 0 | 5917.1 | 0 | 10576.3 | 0 | 0 | 7562.6 | 0 | 0 | 7562.6
2022092114 | 4 | 0.84573 | 67658.4 | 0 | 0 | 0.16941 | 5929.35 | 0.75833 | 10616.62 | 40000 | 0 | 5929.35 | 0 | 10616.62 | 0 | 0 | 11112.43 | 0 | 0 | 11112.43
2022092115 | 4 | 0.87303 | 69842.4 | 0 | 0 | 0.14979 | 5242.65 | 0.756 | 10584 | 40000 | 0 | 5242.65 | 0 | 10584 | 0 | 0 | 14015.75 | 0 | 0 | 14015.75
2022092116 | 4 | 0.88088 | 70470.4 | 0 | 0 | 0.13769 | 4819.15 | 0.76017 | 10642.38 | 40000 | 0 | 4819.15 | 0 | 10642.38 | 0 | 0 | 15008.87 | 0 | 0 | 15008.87
2022092117 | 4 | 0.88516 | 70812.8 | 0 | 0 | 0.13371 | 4679.85 | 0.75309 | 10543.26 | 40000 | 0 | 4679.85 | 0 | 10543.26 | 0 | 0 | 15589.69 | 0 | 0 | 15589.69
2022092118 | 4 | 0.88341 | 70672.8 | 0 | 0 | 0.13939 | 4878.65 | 0.70047 | 9806.58 | 40000 | 0 | 4878.65 | 0 | 9806.58 | 0 | 0 | 15987.57 | 0 | 0 | 15987.57
2022092119 | 4 | 0.86591 | 69272.8 | 0 | 0 | 0.14612 | 5114.2 | 0.39879 | 5583.06 | 40000 | 0 | 5114.2 | 0 | 5583.06 | 0 | 0 | 18575.54 | 0 | 0 | 18575.54
2022092120 | 4 | 0.83173 | 66538.4 | 0 | 0 | 0.15493 | 5422.55 | 0.03958 | 554.12 | 40000 | 0 | 5422.55 | 0 | 554.12 | 0 | 0 | 20561.73 | 0 | 0 | 20561.73
2022092121 | 4 | 0.79922 | 63937.6 | 0 | 0 | 0.21195 | 7418.25 | 0 | 0 | 40000 | 0 | 7418.25 | 0 | 0 | 0 | 0 | 16519.35 | 0 | 0 | 16519.35
2022092122 | 4 | 0.7539 | 60312 | 0 | 0 | 0.28542 | 9989.7 | 0 | 0 | 40000 | 0 | 9989.7 | 0 | 0 | 0 | 0 | 10322.3 | 0 | 0 | 10322.3
2022092123 | 4 | 0.69674 | 55739.2 | 0 | 0 | 0.34326 | 12014.1 | 0 | 0 | 40000 | 0 | 12014.1 | 0 | 0 | 0 | 0 | 3725.1 | 0 | 0 | 3725.1
2022092124 | 4 | 0.64345 | 51476 | 0 | 0 | 0.38176 | 13361.6 | 0 | 0 | 40000 | 0 | 11476 | 1885.6 | 0 | 0 | 1885.6 | 0 | 0 | 0 | 0
2022092201 | 5 | 0.59971 | 47976.8 | 0 | 0 | 0.38428 | 13449.8 | 0 | 0 | 40000 | 0 | 7976.8 | 5473 | 0 | 0 | 5473 | 0 | 0 | 0 | 0
2022092202 | 5 | 0.56545 | 45236 | 0 | 0 | 0.36459 | 12760.65 | 0 | 0 | 40000 | 0 | 5236 | 7524.65 | 0 | 0 | 7524.65 | 0 | 0 | 0 | 0
2022092203 | 5 | 0.54259 | 43407.2 | 0 | 0 | 0.32851 | 11497.85 | 0 | 0 | 40000 | 0 | 3407.2 | 8090.65 | 0 | 0 | 8090.65 | 0 | 0 | 0 | 0
2022092204 | 5 | 0.52833 | 42266.4 | 0 | 0 | 0.30827 | 10789.45 | 0 | 0 | 40000 | 0 | 2266.4 | 8523.05 | 0 | 0 | 8523.05 | 0 | 0 | 0 | 0
2022092205 | 5 | 0.52456 | 41964.8 | 0 | 0 | 0.28499 | 9974.65 | 0 | 0 | 40000 | 0 | 1964.8 | 8009.85 | 0 | 0 | 8009.85 | 0 | 0 | 0 | 0
2022092206 | 5 | 0.53694 | 42955.2 | 0 | 0 | 0.24714 | 8649.9 | 0 | 0 | 40000 | 0 | 2955.2 | 5694.7 | 0 | 0 | 5694.7 | 0 | 0 | 0 | 0
2022092207 | 5 | 0.56178 | 44942.4 | 0 | 0 | 0.21257 | 7439.95 | 0 | 0 | 40000 | 0 | 4942.4 | 2497.55 | 0 | 0 | 2497.55 | 0 | 0 | 0 | 0
2022092208 | 5 | 0.56826 | 45460.8 | 0 | 0 | 0.19479 | 6817.65 | 0.01915 | 268.1 | 40000 | 0 | 5460.8 | 1356.85 | 0 | 268.1 | 1624.95 | 0 | 0 | 0 | 0
2022092209 | 5 | 0.58581 | 46864.8 | 0 | 0 | 0.1511 | 5288.5 | 0.34621 | 4846.94 | 40000 | 0 | 5288.5 | 0 | 1576.3 | 3270.64 | 3270.64 | 0 | 0 | 0 | 0
2022092210 | 5 | 0.63113 | 50490.4 | 0 | 0 | 0.10106 | 3537.1 | 0.72392 | 10134.88 | 40000 | 0 | 3537.1 | 0 | 6953.3 | 3181.58 | 3181.58 | 0 | 0 | 0 | 0
2022092211 | 5 | 0.68425 | 54740 | 0 | 0 | 0.07082 | 2478.7 | 0.78163 | 10942.82 | 40000 | 0 | 2478.7 | 0 | 10942.82 | 0 | 0 | 1318.48 | 0 | 0 | 1318.48
2022092212 | 5 | 0.73969 | 59175.2 | 0 | 0 | 0.0538 | 1883 | 0.789 | 11046 | 40000 | 0 | 1883 | 0 | 11046 | 0 | 0 | 6246.2 | 0 | 0 | 6246.2
2022092213 | 5 | 0.79401 | 63520.8 | 0 | 0 | 0.04682 | 1638.7 | 0.78535 | 10994.9 | 40000 | 0 | 1638.7 | 0 | 10994.9 | 0 | 0 | 10887.2 | 0 | 0 | 10887.2
2022092214 | 5 | 0.84135 | 67308 | 0 | 0 | 0.05084 | 1779.4 | 0.76798 | 10751.72 | 40000 | 0 | 1779.4 | 0 | 10751.72 | 0 | 0 | 14776.88 | 0 | 0 | 14776.88
2022092215 | 5 | 0.87196 | 69756.8 | 0 | 0 | 0.05431 | 1900.85 | 0.76122 | 10657.08 | 40000 | 0 | 1900.85 | 0 | 10657.08 | 0 | 0 | 17198.87 | 0 | 0 | 17198.87
2022092216 | 5 | 0.87958 | 70366.4 | 0 | 0 | 0.05063 | 1772.05 | 0.7546 | 10564.4 | 40000 | 0 | 1772.05 | 0 | 10564.4 | 0 | 0 | 18029.95 | 0 | 0 | 18029.95
2022092217 | 5 | 0.88316 | 70652.8 | 0 | 0 | 0.05651 | 1977.85 | 0.75249 | 10534.86 | 40000 | 0 | 1977.85 | 0 | 10534.86 | 0 | 0 | 18140.09 | 0 | 0 | 18140.09
2022092218 | 5 | 0.87881 | 70304.8 | 0 | 0 | 0.07265 | 2542.75 | 0.66901 | 9366.14 | 40000 | 0 | 2542.75 | 0 | 9366.14 | 0 | 0 | 18395.91 | 0 | 0 | 18395.91
2022092219 | 5 | 0.85677 | 68541.6 | 0 | 0 | 0.08581 | 3003.35 | 0.37294 | 5221.16 | 40000 | 0 | 3003.35 | 0 | 5221.16 | 0 | 0 | 20317.09 | 0 | 0 | 20317.09
2022092220 | 5 | 0.82148 | 65718.4 | 0 | 0 | 0.11782 | 4123.7 | 0.03631 | 508.34 | 40000 | 0 | 4123.7 | 0 | 508.34 | 0 | 0 | 21086.36 | 0 | 0 | 21086.36
2022092221 | 5 | 0.78629 | 62903.2 | 0 | 0 | 0.16957 | 5934.95 | 8e-05 | 1.12 | 40000 | 0 | 5934.95 | 0 | 1.12 | 0 | 0 | 16967.13 | 0 | 0 | 16967.13
2022092222 | 5 | 0.74144 | 59315.2 | 0 | 0 | 0.2209 | 7731.5 | 0 | 0 | 40000 | 0 | 7731.5 | 0 | 0 | 0 | 0 | 11583.7 | 0 | 0 | 11583.7
2022092223 | 5 | 0.68862 | 55089.6 | 0 | 0 | 0.23839 | 8343.65 | 0 | 0 | 40000 | 0 | 8343.65 | 0 | 0 | 0 | 0 | 6745.95 | 0 | 0 | 6745.95
2022092224 | 5 | 0.63698 | 50958.4 | 0 | 0 | 0.23646 | 8276.1 | 0 | 0 | 40000 | 0 | 8276.1 | 0 | 0 | 0 | 0 | 2682.3 | 0 | 0 | 2682.3
2022092301 | 6 | 0.59396 | 47516.8 | 0 | 0 | 0.21383 | 7484.05 | 4e-05 | 0.56 | 40000 | 0 | 7484.05 | 0 | 0.56 | 0 | 0 | 32.19 | 0 | 0 | 32.19
2022092302 | 6 | 0.5617 | 44936 | 0 | 0 | 0.20528 | 7184.8 | 4e-05 | 0.56 | 40000 | 0 | 4936 | 2248.8 | 0 | 0.56 | 2249.36 | 0 | 0 | 0 | 0
2022092303 | 6 | 0.54391 | 43512.8 | 0 | 0 | 0.17679 | 6187.65 | 4e-05 | 0.56 | 40000 | 0 | 3512.8 | 2674.85 | 0 | 0.56 | 2675.41 | 0 | 0 | 0 | 0
2022092304 | 6 | 0.53185 | 42548 | 0 | 0 | 0.15675 | 5486.25 | 5e-05 | 0.7 | 40000 | 0 | 2548 | 2938.25 | 0 | 0.7 | 2938.95 | 0 | 0 | 0 | 0
2022092305 | 6 | 0.52811 | 42248.8 | 0 | 0 | 0.12745 | 4460.75 | 5e-05 | 0.7 | 40000 | 0 | 2248.8 | 2211.95 | 0 | 0.7 | 2212.65 | 0 | 0 | 0 | 0
2022092306 | 6 | 0.54097 | 43277.6 | 0 | 0 | 0.12532 | 4386.2 | 5e-05 | 0.7 | 40000 | 0 | 3277.6 | 1108.6 | 0 | 0.7 | 1109.3 | 0 | 0 | 0 | 0
2022092307 | 6 | 0.5672 | 45376 | 0 | 0 | 0.13288 | 4650.8 | 5e-05 | 0.7 | 40000 | 0 | 4650.8 | 0 | 0.7 | 0 | 0 | 724.5 | 0 | 0 | 724.5
2022092308 | 6 | 0.57282 | 45825.6 | 0 | 0 | 0.13016 | 4555.6 | 0.01563 | 218.82 | 40000 | 0 | 4555.6 | 0 | 218.82 | 0 | 0 | 1051.18 | 0 | 0 | 1051.18
2022092309 | 6 | 0.59039 | 47231.2 | 0 | 0 | 0.12292 | 4302.2 | 0.31615 | 4426.1 | 40000 | 0 | 4302.2 | 0 | 2929 | 1497.1 | 1497.1 | 0 | 0 | 0 | 0
2022092310 | 6 | 0.63501 | 50800.8 | 0 | 0 | 0.10118 | 3541.3 | 0.70028 | 9803.92 | 40000 | 0 | 3541.3 | 0 | 7259.5 | 2544.42 | 2544.42 | 0 | 0 | 0 | 0
2022092311 | 6 | 0.68722 | 54977.6 | 0 | 0 | 0.12071 | 4224.85 | 0.78078 | 10930.92 | 40000 | 0 | 4224.85 | 0 | 10752.75 | 178.17 | 178.17 | 0 | 0 | 0 | 0
2022092312 | 6 | 0.73777 | 59021.6 | 0 | 0 | 0.19905 | 6966.75 | 0.77403 | 10836.42 | 40000 | 0 | 6966.75 | 0 | 10836.42 | 0 | 0 | 1218.43 | 0 | 0 | 1218.43
2022092313 | 6 | 0.79606 | 63684.8 | 0 | 0 | 0.2763 | 9670.5 | 0.75926 | 10629.64 | 40000 | 0 | 9670.5 | 0 | 10629.64 | 0 | 0 | 3384.66 | 0 | 0 | 3384.66
2022092314 | 6 | 0.84347 | 67477.6 | 0 | 0 | 0.30122 | 10542.7 | 0.75449 | 10562.86 | 40000 | 0 | 10542.7 | 0 | 10562.86 | 0 | 0 | 6372.04 | 0 | 0 | 6372.04
2022092315 | 6 | 0.87439 | 69951.2 | 0 | 0 | 0.33353 | 11673.55 | 0.77018 | 10782.52 | 40000 | 0 | 11673.55 | 0 | 10782.52 | 0 | 0 | 7495.13 | 0 | 0 | 7495.13
2022092316 | 6 | 0.87984 | 70387.2 | 0 | 0 | 0.32267 | 11293.45 | 0.76571 | 10719.94 | 40000 | 0 | 11293.45 | 0 | 10719.94 | 0 | 0 | 8373.81 | 0 | 0 | 8373.81
2022092317 | 6 | 0.88179 | 70543.2 | 0 | 0 | 0.31073 | 10875.55 | 0.76463 | 10704.82 | 40000 | 0 | 10875.55 | 0 | 10704.82 | 0 | 0 | 8962.83 | 0 | 0 | 8962.83
2022092318 | 6 | 0.87558 | 70046.4 | 0 | 0 | 0.29809 | 10433.15 | 0.69424 | 9719.36 | 40000 | 0 | 10433.15 | 0 | 9719.36 | 0 | 0 | 9893.89 | 0 | 0 | 9893.89
2022092319 | 6 | 0.84757 | 67805.6 | 0 | 0 | 0.28034 | 9811.9 | 0.37603 | 5264.42 | 40000 | 0 | 9811.9 | 0 | 5264.42 | 0 | 0 | 12729.28 | 0 | 0 | 12729.28
2022092320 | 6 | 0.81081 | 64864.8 | 0 | 0 | 0.24436 | 8552.6 | 0.03405 | 476.7 | 40000 | 0 | 8552.6 | 0 | 476.7 | 0 | 0 | 15835.5 | 0 | 0 | 15835.5
2022092321 | 6 | 0.77659 | 62127.2 | 0 | 0 | 0.29138 | 10198.3 | 0 | 0 | 40000 | 0 | 10198.3 | 0 | 0 | 0 | 0 | 11928.9 | 0 | 0 | 11928.9
2022092322 | 6 | 0.73844 | 59075.2 | 0 | 0 | 0.34714 | 12149.9 | 0 | 0 | 40000 | 0 | 12149.9 | 0 | 0 | 0 | 0 | 6925.3 | 0 | 0 | 6925.3
2022092323 | 6 | 0.69764 | 55811.2 | 0 | 0 | 0.39594 | 13857.9 | 0 | 0 | 40000 | 0 | 13857.9 | 0 | 0 | 0 | 0 | 1953.3 | 0 | 0 | 1953.3
2022092324 | 6 | 0.6551 | 52408 | 0 | 0 | 0.42997 | 15048.95 | 0 | 0 | 40000 | 0 | 12408 | 2640.95 | 0 | 0 | 2640.95 | 0 | 0 | 0 | 0
2022092401 | 7 | 0.6178 | 49424 | 0 | 0 | 0.45448 | 15906.8 | 0 | 0 | 40000 | 0 | 9424 | 6482.8 | 0 | 0 | 6482.8 | 0 | 0 | 0 | 0
2022092402 | 7 | 0.58641 | 46912.8 | 0 | 0 | 0.46054 | 16118.9 | 0 | 0 | 40000 | 0 | 6912.8 | 9206.1 | 0 | 0 | 9206.1 | 0 | 0 | 0 | 0
2022092403 | 7 | 0.56315 | 45052 | 0 | 0 | 0.45422 | 15897.7 | 0 | 0 | 40000 | 0 | 5052 | 10845.7 | 0 | 0 | 10845.7 | 0 | 0 | 0 | 0
2022092404 | 7 | 0.54611 | 43688.8 | 0 | 0 | 0.43671 | 15284.85 | 0 | 0 | 40000 | 0 | 3688.8 | 11596.05 | 0 | 0 | 11596.05 | 0 | 0 | 0 | 0
2022092405 | 7 | 0.53424 | 42739.2 | 0 | 0 | 0.41196 | 14418.6 | 0 | 0 | 40000 | 0 | 2739.2 | 11679.4 | 0 | 0 | 11679.4 | 0 | 0 | 0 | 0
2022092406 | 7 | 0.52887 | 42309.6 | 0 | 0 | 0.40049 | 14017.15 | 0 | 0 | 40000 | 0 | 2309.6 | 11707.55 | 0 | 0 | 11707.55 | 0 | 0 | 0 | 0
2022092407 | 7 | 0.53138 | 42510.4 | 0 | 0 | 0.3983 | 13940.5 | 0 | 0 | 40000 | 0 | 2510.4 | 11430.1 | 0 | 0 | 11430.1 | 0 | 0 | 0 | 0
2022092408 | 7 | 0.53385 | 42708 | 0 | 0 | 0.36185 | 12664.75 | 0.01648 | 230.72 | 40000 | 0 | 2708 | 9956.75 | 0 | 230.72 | 10187.47 | 0 | 0 | 0 | 0
2022092409 | 7 | 0.55993 | 44794.4 | 0 | 0 | 0.28764 | 10067.4 | 0.3279 | 4590.6 | 40000 | 0 | 4794.4 | 5273 | 0 | 4590.6 | 9863.6 | 0 | 0 | 0 | 0
2022092410 | 7 | 0.61124 | 48899.2 | 0 | 0 | 0.20709 | 7248.15 | 0.70088 | 9812.32 | 40000 | 0 | 7248.15 | 0 | 1651.05 | 8161.27 | 8161.27 | 0 | 0 | 0 | 0
2022092411 | 7 | 0.66388 | 53110.4 | 0 | 0 | 0.20741 | 7259.35 | 0.7654 | 10715.6 | 40000 | 0 | 7259.35 | 0 | 5851.05 | 4864.55 | 4864.55 | 0 | 0 | 0 | 0
2022092412 | 7 | 0.71509 | 57207.2 | 0 | 0 | 0.18695 | 6543.25 | 0.78638 | 11009.32 | 40000 | 0 | 6543.25 | 0 | 10663.95 | 345.37 | 345.37 | 0 | 0 | 0 | 0
2022092413 | 7 | 0.76006 | 60804.8 | 0 | 0 | 0.1796 | 6286 | 0.76501 | 10710.14 | 40000 | 0 | 6286 | 0 | 10710.14 | 0 | 0 | 3808.66 | 0 | 0 | 3808.66
2022092414 | 7 | 0.79672 | 63737.6 | 0 | 0 | 0.14055 | 4919.25 | 0.75828 | 10615.92 | 40000 | 0 | 4919.25 | 0 | 10615.92 | 0 | 0 | 8202.43 | 0 | 0 | 8202.43
2022092415 | 7 | 0.82413 | 65930.4 | 0 | 0 | 0.11332 | 3966.2 | 0.75847 | 10618.58 | 40000 | 0 | 3966.2 | 0 | 10618.58 | 0 | 0 | 11345.62 | 0 | 0 | 11345.62
2022092416 | 7 | 0.84448 | 67558.4 | 0 | 0 | 0.11062 | 3871.7 | 0.75944 | 10632.16 | 40000 | 0 | 3871.7 | 0 | 10632.16 | 0 | 0 | 13054.54 | 0 | 0 | 13054.54
2022092417 | 7 | 0.85403 | 68322.4 | 0 | 0 | 0.12336 | 4317.6 | 0.75756 | 10605.84 | 40000 | 0 | 4317.6 | 0 | 10605.84 | 0 | 0 | 13398.96 | 0 | 0 | 13398.96
2022092418 | 7 | 0.84686 | 67748.8 | 0 | 0 | 0.12578 | 4402.3 | 0.69239 | 9693.46 | 40000 | 0 | 4402.3 | 0 | 9693.46 | 0 | 0 | 13653.04 | 0 | 0 | 13653.04
2022092419 | 7 | 0.81939 | 65551.2 | 0 | 0 | 0.14581 | 5103.35 | 0.35314 | 4943.96 | 40000 | 0 | 5103.35 | 0 | 4943.96 | 0 | 0 | 15503.89 | 0 | 0 | 15503.89
2022092420 | 7 | 0.78198 | 62558.4 | 0 | 0 | 0.1733 | 6065.5 | 0.02807 | 392.98 | 40000 | 0 | 6065.5 | 0 | 392.98 | 0 | 0 | 16099.92 | 0 | 0 | 16099.92
2022092421 | 7 | 0.74881 | 59904.8 | 0 | 0 | 0.24105 | 8436.75 | 0 | 0 | 40000 | 0 | 8436.75 | 0 | 0 | 0 | 0 | 11468.05 | 0 | 0 | 11468.05
2022092422 | 7 | 0.71194 | 56955.2 | 0 | 0 | 0.32456 | 11359.6 | 0 | 0 | 40000 | 0 | 11359.6 | 0 | 0 | 0 | 0 | 5595.6 | 0 | 0 | 5595.6
2022092423 | 7 | 0.6724 | 53792 | 0 | 0 | 0.39019 | 13656.65 | 0 | 0 | 40000 | 0 | 13656.65 | 0 | 0 | 0 | 0 | 135.35 | 0 | 0 | 135.35
2022092424 | 7 | 0.63356 | 50684.8 | 0 | 0 | 0.40773 | 14270.55 | 0 | 0 | 40000 | 0 | 10684.8 | 3585.75 | 0 | 0 | 3585.75 | 0 | 0 | 0 | 0
2022092501 | 1 | 0.59576 | 47660.8 | 0 | 0 | 0.39424 | 13798.4 | 0 | 0 | 40000 | 0 | 7660.8 | 6137.6 | 0 | 0 | 6137.6 | 0 | 0 | 0 | 0
2022092502 | 1 | 0.56603 | 45282.4 | 0 | 0 | 0.3712 | 12992 | 0 | 0 | 40000 | 0 | 5282.4 | 7709.6 | 0 | 0 | 7709.6 | 0 | 0 | 0 | 0
2022092503 | 1 | 0.54603 | 43682.4 | 0 | 0 | 0.3411 | 11938.5 | 0 | 0 | 40000 | 0 | 3682.4 | 8256.1 | 0 | 0 | 8256.1 | 0 | 0 | 0 | 0
2022092504 | 1 | 0.52977 | 42381.6 | 0 | 0 | 0.30762 | 10766.7 | 0 | 0 | 40000 | 0 | 2381.6 | 8385.1 | 0 | 0 | 8385.1 | 0 | 0 | 0 | 0
2022092505 | 1 | 0.51892 | 41513.6 | 0 | 0 | 0.25477 | 8916.95 | 0 | 0 | 40000 | 0 | 1513.6 | 7403.35 | 0 | 0 | 7403.35 | 0 | 0 | 0 | 0
2022092506 | 1 | 0.51254 | 41003.2 | 0 | 0 | 0.21706 | 7597.1 | 0 | 0 | 40000 | 0 | 1003.2 | 6593.9 | 0 | 0 | 6593.9 | 0 | 0 | 0 | 0
2022092507 | 1 | 0.51234 | 40987.2 | 0 | 0 | 0.18758 | 6565.3 | 0 | 0 | 40000 | 0 | 987.2 | 5578.1 | 0 | 0 | 5578.1 | 0 | 0 | 0 | 0
2022092508 | 1 | 0.51504 | 41203.2 | 0 | 0 | 0.16149 | 5652.15 | 0.01052 | 147.28 | 40000 | 0 | 1203.2 | 4448.95 | 0 | 147.28 | 4596.23 | 0 | 0 | 0 | 0
2022092509 | 1 | 0.53973 | 43178.4 | 0 | 0 | 0.13534 | 4736.9 | 0.24248 | 3394.72 | 40000 | 0 | 3178.4 | 1558.5 | 0 | 3394.72 | 4953.22 | 0 | 0 | 0 | 0
2022092510 | 1 | 0.59166 | 47332.8 | 0 | 0 | 0.10517 | 3680.95 | 0.538 | 7532 | 40000 | 0 | 3680.95 | 0 | 3651.85 | 3880.15 | 3880.15 | 0 | 0 | 0 | 0
2022092511 | 1 | 0.64426 | 51540.8 | 0 | 0 | 0.09775 | 3421.25 | 0.63903 | 8946.42 | 40000 | 0 | 3421.25 | 0 | 8119.55 | 826.87 | 826.87 | 0 | 0 | 0 | 0
2022092512 | 1 | 0.69573 | 55658.4 | 0 | 0 | 0.10114 | 3539.9 | 0.67459 | 9444.26 | 40000 | 0 | 3539.9 | 0 | 9444.26 | 0 | 0 | 2674.24 | 0 | 0 | 2674.24
2022092513 | 1 | 0.75169 | 60135.2 | 0 | 0 | 0.11642 | 4074.7 | 0.65701 | 9198.14 | 40000 | 0 | 4074.7 | 0 | 9198.14 | 0 | 0 | 6862.36 | 0 | 0 | 6862.36
2022092514 | 1 | 0.79858 | 63886.4 | 0 | 0 | 0.16033 | 5611.55 | 0.63735 | 8922.9 | 40000 | 0 | 5611.55 | 0 | 8922.9 | 0 | 0 | 9351.95 | 0 | 0 | 9351.95
2022092515 | 1 | 0.83201 | 66560.8 | 0 | 0 | 0.2144 | 7504 | 0.65916 | 9228.24 | 40000 | 0 | 7504 | 0 | 9228.24 | 0 | 0 | 9828.56 | 0 | 0 | 9828.56
2022092516 | 1 | 0.85539 | 68431.2 | 0 | 0 | 0.26574 | 9300.9 | 0.64944 | 9092.16 | 40000 | 0 | 9300.9 | 0 | 9092.16 | 0 | 0 | 10038.14 | 0 | 0 | 10038.14
2022092517 | 1 | 0.86242 | 68993.6 | 0 | 0 | 0.29018 | 10156.3 | 0.61448 | 8602.72 | 40000 | 0 | 10156.3 | 0 | 8602.72 | 0 | 0 | 10234.58 | 0 | 0 | 10234.58
2022092518 | 1 | 0.85156 | 68124.8 | 0 | 0 | 0.3168 | 11088 | 0.49871 | 6981.94 | 40000 | 0 | 11088 | 0 | 6981.94 | 0 | 0 | 10054.86 | 0 | 0 | 10054.86
2022092519 | 1 | 0.81911 | 65528.8 | 0 | 0 | 0.30158 | 10555.3 | 0.25549 | 3576.86 | 40000 | 0 | 10555.3 | 0 | 3576.86 | 0 | 0 | 11396.64 | 0 | 0 | 11396.64
2022092520 | 1 | 0.78516 | 62812.8 | 0 | 0 | 0.26588 | 9305.8 | 0.01407 | 196.98 | 40000 | 0 | 9305.8 | 0 | 196.98 | 0 | 0 | 13310.02 | 0 | 0 | 13310.02
2022092521 | 1 | 0.75701 | 60560.8 | 0 | 0 | 0.25489 | 8921.15 | 0 | 0 | 40000 | 0 | 8921.15 | 0 | 0 | 0 | 0 | 11639.65 | 0 | 0 | 11639.65
2022092522 | 1 | 0.71577 | 57261.6 | 0 | 0 | 0.25817 | 9035.95 | 0 | 0 | 40000 | 0 | 9035.95 | 0 | 0 | 0 | 0 | 8225.65 | 0 | 0 | 8225.65
2022092523 | 1 | 0.66629 | 53303.2 | 0 | 0 | 0.27768 | 9718.8 | 0 | 0 | 40000 | 0 | 9718.8 | 0 | 0 | 0 | 0 | 3584.4 | 0 | 0 | 3584.4
2022092524 | 1 | 0.61696 | 49356.8 | 0 | 0 | 0.30393 | 10637.55 | 0 | 0 | 40000 | 0 | 9356.8 | 1280.75 | 0 | 0 | 1280.75 | 0 | 0 | 0 | 0
2022092601 | 2 | 0.57538 | 46030.4 | 0 | 0 | 0.31723 | 11103.05 | 0 | 0 | 40000 | 0 | 6030.4 | 5072.65 | 0 | 0 | 5072.65 | 0 | 0 | 0 | 0
2022092602 | 2 | 0.54477 | 43581.6 | 0 | 0 | 0.32101 | 11235.35 | 0 | 0 | 40000 | 0 | 3581.6 | 7653.75 | 0 | 0 | 7653.75 | 0 | 0 | 0 | 0
2022092603 | 2 | 0.52853 | 42282.4 | 0 | 0 | 0.32642 | 11424.7 | 0 | 0 | 40000 | 0 | 2282.4 | 9142.3 | 0 | 0 | 9142.3 | 0 | 0 | 0 | 0
2022092604 | 2 | 0.51945 | 41556 | 0 | 0 | 0.32815 | 11485.25 | 0 | 0 | 40000 | 0 | 1556 | 9929.25 | 0 | 0 | 9929.25 | 0 | 0 | 0 | 0
2022092605 | 2 | 0.51763 | 41410.4 | 0 | 0 | 0.31847 | 11146.45 | 0 | 0 | 40000 | 0 | 1410.4 | 9736.05 | 0 | 0 | 9736.05 | 0 | 0 | 0 | 0
2022092606 | 2 | 0.5304 | 42432 | 0 | 0 | 0.29358 | 10275.3 | 0 | 0 | 40000 | 0 | 2432 | 7843.3 | 0 | 0 | 7843.3 | 0 | 0 | 0 | 0
2022092607 | 2 | 0.55642 | 44513.6 | 0 | 0 | 0.2708 | 9478 | 0 | 0 | 40000 | 0 | 4513.6 | 4964.4 | 0 | 0 | 4964.4 | 0 | 0 | 0 | 0
2022092608 | 2 | 0.56153 | 44922.4 | 0 | 0 | 0.24303 | 8506.05 | 0.01291 | 180.74 | 40000 | 0 | 4922.4 | 3583.65 | 0 | 180.74 | 3764.39 | 0 | 0 | 0 | 0
2022092609 | 2 | 0.57019 | 45615.2 | 0 | 0 | 0.20187 | 7065.45 | 0.29021 | 4062.94 | 40000 | 0 | 5615.2 | 1450.25 | 0 | 4062.94 | 5513.19 | 0 | 0 | 0 | 0
2022092610 | 2 | 0.60383 | 48306.4 | 0 | 0 | 0.1413 | 4945.5 | 0.66725 | 9341.5 | 40000 | 0 | 4945.5 | 0 | 3360.9 | 5980.6 | 5980.6 | 0 | 0 | 0 | 0
2022092611 | 2 | 0.63765 | 51012 | 0 | 0 | 0.14596 | 5108.6 | 0.76206 | 10668.84 | 40000 | 0 | 5108.6 | 0 | 5903.4 | 4765.44 | 4765.44 | 0 | 0 | 0 | 0
2022092612 | 2 | 0.67441 | 53952.8 | 0 | 0 | 0.15591 | 5456.85 | 0.76508 | 10711.12 | 40000 | 0 | 5456.85 | 0 | 8495.95 | 2215.17 | 2215.17 | 0 | 0 | 0 | 0
2022092613 | 2 | 0.70915 | 56732 | 0 | 0 | 0.14941 | 5229.35 | 0.77671 | 10873.94 | 40000 | 0 | 5229.35 | 0 | 10873.94 | 0 | 0 | 628.71 | 0 | 0 | 628.71
2022092614 | 2 | 0.74567 | 59653.6 | 0 | 0 | 0.13423 | 4698.05 | 0.77268 | 10817.52 | 40000 | 0 | 4698.05 | 0 | 10817.52 | 0 | 0 | 4138.03 | 0 | 0 | 4138.03
2022092615 | 2 | 0.77215 | 61772 | 0 | 0 | 0.12419 | 4346.65 | 0.77786 | 10890.04 | 40000 | 0 | 4346.65 | 0 | 10890.04 | 0 | 0 | 6535.31 | 0 | 0 | 6535.31
2022092616 | 2 | 0.79128 | 63302.4 | 0 | 0 | 0.11789 | 4126.15 | 0.77008 | 10781.12 | 40000 | 0 | 4126.15 | 0 | 10781.12 | 0 | 0 | 8395.13 | 0 | 0 | 8395.13
2022092617 | 2 | 0.79903 | 63922.4 | 0 | 0 | 0.1114 | 3899 | 0.74656 | 10451.84 | 40000 | 0 | 3899 | 0 | 10451.84 | 0 | 0 | 9571.56 | 0 | 0 | 9571.56
2022092618 | 2 | 0.78991 | 63192.8 | 0 | 0 | 0.09986 | 3495.1 | 0.67204 | 9408.56 | 40000 | 0 | 3495.1 | 0 | 9408.56 | 0 | 0 | 10289.14 | 0 | 0 | 10289.14
2022092619 | 2 | 0.76067 | 60853.6 | 0 | 0 | 0.08649 | 3027.15 | 0.32369 | 4531.66 | 40000 | 0 | 3027.15 | 0 | 4531.66 | 0 | 0 | 13294.79 | 0 | 0 | 13294.79
2022092620 | 2 | 0.7276 | 58208 | 0 | 0 | 0.08692 | 3042.2 | 0.02111 | 295.54 | 40000 | 0 | 3042.2 | 0 | 295.54 | 0 | 0 | 14870.26 | 0 | 0 | 14870.26
2022092621 | 2 | 0.6956 | 55648 | 0 | 0 | 0.11989 | 4196.15 | 0 | 0 | 40000 | 0 | 4196.15 | 0 | 0 | 0 | 0 | 11451.85 | 0 | 0 | 11451.85
2022092622 | 2 | 0.6542 | 52336 | 0 | 0 | 0.14551 | 5092.85 | 0 | 0 | 40000 | 0 | 5092.85 | 0 | 0 | 0 | 0 | 7243.15 | 0 | 0 | 7243.15
2022092623 | 2 | 0.60152 | 48121.6 | 0 | 0 | 0.17792 | 6227.2 | 0 | 0 | 40000 | 0 | 6227.2 | 0 | 0 | 0 | 0 | 1894.4 | 0 | 0 | 1894.4
2022092624 | 2 | 0.55117 | 44093.6 | 0 | 0 | 0.21907 | 7667.45 | 0 | 0 | 40000 | 0 | 4093.6 | 3573.85 | 0 | 0 | 3573.85 | 0 | 0 | 0 | 0
2022092701 | 3 | 0.5115 | 40920 | 0 | 0 | 0.2682 | 9387 | 0 | 0 | 40000 | 0 | 920 | 8467 | 0 | 0 | 8467 | 0 | 0 | 0 | 0
2022092702 | 3 | 0.48155 | 38524 | 0 | 0 | 0.28201 | 9870.35 | 0 | 0 | 38524 | 1476 | 0 | 9870.35 | 0 | 0 | 11346.35 | 0 | 0 | 0 | 0
2022092703 | 3 | 0.46648 | 37318.4 | 0 | 0 | 0.29427 | 10299.45 | 0 | 0 | 37318.4 | 2681.6 | 0 | 10299.45 | 0 | 0 | 12981.05 | 0 | 0 | 0 | 0
2022092704 | 3 | 0.45677 | 36541.6 | 0 | 0 | 0.2945 | 10307.5 | 0 | 0 | 36541.6 | 3458.4 | 0 | 10307.5 | 0 | 0 | 13765.9 | 0 | 0 | 0 | 0
2022092705 | 3 | 0.45438 | 36350.4 | 0 | 0 | 0.29699 | 10394.65 | 0 | 0 | 36350.4 | 3649.6 | 0 | 10394.65 | 0 | 0 | 14044.25 | 0 | 0 | 0 | 0
2022092706 | 3 | 0.46505 | 37204 | 0 | 0 | 0.29741 | 10409.35 | 0 | 0 | 37204 | 2796 | 0 | 10409.35 | 0 | 0 | 13205.35 | 0 | 0 | 0 | 0
2022092707 | 3 | 0.49418 | 39534.4 | 0 | 0 | 0.28521 | 9982.35 | 0 | 0 | 39534.4 | 465.6 | 0 | 9982.35 | 0 | 0 | 10447.95 | 0 | 0 | 0 | 0
2022092708 | 3 | 0.50099 | 40079.2 | 0 | 0 | 0.2754 | 9639 | 0.01748 | 244.72 | 40000 | 0 | 79.2 | 9559.8 | 0 | 244.72 | 9804.52 | 0 | 0 | 0 | 0
2022092709 | 3 | 0.51254 | 41003.2 | 0 | 0 | 0.245 | 8575 | 0.3163 | 4428.2 | 40000 | 0 | 1003.2 | 7571.8 | 0 | 4428.2 | 12000 | 0 | 0 | 0 | 0
2022092710 | 3 | 0.5377 | 43016 | 0 | 0 | 0.16534 | 5786.9 | 0.68156 | 9541.84 | 40000 | 0 | 3016 | 2770.9 | 0 | 9541.84 | 12312.74 | 0 | 0 | 0 | 0
2022092711 | 3 | 0.56469 | 45175.2 | 0 | 0 | 0.1762 | 6167 | 0.77636 | 10869.04 | 40000 | 0 | 5175.2 | 991.8 | 0 | 10869.04 | 11860.84 | 0 | 0 | 0 | 0
2022092712 | 3 | 0.5985 | 47880 | 0 | 0 | 0.17744 | 6210.4 | 0.79389 | 11114.46 | 40000 | 0 | 6210.4 | 0 | 1669.6 | 9444.86 | 9444.86 | 0 | 0 | 0 | 0
2022092713 | 3 | 0.63307 | 50645.6 | 0 | 0 | 0.16239 | 5683.65 | 0.78571 | 10999.94 | 40000 | 0 | 5683.65 | 0 | 4961.95 | 6037.99 | 6037.99 | 0 | 0 | 0 | 0
2022092714 | 3 | 0.67331 | 53864.8 | 0 | 0 | 0.12812 | 4484.2 | 0.77836 | 10897.04 | 40000 | 0 | 4484.2 | 0 | 9380.6 | 1516.44 | 1516.44 | 0 | 0 | 0 | 0
2022092715 | 3 | 0.70683 | 56546.4 | 0 | 0 | 0.0982 | 3437 | 0.79541 | 11135.74 | 40000 | 0 | 3437 | 0 | 11135.74 | 0 | 0 | 1973.66 | 0 | 0 | 1973.66
2022092716 | 3 | 0.73423 | 58738.4 | 0 | 0 | 0.08393 | 2937.55 | 0.78341 | 10967.74 | 40000 | 0 | 2937.55 | 0 | 10967.74 | 0 | 0 | 4833.11 | 0 | 0 | 4833.11
2022092717 | 3 | 0.75182 | 60145.6 | 0 | 0 | 0.08136 | 2847.6 | 0.75714 | 10599.96 | 40000 | 0 | 2847.6 | 0 | 10599.96 | 0 | 0 | 6698.04 | 0 | 0 | 6698.04
2022092718 | 3 | 0.75397 | 60317.6 | 0 | 0 | 0.09288 | 3250.8 | 0.67026 | 9383.64 | 40000 | 0 | 3250.8 | 0 | 9383.64 | 0 | 0 | 7683.16 | 0 | 0 | 7683.16
2022092719 | 3 | 0.72875 | 58300 | 0 | 0 | 0.10746 | 3761.1 | 0.33875 | 4742.5 | 40000 | 0 | 3761.1 | 0 | 4742.5 | 0 | 0 | 9796.4 | 0 | 0 | 9796.4
2022092720 | 3 | 0.69562 | 55649.6 | 0 | 0 | 0.16015 | 5605.25 | 0.02456 | 343.84 | 40000 | 0 | 5605.25 | 0 | 343.84 | 0 | 0 | 9700.51 | 0 | 0 | 9700.51
2022092721 | 3 | 0.67087 | 53669.6 | 0 | 0 | 0.2687 | 9404.5 | 0 | 0 | 40000 | 0 | 9404.5 | 0 | 0 | 0 | 0 | 4265.1 | 0 | 0 | 4265.1
2022092722 | 3 | 0.63563 | 50850.4 | 0 | 0 | 0.36391 | 12736.85 | 0 | 0 | 40000 | 0 | 10850.4 | 1886.45 | 0 | 0 | 1886.45 | 0 | 0 | 0 | 0
2022092723 | 3 | 0.59318 | 47454.4 | 0 | 0 | 0.4223 | 14780.5 | 0 | 0 | 40000 | 0 | 7454.4 | 7326.1 | 0 | 0 | 7326.1 | 0 | 0 | 0 | 0
2022092724 | 3 | 0.54427 | 43541.6 | 0 | 0 | 0.43811 | 15333.85 | 0 | 0 | 40000 | 0 | 3541.6 | 11792.25 | 0 | 0 | 11792.25 | 0 | 0 | 0 | 0
2022092801 | 4 | 0.50834 | 40667.2 | 0 | 0 | 0.41717 | 14600.95 | 0 | 0 | 40000 | 0 | 667.2 | 13933.75 | 0 | 0 | 13933.75 | 0 | 0 | 0 | 0
2022092802 | 4 | 0.48325 | 38660 | 0 | 0 | 0.39762 | 13916.7 | 0 | 0 | 38660 | 1340 | 0 | 13916.7 | 0 | 0 | 15256.7 | 0 | 0 | 0 | 0
2022092803 | 4 | 0.46748 | 37398.4 | 0 | 0 | 0.37399 | 13089.65 | 0 | 0 | 37398.4 | 2601.6 | 0 | 13089.65 | 0 | 0 | 15691.25 | 0 | 0 | 0 | 0
2022092804 | 4 | 0.45924 | 36739.2 | 0 | 0 | 0.33937 | 11877.95 | 0 | 0 | 36739.2 | 3260.8 | 0 | 11877.95 | 0 | 0 | 15138.75 | 0 | 0 | 0 | 0
2022092805 | 4 | 0.45615 | 36492 | 0 | 0 | 0.29979 | 10492.65 | 0 | 0 | 36492 | 3508 | 0 | 10492.65 | 0 | 0 | 14000.65 | 0 | 0 | 0 | 0
2022092806 | 4 | 0.46652 | 37321.6 | 0 | 0 | 0.2623 | 9180.5 | 0 | 0 | 37321.6 | 2678.4 | 0 | 9180.5 | 0 | 0 | 11858.9 | 0 | 0 | 0 | 0
2022092807 | 4 | 0.49295 | 39436 | 0 | 0 | 0.24317 | 8510.95 | 0 | 0 | 39436 | 564 | 0 | 8510.95 | 0 | 0 | 9074.95 | 0 | 0 | 0 | 0
2022092808 | 4 | 0.50448 | 40358.4 | 0 | 0 | 0.23145 | 8100.75 | 0.01437 | 201.18 | 40000 | 0 | 358.4 | 7742.35 | 0 | 201.18 | 7943.53 | 0 | 0 | 0 | 0
2022092809 | 4 | 0.51749 | 41399.2 | 0 | 0 | 0.19674 | 6885.9 | 0.28555 | 3997.7 | 40000 | 0 | 1399.2 | 5486.7 | 0 | 3997.7 | 9484.4 | 0 | 0 | 0 | 0
2022092810 | 4 | 0.53882 | 43105.6 | 0 | 0 | 0.1081 | 3783.5 | 0.68543 | 9596.02 | 40000 | 0 | 3105.6 | 677.9 | 0 | 9596.02 | 10273.92 | 0 | 0 | 0 | 0
2022092811 | 4 | 0.56769 | 45415.2 | 0 | 0 | 0.11205 | 3921.75 | 0.78478 | 10986.92 | 40000 | 0 | 3921.75 | 0 | 1493.45 | 9493.47 | 9493.47 | 0 | 0 | 0 | 0
2022092812 | 4 | 0.59952 | 47961.6 | 0 | 0 | 0.14278 | 4997.3 | 0.7897 | 11055.8 | 40000 | 0 | 4997.3 | 0 | 2964.3 | 8091.5 | 8091.5 | 0 | 0 | 0 | 0
2022092813 | 4 | 0.63322 | 50657.6 | 0 | 0 | 0.15283 | 5349.05 | 0.79392 | 11114.88 | 40000 | 0 | 5349.05 | 0 | 5308.55 | 5806.33 | 5806.33 | 0 | 0 | 0 | 0
2022092814 | 4 | 0.67233 | 53786.4 | 0 | 0 | 0.14216 | 4975.6 | 0.78962 | 11054.68 | 40000 | 0 | 4975.6 | 0 | 8810.8 | 2243.88 | 2243.88 | 0 | 0 | 0 | 0
2022092815 | 4 | 0.70793 | 56634.4 | 0 | 0 | 0.12539 | 4388.65 | 0.79393 | 11115.02 | 40000 | 0 | 4388.65 | 0 | 11115.02 | 0 | 0 | 1130.73 | 0 | 0 | 1130.73
2022092816 | 4 | 0.73907 | 59125.6 | 0 | 0 | 0.11979 | 4192.65 | 0.78742 | 11023.88 | 40000 | 0 | 4192.65 | 0 | 11023.88 | 0 | 0 | 3909.07 | 0 | 0 | 3909.07
2022092817 | 4 | 0.76262 | 61009.6 | 0 | 0 | 0.12625 | 4418.75 | 0.7769 | 10876.6 | 40000 | 0 | 4418.75 | 0 | 10876.6 | 0 | 0 | 5714.25 | 0 | 0 | 5714.25
2022092818 | 4 | 0.76484 | 61187.2 | 0 | 0 | 0.12985 | 4544.75 | 0.68442 | 9581.88 | 40000 | 0 | 4544.75 | 0 | 9581.88 | 0 | 0 | 7060.57 | 0 | 0 | 7060.57
2022092819 | 4 | 0.73886 | 59108.8 | 0 | 0 | 0.14117 | 4940.95 | 0.32574 | 4560.36 | 40000 | 0 | 4940.95 | 0 | 4560.36 | 0 | 0 | 9607.49 | 0 | 0 | 9607.49
2022092820 | 4 | 0.70401 | 56320.8 | 0 | 0 | 0.16715 | 5850.25 | 0.02004 | 280.56 | 40000 | 0 | 5850.25 | 0 | 280.56 | 0 | 0 | 10189.99 | 0 | 0 | 10189.99
2022092821 | 4 | 0.6764 | 54112 | 0 | 0 | 0.21994 | 7697.9 | 4e-05 | 0.56 | 40000 | 0 | 7697.9 | 0 | 0.56 | 0 | 0 | 6413.54 | 0 | 0 | 6413.54
2022092822 | 4 | 0.63638 | 50910.4 | 0 | 0 | 0.25535 | 8937.25 | 0 | 0 | 40000 | 0 | 8937.25 | 0 | 0 | 0 | 0 | 1973.15 | 0 | 0 | 1973.15
2022092823 | 4 | 0.5882 | 47056 | 0 | 0 | 0.29431 | 10300.85 | 0 | 0 | 40000 | 0 | 7056 | 3244.85 | 0 | 0 | 3244.85 | 0 | 0 | 0 | 0
2022092824 | 4 | 0.54172 | 43337.6 | 0 | 0 | 0.31167 | 10908.45 | 0 | 0 | 40000 | 0 | 3337.6 | 7570.85 | 0 | 0 | 7570.85 | 0 | 0 | 0 | 0
2022092901 | 5 | 0.50759 | 40607.2 | 0 | 0 | 0.32039 | 11213.65 | 0 | 0 | 40000 | 0 | 607.2 | 10606.45 | 0 | 0 | 10606.45 | 0 | 0 | 0 | 0
2022092902 | 5 | 0.48121 | 38496.8 | 0 | 0 | 0.31956 | 11184.6 | 0 | 0 | 38496.8 | 1503.2 | 0 | 11184.6 | 0 | 0 | 12687.8 | 0 | 0 | 0 | 0
2022092903 | 5 | 0.46749 | 37399.2 | 0 | 0 | 0.30829 | 10790.15 | 0 | 0 | 37399.2 | 2600.8 | 0 | 10790.15 | 0 | 0 | 13390.95 | 0 | 0 | 0 | 0
2022092904 | 5 | 0.45874 | 36699.2 | 0 | 0 | 0.30081 | 10528.35 | 0 | 0 | 36699.2 | 3300.8 | 0 | 10528.35 | 0 | 0 | 13829.15 | 0 | 0 | 0 | 0
2022092905 | 5 | 0.458 | 36640 | 0 | 0 | 0.2942 | 10297 | 0 | 0 | 36640 | 3360 | 0 | 10297 | 0 | 0 | 13657 | 0 | 0 | 0 | 0
2022092906 | 5 | 0.46986 | 37588.8 | 0 | 0 | 0.29833 | 10441.55 | 0 | 0 | 37588.8 | 2411.2 | 0 | 10441.55 | 0 | 0 | 12852.75 | 0 | 0 | 0 | 0
2022092907 | 5 | 0.49932 | 39945.6 | 0 | 0 | 0.27962 | 9786.7 | 0 | 0 | 39945.6 | 54.4 | 0 | 9786.7 | 0 | 0 | 9841.1 | 0 | 0 | 0 | 0
2022092908 | 5 | 0.5091 | 40728 | 0 | 0 | 0.26424 | 9248.4 | 0.01323 | 185.22 | 40000 | 0 | 728 | 8520.4 | 0 | 185.22 | 8705.62 | 0 | 0 | 0 | 0
2022092909 | 5 | 0.51563 | 41250.4 | 0 | 0 | 0.21796 | 7628.6 | 0.3068 | 4295.2 | 40000 | 0 | 1250.4 | 6378.2 | 0 | 4295.2 | 10673.4 | 0 | 0 | 0 | 0
2022092910 | 5 | 0.53412 | 42729.6 | 0 | 0 | 0.12482 | 4368.7 | 0.7081 | 9913.4 | 40000 | 0 | 2729.6 | 1639.1 | 0 | 9913.4 | 11552.5 | 0 | 0 | 0 | 0
2022092911 | 5 | 0.55653 | 44522.4 | 0 | 0 | 0.12271 | 4294.85 | 0.79496 | 11129.44 | 40000 | 0 | 4294.85 | 0 | 227.55 | 10901.89 | 10901.89 | 0 | 0 | 0 | 0
2022092912 | 5 | 0.58013 | 46410.4 | 0 | 0 | 0.11366 | 3978.1 | 0.8053 | 11274.2 | 40000 | 0 | 3978.1 | 0 | 2432.3 | 8841.9 | 8841.9 | 0 | 0 | 0 | 0
2022092913 | 5 | 0.60829 | 48663.2 | 0 | 0 | 0.08809 | 3083.15 | 0.79754 | 11165.56 | 40000 | 0 | 3083.15 | 0 | 5580.05 | 5585.51 | 5585.51 | 0 | 0 | 0 | 0
2022092914 | 5 | 0.64246 | 51396.8 | 0 | 0 | 0.06311 | 2208.85 | 0.78958 | 11054.12 | 40000 | 0 | 2208.85 | 0 | 9187.95 | 1866.17 | 1866.17 | 0 | 0 | 0 | 0
2022092915 | 5 | 0.67361 | 53888.8 | 0 | 0 | 0.05764 | 2017.4 | 0.79304 | 11102.56 | 40000 | 0 | 2017.4 | 0 | 11102.56 | 0 | 0 | 768.84 | 0 | 0 | 768.84
2022092916 | 5 | 0.70377 | 56301.6 | 0 | 0 | 0.06093 | 2132.55 | 0.79647 | 11150.58 | 40000 | 0 | 2132.55 | 0 | 11150.58 | 0 | 0 | 3018.47 | 0 | 0 | 3018.47
2022092917 | 5 | 0.72765 | 58212 | 0 | 0 | 0.0652 | 2282 | 0.78253 | 10955.42 | 40000 | 0 | 2282 | 0 | 10955.42 | 0 | 0 | 4974.58 | 0 | 0 | 4974.58
2022092918 | 5 | 0.72903 | 58322.4 | 0 | 0 | 0.07605 | 2661.75 | 0.67285 | 9419.9 | 40000 | 0 | 2661.75 | 0 | 9419.9 | 0 | 0 | 6240.75 | 0 | 0 | 6240.75
2022092919 | 5 | 0.70497 | 56397.6 | 0 | 0 | 0.09371 | 3279.85 | 0.2995 | 4193 | 40000 | 0 | 3279.85 | 0 | 4193 | 0 | 0 | 8924.75 | 0 | 0 | 8924.75
2022092920 | 5 | 0.67815 | 54252 | 0 | 0 | 0.1178 | 4123 | 0.0152 | 212.8 | 40000 | 0 | 4123 | 0 | 212.8 | 0 | 0 | 9916.2 | 0 | 0 | 9916.2
2022092921 | 5 | 0.65063 | 52050.4 | 0 | 0 | 0.19375 | 6781.25 | 0 | 0 | 40000 | 0 | 6781.25 | 0 | 0 | 0 | 0 | 5269.15 | 0 | 0 | 5269.15
2022092922 | 5 | 0.616 | 49280 | 0 | 0 | 0.26213 | 9174.55 | 0 | 0 | 40000 | 0 | 9174.55 | 0 | 0 | 0 | 0 | 105.45 | 0 | 0 | 105.45
2022092923 | 5 | 0.5732 | 45856 | 0 | 0 | 0.29952 | 10483.2 | 0 | 0 | 40000 | 0 | 5856 | 4627.2 | 0 | 0 | 4627.2 | 0 | 0 | 0 | 0
2022092924 | 5 | 0.53033 | 42426.4 | 0 | 0 | 0.33188 | 11615.8 | 0 | 0 | 40000 | 0 | 2426.4 | 9189.4 | 0 | 0 | 9189.4 | 0 | 0 | 0 | 0
2022093001 | 6 | 0.49463 | 39570.4 | 0 | 0 | 0.37016 | 12955.6 | 0 | 0 | 39570.4 | 429.6 | 0 | 12955.6 | 0 | 0 | 13385.2 | 0 | 0 | 0 | 0
2022093002 | 6 | 0.46888 | 37510.4 | 0 | 0 | 0.36153 | 12653.55 | 0 | 0 | 37510.4 | 2489.6 | 0 | 12653.55 | 0 | 0 | 15143.15 | 0 | 0 | 0 | 0
2022093003 | 6 | 0.45352 | 36281.6 | 0 | 0 | 0.34827 | 12189.45 | 0 | 0 | 36281.6 | 3718.4 | 0 | 12189.45 | 0 | 0 | 15907.85 | 0 | 0 | 0 | 0
2022093004 | 6 | 0.44325 | 35460 | 0 | 0 | 0.3281 | 11483.5 | 0 | 0 | 35460 | 4540 | 0 | 11483.5 | 0 | 0 | 16023.5 | 0 | 0 | 0 | 0
2022093005 | 6 | 0.44262 | 35409.6 | 0 | 0 | 0.30397 | 10638.95 | 0 | 0 | 35409.6 | 4590.4 | 0 | 10638.95 | 0 | 0 | 15229.35 | 0 | 0 | 0 | 0
2022093006 | 6 | 0.45403 | 36322.4 | 0 | 0 | 0.27725 | 9703.75 | 0 | 0 | 36322.4 | 3677.6 | 0 | 9703.75 | 0 | 0 | 13381.35 | 0 | 0 | 0 | 0
2022093007 | 6 | 0.48063 | 38450.4 | 0 | 0 | 0.24268 | 8493.8 | 0 | 0 | 38450.4 | 1549.6 | 0 | 8493.8 | 0 | 0 | 10043.4 | 0 | 0 | 0 | 0
2022093008 | 6 | 0.49224 | 39379.2 | 0 | 0 | 0.20799 | 7279.65 | 0.01467 | 205.38 | 39379.2 | 620.8 | 0 | 7279.65 | 0 | 205.38 | 8105.83 | 0 | 0 | 0 | 0
2022093009 | 6 | 0.50193 | 40154.4 | 0 | 0 | 0.16262 | 5691.7 | 0.31563 | 4418.82 | 40000 | 0 | 154.4 | 5537.3 | 0 | 4418.82 | 9956.12 | 0 | 0 | 0 | 0
2022093010 | 6 | 0.52323 | 41858.4 | 0 | 0 | 0.09148 | 3201.8 | 0.71543 | 10016.02 | 40000 | 0 | 1858.4 | 1343.4 | 0 | 10016.02 | 11359.42 | 0 | 0 | 0 | 0
2022093011 | 6 | 0.53944 | 43155.2 | 0 | 0 | 0.06609 | 2313.15 | 0.78906 | 11046.84 | 40000 | 0 | 2313.15 | 0 | 842.05 | 10204.79 | 10204.79 | 0 | 0 | 0 | 0
2022093012 | 6 | 0.56286 | 45028.8 | 0 | 0 | 0.05965 | 2087.75 | 0.79019 | 11062.66 | 40000 | 0 | 2087.75 | 0 | 2941.05 | 8121.61 | 8121.61 | 0 | 0 | 0 | 0
2022093013 | 6 | 0.58956 | 47164.8 | 0 | 0 | 0.06086 | 2130.1 | 0.79308 | 11103.12 | 40000 | 0 | 2130.1 | 0 | 5034.7 | 6068.42 | 6068.42 | 0 | 0 | 0 | 0
2022093014 | 6 | 0.62267 | 49813.6 | 0 | 0 | 0.06594 | 2307.9 | 0.76845 | 10758.3 | 40000 | 0 | 2307.9 | 0 | 7505.7 | 3252.6 | 3252.6 | 0 | 0 | 0 | 0
2022093015 | 6 | 0.65281 | 52224.8 | 0 | 0 | 0.079 | 2765 | 0.76586 | 10722.04 | 40000 | 0 | 2765 | 0 | 9459.8 | 1262.24 | 1262.24 | 0 | 0 | 0 | 0
2022093016 | 6 | 0.6803 | 54424 | 0 | 0 | 0.09684 | 3389.4 | 0.76691 | 10736.74 | 40000 | 0 | 3389.4 | 0 | 10736.74 | 0 | 0 | 297.86 | 0 | 0 | 297.86
2022093017 | 6 | 0.70003 | 56002.4 | 0 | 0 | 0.13095 | 4583.25 | 0.76994 | 10779.16 | 40000 | 0 | 4583.25 | 0 | 10779.16 | 0 | 0 | 639.99 | 0 | 0 | 639.99
2022093018 | 6 | 0.7003 | 56024 | 0 | 0 | 0.15634 | 5471.9 | 0.6771 | 9479.4 | 40000 | 0 | 5471.9 | 0 | 9479.4 | 0 | 0 | 1072.7 | 0 | 0 | 1072.7
2022093019 | 6 | 0.67217 | 53773.6 | 0 | 0 | 0.19178 | 6712.3 | 0.311 | 4354 | 40000 | 0 | 6712.3 | 0 | 4354 | 0 | 0 | 2707.3 | 0 | 0 | 2707.3
2022093020 | 6 | 0.63702 | 50961.6 | 0 | 0 | 0.21228 | 7429.8 | 0.01353 | 189.42 | 40000 | 0 | 7429.8 | 0 | 189.42 | 0 | 0 | 3342.38 | 0 | 0 | 3342.38
2022093021 | 6 | 0.61172 | 48937.6 | 0 | 0 | 0.30102 | 10535.7 | 0 | 0 | 40000 | 0 | 8937.6 | 1598.1 | 0 | 0 | 1598.1 | 0 | 0 | 0 | 0
2022093022 | 6 | 0.58405 | 46724 | 0 | 0 | 0.39698 | 13894.3 | 0 | 0 | 40000 | 0 | 6724 | 7170.3 | 0 | 0 | 7170.3 | 0 | 0 | 0 | 0
2022093023 | 6 | 0.55158 | 44126.4 | 0 | 0 | 0.44327 | 15514.45 | 0 | 0 | 40000 | 0 | 4126.4 | 11388.05 | 0 | 0 | 11388.05 | 0 | 0 | 0 | 0
2022093024 | 6 | 0.516 | 41280 | 0 | 0 | 0.46112 | 16139.2 | 0 | 0 | 40000 | 0 | 1280 | 14859.2 | 0 | 0 | 14859.2 | 0 | 0 | 0 | 0
2022100101 | 7 | 0.48266 | 38612.8 | 0 | 0 | 0.44886 | 15710.1 | 0 | 0 | 38612.8 | 1387.2 | 0 | 15710.1 | 0 | 0 | 17097.3 | 0 | 0 | 0 | 0
2022100102 | 7 | 0.45785 | 36628 | 0 | 0 | 0.41895 | 14663.25 | 0 | 0 | 36628 | 3372 | 0 | 14663.25 | 0 | 0 | 18035.25 | 0 | 0 | 0 | 0
2022100103 | 7 | 0.44111 | 35288.8 | 0 | 0 | 0.38219 | 13376.65 | 0 | 0 | 35288.8 | 4711.2 | 0 | 13376.65 | 0 | 0 | 18087.85 | 0 | 0 | 0 | 0
2022100104 | 7 | 0.42964 | 34371.2 | 0 | 0 | 0.35202 | 12320.7 | 0 | 0 | 34371.2 | 5628.8 | 0 | 12320.7 | 0 | 0 | 17949.5 | 0 | 0 | 0 | 0
2022100105 | 7 | 0.42522 | 34017.6 | 0 | 0 | 0.32856 | 11499.6 | 0 | 0 | 34017.6 | 5982.4 | 0 | 11499.6 | 0 | 0 | 17482 | 0 | 0 | 0 | 0
2022100106 | 7 | 0.42475 | 33980 | 0 | 0 | 0.30502 | 10675.7 | 0 | 0 | 33980 | 6020 | 0 | 10675.7 | 0 | 0 | 16695.7 | 0 | 0 | 0 | 0
2022100107 | 7 | 0.43239 | 34591.2 | 0 | 0 | 0.27535 | 9637.25 | 0 | 0 | 34591.2 | 5408.8 | 0 | 9637.25 | 0 | 0 | 15046.05 | 0 | 0 | 0 | 0
2022100108 | 7 | 0.43994 | 35195.2 | 0 | 0 | 0.2489 | 8711.5 | 0.01557 | 217.98 | 35195.2 | 4804.8 | 0 | 8711.5 | 0 | 217.98 | 13734.28 | 0 | 0 | 0 | 0
2022100109 | 7 | 0.45839 | 36671.2 | 0 | 0 | 0.20717 | 7250.95 | 0.32122 | 4497.08 | 36671.2 | 3328.8 | 0 | 7250.95 | 0 | 4497.08 | 15076.83 | 0 | 0 | 0 | 0
2022100110 | 7 | 0.48419 | 38735.2 | 0 | 0 | 0.11667 | 4083.45 | 0.71671 | 10033.94 | 38735.2 | 1264.8 | 0 | 4083.45 | 0 | 10033.94 | 15382.19 | 0 | 0 | 0 | 0
2022100111 | 7 | 0.50925 | 40740 | 0 | 0 | 0.10537 | 3687.95 | 0.80802 | 11312.28 | 40000 | 0 | 740 | 2947.95 | 0 | 11312.28 | 14260.23 | 0 | 0 | 0 | 0
2022100112 | 7 | 0.53254 | 42603.2 | 0 | 0 | 0.08719 | 3051.65 | 0.80984 | 11337.76 | 40000 | 0 | 2603.2 | 448.45 | 0 | 11337.76 | 11786.21 | 0 | 0 | 0 | 0
2022100113 | 7 | 0.55966 | 44772.8 | 0 | 0 | 0.06911 | 2418.85 | 0.80132 | 11218.48 | 40000 | 0 | 2418.85 | 0 | 2353.95 | 8864.53 | 8864.53 | 0 | 0 | 0 | 0
2022100114 | 7 | 0.58828 | 47062.4 | 0 | 0 | 0.08044 | 2815.4 | 0.79763 | 11166.82 | 40000 | 0 | 2815.4 | 0 | 4247 | 6919.82 | 6919.82 | 0 | 0 | 0 | 0
2022100115 | 7 | 0.61831 | 49464.8 | 0 | 0 | 0.10299 | 3604.65 | 0.80476 | 11266.64 | 40000 | 0 | 3604.65 | 0 | 5860.15 | 5406.49 | 5406.49 | 0 | 0 | 0 | 0
2022100116 | 7 | 0.64614 | 51691.2 | 0 | 0 | 0.1214 | 4249 | 0.80121 | 11216.94 | 40000 | 0 | 4249 | 0 | 7442.2 | 3774.74 | 3774.74 | 0 | 0 | 0 | 0
2022100117 | 7 | 0.66451 | 53160.8 | 0 | 0 | 0.1371 | 4798.5 | 0.77531 | 10854.34 | 40000 | 0 | 4798.5 | 0 | 8362.3 | 2492.04 | 2492.04 | 0 | 0 | 0 | 0
2022100118 | 7 | 0.66658 | 53326.4 | 0 | 0 | 0.15929 | 5575.15 | 0.65623 | 9187.22 | 40000 | 0 | 5575.15 | 0 | 7751.25 | 1435.97 | 1435.97 | 0 | 0 | 0 | 0
2022100119 | 7 | 0.64345 | 51476 | 0 | 0 | 0.18123 | 6343.05 | 0.24905 | 3486.7 | 40000 | 0 | 6343.05 | 0 | 3486.7 | 0 | 0 | 1646.25 | 0 | 0 | 1646.25
2022100120 | 7 | 0.61331 | 49064.8 | 0 | 0 | 0.21662 | 7581.7 | 0.00803 | 112.42 | 40000 | 0 | 7581.7 | 0 | 112.42 | 0 | 0 | 1370.68 | 0 | 0 | 1370.68
2022100121 | 7 | 0.58838 | 47070.4 | 0 | 0 | 0.29961 | 10486.35 | 0 | 0 | 40000 | 0 | 7070.4 | 3415.95 | 0 | 0 | 3415.95 | 0 | 0 | 0 | 0
2022100122 | 7 | 0.56086 | 44868.8 | 0 | 0 | 0.37431 | 13100.85 | 0 | 0 | 40000 | 0 | 4868.8 | 8232.05 | 0 | 0 | 8232.05 | 0 | 0 | 0 | 0
2022100123 | 7 | 0.53011 | 42408.8 | 0 | 0 | 0.40196 | 14068.6 | 0 | 0 | 40000 | 0 | 2408.8 | 11659.8 | 0 | 0 | 11659.8 | 0 | 0 | 0 | 0
2022100124 | 7 | 0.49769 | 39815.2 | 0 | 0 | 0.39938 | 13978.3 | 0 | 0 | 39815.2 | 184.8 | 0 | 13978.3 | 0 | 0 | 14163.1 | 0 | 0 | 0 | 0
2022100201 | 1 | 0.46992 | 37593.6 | 0 | 0 | 0.37751 | 13212.85 | 0 | 0 | 37593.6 | 2406.4 | 0 | 13212.85 | 0 | 0 | 15619.25 | 0 | 0 | 0 | 0
2022100202 | 1 | 0.44728 | 35782.4 | 0 | 0 | 0.34724 | 12153.4 | 0 | 0 | 35782.4 | 4217.6 | 0 | 12153.4 | 0 | 0 | 16371 | 0 | 0 | 0 | 0
2022100203 | 1 | 0.43096 | 34476.8 | 0 | 0 | 0.31218 | 10926.3 | 0 | 0 | 34476.8 | 5523.2 | 0 | 10926.3 | 0 | 0 | 16449.5 | 0 | 0 | 0 | 0
2022100204 | 1 | 0.42256 | 33804.8 | 0 | 0 | 0.27348 | 9571.8 | 0 | 0 | 33804.8 | 6195.2 | 0 | 9571.8 | 0 | 0 | 15767 | 0 | 0 | 0 | 0
2022100205 | 1 | 0.4167 | 33336 | 0 | 0 | 0.22832 | 7991.2 | 0 | 0 | 33336 | 6664 | 0 | 7991.2 | 0 | 0 | 14655.2 | 0 | 0 | 0 | 0
2022100206 | 1 | 0.41399 | 33119.2 | 0 | 0 | 0.18215 | 6375.25 | 0 | 0 | 33119.2 | 6880.8 | 0 | 6375.25 | 0 | 0 | 13256.05 | 0 | 0 | 0 | 0
2022100207 | 1 | 0.42041 | 33632.8 | 0 | 0 | 0.1521 | 5323.5 | 0 | 0 | 33632.8 | 6367.2 | 0 | 5323.5 | 0 | 0 | 11690.7 | 0 | 0 | 0 | 0
2022100208 | 1 | 0.42705 | 34164 | 0 | 0 | 0.12792 | 4477.2 | 0.01286 | 180.04 | 34164 | 5836 | 0 | 4477.2 | 0 | 180.04 | 10493.24 | 0 | 0 | 0 | 0
2022100209 | 1 | 0.44412 | 35529.6 | 0 | 0 | 0.10398 | 3639.3 | 0.28783 | 4029.62 | 35529.6 | 4470.4 | 0 | 3639.3 | 0 | 4029.62 | 12139.32 | 0 | 0 | 0 | 0
2022100210 | 1 | 0.47026 | 37620.8 | 0 | 0 | 0.05351 | 1872.85 | 0.66235 | 9272.9 | 37620.8 | 2379.2 | 0 | 1872.85 | 0 | 9272.9 | 13524.95 | 0 | 0 | 0 | 0
2022100211 | 1 | 0.49684 | 39747.2 | 0 | 0 | 0.05514 | 1929.9 | 0.74665 | 10453.1 | 39747.2 | 252.8 | 0 | 1929.9 | 0 | 10453.1 | 12635.8 | 0 | 0 | 0 | 0
2022100212 | 1 | 0.52645 | 42116 | 0 | 0 | 0.0546 | 1911 | 0.76139 | 10659.46 | 40000 | 0 | 1911 | 0 | 205 | 10454.46 | 10454.46 | 0 | 0 | 0 | 0
2022100213 | 1 | 0.55533 | 44426.4 | 0 | 0 | 0.03806 | 1332.1 | 0.75848 | 10618.72 | 40000 | 0 | 1332.1 | 0 | 3094.3 | 7524.42 | 7524.42 | 0 | 0 | 0 | 0
2022100214 | 1 | 0.58408 | 46726.4 | 0 | 0 | 0.04221 | 1477.35 | 0.77414 | 10837.96 | 40000 | 0 | 1477.35 | 0 | 5249.05 | 5588.91 | 5588.91 | 0 | 0 | 0 | 0
2022100215 | 1 | 0.61332 | 49065.6 | 0 | 0 | 0.05003 | 1751.05 | 0.75327 | 10545.78 | 40000 | 0 | 1751.05 | 0 | 7314.55 | 3231.23 | 3231.23 | 0 | 0 | 0 | 0
2022100216 | 1 | 0.64074 | 51259.2 | 0 | 0 | 0.05669 | 1984.15 | 0.75144 | 10520.16 | 40000 | 0 | 1984.15 | 0 | 9275.05 | 1245.11 | 1245.11 | 0 | 0 | 0 | 0
2022100217 | 1 | 0.65659 | 52527.2 | 0 | 0 | 0.06534 | 2286.9 | 0.69841 | 9777.74 | 40000 | 0 | 2286.9 | 0 | 9777.74 | 0 | 0 | 462.56 | 0 | 0 | 462.56
2022100218 | 1 | 0.65879 | 52703.2 | 0 | 0 | 0.07986 | 2795.1 | 0.5968 | 8355.2 | 40000 | 0 | 2795.1 | 0 | 8355.2 | 0 | 0 | 1552.9 | 0 | 0 | 1552.9
2022100219 | 1 | 0.64272 | 51417.6 | 0 | 0 | 0.10092 | 3532.2 | 0.27204 | 3808.56 | 40000 | 0 | 3532.2 | 0 | 3808.56 | 0 | 0 | 4076.84 | 0 | 0 | 4076.84
2022100220 | 1 | 0.62769 | 50215.2 | 0 | 0 | 0.15315 | 5360.25 | 0.01282 | 179.48 | 40000 | 0 | 5360.25 | 0 | 179.48 | 0 | 0 | 4675.47 | 0 | 0 | 4675.47
2022100221 | 1 | 0.60499 | 48399.2 | 0 | 0 | 0.23319 | 8161.65 | 0 | 0 | 40000 | 0 | 8161.65 | 0 | 0 | 0 | 0 | 237.55 | 0 | 0 | 237.55
2022100222 | 1 | 0.57715 | 46172 | 0 | 0 | 0.29141 | 10199.35 | 0 | 0 | 40000 | 0 | 6172 | 4027.35 | 0 | 0 | 4027.35 | 0 | 0 | 0 | 0
2022100223 | 1 | 0.53457 | 42765.6 | 0 | 0 | 0.31841 | 11144.35 | 0 | 0 | 40000 | 0 | 2765.6 | 8378.75 | 0 | 0 | 8378.75 | 0 | 0 | 0 | 0
2022100224 | 1 | 0.49488 | 39590.4 | 0 | 0 | 0.33442 | 11704.7 | 0 | 0 | 39590.4 | 409.6 | 0 | 11704.7 | 0 | 0 | 12114.3 | 0 | 0 | 0 | 0
2022100301 | 2 | 0.46167 | 36933.6 | 0 | 0 | 0.31752 | 11113.2 | 0 | 0 | 36933.6 | 3066.4 | 0 | 11113.2 | 0 | 0 | 14179.6 | 0 | 0 | 0 | 0
2022100302 | 2 | 0.4417 | 35336 | 0 | 0 | 0.30352 | 10623.2 | 0 | 0 | 35336 | 4664 | 0 | 10623.2 | 0 | 0 | 15287.2 | 0 | 0 | 0 | 0
2022100303 | 2 | 0.42956 | 34364.8 | 0 | 0 | 0.26744 | 9360.4 | 0 | 0 | 34364.8 | 5635.2 | 0 | 9360.4 | 0 | 0 | 14995.6 | 0 | 0 | 0 | 0
2022100304 | 2 | 0.42494 | 33995.2 | 0 | 0 | 0.22286 | 7800.1 | 0 | 0 | 33995.2 | 6004.8 | 0 | 7800.1 | 0 | 0 | 13804.9 | 0 | 0 | 0 | 0
2022100305 | 2 | 0.42776 | 34220.8 | 0 | 0 | 0.18292 | 6402.2 | 0 | 0 | 34220.8 | 5779.2 | 0 | 6402.2 | 0 | 0 | 12181.4 | 0 | 0 | 0 | 0
2022100306 | 2 | 0.44651 | 35720.8 | 0 | 0 | 0.15048 | 5266.8 | 0 | 0 | 35720.8 | 4279.2 | 0 | 5266.8 | 0 | 0 | 9546 | 0 | 0 | 0 | 0
2022100307 | 2 | 0.47684 | 38147.2 | 0 | 0 | 0.12822 | 4487.7 | 0 | 0 | 38147.2 | 1852.8 | 0 | 4487.7 | 0 | 0 | 6340.5 | 0 | 0 | 0 | 0
2022100308 | 2 | 0.4897 | 39176 | 0 | 0 | 0.11981 | 4193.35 | 0.01267 | 177.38 | 39176 | 824 | 0 | 4193.35 | 0 | 177.38 | 5194.73 | 0 | 0 | 0 | 0
2022100309 | 2 | 0.4995 | 39960 | 0 | 0 | 0.11524 | 4033.4 | 0.23747 | 3324.58 | 39960 | 40 | 0 | 4033.4 | 0 | 3324.58 | 7397.98 | 0 | 0 | 0 | 0
2022100310 | 2 | 0.51963 | 41570.4 | 0 | 0 | 0.0677 | 2369.5 | 0.57664 | 8072.96 | 40000 | 0 | 1570.4 | 799.1 | 0 | 8072.96 | 8872.06 | 0 | 0 | 0 | 0
2022100311 | 2 | 0.53855 | 43084 | 0 | 0 | 0.07097 | 2483.95 | 0.70803 | 9912.42 | 40000 | 0 | 2483.95 | 0 | 600.05 | 9312.37 | 9312.37 | 0 | 0 | 0 | 0
2022100312 | 2 | 0.5605 | 44840 | 0 | 0 | 0.07502 | 2625.7 | 0.76779 | 10749.06 | 40000 | 0 | 2625.7 | 0 | 2214.3 | 8534.76 | 8534.76 | 0 | 0 | 0 | 0
2022100313 | 2 | 0.58933 | 47146.4 | 0 | 0 | 0.06377 | 2231.95 | 0.74075 | 10370.5 | 40000 | 0 | 2231.95 | 0 | 4914.45 | 5456.05 | 5456.05 | 0 | 0 | 0 | 0
2022100314 | 2 | 0.62086 | 49668.8 | 0 | 0 | 0.06065 | 2122.75 | 0.75009 | 10501.26 | 40000 | 0 | 2122.75 | 0 | 7546.05 | 2955.21 | 2955.21 | 0 | 0 | 0 | 0
2022100315 | 2 | 0.65276 | 52220.8 | 0 | 0 | 0.06258 | 2190.3 | 0.7474 | 10463.6 | 40000 | 0 | 2190.3 | 0 | 10030.5 | 433.1 | 433.1 | 0 | 0 | 0 | 0
2022100316 | 2 | 0.6814 | 54512 | 0 | 0 | 0.07118 | 2491.3 | 0.74833 | 10476.62 | 40000 | 0 | 2491.3 | 0 | 10476.62 | 0 | 0 | 1544.08 | 0 | 0 | 1544.08
2022100317 | 2 | 0.7009 | 56072 | 0 | 0 | 0.08051 | 2817.85 | 0.69394 | 9715.16 | 40000 | 0 | 2817.85 | 0 | 9715.16 | 0 | 0 | 3538.99 | 0 | 0 | 3538.99
2022100318 | 2 | 0.70095 | 56076 | 0 | 0 | 0.0916 | 3206 | 0.53987 | 7558.18 | 40000 | 0 | 3206 | 0 | 7558.18 | 0 | 0 | 5311.82 | 0 | 0 | 5311.82
2022100319 | 2 | 0.67909 | 54327.2 | 0 | 0 | 0.10525 | 3683.75 | 0.18896 | 2645.44 | 40000 | 0 | 3683.75 | 0 | 2645.44 | 0 | 0 | 7998.01 | 0 | 0 | 7998.01
2022100320 | 2 | 0.65689 | 52551.2 | 0 | 0 | 0.13965 | 4887.75 | 0.00604 | 84.56 | 40000 | 0 | 4887.75 | 0 | 84.56 | 0 | 0 | 7578.89 | 0 | 0 | 7578.89
2022100321 | 2 | 0.63276 | 50620.8 | 0 | 0 | 0.19959 | 6985.65 | 0 | 0 | 40000 | 0 | 6985.65 | 0 | 0 | 0 | 0 | 3635.15 | 0 | 0 | 3635.15
2022100322 | 2 | 0.5977 | 47816 | 0 | 0 | 0.25949 | 9082.15 | 0 | 0 | 40000 | 0 | 7816 | 1266.15 | 0 | 0 | 1266.15 | 0 | 0 | 0 | 0
2022100323 | 2 | 0.55496 | 44396.8 | 0 | 0 | 0.30279 | 10597.65 | 0 | 0 | 40000 | 0 | 4396.8 | 6200.85 | 0 | 0 | 6200.85 | 0 | 0 | 0 | 0
2022100324 | 2 | 0.51245 | 40996 | 0 | 0 | 0.33023 | 11558.05 | 0 | 0 | 40000 | 0 | 996 | 10562.05 | 0 | 0 | 10562.05 | 0 | 0 | 0 | 0
2022100401 | 3 | 0.48206 | 38564.8 | 0 | 0 | 0.32945 | 11530.75 | 0 | 0 | 38564.8 | 1435.2 | 0 | 11530.75 | 0 | 0 | 12965.95 | 0 | 0 | 0 | 0
2022100402 | 3 | 0.46129 | 36903.2 | 0 | 0 | 0.29988 | 10495.8 | 0 | 0 | 36903.2 | 3096.8 | 0 | 10495.8 | 0 | 0 | 13592.6 | 0 | 0 | 0 | 0
2022100403 | 3 | 0.44609 | 35687.2 | 0 | 0 | 0.27447 | 9606.45 | 0 | 0 | 35687.2 | 4312.8 | 0 | 9606.45 | 0 | 0 | 13919.25 | 0 | 0 | 0 | 0
2022100404 | 3 | 0.44016 | 35212.8 | 0 | 0 | 0.24575 | 8601.25 | 0 | 0 | 35212.8 | 4787.2 | 0 | 8601.25 | 0 | 0 | 13388.45 | 0 | 0 | 0 | 0
2022100405 | 3 | 0.44205 | 35364 | 0 | 0 | 0.20598 | 7209.3 | 0 | 0 | 35364 | 4636 | 0 | 7209.3 | 0 | 0 | 11845.3 | 0 | 0 | 0 | 0
2022100406 | 3 | 0.45644 | 36515.2 | 0 | 0 | 0.19065 | 6672.75 | 0 | 0 | 36515.2 | 3484.8 | 0 | 6672.75 | 0 | 0 | 10157.55 | 0 | 0 | 0 | 0
2022100407 | 3 | 0.48604 | 38883.2 | 0 | 0 | 0.17413 | 6094.55 | 0 | 0 | 38883.2 | 1116.8 | 0 | 6094.55 | 0 | 0 | 7211.35 | 0 | 0 | 0 | 0
2022100408 | 3 | 0.49962 | 39969.6 | 0 | 0 | 0.16826 | 5889.1 | 0.0068 | 95.2 | 39969.6 | 30.4 | 0 | 5889.1 | 0 | 95.2 | 6014.7 | 0 | 0 | 0 | 0
2022100409 | 3 | 0.50503 | 40402.4 | 0 | 0 | 0.15052 | 5268.2 | 0.20154 | 2821.56 | 40000 | 0 | 402.4 | 4865.8 | 0 | 2821.56 | 7687.36 | 0 | 0 | 0 | 0
2022100410 | 3 | 0.52329 | 41863.2 | 0 | 0 | 0.08908 | 3117.8 | 0.55587 | 7782.18 | 40000 | 0 | 1863.2 | 1254.6 | 0 | 7782.18 | 9036.78 | 0 | 0 | 0 | 0
2022100411 | 3 | 0.54432 | 43545.6 | 0 | 0 | 0.10259 | 3590.65 | 0.6738 | 9433.2 | 40000 | 0 | 3545.6 | 45.05 | 0 | 9433.2 | 9478.25 | 0 | 0 | 0 | 0
2022100412 | 3 | 0.56955 | 45564 | 0 | 0 | 0.14185 | 4964.75 | 0.6862 | 9606.8 | 40000 | 0 | 4964.75 | 0 | 599.25 | 9007.55 | 9007.55 | 0 | 0 | 0 | 0
2022100413 | 3 | 0.59818 | 47854.4 | 0 | 0 | 0.11568 | 4048.8 | 0.7064 | 9889.6 | 40000 | 0 | 4048.8 | 0 | 3805.6 | 6084 | 6084 | 0 | 0 | 0 | 0
2022100414 | 3 | 0.63143 | 50514.4 | 0 | 0 | 0.0877 | 3069.5 | 0.70768 | 9907.52 | 40000 | 0 | 3069.5 | 0 | 7444.9 | 2462.62 | 2462.62 | 0 | 0 | 0 | 0
2022100415 | 3 | 0.66317 | 53053.6 | 0 | 0 | 0.07607 | 2662.45 | 0.71608 | 10025.12 | 40000 | 0 | 2662.45 | 0 | 10025.12 | 0 | 0 | 366.03 | 0 | 0 | 366.03
2022100416 | 3 | 0.68927 | 55141.6 | 0 | 0 | 0.07156 | 2504.6 | 0.71773 | 10048.22 | 40000 | 0 | 2504.6 | 0 | 10048.22 | 0 | 0 | 2588.78 | 0 | 0 | 2588.78
2022100417 | 3 | 0.70612 | 56489.6 | 0 | 0 | 0.07003 | 2451.05 | 0.67034 | 9384.76 | 40000 | 0 | 2451.05 | 0 | 9384.76 | 0 | 0 | 4653.79 | 0 | 0 | 4653.79
2022100418 | 3 | 0.70618 | 56494.4 | 0 | 0 | 0.07914 | 2769.9 | 0.53328 | 7465.92 | 40000 | 0 | 2769.9 | 0 | 7465.92 | 0 | 0 | 6258.58 | 0 | 0 | 6258.58
2022100419 | 3 | 0.68319 | 54655.2 | 0 | 0 | 0.10308 | 3607.8 | 0.18218 | 2550.52 | 40000 | 0 | 3607.8 | 0 | 2550.52 | 0 | 0 | 8496.88 | 0 | 0 | 8496.88
2022100420 | 3 | 0.66146 | 52916.8 | 0 | 0 | 0.14125 | 4943.75 | 0.00279 | 39.06 | 40000 | 0 | 4943.75 | 0 | 39.06 | 0 | 0 | 7933.99 | 0 | 0 | 7933.99
2022100421 | 3 | 0.63734 | 50987.2 | 0 | 0 | 0.21215 | 7425.25 | 0 | 0 | 40000 | 0 | 7425.25 | 0 | 0 | 0 | 0 | 3561.95 | 0 | 0 | 3561.95
2022100422 | 3 | 0.60268 | 48214.4 | 0 | 0 | 0.28861 | 10101.35 | 0 | 0 | 40000 | 0 | 8214.4 | 1886.95 | 0 | 0 | 1886.95 | 0 | 0 | 0 | 0
2022100423 | 3 | 0.56225 | 44980 | 0 | 0 | 0.34216 | 11975.6 | 0 | 0 | 40000 | 0 | 4980 | 6995.6 | 0 | 0 | 6995.6 | 0 | 0 | 0 | 0
2022100424 | 3 | 0.51887 | 41509.6 | 0 | 0 | 0.35926 | 12574.1 | 0 | 0 | 40000 | 0 | 1509.6 | 11064.5 | 0 | 0 | 11064.5 | 0 | 0 | 0 | 0
2022100501 | 4 | 0.48302 | 38641.6 | 0 | 0 | 0.36127 | 12644.45 | 0 | 0 | 38641.6 | 1358.4 | 0 | 12644.45 | 0 | 0 | 14002.85 | 0 | 0 | 0 | 0
2022100502 | 4 | 0.46047 | 36837.6 | 0 | 0 | 0.34941 | 12229.35 | 0 | 0 | 36837.6 | 3162.4 | 0 | 12229.35 | 0 | 0 | 15391.75 | 0 | 0 | 0 | 0
2022100503 | 4 | 0.44755 | 35804 | 0 | 0 | 0.31134 | 10896.9 | 0 | 0 | 35804 | 4196 | 0 | 10896.9 | 0 | 0 | 15092.9 | 0 | 0 | 0 | 0
2022100504 | 4 | 0.43877 | 35101.6 | 0 | 0 | 0.25878 | 9057.3 | 0 | 0 | 35101.6 | 4898.4 | 0 | 9057.3 | 0 | 0 | 13955.7 | 0 | 0 | 0 | 0
2022100505 | 4 | 0.43958 | 35166.4 | 0 | 0 | 0.21547 | 7541.45 | 0 | 0 | 35166.4 | 4833.6 | 0 | 7541.45 | 0 | 0 | 12375.05 | 0 | 0 | 0 | 0
2022100506 | 4 | 0.4542 | 36336 | 0 | 0 | 0.18196 | 6368.6 | 0 | 0 | 36336 | 3664 | 0 | 6368.6 | 0 | 0 | 10032.6 | 0 | 0 | 0 | 0
2022100507 | 4 | 0.48419 | 38735.2 | 0 | 0 | 0.15184 | 5314.4 | 0 | 0 | 38735.2 | 1264.8 | 0 | 5314.4 | 0 | 0 | 6579.2 | 0 | 0 | 0 | 0
2022100508 | 4 | 0.49672 | 39737.6 | 0 | 0 | 0.13052 | 4568.2 | 0.01087 | 152.18 | 39737.6 | 262.4 | 0 | 4568.2 | 0 | 152.18 | 4982.78 | 0 | 0 | 0 | 0
2022100509 | 4 | 0.5042 | 40336 | 0 | 0 | 0.11008 | 3852.8 | 0.23975 | 3356.5 | 40000 | 0 | 336 | 3516.8 | 0 | 3356.5 | 6873.3 | 0 | 0 | 0 | 0
2022100510 | 4 | 0.52501 | 42000.8 | 0 | 0 | 0.07018 | 2456.3 | 0.50693 | 7097.02 | 40000 | 0 | 2000.8 | 455.5 | 0 | 7097.02 | 7552.52 | 0 | 0 | 0 | 0
2022100511 | 4 | 0.55305 | 44244 | 0 | 0 | 0.07293 | 2552.55 | 0.65773 | 9208.22 | 40000 | 0 | 2552.55 | 0 | 1691.45 | 7516.77 | 7516.77 | 0 | 0 | 0 | 0
2022100512 | 4 | 0.58589 | 46871.2 | 0 | 0 | 0.05636 | 1972.6 | 0.73041 | 10225.74 | 40000 | 0 | 1972.6 | 0 | 4898.6 | 5327.14 | 5327.14 | 0 | 0 | 0 | 0
2022100513 | 4 | 0.6221 | 49768 | 0 | 0 | 0.04678 | 1637.3 | 0.72716 | 10180.24 | 40000 | 0 | 1637.3 | 0 | 8130.7 | 2049.54 | 2049.54 | 0 | 0 | 0 | 0
2022100514 | 4 | 0.65948 | 52758.4 | 0 | 0 | 0.04776 | 1671.6 | 0.68623 | 9607.22 | 40000 | 0 | 1671.6 | 0 | 9607.22 | 0 | 0 | 1479.58 | 0 | 0 | 1479.58
2022100515 | 4 | 0.69221 | 55376.8 | 0 | 0 | 0.06028 | 2109.8 | 0.65943 | 9232.02 | 40000 | 0 | 2109.8 | 0 | 9232.02 | 0 | 0 | 4034.98 | 0 | 0 | 4034.98
2022100516 | 4 | 0.71894 | 57515.2 | 0 | 0 | 0.08258 | 2890.3 | 0.61569 | 8619.66 | 40000 | 0 | 2890.3 | 0 | 8619.66 | 0 | 0 | 6005.24 | 0 | 0 | 6005.24
2022100517 | 4 | 0.73781 | 59024.8 | 0 | 0 | 0.09049 | 3167.15 | 0.58605 | 8204.7 | 40000 | 0 | 3167.15 | 0 | 8204.7 | 0 | 0 | 7652.95 | 0 | 0 | 7652.95
2022100518 | 4 | 0.73426 | 58740.8 | 0 | 0 | 0.10379 | 3632.65 | 0.44458 | 6224.12 | 40000 | 0 | 3632.65 | 0 | 6224.12 | 0 | 0 | 8884.03 | 0 | 0 | 8884.03
2022100519 | 4 | 0.70439 | 56351.2 | 0 | 0 | 0.14134 | 4946.9 | 0.11144 | 1560.16 | 40000 | 0 | 4946.9 | 0 | 1560.16 | 0 | 0 | 9844.14 | 0 | 0 | 9844.14
2022100520 | 4 | 0.6815 | 54520 | 0 | 0 | 0.1704 | 5964 | 0.00245 | 34.3 | 40000 | 0 | 5964 | 0 | 34.3 | 0 | 0 | 8521.7 | 0 | 0 | 8521.7
2022100521 | 4 | 0.65615 | 52492 | 0 | 0 | 0.20478 | 7167.3 | 0 | 0 | 40000 | 0 | 7167.3 | 0 | 0 | 0 | 0 | 5324.7 | 0 | 0 | 5324.7
2022100522 | 4 | 0.61756 | 49404.8 | 0 | 0 | 0.21246 | 7436.1 | 0 | 0 | 40000 | 0 | 7436.1 | 0 | 0 | 0 | 0 | 1968.7 | 0 | 0 | 1968.7
2022100523 | 4 | 0.57372 | 45897.6 | 0 | 0 | 0.20291 | 7101.85 | 0 | 0 | 40000 | 0 | 5897.6 | 1204.25 | 0 | 0 | 1204.25 | 0 | 0 | 0 | 0
2022100524 | 4 | 0.52611 | 42088.8 | 0 | 0 | 0.17146 | 6001.1 | 0 | 0 | 40000 | 0 | 2088.8 | 3912.3 | 0 | 0 | 3912.3 | 0 | 0 | 0 | 0
2022100601 | 5 | 0.49067 | 39253.6 | 0 | 0 | 0.15148 | 5301.8 | 0 | 0 | 39253.6 | 746.4 | 0 | 5301.8 | 0 | 0 | 6048.2 | 0 | 0 | 0 | 0
2022100602 | 5 | 0.4675 | 37400 | 0 | 0 | 0.14313 | 5009.55 | 0 | 0 | 37400 | 2600 | 0 | 5009.55 | 0 | 0 | 7609.55 | 0 | 0 | 0 | 0
2022100603 | 5 | 0.45242 | 36193.6 | 0 | 0 | 0.12811 | 4483.85 | 0 | 0 | 36193.6 | 3806.4 | 0 | 4483.85 | 0 | 0 | 8290.25 | 0 | 0 | 0 | 0
2022100604 | 5 | 0.44549 | 35639.2 | 0 | 0 | 0.11332 | 3966.2 | 0 | 0 | 35639.2 | 4360.8 | 0 | 3966.2 | 0 | 0 | 8327 | 0 | 0 | 0 | 0
2022100605 | 5 | 0.44707 | 35765.6 | 0 | 0 | 0.09794 | 3427.9 | 0 | 0 | 35765.6 | 4234.4 | 0 | 3427.9 | 0 | 0 | 7662.3 | 0 | 0 | 0 | 0
2022100606 | 5 | 0.46232 | 36985.6 | 0 | 0 | 0.09191 | 3216.85 | 0 | 0 | 36985.6 | 3014.4 | 0 | 3216.85 | 0 | 0 | 6231.25 | 0 | 0 | 0 | 0
2022100607 | 5 | 0.492 | 39360 | 0 | 0 | 0.07275 | 2546.25 | 0 | 0 | 39360 | 640 | 0 | 2546.25 | 0 | 0 | 3186.25 | 0 | 0 | 0 | 0
2022100608 | 5 | 0.50523 | 40418.4 | 0 | 0 | 0.05965 | 2087.75 | 0.00955 | 133.7 | 40000 | 0 | 418.4 | 1669.35 | 0 | 133.7 | 1803.05 | 0 | 0 | 0 | 0
2022100609 | 5 | 0.51614 | 41291.2 | 0 | 0 | 0.05426 | 1899.1 | 0.21944 | 3072.16 | 40000 | 0 | 1291.2 | 607.9 | 0 | 3072.16 | 3680.06 | 0 | 0 | 0 | 0
2022100610 | 5 | 0.53998 | 43198.4 | 0 | 0 | 0.03359 | 1175.65 | 0.52107 | 7294.98 | 40000 | 0 | 1175.65 | 0 | 2022.75 | 5272.23 | 5272.23 | 0 | 0 | 0 | 0
2022100611 | 5 | 0.57078 | 45662.4 | 0 | 0 | 0.02381 | 833.35 | 0.62742 | 8783.88 | 40000 | 0 | 833.35 | 0 | 4829.05 | 3954.83 | 3954.83 | 0 | 0 | 0 | 0
2022100612 | 5 | 0.60443 | 48354.4 | 0 | 0 | 0.0211 | 738.5 | 0.6374 | 8923.6 | 40000 | 0 | 738.5 | 0 | 7615.9 | 1307.7 | 1307.7 | 0 | 0 | 0 | 0
2022100613 | 5 | 0.64521 | 51616.8 | 0 | 0 | 0.02271 | 794.85 | 0.64842 | 9077.88 | 40000 | 0 | 794.85 | 0 | 9077.88 | 0 | 0 | 1744.07 | 0 | 0 | 1744.07
2022100614 | 5 | 0.68302 | 54641.6 | 0 | 0 | 0.02507 | 877.45 | 0.64781 | 9069.34 | 40000 | 0 | 877.45 | 0 | 9069.34 | 0 | 0 | 4694.81 | 0 | 0 | 4694.81
2022100615 | 5 | 0.71317 | 57053.6 | 0 | 0 | 0.02603 | 911.05 | 0.63662 | 8912.68 | 40000 | 0 | 911.05 | 0 | 8912.68 | 0 | 0 | 7229.87 | 0 | 0 | 7229.87
2022100616 | 5 | 0.73553 | 58842.4 | 0 | 0 | 0.0345 | 1207.5 | 0.60128 | 8417.92 | 40000 | 0 | 1207.5 | 0 | 8417.92 | 0 | 0 | 9216.98 | 0 | 0 | 9216.98
2022100617 | 5 | 0.74573 | 59658.4 | 0 | 0 | 0.04803 | 1681.05 | 0.50536 | 7075.04 | 40000 | 0 | 1681.05 | 0 | 7075.04 | 0 | 0 | 10902.31 | 0 | 0 | 10902.31
2022100618 | 5 | 0.73913 | 59130.4 | 0 | 0 | 0.06893 | 2412.55 | 0.38573 | 5400.22 | 40000 | 0 | 2412.55 | 0 | 5400.22 | 0 | 0 | 11317.63 | 0 | 0 | 11317.63
2022100619 | 5 | 0.70954 | 56763.2 | 0 | 0 | 0.0721 | 2523.5 | 0.1383 | 1936.2 | 40000 | 0 | 2523.5 | 0 | 1936.2 | 0 | 0 | 12303.5 | 0 | 0 | 12303.5
2022100620 | 5 | 0.68461 | 54768.8 | 0 | 0 | 0.09069 | 3174.15 | 0.00762 | 106.68 | 40000 | 0 | 3174.15 | 0 | 106.68 | 0 | 0 | 11487.97 | 0 | 0 | 11487.97
2022100621 | 5 | 0.66141 | 52912.8 | 0 | 0 | 0.1134 | 3969 | 0 | 0 | 40000 | 0 | 3969 | 0 | 0 | 0 | 0 | 8943.8 | 0 | 0 | 8943.8
2022100622 | 5 | 0.62503 | 50002.4 | 0 | 0 | 0.13512 | 4729.2 | 0 | 0 | 40000 | 0 | 4729.2 | 0 | 0 | 0 | 0 | 5273.2 | 0 | 0 | 5273.2
2022100623 | 5 | 0.58327 | 46661.6 | 0 | 0 | 0.1377 | 4819.5 | 0 | 0 | 40000 | 0 | 4819.5 | 0 | 0 | 0 | 0 | 1842.1 | 0 | 0 | 1842.1
2022100624 | 5 | 0.54118 | 43294.4 | 0 | 0 | 0.14375 | 5031.25 | 0 | 0 | 40000 | 0 | 3294.4 | 1736.85 | 0 | 0 | 1736.85 | 0 | 0 | 0 | 0
2022100701 | 6 | 0.50683 | 40546.4 | 0 | 0 | 0.13931 | 4875.85 | 0 | 0 | 40000 | 0 | 546.4 | 4329.45 | 0 | 0 | 4329.45 | 0 | 0 | 0 | 0
2022100702 | 6 | 0.48152 | 38521.6 | 0 | 0 | 0.13404 | 4691.4 | 0 | 0 | 38521.6 | 1478.4 | 0 | 4691.4 | 0 | 0 | 6169.8 | 0 | 0 | 0 | 0
2022100703 | 6 | 0.46615 | 37292 | 0 | 0 | 0.13639 | 4773.65 | 0 | 0 | 37292 | 2708 | 0 | 4773.65 | 0 | 0 | 7481.65 | 0 | 0 | 0 | 0
2022100704 | 6 | 0.45698 | 36558.4 | 0 | 0 | 0.12403 | 4341.05 | 0 | 0 | 36558.4 | 3441.6 | 0 | 4341.05 | 0 | 0 | 7782.65 | 0 | 0 | 0 | 0
2022100705 | 6 | 0.4584 | 36672 | 0 | 0 | 0.104 | 3640 | 0 | 0 | 36672 | 3328 | 0 | 3640 | 0 | 0 | 6968 | 0 | 0 | 0 | 0
2022100706 | 6 | 0.47424 | 37939.2 | 0 | 0 | 0.09329 | 3265.15 | 0 | 0 | 37939.2 | 2060.8 | 0 | 3265.15 | 0 | 0 | 5325.95 | 0 | 0 | 0 | 0
2022100707 | 6 | 0.50057 | 40045.6 | 0 | 0 | 0.09134 | 3196.9 | 0 | 0 | 40000 | 0 | 45.6 | 3151.3 | 0 | 0 | 3151.3 | 0 | 0 | 0 | 0
2022100708 | 6 | 0.51251 | 41000.8 | 0 | 0 | 0.09932 | 3476.2 | 0.00603 | 84.42 | 40000 | 0 | 1000.8 | 2475.4 | 0 | 84.42 | 2559.82 | 0 | 0 | 0 | 0
2022100709 | 6 | 0.5221 | 41768 | 0 | 0 | 0.1026 | 3591 | 0.11499 | 1609.86 | 40000 | 0 | 1768 | 1823 | 0 | 1609.86 | 3432.86 | 0 | 0 | 0 | 0
2022100710 | 6 | 0.54691 | 43752.8 | 0 | 0 | 0.0798 | 2793 | 0.31849 | 4458.86 | 40000 | 0 | 2793 | 0 | 959.8 | 3499.06 | 3499.06 | 0 | 0 | 0 | 0
2022100711 | 6 | 0.57119 | 45695.2 | 0 | 0 | 0.08437 | 2952.95 | 0.44655 | 6251.7 | 40000 | 0 | 2952.95 | 0 | 2742.25 | 3509.45 | 3509.45 | 0 | 0 | 0 | 0
2022100712 | 6 | 0.596 | 47680 | 0 | 0 | 0.09248 | 3236.8 | 0.56309 | 7883.26 | 40000 | 0 | 3236.8 | 0 | 4443.2 | 3440.06 | 3440.06 | 0 | 0 | 0 | 0
2022100713 | 6 | 0.62271 | 49816.8 | 0 | 0 | 0.10583 | 3704.05 | 0.57128 | 7997.92 | 40000 | 0 | 3704.05 | 0 | 6112.75 | 1885.17 | 1885.17 | 0 | 0 | 0 | 0
2022100714 | 6 | 0.64799 | 51839.2 | 0 | 0 | 0.12756 | 4464.6 | 0.54443 | 7622.02 | 40000 | 0 | 4464.6 | 0 | 7374.6 | 247.42 | 247.42 | 0 | 0 | 0 | 0
2022100715 | 6 | 0.66644 | 53315.2 | 0 | 0 | 0.15474 | 5415.9 | 0.46951 | 6573.14 | 40000 | 0 | 5415.9 | 0 | 6573.14 | 0 | 0 | 1326.16 | 0 | 0 | 1326.16
2022100716 | 6 | 0.6787 | 54296 | 0 | 0 | 0.19211 | 6723.85 | 0.36073 | 5050.22 | 40000 | 0 | 6723.85 | 0 | 5050.22 | 0 | 0 | 2521.93 | 0 | 0 | 2521.93
2022100717 | 6 | 0.68237 | 54589.6 | 0 | 0 | 0.24832 | 8691.2 | 0.29918 | 4188.52 | 40000 | 0 | 8691.2 | 0 | 4188.52 | 0 | 0 | 1709.88 | 0 | 0 | 1709.88
2022100718 | 6 | 0.67145 | 53716 | 0 | 0 | 0.25812 | 9034.2 | 0.21291 | 2980.74 | 40000 | 0 | 9034.2 | 0 | 2980.74 | 0 | 0 | 1701.06 | 0 | 0 | 1701.06
2022100719 | 6 | 0.64892 | 51913.6 | 0 | 0 | 0.27246 | 9536.1 | 0.06267 | 877.38 | 40000 | 0 | 9536.1 | 0 | 877.38 | 0 | 0 | 1500.12 | 0 | 0 | 1500.12
2022100720 | 6 | 0.63556 | 50844.8 | 0 | 0 | 0.27273 | 9545.55 | 0.0016 | 22.4 | 40000 | 0 | 9545.55 | 0 | 22.4 | 0 | 0 | 1276.85 | 0 | 0 | 1276.85
2022100721 | 6 | 0.61721 | 49376.8 | 0 | 0 | 0.28104 | 9836.4 | 0 | 0 | 40000 | 0 | 9376.8 | 459.6 | 0 | 0 | 459.6 | 0 | 0 | 0 | 0
2022100722 | 6 | 0.59424 | 47539.2 | 0 | 0 | 0.25904 | 9066.4 | 0 | 0 | 40000 | 0 | 7539.2 | 1527.2 | 0 | 0 | 1527.2 | 0 | 0 | 0 | 0
2022100723 | 6 | 0.56349 | 45079.2 | 0 | 0 | 0.23286 | 8150.1 | 0 | 0 | 40000 | 0 | 5079.2 | 3070.9 | 0 | 0 | 3070.9 | 0 | 0 | 0 | 0
2022100724 | 6 | 0.5319 | 42552 | 0 | 0 | 0.214 | 7490 | 0 | 0 | 40000 | 0 | 2552 | 4938 | 0 | 0 | 4938 | 0 | 0 | 0 | 0
2022100801 | 7 | 0.50065 | 40052 | 0 | 0 | 0.19278 | 6747.3 | 0 | 0 | 40000 | 0 | 52 | 6695.3 | 0 | 0 | 6695.3 | 0 | 0 | 0 | 0
2022100802 | 7 | 0.47839 | 38271.2 | 0 | 0 | 0.1861 | 6513.5 | 0 | 0 | 38271.2 | 1728.8 | 0 | 6513.5 | 0 | 0 | 8242.3 | 0 | 0 | 0 | 0
2022100803 | 7 | 0.46007 | 36805.6 | 0 | 0 | 0.19282 | 6748.7 | 0 | 0 | 36805.6 | 3194.4 | 0 | 6748.7 | 0 | 0 | 9943.1 | 0 | 0 | 0 | 0
2022100804 | 7 | 0.44691 | 35752.8 | 0 | 0 | 0.19973 | 6990.55 | 0 | 0 | 35752.8 | 4247.2 | 0 | 6990.55 | 0 | 0 | 11237.75 | 0 | 0 | 0 | 0
2022100805 | 7 | 0.44339 | 35471.2 | 0 | 0 | 0.2196 | 7686 | 0 | 0 | 35471.2 | 4528.8 | 0 | 7686 | 0 | 0 | 12214.8 | 0 | 0 | 0 | 0
2022100806 | 7 | 0.44576 | 35660.8 | 0 | 0 | 0.2316 | 8106 | 0 | 0 | 35660.8 | 4339.2 | 0 | 8106 | 0 | 0 | 12445.2 | 0 | 0 | 0 | 0
2022100807 | 7 | 0.45337 | 36269.6 | 0 | 0 | 0.23269 | 8144.15 | 0 | 0 | 36269.6 | 3730.4 | 0 | 8144.15 | 0 | 0 | 11874.55 | 0 | 0 | 0 | 0
2022100808 | 7 | 0.46271 | 37016.8 | 0 | 0 | 0.24071 | 8424.85 | 0.00419 | 58.66 | 37016.8 | 2983.2 | 0 | 8424.85 | 0 | 58.66 | 11466.71 | 0 | 0 | 0 | 0
2022100809 | 7 | 0.47604 | 38083.2 | 0 | 0 | 0.22222 | 7777.7 | 0.15011 | 2101.54 | 38083.2 | 1916.8 | 0 | 7777.7 | 0 | 2101.54 | 11796.04 | 0 | 0 | 0 | 0
2022100810 | 7 | 0.4991 | 39928 | 0 | 0 | 0.17627 | 6169.45 | 0.4227 | 5917.8 | 39928 | 72 | 0 | 6169.45 | 0 | 5917.8 | 12159.25 | 0 | 0 | 0 | 0
2022100811 | 7 | 0.52883 | 42306.4 | 0 | 0 | 0.14357 | 5024.95 | 0.49482 | 6927.48 | 40000 | 0 | 2306.4 | 2718.55 | 0 | 6927.48 | 9646.03 | 0 | 0 | 0 | 0
2022100812 | 7 | 0.5554 | 44432 | 0 | 0 | 0.11512 | 4029.2 | 0.55385 | 7753.9 | 40000 | 0 | 4029.2 | 0 | 402.8 | 7351.1 | 7351.1 | 0 | 0 | 0 | 0
2022100813 | 7 | 0.58339 | 46671.2 | 0 | 0 | 0.10238 | 3583.3 | 0.59078 | 8270.92 | 40000 | 0 | 3583.3 | 0 | 3087.9 | 5183.02 | 5183.02 | 0 | 0 | 0 | 0
2022100814 | 7 | 0.61241 | 48992.8 | 0 | 0 | 0.0989 | 3461.5 | 0.57295 | 8021.3 | 40000 | 0 | 3461.5 | 0 | 5531.3 | 2490 | 2490 | 0 | 0 | 0 | 0
2022100815 | 7 | 0.6367 | 50936 | 0 | 0 | 0.09148 | 3201.8 | 0.55754 | 7805.56 | 40000 | 0 | 3201.8 | 0 | 7734.2 | 71.36 | 71.36 | 0 | 0 | 0 | 0
2022100816 | 7 | 0.65577 | 52461.6 | 0 | 0 | 0.08893 | 3112.55 | 0.50867 | 7121.38 | 40000 | 0 | 3112.55 | 0 | 7121.38 | 0 | 0 | 2227.67 | 0 | 0 | 2227.67
2022100817 | 7 | 0.66295 | 53036 | 0 | 0 | 0.09881 | 3458.35 | 0.36575 | 5120.5 | 40000 | 0 | 3458.35 | 0 | 5120.5 | 0 | 0 | 4457.15 | 0 | 0 | 4457.15
2022100818 | 7 | 0.6569 | 52552 | 0 | 0 | 0.1135 | 3972.5 | 0.23866 | 3341.24 | 40000 | 0 | 3972.5 | 0 | 3341.24 | 0 | 0 | 5238.26 | 0 | 0 | 5238.26
2022100819 | 7 | 0.63448 | 50758.4 | 0 | 0 | 0.12842 | 4494.7 | 0.06982 | 977.48 | 40000 | 0 | 4494.7 | 0 | 977.48 | 0 | 0 | 5286.22 | 0 | 0 | 5286.22
2022100820 | 7 | 0.62037 | 49629.6 | 0 | 0 | 0.14577 | 5101.95 | 0.00071 | 9.94 | 40000 | 0 | 5101.95 | 0 | 9.94 | 0 | 0 | 4517.71 | 0 | 0 | 4517.71
2022100821 | 7 | 0.59899 | 47919.2 | 0 | 0 | 0.16904 | 5916.4 | 0.00017 | 2.38 | 40000 | 0 | 5916.4 | 0 | 2.38 | 0 | 0 | 2000.42 | 0 | 0 | 2000.42
2022100822 | 7 | 0.57174 | 45739.2 | 0 | 0 | 0.17286 | 6050.1 | 0.00017 | 2.38 | 40000 | 0 | 5739.2 | 310.9 | 0 | 2.38 | 313.28 | 0 | 0 | 0 | 0
2022100823 | 7 | 0.54184 | 43347.2 | 0 | 0 | 0.16515 | 5780.25 | 0.00011 | 1.54 | 40000 | 0 | 3347.2 | 2433.05 | 0 | 1.54 | 2434.59 | 0 | 0 | 0 | 0
2022100824 | 7 | 0.51231 | 40984.8 | 0 | 0 | 0.1395 | 4882.5 | 0 | 0 | 40000 | 0 | 984.8 | 3897.7 | 0 | 0 | 3897.7 | 0 | 0 | 0 | 0
2022100901 | 1 | 0.48398 | 38718.4 | 0 | 0 | 0.12816 | 4485.6 | 0 | 0 | 38718.4 | 1281.6 | 0 | 4485.6 | 0 | 0 | 5767.2 | 0 | 0 | 0 | 0
2022100902 | 1 | 0.4614 | 36912 | 0 | 0 | 0.10773 | 3770.55 | 0 | 0 | 36912 | 3088 | 0 | 3770.55 | 0 | 0 | 6858.55 | 0 | 0 | 0 | 0
2022100903 | 1 | 0.4468 | 35744 | 0 | 0 | 0.09384 | 3284.4 | 0 | 0 | 35744 | 4256 | 0 | 3284.4 | 0 | 0 | 7540.4 | 0 | 0 | 0 | 0
2022100904 | 1 | 0.43541 | 34832.8 | 0 | 0 | 0.0885 | 3097.5 | 0 | 0 | 34832.8 | 5167.2 | 0 | 3097.5 | 0 | 0 | 8264.7 | 0 | 0 | 0 | 0
2022100905 | 1 | 0.42774 | 34219.2 | 0 | 0 | 0.08284 | 2899.4 | 0 | 0 | 34219.2 | 5780.8 | 0 | 2899.4 | 0 | 0 | 8680.2 | 0 | 0 | 0 | 0
2022100906 | 1 | 0.42846 | 34276.8 | 0 | 0 | 0.08342 | 2919.7 | 0 | 0 | 34276.8 | 5723.2 | 0 | 2919.7 | 0 | 0 | 8642.9 | 0 | 0 | 0 | 0
2022100907 | 1 | 0.43247 | 34597.6 | 0 | 0 | 0.08081 | 2828.35 | 0 | 0 | 34597.6 | 5402.4 | 0 | 2828.35 | 0 | 0 | 8230.75 | 0 | 0 | 0 | 0
2022100908 | 1 | 0.4372 | 34976 | 0 | 0 | 0.09184 | 3214.4 | 0.00471 | 65.94 | 34976 | 5024 | 0 | 3214.4 | 0 | 65.94 | 8304.34 | 0 | 0 | 0 | 0
2022100909 | 1 | 0.45686 | 36548.8 | 0 | 0 | 0.0883 | 3090.5 | 0.13712 | 1919.68 | 36548.8 | 3451.2 | 0 | 3090.5 | 0 | 1919.68 | 8461.38 | 0 | 0 | 0 | 0
2022100910 | 1 | 0.48463 | 38770.4 | 0 | 0 | 0.0545 | 1907.5 | 0.34562 | 4838.68 | 38770.4 | 1229.6 | 0 | 1907.5 | 0 | 4838.68 | 7975.78 | 0 | 0 | 0 | 0
2022100911 | 1 | 0.51284 | 41027.2 | 0 | 0 | 0.05108 | 1787.8 | 0.47812 | 6693.68 | 40000 | 0 | 1027.2 | 760.6 | 0 | 6693.68 | 7454.28 | 0 | 0 | 0 | 0
2022100912 | 1 | 0.54367 | 43493.6 | 0 | 0 | 0.08214 | 2874.9 | 0.529 | 7406 | 40000 | 0 | 2874.9 | 0 | 618.7 | 6787.3 | 6787.3 | 0 | 0 | 0 | 0
2022100913 | 1 | 0.57719 | 46175.2 | 0 | 0 | 0.11112 | 3889.2 | 0.54377 | 7612.78 | 40000 | 0 | 3889.2 | 0 | 2286 | 5326.78 | 5326.78 | 0 | 0 | 0 | 0
2022100914 | 1 | 0.60804 | 48643.2 | 0 | 0 | 0.12071 | 4224.85 | 0.54135 | 7578.9 | 40000 | 0 | 4224.85 | 0 | 4418.35 | 3160.55 | 3160.55 | 0 | 0 | 0 | 0
2022100915 | 1 | 0.63605 | 50884 | 0 | 0 | 0.119 | 4165 | 0.52965 | 7415.1 | 40000 | 0 | 4165 | 0 | 6719 | 696.1 | 696.1 | 0 | 0 | 0 | 0
2022100916 | 1 | 0.65736 | 52588.8 | 0 | 0 | 0.11399 | 3989.65 | 0.52073 | 7290.22 | 40000 | 0 | 3989.65 | 0 | 7290.22 | 0 | 0 | 1308.93 | 0 | 0 | 1308.93
2022100917 | 1 | 0.66907 | 53525.6 | 0 | 0 | 0.12642 | 4424.7 | 0.37539 | 5255.46 | 40000 | 0 | 4424.7 | 0 | 5255.46 | 0 | 0 | 3845.44 | 0 | 0 | 3845.44
2022100918 | 1 | 0.66791 | 53432.8 | 0 | 0 | 0.14348 | 5021.8 | 0.24798 | 3471.72 | 40000 | 0 | 5021.8 | 0 | 3471.72 | 0 | 0 | 4939.28 | 0 | 0 | 4939.28
2022100919 | 1 | 0.65116 | 52092.8 | 0 | 0 | 0.15525 | 5433.75 | 0.08633 | 1208.62 | 40000 | 0 | 5433.75 | 0 | 1208.62 | 0 | 0 | 5450.43 | 0 | 0 | 5450.43
2022100920 | 1 | 0.63811 | 51048.8 | 0 | 0 | 0.15174 | 5310.9 | 0.00139 | 19.46 | 40000 | 0 | 5310.9 | 0 | 19.46 | 0 | 0 | 5718.44 | 0 | 0 | 5718.44
2022100921 | 1 | 0.61821 | 49456.8 | 0 | 0 | 0.19183 | 6714.05 | 0 | 0 | 40000 | 0 | 6714.05 | 0 | 0 | 0 | 0 | 2742.75 | 0 | 0 | 2742.75
2022100922 | 1 | 0.58933 | 47146.4 | 0 | 0 | 0.22069 | 7724.15 | 0 | 0 | 40000 | 0 | 7146.4 | 577.75 | 0 | 0 | 577.75 | 0 | 0 | 0 | 0
2022100923 | 1 | 0.55466 | 44372.8 | 0 | 0 | 0.23739 | 8308.65 | 0 | 0 | 40000 | 0 | 4372.8 | 3935.85 | 0 | 0 | 3935.85 | 0 | 0 | 0 | 0
2022100924 | 1 | 0.51696 | 41356.8 | 0 | 0 | 0.2332 | 8162 | 0 | 0 | 40000 | 0 | 1356.8 | 6805.2 | 0 | 0 | 6805.2 | 0 | 0 | 0 | 0
2022101001 | 2 | 0.48535 | 38828 | 0 | 0 | 0.21702 | 7595.7 | 0 | 0 | 38828 | 1172 | 0 | 7595.7 | 0 | 0 | 8767.7 | 0 | 0 | 0 | 0
2022101002 | 2 | 0.46376 | 37100.8 | 0 | 0 | 0.23365 | 8177.75 | 0 | 0 | 37100.8 | 2899.2 | 0 | 8177.75 | 0 | 0 | 11076.95 | 0 | 0 | 0 | 0
2022101003 | 2 | 0.45181 | 36144.8 | 0 | 0 | 0.23587 | 8255.45 | 0 | 0 | 36144.8 | 3855.2 | 0 | 8255.45 | 0 | 0 | 12110.65 | 0 | 0 | 0 | 0
2022101004 | 2 | 0.44367 | 35493.6 | 0 | 0 | 0.23173 | 8110.55 | 0 | 0 | 35493.6 | 4506.4 | 0 | 8110.55 | 0 | 0 | 12616.95 | 0 | 0 | 0 | 0
2022101005 | 2 | 0.4442 | 35536 | 0 | 0 | 0.21419 | 7496.65 | 0 | 0 | 35536 | 4464 | 0 | 7496.65 | 0 | 0 | 11960.65 | 0 | 0 | 0 | 0
2022101006 | 2 | 0.45913 | 36730.4 | 0 | 0 | 0.21624 | 7568.4 | 0 | 0 | 36730.4 | 3269.6 | 0 | 7568.4 | 0 | 0 | 10838 | 0 | 0 | 0 | 0
2022101007 | 2 | 0.48021 | 38416.8 | 0 | 0 | 0.20674 | 7235.9 | 0 | 0 | 38416.8 | 1583.2 | 0 | 7235.9 | 0 | 0 | 8819.1 | 0 | 0 | 0 | 0
2022101008 | 2 | 0.49472 | 39577.6 | 0 | 0 | 0.19241 | 6734.35 | 0.00623 | 87.22 | 39577.6 | 422.4 | 0 | 6734.35 | 0 | 87.22 | 7243.97 | 0 | 0 | 0 | 0
2022101009 | 2 | 0.5092 | 40736 | 0 | 0 | 0.18183 | 6364.05 | 0.13762 | 1926.68 | 40000 | 0 | 736 | 5628.05 | 0 | 1926.68 | 7554.73 | 0 | 0 | 0 | 0
2022101010 | 2 | 0.5383 | 43064 | 0 | 0 | 0.1336 | 4676 | 0.3192 | 4468.8 | 40000 | 0 | 3064 | 1612 | 0 | 4468.8 | 6080.8 | 0 | 0 | 0 | 0
2022101011 | 2 | 0.57172 | 45737.6 | 0 | 0 | 0.16699 | 5844.65 | 0.45045 | 6306.3 | 40000 | 0 | 5737.6 | 107.05 | 0 | 6306.3 | 6413.35 | 0 | 0 | 0 | 0
2022101012 | 2 | 0.60529 | 48423.2 | 0 | 0 | 0.19427 | 6799.45 | 0.51026 | 7143.64 | 40000 | 0 | 6799.45 | 0 | 1623.75 | 5519.89 | 5519.89 | 0 | 0 | 0 | 0
2022101013 | 2 | 0.63816 | 51052.8 | 0 | 0 | 0.19957 | 6984.95 | 0.56357 | 7889.98 | 40000 | 0 | 6984.95 | 0 | 4067.85 | 3822.13 | 3822.13 | 0 | 0 | 0 | 0
2022101014 | 2 | 0.67132 | 53705.6 | 0 | 0 | 0.21275 | 7446.25 | 0.57415 | 8038.1 | 40000 | 0 | 7446.25 | 0 | 6259.35 | 1778.75 | 1778.75 | 0 | 0 | 0 | 0
2022101015 | 2 | 0.69916 | 55932.8 | 0 | 0 | 0.19563 | 6847.05 | 0.55559 | 7778.26 | 40000 | 0 | 6847.05 | 0 | 7778.26 | 0 | 0 | 1307.49 | 0 | 0 | 1307.49
2022101016 | 2 | 0.71774 | 57419.2 | 0 | 0 | 0.21544 | 7540.4 | 0.54055 | 7567.7 | 40000 | 0 | 7540.4 | 0 | 7567.7 | 0 | 0 | 2311.1 | 0 | 0 | 2311.1
2022101017 | 2 | 0.72394 | 57915.2 | 0 | 0 | 0.24203 | 8471.05 | 0.51386 | 7194.04 | 40000 | 0 | 8471.05 | 0 | 7194.04 | 0 | 0 | 2250.11 | 0 | 0 | 2250.11
2022101018 | 2 | 0.714 | 57120 | 0 | 0 | 0.24235 | 8482.25 | 0.33158 | 4642.12 | 40000 | 0 | 8482.25 | 0 | 4642.12 | 0 | 0 | 3995.63 | 0 | 0 | 3995.63
2022101019 | 2 | 0.68813 | 55050.4 | 0 | 0 | 0.25504 | 8926.4 | 0.08543 | 1196.02 | 40000 | 0 | 8926.4 | 0 | 1196.02 | 0 | 0 | 4927.98 | 0 | 0 | 4927.98
2022101020 | 2 | 0.67255 | 53804 | 0 | 0 | 0.25822 | 9037.7 | 0.00357 | 49.98 | 40000 | 0 | 9037.7 | 0 | 49.98 | 0 | 0 | 4716.32 | 0 | 0 | 4716.32
2022101021 | 2 | 0.6508 | 52064 | 0 | 0 | 0.27776 | 9721.6 | 0 | 0 | 40000 | 0 | 9721.6 | 0 | 0 | 0 | 0 | 2342.4 | 0 | 0 | 2342.4
2022101022 | 2 | 0.61825 | 49460 | 0 | 0 | 0.2949 | 10321.5 | 0 | 0 | 40000 | 0 | 9460 | 861.5 | 0 | 0 | 861.5 | 0 | 0 | 0 | 0
2022101023 | 2 | 0.57642 | 46113.6 | 0 | 0 | 0.32539 | 11388.65 | 0 | 0 | 40000 | 0 | 6113.6 | 5275.05 | 0 | 0 | 5275.05 | 0 | 0 | 0 | 0
2022101024 | 2 | 0.53792 | 43033.6 | 0 | 0 | 0.3375 | 11812.5 | 0 | 0 | 40000 | 0 | 3033.6 | 8778.9 | 0 | 0 | 8778.9 | 0 | 0 | 0 | 0
2022101101 | 3 | 0.5026 | 40208 | 0 | 0 | 0.34033 | 11911.55 | 0 | 0 | 40000 | 0 | 208 | 11703.55 | 0 | 0 | 11703.55 | 0 | 0 | 0 | 0
2022101102 | 3 | 0.48101 | 38480.8 | 0 | 0 | 0.32961 | 11536.35 | 0 | 0 | 38480.8 | 1519.2 | 0 | 11536.35 | 0 | 0 | 13055.55 | 0 | 0 | 0 | 0
2022101103 | 3 | 0.46299 | 37039.2 | 0 | 0 | 0.31612 | 11064.2 | 0 | 0 | 37039.2 | 2960.8 | 0 | 11064.2 | 0 | 0 | 14025 | 0 | 0 | 0 | 0
2022101104 | 3 | 0.45371 | 36296.8 | 0 | 0 | 0.3067 | 10734.5 | 0 | 0 | 36296.8 | 3703.2 | 0 | 10734.5 | 0 | 0 | 14437.7 | 0 | 0 | 0 | 0
2022101105 | 3 | 0.45386 | 36308.8 | 0 | 0 | 0.31334 | 10966.9 | 0 | 0 | 36308.8 | 3691.2 | 0 | 10966.9 | 0 | 0 | 14658.1 | 0 | 0 | 0 | 0
2022101106 | 3 | 0.47099 | 37679.2 | 0 | 0 | 0.3321 | 11623.5 | 0 | 0 | 37679.2 | 2320.8 | 0 | 11623.5 | 0 | 0 | 13944.3 | 0 | 0 | 0 | 0
2022101107 | 3 | 0.50168 | 40134.4 | 0 | 0 | 0.37631 | 13170.85 | 0 | 0 | 40000 | 0 | 134.4 | 13036.45 | 0 | 0 | 13036.45 | 0 | 0 | 0 | 0
2022101108 | 3 | 0.51585 | 41268 | 0 | 0 | 0.3895 | 13632.5 | 0.00533 | 74.62 | 40000 | 0 | 1268 | 12364.5 | 0 | 74.62 | 12439.12 | 0 | 0 | 0 | 0
2022101109 | 3 | 0.52479 | 41983.2 | 0 | 0 | 0.36146 | 12651.1 | 0.17404 | 2436.56 | 40000 | 0 | 1983.2 | 10667.9 | 0 | 2436.56 | 13104.46 | 0 | 0 | 0 | 0
2022101110 | 3 | 0.54959 | 43967.2 | 0 | 0 | 0.3106 | 10871 | 0.46783 | 6549.62 | 40000 | 0 | 3967.2 | 6903.8 | 0 | 6549.62 | 13453.42 | 0 | 0 | 0 | 0
2022101111 | 3 | 0.57966 | 46372.8 | 0 | 0 | 0.36429 | 12750.15 | 0.59212 | 8289.68 | 40000 | 0 | 6372.8 | 6377.35 | 0 | 8289.68 | 14667.03 | 0 | 0 | 0 | 0
2022101112 | 3 | 0.61385 | 49108 | 0 | 0 | 0.4179 | 14626.5 | 0.56205 | 7868.7 | 40000 | 0 | 9108 | 5518.5 | 0 | 7868.7 | 13387.2 | 0 | 0 | 0 | 0
2022101113 | 3 | 0.64161 | 51328.8 | 0 | 0 | 0.42821 | 14987.35 | 0.54957 | 7693.98 | 40000 | 0 | 11328.8 | 3658.55 | 0 | 7693.98 | 11352.53 | 0 | 0 | 0 | 0
2022101114 | 3 | 0.6631 | 53048 | 0 | 0 | 0.43813 | 15334.55 | 0.53159 | 7442.26 | 40000 | 0 | 13048 | 2286.55 | 0 | 7442.26 | 9728.81 | 0 | 0 | 0 | 0
2022101115 | 3 | 0.68082 | 54465.6 | 0 | 0 | 0.43559 | 15245.65 | 0.55015 | 7702.1 | 40000 | 0 | 14465.6 | 780.05 | 0 | 7702.1 | 8482.15 | 0 | 0 | 0 | 0
2022101116 | 3 | 0.7002 | 56016 | 0 | 0 | 0.42538 | 14888.3 | 0.58473 | 8186.22 | 40000 | 0 | 14888.3 | 0 | 1127.7 | 7058.52 | 7058.52 | 0 | 0 | 0 | 0
2022101117 | 3 | 0.71322 | 57057.6 | 0 | 0 | 0.42488 | 14870.8 | 0.57331 | 8026.34 | 40000 | 0 | 14870.8 | 0 | 2186.8 | 5839.54 | 5839.54 | 0 | 0 | 0 | 0
2022101118 | 3 | 0.71105 | 56884 | 0 | 0 | 0.42376 | 14831.6 | 0.49 | 6860 | 40000 | 0 | 14831.6 | 0 | 2052.4 | 4807.6 | 4807.6 | 0 | 0 | 0 | 0
2022101119 | 3 | 0.6919 | 55352 | 0 | 0 | 0.40647 | 14226.45 | 0.18278 | 2558.92 | 40000 | 0 | 14226.45 | 0 | 1125.55 | 1433.37 | 1433.37 | 0 | 0 | 0 | 0
2022101120 | 3 | 0.67974 | 54379.2 | 0 | 0 | 0.39332 | 13766.2 | 0.00283 | 39.62 | 40000 | 0 | 13766.2 | 0 | 39.62 | 0 | 0 | 573.38 | 0 | 0 | 573.38
2022101121 | 3 | 0.6665 | 53320 | 0 | 0 | 0.47885 | 16759.75 | 0 | 0 | 40000 | 0 | 13320 | 3439.75 | 0 | 0 | 3439.75 | 0 | 0 | 0 | 0
2022101122 | 3 | 0.64239 | 51391.2 | 0 | 0 | 0.53983 | 18894.05 | 0 | 0 | 40000 | 0 | 11391.2 | 7502.85 | 0 | 0 | 7502.85 | 0 | 0 | 0 | 0
2022101123 | 3 | 0.6064 | 48512 | 0 | 0 | 0.56321 | 19712.35 | 0 | 0 | 40000 | 0 | 8512 | 11200.35 | 0 | 0 | 11200.35 | 0 | 0 | 0 | 0
2022101124 | 3 | 0.5647 | 45176 | 0 | 0 | 0.55387 | 19385.45 | 0 | 0 | 40000 | 0 | 5176 | 14209.45 | 0 | 0 | 14209.45 | 0 | 0 | 0 | 0
2022101201 | 4 | 0.53113 | 42490.4 | 0 | 0 | 0.53835 | 18842.25 | 0 | 0 | 40000 | 0 | 2490.4 | 16351.85 | 0 | 0 | 16351.85 | 0 | 0 | 0 | 0
2022101202 | 4 | 0.50974 | 40779.2 | 0 | 0 | 0.5178 | 18123 | 0 | 0 | 40000 | 0 | 779.2 | 17343.8 | 0 | 0 | 17343.8 | 0 | 0 | 0 | 0
2022101203 | 4 | 0.49742 | 39793.6 | 0 | 0 | 0.49791 | 17426.85 | 0 | 0 | 39793.6 | 206.4 | 0 | 17426.85 | 0 | 0 | 17633.25 | 0 | 0 | 0 | 0
2022101204 | 4 | 0.48947 | 39157.6 | 0 | 0 | 0.48758 | 17065.3 | 0 | 0 | 39157.6 | 842.4 | 0 | 17065.3 | 0 | 0 | 17907.7 | 0 | 0 | 0 | 0
2022101205 | 4 | 0.49116 | 39292.8 | 0 | 0 | 0.4837 | 16929.5 | 0 | 0 | 39292.8 | 707.2 | 0 | 16929.5 | 0 | 0 | 17636.7 | 0 | 0 | 0 | 0
2022101206 | 4 | 0.50864 | 40691.2 | 0 | 0 | 0.48382 | 16933.7 | 0 | 0 | 40000 | 0 | 691.2 | 16242.5 | 0 | 0 | 16242.5 | 0 | 0 | 0 | 0
2022101207 | 4 | 0.5382 | 43056 | 0 | 0 | 0.47705 | 16696.75 | 0 | 0 | 40000 | 0 | 3056 | 13640.75 | 0 | 0 | 13640.75 | 0 | 0 | 0 | 0
2022101208 | 4 | 0.55477 | 44381.6 | 0 | 0 | 0.45449 | 15907.15 | 0.00438 | 61.32 | 40000 | 0 | 4381.6 | 11525.55 | 0 | 61.32 | 11586.87 | 0 | 0 | 0 | 0
2022101209 | 4 | 0.56485 | 45188 | 0 | 0 | 0.3927 | 13744.5 | 0.22252 | 3115.28 | 40000 | 0 | 5188 | 8556.5 | 0 | 3115.28 | 11671.78 | 0 | 0 | 0 | 0
2022101210 | 4 | 0.59706 | 47764.8 | 0 | 0 | 0.30811 | 10783.85 | 0.61354 | 8589.56 | 40000 | 0 | 7764.8 | 3019.05 | 0 | 8589.56 | 11608.61 | 0 | 0 | 0 | 0
2022101211 | 4 | 0.63454 | 50763.2 | 0 | 0 | 0.29676 | 10386.6 | 0.71873 | 10062.22 | 40000 | 0 | 10386.6 | 0 | 376.6 | 9685.62 | 9685.62 | 0 | 0 | 0 | 0
2022101212 | 4 | 0.6757 | 54056 | 0 | 0 | 0.24942 | 8729.7 | 0.72842 | 10197.88 | 40000 | 0 | 8729.7 | 0 | 5326.3 | 4871.58 | 4871.58 | 0 | 0 | 0 | 0
2022101213 | 4 | 0.71788 | 57430.4 | 0 | 0 | 0.20561 | 7196.35 | 0.73065 | 10229.1 | 40000 | 0 | 7196.35 | 0 | 10229.1 | 0 | 0 | 4.95 | 0 | 0 | 4.95
2022101214 | 4 | 0.7612 | 60896 | 0 | 0 | 0.16682 | 5838.7 | 0.71301 | 9982.14 | 40000 | 0 | 5838.7 | 0 | 9982.14 | 0 | 0 | 5075.16 | 0 | 0 | 5075.16
2022101215 | 4 | 0.79579 | 63663.2 | 0 | 0 | 0.15318 | 5361.3 | 0.70943 | 9932.02 | 40000 | 0 | 5361.3 | 0 | 9932.02 | 0 | 0 | 8369.88 | 0 | 0 | 8369.88
2022101216 | 4 | 0.81799 | 65439.2 | 0 | 0 | 0.15181 | 5313.35 | 0.71392 | 9994.88 | 40000 | 0 | 5313.35 | 0 | 9994.88 | 0 | 0 | 10130.97 | 0 | 0 | 10130.97
2022101217 | 4 | 0.82753 | 66202.4 | 0 | 0 | 0.148 | 5180 | 0.69397 | 9715.58 | 40000 | 0 | 5180 | 0 | 9715.58 | 0 | 0 | 11306.82 | 0 | 0 | 11306.82
2022101218 | 4 | 0.8166 | 65328 | 0 | 0 | 0.14621 | 5117.35 | 0.5727 | 8017.8 | 40000 | 0 | 5117.35 | 0 | 8017.8 | 0 | 0 | 12192.85 | 0 | 0 | 12192.85
2022101219 | 4 | 0.77575 | 62060 | 0 | 0 | 0.1357 | 4749.5 | 0.19555 | 2737.7 | 40000 | 0 | 4749.5 | 0 | 2737.7 | 0 | 0 | 14572.8 | 0 | 0 | 14572.8
2022101220 | 4 | 0.74307 | 59445.6 | 0 | 0 | 0.14421 | 5047.35 | 0.00303 | 42.42 | 40000 | 0 | 5047.35 | 0 | 42.42 | 0 | 0 | 14355.83 | 0 | 0 | 14355.83
2022101221 | 4 | 0.72192 | 57753.6 | 0 | 0 | 0.19153 | 6703.55 | 0 | 0 | 40000 | 0 | 6703.55 | 0 | 0 | 0 | 0 | 11050.05 | 0 | 0 | 11050.05
2022101222 | 4 | 0.68631 | 54904.8 | 0 | 0 | 0.22235 | 7782.25 | 0 | 0 | 40000 | 0 | 7782.25 | 0 | 0 | 0 | 0 | 7122.55 | 0 | 0 | 7122.55
2022101223 | 4 | 0.63812 | 51049.6 | 0 | 0 | 0.2362 | 8267 | 0 | 0 | 40000 | 0 | 8267 | 0 | 0 | 0 | 0 | 2782.6 | 0 | 0 | 2782.6
2022101224 | 4 | 0.58766 | 47012.8 | 0 | 0 | 0.24487 | 8570.45 | 0 | 0 | 40000 | 0 | 7012.8 | 1557.65 | 0 | 0 | 1557.65 | 0 | 0 | 0 | 0
2022101301 | 5 | 0.54601 | 43680.8 | 0 | 0 | 0.23758 | 8315.3 | 0 | 0 | 40000 | 0 | 3680.8 | 4634.5 | 0 | 0 | 4634.5 | 0 | 0 | 0 | 0
2022101302 | 5 | 0.51854 | 41483.2 | 0 | 0 | 0.23793 | 8327.55 | 0 | 0 | 40000 | 0 | 1483.2 | 6844.35 | 0 | 0 | 6844.35 | 0 | 0 | 0 | 0
2022101303 | 5 | 0.49959 | 39967.2 | 0 | 0 | 0.23745 | 8310.75 | 0 | 0 | 39967.2 | 32.8 | 0 | 8310.75 | 0 | 0 | 8343.55 | 0 | 0 | 0 | 0
2022101304 | 5 | 0.48848 | 39078.4 | 0 | 0 | 0.25243 | 8835.05 | 0 | 0 | 39078.4 | 921.6 | 0 | 8835.05 | 0 | 0 | 9756.65 | 0 | 0 | 0 | 0
2022101305 | 5 | 0.48532 | 38825.6 | 0 | 0 | 0.2512 | 8792 | 0 | 0 | 38825.6 | 1174.4 | 0 | 8792 | 0 | 0 | 9966.4 | 0 | 0 | 0 | 0
2022101306 | 5 | 0.49973 | 39978.4 | 0 | 0 | 0.24876 | 8706.6 | 0 | 0 | 39978.4 | 21.6 | 0 | 8706.6 | 0 | 0 | 8728.2 | 0 | 0 | 0 | 0
2022101307 | 5 | 0.52797 | 42237.6 | 0 | 0 | 0.2443 | 8550.5 | 0 | 0 | 40000 | 0 | 2237.6 | 6312.9 | 0 | 0 | 6312.9 | 0 | 0 | 0 | 0
2022101308 | 5 | 0.53722 | 42977.6 | 0 | 0 | 0.2315 | 8102.5 | 0.00432 | 60.48 | 40000 | 0 | 2977.6 | 5124.9 | 0 | 60.48 | 5185.38 | 0 | 0 | 0 | 0
2022101309 | 5 | 0.54074 | 43259.2 | 0 | 0 | 0.19602 | 6860.7 | 0.21099 | 2953.86 | 40000 | 0 | 3259.2 | 3601.5 | 0 | 2953.86 | 6555.36 | 0 | 0 | 0 | 0
2022101310 | 5 | 0.55917 | 44733.6 | 0 | 0 | 0.12775 | 4471.25 | 0.59812 | 8373.68 | 40000 | 0 | 4471.25 | 0 | 262.35 | 8111.33 | 8111.33 | 0 | 0 | 0 | 0
2022101311 | 5 | 0.58126 | 46500.8 | 0 | 0 | 0.11043 | 3865.05 | 0.67826 | 9495.64 | 40000 | 0 | 3865.05 | 0 | 2635.75 | 6859.89 | 6859.89 | 0 | 0 | 0 | 0
2022101312 | 5 | 0.61079 | 48863.2 | 0 | 0 | 0.09392 | 3287.2 | 0.67115 | 9396.1 | 40000 | 0 | 3287.2 | 0 | 5576 | 3820.1 | 3820.1 | 0 | 0 | 0 | 0
2022101313 | 5 | 0.64087 | 51269.6 | 0 | 0 | 0.06928 | 2424.8 | 0.70016 | 9802.24 | 40000 | 0 | 2424.8 | 0 | 8844.8 | 957.44 | 957.44 | 0 | 0 | 0 | 0
2022101314 | 5 | 0.67389 | 53911.2 | 0 | 0 | 0.05312 | 1859.2 | 0.70551 | 9877.14 | 40000 | 0 | 1859.2 | 0 | 9877.14 | 0 | 0 | 2174.86 | 0 | 0 | 2174.86
2022101315 | 5 | 0.70251 | 56200.8 | 0 | 0 | 0.04381 | 1533.35 | 0.69479 | 9727.06 | 40000 | 0 | 1533.35 | 0 | 9727.06 | 0 | 0 | 4940.39 | 0 | 0 | 4940.39
2022101316 | 5 | 0.72453 | 57962.4 | 0 | 0 | 0.07042 | 2464.7 | 0.6713 | 9398.2 | 40000 | 0 | 2464.7 | 0 | 9398.2 | 0 | 0 | 6099.5 | 0 | 0 | 6099.5
2022101317 | 5 | 0.73418 | 58734.4 | 0 | 0 | 0.08468 | 2963.8 | 0.61632 | 8628.48 | 40000 | 0 | 2963.8 | 0 | 8628.48 | 0 | 0 | 7142.12 | 0 | 0 | 7142.12
2022101318 | 5 | 0.7232 | 57856 | 0 | 0 | 0.07308 | 2557.8 | 0.48234 | 6752.76 | 40000 | 0 | 2557.8 | 0 | 6752.76 | 0 | 0 | 8545.44 | 0 | 0 | 8545.44
2022101319 | 5 | 0.68574 | 54859.2 | 0 | 0 | 0.06207 | 2172.45 | 0.14543 | 2036.02 | 40000 | 0 | 2172.45 | 0 | 2036.02 | 0 | 0 | 10650.73 | 0 | 0 | 10650.73
2022101320 | 5 | 0.66524 | 53219.2 | 0 | 0 | 0.0816 | 2856 | 0.00157 | 21.98 | 40000 | 0 | 2856 | 0 | 21.98 | 0 | 0 | 10341.22 | 0 | 0 | 10341.22
2022101321 | 5 | 0.64375 | 51500 | 0 | 0 | 0.1222 | 4277 | 0.00018 | 2.52 | 40000 | 0 | 4277 | 0 | 2.52 | 0 | 0 | 7220.48 | 0 | 0 | 7220.48
2022101322 | 5 | 0.60991 | 48792.8 | 0 | 0 | 0.13989 | 4896.15 | 0.00018 | 2.52 | 40000 | 0 | 4896.15 | 0 | 2.52 | 0 | 0 | 3894.13 | 0 | 0 | 3894.13
2022101323 | 5 | 0.56833 | 45466.4 | 0 | 0 | 0.15359 | 5375.65 | 0.00018 | 2.52 | 40000 | 0 | 5375.65 | 0 | 2.52 | 0 | 0 | 88.23 | 0 | 0 | 88.23
2022101324 | 5 | 0.52719 | 42175.2 | 0 | 0 | 0.16339 | 5718.65 | 0.00018 | 2.52 | 40000 | 0 | 2175.2 | 3543.45 | 0 | 2.52 | 3545.97 | 0 | 0 | 0 | 0
2022101401 | 6 | 0.49331 | 39464.8 | 0 | 0 | 0.17175 | 6011.25 | 0.00018 | 2.52 | 39464.8 | 535.2 | 0 | 6011.25 | 0 | 2.52 | 6548.97 | 0 | 0 | 0 | 0
2022101402 | 6 | 0.46941 | 37552.8 | 0 | 0 | 0.17978 | 6292.3 | 0.00018 | 2.52 | 37552.8 | 2447.2 | 0 | 6292.3 | 0 | 2.52 | 8742.02 | 0 | 0 | 0 | 0
2022101403 | 6 | 0.45602 | 36481.6 | 0 | 0 | 0.18571 | 6499.85 | 0.00018 | 2.52 | 36481.6 | 3518.4 | 0 | 6499.85 | 0 | 2.52 | 10020.77 | 0 | 0 | 0 | 0
2022101404 | 6 | 0.44803 | 35842.4 | 0 | 0 | 0.185 | 6475 | 0.00018 | 2.52 | 35842.4 | 4157.6 | 0 | 6475 | 0 | 2.52 | 10635.12 | 0 | 0 | 0 | 0
2022101405 | 6 | 0.45086 | 36068.8 | 0 | 0 | 0.19352 | 6773.2 | 0.00018 | 2.52 | 36068.8 | 3931.2 | 0 | 6773.2 | 0 | 2.52 | 10706.92 | 0 | 0 | 0 | 0
2022101406 | 6 | 0.46342 | 37073.6 | 0 | 0 | 0.20354 | 7123.9 | 0.00018 | 2.52 | 37073.6 | 2926.4 | 0 | 7123.9 | 0 | 2.52 | 10052.82 | 0 | 0 | 0 | 0
2022101407 | 6 | 0.49124 | 39299.2 | 0 | 0 | 0.21023 | 7358.05 | 0.00018 | 2.52 | 39299.2 | 700.8 | 0 | 7358.05 | 0 | 2.52 | 8061.37 | 0 | 0 | 0 | 0
2022101408 | 6 | 0.50541 | 40432.8 | 0 | 0 | 0.23075 | 8076.25 | 0.00531 | 74.34 | 40000 | 0 | 432.8 | 7643.45 | 0 | 74.34 | 7717.79 | 0 | 0 | 0 | 0
2022101409 | 6 | 0.51395 | 41116 | 0 | 0 | 0.26211 | 9173.85 | 0.22046 | 3086.44 | 40000 | 0 | 1116 | 8057.85 | 0 | 3086.44 | 11144.29 | 0 | 0 | 0 | 0
2022101410 | 6 | 0.53846 | 43076.8 | 0 | 0 | 0.21572 | 7550.2 | 0.62888 | 8804.32 | 40000 | 0 | 3076.8 | 4473.4 | 0 | 8804.32 | 13277.72 | 0 | 0 | 0 | 0
2022101411 | 6 | 0.56598 | 45278.4 | 0 | 0 | 0.22362 | 7826.7 | 0.7478 | 10469.2 | 40000 | 0 | 5278.4 | 2548.3 | 0 | 10469.2 | 13017.5 | 0 | 0 | 0 | 0
2022101412 | 6 | 0.59578 | 47662.4 | 0 | 0 | 0.28738 | 10058.3 | 0.75198 | 10527.72 | 40000 | 0 | 7662.4 | 2395.9 | 0 | 10527.72 | 12923.62 | 0 | 0 | 0 | 0
2022101413 | 6 | 0.62607 | 50085.6 | 0 | 0 | 0.30047 | 10516.45 | 0.741 | 10374 | 40000 | 0 | 10085.6 | 430.85 | 0 | 10374 | 10804.85 | 0 | 0 | 0 | 0
2022101414 | 6 | 0.65761 | 52608.8 | 0 | 0 | 0.30022 | 10507.7 | 0.73371 | 10271.94 | 40000 | 0 | 10507.7 | 0 | 2101.1 | 8170.84 | 8170.84 | 0 | 0 | 0 | 0
2022101415 | 6 | 0.68932 | 55145.6 | 0 | 0 | 0.28475 | 9966.25 | 0.71538 | 10015.32 | 40000 | 0 | 9966.25 | 0 | 5179.35 | 4835.97 | 4835.97 | 0 | 0 | 0 | 0
2022101416 | 6 | 0.71352 | 57081.6 | 0 | 0 | 0.2915 | 10202.5 | 0.68063 | 9528.82 | 40000 | 0 | 10202.5 | 0 | 6879.1 | 2649.72 | 2649.72 | 0 | 0 | 0 | 0
2022101417 | 6 | 0.72823 | 58258.4 | 0 | 0 | 0.32429 | 11350.15 | 0.59116 | 8276.24 | 40000 | 0 | 11350.15 | 0 | 6908.25 | 1367.99 | 1367.99 | 0 | 0 | 0 | 0
2022101418 | 6 | 0.72061 | 57648.8 | 0 | 0 | 0.35507 | 12427.45 | 0.35463 | 4964.82 | 40000 | 0 | 12427.45 | 0 | 4964.82 | 0 | 0 | 256.53 | 0 | 0 | 256.53
2022101419 | 6 | 0.6857 | 54856 | 0 | 0 | 0.30964 | 10837.4 | 0.06973 | 976.22 | 40000 | 0 | 10837.4 | 0 | 976.22 | 0 | 0 | 3042.38 | 0 | 0 | 3042.38
2022101420 | 6 | 0.66334 | 53067.2 | 0 | 0 | 0.31791 | 11126.85 | 0.00037 | 5.18 | 40000 | 0 | 11126.85 | 0 | 5.18 | 0 | 0 | 1935.17 | 0 | 0 | 1935.17
2022101421 | 6 | 0.64002 | 51201.6 | 0 | 0 | 0.39004 | 13651.4 | 0 | 0 | 40000 | 0 | 11201.6 | 2449.8 | 0 | 0 | 2449.8 | 0 | 0 | 0 | 0
2022101422 | 6 | 0.61687 | 49349.6 | 0 | 0 | 0.44272 | 15495.2 | 0 | 0 | 40000 | 0 | 9349.6 | 6145.6 | 0 | 0 | 6145.6 | 0 | 0 | 0 | 0
2022101423 | 6 | 0.59039 | 47231.2 | 0 | 0 | 0.47644 | 16675.4 | 0 | 0 | 40000 | 0 | 7231.2 | 9444.2 | 0 | 0 | 9444.2 | 0 | 0 | 0 | 0
2022101424 | 6 | 0.56057 | 44845.6 | 0 | 0 | 0.50964 | 17837.4 | 0 | 0 | 40000 | 0 | 4845.6 | 12991.8 | 0 | 0 | 12991.8 | 0 | 0 | 0 | 0
2022101501 | 7 | 0.53426 | 42740.8 | 0 | 0 | 0.54064 | 18922.4 | 0 | 0 | 40000 | 0 | 2740.8 | 16181.6 | 0 | 0 | 16181.6 | 0 | 0 | 0 | 0
2022101502 | 7 | 0.5122 | 40976 | 0 | 0 | 0.54181 | 18963.35 | 0 | 0 | 40000 | 0 | 976 | 17987.35 | 0 | 0 | 17987.35 | 0 | 0 | 0 | 0
2022101503 | 7 | 0.498 | 39840 | 0 | 0 | 0.53334 | 18666.9 | 0 | 0 | 39840 | 160 | 0 | 18666.9 | 0 | 0 | 18826.9 | 0 | 0 | 0 | 0
2022101504 | 7 | 0.48834 | 39067.2 | 0 | 0 | 0.51028 | 17859.8 | 0 | 0 | 39067.2 | 932.8 | 0 | 17859.8 | 0 | 0 | 18792.6 | 0 | 0 | 0 | 0
2022101505 | 7 | 0.48254 | 38603.2 | 0 | 0 | 0.50478 | 17667.3 | 0 | 0 | 38603.2 | 1396.8 | 0 | 17667.3 | 0 | 0 | 19064.1 | 0 | 0 | 0 | 0
2022101506 | 7 | 0.48451 | 38760.8 | 0 | 0 | 0.48572 | 17000.2 | 0 | 0 | 38760.8 | 1239.2 | 0 | 17000.2 | 0 | 0 | 18239.4 | 0 | 0 | 0 | 0
2022101507 | 7 | 0.49356 | 39484.8 | 0 | 0 | 0.45725 | 16003.75 | 0 | 0 | 39484.8 | 515.2 | 0 | 16003.75 | 0 | 0 | 16518.95 | 0 | 0 | 0 | 0
2022101508 | 7 | 0.50374 | 40299.2 | 0 | 0 | 0.43385 | 15184.75 | 0.00434 | 60.76 | 40000 | 0 | 299.2 | 14885.55 | 0 | 60.76 | 14946.31 | 0 | 0 | 0 | 0
2022101509 | 7 | 0.52474 | 41979.2 | 0 | 0 | 0.39149 | 13702.15 | 0.14621 | 2046.94 | 40000 | 0 | 1979.2 | 11722.95 | 0 | 2046.94 | 13769.89 | 0 | 0 | 0 | 0
2022101510 | 7 | 0.56158 | 44926.4 | 0 | 0 | 0.34854 | 12198.9 | 0.42722 | 5981.08 | 40000 | 0 | 4926.4 | 7272.5 | 0 | 5981.08 | 13253.58 | 0 | 0 | 0 | 0
2022101511 | 7 | 0.60708 | 48566.4 | 0 | 0 | 0.38106 | 13337.1 | 0.59616 | 8346.24 | 40000 | 0 | 8566.4 | 4770.7 | 0 | 8346.24 | 13116.94 | 0 | 0 | 0 | 0
2022101512 | 7 | 0.65064 | 52051.2 | 0 | 0 | 0.38622 | 13517.7 | 0.6761 | 9465.4 | 40000 | 0 | 12051.2 | 1466.5 | 0 | 9465.4 | 10931.9 | 0 | 0 | 0 | 0
2022101513 | 7 | 0.68788 | 55030.4 | 0 | 0 | 0.33568 | 11748.8 | 0.67836 | 9497.04 | 40000 | 0 | 11748.8 | 0 | 3281.6 | 6215.44 | 6215.44 | 0 | 0 | 0 | 0
2022101514 | 7 | 0.71969 | 57575.2 | 0 | 0 | 0.29533 | 10336.55 | 0.67895 | 9505.3 | 40000 | 0 | 10336.55 | 0 | 7238.65 | 2266.65 | 2266.65 | 0 | 0 | 0 | 0
2022101515 | 7 | 0.74889 | 59911.2 | 0 | 0 | 0.27952 | 9783.2 | 0.68606 | 9604.84 | 40000 | 0 | 9783.2 | 0 | 9604.84 | 0 | 0 | 523.16 | 0 | 0 | 523.16
2022101516 | 7 | 0.76914 | 61531.2 | 0 | 0 | 0.27725 | 9703.75 | 0.67702 | 9478.28 | 40000 | 0 | 9703.75 | 0 | 9478.28 | 0 | 0 | 2349.17 | 0 | 0 | 2349.17
2022101517 | 7 | 0.77665 | 62132 | 0 | 0 | 0.29302 | 10255.7 | 0.63801 | 8932.14 | 40000 | 0 | 10255.7 | 0 | 8932.14 | 0 | 0 | 2944.16 | 0 | 0 | 2944.16
2022101518 | 7 | 0.76688 | 61350.4 | 0 | 0 | 0.30006 | 10502.1 | 0.4929 | 6900.6 | 40000 | 0 | 10502.1 | 0 | 6900.6 | 0 | 0 | 3947.7 | 0 | 0 | 3947.7
2022101519 | 7 | 0.7257 | 58056 | 0 | 0 | 0.29151 | 10202.85 | 0.11004 | 1540.56 | 40000 | 0 | 10202.85 | 0 | 1540.56 | 0 | 0 | 6312.59 | 0 | 0 | 6312.59
2022101520 | 7 | 0.70079 | 56063.2 | 0 | 0 | 0.31471 | 11014.85 | 0.00585 | 81.9 | 40000 | 0 | 11014.85 | 0 | 81.9 | 0 | 0 | 4966.45 | 0 | 0 | 4966.45
2022101521 | 7 | 0.6801 | 54408 | 0 | 0 | 0.42537 | 14887.95 | 0.00095 | 13.3 | 40000 | 0 | 14408 | 479.95 | 0 | 13.3 | 493.25 | 0 | 0 | 0 | 0
2022101522 | 7 | 0.65487 | 52389.6 | 0 | 0 | 0.52372 | 18330.2 | 0 | 0 | 40000 | 0 | 12389.6 | 5940.6 | 0 | 0 | 5940.6 | 0 | 0 | 0 | 0
2022101523 | 7 | 0.62383 | 49906.4 | 0 | 0 | 0.54932 | 19226.2 | 0 | 0 | 40000 | 0 | 9906.4 | 9319.8 | 0 | 0 | 9319.8 | 0 | 0 | 0 | 0
2022101524 | 7 | 0.59016 | 47212.8 | 0 | 0 | 0.55945 | 19580.75 | 0 | 0 | 40000 | 0 | 7212.8 | 12367.95 | 0 | 0 | 12367.95 | 0 | 0 | 0 | 0
2022101601 | 1 | 0.55899 | 44719.2 | 0 | 0 | 0.53136 | 18597.6 | 0 | 0 | 40000 | 0 | 4719.2 | 13878.4 | 0 | 0 | 13878.4 | 0 | 0 | 0 | 0
2022101602 | 1 | 0.53387 | 42709.6 | 0 | 0 | 0.50542 | 17689.7 | 0 | 0 | 40000 | 0 | 2709.6 | 14980.1 | 0 | 0 | 14980.1 | 0 | 0 | 0 | 0
2022101603 | 1 | 0.51187 | 40949.6 | 0 | 0 | 0.42094 | 14732.9 | 0 | 0 | 40000 | 0 | 949.6 | 13783.3 | 0 | 0 | 13783.3 | 0 | 0 | 0 | 0
2022101604 | 1 | 0.49685 | 39748 | 0 | 0 | 0.34259 | 11990.65 | 0 | 0 | 39748 | 252 | 0 | 11990.65 | 0 | 0 | 12242.65 | 0 | 0 | 0 | 0
2022101605 | 1 | 0.48976 | 39180.8 | 0 | 0 | 0.30809 | 10783.15 | 0 | 0 | 39180.8 | 819.2 | 0 | 10783.15 | 0 | 0 | 11602.35 | 0 | 0 | 0 | 0
2022101606 | 1 | 0.48692 | 38953.6 | 0 | 0 | 0.27811 | 9733.85 | 0 | 0 | 38953.6 | 1046.4 | 0 | 9733.85 | 0 | 0 | 10780.25 | 0 | 0 | 0 | 0
2022101607 | 1 | 0.48605 | 38884 | 0 | 0 | 0.27555 | 9644.25 | 0 | 0 | 38884 | 1116 | 0 | 9644.25 | 0 | 0 | 10760.25 | 0 | 0 | 0 | 0
2022101608 | 1 | 0.48948 | 39158.4 | 0 | 0 | 0.27965 | 9787.75 | 0.00241 | 33.74 | 39158.4 | 841.6 | 0 | 9787.75 | 0 | 33.74 | 10663.09 | 0 | 0 | 0 | 0
2022101609 | 1 | 0.50375 | 40300 | 0 | 0 | 0.25828 | 9039.8 | 0.07351 | 1029.14 | 40000 | 0 | 300 | 8739.8 | 0 | 1029.14 | 9768.94 | 0 | 0 | 0 | 0
2022101610 | 1 | 0.53804 | 43043.2 | 0 | 0 | 0.23408 | 8192.8 | 0.1906 | 2668.4 | 40000 | 0 | 3043.2 | 5149.6 | 0 | 2668.4 | 7818 | 0 | 0 | 0 | 0
2022101611 | 1 | 0.56913 | 45530.4 | 0 | 0 | 0.22193 | 7767.55 | 0.23559 | 3298.26 | 40000 | 0 | 5530.4 | 2237.15 | 0 | 3298.26 | 5535.41 | 0 | 0 | 0 | 0
2022101612 | 1 | 0.59506 | 47604.8 | 0 | 0 | 0.19837 | 6942.95 | 0.26138 | 3659.32 | 40000 | 0 | 6942.95 | 0 | 661.85 | 2997.47 | 2997.47 | 0 | 0 | 0 | 0
2022101613 | 1 | 0.62577 | 50061.6 | 0 | 0 | 0.21938 | 7678.3 | 0.30987 | 4338.18 | 40000 | 0 | 7678.3 | 0 | 2383.3 | 1954.88 | 1954.88 | 0 | 0 | 0 | 0
2022101614 | 1 | 0.65439 | 52351.2 | 0 | 0 | 0.2693 | 9425.5 | 0.32669 | 4573.66 | 40000 | 0 | 9425.5 | 0 | 2925.7 | 1647.96 | 1647.96 | 0 | 0 | 0 | 0
2022101615 | 1 | 0.67302 | 53841.6 | 0 | 0 | 0.32158 | 11255.3 | 0.29406 | 4116.84 | 40000 | 0 | 11255.3 | 0 | 2586.3 | 1530.54 | 1530.54 | 0 | 0 | 0 | 0
2022101616 | 1 | 0.68578 | 54862.4 | 0 | 0 | 0.38696 | 13543.6 | 0.27024 | 3783.36 | 40000 | 0 | 13543.6 | 0 | 1318.8 | 2464.56 | 2464.56 | 0 | 0 | 0 | 0
2022101617 | 1 | 0.69403 | 55522.4 | 0 | 0 | 0.45178 | 15812.3 | 0.18732 | 2622.48 | 40000 | 0 | 15522.4 | 289.9 | 0 | 2622.48 | 2912.38 | 0 | 0 | 0 | 0
2022101618 | 1 | 0.68936 | 55148.8 | 0 | 0 | 0.4472 | 15652 | 0.10555 | 1477.7 | 40000 | 0 | 15148.8 | 503.2 | 0 | 1477.7 | 1980.9 | 0 | 0 | 0 | 0
2022101619 | 1 | 0.67392 | 53913.6 | 0 | 0 | 0.42687 | 14940.45 | 0.03006 | 420.84 | 40000 | 0 | 13913.6 | 1026.85 | 0 | 420.84 | 1447.69 | 0 | 0 | 0 | 0
2022101620 | 1 | 0.66641 | 53312.8 | 0 | 0 | 0.42101 | 14735.35 | 0.01271 | 177.94 | 40000 | 0 | 13312.8 | 1422.55 | 0 | 177.94 | 1600.49 | 0 | 0 | 0 | 0
2022101621 | 1 | 0.64642 | 51713.6 | 0 | 0 | 0.40681 | 14238.35 | 0.00601 | 84.14 | 40000 | 0 | 11713.6 | 2524.75 | 0 | 84.14 | 2608.89 | 0 | 0 | 0 | 0
2022101622 | 1 | 0.6179 | 49432 | 0 | 0 | 0.38146 | 13351.1 | 0 | 0 | 40000 | 0 | 9432 | 3919.1 | 0 | 0 | 3919.1 | 0 | 0 | 0 | 0
2022101623 | 1 | 0.58354 | 46683.2 | 0 | 0 | 0.37294 | 13052.9 | 0 | 0 | 40000 | 0 | 6683.2 | 6369.7 | 0 | 0 | 6369.7 | 0 | 0 | 0 | 0
2022101624 | 1 | 0.54507 | 43605.6 | 0 | 0 | 0.37026 | 12959.1 | 0 | 0 | 40000 | 0 | 3605.6 | 9353.5 | 0 | 0 | 9353.5 | 0 | 0 | 0 | 0
2022101701 | 2 | 0.51083 | 40866.4 | 0 | 0 | 0.35013 | 12254.55 | 0 | 0 | 40000 | 0 | 866.4 | 11388.15 | 0 | 0 | 11388.15 | 0 | 0 | 0 | 0
2022101702 | 2 | 0.48845 | 39076 | 0 | 0 | 0.31788 | 11125.8 | 0 | 0 | 39076 | 924 | 0 | 11125.8 | 0 | 0 | 12049.8 | 0 | 0 | 0 | 0
2022101703 | 2 | 0.47491 | 37992.8 | 0 | 0 | 0.29646 | 10376.1 | 0 | 0 | 37992.8 | 2007.2 | 0 | 10376.1 | 0 | 0 | 12383.3 | 0 | 0 | 0 | 0
2022101704 | 2 | 0.46854 | 37483.2 | 0 | 0 | 0.28982 | 10143.7 | 0 | 0 | 37483.2 | 2516.8 | 0 | 10143.7 | 0 | 0 | 12660.5 | 0 | 0 | 0 | 0
2022101705 | 2 | 0.47108 | 37686.4 | 0 | 0 | 0.32378 | 11332.3 | 0 | 0 | 37686.4 | 2313.6 | 0 | 11332.3 | 0 | 0 | 13645.9 | 0 | 0 | 0 | 0
2022101706 | 2 | 0.48496 | 38796.8 | 0 | 0 | 0.32608 | 11412.8 | 0 | 0 | 38796.8 | 1203.2 | 0 | 11412.8 | 0 | 0 | 12616 | 0 | 0 | 0 | 0
2022101707 | 2 | 0.51035 | 40828 | 0 | 0 | 0.30619 | 10716.65 | 0 | 0 | 40000 | 0 | 828 | 9888.65 | 0 | 0 | 9888.65 | 0 | 0 | 0 | 0
2022101708 | 2 | 0.52478 | 41982.4 | 0 | 0 | 0.2907 | 10174.5 | 0.00137 | 19.18 | 40000 | 0 | 1982.4 | 8192.1 | 0 | 19.18 | 8211.28 | 0 | 0 | 0 | 0
2022101709 | 2 | 0.52705 | 42164 | 0 | 0 | 0.27764 | 9717.4 | 0.05295 | 741.3 | 40000 | 0 | 2164 | 7553.4 | 0 | 741.3 | 8294.7 | 0 | 0 | 0 | 0
2022101710 | 2 | 0.53874 | 43099.2 | 0 | 0 | 0.25812 | 9034.2 | 0.13616 | 1906.24 | 40000 | 0 | 3099.2 | 5935 | 0 | 1906.24 | 7841.24 | 0 | 0 | 0 | 0
2022101711 | 2 | 0.54574 | 43659.2 | 0 | 0 | 0.27068 | 9473.8 | 0.21437 | 3001.18 | 40000 | 0 | 3659.2 | 5814.6 | 0 | 3001.18 | 8815.78 | 0 | 0 | 0 | 0
2022101712 | 2 | 0.54971 | 43976.8 | 0 | 0 | 0.2796 | 9786 | 0.26078 | 3650.92 | 40000 | 0 | 3976.8 | 5809.2 | 0 | 3650.92 | 9460.12 | 0 | 0 | 0 | 0
2022101713 | 2 | 0.55083 | 44066.4 | 0 | 0 | 0.28385 | 9934.75 | 0.30586 | 4282.04 | 40000 | 0 | 4066.4 | 5868.35 | 0 | 4282.04 | 10150.39 | 0 | 0 | 0 | 0
2022101714 | 2 | 0.55386 | 44308.8 | 0 | 0 | 0.28888 | 10110.8 | 0.33411 | 4677.54 | 40000 | 0 | 4308.8 | 5802 | 0 | 4677.54 | 10479.54 | 0 | 0 | 0 | 0
2022101715 | 2 | 0.55282 | 44225.6 | 0 | 0 | 0.28627 | 10019.45 | 0.3348 | 4687.2 | 40000 | 0 | 4225.6 | 5793.85 | 0 | 4687.2 | 10481.05 | 0 | 0 | 0 | 0
2022101716 | 2 | 0.5527 | 44216 | 0 | 0 | 0.2995 | 10482.5 | 0.35208 | 4929.12 | 40000 | 0 | 4216 | 6266.5 | 0 | 4929.12 | 11195.62 | 0 | 0 | 0 | 0
2022101717 | 2 | 0.55829 | 44663.2 | 0 | 0 | 0.30579 | 10702.65 | 0.32966 | 4615.24 | 40000 | 0 | 4663.2 | 6039.45 | 0 | 4615.24 | 10654.69 | 0 | 0 | 0 | 0
2022101718 | 2 | 0.55778 | 44622.4 | 0 | 0 | 0.2994 | 10479 | 0.23842 | 3337.88 | 40000 | 0 | 4622.4 | 5856.6 | 0 | 3337.88 | 9194.48 | 0 | 0 | 0 | 0
2022101719 | 2 | 0.55363 | 44290.4 | 0 | 0 | 0.26183 | 9164.05 | 0.04819 | 674.66 | 40000 | 0 | 4290.4 | 4873.65 | 0 | 674.66 | 5548.31 | 0 | 0 | 0 | 0
2022101720 | 2 | 0.55979 | 44783.2 | 0 | 0 | 0.24308 | 8507.8 | 8e-05 | 1.12 | 40000 | 0 | 4783.2 | 3724.6 | 0 | 1.12 | 3725.72 | 0 | 0 | 0 | 0
2022101721 | 2 | 0.54999 | 43999.2 | 0 | 0 | 0.25587 | 8955.45 | 0 | 0 | 40000 | 0 | 3999.2 | 4956.25 | 0 | 0 | 4956.25 | 0 | 0 | 0 | 0
2022101722 | 2 | 0.52695 | 42156 | 0 | 0 | 0.261 | 9135 | 0 | 0 | 40000 | 0 | 2156 | 6979 | 0 | 0 | 6979 | 0 | 0 | 0 | 0
2022101723 | 2 | 0.49304 | 39443.2 | 0 | 0 | 0.25588 | 8955.8 | 0 | 0 | 39443.2 | 556.8 | 0 | 8955.8 | 0 | 0 | 9512.6 | 0 | 0 | 0 | 0
2022101724 | 2 | 0.4604 | 36832 | 0 | 0 | 0.24152 | 8453.2 | 0 | 0 | 36832 | 3168 | 0 | 8453.2 | 0 | 0 | 11621.2 | 0 | 0 | 0 | 0
2022101801 | 3 | 0.43847 | 35077.6 | 0 | 0 | 0.2315 | 8102.5 | 0 | 0 | 35077.6 | 4922.4 | 0 | 8102.5 | 0 | 0 | 13024.9 | 0 | 0 | 0 | 0
2022101802 | 3 | 0.42605 | 34084 | 0 | 0 | 0.21654 | 7578.9 | 0 | 0 | 34084 | 5916 | 0 | 7578.9 | 0 | 0 | 13494.9 | 0 | 0 | 0 | 0
2022101803 | 3 | 0.41684 | 33347.2 | 0 | 0 | 0.20636 | 7222.6 | 0 | 0 | 33347.2 | 6652.8 | 0 | 7222.6 | 0 | 0 | 13875.4 | 0 | 0 | 0 | 0
2022101804 | 3 | 0.41239 | 32991.2 | 0 | 0 | 0.19448 | 6806.8 | 0 | 0 | 32991.2 | 7008.8 | 0 | 6806.8 | 0 | 0 | 13815.6 | 0 | 0 | 0 | 0
2022101805 | 3 | 0.41819 | 33455.2 | 0 | 0 | 0.17263 | 6042.05 | 0 | 0 | 33455.2 | 6544.8 | 0 | 6042.05 | 0 | 0 | 12586.85 | 0 | 0 | 0 | 0
2022101806 | 3 | 0.43687 | 34949.6 | 0 | 0 | 0.16325 | 5713.75 | 0 | 0 | 34949.6 | 5050.4 | 0 | 5713.75 | 0 | 0 | 10764.15 | 0 | 0 | 0 | 0
2022101807 | 3 | 0.47338 | 37870.4 | 0 | 0 | 0.16731 | 5855.85 | 0 | 0 | 37870.4 | 2129.6 | 0 | 5855.85 | 0 | 0 | 7985.45 | 0 | 0 | 0 | 0
2022101808 | 3 | 0.49217 | 39373.6 | 0 | 0 | 0.1729 | 6051.5 | 0.0032 | 44.8 | 39373.6 | 626.4 | 0 | 6051.5 | 0 | 44.8 | 6722.7 | 0 | 0 | 0 | 0
2022101809 | 3 | 0.49351 | 39480.8 | 0 | 0 | 0.16438 | 5753.3 | 0.1001 | 1401.4 | 39480.8 | 519.2 | 0 | 5753.3 | 0 | 1401.4 | 7673.9 | 0 | 0 | 0 | 0
2022101810 | 3 | 0.4987 | 39896 | 0 | 0 | 0.14154 | 4953.9 | 0.25367 | 3551.38 | 39896 | 104 | 0 | 4953.9 | 0 | 3551.38 | 8609.28 | 0 | 0 | 0 | 0
2022101811 | 3 | 0.50106 | 40084.8 | 0 | 0 | 0.13771 | 4819.85 | 0.33286 | 4660.04 | 40000 | 0 | 84.8 | 4735.05 | 0 | 4660.04 | 9395.09 | 0 | 0 | 0 | 0
2022101812 | 3 | 0.49623 | 39698.4 | 0 | 0 | 0.112 | 3920 | 0.44747 | 6264.58 | 39698.4 | 301.6 | 0 | 3920 | 0 | 6264.58 | 10486.18 | 0 | 0 | 0 | 0
2022101813 | 3 | 0.49242 | 39393.6 | 0 | 0 | 0.09319 | 3261.65 | 0.54627 | 7647.78 | 39393.6 | 606.4 | 0 | 3261.65 | 0 | 7647.78 | 11515.83 | 0 | 0 | 0 | 0
2022101814 | 3 | 0.4958 | 39664 | 0 | 0 | 0.08935 | 3127.25 | 0.59846 | 8378.44 | 39664 | 336 | 0 | 3127.25 | 0 | 8378.44 | 11841.69 | 0 | 0 | 0 | 0
2022101815 | 3 | 0.4952 | 39616 | 0 | 0 | 0.07718 | 2701.3 | 0.59956 | 8393.84 | 39616 | 384 | 0 | 2701.3 | 0 | 8393.84 | 11479.14 | 0 | 0 | 0 | 0
2022101816 | 3 | 0.4982 | 39856 | 0 | 0 | 0.07088 | 2480.8 | 0.57483 | 8047.62 | 39856 | 144 | 0 | 2480.8 | 0 | 8047.62 | 10672.42 | 0 | 0 | 0 | 0
2022101817 | 3 | 0.50521 | 40416.8 | 0 | 0 | 0.06349 | 2222.15 | 0.55291 | 7740.74 | 40000 | 0 | 416.8 | 1805.35 | 0 | 7740.74 | 9546.09 | 0 | 0 | 0 | 0
2022101818 | 3 | 0.5074 | 40592 | 0 | 0 | 0.06141 | 2149.35 | 0.41179 | 5765.06 | 40000 | 0 | 592 | 1557.35 | 0 | 5765.06 | 7322.41 | 0 | 0 | 0 | 0
2022101819 | 3 | 0.51355 | 41084 | 0 | 0 | 0.06333 | 2216.55 | 0.11234 | 1572.76 | 40000 | 0 | 1084 | 1132.55 | 0 | 1572.76 | 2705.31 | 0 | 0 | 0 | 0
2022101820 | 3 | 0.52303 | 41842.4 | 0 | 0 | 0.07754 | 2713.9 | 0.00443 | 62.02 | 40000 | 0 | 1842.4 | 871.5 | 0 | 62.02 | 933.52 | 0 | 0 | 0 | 0
2022101821 | 3 | 0.51968 | 41574.4 | 0 | 0 | 0.10491 | 3671.85 | 0.00291 | 40.74 | 40000 | 0 | 1574.4 | 2097.45 | 0 | 40.74 | 2138.19 | 0 | 0 | 0 | 0
2022101822 | 3 | 0.50268 | 40214.4 | 0 | 0 | 0.13404 | 4691.4 | 0 | 0 | 40000 | 0 | 214.4 | 4477 | 0 | 0 | 4477 | 0 | 0 | 0 | 0
2022101823 | 3 | 0.47548 | 38038.4 | 0 | 0 | 0.14554 | 5093.9 | 0 | 0 | 38038.4 | 1961.6 | 0 | 5093.9 | 0 | 0 | 7055.5 | 0 | 0 | 0 | 0
2022101824 | 3 | 0.44807 | 35845.6 | 0 | 0 | 0.15341 | 5369.35 | 0 | 0 | 35845.6 | 4154.4 | 0 | 5369.35 | 0 | 0 | 9523.75 | 0 | 0 | 0 | 0
2022101901 | 4 | 0.43202 | 34561.6 | 0 | 0 | 0.15365 | 5377.75 | 0 | 0 | 34561.6 | 5438.4 | 0 | 5377.75 | 0 | 0 | 10816.15 | 0 | 0 | 0 | 0
2022101902 | 4 | 0.4231 | 33848 | 0 | 0 | 0.15329 | 5365.15 | 0 | 0 | 33848 | 6152 | 0 | 5365.15 | 0 | 0 | 11517.15 | 0 | 0 | 0 | 0
2022101903 | 4 | 0.41862 | 33489.6 | 0 | 0 | 0.15765 | 5517.75 | 0 | 0 | 33489.6 | 6510.4 | 0 | 5517.75 | 0 | 0 | 12028.15 | 0 | 0 | 0 | 0
2022101904 | 4 | 0.4188 | 33504 | 0 | 0 | 0.15169 | 5309.15 | 0 | 0 | 33504 | 6496 | 0 | 5309.15 | 0 | 0 | 11805.15 | 0 | 0 | 0 | 0
2022101905 | 4 | 0.4274 | 34192 | 0 | 0 | 0.15007 | 5252.45 | 0 | 0 | 34192 | 5808 | 0 | 5252.45 | 0 | 0 | 11060.45 | 0 | 0 | 0 | 0
2022101906 | 4 | 0.44936 | 35948.8 | 0 | 0 | 0.15503 | 5426.05 | 0 | 0 | 35948.8 | 4051.2 | 0 | 5426.05 | 0 | 0 | 9477.25 | 0 | 0 | 0 | 0
2022101907 | 4 | 0.48859 | 39087.2 | 0 | 0 | 0.162 | 5670 | 0 | 0 | 39087.2 | 912.8 | 0 | 5670 | 0 | 0 | 6582.8 | 0 | 0 | 0 | 0
2022101908 | 4 | 0.50996 | 40796.8 | 0 | 0 | 0.16211 | 5673.85 | 0.00516 | 72.24 | 40000 | 0 | 796.8 | 4877.05 | 0 | 72.24 | 4949.29 | 0 | 0 | 0 | 0
2022101909 | 4 | 0.50839 | 40671.2 | 0 | 0 | 0.15615 | 5465.25 | 0.21378 | 2992.92 | 40000 | 0 | 671.2 | 4794.05 | 0 | 2992.92 | 7786.97 | 0 | 0 | 0 | 0
2022101910 | 4 | 0.50541 | 40432.8 | 0 | 0 | 0.11293 | 3952.55 | 0.64213 | 8989.82 | 40000 | 0 | 432.8 | 3519.75 | 0 | 8989.82 | 12509.57 | 0 | 0 | 0 | 0
2022101911 | 4 | 0.49997 | 39997.6 | 0 | 0 | 0.09537 | 3337.95 | 0.77127 | 10797.78 | 39997.6 | 2.4 | 0 | 3337.95 | 0 | 10797.78 | 14138.13 | 0 | 0 | 0 | 0
2022101912 | 4 | 0.49616 | 39692.8 | 0 | 0 | 0.1164 | 4074 | 0.77965 | 10915.1 | 39692.8 | 307.2 | 0 | 4074 | 0 | 10915.1 | 15296.3 | 0 | 0 | 0 | 0
2022101913 | 4 | 0.4936 | 39488 | 0 | 0 | 0.12805 | 4481.75 | 0.76907 | 10766.98 | 39488 | 512 | 0 | 4481.75 | 0 | 10766.98 | 15760.73 | 0 | 0 | 0 | 0
2022101914 | 4 | 0.49774 | 39819.2 | 0 | 0 | 0.12392 | 4337.2 | 0.76491 | 10708.74 | 39819.2 | 180.8 | 0 | 4337.2 | 0 | 10708.74 | 15226.74 | 0 | 0 | 0 | 0
2022101915 | 4 | 0.49907 | 39925.6 | 0 | 0 | 0.11156 | 3904.6 | 0.77323 | 10825.22 | 39925.6 | 74.4 | 0 | 3904.6 | 0 | 10825.22 | 14804.22 | 0 | 0 | 0 | 0
2022101916 | 4 | 0.50442 | 40353.6 | 0 | 0 | 0.09804 | 3431.4 | 0.78931 | 11050.34 | 40000 | 0 | 353.6 | 3077.8 | 0 | 11050.34 | 14128.14 | 0 | 0 | 0 | 0
2022101917 | 4 | 0.51366 | 41092.8 | 0 | 0 | 0.09316 | 3260.6 | 0.77641 | 10869.74 | 40000 | 0 | 1092.8 | 2167.8 | 0 | 10869.74 | 13037.54 | 0 | 0 | 0 | 0
2022101918 | 4 | 0.51874 | 41499.2 | 0 | 0 | 0.0934 | 3269 | 0.61014 | 8541.96 | 40000 | 0 | 1499.2 | 1769.8 | 0 | 8541.96 | 10311.76 | 0 | 0 | 0 | 0
2022101919 | 4 | 0.51817 | 41453.6 | 0 | 0 | 0.08445 | 2955.75 | 0.1659 | 2322.6 | 40000 | 0 | 1453.6 | 1502.15 | 0 | 2322.6 | 3824.75 | 0 | 0 | 0 | 0
2022101920 | 4 | 0.52447 | 41957.6 | 0 | 0 | 0.12202 | 4270.7 | 0.00092 | 12.88 | 40000 | 0 | 1957.6 | 2313.1 | 0 | 12.88 | 2325.98 | 0 | 0 | 0 | 0
2022101921 | 4 | 0.5178 | 41424 | 0 | 0 | 0.21563 | 7547.05 | 0 | 0 | 40000 | 0 | 1424 | 6123.05 | 0 | 0 | 6123.05 | 0 | 0 | 0 | 0
2022101922 | 4 | 0.50094 | 40075.2 | 0 | 0 | 0.32278 | 11297.3 | 0 | 0 | 40000 | 0 | 75.2 | 11222.1 | 0 | 0 | 11222.1 | 0 | 0 | 0 | 0
2022101923 | 4 | 0.47435 | 37948 | 0 | 0 | 0.4219 | 14766.5 | 0 | 0 | 37948 | 2052 | 0 | 14766.5 | 0 | 0 | 16818.5 | 0 | 0 | 0 | 0
2022101924 | 4 | 0.45256 | 36204.8 | 0 | 0 | 0.47512 | 16629.2 | 0 | 0 | 36204.8 | 3795.2 | 0 | 16629.2 | 0 | 0 | 20424.4 | 0 | 0 | 0 | 0
2022102001 | 5 | 0.43298 | 34638.4 | 0 | 0 | 0.48901 | 17115.35 | 0 | 0 | 34638.4 | 5361.6 | 0 | 17115.35 | 0 | 0 | 22476.95 | 0 | 0 | 0 | 0
2022102002 | 5 | 0.42445 | 33956 | 0 | 0 | 0.49597 | 17358.95 | 0 | 0 | 33956 | 6044 | 0 | 17358.95 | 0 | 0 | 23402.95 | 0 | 0 | 0 | 0
2022102003 | 5 | 0.42027 | 33621.6 | 0 | 0 | 0.49745 | 17410.75 | 0 | 0 | 33621.6 | 6378.4 | 0 | 17410.75 | 0 | 0 | 23789.15 | 0 | 0 | 0 | 0
2022102004 | 5 | 0.41918 | 33534.4 | 0 | 0 | 0.49406 | 17292.1 | 0 | 0 | 33534.4 | 6465.6 | 0 | 17292.1 | 0 | 0 | 23757.7 | 0 | 0 | 0 | 0
2022102005 | 5 | 0.42513 | 34010.4 | 0 | 0 | 0.4895 | 17132.5 | 0 | 0 | 34010.4 | 5989.6 | 0 | 17132.5 | 0 | 0 | 23122.1 | 0 | 0 | 0 | 0
2022102006 | 5 | 0.44942 | 35953.6 | 0 | 0 | 0.50941 | 17829.35 | 0 | 0 | 35953.6 | 4046.4 | 0 | 17829.35 | 0 | 0 | 21875.75 | 0 | 0 | 0 | 0
2022102007 | 5 | 0.48524 | 38819.2 | 0 | 0 | 0.48252 | 16888.2 | 0 | 0 | 38819.2 | 1180.8 | 0 | 16888.2 | 0 | 0 | 18069 | 0 | 0 | 0 | 0
2022102008 | 5 | 0.50435 | 40348 | 0 | 0 | 0.44006 | 15402.1 | 0.00392 | 54.88 | 40000 | 0 | 348 | 15054.1 | 0 | 54.88 | 15108.98 | 0 | 0 | 0 | 0
2022102009 | 5 | 0.50406 | 40324.8 | 0 | 0 | 0.37405 | 13091.75 | 0.22418 | 3138.52 | 40000 | 0 | 324.8 | 12766.95 | 0 | 3138.52 | 15905.47 | 0 | 0 | 0 | 0
2022102010 | 5 | 0.50291 | 40232.8 | 0 | 0 | 0.24441 | 8554.35 | 0.67731 | 9482.34 | 40000 | 0 | 232.8 | 8321.55 | 0 | 9482.34 | 17803.89 | 0 | 0 | 0 | 0
2022102011 | 5 | 0.50334 | 40267.2 | 0 | 0 | 0.14853 | 5198.55 | 0.79108 | 11075.12 | 40000 | 0 | 267.2 | 4931.35 | 0 | 11075.12 | 16006.47 | 0 | 0 | 0 | 0
2022102012 | 5 | 0.50796 | 40636.8 | 0 | 0 | 0.11054 | 3868.9 | 0.79119 | 11076.66 | 40000 | 0 | 636.8 | 3232.1 | 0 | 11076.66 | 14308.76 | 0 | 0 | 0 | 0
2022102013 | 5 | 0.51612 | 41289.6 | 0 | 0 | 0.07493 | 2622.55 | 0.77538 | 10855.32 | 40000 | 0 | 1289.6 | 1332.95 | 0 | 10855.32 | 12188.27 | 0 | 0 | 0 | 0
2022102014 | 5 | 0.5306 | 42448 | 0 | 0 | 0.05379 | 1882.65 | 0.76643 | 10730.02 | 40000 | 0 | 1882.65 | 0 | 565.35 | 10164.67 | 10164.67 | 0 | 0 | 0 | 0
2022102015 | 5 | 0.54585 | 43668 | 0 | 0 | 0.04677 | 1636.95 | 0.77073 | 10790.22 | 40000 | 0 | 1636.95 | 0 | 2031.05 | 8759.17 | 8759.17 | 0 | 0 | 0 | 0
2022102016 | 5 | 0.56414 | 45131.2 | 0 | 0 | 0.04818 | 1686.3 | 0.77974 | 10916.36 | 40000 | 0 | 1686.3 | 0 | 3444.9 | 7471.46 | 7471.46 | 0 | 0 | 0 | 0
2022102017 | 5 | 0.58117 | 46493.6 | 0 | 0 | 0.05734 | 2006.9 | 0.76426 | 10699.64 | 40000 | 0 | 2006.9 | 0 | 4486.7 | 6212.94 | 6212.94 | 0 | 0 | 0 | 0
2022102018 | 5 | 0.58669 | 46935.2 | 0 | 0 | 0.06898 | 2414.3 | 0.60034 | 8404.76 | 40000 | 0 | 2414.3 | 0 | 4520.9 | 3883.86 | 3883.86 | 0 | 0 | 0 | 0
2022102019 | 5 | 0.57278 | 45822.4 | 0 | 0 | 0.07916 | 2770.6 | 0.16774 | 2348.36 | 40000 | 0 | 2770.6 | 0 | 2348.36 | 0 | 0 | 703.44 | 0 | 0 | 703.44
2022102020 | 5 | 0.56696 | 45356.8 | 0 | 0 | 0.10494 | 3672.9 | 0.01284 | 179.76 | 40000 | 0 | 3672.9 | 0 | 179.76 | 0 | 0 | 1504.14 | 0 | 0 | 1504.14
2022102021 | 5 | 0.55737 | 44589.6 | 0 | 0 | 0.14588 | 5105.8 | 0 | 0 | 40000 | 0 | 4589.6 | 516.2 | 0 | 0 | 516.2 | 0 | 0 | 0 | 0
2022102022 | 5 | 0.53968 | 43174.4 | 0 | 0 | 0.21542 | 7539.7 | 0 | 0 | 40000 | 0 | 3174.4 | 4365.3 | 0 | 0 | 4365.3 | 0 | 0 | 0 | 0
2022102023 | 5 | 0.50777 | 40621.6 | 0 | 0 | 0.26813 | 9384.55 | 0 | 0 | 40000 | 0 | 621.6 | 8762.95 | 0 | 0 | 8762.95 | 0 | 0 | 0 | 0
2022102024 | 5 | 0.47424 | 37939.2 | 0 | 0 | 0.3166 | 11081 | 0 | 0 | 37939.2 | 2060.8 | 0 | 11081 | 0 | 0 | 13141.8 | 0 | 0 | 0 | 0
2022102101 | 6 | 0.45081 | 36064.8 | 0 | 0 | 0.40313 | 14109.55 | 0 | 0 | 36064.8 | 3935.2 | 0 | 14109.55 | 0 | 0 | 18044.75 | 0 | 0 | 0 | 0
2022102102 | 6 | 0.43657 | 34925.6 | 0 | 0 | 0.45513 | 15929.55 | 0 | 0 | 34925.6 | 5074.4 | 0 | 15929.55 | 0 | 0 | 21003.95 | 0 | 0 | 0 | 0
2022102103 | 6 | 0.42701 | 34160.8 | 0 | 0 | 0.46407 | 16242.45 | 0 | 0 | 34160.8 | 5839.2 | 0 | 16242.45 | 0 | 0 | 22081.65 | 0 | 0 | 0 | 0
2022102104 | 6 | 0.42446 | 33956.8 | 0 | 0 | 0.4734 | 16569 | 0 | 0 | 33956.8 | 6043.2 | 0 | 16569 | 0 | 0 | 22612.2 | 0 | 0 | 0 | 0
2022102105 | 6 | 0.42859 | 34287.2 | 0 | 0 | 0.486 | 17010 | 0 | 0 | 34287.2 | 5712.8 | 0 | 17010 | 0 | 0 | 22722.8 | 0 | 0 | 0 | 0
2022102106 | 6 | 0.44546 | 35636.8 | 0 | 0 | 0.48106 | 16837.1 | 4e-05 | 0.56 | 35636.8 | 4363.2 | 0 | 16837.1 | 0 | 0.56 | 21200.86 | 0 | 0 | 0 | 0
2022102107 | 6 | 0.47906 | 38324.8 | 0 | 0 | 0.45604 | 15961.4 | 0 | 0 | 38324.8 | 1675.2 | 0 | 15961.4 | 0 | 0 | 17636.6 | 0 | 0 | 0 | 0
2022102108 | 6 | 0.49607 | 39685.6 | 0 | 0 | 0.45677 | 15986.95 | 0.00388 | 54.32 | 39685.6 | 314.4 | 0 | 15986.95 | 0 | 54.32 | 16355.67 | 0 | 0 | 0 | 0
2022102109 | 6 | 0.50038 | 40030.4 | 0 | 0 | 0.43876 | 15356.6 | 0.22518 | 3152.52 | 40000 | 0 | 30.4 | 15326.2 | 0 | 3152.52 | 18478.72 | 0 | 0 | 0 | 0
2022102110 | 6 | 0.51083 | 40866.4 | 0 | 0 | 0.30875 | 10806.25 | 0.68578 | 9600.92 | 40000 | 0 | 866.4 | 9939.85 | 0 | 9600.92 | 19540.77 | 0 | 0 | 0 | 0
2022102111 | 6 | 0.52256 | 41804.8 | 0 | 0 | 0.21927 | 7674.45 | 0.78689 | 11016.46 | 40000 | 0 | 1804.8 | 5869.65 | 0 | 11016.46 | 16886.11 | 0 | 0 | 0 | 0
2022102112 | 6 | 0.53584 | 42867.2 | 0 | 0 | 0.22074 | 7725.9 | 0.77791 | 10890.74 | 40000 | 0 | 2867.2 | 4858.7 | 0 | 10890.74 | 15749.44 | 0 | 0 | 0 | 0
2022102113 | 6 | 0.55745 | 44596 | 0 | 0 | 0.25829 | 9040.15 | 0.74824 | 10475.36 | 40000 | 0 | 4596 | 4444.15 | 0 | 10475.36 | 14919.51 | 0 | 0 | 0 | 0
2022102114 | 6 | 0.58724 | 46979.2 | 0 | 0 | 0.36391 | 12736.85 | 0.74377 | 10412.78 | 40000 | 0 | 6979.2 | 5757.65 | 0 | 10412.78 | 16170.43 | 0 | 0 | 0 | 0
2022102115 | 6 | 0.6157 | 49256 | 0 | 0 | 0.46311 | 16208.85 | 0.65327 | 9145.78 | 40000 | 0 | 9256 | 6952.85 | 0 | 9145.78 | 16098.63 | 0 | 0 | 0 | 0
2022102116 | 6 | 0.64 | 51200 | 0 | 0 | 0.52843 | 18495.05 | 0.53846 | 7538.44 | 40000 | 0 | 11200 | 7295.05 | 0 | 7538.44 | 14833.49 | 0 | 0 | 0 | 0
2022102117 | 6 | 0.65569 | 52455.2 | 0 | 0 | 0.5328 | 18648 | 0.54607 | 7644.98 | 40000 | 0 | 12455.2 | 6192.8 | 0 | 7644.98 | 13837.78 | 0 | 0 | 0 | 0
2022102118 | 6 | 0.65444 | 52355.2 | 0 | 0 | 0.55175 | 19311.25 | 0.39079 | 5471.06 | 40000 | 0 | 12355.2 | 6956.05 | 0 | 5471.06 | 12427.11 | 0 | 0 | 0 | 0
2022102119 | 6 | 0.63154 | 50523.2 | 0 | 0 | 0.54852 | 19198.2 | 0.12763 | 1786.82 | 40000 | 0 | 10523.2 | 8675 | 0 | 1786.82 | 10461.82 | 0 | 0 | 0 | 0
2022102120 | 6 | 0.61547 | 49237.6 | 0 | 0 | 0.58335 | 20417.25 | 0.00046 | 6.44 | 40000 | 0 | 9237.6 | 11179.65 | 0 | 6.44 | 11186.09 | 0 | 0 | 0 | 0
2022102121 | 6 | 0.59593 | 47674.4 | 0 | 0 | 0.66267 | 23193.45 | 0 | 0 | 40000 | 0 | 7674.4 | 15519.05 | 0 | 0 | 15519.05 | 0 | 0 | 0 | 0
2022102122 | 6 | 0.57469 | 45975.2 | 0 | 0 | 0.6736 | 23576 | 0 | 0 | 40000 | 0 | 5975.2 | 17600.8 | 0 | 0 | 17600.8 | 0 | 0 | 0 | 0
2022102123 | 6 | 0.54834 | 43867.2 | 0 | 0 | 0.67373 | 23580.55 | 0 | 0 | 40000 | 0 | 3867.2 | 19713.35 | 0 | 0 | 19713.35 | 0 | 0 | 0 | 0
2022102124 | 6 | 0.51794 | 41435.2 | 0 | 0 | 0.66824 | 23388.4 | 0 | 0 | 40000 | 0 | 1435.2 | 21953.2 | 0 | 0 | 21953.2 | 0 | 0 | 0 | 0
2022102201 | 7 | 0.49211 | 39368.8 | 0 | 0 | 0.66391 | 23236.85 | 0 | 0 | 39368.8 | 631.2 | 0 | 23236.85 | 0 | 0 | 23868.05 | 0 | 0 | 0 | 0
2022102202 | 7 | 0.46938 | 37550.4 | 0 | 0 | 0.65535 | 22937.25 | 0 | 0 | 37550.4 | 2449.6 | 0 | 22937.25 | 0 | 0 | 25386.85 | 0 | 0 | 0 | 0
2022102203 | 7 | 0.45544 | 36435.2 | 0 | 0 | 0.64883 | 22709.05 | 0 | 0 | 36435.2 | 3564.8 | 0 | 22709.05 | 0 | 0 | 26273.85 | 0 | 0 | 0 | 0
2022102204 | 7 | 0.44671 | 35736.8 | 0 | 0 | 0.6427 | 22494.5 | 0 | 0 | 35736.8 | 4263.2 | 0 | 22494.5 | 0 | 0 | 26757.7 | 0 | 0 | 0 | 0
2022102205 | 7 | 0.44302 | 35441.6 | 0 | 0 | 0.64307 | 22507.45 | 0 | 0 | 35441.6 | 4558.4 | 0 | 22507.45 | 0 | 0 | 27065.85 | 0 | 0 | 0 | 0
2022102206 | 7 | 0.44681 | 35744.8 | 0 | 0 | 0.64615 | 22615.25 | 0 | 0 | 35744.8 | 4255.2 | 0 | 22615.25 | 0 | 0 | 26870.45 | 0 | 0 | 0 | 0
2022102207 | 7 | 0.45844 | 36675.2 | 0 | 0 | 0.65039 | 22763.65 | 0 | 0 | 36675.2 | 3324.8 | 0 | 22763.65 | 0 | 0 | 26088.45 | 0 | 0 | 0 | 0
2022102208 | 7 | 0.46979 | 37583.2 | 0 | 0 | 0.6405 | 22417.5 | 0.00316 | 44.24 | 37583.2 | 2416.8 | 0 | 22417.5 | 0 | 44.24 | 24878.54 | 0 | 0 | 0 | 0
2022102209 | 7 | 0.48683 | 38946.4 | 0 | 0 | 0.6104 | 21364 | 0.15647 | 2190.58 | 38946.4 | 1053.6 | 0 | 21364 | 0 | 2190.58 | 24608.18 | 0 | 0 | 0 | 0
2022102210 | 7 | 0.51221 | 40976.8 | 0 | 0 | 0.53499 | 18724.65 | 0.45593 | 6383.02 | 40000 | 0 | 976.8 | 17747.85 | 0 | 6383.02 | 24130.87 | 0 | 0 | 0 | 0
2022102211 | 7 | 0.53601 | 42880.8 | 0 | 0 | 0.52307 | 18307.45 | 0.59921 | 8388.94 | 40000 | 0 | 2880.8 | 15426.65 | 0 | 8388.94 | 23815.59 | 0 | 0 | 0 | 0
2022102212 | 7 | 0.5629 | 45032 | 0 | 0 | 0.52563 | 18397.05 | 0.62947 | 8812.58 | 40000 | 0 | 5032 | 13365.05 | 0 | 8812.58 | 22177.63 | 0 | 0 | 0 | 0
2022102213 | 7 | 0.59074 | 47259.2 | 0 | 0 | 0.53366 | 18678.1 | 0.65654 | 9191.56 | 40000 | 0 | 7259.2 | 11418.9 | 0 | 9191.56 | 20610.46 | 0 | 0 | 0 | 0
2022102214 | 7 | 0.61537 | 49229.6 | 0 | 0 | 0.55098 | 19284.3 | 0.64922 | 9089.08 | 40000 | 0 | 9229.6 | 10054.7 | 0 | 9089.08 | 19143.78 | 0 | 0 | 0 | 0
2022102215 | 7 | 0.63904 | 51123.2 | 0 | 0 | 0.56428 | 19749.8 | 0.61837 | 8657.18 | 40000 | 0 | 11123.2 | 8626.6 | 0 | 8657.18 | 17283.78 | 0 | 0 | 0 | 0
2022102216 | 7 | 0.65637 | 52509.6 | 0 | 0 | 0.57946 | 20281.1 | 0.58024 | 8123.36 | 40000 | 0 | 12509.6 | 7771.5 | 0 | 8123.36 | 15894.86 | 0 | 0 | 0 | 0
2022102217 | 7 | 0.66437 | 53149.6 | 0 | 0 | 0.6106 | 21371 | 0.4859 | 6802.6 | 40000 | 0 | 13149.6 | 8221.4 | 0 | 6802.6 | 15024 | 0 | 0 | 0 | 0
2022102218 | 7 | 0.65838 | 52670.4 | 0 | 0 | 0.62291 | 21801.85 | 0.35167 | 4923.38 | 40000 | 0 | 12670.4 | 9131.45 | 0 | 4923.38 | 14054.83 | 0 | 0 | 0 | 0
2022102219 | 7 | 0.63635 | 50908 | 0 | 0 | 0.61887 | 21660.45 | 0.08127 | 1137.78 | 40000 | 0 | 10908 | 10752.45 | 0 | 1137.78 | 11890.23 | 0 | 0 | 0 | 0
2022102220 | 7 | 0.63047 | 50437.6 | 0 | 0 | 0.66882 | 23408.7 | 0.0004 | 5.6 | 40000 | 0 | 10437.6 | 12971.1 | 0 | 5.6 | 12976.7 | 0 | 0 | 0 | 0
2022102221 | 7 | 0.61444 | 49155.2 | 0 | 0 | 0.69301 | 24255.35 | 0 | 0 | 40000 | 0 | 9155.2 | 15100.15 | 0 | 0 | 15100.15 | 0 | 0 | 0 | 0
2022102222 | 7 | 0.59395 | 47516 | 0 | 0 | 0.69897 | 24463.95 | 0 | 0 | 40000 | 0 | 7516 | 16947.95 | 0 | 0 | 16947.95 | 0 | 0 | 0 | 0
2022102223 | 7 | 0.57 | 45600 | 0 | 0 | 0.69285 | 24249.75 | 0 | 0 | 40000 | 0 | 5600 | 18649.75 | 0 | 0 | 18649.75 | 0 | 0 | 0 | 0
2022102224 | 7 | 0.54383 | 43506.4 | 0 | 0 | 0.6915 | 24202.5 | 0 | 0 | 40000 | 0 | 3506.4 | 20696.1 | 0 | 0 | 20696.1 | 0 | 0 | 0 | 0
2022102301 | 1 | 0.51582 | 41265.6 | 0 | 0 | 0.68162 | 23856.7 | 0 | 0 | 40000 | 0 | 1265.6 | 22591.1 | 0 | 0 | 22591.1 | 0 | 0 | 0 | 0
2022102302 | 1 | 0.49465 | 39572 | 0 | 0 | 0.67446 | 23606.1 | 0 | 0 | 39572 | 428 | 0 | 23606.1 | 0 | 0 | 24034.1 | 0 | 0 | 0 | 0
2022102303 | 1 | 0.47832 | 38265.6 | 0 | 0 | 0.6662 | 23317 | 0 | 0 | 38265.6 | 1734.4 | 0 | 23317 | 0 | 0 | 25051.4 | 0 | 0 | 0 | 0
2022102304 | 1 | 0.4689 | 37512 | 0 | 0 | 0.66207 | 23172.45 | 0 | 0 | 37512 | 2488 | 0 | 23172.45 | 0 | 0 | 25660.45 | 0 | 0 | 0 | 0
2022102305 | 1 | 0.46302 | 37041.6 | 0 | 0 | 0.65598 | 22959.3 | 0 | 0 | 37041.6 | 2958.4 | 0 | 22959.3 | 0 | 0 | 25917.7 | 0 | 0 | 0 | 0
2022102306 | 1 | 0.46378 | 37102.4 | 0 | 0 | 0.6567 | 22984.5 | 0 | 0 | 37102.4 | 2897.6 | 0 | 22984.5 | 0 | 0 | 25882.1 | 0 | 0 | 0 | 0
2022102307 | 1 | 0.46991 | 37592.8 | 0 | 0 | 0.66132 | 23146.2 | 0 | 0 | 37592.8 | 2407.2 | 0 | 23146.2 | 0 | 0 | 25553.4 | 0 | 0 | 0 | 0
2022102308 | 1 | 0.47791 | 38232.8 | 0 | 0 | 0.66169 | 23159.15 | 0.00229 | 32.06 | 38232.8 | 1767.2 | 0 | 23159.15 | 0 | 32.06 | 24958.41 | 0 | 0 | 0 | 0
2022102309 | 1 | 0.49607 | 39685.6 | 0 | 0 | 0.64976 | 22741.6 | 0.09953 | 1393.42 | 39685.6 | 314.4 | 0 | 22741.6 | 0 | 1393.42 | 24449.42 | 0 | 0 | 0 | 0
2022102310 | 1 | 0.52669 | 42135.2 | 0 | 0 | 0.63023 | 22058.05 | 0.30738 | 4303.32 | 40000 | 0 | 2135.2 | 19922.85 | 0 | 4303.32 | 24226.17 | 0 | 0 | 0 | 0
2022102311 | 1 | 0.55891 | 44712.8 | 0 | 0 | 0.66217 | 23175.95 | 0.32167 | 4503.38 | 40000 | 0 | 4712.8 | 18463.15 | 0 | 4503.38 | 22966.53 | 0 | 0 | 0 | 0
2022102312 | 1 | 0.59177 | 47341.6 | 0 | 0 | 0.66777 | 23371.95 | 0.29014 | 4061.96 | 40000 | 0 | 7341.6 | 16030.35 | 0 | 4061.96 | 20092.31 | 0 | 0 | 0 | 0
2022102313 | 1 | 0.61831 | 49464.8 | 0 | 0 | 0.67309 | 23558.15 | 0.30965 | 4335.1 | 40000 | 0 | 9464.8 | 14093.35 | 0 | 4335.1 | 18428.45 | 0 | 0 | 0 | 0
2022102314 | 1 | 0.64032 | 51225.6 | 0 | 0 | 0.67579 | 23652.65 | 0.31264 | 4376.96 | 40000 | 0 | 11225.6 | 12427.05 | 0 | 4376.96 | 16804.01 | 0 | 0 | 0 | 0
2022102315 | 1 | 0.66096 | 52876.8 | 0 | 0 | 0.6753 | 23635.5 | 0.31006 | 4340.84 | 40000 | 0 | 12876.8 | 10758.7 | 0 | 4340.84 | 15099.54 | 0 | 0 | 0 | 0
2022102316 | 1 | 0.67637 | 54109.6 | 0 | 0 | 0.6758 | 23653 | 0.29878 | 4182.92 | 40000 | 0 | 14109.6 | 9543.4 | 0 | 4182.92 | 13726.32 | 0 | 0 | 0 | 0
2022102317 | 1 | 0.68385 | 54708 | 0 | 0 | 0.67844 | 23745.4 | 0.27211 | 3809.54 | 40000 | 0 | 14708 | 9037.4 | 0 | 3809.54 | 12846.94 | 0 | 0 | 0 | 0
2022102318 | 1 | 0.68003 | 54402.4 | 0 | 0 | 0.68126 | 23844.1 | 0.17367 | 2431.38 | 40000 | 0 | 14402.4 | 9441.7 | 0 | 2431.38 | 11873.08 | 0 | 0 | 0 | 0
2022102319 | 1 | 0.66659 | 53327.2 | 0 | 0 | 0.694 | 24290 | 0.04064 | 568.96 | 40000 | 0 | 13327.2 | 10962.8 | 0 | 568.96 | 11531.76 | 0 | 0 | 0 | 0
2022102320 | 1 | 0.66692 | 53353.6 | 0 | 0 | 0.70734 | 24756.9 | 0.00022 | 3.08 | 40000 | 0 | 13353.6 | 11403.3 | 0 | 3.08 | 11406.38 | 0 | 0 | 0 | 0
2022102321 | 1 | 0.65374 | 52299.2 | 0 | 0 | 0.70573 | 24700.55 | 0 | 0 | 40000 | 0 | 12299.2 | 12401.35 | 0 | 0 | 12401.35 | 0 | 0 | 0 | 0
2022102322 | 1 | 0.63173 | 50538.4 | 0 | 0 | 0.70174 | 24560.9 | 0 | 0 | 40000 | 0 | 10538.4 | 14022.5 | 0 | 0 | 14022.5 | 0 | 0 | 0 | 0
2022102323 | 1 | 0.60274 | 48219.2 | 0 | 0 | 0.70196 | 24568.6 | 0 | 0 | 40000 | 0 | 8219.2 | 16349.4 | 0 | 0 | 16349.4 | 0 | 0 | 0 | 0
2022102324 | 1 | 0.56916 | 45532.8 | 0 | 0 | 0.69139 | 24198.65 | 0 | 0 | 40000 | 0 | 5532.8 | 18665.85 | 0 | 0 | 18665.85 | 0 | 0 | 0 | 0
2022102401 | 2 | 0.54121 | 43296.8 | 0 | 0 | 0.68101 | 23835.35 | 0 | 0 | 40000 | 0 | 3296.8 | 20538.55 | 0 | 0 | 20538.55 | 0 | 0 | 0 | 0
2022102402 | 2 | 0.5213 | 41704 | 0 | 0 | 0.67176 | 23511.6 | 0 | 0 | 40000 | 0 | 1704 | 21807.6 | 0 | 0 | 21807.6 | 0 | 0 | 0 | 0
2022102403 | 2 | 0.51073 | 40858.4 | 0 | 0 | 0.66479 | 23267.65 | 0 | 0 | 40000 | 0 | 858.4 | 22409.25 | 0 | 0 | 22409.25 | 0 | 0 | 0 | 0
2022102404 | 2 | 0.50592 | 40473.6 | 0 | 0 | 0.64092 | 22432.2 | 0 | 0 | 40000 | 0 | 473.6 | 21958.6 | 0 | 0 | 21958.6 | 0 | 0 | 0 | 0
2022102405 | 2 | 0.50893 | 40714.4 | 0 | 0 | 0.63752 | 22313.2 | 0 | 0 | 40000 | 0 | 714.4 | 21598.8 | 0 | 0 | 21598.8 | 0 | 0 | 0 | 0
2022102406 | 2 | 0.52734 | 42187.2 | 0 | 0 | 0.58738 | 20558.3 | 0 | 0 | 40000 | 0 | 2187.2 | 18371.1 | 0 | 0 | 18371.1 | 0 | 0 | 0 | 0
2022102407 | 2 | 0.56009 | 44807.2 | 0 | 0 | 0.558 | 19530 | 0 | 0 | 40000 | 0 | 4807.2 | 14722.8 | 0 | 0 | 14722.8 | 0 | 0 | 0 | 0
2022102408 | 2 | 0.57446 | 45956.8 | 0 | 0 | 0.41173 | 14410.55 | 0.00065 | 9.1 | 40000 | 0 | 5956.8 | 8453.75 | 0 | 9.1 | 8462.85 | 0 | 0 | 0 | 0
2022102409 | 2 | 0.57647 | 46117.6 | 0 | 0 | 0.32967 | 11538.45 | 0.06722 | 941.08 | 40000 | 0 | 6117.6 | 5420.85 | 0 | 941.08 | 6361.93 | 0 | 0 | 0 | 0
2022102410 | 2 | 0.59 | 47200 | 0 | 0 | 0.29335 | 10267.25 | 0.26712 | 3739.68 | 40000 | 0 | 7200 | 3067.25 | 0 | 3739.68 | 6806.93 | 0 | 0 | 0 | 0
2022102411 | 2 | 0.60355 | 48284 | 0 | 0 | 0.28445 | 9955.75 | 0.41102 | 5754.28 | 40000 | 0 | 8284 | 1671.75 | 0 | 5754.28 | 7426.03 | 0 | 0 | 0 | 0
2022102412 | 2 | 0.61222 | 48977.6 | 0 | 0 | 0.29215 | 10225.25 | 0.45889 | 6424.46 | 40000 | 0 | 8977.6 | 1247.65 | 0 | 6424.46 | 7672.11 | 0 | 0 | 0 | 0
2022102413 | 2 | 0.61533 | 49226.4 | 0 | 0 | 0.29964 | 10487.4 | 0.47072 | 6590.08 | 40000 | 0 | 9226.4 | 1261 | 0 | 6590.08 | 7851.08 | 0 | 0 | 0 | 0
2022102414 | 2 | 0.61977 | 49581.6 | 0 | 0 | 0.31079 | 10877.65 | 0.40078 | 5610.92 | 40000 | 0 | 9581.6 | 1296.05 | 0 | 5610.92 | 6906.97 | 0 | 0 | 0 | 0
2022102415 | 2 | 0.62366 | 49892.8 | 0 | 0 | 0.34605 | 12111.75 | 0.38452 | 5383.28 | 40000 | 0 | 9892.8 | 2218.95 | 0 | 5383.28 | 7602.23 | 0 | 0 | 0 | 0
2022102416 | 2 | 0.63178 | 50542.4 | 0 | 0 | 0.41166 | 14408.1 | 0.39516 | 5532.24 | 40000 | 0 | 10542.4 | 3865.7 | 0 | 5532.24 | 9397.94 | 0 | 0 | 0 | 0
2022102417 | 2 | 0.63901 | 51120.8 | 0 | 0 | 0.48882 | 17108.7 | 0.27717 | 3880.38 | 40000 | 0 | 11120.8 | 5987.9 | 0 | 3880.38 | 9868.28 | 0 | 0 | 0 | 0
2022102418 | 2 | 0.64106 | 51284.8 | 0 | 0 | 0.51252 | 17938.2 | 0.23496 | 3289.44 | 40000 | 0 | 11284.8 | 6653.4 | 0 | 3289.44 | 9942.84 | 0 | 0 | 0 | 0
2022102419 | 2 | 0.63821 | 51056.8 | 0 | 0 | 0.56352 | 19723.2 | 0.08186 | 1146.04 | 40000 | 0 | 11056.8 | 8666.4 | 0 | 1146.04 | 9812.44 | 0 | 0 | 0 | 0
2022102420 | 2 | 0.64243 | 51394.4 | 0 | 0 | 0.60018 | 21006.3 | 0.0035 | 49 | 40000 | 0 | 11394.4 | 9611.9 | 0 | 49 | 9660.9 | 0 | 0 | 0 | 0
2022102421 | 2 | 0.62927 | 50341.6 | 0 | 0 | 0.61921 | 21672.35 | 0 | 0 | 40000 | 0 | 10341.6 | 11330.75 | 0 | 0 | 11330.75 | 0 | 0 | 0 | 0
2022102422 | 2 | 0.60126 | 48100.8 | 0 | 0 | 0.61895 | 21663.25 | 0 | 0 | 40000 | 0 | 8100.8 | 13562.45 | 0 | 0 | 13562.45 | 0 | 0 | 0 | 0
2022102423 | 2 | 0.55515 | 44412 | 0 | 0 | 0.62185 | 21764.75 | 0 | 0 | 40000 | 0 | 4412 | 17352.75 | 0 | 0 | 17352.75 | 0 | 0 | 0 | 0
2022102424 | 2 | 0.51776 | 41420.8 | 0 | 0 | 0.62158 | 21755.3 | 0 | 0 | 40000 | 0 | 1420.8 | 20334.5 | 0 | 0 | 20334.5 | 0 | 0 | 0 | 0
2022102501 | 3 | 0.48549 | 38839.2 | 0 | 0 | 0.60343 | 21120.05 | 0 | 0 | 38839.2 | 1160.8 | 0 | 21120.05 | 0 | 0 | 22280.85 | 0 | 0 | 0 | 0
2022102502 | 3 | 0.45243 | 36194.4 | 0 | 0 | 0.56495 | 19773.25 | 0 | 0 | 36194.4 | 3805.6 | 0 | 19773.25 | 0 | 0 | 23578.85 | 0 | 0 | 0 | 0
2022102503 | 3 | 0.43443 | 34754.4 | 0 | 0 | 0.53249 | 18637.15 | 0 | 0 | 34754.4 | 5245.6 | 0 | 18637.15 | 0 | 0 | 23882.75 | 0 | 0 | 0 | 0
2022102504 | 3 | 0.42466 | 33972.8 | 0 | 0 | 0.4974 | 17409 | 0 | 0 | 33972.8 | 6027.2 | 0 | 17409 | 0 | 0 | 23436.2 | 0 | 0 | 0 | 0
2022102505 | 3 | 0.42572 | 34057.6 | 0 | 0 | 0.47429 | 16600.15 | 0 | 0 | 34057.6 | 5942.4 | 0 | 16600.15 | 0 | 0 | 22542.55 | 0 | 0 | 0 | 0
2022102506 | 3 | 0.44561 | 35648.8 | 0 | 0 | 0.46192 | 16167.2 | 0 | 0 | 35648.8 | 4351.2 | 0 | 16167.2 | 0 | 0 | 20518.4 | 0 | 0 | 0 | 0
2022102507 | 3 | 0.47835 | 38268 | 0 | 0 | 0.45476 | 15916.6 | 0 | 0 | 38268 | 1732 | 0 | 15916.6 | 0 | 0 | 17648.6 | 0 | 0 | 0 | 0
2022102508 | 3 | 0.49257 | 39405.6 | 0 | 0 | 0.42247 | 14786.45 | 0.00182 | 25.48 | 39405.6 | 594.4 | 0 | 14786.45 | 0 | 25.48 | 15406.33 | 0 | 0 | 0 | 0
2022102509 | 3 | 0.49112 | 39289.6 | 0 | 0 | 0.38978 | 13642.3 | 0.16748 | 2344.72 | 39289.6 | 710.4 | 0 | 13642.3 | 0 | 2344.72 | 16697.42 | 0 | 0 | 0 | 0
2022102510 | 3 | 0.49556 | 39644.8 | 0 | 0 | 0.30134 | 10546.9 | 0.61245 | 8574.3 | 39644.8 | 355.2 | 0 | 10546.9 | 0 | 8574.3 | 19476.4 | 0 | 0 | 0 | 0
2022102511 | 3 | 0.50037 | 40029.6 | 0 | 0 | 0.26112 | 9139.2 | 0.75028 | 10503.92 | 40000 | 0 | 29.6 | 9109.6 | 0 | 10503.92 | 19613.52 | 0 | 0 | 0 | 0
2022102512 | 3 | 0.50363 | 40290.4 | 0 | 0 | 0.23463 | 8212.05 | 0.76857 | 10759.98 | 40000 | 0 | 290.4 | 7921.65 | 0 | 10759.98 | 18681.63 | 0 | 0 | 0 | 0
2022102513 | 3 | 0.50865 | 40692 | 0 | 0 | 0.1907 | 6674.5 | 0.76223 | 10671.22 | 40000 | 0 | 692 | 5982.5 | 0 | 10671.22 | 16653.72 | 0 | 0 | 0 | 0
2022102514 | 3 | 0.51603 | 41282.4 | 0 | 0 | 0.14379 | 5032.65 | 0.75656 | 10591.84 | 40000 | 0 | 1282.4 | 3750.25 | 0 | 10591.84 | 14342.09 | 0 | 0 | 0 | 0
2022102515 | 3 | 0.52286 | 41828.8 | 0 | 0 | 0.10899 | 3814.65 | 0.76674 | 10734.36 | 40000 | 0 | 1828.8 | 1985.85 | 0 | 10734.36 | 12720.21 | 0 | 0 | 0 | 0
2022102516 | 3 | 0.53608 | 42886.4 | 0 | 0 | 0.07281 | 2548.35 | 0.78107 | 10934.98 | 40000 | 0 | 2548.35 | 0 | 338.05 | 10596.93 | 10596.93 | 0 | 0 | 0 | 0
2022102517 | 3 | 0.54593 | 43674.4 | 0 | 0 | 0.04024 | 1408.4 | 0.77005 | 10780.7 | 40000 | 0 | 1408.4 | 0 | 2266 | 8514.7 | 8514.7 | 0 | 0 | 0 | 0
2022102518 | 3 | 0.54968 | 43974.4 | 0 | 0 | 0.0227 | 794.5 | 0.58777 | 8228.78 | 40000 | 0 | 794.5 | 0 | 3179.9 | 5048.88 | 5048.88 | 0 | 0 | 0 | 0
2022102519 | 3 | 0.54097 | 43277.6 | 0 | 0 | 0.01791 | 626.85 | 0.14023 | 1963.22 | 40000 | 0 | 626.85 | 0 | 1963.22 | 0 | 0 | 687.53 | 0 | 0 | 687.53
2022102520 | 3 | 0.54046 | 43236.8 | 0 | 0 | 0.03044 | 1065.4 | 0.00267 | 37.38 | 40000 | 0 | 1065.4 | 0 | 37.38 | 0 | 0 | 2134.02 | 0 | 0 | 2134.02
2022102521 | 3 | 0.53467 | 42773.6 | 0 | 0 | 0.04844 | 1695.4 | 0.00243 | 34.02 | 40000 | 0 | 1695.4 | 0 | 34.02 | 0 | 0 | 1044.18 | 0 | 0 | 1044.18
2022102522 | 3 | 0.51542 | 41233.6 | 0 | 0 | 0.06876 | 2406.6 | 0.0006 | 8.4 | 40000 | 0 | 1233.6 | 1173 | 0 | 8.4 | 1181.4 | 0 | 0 | 0 | 0
2022102523 | 3 | 0.48318 | 38654.4 | 0 | 0 | 0.09441 | 3304.35 | 0 | 0 | 38654.4 | 1345.6 | 0 | 3304.35 | 0 | 0 | 4649.95 | 0 | 0 | 0 | 0
2022102524 | 3 | 0.45297 | 36237.6 | 0 | 0 | 0.12719 | 4451.65 | 0 | 0 | 36237.6 | 3762.4 | 0 | 4451.65 | 0 | 0 | 8214.05 | 0 | 0 | 0 | 0
2022102601 | 4 | 0.43281 | 34624.8 | 0 | 0 | 0.15301 | 5355.35 | 0 | 0 | 34624.8 | 5375.2 | 0 | 5355.35 | 0 | 0 | 10730.55 | 0 | 0 | 0 | 0
2022102602 | 4 | 0.42067 | 33653.6 | 0 | 0 | 0.18751 | 6562.85 | 0 | 0 | 33653.6 | 6346.4 | 0 | 6562.85 | 0 | 0 | 12909.25 | 0 | 0 | 0 | 0
2022102603 | 4 | 0.4144 | 33152 | 0 | 0 | 0.22373 | 7830.55 | 0 | 0 | 33152 | 6848 | 0 | 7830.55 | 0 | 0 | 14678.55 | 0 | 0 | 0 | 0
2022102604 | 4 | 0.41422 | 33137.6 | 0 | 0 | 0.23541 | 8239.35 | 0 | 0 | 33137.6 | 6862.4 | 0 | 8239.35 | 0 | 0 | 15101.75 | 0 | 0 | 0 | 0
2022102605 | 4 | 0.41954 | 33563.2 | 0 | 0 | 0.22707 | 7947.45 | 0 | 0 | 33563.2 | 6436.8 | 0 | 7947.45 | 0 | 0 | 14384.25 | 0 | 0 | 0 | 0
2022102606 | 4 | 0.44306 | 35444.8 | 0 | 0 | 0.23096 | 8083.6 | 0 | 0 | 35444.8 | 4555.2 | 0 | 8083.6 | 0 | 0 | 12638.8 | 0 | 0 | 0 | 0
2022102607 | 4 | 0.48105 | 38484 | 0 | 0 | 0.24746 | 8661.1 | 0 | 0 | 38484 | 1516 | 0 | 8661.1 | 0 | 0 | 10177.1 | 0 | 0 | 0 | 0
2022102608 | 4 | 0.50272 | 40217.6 | 0 | 0 | 0.26367 | 9228.45 | 0.0027 | 37.8 | 40000 | 0 | 217.6 | 9010.85 | 0 | 37.8 | 9048.65 | 0 | 0 | 0 | 0
2022102609 | 4 | 0.50348 | 40278.4 | 0 | 0 | 0.26805 | 9381.75 | 0.19732 | 2762.48 | 40000 | 0 | 278.4 | 9103.35 | 0 | 2762.48 | 11865.83 | 0 | 0 | 0 | 0
2022102610 | 4 | 0.50335 | 40268 | 0 | 0 | 0.2162 | 7567 | 0.64546 | 9036.44 | 40000 | 0 | 268 | 7299 | 0 | 9036.44 | 16335.44 | 0 | 0 | 0 | 0
2022102611 | 4 | 0.5036 | 40288 | 0 | 0 | 0.18617 | 6515.95 | 0.75794 | 10611.16 | 40000 | 0 | 288 | 6227.95 | 0 | 10611.16 | 16839.11 | 0 | 0 | 0 | 0
2022102612 | 4 | 0.50642 | 40513.6 | 0 | 0 | 0.28325 | 9913.75 | 0.7076 | 9906.4 | 40000 | 0 | 513.6 | 9400.15 | 0 | 9906.4 | 19306.55 | 0 | 0 | 0 | 0
2022102613 | 4 | 0.51046 | 40836.8 | 0 | 0 | 0.3468 | 12138 | 0.61075 | 8550.5 | 40000 | 0 | 836.8 | 11301.2 | 0 | 8550.5 | 19851.7 | 0 | 0 | 0 | 0
2022102614 | 4 | 0.5201 | 41608 | 0 | 0 | 0.3622 | 12677 | 0.64539 | 9035.46 | 40000 | 0 | 1608 | 11069 | 0 | 9035.46 | 20104.46 | 0 | 0 | 0 | 0
2022102615 | 4 | 0.53024 | 42419.2 | 0 | 0 | 0.36672 | 12835.2 | 0.66178 | 9264.92 | 40000 | 0 | 2419.2 | 10416 | 0 | 9264.92 | 19680.92 | 0 | 0 | 0 | 0
2022102616 | 4 | 0.54384 | 43507.2 | 0 | 0 | 0.36937 | 12927.95 | 0.68253 | 9555.42 | 40000 | 0 | 3507.2 | 9420.75 | 0 | 9555.42 | 18976.17 | 0 | 0 | 0 | 0
2022102617 | 4 | 0.55562 | 44449.6 | 0 | 0 | 0.38596 | 13508.6 | 0.64485 | 9027.9 | 40000 | 0 | 4449.6 | 9059 | 0 | 9027.9 | 18086.9 | 0 | 0 | 0 | 0
2022102618 | 4 | 0.5577 | 44616 | 0 | 0 | 0.39372 | 13780.2 | 0.5018 | 7025.2 | 40000 | 0 | 4616 | 9164.2 | 0 | 7025.2 | 16189.4 | 0 | 0 | 0 | 0
2022102619 | 4 | 0.55093 | 44074.4 | 0 | 0 | 0.37677 | 13186.95 | 0.13249 | 1854.86 | 40000 | 0 | 4074.4 | 9112.55 | 0 | 1854.86 | 10967.41 | 0 | 0 | 0 | 0
2022102620 | 4 | 0.55198 | 44158.4 | 0 | 0 | 0.42525 | 14883.75 | 0.01072 | 150.08 | 40000 | 0 | 4158.4 | 10725.35 | 0 | 150.08 | 10875.43 | 0 | 0 | 0 | 0
2022102621 | 4 | 0.54292 | 43433.6 | 0 | 0 | 0.50492 | 17672.2 | 0 | 0 | 40000 | 0 | 3433.6 | 14238.6 | 0 | 0 | 14238.6 | 0 | 0 | 0 | 0
2022102622 | 4 | 0.52469 | 41975.2 | 0 | 0 | 0.52902 | 18515.7 | 0 | 0 | 40000 | 0 | 1975.2 | 16540.5 | 0 | 0 | 16540.5 | 0 | 0 | 0 | 0
2022102623 | 4 | 0.49274 | 39419.2 | 0 | 0 | 0.53196 | 18618.6 | 0 | 0 | 39419.2 | 580.8 | 0 | 18618.6 | 0 | 0 | 19199.4 | 0 | 0 | 0 | 0
2022102624 | 4 | 0.46151 | 36920.8 | 0 | 0 | 0.53243 | 18635.05 | 0 | 0 | 36920.8 | 3079.2 | 0 | 18635.05 | 0 | 0 | 21714.25 | 0 | 0 | 0 | 0
2022102701 | 5 | 0.43944 | 35155.2 | 0 | 0 | 0.53965 | 18887.75 | 0 | 0 | 35155.2 | 4844.8 | 0 | 18887.75 | 0 | 0 | 23732.55 | 0 | 0 | 0 | 0
2022102702 | 5 | 0.42712 | 34169.6 | 0 | 0 | 0.54293 | 19002.55 | 0 | 0 | 34169.6 | 5830.4 | 0 | 19002.55 | 0 | 0 | 24832.95 | 0 | 0 | 0 | 0
2022102703 | 5 | 0.42029 | 33623.2 | 0 | 0 | 0.53918 | 18871.3 | 0 | 0 | 33623.2 | 6376.8 | 0 | 18871.3 | 0 | 0 | 25248.1 | 0 | 0 | 0 | 0
2022102704 | 5 | 0.41683 | 33346.4 | 0 | 0 | 0.53371 | 18679.85 | 0 | 0 | 33346.4 | 6653.6 | 0 | 18679.85 | 0 | 0 | 25333.45 | 0 | 0 | 0 | 0
2022102705 | 5 | 0.4243 | 33944 | 0 | 0 | 0.53009 | 18553.15 | 0 | 0 | 33944 | 6056 | 0 | 18553.15 | 0 | 0 | 24609.15 | 0 | 0 | 0 | 0
2022102706 | 5 | 0.44702 | 35761.6 | 0 | 0 | 0.53042 | 18564.7 | 0 | 0 | 35761.6 | 4238.4 | 0 | 18564.7 | 0 | 0 | 22803.1 | 0 | 0 | 0 | 0
2022102707 | 5 | 0.48394 | 38715.2 | 0 | 0 | 0.52548 | 18391.8 | 0 | 0 | 38715.2 | 1284.8 | 0 | 18391.8 | 0 | 0 | 19676.6 | 0 | 0 | 0 | 0
2022102708 | 5 | 0.50271 | 40216.8 | 0 | 0 | 0.52648 | 18426.8 | 0.00231 | 32.34 | 40000 | 0 | 216.8 | 18210 | 0 | 32.34 | 18242.34 | 0 | 0 | 0 | 0
2022102709 | 5 | 0.50413 | 40330.4 | 0 | 0 | 0.51477 | 18016.95 | 0.1309 | 1832.6 | 40000 | 0 | 330.4 | 17686.55 | 0 | 1832.6 | 19519.15 | 0 | 0 | 0 | 0
2022102710 | 5 | 0.50897 | 40717.6 | 0 | 0 | 0.46686 | 16340.1 | 0.37768 | 5287.52 | 40000 | 0 | 717.6 | 15622.5 | 0 | 5287.52 | 20910.02 | 0 | 0 | 0 | 0
2022102711 | 5 | 0.51235 | 40988 | 0 | 0 | 0.49199 | 17219.65 | 0.42331 | 5926.34 | 40000 | 0 | 988 | 16231.65 | 0 | 5926.34 | 22157.99 | 0 | 0 | 0 | 0
2022102712 | 5 | 0.51715 | 41372 | 0 | 0 | 0.50552 | 17693.2 | 0.40947 | 5732.58 | 40000 | 0 | 1372 | 16321.2 | 0 | 5732.58 | 22053.78 | 0 | 0 | 0 | 0
2022102713 | 5 | 0.52256 | 41804.8 | 0 | 0 | 0.50453 | 17658.55 | 0.41724 | 5841.36 | 40000 | 0 | 1804.8 | 15853.75 | 0 | 5841.36 | 21695.11 | 0 | 0 | 0 | 0
2022102714 | 5 | 0.53296 | 42636.8 | 0 | 0 | 0.50522 | 17682.7 | 0.41515 | 5812.1 | 40000 | 0 | 2636.8 | 15045.9 | 0 | 5812.1 | 20858 | 0 | 0 | 0 | 0
2022102715 | 5 | 0.54479 | 43583.2 | 0 | 0 | 0.49431 | 17300.85 | 0.44675 | 6254.5 | 40000 | 0 | 3583.2 | 13717.65 | 0 | 6254.5 | 19972.15 | 0 | 0 | 0 | 0
2022102716 | 5 | 0.55537 | 44429.6 | 0 | 0 | 0.47084 | 16479.4 | 0.45142 | 6319.88 | 40000 | 0 | 4429.6 | 12049.8 | 0 | 6319.88 | 18369.68 | 0 | 0 | 0 | 0
2022102717 | 5 | 0.5637 | 45096 | 0 | 0 | 0.44683 | 15639.05 | 0.42638 | 5969.32 | 40000 | 0 | 5096 | 10543.05 | 0 | 5969.32 | 16512.37 | 0 | 0 | 0 | 0
2022102718 | 5 | 0.56062 | 44849.6 | 0 | 0 | 0.43387 | 15185.45 | 0.32445 | 4542.3 | 40000 | 0 | 4849.6 | 10335.85 | 0 | 4542.3 | 14878.15 | 0 | 0 | 0 | 0
2022102719 | 5 | 0.55684 | 44547.2 | 0 | 0 | 0.43163 | 15107.05 | 0.08502 | 1190.28 | 40000 | 0 | 4547.2 | 10559.85 | 0 | 1190.28 | 11750.13 | 0 | 0 | 0 | 0
2022102720 | 5 | 0.56231 | 44984.8 | 0 | 0 | 0.4779 | 16726.5 | 0.00033 | 4.62 | 40000 | 0 | 4984.8 | 11741.7 | 0 | 4.62 | 11746.32 | 0 | 0 | 0 | 0
2022102721 | 5 | 0.55949 | 44759.2 | 0 | 0 | 0.54329 | 19015.15 | 0 | 0 | 40000 | 0 | 4759.2 | 14255.95 | 0 | 0 | 14255.95 | 0 | 0 | 0 | 0
2022102722 | 5 | 0.54292 | 43433.6 | 0 | 0 | 0.55569 | 19449.15 | 0 | 0 | 40000 | 0 | 3433.6 | 16015.55 | 0 | 0 | 16015.55 | 0 | 0 | 0 | 0
2022102723 | 5 | 0.51414 | 41131.2 | 0 | 0 | 0.52391 | 18336.85 | 4e-05 | 0.56 | 40000 | 0 | 1131.2 | 17205.65 | 0 | 0.56 | 17206.21 | 0 | 0 | 0 | 0
2022102724 | 5 | 0.4804 | 38432 | 0 | 0 | 0.45862 | 16051.7 | 4e-05 | 0.56 | 38432 | 1568 | 0 | 16051.7 | 0 | 0.56 | 17620.26 | 0 | 0 | 0 | 0
2022102801 | 6 | 0.45495 | 36396 | 0 | 0 | 0.40381 | 14133.35 | 4e-05 | 0.56 | 36396 | 3604 | 0 | 14133.35 | 0 | 0.56 | 17737.91 | 0 | 0 | 0 | 0
2022102802 | 6 | 0.43965 | 35172 | 0 | 0 | 0.39065 | 13672.75 | 0 | 0 | 35172 | 4828 | 0 | 13672.75 | 0 | 0 | 18500.75 | 0 | 0 | 0 | 0
2022102803 | 6 | 0.43127 | 34501.6 | 0 | 0 | 0.38592 | 13507.2 | 4e-05 | 0.56 | 34501.6 | 5498.4 | 0 | 13507.2 | 0 | 0.56 | 19006.16 | 0 | 0 | 0 | 0
2022102804 | 6 | 0.42531 | 34024.8 | 0 | 0 | 0.33737 | 11807.95 | 4e-05 | 0.56 | 34024.8 | 5975.2 | 0 | 11807.95 | 0 | 0.56 | 17783.71 | 0 | 0 | 0 | 0
2022102805 | 6 | 0.43395 | 34716 | 0 | 0 | 0.38567 | 13498.45 | 0 | 0 | 34716 | 5284 | 0 | 13498.45 | 0 | 0 | 18782.45 | 0 | 0 | 0 | 0
2022102806 | 6 | 0.45359 | 36287.2 | 0 | 0 | 0.4233 | 14815.5 | 0 | 0 | 36287.2 | 3712.8 | 0 | 14815.5 | 0 | 0 | 18528.3 | 0 | 0 | 0 | 0
2022102807 | 6 | 0.48742 | 38993.6 | 0 | 0 | 0.44376 | 15531.6 | 4e-05 | 0.56 | 38993.6 | 1006.4 | 0 | 15531.6 | 0 | 0.56 | 16538.56 | 0 | 0 | 0 | 0
2022102808 | 6 | 0.50684 | 40547.2 | 0 | 0 | 0.40065 | 14022.75 | 0.00013 | 1.82 | 40000 | 0 | 547.2 | 13475.55 | 0 | 1.82 | 13477.37 | 0 | 0 | 0 | 0
2022102809 | 6 | 0.5126 | 41008 | 0 | 0 | 0.37241 | 13034.35 | 0.03587 | 502.18 | 40000 | 0 | 1008 | 12026.35 | 0 | 502.18 | 12528.53 | 0 | 0 | 0 | 0
2022102810 | 6 | 0.52803 | 42242.4 | 0 | 0 | 0.37495 | 13123.25 | 0.21761 | 3046.54 | 40000 | 0 | 2242.4 | 10880.85 | 0 | 3046.54 | 13927.39 | 0 | 0 | 0 | 0
2022102811 | 6 | 0.53839 | 43071.2 | 0 | 0 | 0.39145 | 13700.75 | 0.30169 | 4223.66 | 40000 | 0 | 3071.2 | 10629.55 | 0 | 4223.66 | 14853.21 | 0 | 0 | 0 | 0
2022102812 | 6 | 0.53922 | 43137.6 | 0 | 0 | 0.37568 | 13148.8 | 0.2592 | 3628.8 | 40000 | 0 | 3137.6 | 10011.2 | 0 | 3628.8 | 13640 | 0 | 0 | 0 | 0
2022102813 | 6 | 0.5441 | 43528 | 0 | 0 | 0.41368 | 14478.8 | 0.28493 | 3989.02 | 40000 | 0 | 3528 | 10950.8 | 0 | 3989.02 | 14939.82 | 0 | 0 | 0 | 0
2022102814 | 6 | 0.55016 | 44012.8 | 0 | 0 | 0.475 | 16625 | 0.2768 | 3875.2 | 40000 | 0 | 4012.8 | 12612.2 | 0 | 3875.2 | 16487.4 | 0 | 0 | 0 | 0
2022102815 | 6 | 0.54748 | 43798.4 | 0 | 0 | 0.52714 | 18449.9 | 0.31414 | 4397.96 | 40000 | 0 | 3798.4 | 14651.5 | 0 | 4397.96 | 19049.46 | 0 | 0 | 0 | 0
2022102816 | 6 | 0.54659 | 43727.2 | 0 | 0 | 0.56265 | 19692.75 | 0.30264 | 4236.96 | 40000 | 0 | 3727.2 | 15965.55 | 0 | 4236.96 | 20202.51 | 0 | 0 | 0 | 0
2022102817 | 6 | 0.54714 | 43771.2 | 0 | 0 | 0.56169 | 19659.15 | 0.23917 | 3348.38 | 40000 | 0 | 3771.2 | 15887.95 | 0 | 3348.38 | 19236.33 | 0 | 0 | 0 | 0
2022102818 | 6 | 0.545 | 43600 | 0 | 0 | 0.54183 | 18964.05 | 0.18652 | 2611.28 | 40000 | 0 | 3600 | 15364.05 | 0 | 2611.28 | 17975.33 | 0 | 0 | 0 | 0
2022102819 | 6 | 0.54405 | 43524 | 0 | 0 | 0.52741 | 18459.35 | 0.04962 | 694.68 | 40000 | 0 | 3524 | 14935.35 | 0 | 694.68 | 15630.03 | 0 | 0 | 0 | 0
2022102820 | 6 | 0.53999 | 43199.2 | 0 | 0 | 0.46365 | 16227.75 | 9e-05 | 1.26 | 40000 | 0 | 3199.2 | 13028.55 | 0 | 1.26 | 13029.81 | 0 | 0 | 0 | 0
2022102821 | 6 | 0.52485 | 41988 | 0 | 0 | 0.42142 | 14749.7 | 0 | 0 | 40000 | 0 | 1988 | 12761.7 | 0 | 0 | 12761.7 | 0 | 0 | 0 | 0
2022102822 | 6 | 0.50718 | 40574.4 | 0 | 0 | 0.36006 | 12602.1 | 0 | 0 | 40000 | 0 | 574.4 | 12027.7 | 0 | 0 | 12027.7 | 0 | 0 | 0 | 0
2022102823 | 6 | 0.48518 | 38814.4 | 0 | 0 | 0.31503 | 11026.05 | 0 | 0 | 38814.4 | 1185.6 | 0 | 11026.05 | 0 | 0 | 12211.65 | 0 | 0 | 0 | 0
2022102824 | 6 | 0.46224 | 36979.2 | 0 | 0 | 0.29231 | 10230.85 | 0 | 0 | 36979.2 | 3020.8 | 0 | 10230.85 | 0 | 0 | 13251.65 | 0 | 0 | 0 | 0
2022102901 | 7 | 0.43962 | 35169.6 | 0 | 0 | 0.27216 | 9525.6 | 0 | 0 | 35169.6 | 4830.4 | 0 | 9525.6 | 0 | 0 | 14356 | 0 | 0 | 0 | 0
2022102902 | 7 | 0.42647 | 34117.6 | 0 | 0 | 0.27175 | 9511.25 | 0 | 0 | 34117.6 | 5882.4 | 0 | 9511.25 | 0 | 0 | 15393.65 | 0 | 0 | 0 | 0
2022102903 | 7 | 0.41745 | 33396 | 0 | 0 | 0.27048 | 9466.8 | 0 | 0 | 33396 | 6604 | 0 | 9466.8 | 0 | 0 | 16070.8 | 0 | 0 | 0 | 0
2022102904 | 7 | 0.41205 | 32964 | 0 | 0 | 0.26718 | 9351.3 | 0 | 0 | 32964 | 7036 | 0 | 9351.3 | 0 | 0 | 16387.3 | 0 | 0 | 0 | 0
2022102905 | 7 | 0.41063 | 32850.4 | 0 | 0 | 0.25284 | 8849.4 | 0 | 0 | 32850.4 | 7149.6 | 0 | 8849.4 | 0 | 0 | 15999 | 0 | 0 | 0 | 0
2022102906 | 7 | 0.41736 | 33388.8 | 0 | 0 | 0.24698 | 8644.3 | 0 | 0 | 33388.8 | 6611.2 | 0 | 8644.3 | 0 | 0 | 15255.5 | 0 | 0 | 0 | 0
2022102907 | 7 | 0.42814 | 34251.2 | 0 | 0 | 0.24974 | 8740.9 | 0 | 0 | 34251.2 | 5748.8 | 0 | 8740.9 | 0 | 0 | 14489.7 | 0 | 0 | 0 | 0
2022102908 | 7 | 0.44679 | 35743.2 | 0 | 0 | 0.25611 | 8963.85 | 0.00122 | 17.08 | 35743.2 | 4256.8 | 0 | 8963.85 | 0 | 17.08 | 13237.73 | 0 | 0 | 0 | 0
2022102909 | 7 | 0.46286 | 37028.8 | 0 | 0 | 0.25851 | 9047.85 | 0.10961 | 1534.54 | 37028.8 | 2971.2 | 0 | 9047.85 | 0 | 1534.54 | 13553.59 | 0 | 0 | 0 | 0
2022102910 | 7 | 0.47709 | 38167.2 | 0 | 0 | 0.19517 | 6830.95 | 0.38138 | 5339.32 | 38167.2 | 1832.8 | 0 | 6830.95 | 0 | 5339.32 | 14003.07 | 0 | 0 | 0 | 0
2022102911 | 7 | 0.48683 | 38946.4 | 0 | 0 | 0.2105 | 7367.5 | 0.53041 | 7425.74 | 38946.4 | 1053.6 | 0 | 7367.5 | 0 | 7425.74 | 15846.84 | 0 | 0 | 0 | 0
2022102912 | 7 | 0.48865 | 39092 | 0 | 0 | 0.21414 | 7494.9 | 0.57471 | 8045.94 | 39092 | 908 | 0 | 7494.9 | 0 | 8045.94 | 16448.84 | 0 | 0 | 0 | 0
2022102913 | 7 | 0.49044 | 39235.2 | 0 | 0 | 0.22821 | 7987.35 | 0.61328 | 8585.92 | 39235.2 | 764.8 | 0 | 7987.35 | 0 | 8585.92 | 17338.07 | 0 | 0 | 0 | 0
2022102914 | 7 | 0.4905 | 39240 | 0 | 0 | 0.22214 | 7774.9 | 0.60736 | 8503.04 | 39240 | 760 | 0 | 7774.9 | 0 | 8503.04 | 17037.94 | 0 | 0 | 0 | 0
2022102915 | 7 | 0.49018 | 39214.4 | 0 | 0 | 0.20858 | 7300.3 | 0.58881 | 8243.34 | 39214.4 | 785.6 | 0 | 7300.3 | 0 | 8243.34 | 16329.24 | 0 | 0 | 0 | 0
2022102916 | 7 | 0.49071 | 39256.8 | 0 | 0 | 0.18572 | 6500.2 | 0.58835 | 8236.9 | 39256.8 | 743.2 | 0 | 6500.2 | 0 | 8236.9 | 15480.3 | 0 | 0 | 0 | 0
2022102917 | 7 | 0.49372 | 39497.6 | 0 | 0 | 0.14969 | 5239.15 | 0.57337 | 8027.18 | 39497.6 | 502.4 | 0 | 5239.15 | 0 | 8027.18 | 13768.73 | 0 | 0 | 0 | 0
2022102918 | 7 | 0.49441 | 39552.8 | 0 | 0 | 0.10242 | 3584.7 | 0.43649 | 6110.86 | 39552.8 | 447.2 | 0 | 3584.7 | 0 | 6110.86 | 10142.76 | 0 | 0 | 0 | 0
2022102919 | 7 | 0.49675 | 39740 | 0 | 0 | 0.05239 | 1833.65 | 0.09735 | 1362.9 | 39740 | 260 | 0 | 1833.65 | 0 | 1362.9 | 3456.55 | 0 | 0 | 0 | 0
2022102920 | 7 | 0.49738 | 39790.4 | 0 | 0 | 0.03476 | 1216.6 | 0.0001 | 1.4 | 39790.4 | 209.6 | 0 | 1216.6 | 0 | 1.4 | 1427.6 | 0 | 0 | 0 | 0
2022102921 | 7 | 0.4915 | 39320 | 0 | 0 | 0.03096 | 1083.6 | 0 | 0 | 39320 | 680 | 0 | 1083.6 | 0 | 0 | 1763.6 | 0 | 0 | 0 | 0
2022102922 | 7 | 0.47934 | 38347.2 | 0 | 0 | 0.03437 | 1202.95 | 0 | 0 | 38347.2 | 1652.8 | 0 | 1202.95 | 0 | 0 | 2855.75 | 0 | 0 | 0 | 0
2022102923 | 7 | 0.46389 | 37111.2 | 0 | 0 | 0.04374 | 1530.9 | 0 | 0 | 37111.2 | 2888.8 | 0 | 1530.9 | 0 | 0 | 4419.7 | 0 | 0 | 0 | 0
2022102924 | 7 | 0.44619 | 35695.2 | 0 | 0 | 0.0464 | 1624 | 0 | 0 | 35695.2 | 4304.8 | 0 | 1624 | 0 | 0 | 5928.8 | 0 | 0 | 0 | 0
2022103001 | 1 | 0.43032 | 34425.6 | 0 | 0 | 0.0469 | 1641.5 | 0 | 0 | 34425.6 | 5574.4 | 0 | 1641.5 | 0 | 0 | 7215.9 | 0 | 0 | 0 | 0
2022103002 | 1 | 0.41862 | 33489.6 | 0 | 0 | 0.04832 | 1691.2 | 0 | 0 | 33489.6 | 6510.4 | 0 | 1691.2 | 0 | 0 | 8201.6 | 0 | 0 | 0 | 0
2022103003 | 1 | 0.41046 | 32836.8 | 0 | 0 | 0.05373 | 1880.55 | 0 | 0 | 32836.8 | 7163.2 | 0 | 1880.55 | 0 | 0 | 9043.75 | 0 | 0 | 0 | 0
2022103004 | 1 | 0.40753 | 32602.4 | 0 | 0 | 0.05734 | 2006.9 | 0 | 0 | 32602.4 | 7397.6 | 0 | 2006.9 | 0 | 0 | 9404.5 | 0 | 0 | 0 | 0
2022103005 | 1 | 0.40733 | 32586.4 | 0 | 0 | 0.07097 | 2483.95 | 0 | 0 | 32586.4 | 7413.6 | 0 | 2483.95 | 0 | 0 | 9897.55 | 0 | 0 | 0 | 0
2022103006 | 1 | 0.40848 | 32678.4 | 0 | 0 | 0.08147 | 2851.45 | 0 | 0 | 32678.4 | 7321.6 | 0 | 2851.45 | 0 | 0 | 10173.05 | 0 | 0 | 0 | 0
2022103007 | 1 | 0.41571 | 33256.8 | 0 | 0 | 0.09277 | 3246.95 | 0 | 0 | 33256.8 | 6743.2 | 0 | 3246.95 | 0 | 0 | 9990.15 | 0 | 0 | 0 | 0
2022103008 | 1 | 0.42729 | 34183.2 | 0 | 0 | 0.09181 | 3213.35 | 0.00118 | 16.52 | 34183.2 | 5816.8 | 0 | 3213.35 | 0 | 16.52 | 9046.67 | 0 | 0 | 0 | 0
2022103009 | 1 | 0.44212 | 35369.6 | 0 | 0 | 0.08114 | 2839.9 | 0.1467 | 2053.8 | 35369.6 | 4630.4 | 0 | 2839.9 | 0 | 2053.8 | 9524.1 | 0 | 0 | 0 | 0
2022103010 | 1 | 0.46033 | 36826.4 | 0 | 0 | 0.05232 | 1831.2 | 0.57656 | 8071.84 | 36826.4 | 3173.6 | 0 | 1831.2 | 0 | 8071.84 | 13076.64 | 0 | 0 | 0 | 0
2022103011 | 1 | 0.467 | 37360 | 0 | 0 | 0.02232 | 781.2 | 0.69785 | 9769.9 | 37360 | 2640 | 0 | 781.2 | 0 | 9769.9 | 13191.1 | 0 | 0 | 0 | 0
2022103012 | 1 | 0.47319 | 37855.2 | 0 | 0 | 0.01736 | 607.6 | 0.68676 | 9614.64 | 37855.2 | 2144.8 | 0 | 607.6 | 0 | 9614.64 | 12367.04 | 0 | 0 | 0 | 0
2022103013 | 1 | 0.48422 | 38737.6 | 0 | 0 | 0.0158 | 553 | 0.67737 | 9483.18 | 38737.6 | 1262.4 | 0 | 553 | 0 | 9483.18 | 11298.58 | 0 | 0 | 0 | 0
2022103014 | 1 | 0.49582 | 39665.6 | 0 | 0 | 0.01444 | 505.4 | 0.66532 | 9314.48 | 39665.6 | 334.4 | 0 | 505.4 | 0 | 9314.48 | 10154.28 | 0 | 0 | 0 | 0
2022103015 | 1 | 0.50645 | 40516 | 0 | 0 | 0.01424 | 498.4 | 0.66438 | 9301.32 | 40000 | 0 | 498.4 | 0 | 17.6 | 9283.72 | 9283.72 | 0 | 0 | 0 | 0
2022103016 | 1 | 0.51839 | 41471.2 | 0 | 0 | 0.01732 | 606.2 | 0.6509 | 9112.6 | 40000 | 0 | 606.2 | 0 | 865 | 8247.6 | 8247.6 | 0 | 0 | 0 | 0
2022103017 | 1 | 0.52843 | 42274.4 | 0 | 0 | 0.02284 | 799.4 | 0.58657 | 8211.98 | 40000 | 0 | 799.4 | 0 | 1475 | 6736.98 | 6736.98 | 0 | 0 | 0 | 0
2022103018 | 1 | 0.53229 | 42583.2 | 0 | 0 | 0.03116 | 1090.6 | 0.43439 | 6081.46 | 40000 | 0 | 1090.6 | 0 | 1492.6 | 4588.86 | 4588.86 | 0 | 0 | 0 | 0
2022103019 | 1 | 0.53461 | 42768.8 | 0 | 0 | 0.03688 | 1290.8 | 0.06907 | 966.98 | 40000 | 0 | 1290.8 | 0 | 966.98 | 0 | 0 | 511.02 | 0 | 0 | 511.02
2022103020 | 1 | 0.54243 | 43394.4 | 0 | 0 | 0.05265 | 1842.75 | 0 | 0 | 40000 | 0 | 1842.75 | 0 | 0 | 0 | 0 | 1551.65 | 0 | 0 | 1551.65
2022103021 | 1 | 0.53157 | 42525.6 | 0 | 0 | 0.06824 | 2388.4 | 0 | 0 | 40000 | 0 | 2388.4 | 0 | 0 | 0 | 0 | 137.2 | 0 | 0 | 137.2
2022103022 | 1 | 0.51159 | 40927.2 | 0 | 0 | 0.09787 | 3425.45 | 0 | 0 | 40000 | 0 | 927.2 | 2498.25 | 0 | 0 | 2498.25 | 0 | 0 | 0 | 0
2022103023 | 1 | 0.48414 | 38731.2 | 0 | 0 | 0.10599 | 3709.65 | 0 | 0 | 38731.2 | 1268.8 | 0 | 3709.65 | 0 | 0 | 4978.45 | 0 | 0 | 0 | 0
2022103024 | 1 | 0.45311 | 36248.8 | 0 | 0 | 0.11362 | 3976.7 | 0 | 0 | 36248.8 | 3751.2 | 0 | 3976.7 | 0 | 0 | 7727.9 | 0 | 0 | 0 | 0
2022103101 | 2 | 0.42946 | 34356.8 | 0 | 0 | 0.11998 | 4199.3 | 0 | 0 | 34356.8 | 5643.2 | 0 | 4199.3 | 0 | 0 | 9842.5 | 0 | 0 | 0 | 0
2022103102 | 2 | 0.41519 | 33215.2 | 0 | 0 | 0.11885 | 4159.75 | 0 | 0 | 33215.2 | 6784.8 | 0 | 4159.75 | 0 | 0 | 10944.55 | 0 | 0 | 0 | 0
2022103103 | 2 | 0.40924 | 32739.2 | 0 | 0 | 0.12386 | 4335.1 | 0 | 0 | 32739.2 | 7260.8 | 0 | 4335.1 | 0 | 0 | 11595.9 | 0 | 0 | 0 | 0
2022103104 | 2 | 0.40707 | 32565.6 | 0 | 0 | 0.12086 | 4230.1 | 0 | 0 | 32565.6 | 7434.4 | 0 | 4230.1 | 0 | 0 | 11664.5 | 0 | 0 | 0 | 0
2022103105 | 2 | 0.41534 | 33227.2 | 0 | 0 | 0.11193 | 3917.55 | 0 | 0 | 33227.2 | 6772.8 | 0 | 3917.55 | 0 | 0 | 10690.35 | 0 | 0 | 0 | 0
2022103106 | 2 | 0.4355 | 34840 | 0 | 0 | 0.09598 | 3359.3 | 0 | 0 | 34840 | 5160 | 0 | 3359.3 | 0 | 0 | 8519.3 | 0 | 0 | 0 | 0
2022103107 | 2 | 0.47329 | 37863.2 | 0 | 0 | 0.08769 | 3069.15 | 0 | 0 | 37863.2 | 2136.8 | 0 | 3069.15 | 0 | 0 | 5205.95 | 0 | 0 | 0 | 0
2022103108 | 2 | 0.49667 | 39733.6 | 0 | 0 | 0.08875 | 3106.25 | 0.00108 | 15.12 | 39733.6 | 266.4 | 0 | 3106.25 | 0 | 15.12 | 3387.77 | 0 | 0 | 0 | 0
2022103109 | 2 | 0.49981 | 39984.8 | 0 | 0 | 0.09033 | 3161.55 | 0.09913 | 1387.82 | 39984.8 | 15.2 | 0 | 3161.55 | 0 | 1387.82 | 4564.57 | 0 | 0 | 0 | 0
2022103110 | 2 | 0.50546 | 40436.8 | 0 | 0 | 0.08189 | 2866.15 | 0.36678 | 5134.92 | 40000 | 0 | 436.8 | 2429.35 | 0 | 5134.92 | 7564.27 | 0 | 0 | 0 | 0
2022103111 | 2 | 0.51107 | 40885.6 | 0 | 0 | 0.07485 | 2619.75 | 0.51077 | 7150.78 | 40000 | 0 | 885.6 | 1734.15 | 0 | 7150.78 | 8884.93 | 0 | 0 | 0 | 0
2022103112 | 2 | 0.51814 | 41451.2 | 0 | 0 | 0.09461 | 3311.35 | 0.54946 | 7692.44 | 40000 | 0 | 1451.2 | 1860.15 | 0 | 7692.44 | 9552.59 | 0 | 0 | 0 | 0
2022103113 | 2 | 0.52743 | 42194.4 | 0 | 0 | 0.11197 | 3918.95 | 0.5782 | 8094.8 | 40000 | 0 | 2194.4 | 1724.55 | 0 | 8094.8 | 9819.35 | 0 | 0 | 0 | 0
2022103114 | 2 | 0.54091 | 43272.8 | 0 | 0 | 0.1282 | 4487 | 0.56033 | 7844.62 | 40000 | 0 | 3272.8 | 1214.2 | 0 | 7844.62 | 9058.82 | 0 | 0 | 0 | 0
2022103115 | 2 | 0.55045 | 44036 | 0 | 0 | 0.13571 | 4749.85 | 0.5622 | 7870.8 | 40000 | 0 | 4036 | 713.85 | 0 | 7870.8 | 8584.65 | 0 | 0 | 0 | 0
2022103116 | 2 | 0.56025 | 44820 | 0 | 0 | 0.13647 | 4776.45 | 0.53396 | 7475.44 | 40000 | 0 | 4776.45 | 0 | 43.55 | 7431.89 | 7431.89 | 0 | 0 | 0 | 0
2022103117 | 2 | 0.56945 | 45556 | 0 | 0 | 0.13737 | 4807.95 | 0.44522 | 6233.08 | 40000 | 0 | 4807.95 | 0 | 748.05 | 5485.03 | 5485.03 | 0 | 0 | 0 | 0
2022103118 | 2 | 0.56735 | 45388 | 0 | 0 | 0.13972 | 4890.2 | 0.27809 | 3893.26 | 40000 | 0 | 4890.2 | 0 | 497.8 | 3395.46 | 3395.46 | 0 | 0 | 0 | 0
2022103119 | 2 | 0.55025 | 44020 | 0 | 0 | 0.16441 | 5754.35 | 0.04597 | 643.58 | 40000 | 0 | 4020 | 1734.35 | 0 | 643.58 | 2377.93 | 0 | 0 | 0 | 0
2022103120 | 2 | 0.5431 | 43448 | 0 | 0 | 0.2017 | 7059.5 | 5e-05 | 0.7 | 40000 | 0 | 3448 | 3611.5 | 0 | 0.7 | 3612.2 | 0 | 0 | 0 | 0
2022103121 | 2 | 0.53477 | 42781.6 | 0 | 0 | 0.234 | 8190 | 0 | 0 | 40000 | 0 | 2781.6 | 5408.4 | 0 | 0 | 5408.4 | 0 | 0 | 0 | 0
2022103122 | 2 | 0.5247 | 41976 | 0 | 0 | 0.26345 | 9220.75 | 0 | 0 | 40000 | 0 | 1976 | 7244.75 | 0 | 0 | 7244.75 | 0 | 0 | 0 | 0
2022103123 | 2 | 0.49781 | 39824.8 | 0 | 0 | 0.312 | 10920 | 0 | 0 | 39824.8 | 175.2 | 0 | 10920 | 0 | 0 | 11095.2 | 0 | 0 | 0 | 0
2022103124 | 2 | 0.46402 | 37121.6 | 0 | 0 | 0.34009 | 11903.15 | 0 | 0 | 37121.6 | 2878.4 | 0 | 11903.15 | 0 | 0 | 14781.55 | 0 | 0 | 0 | 0
2022110101 | 3 | 0.44353 | 35482.4 | 0 | 0 | 0.372 | 13020 | 0 | 0 | 35482.4 | 4517.6 | 0 | 13020 | 0 | 0 | 17537.6 | 0 | 0 | 0 | 0
2022110102 | 3 | 0.4312 | 34496 | 0 | 0 | 0.3793 | 13275.5 | 0 | 0 | 34496 | 5504 | 0 | 13275.5 | 0 | 0 | 18779.5 | 0 | 0 | 0 | 0
2022110103 | 3 | 0.42371 | 33896.8 | 0 | 0 | 0.36629 | 12820.15 | 0 | 0 | 33896.8 | 6103.2 | 0 | 12820.15 | 0 | 0 | 18923.35 | 0 | 0 | 0 | 0
2022110104 | 3 | 0.42013 | 33610.4 | 0 | 0 | 0.32356 | 11324.6 | 0 | 0 | 33610.4 | 6389.6 | 0 | 11324.6 | 0 | 0 | 17714.2 | 0 | 0 | 0 | 0
2022110105 | 3 | 0.42273 | 33818.4 | 0 | 0 | 0.29923 | 10473.05 | 0 | 0 | 33818.4 | 6181.6 | 0 | 10473.05 | 0 | 0 | 16654.65 | 0 | 0 | 0 | 0
2022110106 | 3 | 0.44082 | 35265.6 | 0 | 0 | 0.30002 | 10500.7 | 0 | 0 | 35265.6 | 4734.4 | 0 | 10500.7 | 0 | 0 | 15235.1 | 0 | 0 | 0 | 0
2022110107 | 3 | 0.47503 | 38002.4 | 0 | 0 | 0.29779 | 10422.65 | 0 | 0 | 38002.4 | 1997.6 | 0 | 10422.65 | 0 | 0 | 12420.25 | 0 | 0 | 0 | 0
2022110108 | 3 | 0.49573 | 39658.4 | 0 | 0 | 0.27389 | 9586.15 | 0.00011 | 1.54 | 39658.4 | 341.6 | 0 | 9586.15 | 0 | 1.54 | 9929.29 | 0 | 0 | 0 | 0
2022110109 | 3 | 0.49798 | 39838.4 | 0 | 0 | 0.24824 | 8688.4 | 0.06905 | 966.7 | 39838.4 | 161.6 | 0 | 8688.4 | 0 | 966.7 | 9816.7 | 0 | 0 | 0 | 0
2022110110 | 3 | 0.50498 | 40398.4 | 0 | 0 | 0.19557 | 6844.95 | 0.34832 | 4876.48 | 40000 | 0 | 398.4 | 6446.55 | 0 | 4876.48 | 11323.03 | 0 | 0 | 0 | 0
2022110111 | 3 | 0.51416 | 41132.8 | 0 | 0 | 0.15445 | 5405.75 | 0.50164 | 7022.96 | 40000 | 0 | 1132.8 | 4272.95 | 0 | 7022.96 | 11295.91 | 0 | 0 | 0 | 0
2022110112 | 3 | 0.52171 | 41736.8 | 0 | 0 | 0.15896 | 5563.6 | 0.54887 | 7684.18 | 40000 | 0 | 1736.8 | 3826.8 | 0 | 7684.18 | 11510.98 | 0 | 0 | 0 | 0
2022110113 | 3 | 0.52727 | 42181.6 | 0 | 0 | 0.17414 | 6094.9 | 0.55018 | 7702.52 | 40000 | 0 | 2181.6 | 3913.3 | 0 | 7702.52 | 11615.82 | 0 | 0 | 0 | 0
2022110114 | 3 | 0.53408 | 42726.4 | 0 | 0 | 0.18735 | 6557.25 | 0.55315 | 7744.1 | 40000 | 0 | 2726.4 | 3830.85 | 0 | 7744.1 | 11574.95 | 0 | 0 | 0 | 0
2022110115 | 3 | 0.53821 | 43056.8 | 0 | 0 | 0.22189 | 7766.15 | 0.55177 | 7724.78 | 40000 | 0 | 3056.8 | 4709.35 | 0 | 7724.78 | 12434.13 | 0 | 0 | 0 | 0
2022110116 | 3 | 0.5422 | 43376 | 0 | 0 | 0.262 | 9170 | 0.54334 | 7606.76 | 40000 | 0 | 3376 | 5794 | 0 | 7606.76 | 13400.76 | 0 | 0 | 0 | 0
2022110117 | 3 | 0.54878 | 43902.4 | 0 | 0 | 0.29389 | 10286.15 | 0.53307 | 7462.98 | 40000 | 0 | 3902.4 | 6383.75 | 0 | 7462.98 | 13846.73 | 0 | 0 | 0 | 0
2022110118 | 3 | 0.54864 | 43891.2 | 0 | 0 | 0.304 | 10640 | 0.41133 | 5758.62 | 40000 | 0 | 3891.2 | 6748.8 | 0 | 5758.62 | 12507.42 | 0 | 0 | 0 | 0
2022110119 | 3 | 0.54988 | 43990.4 | 0 | 0 | 0.30905 | 10816.75 | 0.0821 | 1149.4 | 40000 | 0 | 3990.4 | 6826.35 | 0 | 1149.4 | 7975.75 | 0 | 0 | 0 | 0
2022110120 | 3 | 0.55557 | 44445.6 | 0 | 0 | 0.36932 | 12926.2 | 0.00299 | 41.86 | 40000 | 0 | 4445.6 | 8480.6 | 0 | 41.86 | 8522.46 | 0 | 0 | 0 | 0
2022110121 | 3 | 0.54648 | 43718.4 | 0 | 0 | 0.44294 | 15502.9 | 0 | 0 | 40000 | 0 | 3718.4 | 11784.5 | 0 | 0 | 11784.5 | 0 | 0 | 0 | 0
2022110122 | 3 | 0.52809 | 42247.2 | 0 | 0 | 0.48376 | 16931.6 | 0 | 0 | 40000 | 0 | 2247.2 | 14684.4 | 0 | 0 | 14684.4 | 0 | 0 | 0 | 0
2022110123 | 3 | 0.50273 | 40218.4 | 0 | 0 | 0.50325 | 17613.75 | 0 | 0 | 40000 | 0 | 218.4 | 17395.35 | 0 | 0 | 17395.35 | 0 | 0 | 0 | 0
2022110124 | 3 | 0.47137 | 37709.6 | 0 | 0 | 0.49285 | 17249.75 | 0 | 0 | 37709.6 | 2290.4 | 0 | 17249.75 | 0 | 0 | 19540.15 | 0 | 0 | 0 | 0
2022110201 | 4 | 0.44815 | 35852 | 0 | 0 | 0.48103 | 16836.05 | 0 | 0 | 35852 | 4148 | 0 | 16836.05 | 0 | 0 | 20984.05 | 0 | 0 | 0 | 0
2022110202 | 4 | 0.43435 | 34748 | 0 | 0 | 0.47304 | 16556.4 | 0 | 0 | 34748 | 5252 | 0 | 16556.4 | 0 | 0 | 21808.4 | 0 | 0 | 0 | 0
2022110203 | 4 | 0.42738 | 34190.4 | 0 | 0 | 0.46301 | 16205.35 | 0 | 0 | 34190.4 | 5809.6 | 0 | 16205.35 | 0 | 0 | 22014.95 | 0 | 0 | 0 | 0
2022110204 | 4 | 0.42343 | 33874.4 | 0 | 0 | 0.45696 | 15993.6 | 0 | 0 | 33874.4 | 6125.6 | 0 | 15993.6 | 0 | 0 | 22119.2 | 0 | 0 | 0 | 0
2022110205 | 4 | 0.42874 | 34299.2 | 0 | 0 | 0.45687 | 15990.45 | 0 | 0 | 34299.2 | 5700.8 | 0 | 15990.45 | 0 | 0 | 21691.25 | 0 | 0 | 0 | 0
2022110206 | 4 | 0.44928 | 35942.4 | 0 | 0 | 0.45745 | 16010.75 | 0 | 0 | 35942.4 | 4057.6 | 0 | 16010.75 | 0 | 0 | 20068.35 | 0 | 0 | 0 | 0
2022110207 | 4 | 0.48278 | 38622.4 | 0 | 0 | 0.45055 | 15769.25 | 0 | 0 | 38622.4 | 1377.6 | 0 | 15769.25 | 0 | 0 | 17146.85 | 0 | 0 | 0 | 0
2022110208 | 4 | 0.50488 | 40390.4 | 0 | 0 | 0.42967 | 15038.45 | 0.0002 | 2.8 | 40000 | 0 | 390.4 | 14648.05 | 0 | 2.8 | 14650.85 | 0 | 0 | 0 | 0
2022110209 | 4 | 0.50621 | 40496.8 | 0 | 0 | 0.39672 | 13885.2 | 0.03334 | 466.76 | 40000 | 0 | 496.8 | 13388.4 | 0 | 466.76 | 13855.16 | 0 | 0 | 0 | 0
2022110210 | 4 | 0.51304 | 41043.2 | 0 | 0 | 0.36387 | 12735.45 | 0.16489 | 2308.46 | 40000 | 0 | 1043.2 | 11692.25 | 0 | 2308.46 | 14000.71 | 0 | 0 | 0 | 0
2022110211 | 4 | 0.51921 | 41536.8 | 0 | 0 | 0.38483 | 13469.05 | 0.30483 | 4267.62 | 40000 | 0 | 1536.8 | 11932.25 | 0 | 4267.62 | 16199.87 | 0 | 0 | 0 | 0
2022110212 | 4 | 0.529 | 42320 | 0 | 0 | 0.38683 | 13539.05 | 0.41164 | 5762.96 | 40000 | 0 | 2320 | 11219.05 | 0 | 5762.96 | 16982.01 | 0 | 0 | 0 | 0
2022110213 | 4 | 0.53933 | 43146.4 | 0 | 0 | 0.37 | 12950 | 0.46593 | 6523.02 | 40000 | 0 | 3146.4 | 9803.6 | 0 | 6523.02 | 16326.62 | 0 | 0 | 0 | 0
2022110214 | 4 | 0.55434 | 44347.2 | 0 | 0 | 0.37584 | 13154.4 | 0.46103 | 6454.42 | 40000 | 0 | 4347.2 | 8807.2 | 0 | 6454.42 | 15261.62 | 0 | 0 | 0 | 0
2022110215 | 4 | 0.56569 | 45255.2 | 0 | 0 | 0.39728 | 13904.8 | 0.40182 | 5625.48 | 40000 | 0 | 5255.2 | 8649.6 | 0 | 5625.48 | 14275.08 | 0 | 0 | 0 | 0
2022110216 | 4 | 0.57437 | 45949.6 | 0 | 0 | 0.41275 | 14446.25 | 0.32008 | 4481.12 | 40000 | 0 | 5949.6 | 8496.65 | 0 | 4481.12 | 12977.77 | 0 | 0 | 0 | 0
2022110217 | 4 | 0.58345 | 46676 | 0 | 0 | 0.41486 | 14520.1 | 0.25722 | 3601.08 | 40000 | 0 | 6676 | 7844.1 | 0 | 3601.08 | 11445.18 | 0 | 0 | 0 | 0
2022110218 | 4 | 0.5854 | 46832 | 0 | 0 | 0.4289 | 15011.5 | 0.14664 | 2052.96 | 40000 | 0 | 6832 | 8179.5 | 0 | 2052.96 | 10232.46 | 0 | 0 | 0 | 0
2022110219 | 4 | 0.58344 | 46675.2 | 0 | 0 | 0.4205 | 14717.5 | 0.03871 | 541.94 | 40000 | 0 | 6675.2 | 8042.3 | 0 | 541.94 | 8584.24 | 0 | 0 | 0 | 0
2022110220 | 4 | 0.58916 | 47132.8 | 0 | 0 | 0.44623 | 15618.05 | 0 | 0 | 40000 | 0 | 7132.8 | 8485.25 | 0 | 0 | 8485.25 | 0 | 0 | 0 | 0
2022110221 | 4 | 0.57827 | 46261.6 | 0 | 0 | 0.47899 | 16764.65 | 0 | 0 | 40000 | 0 | 6261.6 | 10503.05 | 0 | 0 | 10503.05 | 0 | 0 | 0 | 0
2022110222 | 4 | 0.56082 | 44865.6 | 0 | 0 | 0.48305 | 16906.75 | 0 | 0 | 40000 | 0 | 4865.6 | 12041.15 | 0 | 0 | 12041.15 | 0 | 0 | 0 | 0
2022110223 | 4 | 0.53378 | 42702.4 | 0 | 0 | 0.50114 | 17539.9 | 0 | 0 | 40000 | 0 | 2702.4 | 14837.5 | 0 | 0 | 14837.5 | 0 | 0 | 0 | 0
2022110224 | 4 | 0.50244 | 40195.2 | 0 | 0 | 0.50353 | 17623.55 | 0 | 0 | 40000 | 0 | 195.2 | 17428.35 | 0 | 0 | 17428.35 | 0 | 0 | 0 | 0
2022110301 | 5 | 0.47711 | 38168.8 | 0 | 0 | 0.50244 | 17585.4 | 0 | 0 | 38168.8 | 1831.2 | 0 | 17585.4 | 0 | 0 | 19416.6 | 0 | 0 | 0 | 0
2022110302 | 5 | 0.45986 | 36788.8 | 0 | 0 | 0.4993 | 17475.5 | 0 | 0 | 36788.8 | 3211.2 | 0 | 17475.5 | 0 | 0 | 20686.7 | 0 | 0 | 0 | 0
2022110303 | 5 | 0.45115 | 36092 | 0 | 0 | 0.49354 | 17273.9 | 0 | 0 | 36092 | 3908 | 0 | 17273.9 | 0 | 0 | 21181.9 | 0 | 0 | 0 | 0
2022110304 | 5 | 0.44846 | 35876.8 | 0 | 0 | 0.49093 | 17182.55 | 0 | 0 | 35876.8 | 4123.2 | 0 | 17182.55 | 0 | 0 | 21305.75 | 0 | 0 | 0 | 0
2022110305 | 5 | 0.45399 | 36319.2 | 0 | 0 | 0.49178 | 17212.3 | 0 | 0 | 36319.2 | 3680.8 | 0 | 17212.3 | 0 | 0 | 20893.1 | 0 | 0 | 0 | 0
2022110306 | 5 | 0.47588 | 38070.4 | 0 | 0 | 0.50431 | 17650.85 | 0 | 0 | 38070.4 | 1929.6 | 0 | 17650.85 | 0 | 0 | 19580.45 | 0 | 0 | 0 | 0
2022110307 | 5 | 0.51274 | 41019.2 | 0 | 0 | 0.51532 | 18036.2 | 0 | 0 | 40000 | 0 | 1019.2 | 17017 | 0 | 0 | 17017 | 0 | 0 | 0 | 0
2022110308 | 5 | 0.53421 | 42736.8 | 0 | 0 | 0.52439 | 18353.65 | 0.00029 | 4.06 | 40000 | 0 | 2736.8 | 15616.85 | 0 | 4.06 | 15620.91 | 0 | 0 | 0 | 0
2022110309 | 5 | 0.5402 | 43216 | 0 | 0 | 0.52885 | 18509.75 | 0.02547 | 356.58 | 40000 | 0 | 3216 | 15293.75 | 0 | 356.58 | 15650.33 | 0 | 0 | 0 | 0
2022110310 | 5 | 0.5512 | 44096 | 0 | 0 | 0.51527 | 18034.45 | 0.11267 | 1577.38 | 40000 | 0 | 4096 | 13938.45 | 0 | 1577.38 | 15515.83 | 0 | 0 | 0 | 0
2022110311 | 5 | 0.56808 | 45446.4 | 0 | 0 | 0.53564 | 18747.4 | 0.13605 | 1904.7 | 40000 | 0 | 5446.4 | 13301 | 0 | 1904.7 | 15205.7 | 0 | 0 | 0 | 0
2022110312 | 5 | 0.5842 | 46736 | 0 | 0 | 0.57748 | 20211.8 | 0.14948 | 2092.72 | 40000 | 0 | 6736 | 13475.8 | 0 | 2092.72 | 15568.52 | 0 | 0 | 0 | 0
2022110313 | 5 | 0.59884 | 47907.2 | 0 | 0 | 0.58726 | 20554.1 | 0.20087 | 2812.18 | 40000 | 0 | 7907.2 | 12646.9 | 0 | 2812.18 | 15459.08 | 0 | 0 | 0 | 0
2022110314 | 5 | 0.61479 | 49183.2 | 0 | 0 | 0.59184 | 20714.4 | 0.24837 | 3477.18 | 40000 | 0 | 9183.2 | 11531.2 | 0 | 3477.18 | 15008.38 | 0 | 0 | 0 | 0
2022110315 | 5 | 0.6285 | 50280 | 0 | 0 | 0.61085 | 21379.75 | 0.24896 | 3485.44 | 40000 | 0 | 10280 | 11099.75 | 0 | 3485.44 | 14585.19 | 0 | 0 | 0 | 0
2022110316 | 5 | 0.64274 | 51419.2 | 0 | 0 | 0.64079 | 22427.65 | 0.2133 | 2986.2 | 40000 | 0 | 11419.2 | 11008.45 | 0 | 2986.2 | 13994.65 | 0 | 0 | 0 | 0
2022110317 | 5 | 0.6529 | 52232 | 0 | 0 | 0.66389 | 23236.15 | 0.17839 | 2497.46 | 40000 | 0 | 12232 | 11004.15 | 0 | 2497.46 | 13501.61 | 0 | 0 | 0 | 0
2022110318 | 5 | 0.65188 | 52150.4 | 0 | 0 | 0.66843 | 23395.05 | 0.10628 | 1487.92 | 40000 | 0 | 12150.4 | 11244.65 | 0 | 1487.92 | 12732.57 | 0 | 0 | 0 | 0
2022110319 | 5 | 0.64229 | 51383.2 | 0 | 0 | 0.66691 | 23341.85 | 0.01935 | 270.9 | 40000 | 0 | 11383.2 | 11958.65 | 0 | 270.9 | 12229.55 | 0 | 0 | 0 | 0
2022110320 | 5 | 0.64265 | 51412 | 0 | 0 | 0.66811 | 23383.85 | 0 | 0 | 40000 | 0 | 11412 | 11971.85 | 0 | 0 | 11971.85 | 0 | 0 | 0 | 0
2022110321 | 5 | 0.63027 | 50421.6 | 0 | 0 | 0.65574 | 22950.9 | 0 | 0 | 40000 | 0 | 10421.6 | 12529.3 | 0 | 0 | 12529.3 | 0 | 0 | 0 | 0
2022110322 | 5 | 0.6107 | 48856 | 0 | 0 | 0.65278 | 22847.3 | 0 | 0 | 40000 | 0 | 8856 | 13991.3 | 0 | 0 | 13991.3 | 0 | 0 | 0 | 0
2022110323 | 5 | 0.5822 | 46576 | 0 | 0 | 0.65162 | 22806.7 | 0 | 0 | 40000 | 0 | 6576 | 16230.7 | 0 | 0 | 16230.7 | 0 | 0 | 0 | 0
2022110324 | 5 | 0.55164 | 44131.2 | 0 | 0 | 0.64694 | 22642.9 | 0 | 0 | 40000 | 0 | 4131.2 | 18511.7 | 0 | 0 | 18511.7 | 0 | 0 | 0 | 0
2022110401 | 6 | 0.5262 | 42096 | 0 | 0 | 0.64768 | 22668.8 | 0 | 0 | 40000 | 0 | 2096 | 20572.8 | 0 | 0 | 20572.8 | 0 | 0 | 0 | 0
2022110402 | 6 | 0.50658 | 40526.4 | 0 | 0 | 0.65227 | 22829.45 | 0 | 0 | 40000 | 0 | 526.4 | 22303.05 | 0 | 0 | 22303.05 | 0 | 0 | 0 | 0
2022110403 | 6 | 0.49234 | 39387.2 | 0 | 0 | 0.64849 | 22697.15 | 0 | 0 | 39387.2 | 612.8 | 0 | 22697.15 | 0 | 0 | 23309.95 | 0 | 0 | 0 | 0
2022110404 | 6 | 0.48627 | 38901.6 | 0 | 0 | 0.64653 | 22628.55 | 0 | 0 | 38901.6 | 1098.4 | 0 | 22628.55 | 0 | 0 | 23726.95 | 0 | 0 | 0 | 0
2022110405 | 6 | 0.49205 | 39364 | 0 | 0 | 0.64843 | 22695.05 | 0 | 0 | 39364 | 636 | 0 | 22695.05 | 0 | 0 | 23331.05 | 0 | 0 | 0 | 0
2022110406 | 6 | 0.51011 | 40808.8 | 0 | 0 | 0.63573 | 22250.55 | 0 | 0 | 40000 | 0 | 808.8 | 21441.75 | 0 | 0 | 21441.75 | 0 | 0 | 0 | 0
2022110407 | 6 | 0.54165 | 43332 | 0 | 0 | 0.60045 | 21015.75 | 0 | 0 | 40000 | 0 | 3332 | 17683.75 | 0 | 0 | 17683.75 | 0 | 0 | 0 | 0
2022110408 | 6 | 0.56207 | 44965.6 | 0 | 0 | 0.57803 | 20231.05 | 0.00026 | 3.64 | 40000 | 0 | 4965.6 | 15265.45 | 0 | 3.64 | 15269.09 | 0 | 0 | 0 | 0
2022110409 | 6 | 0.56583 | 45266.4 | 0 | 0 | 0.57051 | 19967.85 | 0.0528 | 739.2 | 40000 | 0 | 5266.4 | 14701.45 | 0 | 739.2 | 15440.65 | 0 | 0 | 0 | 0
2022110410 | 6 | 0.58638 | 46910.4 | 0 | 0 | 0.55969 | 19589.15 | 0.27959 | 3914.26 | 40000 | 0 | 6910.4 | 12678.75 | 0 | 3914.26 | 16593.01 | 0 | 0 | 0 | 0
2022110411 | 6 | 0.60522 | 48417.6 | 0 | 0 | 0.59605 | 20861.75 | 0.25942 | 3631.88 | 40000 | 0 | 8417.6 | 12444.15 | 0 | 3631.88 | 16076.03 | 0 | 0 | 0 | 0
2022110412 | 6 | 0.62267 | 49813.6 | 0 | 0 | 0.62828 | 21989.8 | 0.20099 | 2813.86 | 40000 | 0 | 9813.6 | 12176.2 | 0 | 2813.86 | 14990.06 | 0 | 0 | 0 | 0
2022110413 | 6 | 0.63653 | 50922.4 | 0 | 0 | 0.63813 | 22334.55 | 0.20309 | 2843.26 | 40000 | 0 | 10922.4 | 11412.15 | 0 | 2843.26 | 14255.41 | 0 | 0 | 0 | 0
2022110414 | 6 | 0.64849 | 51879.2 | 0 | 0 | 0.64251 | 22487.85 | 0.20397 | 2855.58 | 40000 | 0 | 11879.2 | 10608.65 | 0 | 2855.58 | 13464.23 | 0 | 0 | 0 | 0
2022110415 | 6 | 0.6546 | 52368 | 0 | 0 | 0.62535 | 21887.25 | 0.22562 | 3158.68 | 40000 | 0 | 12368 | 9519.25 | 0 | 3158.68 | 12677.93 | 0 | 0 | 0 | 0
2022110416 | 6 | 0.65956 | 52764.8 | 0 | 0 | 0.61055 | 21369.25 | 0.24422 | 3419.08 | 40000 | 0 | 12764.8 | 8604.45 | 0 | 3419.08 | 12023.53 | 0 | 0 | 0 | 0
2022110417 | 6 | 0.66127 | 52901.6 | 0 | 0 | 0.60263 | 21092.05 | 0.21649 | 3030.86 | 40000 | 0 | 12901.6 | 8190.45 | 0 | 3030.86 | 11221.31 | 0 | 0 | 0 | 0
2022110418 | 6 | 0.64769 | 51815.2 | 0 | 0 | 0.5783 | 20240.5 | 0.19006 | 2660.84 | 40000 | 0 | 11815.2 | 8425.3 | 0 | 2660.84 | 11086.14 | 0 | 0 | 0 | 0
2022110419 | 6 | 0.62591 | 50072.8 | 0 | 0 | 0.54317 | 19010.95 | 0.05485 | 767.9 | 40000 | 0 | 10072.8 | 8938.15 | 0 | 767.9 | 9706.05 | 0 | 0 | 0 | 0
2022110420 | 6 | 0.61585 | 49268 | 0 | 0 | 0.47368 | 16578.8 | 0 | 0 | 40000 | 0 | 9268 | 7310.8 | 0 | 0 | 7310.8 | 0 | 0 | 0 | 0
2022110421 | 6 | 0.59265 | 47412 | 0 | 0 | 0.44404 | 15541.4 | 0 | 0 | 40000 | 0 | 7412 | 8129.4 | 0 | 0 | 8129.4 | 0 | 0 | 0 | 0
2022110422 | 6 | 0.57061 | 45648.8 | 0 | 0 | 0.43606 | 15262.1 | 0 | 0 | 40000 | 0 | 5648.8 | 9613.3 | 0 | 0 | 9613.3 | 0 | 0 | 0 | 0
2022110423 | 6 | 0.54459 | 43567.2 | 0 | 0 | 0.40958 | 14335.3 | 0 | 0 | 40000 | 0 | 3567.2 | 10768.1 | 0 | 0 | 10768.1 | 0 | 0 | 0 | 0
2022110424 | 6 | 0.51475 | 41180 | 0 | 0 | 0.34781 | 12173.35 | 0 | 0 | 40000 | 0 | 1180 | 10993.35 | 0 | 0 | 10993.35 | 0 | 0 | 0 | 0
2022110501 | 7 | 0.4771 | 38168 | 0 | 0 | 0.30855 | 10799.25 | 0 | 0 | 38168 | 1832 | 0 | 10799.25 | 0 | 0 | 12631.25 | 0 | 0 | 0 | 0
2022110502 | 7 | 0.45038 | 36030.4 | 0 | 0 | 0.3134 | 10969 | 0 | 0 | 36030.4 | 3969.6 | 0 | 10969 | 0 | 0 | 14938.6 | 0 | 0 | 0 | 0
2022110503 | 7 | 0.43696 | 34956.8 | 0 | 0 | 0.32417 | 11345.95 | 0 | 0 | 34956.8 | 5043.2 | 0 | 11345.95 | 0 | 0 | 16389.15 | 0 | 0 | 0 | 0
2022110504 | 7 | 0.4289 | 34312 | 0 | 0 | 0.29251 | 10237.85 | 0 | 0 | 34312 | 5688 | 0 | 10237.85 | 0 | 0 | 15925.85 | 0 | 0 | 0 | 0
2022110505 | 7 | 0.42567 | 34053.6 | 0 | 0 | 0.25136 | 8797.6 | 0 | 0 | 34053.6 | 5946.4 | 0 | 8797.6 | 0 | 0 | 14744 | 0 | 0 | 0 | 0
2022110506 | 7 | 0.43027 | 34421.6 | 0 | 0 | 0.24862 | 8701.7 | 0 | 0 | 34421.6 | 5578.4 | 0 | 8701.7 | 0 | 0 | 14280.1 | 0 | 0 | 0 | 0
2022110507 | 7 | 0.44194 | 35355.2 | 0 | 0 | 0.2403 | 8410.5 | 0 | 0 | 35355.2 | 4644.8 | 0 | 8410.5 | 0 | 0 | 13055.3 | 0 | 0 | 0 | 0
2022110508 | 7 | 0.4589 | 36712 | 0 | 0 | 0.24517 | 8580.95 | 0.00014 | 1.96 | 36712 | 3288 | 0 | 8580.95 | 0 | 1.96 | 11870.91 | 0 | 0 | 0 | 0
2022110509 | 7 | 0.47722 | 38177.6 | 0 | 0 | 0.2415 | 8452.5 | 0.09478 | 1326.92 | 38177.6 | 1822.4 | 0 | 8452.5 | 0 | 1326.92 | 11601.82 | 0 | 0 | 0 | 0
2022110510 | 7 | 0.48888 | 39110.4 | 0 | 0 | 0.22089 | 7731.15 | 0.48616 | 6806.24 | 39110.4 | 889.6 | 0 | 7731.15 | 0 | 6806.24 | 15426.99 | 0 | 0 | 0 | 0
2022110511 | 7 | 0.49693 | 39754.4 | 0 | 0 | 0.20055 | 7019.25 | 0.65459 | 9164.26 | 39754.4 | 245.6 | 0 | 7019.25 | 0 | 9164.26 | 16429.11 | 0 | 0 | 0 | 0
2022110512 | 7 | 0.5002 | 40016 | 0 | 0 | 0.2806 | 9821 | 0.66506 | 9310.84 | 40000 | 0 | 16 | 9805 | 0 | 9310.84 | 19115.84 | 0 | 0 | 0 | 0
2022110513 | 7 | 0.50391 | 40312.8 | 0 | 0 | 0.33553 | 11743.55 | 0.67249 | 9414.86 | 40000 | 0 | 312.8 | 11430.75 | 0 | 9414.86 | 20845.61 | 0 | 0 | 0 | 0
2022110514 | 7 | 0.50991 | 40792.8 | 0 | 0 | 0.3805 | 13317.5 | 0.63613 | 8905.82 | 40000 | 0 | 792.8 | 12524.7 | 0 | 8905.82 | 21430.52 | 0 | 0 | 0 | 0
2022110515 | 7 | 0.51821 | 41456.8 | 0 | 0 | 0.42984 | 15044.4 | 0.48382 | 6773.48 | 40000 | 0 | 1456.8 | 13587.6 | 0 | 6773.48 | 20361.08 | 0 | 0 | 0 | 0
2022110516 | 7 | 0.5274 | 42192 | 0 | 0 | 0.44372 | 15530.2 | 0.41094 | 5753.16 | 40000 | 0 | 2192 | 13338.2 | 0 | 5753.16 | 19091.36 | 0 | 0 | 0 | 0
2022110517 | 7 | 0.53277 | 42621.6 | 0 | 0 | 0.44196 | 15468.6 | 0.37216 | 5210.24 | 40000 | 0 | 2621.6 | 12847 | 0 | 5210.24 | 18057.24 | 0 | 0 | 0 | 0
2022110518 | 7 | 0.5332 | 42656 | 0 | 0 | 0.43819 | 15336.65 | 0.23826 | 3335.64 | 40000 | 0 | 2656 | 12680.65 | 0 | 3335.64 | 16016.29 | 0 | 0 | 0 | 0
2022110519 | 7 | 0.52944 | 42355.2 | 0 | 0 | 0.44731 | 15655.85 | 0.04604 | 644.56 | 40000 | 0 | 2355.2 | 13300.65 | 0 | 644.56 | 13945.21 | 0 | 0 | 0 | 0
2022110520 | 7 | 0.53222 | 42577.6 | 0 | 0 | 0.52718 | 18451.3 | 0 | 0 | 40000 | 0 | 2577.6 | 15873.7 | 0 | 0 | 15873.7 | 0 | 0 | 0 | 0
2022110521 | 7 | 0.52072 | 41657.6 | 0 | 0 | 0.55393 | 19387.55 | 0 | 0 | 40000 | 0 | 1657.6 | 17729.95 | 0 | 0 | 17729.95 | 0 | 0 | 0 | 0
2022110522 | 7 | 0.50597 | 40477.6 | 0 | 0 | 0.53868 | 18853.8 | 0 | 0 | 40000 | 0 | 477.6 | 18376.2 | 0 | 0 | 18376.2 | 0 | 0 | 0 | 0
2022110523 | 7 | 0.48866 | 39092.8 | 0 | 0 | 0.53783 | 18824.05 | 0 | 0 | 39092.8 | 907.2 | 0 | 18824.05 | 0 | 0 | 19731.25 | 0 | 0 | 0 | 0
2022110524 | 7 | 0.47357 | 37885.6 | 0 | 0 | 0.52921 | 18522.35 | 4e-05 | 0.56 | 37885.6 | 2114.4 | 0 | 18522.35 | 0 | 0.56 | 20637.31 | 0 | 0 | 0 | 0
2022110601 | 1 | 0.4514 | 36112 | 0 | 0 | 0.52712 | 18449.2 | 4e-05 | 0.56 | 36112 | 3888 | 0 | 18449.2 | 0 | 0.56 | 22337.76 | 0 | 0 | 0 | 0
2022110602 | 1 | 0.43717 | 34973.6 | 0 | 0 | 0.52492 | 18372.2 | 0 | 0 | 34973.6 | 5026.4 | 0 | 18372.2 | 0 | 0 | 23398.6 | 0 | 0 | 0 | 0
2022110602 | 1 | 0.42895 | 34316 | 0 | 0 | 0.5239 | 18336.5 | 0 | 0 | 34316 | 5684 | 0 | 18336.5 | 0 | 0 | 24020.5 | 0 | 0 | 0 | 0
2022110603 | 1 | 0.42522 | 34017.6 | 0 | 0 | 0.52088 | 18230.8 | 4e-05 | 0.56 | 34017.6 | 5982.4 | 0 | 18230.8 | 0 | 0.56 | 24213.76 | 0 | 0 | 0 | 0
2022110604 | 1 | 0.42182 | 33745.6 | 0 | 0 | 0.50969 | 17839.15 | 4e-05 | 0.56 | 33745.6 | 6254.4 | 0 | 17839.15 | 0 | 0.56 | 24094.11 | 0 | 0 | 0 | 0
2022110605 | 1 | 0.4225 | 33800 | 0 | 0 | 0.50434 | 17651.9 | 0 | 0 | 33800 | 6200 | 0 | 17651.9 | 0 | 0 | 23851.9 | 0 | 0 | 0 | 0
2022110606 | 1 | 0.42994 | 34395.2 | 0 | 0 | 0.49967 | 17488.45 | 4e-05 | 0.56 | 34395.2 | 5604.8 | 0 | 17488.45 | 0 | 0.56 | 23093.81 | 0 | 0 | 0 | 0
2022110607 | 1 | 0.44169 | 35335.2 | 0 | 0 | 0.49593 | 17357.55 | 0.0002 | 2.8 | 35335.2 | 4664.8 | 0 | 17357.55 | 0 | 2.8 | 22025.15 | 0 | 0 | 0 | 0
2022110608 | 1 | 0.45757 | 36605.6 | 0 | 0 | 0.47067 | 16473.45 | 0.08514 | 1191.96 | 36605.6 | 3394.4 | 0 | 16473.45 | 0 | 1191.96 | 21059.81 | 0 | 0 | 0 | 0
2022110609 | 1 | 0.47825 | 38260 | 0 | 0 | 0.36611 | 12813.85 | 0.41334 | 5786.76 | 38260 | 1740 | 0 | 12813.85 | 0 | 5786.76 | 20340.61 | 0 | 0 | 0 | 0
2022110610 | 1 | 0.49863 | 39890.4 | 0 | 0 | 0.26473 | 9265.55 | 0.61016 | 8542.24 | 39890.4 | 109.6 | 0 | 9265.55 | 0 | 8542.24 | 17917.39 | 0 | 0 | 0 | 0
2022110611 | 1 | 0.51696 | 41356.8 | 0 | 0 | 0.234 | 8190 | 0.63967 | 8955.38 | 40000 | 0 | 1356.8 | 6833.2 | 0 | 8955.38 | 15788.58 | 0 | 0 | 0 | 0
2022110612 | 1 | 0.53555 | 42844 | 0 | 0 | 0.2075 | 7262.5 | 0.62593 | 8763.02 | 40000 | 0 | 2844 | 4418.5 | 0 | 8763.02 | 13181.52 | 0 | 0 | 0 | 0
2022110613 | 1 | 0.55697 | 44557.6 | 0 | 0 | 0.17723 | 6203.05 | 0.6323 | 8852.2 | 40000 | 0 | 4557.6 | 1645.45 | 0 | 8852.2 | 10497.65 | 0 | 0 | 0 | 0
2022110614 | 1 | 0.58052 | 46441.6 | 0 | 0 | 0.16531 | 5785.85 | 0.64894 | 9085.16 | 40000 | 0 | 5785.85 | 0 | 655.75 | 8429.41 | 8429.41 | 0 | 0 | 0 | 0
2022110615 | 1 | 0.59844 | 47875.2 | 0 | 0 | 0.16046 | 5616.1 | 0.66103 | 9254.42 | 40000 | 0 | 5616.1 | 0 | 2259.1 | 6995.32 | 6995.32 | 0 | 0 | 0 | 0
2022110616 | 1 | 0.60551 | 48440.8 | 0 | 0 | 0.14654 | 5128.9 | 0.63096 | 8833.44 | 40000 | 0 | 5128.9 | 0 | 3311.9 | 5521.54 | 5521.54 | 0 | 0 | 0 | 0
2022110617 | 1 | 0.60795 | 48636 | 0 | 0 | 0.13158 | 4605.3 | 0.42232 | 5912.48 | 40000 | 0 | 4605.3 | 0 | 4030.7 | 1881.78 | 1881.78 | 0 | 0 | 0 | 0
2022110618 | 1 | 0.59781 | 47824.8 | 0 | 0 | 0.13782 | 4823.7 | 0.07007 | 980.98 | 40000 | 0 | 4823.7 | 0 | 980.98 | 0 | 0 | 2020.12 | 0 | 0 | 2020.12
2022110619 | 1 | 0.59954 | 47963.2 | 0 | 0 | 0.18876 | 6606.6 | 0 | 0 | 40000 | 0 | 6606.6 | 0 | 0 | 0 | 0 | 1356.6 | 0 | 0 | 1356.6
2022110620 | 1 | 0.59586 | 47668.8 | 0 | 0 | 0.27451 | 9607.85 | 0 | 0 | 40000 | 0 | 7668.8 | 1939.05 | 0 | 0 | 1939.05 | 0 | 0 | 0 | 0
2022110621 | 1 | 0.57992 | 46393.6 | 0 | 0 | 0.33612 | 11764.2 | 0 | 0 | 40000 | 0 | 6393.6 | 5370.6 | 0 | 0 | 5370.6 | 0 | 0 | 0 | 0
2022110622 | 1 | 0.56278 | 45022.4 | 0 | 0 | 0.36949 | 12932.15 | 0 | 0 | 40000 | 0 | 5022.4 | 7909.75 | 0 | 0 | 7909.75 | 0 | 0 | 0 | 0
2022110623 | 1 | 0.5366 | 42928 | 0 | 0 | 0.39911 | 13968.85 | 0 | 0 | 40000 | 0 | 2928 | 11040.85 | 0 | 0 | 11040.85 | 0 | 0 | 0 | 0
2022110624 | 1 | 0.50931 | 40744.8 | 0 | 0 | 0.39278 | 13747.3 | 0 | 0 | 40000 | 0 | 744.8 | 13002.5 | 0 | 0 | 13002.5 | 0 | 0 | 0 | 0
2022110701 | 2 | 0.48547 | 38837.6 | 0 | 0 | 0.34607 | 12112.45 | 0 | 0 | 38837.6 | 1162.4 | 0 | 12112.45 | 0 | 0 | 13274.85 | 0 | 0 | 0 | 0
2022110702 | 2 | 0.47185 | 37748 | 0 | 0 | 0.31483 | 11019.05 | 0 | 0 | 37748 | 2252 | 0 | 11019.05 | 0 | 0 | 13271.05 | 0 | 0 | 0 | 0
2022110703 | 2 | 0.46433 | 37146.4 | 0 | 0 | 0.27626 | 9669.1 | 0 | 0 | 37146.4 | 2853.6 | 0 | 9669.1 | 0 | 0 | 12522.7 | 0 | 0 | 0 | 0
2022110704 | 2 | 0.46161 | 36928.8 | 0 | 0 | 0.25625 | 8968.75 | 0 | 0 | 36928.8 | 3071.2 | 0 | 8968.75 | 0 | 0 | 12039.95 | 0 | 0 | 0 | 0
2022110705 | 2 | 0.46994 | 37595.2 | 0 | 0 | 0.23582 | 8253.7 | 0 | 0 | 37595.2 | 2404.8 | 0 | 8253.7 | 0 | 0 | 10658.5 | 0 | 0 | 0 | 0
2022110706 | 2 | 0.49005 | 39204 | 0 | 0 | 0.2046 | 7161 | 0 | 0 | 39204 | 796 | 0 | 7161 | 0 | 0 | 7957 | 0 | 0 | 0 | 0
2022110707 | 2 | 0.52175 | 41740 | 0 | 0 | 0.18426 | 6449.1 | 0.00013 | 1.82 | 40000 | 0 | 1740 | 4709.1 | 0 | 1.82 | 4710.92 | 0 | 0 | 0 | 0
2022110708 | 2 | 0.54403 | 43522.4 | 0 | 0 | 0.16087 | 5630.45 | 0.04115 | 576.1 | 40000 | 0 | 3522.4 | 2108.05 | 0 | 576.1 | 2684.15 | 0 | 0 | 0 | 0
2022110709 | 2 | 0.55967 | 44773.6 | 0 | 0 | 0.11955 | 4184.25 | 0.21557 | 3017.98 | 40000 | 0 | 4184.25 | 0 | 589.35 | 2428.63 | 2428.63 | 0 | 0 | 0 | 0
2022110710 | 2 | 0.57865 | 46292 | 0 | 0 | 0.11268 | 3943.8 | 0.29502 | 4130.28 | 40000 | 0 | 3943.8 | 0 | 2348.2 | 1782.08 | 1782.08 | 0 | 0 | 0 | 0
2022110711 | 2 | 0.5984 | 47872 | 0 | 0 | 0.1121 | 3923.5 | 0.36222 | 5071.08 | 40000 | 0 | 3923.5 | 0 | 3948.5 | 1122.58 | 1122.58 | 0 | 0 | 0 | 0
2022110712 | 2 | 0.62122 | 49697.6 | 0 | 0 | 0.11147 | 3901.45 | 0.43083 | 6031.62 | 40000 | 0 | 3901.45 | 0 | 5796.15 | 235.47 | 235.47 | 0 | 0 | 0 | 0
2022110713 | 2 | 0.64494 | 51595.2 | 0 | 0 | 0.11978 | 4192.3 | 0.47343 | 6628.02 | 40000 | 0 | 4192.3 | 0 | 6628.02 | 0 | 0 | 774.88 | 0 | 0 | 774.88
2022110714 | 2 | 0.66192 | 52953.6 | 0 | 0 | 0.14302 | 5005.7 | 0.48119 | 6736.66 | 40000 | 0 | 5005.7 | 0 | 6736.66 | 0 | 0 | 1211.24 | 0 | 0 | 1211.24
2022110715 | 2 | 0.66795 | 53436 | 0 | 0 | 0.17527 | 6134.45 | 0.4669 | 6536.6 | 40000 | 0 | 6134.45 | 0 | 6536.6 | 0 | 0 | 764.95 | 0 | 0 | 764.95
2022110716 | 2 | 0.66786 | 53428.8 | 0 | 0 | 0.19964 | 6987.4 | 0.43182 | 6045.48 | 40000 | 0 | 6987.4 | 0 | 6045.48 | 0 | 0 | 395.92 | 0 | 0 | 395.92
2022110717 | 2 | 0.66053 | 52842.4 | 0 | 0 | 0.21238 | 7433.3 | 0.25974 | 3636.36 | 40000 | 0 | 7433.3 | 0 | 3636.36 | 0 | 0 | 1772.74 | 0 | 0 | 1772.74
2022110718 | 2 | 0.65187 | 52149.6 | 0 | 0 | 0.23517 | 8230.95 | 0.03332 | 466.48 | 40000 | 0 | 8230.95 | 0 | 466.48 | 0 | 0 | 3452.17 | 0 | 0 | 3452.17
2022110719 | 2 | 0.64719 | 51775.2 | 0 | 0 | 0.28946 | 10131.1 | 0 | 0 | 40000 | 0 | 10131.1 | 0 | 0 | 0 | 0 | 1644.1 | 0 | 0 | 1644.1
2022110720 | 2 | 0.63017 | 50413.6 | 0 | 0 | 0.34987 | 12245.45 | 0 | 0 | 40000 | 0 | 10413.6 | 1831.85 | 0 | 0 | 1831.85 | 0 | 0 | 0 | 0
2022110721 | 2 | 0.6096 | 48768 | 0 | 0 | 0.38579 | 13502.65 | 0 | 0 | 40000 | 0 | 8768 | 4734.65 | 0 | 0 | 4734.65 | 0 | 0 | 0 | 0
2022110722 | 2 | 0.58568 | 46854.4 | 0 | 0 | 0.40329 | 14115.15 | 0 | 0 | 40000 | 0 | 6854.4 | 7260.75 | 0 | 0 | 7260.75 | 0 | 0 | 0 | 0
2022110723 | 2 | 0.55029 | 44023.2 | 0 | 0 | 0.41484 | 14519.4 | 0 | 0 | 40000 | 0 | 4023.2 | 10496.2 | 0 | 0 | 10496.2 | 0 | 0 | 0 | 0
2022110724 | 2 | 0.51833 | 41466.4 | 0 | 0 | 0.44518 | 15581.3 | 0 | 0 | 40000 | 0 | 1466.4 | 14114.9 | 0 | 0 | 14114.9 | 0 | 0 | 0 | 0
2022110801 | 3 | 0.49212 | 39369.6 | 0 | 0 | 0.44885 | 15709.75 | 0 | 0 | 39369.6 | 630.4 | 0 | 15709.75 | 0 | 0 | 16340.15 | 0 | 0 | 0 | 0
2022110802 | 3 | 0.47618 | 38094.4 | 0 | 0 | 0.43796 | 15328.6 | 0 | 0 | 38094.4 | 1905.6 | 0 | 15328.6 | 0 | 0 | 17234.2 | 0 | 0 | 0 | 0
2022110803 | 3 | 0.46354 | 37083.2 | 0 | 0 | 0.41959 | 14685.65 | 0 | 0 | 37083.2 | 2916.8 | 0 | 14685.65 | 0 | 0 | 17602.45 | 0 | 0 | 0 | 0
2022110804 | 3 | 0.45867 | 36693.6 | 0 | 0 | 0.41747 | 14611.45 | 0 | 0 | 36693.6 | 3306.4 | 0 | 14611.45 | 0 | 0 | 17917.85 | 0 | 0 | 0 | 0
2022110805 | 3 | 0.46345 | 37076 | 0 | 0 | 0.42452 | 14858.2 | 0 | 0 | 37076 | 2924 | 0 | 14858.2 | 0 | 0 | 17782.2 | 0 | 0 | 0 | 0
2022110806 | 3 | 0.47607 | 38085.6 | 0 | 0 | 0.42139 | 14748.65 | 0 | 0 | 38085.6 | 1914.4 | 0 | 14748.65 | 0 | 0 | 16663.05 | 0 | 0 | 0 | 0
2022110807 | 3 | 0.51692 | 41353.6 | 0 | 0 | 0.41564 | 14547.4 | 0.0001 | 1.4 | 40000 | 0 | 1353.6 | 13193.8 | 0 | 1.4 | 13195.2 | 0 | 0 | 0 | 0
2022110808 | 3 | 0.53375 | 42700 | 0 | 0 | 0.39675 | 13886.25 | 0.037 | 518 | 40000 | 0 | 2700 | 11186.25 | 0 | 518 | 11704.25 | 0 | 0 | 0 | 0
2022110809 | 3 | 0.54934 | 43947.2 | 0 | 0 | 0.36963 | 12937.05 | 0.1673 | 2342.2 | 40000 | 0 | 3947.2 | 8989.85 | 0 | 2342.2 | 11332.05 | 0 | 0 | 0 | 0
2022110810 | 3 | 0.57247 | 45797.6 | 0 | 0 | 0.39254 | 13738.9 | 0.26219 | 3670.66 | 40000 | 0 | 5797.6 | 7941.3 | 0 | 3670.66 | 11611.96 | 0 | 0 | 0 | 0
2022110811 | 3 | 0.59889 | 47911.2 | 0 | 0 | 0.43689 | 15291.15 | 0.30508 | 4271.12 | 40000 | 0 | 7911.2 | 7379.95 | 0 | 4271.12 | 11651.07 | 0 | 0 | 0 | 0
2022110812 | 3 | 0.61971 | 49576.8 | 0 | 0 | 0.43813 | 15334.55 | 0.34599 | 4843.86 | 40000 | 0 | 9576.8 | 5757.75 | 0 | 4843.86 | 10601.61 | 0 | 0 | 0 | 0
2022110813 | 3 | 0.63784 | 51027.2 | 0 | 0 | 0.43111 | 15088.85 | 0.37874 | 5302.36 | 40000 | 0 | 11027.2 | 4061.65 | 0 | 5302.36 | 9364.01 | 0 | 0 | 0 | 0
2022110814 | 3 | 0.65181 | 52144.8 | 0 | 0 | 0.43708 | 15297.8 | 0.39174 | 5484.36 | 40000 | 0 | 12144.8 | 3153 | 0 | 5484.36 | 8637.36 | 0 | 0 | 0 | 0
2022110815 | 3 | 0.66143 | 52914.4 | 0 | 0 | 0.45894 | 16062.9 | 0.34852 | 4879.28 | 40000 | 0 | 12914.4 | 3148.5 | 0 | 4879.28 | 8027.78 | 0 | 0 | 0 | 0
2022110816 | 3 | 0.6672 | 53376 | 0 | 0 | 0.47686 | 16690.1 | 0.26554 | 3717.56 | 40000 | 0 | 13376 | 3314.1 | 0 | 3717.56 | 7031.66 | 0 | 0 | 0 | 0
2022110817 | 3 | 0.66293 | 53034.4 | 0 | 0 | 0.49694 | 17392.9 | 0.1469 | 2056.6 | 40000 | 0 | 13034.4 | 4358.5 | 0 | 2056.6 | 6415.1 | 0 | 0 | 0 | 0
2022110818 | 3 | 0.65561 | 52448.8 | 0 | 0 | 0.50867 | 17803.45 | 0.02576 | 360.64 | 40000 | 0 | 12448.8 | 5354.65 | 0 | 360.64 | 5715.29 | 0 | 0 | 0 | 0
2022110819 | 3 | 0.65345 | 52276 | 0 | 0 | 0.51639 | 18073.65 | 0 | 0 | 40000 | 0 | 12276 | 5797.65 | 0 | 0 | 5797.65 | 0 | 0 | 0 | 0
2022110820 | 3 | 0.63732 | 50985.6 | 0 | 0 | 0.54024 | 18908.4 | 0 | 0 | 40000 | 0 | 10985.6 | 7922.8 | 0 | 0 | 7922.8 | 0 | 0 | 0 | 0
2022110821 | 3 | 0.61864 | 49491.2 | 0 | 0 | 0.55184 | 19314.4 | 0 | 0 | 40000 | 0 | 9491.2 | 9823.2 | 0 | 0 | 9823.2 | 0 | 0 | 0 | 0
2022110822 | 3 | 0.59438 | 47550.4 | 0 | 0 | 0.55973 | 19590.55 | 0 | 0 | 40000 | 0 | 7550.4 | 12040.15 | 0 | 0 | 12040.15 | 0 | 0 | 0 | 0
2022110823 | 3 | 0.55869 | 44695.2 | 0 | 0 | 0.55381 | 19383.35 | 0 | 0 | 40000 | 0 | 4695.2 | 14688.15 | 0 | 0 | 14688.15 | 0 | 0 | 0 | 0
2022110824 | 3 | 0.52265 | 41812 | 0 | 0 | 0.54473 | 19065.55 | 0 | 0 | 40000 | 0 | 1812 | 17253.55 | 0 | 0 | 17253.55 | 0 | 0 | 0 | 0
2022110901 | 4 | 0.49634 | 39707.2 | 0 | 0 | 0.53022 | 18557.7 | 0 | 0 | 39707.2 | 292.8 | 0 | 18557.7 | 0 | 0 | 18850.5 | 0 | 0 | 0 | 0
2022110902 | 4 | 0.47831 | 38264.8 | 0 | 0 | 0.52343 | 18320.05 | 0 | 0 | 38264.8 | 1735.2 | 0 | 18320.05 | 0 | 0 | 20055.25 | 0 | 0 | 0 | 0
2022110903 | 4 | 0.46758 | 37406.4 | 0 | 0 | 0.51887 | 18160.45 | 0 | 0 | 37406.4 | 2593.6 | 0 | 18160.45 | 0 | 0 | 20754.05 | 0 | 0 | 0 | 0
2022110904 | 4 | 0.46234 | 36987.2 | 0 | 0 | 0.51273 | 17945.55 | 0 | 0 | 36987.2 | 3012.8 | 0 | 17945.55 | 0 | 0 | 20958.35 | 0 | 0 | 0 | 0
2022110905 | 4 | 0.46639 | 37311.2 | 0 | 0 | 0.51009 | 17853.15 | 0 | 0 | 37311.2 | 2688.8 | 0 | 17853.15 | 0 | 0 | 20541.95 | 0 | 0 | 0 | 0
2022110906 | 4 | 0.48672 | 38937.6 | 0 | 0 | 0.50491 | 17671.85 | 0 | 0 | 38937.6 | 1062.4 | 0 | 17671.85 | 0 | 0 | 18734.25 | 0 | 0 | 0 | 0
2022110907 | 4 | 0.52035 | 41628 | 0 | 0 | 0.51442 | 18004.7 | 0.00028 | 3.92 | 40000 | 0 | 1628 | 16376.7 | 0 | 3.92 | 16380.62 | 0 | 0 | 0 | 0
2022110908 | 4 | 0.53538 | 42830.4 | 0 | 0 | 0.51363 | 17977.05 | 0.0391 | 547.4 | 40000 | 0 | 2830.4 | 15146.65 | 0 | 547.4 | 15694.05 | 0 | 0 | 0 | 0
2022110909 | 4 | 0.55134 | 44107.2 | 0 | 0 | 0.49795 | 17428.25 | 0.16627 | 2327.78 | 40000 | 0 | 4107.2 | 13321.05 | 0 | 2327.78 | 15648.83 | 0 | 0 | 0 | 0
2022110910 | 4 | 0.57094 | 45675.2 | 0 | 0 | 0.52435 | 18352.25 | 0.21254 | 2975.56 | 40000 | 0 | 5675.2 | 12677.05 | 0 | 2975.56 | 15652.61 | 0 | 0 | 0 | 0
2022110911 | 4 | 0.59388 | 47510.4 | 0 | 0 | 0.53745 | 18810.75 | 0.2418 | 3385.2 | 40000 | 0 | 7510.4 | 11300.35 | 0 | 3385.2 | 14685.55 | 0 | 0 | 0 | 0
2022110912 | 4 | 0.61814 | 49451.2 | 0 | 0 | 0.55067 | 19273.45 | 0.23104 | 3234.56 | 40000 | 0 | 9451.2 | 9822.25 | 0 | 3234.56 | 13056.81 | 0 | 0 | 0 | 0
2022110913 | 4 | 0.638 | 51040 | 0 | 0 | 0.54813 | 19184.55 | 0.22741 | 3183.74 | 40000 | 0 | 11040 | 8144.55 | 0 | 3183.74 | 11328.29 | 0 | 0 | 0 | 0
2022110914 | 4 | 0.65528 | 52422.4 | 0 | 0 | 0.5422 | 18977 | 0.2353 | 3294.2 | 40000 | 0 | 12422.4 | 6554.6 | 0 | 3294.2 | 9848.8 | 0 | 0 | 0 | 0
2022110915 | 4 | 0.66763 | 53410.4 | 0 | 0 | 0.55605 | 19461.75 | 0.22546 | 3156.44 | 40000 | 0 | 13410.4 | 6051.35 | 0 | 3156.44 | 9207.79 | 0 | 0 | 0 | 0
2022110916 | 4 | 0.66842 | 53473.6 | 0 | 0 | 0.56362 | 19726.7 | 0.21498 | 3009.72 | 40000 | 0 | 13473.6 | 6253.1 | 0 | 3009.72 | 9262.82 | 0 | 0 | 0 | 0
2022110917 | 4 | 0.66624 | 53299.2 | 0 | 0 | 0.57566 | 20148.1 | 0.10325 | 1445.5 | 40000 | 0 | 13299.2 | 6848.9 | 0 | 1445.5 | 8294.4 | 0 | 0 | 0 | 0
2022110918 | 4 | 0.65512 | 52409.6 | 0 | 0 | 0.58613 | 20514.55 | 0.01695 | 237.3 | 40000 | 0 | 12409.6 | 8104.95 | 0 | 237.3 | 8342.25 | 0 | 0 | 0 | 0
2022110919 | 4 | 0.64985 | 51988 | 0 | 0 | 0.60408 | 21142.8 | 0.00013 | 1.82 | 40000 | 0 | 11988 | 9154.8 | 0 | 1.82 | 9156.62 | 0 | 0 | 0 | 0
2022110920 | 4 | 0.62821 | 50256.8 | 0 | 0 | 0.61557 | 21544.95 | 0 | 0 | 40000 | 0 | 10256.8 | 11288.15 | 0 | 0 | 11288.15 | 0 | 0 | 0 | 0
2022110921 | 4 | 0.6076 | 48608 | 0 | 0 | 0.60018 | 21006.3 | 0 | 0 | 40000 | 0 | 8608 | 12398.3 | 0 | 0 | 12398.3 | 0 | 0 | 0 | 0
2022110922 | 4 | 0.58298 | 46638.4 | 0 | 0 | 0.5797 | 20289.5 | 0 | 0 | 40000 | 0 | 6638.4 | 13651.1 | 0 | 0 | 13651.1 | 0 | 0 | 0 | 0
2022110923 | 4 | 0.5515 | 44120 | 0 | 0 | 0.56873 | 19905.55 | 0.00027 | 3.78 | 40000 | 0 | 4120 | 15785.55 | 0 | 3.78 | 15789.33 | 0 | 0 | 0 | 0
2022110924 | 4 | 0.5164 | 41312 | 0 | 0 | 0.56129 | 19645.15 | 0 | 0 | 40000 | 0 | 1312 | 18333.15 | 0 | 0 | 18333.15 | 0 | 0 | 0 | 0
2022111001 | 5 | 0.48977 | 39181.6 | 0 | 0 | 0.56022 | 19607.7 | 0 | 0 | 39181.6 | 818.4 | 0 | 19607.7 | 0 | 0 | 20426.1 | 0 | 0 | 0 | 0
2022111002 | 5 | 0.47217 | 37773.6 | 0 | 0 | 0.56144 | 19650.4 | 0 | 0 | 37773.6 | 2226.4 | 0 | 19650.4 | 0 | 0 | 21876.8 | 0 | 0 | 0 | 0
2022111003 | 5 | 0.46131 | 36904.8 | 0 | 0 | 0.54965 | 19237.75 | 0 | 0 | 36904.8 | 3095.2 | 0 | 19237.75 | 0 | 0 | 22332.95 | 0 | 0 | 0 | 0
2022111004 | 5 | 0.45758 | 36606.4 | 0 | 0 | 0.5445 | 19057.5 | 0 | 0 | 36606.4 | 3393.6 | 0 | 19057.5 | 0 | 0 | 22451.1 | 0 | 0 | 0 | 0
2022111005 | 5 | 0.46165 | 36932 | 0 | 0 | 0.53456 | 18709.6 | 0 | 0 | 36932 | 3068 | 0 | 18709.6 | 0 | 0 | 21777.6 | 0 | 0 | 0 | 0
2022111006 | 5 | 0.48081 | 38464.8 | 0 | 0 | 0.514 | 17990 | 0 | 0 | 38464.8 | 1535.2 | 0 | 17990 | 0 | 0 | 19525.2 | 0 | 0 | 0 | 0
2022111007 | 5 | 0.51253 | 41002.4 | 0 | 0 | 0.46175 | 16161.25 | 0.00015 | 2.1 | 40000 | 0 | 1002.4 | 15158.85 | 0 | 2.1 | 15160.95 | 0 | 0 | 0 | 0
2022111008 | 5 | 0.52337 | 41869.6 | 0 | 0 | 0.39916 | 13970.6 | 0.05611 | 785.54 | 40000 | 0 | 1869.6 | 12101 | 0 | 785.54 | 12886.54 | 0 | 0 | 0 | 0
2022111009 | 5 | 0.5396 | 43168 | 0 | 0 | 0.31976 | 11191.6 | 0.31535 | 4414.9 | 40000 | 0 | 3168 | 8023.6 | 0 | 4414.9 | 12438.5 | 0 | 0 | 0 | 0
2022111010 | 5 | 0.564 | 45120 | 0 | 0 | 0.32923 | 11523.05 | 0.49736 | 6963.04 | 40000 | 0 | 5120 | 6403.05 | 0 | 6963.04 | 13366.09 | 0 | 0 | 0 | 0
2022111011 | 5 | 0.58239 | 46591.2 | 0 | 0 | 0.32964 | 11537.4 | 0.51362 | 7190.68 | 40000 | 0 | 6591.2 | 4946.2 | 0 | 7190.68 | 12136.88 | 0 | 0 | 0 | 0
2022111012 | 5 | 0.59536 | 47628.8 | 0 | 0 | 0.26162 | 9156.7 | 0.5066 | 7092.4 | 40000 | 0 | 7628.8 | 1527.9 | 0 | 7092.4 | 8620.3 | 0 | 0 | 0 | 0
2022111013 | 5 | 0.60801 | 48640.8 | 0 | 0 | 0.1938 | 6783 | 0.50734 | 7102.76 | 40000 | 0 | 6783 | 0 | 1857.8 | 5244.96 | 5244.96 | 0 | 0 | 0 | 0
2022111014 | 5 | 0.62028 | 49622.4 | 0 | 0 | 0.14846 | 5196.1 | 0.5275 | 7385 | 40000 | 0 | 5196.1 | 0 | 4426.3 | 2958.7 | 2958.7 | 0 | 0 | 0 | 0
2022111015 | 5 | 0.62882 | 50305.6 | 0 | 0 | 0.1349 | 4721.5 | 0.54923 | 7689.22 | 40000 | 0 | 4721.5 | 0 | 5584.1 | 2105.12 | 2105.12 | 0 | 0 | 0 | 0
2022111016 | 5 | 0.63159 | 50527.2 | 0 | 0 | 0.14243 | 4985.05 | 0.52185 | 7305.9 | 40000 | 0 | 4985.05 | 0 | 5542.15 | 1763.75 | 1763.75 | 0 | 0 | 0 | 0
2022111017 | 5 | 0.62338 | 49870.4 | 0 | 0 | 0.16403 | 5741.05 | 0.31214 | 4369.96 | 40000 | 0 | 5741.05 | 0 | 4129.35 | 240.61 | 240.61 | 0 | 0 | 0 | 0
2022111018 | 5 | 0.6143 | 49144 | 0 | 0 | 0.19688 | 6890.8 | 0.03458 | 484.12 | 40000 | 0 | 6890.8 | 0 | 484.12 | 0 | 0 | 1769.08 | 0 | 0 | 1769.08
2022111019 | 5 | 0.61576 | 49260.8 | 0 | 0 | 0.24154 | 8453.9 | 0 | 0 | 40000 | 0 | 8453.9 | 0 | 0 | 0 | 0 | 806.9 | 0 | 0 | 806.9
2022111020 | 5 | 0.60264 | 48211.2 | 0 | 0 | 0.2677 | 9369.5 | 0 | 0 | 40000 | 0 | 8211.2 | 1158.3 | 0 | 0 | 1158.3 | 0 | 0 | 0 | 0
2022111021 | 5 | 0.58424 | 46739.2 | 0 | 0 | 0.2945 | 10307.5 | 0 | 0 | 40000 | 0 | 6739.2 | 3568.3 | 0 | 0 | 3568.3 | 0 | 0 | 0 | 0
2022111022 | 5 | 0.56636 | 45308.8 | 0 | 0 | 0.34808 | 12182.8 | 0 | 0 | 40000 | 0 | 5308.8 | 6874 | 0 | 0 | 6874 | 0 | 0 | 0 | 0
2022111023 | 5 | 0.53285 | 42628 | 0 | 0 | 0.38124 | 13343.4 | 0 | 0 | 40000 | 0 | 2628 | 10715.4 | 0 | 0 | 10715.4 | 0 | 0 | 0 | 0
2022111024 | 5 | 0.49871 | 39896.8 | 0 | 0 | 0.35475 | 12416.25 | 0 | 0 | 39896.8 | 103.2 | 0 | 12416.25 | 0 | 0 | 12519.45 | 0 | 0 | 0 | 0
2022111101 | 6 | 0.47273 | 37818.4 | 0 | 0 | 0.35923 | 12573.05 | 0 | 0 | 37818.4 | 2181.6 | 0 | 12573.05 | 0 | 0 | 14754.65 | 0 | 0 | 0 | 0
2022111102 | 6 | 0.45541 | 36432.8 | 0 | 0 | 0.36089 | 12631.15 | 0 | 0 | 36432.8 | 3567.2 | 0 | 12631.15 | 0 | 0 | 16198.35 | 0 | 0 | 0 | 0
2022111103 | 6 | 0.44413 | 35530.4 | 0 | 0 | 0.3959 | 13856.5 | 0 | 0 | 35530.4 | 4469.6 | 0 | 13856.5 | 0 | 0 | 18326.1 | 0 | 0 | 0 | 0
2022111104 | 6 | 0.43939 | 35151.2 | 0 | 0 | 0.41435 | 14502.25 | 0 | 0 | 35151.2 | 4848.8 | 0 | 14502.25 | 0 | 0 | 19351.05 | 0 | 0 | 0 | 0
2022111105 | 6 | 0.44525 | 35620 | 0 | 0 | 0.47531 | 16635.85 | 0 | 0 | 35620 | 4380 | 0 | 16635.85 | 0 | 0 | 21015.85 | 0 | 0 | 0 | 0
2022111106 | 6 | 0.46505 | 37204 | 0 | 0 | 0.53602 | 18760.7 | 0 | 0 | 37204 | 2796 | 0 | 18760.7 | 0 | 0 | 21556.7 | 0 | 0 | 0 | 0
2022111107 | 6 | 0.4999 | 39992 | 0 | 0 | 0.56089 | 19631.15 | 0.00014 | 1.96 | 39992 | 8 | 0 | 19631.15 | 0 | 1.96 | 19641.11 | 0 | 0 | 0 | 0
2022111108 | 6 | 0.5166 | 41328 | 0 | 0 | 0.53973 | 18890.55 | 0.03671 | 513.94 | 40000 | 0 | 1328 | 17562.55 | 0 | 513.94 | 18076.49 | 0 | 0 | 0 | 0
2022111109 | 6 | 0.53754 | 43003.2 | 0 | 0 | 0.5185 | 18147.5 | 0.12366 | 1731.24 | 40000 | 0 | 3003.2 | 15144.3 | 0 | 1731.24 | 16875.54 | 0 | 0 | 0 | 0
2022111110 | 6 | 0.56143 | 44914.4 | 0 | 0 | 0.54583 | 19104.05 | 0.13548 | 1896.72 | 40000 | 0 | 4914.4 | 14189.65 | 0 | 1896.72 | 16086.37 | 0 | 0 | 0 | 0
2022111111 | 6 | 0.57746 | 46196.8 | 0 | 0 | 0.54067 | 18923.45 | 0.13474 | 1886.36 | 40000 | 0 | 6196.8 | 12726.65 | 0 | 1886.36 | 14613.01 | 0 | 0 | 0 | 0
2022111112 | 6 | 0.5898 | 47184 | 0 | 0 | 0.52989 | 18546.15 | 0.14546 | 2036.44 | 40000 | 0 | 7184 | 11362.15 | 0 | 2036.44 | 13398.59 | 0 | 0 | 0 | 0
2022111113 | 6 | 0.59511 | 47608.8 | 0 | 0 | 0.52162 | 18256.7 | 0.1562 | 2186.8 | 40000 | 0 | 7608.8 | 10647.9 | 0 | 2186.8 | 12834.7 | 0 | 0 | 0 | 0
2022111114 | 6 | 0.59566 | 47652.8 | 0 | 0 | 0.51446 | 18006.1 | 0.16627 | 2327.78 | 40000 | 0 | 7652.8 | 10353.3 | 0 | 2327.78 | 12681.08 | 0 | 0 | 0 | 0
2022111115 | 6 | 0.59168 | 47334.4 | 0 | 0 | 0.51036 | 17862.6 | 0.16979 | 2377.06 | 40000 | 0 | 7334.4 | 10528.2 | 0 | 2377.06 | 12905.26 | 0 | 0 | 0 | 0
2022111116 | 6 | 0.58863 | 47090.4 | 0 | 0 | 0.50535 | 17687.25 | 0.1751 | 2451.4 | 40000 | 0 | 7090.4 | 10596.85 | 0 | 2451.4 | 13048.25 | 0 | 0 | 0 | 0
2022111117 | 6 | 0.5818 | 46544 | 0 | 0 | 0.51117 | 17890.95 | 0.1354 | 1895.6 | 40000 | 0 | 6544 | 11346.95 | 0 | 1895.6 | 13242.55 | 0 | 0 | 0 | 0
2022111118 | 6 | 0.58176 | 46540.8 | 0 | 0 | 0.48095 | 16833.25 | 0.04391 | 614.74 | 40000 | 0 | 6540.8 | 10292.45 | 0 | 614.74 | 10907.19 | 0 | 0 | 0 | 0
2022111119 | 6 | 0.57711 | 46168.8 | 0 | 0 | 0.45266 | 15843.1 | 0 | 0 | 40000 | 0 | 6168.8 | 9674.3 | 0 | 0 | 9674.3 | 0 | 0 | 0 | 0
2022111120 | 6 | 0.56392 | 45113.6 | 0 | 0 | 0.45402 | 15890.7 | 0 | 0 | 40000 | 0 | 5113.6 | 10777.1 | 0 | 0 | 10777.1 | 0 | 0 | 0 | 0
2022111121 | 6 | 0.55089 | 44071.2 | 0 | 0 | 0.45228 | 15829.8 | 0 | 0 | 40000 | 0 | 4071.2 | 11758.6 | 0 | 0 | 11758.6 | 0 | 0 | 0 | 0
2022111122 | 6 | 0.53705 | 42964 | 0 | 0 | 0.44092 | 15432.2 | 0 | 0 | 40000 | 0 | 2964 | 12468.2 | 0 | 0 | 12468.2 | 0 | 0 | 0 | 0
2022111123 | 6 | 0.51857 | 41485.6 | 0 | 0 | 0.41242 | 14434.7 | 0 | 0 | 40000 | 0 | 1485.6 | 12949.1 | 0 | 0 | 12949.1 | 0 | 0 | 0 | 0
2022111124 | 6 | 0.49639 | 39711.2 | 0 | 0 | 0.37839 | 13243.65 | 0 | 0 | 39711.2 | 288.8 | 0 | 13243.65 | 0 | 0 | 13532.45 | 0 | 0 | 0 | 0
2022111201 | 7 | 0.48051 | 38440.8 | 0 | 0 | 0.34439 | 12053.65 | 0 | 0 | 38440.8 | 1559.2 | 0 | 12053.65 | 0 | 0 | 13612.85 | 0 | 0 | 0 | 0
2022111202 | 7 | 0.47273 | 37818.4 | 0 | 0 | 0.3312 | 11592 | 0 | 0 | 37818.4 | 2181.6 | 0 | 11592 | 0 | 0 | 13773.6 | 0 | 0 | 0 | 0
2022111203 | 7 | 0.46912 | 37529.6 | 0 | 0 | 0.3342 | 11697 | 0 | 0 | 37529.6 | 2470.4 | 0 | 11697 | 0 | 0 | 14167.4 | 0 | 0 | 0 | 0
2022111204 | 7 | 0.47148 | 37718.4 | 0 | 0 | 0.31768 | 11118.8 | 0 | 0 | 37718.4 | 2281.6 | 0 | 11118.8 | 0 | 0 | 13400.4 | 0 | 0 | 0 | 0
2022111205 | 7 | 0.47786 | 38228.8 | 0 | 0 | 0.29133 | 10196.55 | 0 | 0 | 38228.8 | 1771.2 | 0 | 10196.55 | 0 | 0 | 11967.75 | 0 | 0 | 0 | 0
2022111206 | 7 | 0.49402 | 39521.6 | 0 | 0 | 0.27811 | 9733.85 | 0 | 0 | 39521.6 | 478.4 | 0 | 9733.85 | 0 | 0 | 10212.25 | 0 | 0 | 0 | 0
2022111207 | 7 | 0.51657 | 41325.6 | 0 | 0 | 0.24411 | 8543.85 | 0.00013 | 1.82 | 40000 | 0 | 1325.6 | 7218.25 | 0 | 1.82 | 7220.07 | 0 | 0 | 0 | 0
2022111208 | 7 | 0.53612 | 42889.6 | 0 | 0 | 0.22025 | 7708.75 | 0.07498 | 1049.72 | 40000 | 0 | 2889.6 | 4819.15 | 0 | 1049.72 | 5868.87 | 0 | 0 | 0 | 0
2022111209 | 7 | 0.55091 | 44072.8 | 0 | 0 | 0.17701 | 6195.35 | 0.45621 | 6386.94 | 40000 | 0 | 4072.8 | 2122.55 | 0 | 6386.94 | 8509.49 | 0 | 0 | 0 | 0
2022111210 | 7 | 0.55094 | 44075.2 | 0 | 0 | 0.15866 | 5553.1 | 0.64047 | 8966.58 | 40000 | 0 | 4075.2 | 1477.9 | 0 | 8966.58 | 10444.48 | 0 | 0 | 0 | 0
2022111211 | 7 | 0.54035 | 43228 | 0 | 0 | 0.1571 | 5498.5 | 0.6635 | 9289 | 40000 | 0 | 3228 | 2270.5 | 0 | 9289 | 11559.5 | 0 | 0 | 0 | 0
2022111212 | 7 | 0.52549 | 42039.2 | 0 | 0 | 0.15438 | 5403.3 | 0.65655 | 9191.7 | 40000 | 0 | 2039.2 | 3364.1 | 0 | 9191.7 | 12555.8 | 0 | 0 | 0 | 0
2022111213 | 7 | 0.51054 | 40843.2 | 0 | 0 | 0.13913 | 4869.55 | 0.65076 | 9110.64 | 40000 | 0 | 843.2 | 4026.35 | 0 | 9110.64 | 13136.99 | 0 | 0 | 0 | 0
2022111214 | 7 | 0.49757 | 39805.6 | 0 | 0 | 0.13023 | 4558.05 | 0.6637 | 9291.8 | 39805.6 | 194.4 | 0 | 4558.05 | 0 | 9291.8 | 14044.25 | 0 | 0 | 0 | 0
2022111215 | 7 | 0.49042 | 39233.6 | 0 | 0 | 0.12495 | 4373.25 | 0.68172 | 9544.08 | 39233.6 | 766.4 | 0 | 4373.25 | 0 | 9544.08 | 14683.73 | 0 | 0 | 0 | 0
2022111216 | 7 | 0.49083 | 39266.4 | 0 | 0 | 0.11346 | 3971.1 | 0.67628 | 9467.92 | 39266.4 | 733.6 | 0 | 3971.1 | 0 | 9467.92 | 14172.62 | 0 | 0 | 0 | 0
2022111217 | 7 | 0.49538 | 39630.4 | 0 | 0 | 0.10135 | 3547.25 | 0.43142 | 6039.88 | 39630.4 | 369.6 | 0 | 3547.25 | 0 | 6039.88 | 9956.73 | 0 | 0 | 0 | 0
2022111218 | 7 | 0.51978 | 41582.4 | 0 | 0 | 0.10008 | 3502.8 | 0.05685 | 795.9 | 40000 | 0 | 1582.4 | 1920.4 | 0 | 795.9 | 2716.3 | 0 | 0 | 0 | 0
2022111219 | 7 | 0.5397 | 43176 | 0 | 0 | 0.14941 | 5229.35 | 5e-05 | 0.7 | 40000 | 0 | 3176 | 2053.35 | 0 | 0.7 | 2054.05 | 0 | 0 | 0 | 0
2022111220 | 7 | 0.54132 | 43305.6 | 0 | 0 | 0.21886 | 7660.1 | 0 | 0 | 40000 | 0 | 3305.6 | 4354.5 | 0 | 0 | 4354.5 | 0 | 0 | 0 | 0
2022111221 | 7 | 0.53969 | 43175.2 | 0 | 0 | 0.26574 | 9300.9 | 0 | 0 | 40000 | 0 | 3175.2 | 6125.7 | 0 | 0 | 6125.7 | 0 | 0 | 0 | 0
2022111222 | 7 | 0.53599 | 42879.2 | 0 | 0 | 0.29844 | 10445.4 | 0 | 0 | 40000 | 0 | 2879.2 | 7566.2 | 0 | 0 | 7566.2 | 0 | 0 | 0 | 0
2022111223 | 7 | 0.52679 | 42143.2 | 0 | 0 | 0.34485 | 12069.75 | 0 | 0 | 40000 | 0 | 2143.2 | 9926.55 | 0 | 0 | 9926.55 | 0 | 0 | 0 | 0
2022111224 | 7 | 0.51748 | 41398.4 | 0 | 0 | 0.40573 | 14200.55 | 0 | 0 | 40000 | 0 | 1398.4 | 12802.15 | 0 | 0 | 12802.15 | 0 | 0 | 0 | 0
2022111301 | 1 | 0.51012 | 40809.6 | 0 | 0 | 0.45 | 15750 | 0 | 0 | 40000 | 0 | 809.6 | 14940.4 | 0 | 0 | 14940.4 | 0 | 0 | 0 | 0
2022111302 | 1 | 0.50752 | 40601.6 | 0 | 0 | 0.47219 | 16526.65 | 0 | 0 | 40000 | 0 | 601.6 | 15925.05 | 0 | 0 | 15925.05 | 0 | 0 | 0 | 0
2022111303 | 1 | 0.50692 | 40553.6 | 0 | 0 | 0.48938 | 17128.3 | 0 | 0 | 40000 | 0 | 553.6 | 16574.7 | 0 | 0 | 16574.7 | 0 | 0 | 0 | 0
2022111304 | 1 | 0.51095 | 40876 | 0 | 0 | 0.50019 | 17506.65 | 0 | 0 | 40000 | 0 | 876 | 16630.65 | 0 | 0 | 16630.65 | 0 | 0 | 0 | 0
2022111305 | 1 | 0.51739 | 41391.2 | 0 | 0 | 0.49016 | 17155.6 | 0 | 0 | 40000 | 0 | 1391.2 | 15764.4 | 0 | 0 | 15764.4 | 0 | 0 | 0 | 0
2022111306 | 1 | 0.52983 | 42386.4 | 0 | 0 | 0.48503 | 16976.05 | 0 | 0 | 40000 | 0 | 2386.4 | 14589.65 | 0 | 0 | 14589.65 | 0 | 0 | 0 | 0
2022111307 | 1 | 0.54675 | 43740 | 0 | 0 | 0.48996 | 17148.6 | 0.0002 | 2.8 | 40000 | 0 | 3740 | 13408.6 | 0 | 2.8 | 13411.4 | 0 | 0 | 0 | 0
2022111308 | 1 | 0.56158 | 44926.4 | 0 | 0 | 0.49054 | 17168.9 | 0.09199 | 1287.86 | 40000 | 0 | 4926.4 | 12242.5 | 0 | 1287.86 | 13530.36 | 0 | 0 | 0 | 0
2022111309 | 1 | 0.56239 | 44991.2 | 0 | 0 | 0.42961 | 15036.35 | 0.42002 | 5880.28 | 40000 | 0 | 4991.2 | 10045.15 | 0 | 5880.28 | 15925.43 | 0 | 0 | 0 | 0
2022111310 | 1 | 0.55536 | 44428.8 | 0 | 0 | 0.40997 | 14348.95 | 0.50047 | 7006.58 | 40000 | 0 | 4428.8 | 9920.15 | 0 | 7006.58 | 16926.73 | 0 | 0 | 0 | 0
2022111311 | 1 | 0.53986 | 43188.8 | 0 | 0 | 0.4438 | 15533 | 0.44794 | 6271.16 | 40000 | 0 | 3188.8 | 12344.2 | 0 | 6271.16 | 18615.36 | 0 | 0 | 0 | 0
2022111312 | 1 | 0.52423 | 41938.4 | 0 | 0 | 0.44369 | 15529.15 | 0.43987 | 6158.18 | 40000 | 0 | 1938.4 | 13590.75 | 0 | 6158.18 | 19748.93 | 0 | 0 | 0 | 0
2022111313 | 1 | 0.51169 | 40935.2 | 0 | 0 | 0.44751 | 15662.85 | 0.43036 | 6025.04 | 40000 | 0 | 935.2 | 14727.65 | 0 | 6025.04 | 20752.69 | 0 | 0 | 0 | 0
2022111314 | 1 | 0.50322 | 40257.6 | 0 | 0 | 0.45085 | 15779.75 | 0.42074 | 5890.36 | 40000 | 0 | 257.6 | 15522.15 | 0 | 5890.36 | 21412.51 | 0 | 0 | 0 | 0
2022111315 | 1 | 0.49949 | 39959.2 | 0 | 0 | 0.45802 | 16030.7 | 0.39793 | 5571.02 | 39959.2 | 40.8 | 0 | 16030.7 | 0 | 5571.02 | 21642.52 | 0 | 0 | 0 | 0
2022111316 | 1 | 0.49963 | 39970.4 | 0 | 0 | 0.46407 | 16242.45 | 0.35159 | 4922.26 | 39970.4 | 29.6 | 0 | 16242.45 | 0 | 4922.26 | 21194.31 | 0 | 0 | 0 | 0
2022111317 | 1 | 0.50912 | 40729.6 | 0 | 0 | 0.47986 | 16795.1 | 0.16263 | 2276.82 | 40000 | 0 | 729.6 | 16065.5 | 0 | 2276.82 | 18342.32 | 0 | 0 | 0 | 0
2022111318 | 1 | 0.53352 | 42681.6 | 0 | 0 | 0.44939 | 15728.65 | 0.02016 | 282.24 | 40000 | 0 | 2681.6 | 13047.05 | 0 | 282.24 | 13329.29 | 0 | 0 | 0 | 0
2022111319 | 1 | 0.55272 | 44217.6 | 0 | 0 | 0.45331 | 15865.85 | 0 | 0 | 40000 | 0 | 4217.6 | 11648.25 | 0 | 0 | 11648.25 | 0 | 0 | 0 | 0
2022111320 | 1 | 0.55797 | 44637.6 | 0 | 0 | 0.48726 | 17054.1 | 0 | 0 | 40000 | 0 | 4637.6 | 12416.5 | 0 | 0 | 12416.5 | 0 | 0 | 0 | 0
2022111321 | 1 | 0.55402 | 44321.6 | 0 | 0 | 0.51654 | 18078.9 | 0 | 0 | 40000 | 0 | 4321.6 | 13757.3 | 0 | 0 | 13757.3 | 0 | 0 | 0 | 0
2022111322 | 1 | 0.54152 | 43321.6 | 0 | 0 | 0.52765 | 18467.75 | 0 | 0 | 40000 | 0 | 3321.6 | 15146.15 | 0 | 0 | 15146.15 | 0 | 0 | 0 | 0
2022111323 | 1 | 0.52024 | 41619.2 | 0 | 0 | 0.52687 | 18440.45 | 0 | 0 | 40000 | 0 | 1619.2 | 16821.25 | 0 | 0 | 16821.25 | 0 | 0 | 0 | 0
2022111324 | 1 | 0.49698 | 39758.4 | 0 | 0 | 0.53303 | 18656.05 | 0 | 0 | 39758.4 | 241.6 | 0 | 18656.05 | 0 | 0 | 18897.65 | 0 | 0 | 0 | 0
2022111401 | 2 | 0.47931 | 38344.8 | 0 | 0 | 0.53612 | 18764.2 | 0 | 0 | 38344.8 | 1655.2 | 0 | 18764.2 | 0 | 0 | 20419.4 | 0 | 0 | 0 | 0
2022111402 | 2 | 0.47171 | 37736.8 | 0 | 0 | 0.5273 | 18455.5 | 0 | 0 | 37736.8 | 2263.2 | 0 | 18455.5 | 0 | 0 | 20718.7 | 0 | 0 | 0 | 0
2022111403 | 2 | 0.46656 | 37324.8 | 0 | 0 | 0.49509 | 17328.15 | 0 | 0 | 37324.8 | 2675.2 | 0 | 17328.15 | 0 | 0 | 20003.35 | 0 | 0 | 0 | 0
2022111404 | 2 | 0.4684 | 37472 | 0 | 0 | 0.457 | 15995 | 0 | 0 | 37472 | 2528 | 0 | 15995 | 0 | 0 | 18523 | 0 | 0 | 0 | 0
2022111405 | 2 | 0.47862 | 38289.6 | 0 | 0 | 0.41414 | 14494.9 | 0 | 0 | 38289.6 | 1710.4 | 0 | 14494.9 | 0 | 0 | 16205.3 | 0 | 0 | 0 | 0
2022111406 | 2 | 0.50665 | 40532 | 0 | 0 | 0.3719 | 13016.5 | 0 | 0 | 40000 | 0 | 532 | 12484.5 | 0 | 0 | 12484.5 | 0 | 0 | 0 | 0
2022111407 | 2 | 0.54748 | 43798.4 | 0 | 0 | 0.30506 | 10677.1 | 4e-05 | 0.56 | 40000 | 0 | 3798.4 | 6878.7 | 0 | 0.56 | 6879.26 | 0 | 0 | 0 | 0
2022111408 | 2 | 0.56535 | 45228 | 0 | 0 | 0.23776 | 8321.6 | 0.01452 | 203.28 | 40000 | 0 | 5228 | 3093.6 | 0 | 203.28 | 3296.88 | 0 | 0 | 0 | 0
2022111409 | 2 | 0.57366 | 45892.8 | 0 | 0 | 0.23168 | 8108.8 | 0.09152 | 1281.28 | 40000 | 0 | 5892.8 | 2216 | 0 | 1281.28 | 3497.28 | 0 | 0 | 0 | 0
2022111410 | 2 | 0.58214 | 46571.2 | 0 | 0 | 0.20456 | 7159.6 | 0.21482 | 3007.48 | 40000 | 0 | 6571.2 | 588.4 | 0 | 3007.48 | 3595.88 | 0 | 0 | 0 | 0
2022111411 | 2 | 0.58698 | 46958.4 | 0 | 0 | 0.19435 | 6802.25 | 0.32066 | 4489.24 | 40000 | 0 | 6802.25 | 0 | 156.15 | 4333.09 | 4333.09 | 0 | 0 | 0 | 0
2022111412 | 2 | 0.59147 | 47317.6 | 0 | 0 | 0.25909 | 9068.15 | 0.36131 | 5058.34 | 40000 | 0 | 7317.6 | 1750.55 | 0 | 5058.34 | 6808.89 | 0 | 0 | 0 | 0
2022111413 | 2 | 0.59279 | 47423.2 | 0 | 0 | 0.32717 | 11450.95 | 0.34019 | 4762.66 | 40000 | 0 | 7423.2 | 4027.75 | 0 | 4762.66 | 8790.41 | 0 | 0 | 0 | 0
2022111414 | 2 | 0.59685 | 47748 | 0 | 0 | 0.39339 | 13768.65 | 0.34482 | 4827.48 | 40000 | 0 | 7748 | 6020.65 | 0 | 4827.48 | 10848.13 | 0 | 0 | 0 | 0
2022111415 | 2 | 0.59384 | 47507.2 | 0 | 0 | 0.46091 | 16131.85 | 0.29875 | 4182.5 | 40000 | 0 | 7507.2 | 8624.65 | 0 | 4182.5 | 12807.15 | 0 | 0 | 0 | 0
2022111416 | 2 | 0.59074 | 47259.2 | 0 | 0 | 0.51968 | 18188.8 | 0.20742 | 2903.88 | 40000 | 0 | 7259.2 | 10929.6 | 0 | 2903.88 | 13833.48 | 0 | 0 | 0 | 0
2022111417 | 2 | 0.59527 | 47621.6 | 0 | 0 | 0.53201 | 18620.35 | 0.12926 | 1809.64 | 40000 | 0 | 7621.6 | 10998.75 | 0 | 1809.64 | 12808.39 | 0 | 0 | 0 | 0
2022111418 | 2 | 0.6154 | 49232 | 0 | 0 | 0.53797 | 18828.95 | 0.03021 | 422.94 | 40000 | 0 | 9232 | 9596.95 | 0 | 422.94 | 10019.89 | 0 | 0 | 0 | 0
2022111419 | 2 | 0.62312 | 49849.6 | 0 | 0 | 0.52587 | 18405.45 | 0.00047 | 6.58 | 40000 | 0 | 9849.6 | 8555.85 | 0 | 6.58 | 8562.43 | 0 | 0 | 0 | 0
2022111420 | 2 | 0.61041 | 48832.8 | 0 | 0 | 0.50137 | 17547.95 | 0 | 0 | 40000 | 0 | 8832.8 | 8715.15 | 0 | 0 | 8715.15 | 0 | 0 | 0 | 0
2022111421 | 2 | 0.59766 | 47812.8 | 0 | 0 | 0.44617 | 15615.95 | 0 | 0 | 40000 | 0 | 7812.8 | 7803.15 | 0 | 0 | 7803.15 | 0 | 0 | 0 | 0
2022111422 | 2 | 0.57609 | 46087.2 | 0 | 0 | 0.39769 | 13919.15 | 0 | 0 | 40000 | 0 | 6087.2 | 7831.95 | 0 | 0 | 7831.95 | 0 | 0 | 0 | 0
2022111423 | 2 | 0.54793 | 43834.4 | 0 | 0 | 0.36613 | 12814.55 | 0 | 0 | 40000 | 0 | 3834.4 | 8980.15 | 0 | 0 | 8980.15 | 0 | 0 | 0 | 0
2022111424 | 2 | 0.52323 | 41858.4 | 0 | 0 | 0.34093 | 11932.55 | 0 | 0 | 40000 | 0 | 1858.4 | 10074.15 | 0 | 0 | 10074.15 | 0 | 0 | 0 | 0
2022111501 | 3 | 0.51065 | 40852 | 0 | 0 | 0.3394 | 11879 | 0 | 0 | 40000 | 0 | 852 | 11027 | 0 | 0 | 11027 | 0 | 0 | 0 | 0
2022111502 | 3 | 0.50345 | 40276 | 0 | 0 | 0.34596 | 12108.6 | 0 | 0 | 40000 | 0 | 276 | 11832.6 | 0 | 0 | 11832.6 | 0 | 0 | 0 | 0
2022111503 | 3 | 0.50175 | 40140 | 0 | 0 | 0.33392 | 11687.2 | 0 | 0 | 40000 | 0 | 140 | 11547.2 | 0 | 0 | 11547.2 | 0 | 0 | 0 | 0
2022111504 | 3 | 0.50436 | 40348.8 | 0 | 0 | 0.32374 | 11330.9 | 0 | 0 | 40000 | 0 | 348.8 | 10982.1 | 0 | 0 | 10982.1 | 0 | 0 | 0 | 0
2022111505 | 3 | 0.51982 | 41585.6 | 0 | 0 | 0.30705 | 10746.75 | 0 | 0 | 40000 | 0 | 1585.6 | 9161.15 | 0 | 0 | 9161.15 | 0 | 0 | 0 | 0
2022111506 | 3 | 0.55612 | 44489.6 | 0 | 0 | 0.30355 | 10624.25 | 0 | 0 | 40000 | 0 | 4489.6 | 6134.65 | 0 | 0 | 6134.65 | 0 | 0 | 0 | 0
2022111507 | 3 | 0.60968 | 48774.4 | 0 | 0 | 0.32243 | 11285.05 | 4e-05 | 0.56 | 40000 | 0 | 8774.4 | 2510.65 | 0 | 0.56 | 2511.21 | 0 | 0 | 0 | 0
2022111508 | 3 | 0.62338 | 49870.4 | 0 | 0 | 0.31535 | 11037.25 | 0.03631 | 508.34 | 40000 | 0 | 9870.4 | 1166.85 | 0 | 508.34 | 1675.19 | 0 | 0 | 0 | 0
2022111509 | 3 | 0.62185 | 49748 | 0 | 0 | 0.28172 | 9860.2 | 0.23249 | 3254.86 | 40000 | 0 | 9748 | 112.2 | 0 | 3254.86 | 3367.06 | 0 | 0 | 0 | 0
2022111510 | 3 | 0.61626 | 49300.8 | 0 | 0 | 0.2648 | 9268 | 0.37744 | 5284.16 | 40000 | 0 | 9268 | 0 | 32.8 | 5251.36 | 5251.36 | 0 | 0 | 0 | 0
2022111511 | 3 | 0.60638 | 48510.4 | 0 | 0 | 0.24717 | 8650.95 | 0.46481 | 6507.34 | 40000 | 0 | 8510.4 | 140.55 | 0 | 6507.34 | 6647.89 | 0 | 0 | 0 | 0
2022111512 | 3 | 0.5904 | 47232 | 0 | 0 | 0.22035 | 7712.25 | 0.50388 | 7054.32 | 40000 | 0 | 7232 | 480.25 | 0 | 7054.32 | 7534.57 | 0 | 0 | 0 | 0
2022111513 | 3 | 0.5777 | 46216 | 0 | 0 | 0.1917 | 6709.5 | 0.48839 | 6837.46 | 40000 | 0 | 6216 | 493.5 | 0 | 6837.46 | 7330.96 | 0 | 0 | 0 | 0
2022111514 | 3 | 0.5668 | 45344 | 0 | 0 | 0.16724 | 5853.4 | 0.49193 | 6887.02 | 40000 | 0 | 5344 | 509.4 | 0 | 6887.02 | 7396.42 | 0 | 0 | 0 | 0
2022111515 | 3 | 0.55811 | 44648.8 | 0 | 0 | 0.1373 | 4805.5 | 0.44633 | 6248.62 | 40000 | 0 | 4648.8 | 156.7 | 0 | 6248.62 | 6405.32 | 0 | 0 | 0 | 0
2022111516 | 3 | 0.55534 | 44427.2 | 0 | 0 | 0.11631 | 4070.85 | 0.35767 | 5007.38 | 40000 | 0 | 4070.85 | 0 | 356.35 | 4651.03 | 4651.03 | 0 | 0 | 0 | 0
2022111517 | 3 | 0.56949 | 45559.2 | 0 | 0 | 0.10954 | 3833.9 | 0.14967 | 2095.38 | 40000 | 0 | 3833.9 | 0 | 1725.3 | 370.08 | 370.08 | 0 | 0 | 0 | 0
2022111518 | 3 | 0.59971 | 47976.8 | 0 | 0 | 0.10426 | 3649.1 | 0.01296 | 181.44 | 40000 | 0 | 3649.1 | 0 | 181.44 | 0 | 0 | 4146.26 | 0 | 0 | 4146.26
2022111519 | 3 | 0.61965 | 49572 | 0 | 0 | 0.12627 | 4419.45 | 0 | 0 | 40000 | 0 | 4419.45 | 0 | 0 | 0 | 0 | 5152.55 | 0 | 0 | 5152.55
2022111520 | 3 | 0.62213 | 49770.4 | 0 | 0 | 0.1625 | 5687.5 | 0 | 0 | 40000 | 0 | 5687.5 | 0 | 0 | 0 | 0 | 4082.9 | 0 | 0 | 4082.9
2022111521 | 3 | 0.61726 | 49380.8 | 0 | 0 | 0.1645 | 5757.5 | 0 | 0 | 40000 | 0 | 5757.5 | 0 | 0 | 0 | 0 | 3623.3 | 0 | 0 | 3623.3
2022111522 | 3 | 0.60024 | 48019.2 | 0 | 0 | 0.15988 | 5595.8 | 0 | 0 | 40000 | 0 | 5595.8 | 0 | 0 | 0 | 0 | 2423.4 | 0 | 0 | 2423.4
2022111523 | 3 | 0.57155 | 45724 | 0 | 0 | 0.15419 | 5396.65 | 0 | 0 | 40000 | 0 | 5396.65 | 0 | 0 | 0 | 0 | 327.35 | 0 | 0 | 327.35
2022111524 | 3 | 0.54999 | 43999.2 | 0 | 0 | 0.1511 | 5288.5 | 0 | 0 | 40000 | 0 | 3999.2 | 1289.3 | 0 | 0 | 1289.3 | 0 | 0 | 0 | 0
2022111601 | 4 | 0.53214 | 42571.2 | 0 | 0 | 0.14536 | 5087.6 | 0 | 0 | 40000 | 0 | 2571.2 | 2516.4 | 0 | 0 | 2516.4 | 0 | 0 | 0 | 0
2022111602 | 4 | 0.52661 | 42128.8 | 0 | 0 | 0.1531 | 5358.5 | 0 | 0 | 40000 | 0 | 2128.8 | 3229.7 | 0 | 0 | 3229.7 | 0 | 0 | 0 | 0
2022111603 | 4 | 0.52757 | 42205.6 | 0 | 0 | 0.15491 | 5421.85 | 0 | 0 | 40000 | 0 | 2205.6 | 3216.25 | 0 | 0 | 3216.25 | 0 | 0 | 0 | 0
2022111604 | 4 | 0.53151 | 42520.8 | 0 | 0 | 0.16212 | 5674.2 | 0 | 0 | 40000 | 0 | 2520.8 | 3153.4 | 0 | 0 | 3153.4 | 0 | 0 | 0 | 0
2022111605 | 4 | 0.54719 | 43775.2 | 0 | 0 | 0.15671 | 5484.85 | 0 | 0 | 40000 | 0 | 3775.2 | 1709.65 | 0 | 0 | 1709.65 | 0 | 0 | 0 | 0
2022111606 | 4 | 0.57514 | 46011.2 | 0 | 0 | 0.14741 | 5159.35 | 0 | 0 | 40000 | 0 | 5159.35 | 0 | 0 | 0 | 0 | 851.85 | 0 | 0 | 851.85
2022111607 | 4 | 0.6188 | 49504 | 0 | 0 | 0.12793 | 4477.55 | 0 | 0 | 40000 | 0 | 4477.55 | 0 | 0 | 0 | 0 | 5026.45 | 0 | 0 | 5026.45
2022111608 | 4 | 0.63572 | 50857.6 | 0 | 0 | 0.11193 | 3917.55 | 0.01996 | 279.44 | 40000 | 0 | 3917.55 | 0 | 279.44 | 0 | 0 | 6660.61 | 0 | 0 | 6660.61
2022111609 | 4 | 0.62965 | 50372 | 0 | 0 | 0.10127 | 3544.45 | 0.16744 | 2344.16 | 40000 | 0 | 3544.45 | 0 | 2344.16 | 0 | 0 | 4483.39 | 0 | 0 | 4483.39
2022111610 | 4 | 0.61266 | 49012.8 | 0 | 0 | 0.0993 | 3475.5 | 0.29746 | 4164.44 | 40000 | 0 | 3475.5 | 0 | 4164.44 | 0 | 0 | 1372.86 | 0 | 0 | 1372.86
2022111611 | 4 | 0.5944 | 47552 | 0 | 0 | 0.10512 | 3679.2 | 0.38787 | 5430.18 | 40000 | 0 | 3679.2 | 0 | 3872.8 | 1557.38 | 1557.38 | 0 | 0 | 0 | 0
2022111612 | 4 | 0.57563 | 46050.4 | 0 | 0 | 0.11122 | 3892.7 | 0.45459 | 6364.26 | 40000 | 0 | 3892.7 | 0 | 2157.7 | 4206.56 | 4206.56 | 0 | 0 | 0 | 0
2022111613 | 4 | 0.56224 | 44979.2 | 0 | 0 | 0.1155 | 4042.5 | 0.50556 | 7077.84 | 40000 | 0 | 4042.5 | 0 | 936.7 | 6141.14 | 6141.14 | 0 | 0 | 0 | 0
2022111614 | 4 | 0.55349 | 44279.2 | 0 | 0 | 0.11249 | 3937.15 | 0.52697 | 7377.58 | 40000 | 0 | 3937.15 | 0 | 342.05 | 7035.53 | 7035.53 | 0 | 0 | 0 | 0
2022111615 | 4 | 0.54676 | 43740.8 | 0 | 0 | 0.11137 | 3897.95 | 0.507 | 7098 | 40000 | 0 | 3740.8 | 157.15 | 0 | 7098 | 7255.15 | 0 | 0 | 0 | 0
2022111616 | 4 | 0.54405 | 43524 | 0 | 0 | 0.11298 | 3954.3 | 0.3806 | 5328.4 | 40000 | 0 | 3524 | 430.3 | 0 | 5328.4 | 5758.7 | 0 | 0 | 0 | 0
2022111617 | 4 | 0.55389 | 44311.2 | 0 | 0 | 0.10843 | 3795.05 | 0.15347 | 2148.58 | 40000 | 0 | 3795.05 | 0 | 516.15 | 1632.43 | 1632.43 | 0 | 0 | 0 | 0
2022111618 | 4 | 0.5809 | 46472 | 0 | 0 | 0.09301 | 3255.35 | 0.01461 | 204.54 | 40000 | 0 | 3255.35 | 0 | 204.54 | 0 | 0 | 3012.11 | 0 | 0 | 3012.11
2022111619 | 4 | 0.59715 | 47772 | 0 | 0 | 0.08801 | 3080.35 | 0 | 0 | 40000 | 0 | 3080.35 | 0 | 0 | 0 | 0 | 4691.65 | 0 | 0 | 4691.65
2022111620 | 4 | 0.60322 | 48257.6 | 0 | 0 | 0.09236 | 3232.6 | 0 | 0 | 40000 | 0 | 3232.6 | 0 | 0 | 0 | 0 | 5025 | 0 | 0 | 5025
2022111621 | 4 | 0.60449 | 48359.2 | 0 | 0 | 0.09754 | 3413.9 | 0 | 0 | 40000 | 0 | 3413.9 | 0 | 0 | 0 | 0 | 4945.3 | 0 | 0 | 4945.3
2022111622 | 4 | 0.59148 | 47318.4 | 0 | 0 | 0.11282 | 3948.7 | 0 | 0 | 40000 | 0 | 3948.7 | 0 | 0 | 0 | 0 | 3369.7 | 0 | 0 | 3369.7
2022111623 | 4 | 0.56968 | 45574.4 | 0 | 0 | 0.1311 | 4588.5 | 0 | 0 | 40000 | 0 | 4588.5 | 0 | 0 | 0 | 0 | 985.9 | 0 | 0 | 985.9
2022111624 | 4 | 0.54861 | 43888.8 | 0 | 0 | 0.14284 | 4999.4 | 0 | 0 | 40000 | 0 | 3888.8 | 1110.6 | 0 | 0 | 1110.6 | 0 | 0 | 0 | 0
2022111701 | 5 | 0.53058 | 42446.4 | 0 | 0 | 0.15261 | 5341.35 | 0 | 0 | 40000 | 0 | 2446.4 | 2894.95 | 0 | 0 | 2894.95 | 0 | 0 | 0 | 0
2022111702 | 5 | 0.52581 | 42064.8 | 0 | 0 | 0.17381 | 6083.35 | 0 | 0 | 40000 | 0 | 2064.8 | 4018.55 | 0 | 0 | 4018.55 | 0 | 0 | 0 | 0
2022111703 | 5 | 0.52507 | 42005.6 | 0 | 0 | 0.20001 | 7000.35 | 0 | 0 | 40000 | 0 | 2005.6 | 4994.75 | 0 | 0 | 4994.75 | 0 | 0 | 0 | 0
2022111704 | 5 | 0.53081 | 42464.8 | 0 | 0 | 0.22303 | 7806.05 | 0 | 0 | 40000 | 0 | 2464.8 | 5341.25 | 0 | 0 | 5341.25 | 0 | 0 | 0 | 0
2022111705 | 5 | 0.54603 | 43682.4 | 0 | 0 | 0.23283 | 8149.05 | 0 | 0 | 40000 | 0 | 3682.4 | 4466.65 | 0 | 0 | 4466.65 | 0 | 0 | 0 | 0
2022111706 | 5 | 0.5786 | 46288 | 0 | 0 | 0.24768 | 8668.8 | 0 | 0 | 40000 | 0 | 6288 | 2380.8 | 0 | 0 | 2380.8 | 0 | 0 | 0 | 0
2022111707 | 5 | 0.62533 | 50026.4 | 0 | 0 | 0.27381 | 9583.35 | 0 | 0 | 40000 | 0 | 9583.35 | 0 | 0 | 0 | 0 | 443.05 | 0 | 0 | 443.05
2022111708 | 5 | 0.63734 | 50987.2 | 0 | 0 | 0.2906 | 10171 | 0.04552 | 637.28 | 40000 | 0 | 10171 | 0 | 637.28 | 0 | 0 | 178.92 | 0 | 0 | 178.92
2022111709 | 5 | 0.62195 | 49756 | 0 | 0 | 0.2686 | 9401 | 0.36697 | 5137.58 | 40000 | 0 | 9401 | 0 | 355 | 4782.58 | 4782.58 | 0 | 0 | 0 | 0
2022111710 | 5 | 0.60473 | 48378.4 | 0 | 0 | 0.22753 | 7963.55 | 0.55181 | 7725.34 | 40000 | 0 | 7963.55 | 0 | 414.85 | 7310.49 | 7310.49 | 0 | 0 | 0 | 0
2022111711 | 5 | 0.58128 | 46502.4 | 0 | 0 | 0.27679 | 9687.65 | 0.55228 | 7731.92 | 40000 | 0 | 6502.4 | 3185.25 | 0 | 7731.92 | 10917.17 | 0 | 0 | 0 | 0
2022111712 | 5 | 0.56059 | 44847.2 | 0 | 0 | 0.27143 | 9500.05 | 0.54716 | 7660.24 | 40000 | 0 | 4847.2 | 4652.85 | 0 | 7660.24 | 12313.09 | 0 | 0 | 0 | 0
2022111713 | 5 | 0.5449 | 43592 | 0 | 0 | 0.25033 | 8761.55 | 0.55435 | 7760.9 | 40000 | 0 | 3592 | 5169.55 | 0 | 7760.9 | 12930.45 | 0 | 0 | 0 | 0
2022111714 | 5 | 0.53418 | 42734.4 | 0 | 0 | 0.24066 | 8423.1 | 0.56504 | 7910.56 | 40000 | 0 | 2734.4 | 5688.7 | 0 | 7910.56 | 13599.26 | 0 | 0 | 0 | 0
2022111715 | 5 | 0.52731 | 42184.8 | 0 | 0 | 0.22458 | 7860.3 | 0.59059 | 8268.26 | 40000 | 0 | 2184.8 | 5675.5 | 0 | 8268.26 | 13943.76 | 0 | 0 | 0 | 0
2022111716 | 5 | 0.52578 | 42062.4 | 0 | 0 | 0.20563 | 7197.05 | 0.54573 | 7640.22 | 40000 | 0 | 2062.4 | 5134.65 | 0 | 7640.22 | 12774.87 | 0 | 0 | 0 | 0
2022111717 | 5 | 0.53488 | 42790.4 | 0 | 0 | 0.19511 | 6828.85 | 0.33981 | 4757.34 | 40000 | 0 | 2790.4 | 4038.45 | 0 | 4757.34 | 8795.79 | 0 | 0 | 0 | 0
2022111718 | 5 | 0.5603 | 44824 | 0 | 0 | 0.1842 | 6447 | 0.04205 | 588.7 | 40000 | 0 | 4824 | 1623 | 0 | 588.7 | 2211.7 | 0 | 0 | 0 | 0
2022111719 | 5 | 0.57663 | 46130.4 | 0 | 0 | 0.20449 | 7157.15 | 0 | 0 | 40000 | 0 | 6130.4 | 1026.75 | 0 | 0 | 1026.75 | 0 | 0 | 0 | 0
2022111720 | 5 | 0.57872 | 46297.6 | 0 | 0 | 0.2422 | 8477 | 0 | 0 | 40000 | 0 | 6297.6 | 2179.4 | 0 | 0 | 2179.4 | 0 | 0 | 0 | 0
2022111721 | 5 | 0.57492 | 45993.6 | 0 | 0 | 0.2977 | 10419.5 | 0 | 0 | 40000 | 0 | 5993.6 | 4425.9 | 0 | 0 | 4425.9 | 0 | 0 | 0 | 0
2022111722 | 5 | 0.56527 | 45221.6 | 0 | 0 | 0.35797 | 12528.95 | 0 | 0 | 40000 | 0 | 5221.6 | 7307.35 | 0 | 0 | 7307.35 | 0 | 0 | 0 | 0
2022111723 | 5 | 0.54505 | 43604 | 0 | 0 | 0.40217 | 14075.95 | 0 | 0 | 40000 | 0 | 3604 | 10471.95 | 0 | 0 | 10471.95 | 0 | 0 | 0 | 0
2022111724 | 5 | 0.5244 | 41952 | 0 | 0 | 0.43425 | 15198.75 | 0 | 0 | 40000 | 0 | 1952 | 13246.75 | 0 | 0 | 13246.75 | 0 | 0 | 0 | 0
2022111801 | 6 | 0.51067 | 40853.6 | 0 | 0 | 0.45979 | 16092.65 | 0 | 0 | 40000 | 0 | 853.6 | 15239.05 | 0 | 0 | 15239.05 | 0 | 0 | 0 | 0
2022111802 | 6 | 0.50403 | 40322.4 | 0 | 0 | 0.45609 | 15963.15 | 0 | 0 | 40000 | 0 | 322.4 | 15640.75 | 0 | 0 | 15640.75 | 0 | 0 | 0 | 0
2022111803 | 6 | 0.50155 | 40124 | 0 | 0 | 0.42298 | 14804.3 | 0 | 0 | 40000 | 0 | 124 | 14680.3 | 0 | 0 | 14680.3 | 0 | 0 | 0 | 0
2022111804 | 6 | 0.50544 | 40435.2 | 0 | 0 | 0.3941 | 13793.5 | 0 | 0 | 40000 | 0 | 435.2 | 13358.3 | 0 | 0 | 13358.3 | 0 | 0 | 0 | 0
2022111805 | 6 | 0.51976 | 41580.8 | 0 | 0 | 0.38843 | 13595.05 | 0 | 0 | 40000 | 0 | 1580.8 | 12014.25 | 0 | 0 | 12014.25 | 0 | 0 | 0 | 0
2022111806 | 6 | 0.55075 | 44060 | 0 | 0 | 0.3911 | 13688.5 | 0 | 0 | 40000 | 0 | 4060 | 9628.5 | 0 | 0 | 9628.5 | 0 | 0 | 0 | 0
2022111807 | 6 | 0.59546 | 47636.8 | 0 | 0 | 0.39355 | 13774.25 | 5e-05 | 0.7 | 40000 | 0 | 7636.8 | 6137.45 | 0 | 0.7 | 6138.15 | 0 | 0 | 0 | 0
2022111808 | 6 | 0.61203 | 48962.4 | 0 | 0 | 0.37782 | 13223.7 | 0.02125 | 297.5 | 40000 | 0 | 8962.4 | 4261.3 | 0 | 297.5 | 4558.8 | 0 | 0 | 0 | 0
2022111809 | 6 | 0.60949 | 48759.2 | 0 | 0 | 0.3669 | 12841.5 | 0.16773 | 2348.22 | 40000 | 0 | 8759.2 | 4082.3 | 0 | 2348.22 | 6430.52 | 0 | 0 | 0 | 0
2022111810 | 6 | 0.60242 | 48193.6 | 0 | 0 | 0.37491 | 13121.85 | 0.29267 | 4097.38 | 40000 | 0 | 8193.6 | 4928.25 | 0 | 4097.38 | 9025.63 | 0 | 0 | 0 | 0
2022111811 | 6 | 0.58919 | 47135.2 | 0 | 0 | 0.34876 | 12206.6 | 0.33111 | 4635.54 | 40000 | 0 | 7135.2 | 5071.4 | 0 | 4635.54 | 9706.94 | 0 | 0 | 0 | 0
2022111812 | 6 | 0.57795 | 46236 | 0 | 0 | 0.31133 | 10896.55 | 0.37217 | 5210.38 | 40000 | 0 | 6236 | 4660.55 | 0 | 5210.38 | 9870.93 | 0 | 0 | 0 | 0
2022111813 | 6 | 0.56567 | 45253.6 | 0 | 0 | 0.2812 | 9842 | 0.38133 | 5338.62 | 40000 | 0 | 5253.6 | 4588.4 | 0 | 5338.62 | 9927.02 | 0 | 0 | 0 | 0
2022111814 | 6 | 0.56194 | 44955.2 | 0 | 0 | 0.25804 | 9031.4 | 0.34856 | 4879.84 | 40000 | 0 | 4955.2 | 4076.2 | 0 | 4879.84 | 8956.04 | 0 | 0 | 0 | 0
2022111815 | 6 | 0.55954 | 44763.2 | 0 | 0 | 0.27566 | 9648.1 | 0.30156 | 4221.84 | 40000 | 0 | 4763.2 | 4884.9 | 0 | 4221.84 | 9106.74 | 0 | 0 | 0 | 0
2022111816 | 6 | 0.56112 | 44889.6 | 0 | 0 | 0.30388 | 10635.8 | 0.21764 | 3046.96 | 40000 | 0 | 4889.6 | 5746.2 | 0 | 3046.96 | 8793.16 | 0 | 0 | 0 | 0
2022111817 | 6 | 0.57071 | 45656.8 | 0 | 0 | 0.3241 | 11343.5 | 0.1242 | 1738.8 | 40000 | 0 | 5656.8 | 5686.7 | 0 | 1738.8 | 7425.5 | 0 | 0 | 0 | 0
2022111818 | 6 | 0.59453 | 47562.4 | 0 | 0 | 0.32722 | 11452.7 | 0.01447 | 202.58 | 40000 | 0 | 7562.4 | 3890.3 | 0 | 202.58 | 4092.88 | 0 | 0 | 0 | 0
2022111819 | 6 | 0.60029 | 48023.2 | 0 | 0 | 0.29863 | 10452.05 | 5e-05 | 0.7 | 40000 | 0 | 8023.2 | 2428.85 | 0 | 0.7 | 2429.55 | 0 | 0 | 0 | 0
2022111820 | 6 | 0.597 | 47760 | 0 | 0 | 0.272 | 9520 | 0.00012 | 1.68 | 40000 | 0 | 7760 | 1760 | 0 | 1.68 | 1761.68 | 0 | 0 | 0 | 0
2022111821 | 6 | 0.59315 | 47452 | 0 | 0 | 0.25748 | 9011.8 | 6e-05 | 0.84 | 40000 | 0 | 7452 | 1559.8 | 0 | 0.84 | 1560.64 | 0 | 0 | 0 | 0
2022111822 | 6 | 0.58311 | 46648.8 | 0 | 0 | 0.23603 | 8261.05 | 0 | 0 | 40000 | 0 | 6648.8 | 1612.25 | 0 | 0 | 1612.25 | 0 | 0 | 0 | 0
2022111823 | 6 | 0.56547 | 45237.6 | 0 | 0 | 0.22994 | 8047.9 | 0 | 0 | 40000 | 0 | 5237.6 | 2810.3 | 0 | 0 | 2810.3 | 0 | 0 | 0 | 0
2022111824 | 6 | 0.54682 | 43745.6 | 0 | 0 | 0.22609 | 7913.15 | 0 | 0 | 40000 | 0 | 3745.6 | 4167.55 | 0 | 0 | 4167.55 | 0 | 0 | 0 | 0
2022111901 | 7 | 0.5331 | 42648 | 0 | 0 | 0.22774 | 7970.9 | 0 | 0 | 40000 | 0 | 2648 | 5322.9 | 0 | 0 | 5322.9 | 0 | 0 | 0 | 0
2022111902 | 7 | 0.52653 | 42122.4 | 0 | 0 | 0.22918 | 8021.3 | 0 | 0 | 40000 | 0 | 2122.4 | 5898.9 | 0 | 0 | 5898.9 | 0 | 0 | 0 | 0
2022111903 | 7 | 0.52694 | 42155.2 | 0 | 0 | 0.22718 | 7951.3 | 0 | 0 | 40000 | 0 | 2155.2 | 5796.1 | 0 | 0 | 5796.1 | 0 | 0 | 0 | 0
2022111904 | 7 | 0.53063 | 42450.4 | 0 | 0 | 0.2226 | 7791 | 0 | 0 | 40000 | 0 | 2450.4 | 5340.6 | 0 | 0 | 5340.6 | 0 | 0 | 0 | 0
2022111905 | 7 | 0.53921 | 43136.8 | 0 | 0 | 0.22395 | 7838.25 | 0 | 0 | 40000 | 0 | 3136.8 | 4701.45 | 0 | 0 | 4701.45 | 0 | 0 | 0 | 0
2022111906 | 7 | 0.55376 | 44300.8 | 0 | 0 | 0.2231 | 7808.5 | 0 | 0 | 40000 | 0 | 4300.8 | 3507.7 | 0 | 0 | 3507.7 | 0 | 0 | 0 | 0
2022111907 | 7 | 0.5722 | 45776 | 0 | 0 | 0.22646 | 7926.1 | 0 | 0 | 40000 | 0 | 5776 | 2150.1 | 0 | 0 | 2150.1 | 0 | 0 | 0 | 0
2022111908 | 7 | 0.59574 | 47659.2 | 0 | 0 | 0.22814 | 7984.9 | 0.00449 | 62.86 | 40000 | 0 | 7659.2 | 325.7 | 0 | 62.86 | 388.56 | 0 | 0 | 0 | 0
2022111909 | 7 | 0.61949 | 49559.2 | 0 | 0 | 0.21957 | 7684.95 | 0.03066 | 429.24 | 40000 | 0 | 7684.95 | 0 | 429.24 | 0 | 0 | 1445.01 | 0 | 0 | 1445.01
2022111910 | 7 | 0.63822 | 51057.6 | 0 | 0 | 0.23799 | 8329.65 | 0.05911 | 827.54 | 40000 | 0 | 8329.65 | 0 | 827.54 | 0 | 0 | 1900.41 | 0 | 0 | 1900.41
2022111911 | 7 | 0.64625 | 51700 | 0 | 0 | 0.25226 | 8829.1 | 0.0977 | 1367.8 | 40000 | 0 | 8829.1 | 0 | 1367.8 | 0 | 0 | 1503.1 | 0 | 0 | 1503.1
2022111912 | 7 | 0.64747 | 51797.6 | 0 | 0 | 0.26068 | 9123.8 | 0.14016 | 1962.24 | 40000 | 0 | 9123.8 | 0 | 1962.24 | 0 | 0 | 711.56 | 0 | 0 | 711.56
2022111913 | 7 | 0.64219 | 51375.2 | 0 | 0 | 0.27433 | 9601.55 | 0.16901 | 2366.14 | 40000 | 0 | 9601.55 | 0 | 1773.65 | 592.49 | 592.49 | 0 | 0 | 0 | 0
2022111914 | 7 | 0.63344 | 50675.2 | 0 | 0 | 0.25461 | 8911.35 | 0.19191 | 2686.74 | 40000 | 0 | 8911.35 | 0 | 1763.85 | 922.89 | 922.89 | 0 | 0 | 0 | 0
2022111915 | 7 | 0.62234 | 49787.2 | 0 | 0 | 0.23897 | 8363.95 | 0.20181 | 2825.34 | 40000 | 0 | 8363.95 | 0 | 1423.25 | 1402.09 | 1402.09 | 0 | 0 | 0 | 0
2022111916 | 7 | 0.61831 | 49464.8 | 0 | 0 | 0.21849 | 7647.15 | 0.15885 | 2223.9 | 40000 | 0 | 7647.15 | 0 | 1817.65 | 406.25 | 406.25 | 0 | 0 | 0 | 0
2022111917 | 7 | 0.62212 | 49769.6 | 0 | 0 | 0.19155 | 6704.25 | 0.07524 | 1053.36 | 40000 | 0 | 6704.25 | 0 | 1053.36 | 0 | 0 | 2011.99 | 0 | 0 | 2011.99
2022111918 | 7 | 0.64299 | 51439.2 | 0 | 0 | 0.16936 | 5927.6 | 0.0064 | 89.6 | 40000 | 0 | 5927.6 | 0 | 89.6 | 0 | 0 | 5422 | 0 | 0 | 5422
2022111919 | 7 | 0.65275 | 52220 | 0 | 0 | 0.16201 | 5670.35 | 0 | 0 | 40000 | 0 | 5670.35 | 0 | 0 | 0 | 0 | 6549.65 | 0 | 0 | 6549.65
2022111920 | 7 | 0.65033 | 52026.4 | 0 | 0 | 0.15999 | 5599.65 | 0 | 0 | 40000 | 0 | 5599.65 | 0 | 0 | 0 | 0 | 6426.75 | 0 | 0 | 6426.75
2022111921 | 7 | 0.64504 | 51603.2 | 0 | 0 | 0.16097 | 5633.95 | 0 | 0 | 40000 | 0 | 5633.95 | 0 | 0 | 0 | 0 | 5969.25 | 0 | 0 | 5969.25
2022111922 | 7 | 0.63427 | 50741.6 | 0 | 0 | 0.1589 | 5561.5 | 4e-05 | 0.56 | 40000 | 0 | 5561.5 | 0 | 0.56 | 0 | 0 | 5179.54 | 0 | 0 | 5179.54
2022111923 | 7 | 0.61846 | 49476.8 | 0 | 0 | 0.15564 | 5447.4 | 0 | 0 | 40000 | 0 | 5447.4 | 0 | 0 | 0 | 0 | 4029.4 | 0 | 0 | 4029.4
2022111924 | 7 | 0.60135 | 48108 | 0 | 0 | 0.16088 | 5630.8 | 0 | 0 | 40000 | 0 | 5630.8 | 0 | 0 | 0 | 0 | 2477.2 | 0 | 0 | 2477.2
2022112001 | 1 | 0.58798 | 47038.4 | 0 | 0 | 0.15922 | 5572.7 | 0 | 0 | 40000 | 0 | 5572.7 | 0 | 0 | 0 | 0 | 1465.7 | 0 | 0 | 1465.7
2022112002 | 1 | 0.58323 | 46658.4 | 0 | 0 | 0.16561 | 5796.35 | 0 | 0 | 40000 | 0 | 5796.35 | 0 | 0 | 0 | 0 | 862.05 | 0 | 0 | 862.05
2022112003 | 1 | 0.57983 | 46386.4 | 0 | 0 | 0.17127 | 5994.45 | 0 | 0 | 40000 | 0 | 5994.45 | 0 | 0 | 0 | 0 | 391.95 | 0 | 0 | 391.95
2022112004 | 1 | 0.58172 | 46537.6 | 0 | 0 | 0.16737 | 5857.95 | 0 | 0 | 40000 | 0 | 5857.95 | 0 | 0 | 0 | 0 | 679.65 | 0 | 0 | 679.65
2022112005 | 1 | 0.58837 | 47069.6 | 0 | 0 | 0.16603 | 5811.05 | 4e-05 | 0.56 | 40000 | 0 | 5811.05 | 0 | 0.56 | 0 | 0 | 1257.99 | 0 | 0 | 1257.99
2022112006 | 1 | 0.60415 | 48332 | 0 | 0 | 0.15648 | 5476.8 | 0 | 0 | 40000 | 0 | 5476.8 | 0 | 0 | 0 | 0 | 2855.2 | 0 | 0 | 2855.2
2022112007 | 1 | 0.62235 | 49788 | 0 | 0 | 0.15059 | 5270.65 | 6e-05 | 0.84 | 40000 | 0 | 5270.65 | 0 | 0.84 | 0 | 0 | 4516.51 | 0 | 0 | 4516.51
2022112008 | 1 | 0.6369 | 50952 | 0 | 0 | 0.15492 | 5422.2 | 0.0316 | 442.4 | 40000 | 0 | 5422.2 | 0 | 442.4 | 0 | 0 | 5087.4 | 0 | 0 | 5087.4
2022112009 | 1 | 0.63813 | 51050.4 | 0 | 0 | 0.15411 | 5393.85 | 0.16833 | 2356.62 | 40000 | 0 | 5393.85 | 0 | 2356.62 | 0 | 0 | 3299.93 | 0 | 0 | 3299.93
2022112010 | 1 | 0.62945 | 50356 | 0 | 0 | 0.14192 | 4967.2 | 0.26227 | 3671.78 | 40000 | 0 | 4967.2 | 0 | 3671.78 | 0 | 0 | 1717.02 | 0 | 0 | 1717.02
2022112011 | 1 | 0.61134 | 48907.2 | 0 | 0 | 0.16735 | 5857.25 | 0.27257 | 3815.98 | 40000 | 0 | 5857.25 | 0 | 3049.95 | 766.03 | 766.03 | 0 | 0 | 0 | 0
2022112012 | 1 | 0.59348 | 47478.4 | 0 | 0 | 0.18327 | 6414.45 | 0.28373 | 3972.22 | 40000 | 0 | 6414.45 | 0 | 1063.95 | 2908.27 | 2908.27 | 0 | 0 | 0 | 0
2022112013 | 1 | 0.58039 | 46431.2 | 0 | 0 | 0.16534 | 5786.9 | 0.29569 | 4139.66 | 40000 | 0 | 5786.9 | 0 | 644.3 | 3495.36 | 3495.36 | 0 | 0 | 0 | 0
2022112014 | 1 | 0.57255 | 45804 | 0 | 0 | 0.16002 | 5600.7 | 0.25894 | 3625.16 | 40000 | 0 | 5600.7 | 0 | 203.3 | 3421.86 | 3421.86 | 0 | 0 | 0 | 0
2022112015 | 1 | 0.57095 | 45676 | 0 | 0 | 0.15361 | 5376.35 | 0.21864 | 3060.96 | 40000 | 0 | 5376.35 | 0 | 299.65 | 2761.31 | 2761.31 | 0 | 0 | 0 | 0
2022112016 | 1 | 0.57099 | 45679.2 | 0 | 0 | 0.15295 | 5353.25 | 0.15332 | 2146.48 | 40000 | 0 | 5353.25 | 0 | 325.95 | 1820.53 | 1820.53 | 0 | 0 | 0 | 0
2022112017 | 1 | 0.58025 | 46420 | 0 | 0 | 0.15458 | 5410.3 | 0.07477 | 1046.78 | 40000 | 0 | 5410.3 | 0 | 1009.7 | 37.08 | 37.08 | 0 | 0 | 0 | 0
2022112018 | 1 | 0.59867 | 47893.6 | 0 | 0 | 0.16418 | 5746.3 | 0.00847 | 118.58 | 40000 | 0 | 5746.3 | 0 | 118.58 | 0 | 0 | 2028.72 | 0 | 0 | 2028.72
2022112019 | 1 | 0.61174 | 48939.2 | 0 | 0 | 0.20675 | 7236.25 | 0 | 0 | 40000 | 0 | 7236.25 | 0 | 0 | 0 | 0 | 1702.95 | 0 | 0 | 1702.95
2022112020 | 1 | 0.61141 | 48912.8 | 0 | 0 | 0.24826 | 8689.1 | 0 | 0 | 40000 | 0 | 8689.1 | 0 | 0 | 0 | 0 | 223.7 | 0 | 0 | 223.7
2022112021 | 1 | 0.60599 | 48479.2 | 0 | 0 | 0.25546 | 8941.1 | 4e-05 | 0.56 | 40000 | 0 | 8479.2 | 461.9 | 0 | 0.56 | 462.46 | 0 | 0 | 0 | 0
2022112022 | 1 | 0.59281 | 47424.8 | 0 | 0 | 0.25796 | 9028.6 | 0 | 0 | 40000 | 0 | 7424.8 | 1603.8 | 0 | 0 | 1603.8 | 0 | 0 | 0 | 0
2022112023 | 1 | 0.57288 | 45830.4 | 0 | 0 | 0.26583 | 9304.05 | 0 | 0 | 40000 | 0 | 5830.4 | 3473.65 | 0 | 0 | 3473.65 | 0 | 0 | 0 | 0
2022112024 | 1 | 0.55257 | 44205.6 | 0 | 0 | 0.28021 | 9807.35 | 0 | 0 | 40000 | 0 | 4205.6 | 5601.75 | 0 | 0 | 5601.75 | 0 | 0 | 0 | 0
2022112101 | 2 | 0.53838 | 43070.4 | 0 | 0 | 0.27846 | 9746.1 | 0 | 0 | 40000 | 0 | 3070.4 | 6675.7 | 0 | 0 | 6675.7 | 0 | 0 | 0 | 0
2022112102 | 2 | 0.53364 | 42691.2 | 0 | 0 | 0.28035 | 9812.25 | 0 | 0 | 40000 | 0 | 2691.2 | 7121.05 | 0 | 0 | 7121.05 | 0 | 0 | 0 | 0
2022112103 | 2 | 0.52918 | 42334.4 | 0 | 0 | 0.26336 | 9217.6 | 0 | 0 | 40000 | 0 | 2334.4 | 6883.2 | 0 | 0 | 6883.2 | 0 | 0 | 0 | 0
2022112104 | 2 | 0.53192 | 42553.6 | 0 | 0 | 0.23867 | 8353.45 | 0 | 0 | 40000 | 0 | 2553.6 | 5799.85 | 0 | 0 | 5799.85 | 0 | 0 | 0 | 0
2022112105 | 2 | 0.54449 | 43559.2 | 0 | 0 | 0.22166 | 7758.1 | 0 | 0 | 40000 | 0 | 3559.2 | 4198.9 | 0 | 0 | 4198.9 | 0 | 0 | 0 | 0
2022112106 | 2 | 0.56817 | 45453.6 | 0 | 0 | 0.20573 | 7200.55 | 0 | 0 | 40000 | 0 | 5453.6 | 1746.95 | 0 | 0 | 1746.95 | 0 | 0 | 0 | 0
2022112107 | 2 | 0.6003 | 48024 | 0 | 0 | 0.18575 | 6501.25 | 0 | 0 | 40000 | 0 | 6501.25 | 0 | 0 | 0 | 0 | 1522.75 | 0 | 0 | 1522.75
2022112108 | 2 | 0.62489 | 49991.2 | 0 | 0 | 0.16792 | 5877.2 | 0.00943 | 132.02 | 40000 | 0 | 5877.2 | 0 | 132.02 | 0 | 0 | 3981.98 | 0 | 0 | 3981.98
2022112109 | 2 | 0.63508 | 50806.4 | 0 | 0 | 0.15384 | 5384.4 | 0.12033 | 1684.62 | 40000 | 0 | 5384.4 | 0 | 1684.62 | 0 | 0 | 3737.38 | 0 | 0 | 3737.38
2022112110 | 2 | 0.64098 | 51278.4 | 0 | 0 | 0.12981 | 4543.35 | 0.23271 | 3257.94 | 40000 | 0 | 4543.35 | 0 | 3257.94 | 0 | 0 | 3477.11 | 0 | 0 | 3477.11
2022112111 | 2 | 0.64142 | 51313.6 | 0 | 0 | 0.11233 | 3931.55 | 0.34665 | 4853.1 | 40000 | 0 | 3931.55 | 0 | 4853.1 | 0 | 0 | 2528.95 | 0 | 0 | 2528.95
2022112112 | 2 | 0.63738 | 50990.4 | 0 | 0 | 0.10961 | 3836.35 | 0.40518 | 5672.52 | 40000 | 0 | 3836.35 | 0 | 5672.52 | 0 | 0 | 1481.53 | 0 | 0 | 1481.53
2022112113 | 2 | 0.62802 | 50241.6 | 0 | 0 | 0.12002 | 4200.7 | 0.4281 | 5993.4 | 40000 | 0 | 4200.7 | 0 | 5993.4 | 0 | 0 | 47.5 | 0 | 0 | 47.5
2022112114 | 2 | 0.62161 | 49728.8 | 0 | 0 | 0.12812 | 4484.2 | 0.41922 | 5869.08 | 40000 | 0 | 4484.2 | 0 | 5244.6 | 624.48 | 624.48 | 0 | 0 | 0 | 0
2022112115 | 2 | 0.61617 | 49293.6 | 0 | 0 | 0.13173 | 4610.55 | 0.41407 | 5796.98 | 40000 | 0 | 4610.55 | 0 | 4683.05 | 1113.93 | 1113.93 | 0 | 0 | 0 | 0
2022112116 | 2 | 0.61194 | 48955.2 | 0 | 0 | 0.1307 | 4574.5 | 0.39652 | 5551.28 | 40000 | 0 | 4574.5 | 0 | 4380.7 | 1170.58 | 1170.58 | 0 | 0 | 0 | 0
2022112117 | 2 | 0.6149 | 49192 | 0 | 0 | 0.13095 | 4583.25 | 0.27126 | 3797.64 | 40000 | 0 | 4583.25 | 0 | 3797.64 | 0 | 0 | 811.11 | 0 | 0 | 811.11
2022112118 | 2 | 0.63254 | 50603.2 | 0 | 0 | 0.15812 | 5534.2 | 0.03499 | 489.86 | 40000 | 0 | 5534.2 | 0 | 489.86 | 0 | 0 | 4579.14 | 0 | 0 | 4579.14
2022112119 | 2 | 0.64191 | 51352.8 | 0 | 0 | 0.20937 | 7327.95 | 0 | 0 | 40000 | 0 | 7327.95 | 0 | 0 | 0 | 0 | 4024.85 | 0 | 0 | 4024.85
2022112120 | 2 | 0.63513 | 50810.4 | 0 | 0 | 0.26619 | 9316.65 | 4e-05 | 0.56 | 40000 | 0 | 9316.65 | 0 | 0.56 | 0 | 0 | 1493.19 | 0 | 0 | 1493.19
2022112121 | 2 | 0.62985 | 50388 | 0 | 0 | 0.30102 | 10535.7 | 4e-05 | 0.56 | 40000 | 0 | 10388 | 147.7 | 0 | 0.56 | 148.26 | 0 | 0 | 0 | 0
2022112122 | 2 | 0.61473 | 49178.4 | 0 | 0 | 0.33147 | 11601.45 | 4e-05 | 0.56 | 40000 | 0 | 9178.4 | 2423.05 | 0 | 0.56 | 2423.61 | 0 | 0 | 0 | 0
2022112123 | 2 | 0.58719 | 46975.2 | 0 | 0 | 0.33857 | 11849.95 | 4e-05 | 0.56 | 40000 | 0 | 6975.2 | 4874.75 | 0 | 0.56 | 4875.31 | 0 | 0 | 0 | 0
2022112124 | 2 | 0.56213 | 44970.4 | 0 | 0 | 0.32822 | 11487.7 | 0 | 0 | 40000 | 0 | 4970.4 | 6517.3 | 0 | 0 | 6517.3 | 0 | 0 | 0 | 0
2022112201 | 3 | 0.54621 | 43696.8 | 0 | 0 | 0.31491 | 11021.85 | 0 | 0 | 40000 | 0 | 3696.8 | 7325.05 | 0 | 0 | 7325.05 | 0 | 0 | 0 | 0
2022112202 | 3 | 0.5363 | 42904 | 0 | 0 | 0.28156 | 9854.6 | 0 | 0 | 40000 | 0 | 2904 | 6950.6 | 0 | 0 | 6950.6 | 0 | 0 | 0 | 0
2022112203 | 3 | 0.53096 | 42476.8 | 0 | 0 | 0.26578 | 9302.3 | 0 | 0 | 40000 | 0 | 2476.8 | 6825.5 | 0 | 0 | 6825.5 | 0 | 0 | 0 | 0
2022112204 | 3 | 0.52752 | 42201.6 | 0 | 0 | 0.2559 | 8956.5 | 0 | 0 | 40000 | 0 | 2201.6 | 6754.9 | 0 | 0 | 6754.9 | 0 | 0 | 0 | 0
2022112205 | 3 | 0.53656 | 42924.8 | 0 | 0 | 0.24145 | 8450.75 | 0 | 0 | 40000 | 0 | 2924.8 | 5525.95 | 0 | 0 | 5525.95 | 0 | 0 | 0 | 0
2022112206 | 3 | 0.55662 | 44529.6 | 0 | 0 | 0.23624 | 8268.4 | 4e-05 | 0.56 | 40000 | 0 | 4529.6 | 3738.8 | 0 | 0.56 | 3739.36 | 0 | 0 | 0 | 0
2022112207 | 3 | 0.5868 | 46944 | 0 | 0 | 0.21913 | 7669.55 | 0 | 0 | 40000 | 0 | 6944 | 725.55 | 0 | 0 | 725.55 | 0 | 0 | 0 | 0
2022112208 | 3 | 0.60683 | 48546.4 | 0 | 0 | 0.2236 | 7826 | 0.01628 | 227.92 | 40000 | 0 | 7826 | 0 | 227.92 | 0 | 0 | 492.48 | 0 | 0 | 492.48
2022112209 | 3 | 0.61185 | 48948 | 0 | 0 | 0.21058 | 7370.3 | 0.21758 | 3046.12 | 40000 | 0 | 7370.3 | 0 | 1577.7 | 1468.42 | 1468.42 | 0 | 0 | 0 | 0
2022112210 | 3 | 0.60899 | 48719.2 | 0 | 0 | 0.14438 | 5053.3 | 0.3907 | 5469.8 | 40000 | 0 | 5053.3 | 0 | 3665.9 | 1803.9 | 1803.9 | 0 | 0 | 0 | 0
2022112211 | 3 | 0.5997 | 47976 | 0 | 0 | 0.12418 | 4346.3 | 0.44793 | 6271.02 | 40000 | 0 | 4346.3 | 0 | 3629.7 | 2641.32 | 2641.32 | 0 | 0 | 0 | 0
2022112212 | 3 | 0.58397 | 46717.6 | 0 | 0 | 0.14089 | 4931.15 | 0.48248 | 6754.72 | 40000 | 0 | 4931.15 | 0 | 1786.45 | 4968.27 | 4968.27 | 0 | 0 | 0 | 0
2022112213 | 3 | 0.56945 | 45556 | 0 | 0 | 0.154 | 5390 | 0.50135 | 7018.9 | 40000 | 0 | 5390 | 0 | 166 | 6852.9 | 6852.9 | 0 | 0 | 0 | 0
2022112214 | 3 | 0.56027 | 44821.6 | 0 | 0 | 0.1565 | 5477.5 | 0.49652 | 6951.28 | 40000 | 0 | 4821.6 | 655.9 | 0 | 6951.28 | 7607.18 | 0 | 0 | 0 | 0
2022112215 | 3 | 0.55351 | 44280.8 | 0 | 0 | 0.17229 | 6030.15 | 0.49611 | 6945.54 | 40000 | 0 | 4280.8 | 1749.35 | 0 | 6945.54 | 8694.89 | 0 | 0 | 0 | 0
2022112216 | 3 | 0.54868 | 43894.4 | 0 | 0 | 0.18158 | 6355.3 | 0.43133 | 6038.62 | 40000 | 0 | 3894.4 | 2460.9 | 0 | 6038.62 | 8499.52 | 0 | 0 | 0 | 0
2022112217 | 3 | 0.54845 | 43876 | 0 | 0 | 0.18278 | 6397.3 | 0.24357 | 3409.98 | 40000 | 0 | 3876 | 2521.3 | 0 | 3409.98 | 5931.28 | 0 | 0 | 0 | 0
2022112218 | 3 | 0.56561 | 45248.8 | 0 | 0 | 0.19488 | 6820.8 | 0.02961 | 414.54 | 40000 | 0 | 5248.8 | 1572 | 0 | 414.54 | 1986.54 | 0 | 0 | 0 | 0
2022112219 | 3 | 0.57727 | 46181.6 | 0 | 0 | 0.25377 | 8881.95 | 0 | 0 | 40000 | 0 | 6181.6 | 2700.35 | 0 | 0 | 2700.35 | 0 | 0 | 0 | 0
2022112220 | 3 | 0.57663 | 46130.4 | 0 | 0 | 0.32152 | 11253.2 | 0 | 0 | 40000 | 0 | 6130.4 | 5122.8 | 0 | 0 | 5122.8 | 0 | 0 | 0 | 0
2022112221 | 3 | 0.57213 | 45770.4 | 0 | 0 | 0.35563 | 12447.05 | 0 | 0 | 40000 | 0 | 5770.4 | 6676.65 | 0 | 0 | 6676.65 | 0 | 0 | 0 | 0
2022112222 | 3 | 0.56025 | 44820 | 0 | 0 | 0.36482 | 12768.7 | 0 | 0 | 40000 | 0 | 4820 | 7948.7 | 0 | 0 | 7948.7 | 0 | 0 | 0 | 0
2022112223 | 3 | 0.53929 | 43143.2 | 0 | 0 | 0.34851 | 12197.85 | 0 | 0 | 40000 | 0 | 3143.2 | 9054.65 | 0 | 0 | 9054.65 | 0 | 0 | 0 | 0
2022112224 | 3 | 0.51836 | 41468.8 | 0 | 0 | 0.32214 | 11274.9 | 0 | 0 | 40000 | 0 | 1468.8 | 9806.1 | 0 | 0 | 9806.1 | 0 | 0 | 0 | 0
2022112301 | 4 | 0.49893 | 39914.4 | 0 | 0 | 0.3181 | 11133.5 | 0 | 0 | 39914.4 | 85.6 | 0 | 11133.5 | 0 | 0 | 11219.1 | 0 | 0 | 0 | 0
2022112302 | 4 | 0.48752 | 39001.6 | 0 | 0 | 0.29328 | 10264.8 | 0 | 0 | 39001.6 | 998.4 | 0 | 10264.8 | 0 | 0 | 11263.2 | 0 | 0 | 0 | 0
2022112303 | 4 | 0.47931 | 38344.8 | 0 | 0 | 0.24804 | 8681.4 | 0 | 0 | 38344.8 | 1655.2 | 0 | 8681.4 | 0 | 0 | 10336.6 | 0 | 0 | 0 | 0
2022112304 | 4 | 0.47666 | 38132.8 | 0 | 0 | 0.21513 | 7529.55 | 0 | 0 | 38132.8 | 1867.2 | 0 | 7529.55 | 0 | 0 | 9396.75 | 0 | 0 | 0 | 0
2022112305 | 4 | 0.48568 | 38854.4 | 0 | 0 | 0.20451 | 7157.85 | 0 | 0 | 38854.4 | 1145.6 | 0 | 7157.85 | 0 | 0 | 8303.45 | 0 | 0 | 0 | 0
2022112306 | 4 | 0.50455 | 40364 | 0 | 0 | 0.21603 | 7561.05 | 0 | 0 | 40000 | 0 | 364 | 7197.05 | 0 | 0 | 7197.05 | 0 | 0 | 0 | 0
2022112307 | 4 | 0.53086 | 42468.8 | 0 | 0 | 0.21825 | 7638.75 | 4e-05 | 0.56 | 40000 | 0 | 2468.8 | 5169.95 | 0 | 0.56 | 5170.51 | 0 | 0 | 0 | 0
2022112308 | 4 | 0.54503 | 43602.4 | 0 | 0 | 0.21706 | 7597.1 | 0.02206 | 308.84 | 40000 | 0 | 3602.4 | 3994.7 | 0 | 308.84 | 4303.54 | 0 | 0 | 0 | 0
2022112309 | 4 | 0.55106 | 44084.8 | 0 | 0 | 0.20877 | 7306.95 | 0.10627 | 1487.78 | 40000 | 0 | 4084.8 | 3222.15 | 0 | 1487.78 | 4709.93 | 0 | 0 | 0 | 0
2022112310 | 4 | 0.55593 | 44474.4 | 0 | 0 | 0.19882 | 6958.7 | 0.17148 | 2400.72 | 40000 | 0 | 4474.4 | 2484.3 | 0 | 2400.72 | 4885.02 | 0 | 0 | 0 | 0
2022112311 | 4 | 0.55504 | 44403.2 | 0 | 0 | 0.21455 | 7509.25 | 0.23717 | 3320.38 | 40000 | 0 | 4403.2 | 3106.05 | 0 | 3320.38 | 6426.43 | 0 | 0 | 0 | 0
2022112312 | 4 | 0.55382 | 44305.6 | 0 | 0 | 0.2537 | 8879.5 | 0.31195 | 4367.3 | 40000 | 0 | 4305.6 | 4573.9 | 0 | 4367.3 | 8941.2 | 0 | 0 | 0 | 0
2022112313 | 4 | 0.54787 | 43829.6 | 0 | 0 | 0.27614 | 9664.9 | 0.35574 | 4980.36 | 40000 | 0 | 3829.6 | 5835.3 | 0 | 4980.36 | 10815.66 | 0 | 0 | 0 | 0
2022112314 | 4 | 0.54377 | 43501.6 | 0 | 0 | 0.28614 | 10014.9 | 0.35289 | 4940.46 | 40000 | 0 | 3501.6 | 6513.3 | 0 | 4940.46 | 11453.76 | 0 | 0 | 0 | 0
2022112315 | 4 | 0.54175 | 43340 | 0 | 0 | 0.29358 | 10275.3 | 0.35079 | 4911.06 | 40000 | 0 | 3340 | 6935.3 | 0 | 4911.06 | 11846.36 | 0 | 0 | 0 | 0
2022112316 | 4 | 0.53821 | 43056.8 | 0 | 0 | 0.30349 | 10622.15 | 0.34457 | 4823.98 | 40000 | 0 | 3056.8 | 7565.35 | 0 | 4823.98 | 12389.33 | 0 | 0 | 0 | 0
2022112317 | 4 | 0.54018 | 43214.4 | 0 | 0 | 0.32218 | 11276.3 | 0.20086 | 2812.04 | 40000 | 0 | 3214.4 | 8061.9 | 0 | 2812.04 | 10873.94 | 0 | 0 | 0 | 0
2022112318 | 4 | 0.54977 | 43981.6 | 0 | 0 | 0.34785 | 12174.75 | 0.02971 | 415.94 | 40000 | 0 | 3981.6 | 8193.15 | 0 | 415.94 | 8609.09 | 0 | 0 | 0 | 0
2022112319 | 4 | 0.55539 | 44431.2 | 0 | 0 | 0.39677 | 13886.95 | 0 | 0 | 40000 | 0 | 4431.2 | 9455.75 | 0 | 0 | 9455.75 | 0 | 0 | 0 | 0
2022112320 | 4 | 0.55042 | 44033.6 | 0 | 0 | 0.44319 | 15511.65 | 0 | 0 | 40000 | 0 | 4033.6 | 11478.05 | 0 | 0 | 11478.05 | 0 | 0 | 0 | 0
2022112321 | 4 | 0.54304 | 43443.2 | 0 | 0 | 0.48251 | 16887.85 | 0 | 0 | 40000 | 0 | 3443.2 | 13444.65 | 0 | 0 | 13444.65 | 0 | 0 | 0 | 0
2022112322 | 4 | 0.53273 | 42618.4 | 0 | 0 | 0.4868 | 17038 | 0 | 0 | 40000 | 0 | 2618.4 | 14419.6 | 0 | 0 | 14419.6 | 0 | 0 | 0 | 0
2022112323 | 4 | 0.51122 | 40897.6 | 0 | 0 | 0.46622 | 16317.7 | 0 | 0 | 40000 | 0 | 897.6 | 15420.1 | 0 | 0 | 15420.1 | 0 | 0 | 0 | 0
2022112324 | 4 | 0.4872 | 38976 | 0 | 0 | 0.43242 | 15134.7 | 0 | 0 | 38976 | 1024 | 0 | 15134.7 | 0 | 0 | 16158.7 | 0 | 0 | 0 | 0
2022112401 | 5 | 0.46369 | 37095.2 | 0 | 0 | 0.3921 | 13723.5 | 0 | 0 | 37095.2 | 2904.8 | 0 | 13723.5 | 0 | 0 | 16628.3 | 0 | 0 | 0 | 0
2022112402 | 5 | 0.44982 | 35985.6 | 0 | 0 | 0.34518 | 12081.3 | 0 | 0 | 35985.6 | 4014.4 | 0 | 12081.3 | 0 | 0 | 16095.7 | 0 | 0 | 0 | 0
2022112403 | 5 | 0.43871 | 35096.8 | 0 | 0 | 0.32314 | 11309.9 | 0 | 0 | 35096.8 | 4903.2 | 0 | 11309.9 | 0 | 0 | 16213.1 | 0 | 0 | 0 | 0
2022112404 | 5 | 0.42997 | 34397.6 | 0 | 0 | 0.29299 | 10254.65 | 0 | 0 | 34397.6 | 5602.4 | 0 | 10254.65 | 0 | 0 | 15857.05 | 0 | 0 | 0 | 0
2022112405 | 5 | 0.4305 | 34440 | 0 | 0 | 0.26236 | 9182.6 | 0 | 0 | 34440 | 5560 | 0 | 9182.6 | 0 | 0 | 14742.6 | 0 | 0 | 0 | 0
2022112406 | 5 | 0.43958 | 35166.4 | 0 | 0 | 0.23421 | 8197.35 | 0 | 0 | 35166.4 | 4833.6 | 0 | 8197.35 | 0 | 0 | 13030.95 | 0 | 0 | 0 | 0
2022112407 | 5 | 0.4545 | 36360 | 0 | 0 | 0.20998 | 7349.3 | 0 | 0 | 36360 | 3640 | 0 | 7349.3 | 0 | 0 | 10989.3 | 0 | 0 | 0 | 0
2022112408 | 5 | 0.46553 | 37242.4 | 0 | 0 | 0.1796 | 6286 | 0.007 | 98 | 37242.4 | 2757.6 | 0 | 6286 | 0 | 98 | 9141.6 | 0 | 0 | 0 | 0
2022112409 | 5 | 0.4865 | 38920 | 0 | 0 | 0.16547 | 5791.45 | 0.12496 | 1749.44 | 38920 | 1080 | 0 | 5791.45 | 0 | 1749.44 | 8620.89 | 0 | 0 | 0 | 0
2022112410 | 5 | 0.51262 | 41009.6 | 0 | 0 | 0.16462 | 5761.7 | 0.20983 | 2937.62 | 40000 | 0 | 1009.6 | 4752.1 | 0 | 2937.62 | 7689.72 | 0 | 0 | 0 | 0
2022112411 | 5 | 0.52946 | 42356.8 | 0 | 0 | 0.18089 | 6331.15 | 0.25348 | 3548.72 | 40000 | 0 | 2356.8 | 3974.35 | 0 | 3548.72 | 7523.07 | 0 | 0 | 0 | 0
2022112412 | 5 | 0.54025 | 43220 | 0 | 0 | 0.22599 | 7909.65 | 0.26395 | 3695.3 | 40000 | 0 | 3220 | 4689.65 | 0 | 3695.3 | 8384.95 | 0 | 0 | 0 | 0
2022112413 | 5 | 0.54135 | 43308 | 0 | 0 | 0.29611 | 10363.85 | 0.25305 | 3542.7 | 40000 | 0 | 3308 | 7055.85 | 0 | 3542.7 | 10598.55 | 0 | 0 | 0 | 0
2022112414 | 5 | 0.53322 | 42657.6 | 0 | 0 | 0.35693 | 12492.55 | 0.25367 | 3551.38 | 40000 | 0 | 2657.6 | 9834.95 | 0 | 3551.38 | 13386.33 | 0 | 0 | 0 | 0
2022112415 | 5 | 0.52305 | 41844 | 0 | 0 | 0.4026 | 14091 | 0.22102 | 3094.28 | 40000 | 0 | 1844 | 12247 | 0 | 3094.28 | 15341.28 | 0 | 0 | 0 | 0
2022112416 | 5 | 0.51069 | 40855.2 | 0 | 0 | 0.42801 | 14980.35 | 0.15764 | 2206.96 | 40000 | 0 | 855.2 | 14125.15 | 0 | 2206.96 | 16332.11 | 0 | 0 | 0 | 0
2022112417 | 5 | 0.50145 | 40116 | 0 | 0 | 0.45398 | 15889.3 | 0.08943 | 1252.02 | 40000 | 0 | 116 | 15773.3 | 0 | 1252.02 | 17025.32 | 0 | 0 | 0 | 0
2022112418 | 5 | 0.50418 | 40334.4 | 0 | 0 | 0.43692 | 15292.2 | 0.01502 | 210.28 | 40000 | 0 | 334.4 | 14957.8 | 0 | 210.28 | 15168.08 | 0 | 0 | 0 | 0
2022112419 | 5 | 0.50288 | 40230.4 | 0 | 0 | 0.46313 | 16209.55 | 0 | 0 | 40000 | 0 | 230.4 | 15979.15 | 0 | 0 | 15979.15 | 0 | 0 | 0 | 0
2022112420 | 5 | 0.49676 | 39740.8 | 0 | 0 | 0.48662 | 17031.7 | 0 | 0 | 39740.8 | 259.2 | 0 | 17031.7 | 0 | 0 | 17290.9 | 0 | 0 | 0 | 0
2022112421 | 5 | 0.49162 | 39329.6 | 0 | 0 | 0.50172 | 17560.2 | 0 | 0 | 39329.6 | 670.4 | 0 | 17560.2 | 0 | 0 | 18230.6 | 0 | 0 | 0 | 0
2022112422 | 5 | 0.48427 | 38741.6 | 0 | 0 | 0.52076 | 18226.6 | 0 | 0 | 38741.6 | 1258.4 | 0 | 18226.6 | 0 | 0 | 19485 | 0 | 0 | 0 | 0
2022112423 | 5 | 0.47126 | 37700.8 | 0 | 0 | 0.53497 | 18723.95 | 0 | 0 | 37700.8 | 2299.2 | 0 | 18723.95 | 0 | 0 | 21023.15 | 0 | 0 | 0 | 0
2022112424 | 5 | 0.45649 | 36519.2 | 0 | 0 | 0.53495 | 18723.25 | 0 | 0 | 36519.2 | 3480.8 | 0 | 18723.25 | 0 | 0 | 22204.05 | 0 | 0 | 0 | 0
2022112501 | 6 | 0.44228 | 35382.4 | 0 | 0 | 0.53358 | 18675.3 | 0 | 0 | 35382.4 | 4617.6 | 0 | 18675.3 | 0 | 0 | 23292.9 | 0 | 0 | 0 | 0
2022112502 | 6 | 0.43305 | 34644 | 0 | 0 | 0.54689 | 19141.15 | 0 | 0 | 34644 | 5356 | 0 | 19141.15 | 0 | 0 | 24497.15 | 0 | 0 | 0 | 0
2022112503 | 6 | 0.42691 | 34152.8 | 0 | 0 | 0.53729 | 18805.15 | 0 | 0 | 34152.8 | 5847.2 | 0 | 18805.15 | 0 | 0 | 24652.35 | 0 | 0 | 0 | 0
2022112504 | 6 | 0.42613 | 34090.4 | 0 | 0 | 0.53522 | 18732.7 | 0 | 0 | 34090.4 | 5909.6 | 0 | 18732.7 | 0 | 0 | 24642.3 | 0 | 0 | 0 | 0
2022112505 | 6 | 0.43006 | 34404.8 | 0 | 0 | 0.5267 | 18434.5 | 0 | 0 | 34404.8 | 5595.2 | 0 | 18434.5 | 0 | 0 | 24029.7 | 0 | 0 | 0 | 0
2022112506 | 6 | 0.44131 | 35304.8 | 0 | 0 | 0.53408 | 18692.8 | 0 | 0 | 35304.8 | 4695.2 | 0 | 18692.8 | 0 | 0 | 23388 | 0 | 0 | 0 | 0
2022112507 | 6 | 0.45653 | 36522.4 | 0 | 0 | 0.52499 | 18374.65 | 0 | 0 | 36522.4 | 3477.6 | 0 | 18374.65 | 0 | 0 | 21852.25 | 0 | 0 | 0 | 0
2022112508 | 6 | 0.47049 | 37639.2 | 0 | 0 | 0.51837 | 18142.95 | 0.00251 | 35.14 | 37639.2 | 2360.8 | 0 | 18142.95 | 0 | 35.14 | 20538.89 | 0 | 0 | 0 | 0
2022112509 | 6 | 0.48799 | 39039.2 | 0 | 0 | 0.52253 | 18288.55 | 0.01751 | 245.14 | 39039.2 | 960.8 | 0 | 18288.55 | 0 | 245.14 | 19494.49 | 0 | 0 | 0 | 0
2022112510 | 6 | 0.50527 | 40421.6 | 0 | 0 | 0.49237 | 17232.95 | 0.04187 | 586.18 | 40000 | 0 | 421.6 | 16811.35 | 0 | 586.18 | 17397.53 | 0 | 0 | 0 | 0
2022112511 | 6 | 0.5182 | 41456 | 0 | 0 | 0.49918 | 17471.3 | 0.06512 | 911.68 | 40000 | 0 | 1456 | 16015.3 | 0 | 911.68 | 16926.98 | 0 | 0 | 0 | 0
2022112512 | 6 | 0.52357 | 41885.6 | 0 | 0 | 0.52554 | 18393.9 | 0.08606 | 1204.84 | 40000 | 0 | 1885.6 | 16508.3 | 0 | 1204.84 | 17713.14 | 0 | 0 | 0 | 0
2022112513 | 6 | 0.52302 | 41841.6 | 0 | 0 | 0.51458 | 18010.3 | 0.09764 | 1366.96 | 40000 | 0 | 1841.6 | 16168.7 | 0 | 1366.96 | 17535.66 | 0 | 0 | 0 | 0
2022112514 | 6 | 0.51831 | 41464.8 | 0 | 0 | 0.51245 | 17935.75 | 0.08746 | 1224.44 | 40000 | 0 | 1464.8 | 16470.95 | 0 | 1224.44 | 17695.39 | 0 | 0 | 0 | 0
2022112515 | 6 | 0.51242 | 40993.6 | 0 | 0 | 0.49297 | 17253.95 | 0.0642 | 898.8 | 40000 | 0 | 993.6 | 16260.35 | 0 | 898.8 | 17159.15 | 0 | 0 | 0 | 0
2022112516 | 6 | 0.51234 | 40987.2 | 0 | 0 | 0.47236 | 16532.6 | 0.03127 | 437.78 | 40000 | 0 | 987.2 | 15545.4 | 0 | 437.78 | 15983.18 | 0 | 0 | 0 | 0
2022112517 | 6 | 0.5189 | 41512 | 0 | 0 | 0.42066 | 14723.1 | 0.0104 | 145.6 | 40000 | 0 | 1512 | 13211.1 | 0 | 145.6 | 13356.7 | 0 | 0 | 0 | 0
2022112518 | 6 | 0.53376 | 42700.8 | 0 | 0 | 0.39481 | 13818.35 | 0.00025 | 3.5 | 40000 | 0 | 2700.8 | 11117.55 | 0 | 3.5 | 11121.05 | 0 | 0 | 0 | 0
2022112519 | 6 | 0.53505 | 42804 | 0 | 0 | 0.37371 | 13079.85 | 0 | 0 | 40000 | 0 | 2804 | 10275.85 | 0 | 0 | 10275.85 | 0 | 0 | 0 | 0
2022112520 | 6 | 0.52812 | 42249.6 | 0 | 0 | 0.30193 | 10567.55 | 0 | 0 | 40000 | 0 | 2249.6 | 8317.95 | 0 | 0 | 8317.95 | 0 | 0 | 0 | 0
2022112521 | 6 | 0.5194 | 41552 | 0 | 0 | 0.27246 | 9536.1 | 0 | 0 | 40000 | 0 | 1552 | 7984.1 | 0 | 0 | 7984.1 | 0 | 0 | 0 | 0
2022112522 | 6 | 0.51055 | 40844 | 0 | 0 | 0.24138 | 8448.3 | 0 | 0 | 40000 | 0 | 844 | 7604.3 | 0 | 0 | 7604.3 | 0 | 0 | 0 | 0
2022112523 | 6 | 0.4949 | 39592 | 0 | 0 | 0.27847 | 9746.45 | 0 | 0 | 39592 | 408 | 0 | 9746.45 | 0 | 0 | 10154.45 | 0 | 0 | 0 | 0
2022112524 | 6 | 0.47982 | 38385.6 | 0 | 0 | 0.31412 | 10994.2 | 0 | 0 | 38385.6 | 1614.4 | 0 | 10994.2 | 0 | 0 | 12608.6 | 0 | 0 | 0 | 0
2022112601 | 7 | 0.46473 | 37178.4 | 0 | 0 | 0.30765 | 10767.75 | 0 | 0 | 37178.4 | 2821.6 | 0 | 10767.75 | 0 | 0 | 13589.35 | 0 | 0 | 0 | 0
2022112602 | 7 | 0.45115 | 36092 | 0 | 0 | 0.25539 | 8938.65 | 0 | 0 | 36092 | 3908 | 0 | 8938.65 | 0 | 0 | 12846.65 | 0 | 0 | 0 | 0
2022112603 | 7 | 0.44207 | 35365.6 | 0 | 0 | 0.20708 | 7247.8 | 0 | 0 | 35365.6 | 4634.4 | 0 | 7247.8 | 0 | 0 | 11882.2 | 0 | 0 | 0 | 0
2022112604 | 7 | 0.44025 | 35220 | 0 | 0 | 0.19984 | 6994.4 | 0 | 0 | 35220 | 4780 | 0 | 6994.4 | 0 | 0 | 11774.4 | 0 | 0 | 0 | 0
2022112605 | 7 | 0.44338 | 35470.4 | 0 | 0 | 0.2051 | 7178.5 | 0 | 0 | 35470.4 | 4529.6 | 0 | 7178.5 | 0 | 0 | 11708.1 | 0 | 0 | 0 | 0
2022112606 | 7 | 0.44998 | 35998.4 | 0 | 0 | 0.20076 | 7026.6 | 0 | 0 | 35998.4 | 4001.6 | 0 | 7026.6 | 0 | 0 | 11028.2 | 0 | 0 | 0 | 0
2022112607 | 7 | 0.46438 | 37150.4 | 0 | 0 | 0.19022 | 6657.7 | 0 | 0 | 37150.4 | 2849.6 | 0 | 6657.7 | 0 | 0 | 9507.3 | 0 | 0 | 0 | 0
2022112608 | 7 | 0.48145 | 38516 | 0 | 0 | 0.21826 | 7639.1 | 0.00777 | 108.78 | 38516 | 1484 | 0 | 7639.1 | 0 | 108.78 | 9231.88 | 0 | 0 | 0 | 0
2022112609 | 7 | 0.49682 | 39745.6 | 0 | 0 | 0.24135 | 8447.25 | 0.08601 | 1204.14 | 39745.6 | 254.4 | 0 | 8447.25 | 0 | 1204.14 | 9905.79 | 0 | 0 | 0 | 0
2022112610 | 7 | 0.50889 | 40711.2 | 0 | 0 | 0.27211 | 9523.85 | 0.22078 | 3090.92 | 40000 | 0 | 711.2 | 8812.65 | 0 | 3090.92 | 11903.57 | 0 | 0 | 0 | 0
2022112611 | 7 | 0.51056 | 40844.8 | 0 | 0 | 0.29842 | 10444.7 | 0.34059 | 4768.26 | 40000 | 0 | 844.8 | 9599.9 | 0 | 4768.26 | 14368.16 | 0 | 0 | 0 | 0
2022112612 | 7 | 0.51062 | 40849.6 | 0 | 0 | 0.34804 | 12181.4 | 0.39478 | 5526.92 | 40000 | 0 | 849.6 | 11331.8 | 0 | 5526.92 | 16858.72 | 0 | 0 | 0 | 0
2022112613 | 7 | 0.5124 | 40992 | 0 | 0 | 0.40038 | 14013.3 | 0.40825 | 5715.5 | 40000 | 0 | 992 | 13021.3 | 0 | 5715.5 | 18736.8 | 0 | 0 | 0 | 0
2022112614 | 7 | 0.50747 | 40597.6 | 0 | 0 | 0.42107 | 14737.45 | 0.40207 | 5628.98 | 40000 | 0 | 597.6 | 14139.85 | 0 | 5628.98 | 19768.83 | 0 | 0 | 0 | 0
2022112615 | 7 | 0.50306 | 40244.8 | 0 | 0 | 0.38587 | 13505.45 | 0.43915 | 6148.1 | 40000 | 0 | 244.8 | 13260.65 | 0 | 6148.1 | 19408.75 | 0 | 0 | 0 | 0
2022112616 | 7 | 0.5038 | 40304 | 0 | 0 | 0.32318 | 11311.3 | 0.43868 | 6141.52 | 40000 | 0 | 304 | 11007.3 | 0 | 6141.52 | 17148.82 | 0 | 0 | 0 | 0
2022112617 | 7 | 0.50523 | 40418.4 | 0 | 0 | 0.26653 | 9328.55 | 0.31739 | 4443.46 | 40000 | 0 | 418.4 | 8910.15 | 0 | 4443.46 | 13353.61 | 0 | 0 | 0 | 0
2022112618 | 7 | 0.51957 | 41565.6 | 0 | 0 | 0.19091 | 6681.85 | 0.03388 | 474.32 | 40000 | 0 | 1565.6 | 5116.25 | 0 | 474.32 | 5590.57 | 0 | 0 | 0 | 0
2022112619 | 7 | 0.53222 | 42577.6 | 0 | 0 | 0.22164 | 7757.4 | 0 | 0 | 40000 | 0 | 2577.6 | 5179.8 | 0 | 0 | 5179.8 | 0 | 0 | 0 | 0
2022112620 | 7 | 0.53369 | 42695.2 | 0 | 0 | 0.29786 | 10425.1 | 0 | 0 | 40000 | 0 | 2695.2 | 7729.9 | 0 | 0 | 7729.9 | 0 | 0 | 0 | 0
2022112621 | 7 | 0.53451 | 42760.8 | 0 | 0 | 0.37708 | 13197.8 | 0 | 0 | 40000 | 0 | 2760.8 | 10437 | 0 | 0 | 10437 | 0 | 0 | 0 | 0
2022112622 | 7 | 0.52962 | 42369.6 | 0 | 0 | 0.4168 | 14588 | 0 | 0 | 40000 | 0 | 2369.6 | 12218.4 | 0 | 0 | 12218.4 | 0 | 0 | 0 | 0
2022112623 | 7 | 0.52047 | 41637.6 | 0 | 0 | 0.45674 | 15985.9 | 0 | 0 | 40000 | 0 | 1637.6 | 14348.3 | 0 | 0 | 14348.3 | 0 | 0 | 0 | 0
2022112624 | 7 | 0.50649 | 40519.2 | 0 | 0 | 0.47663 | 16682.05 | 0 | 0 | 40000 | 0 | 519.2 | 16162.85 | 0 | 0 | 16162.85 | 0 | 0 | 0 | 0
2022112701 | 1 | 0.49457 | 39565.6 | 0 | 0 | 0.48443 | 16955.05 | 0 | 0 | 39565.6 | 434.4 | 0 | 16955.05 | 0 | 0 | 17389.45 | 0 | 0 | 0 | 0
2022112702 | 1 | 0.48566 | 38852.8 | 0 | 0 | 0.48261 | 16891.35 | 0 | 0 | 38852.8 | 1147.2 | 0 | 16891.35 | 0 | 0 | 18038.55 | 0 | 0 | 0 | 0
2022112703 | 1 | 0.4799 | 38392 | 0 | 0 | 0.4638 | 16233 | 0 | 0 | 38392 | 1608 | 0 | 16233 | 0 | 0 | 17841 | 0 | 0 | 0 | 0
2022112704 | 1 | 0.47606 | 38084.8 | 0 | 0 | 0.44455 | 15559.25 | 0 | 0 | 38084.8 | 1915.2 | 0 | 15559.25 | 0 | 0 | 17474.45 | 0 | 0 | 0 | 0
2022112705 | 1 | 0.47908 | 38326.4 | 0 | 0 | 0.43069 | 15074.15 | 0 | 0 | 38326.4 | 1673.6 | 0 | 15074.15 | 0 | 0 | 16747.75 | 0 | 0 | 0 | 0
2022112706 | 1 | 0.48664 | 38931.2 | 0 | 0 | 0.38374 | 13430.9 | 0 | 0 | 38931.2 | 1068.8 | 0 | 13430.9 | 0 | 0 | 14499.7 | 0 | 0 | 0 | 0
2022112707 | 1 | 0.50149 | 40119.2 | 0 | 0 | 0.33869 | 11854.15 | 0 | 0 | 40000 | 0 | 119.2 | 11734.95 | 0 | 0 | 11734.95 | 0 | 0 | 0 | 0
2022112708 | 1 | 0.50983 | 40786.4 | 0 | 0 | 0.29454 | 10308.9 | 0.04463 | 624.82 | 40000 | 0 | 786.4 | 9522.5 | 0 | 624.82 | 10147.32 | 0 | 0 | 0 | 0
2022112709 | 1 | 0.51473 | 41178.4 | 0 | 0 | 0.21467 | 7513.45 | 0.38182 | 5345.48 | 40000 | 0 | 1178.4 | 6335.05 | 0 | 5345.48 | 11680.53 | 0 | 0 | 0 | 0
2022112710 | 1 | 0.50994 | 40795.2 | 0 | 0 | 0.14381 | 5033.35 | 0.60464 | 8464.96 | 40000 | 0 | 795.2 | 4238.15 | 0 | 8464.96 | 12703.11 | 0 | 0 | 0 | 0
2022112711 | 1 | 0.49914 | 39931.2 | 0 | 0 | 0.13594 | 4757.9 | 0.62164 | 8702.96 | 39931.2 | 68.8 | 0 | 4757.9 | 0 | 8702.96 | 13529.66 | 0 | 0 | 0 | 0
2022112712 | 1 | 0.48798 | 39038.4 | 0 | 0 | 0.1137 | 3979.5 | 0.60202 | 8428.28 | 39038.4 | 961.6 | 0 | 3979.5 | 0 | 8428.28 | 13369.38 | 0 | 0 | 0 | 0
2022112713 | 1 | 0.48571 | 38856.8 | 0 | 0 | 0.10717 | 3750.95 | 0.59584 | 8341.76 | 38856.8 | 1143.2 | 0 | 3750.95 | 0 | 8341.76 | 13235.91 | 0 | 0 | 0 | 0
2022112714 | 1 | 0.48609 | 38887.2 | 0 | 0 | 0.09962 | 3486.7 | 0.60946 | 8532.44 | 38887.2 | 1112.8 | 0 | 3486.7 | 0 | 8532.44 | 13131.94 | 0 | 0 | 0 | 0
2022112715 | 1 | 0.49043 | 39234.4 | 0 | 0 | 0.08355 | 2924.25 | 0.6296 | 8814.4 | 39234.4 | 765.6 | 0 | 2924.25 | 0 | 8814.4 | 12504.25 | 0 | 0 | 0 | 0
2022112716 | 1 | 0.49276 | 39420.8 | 0 | 0 | 0.07597 | 2658.95 | 0.6159 | 8622.6 | 39420.8 | 579.2 | 0 | 2658.95 | 0 | 8622.6 | 11860.75 | 0 | 0 | 0 | 0
2022112717 | 1 | 0.5007 | 40056 | 0 | 0 | 0.06544 | 2290.4 | 0.36725 | 5141.5 | 40000 | 0 | 56 | 2234.4 | 0 | 5141.5 | 7375.9 | 0 | 0 | 0 | 0
2022112718 | 1 | 0.51967 | 41573.6 | 0 | 0 | 0.07072 | 2475.2 | 0.0364 | 509.6 | 40000 | 0 | 1573.6 | 901.6 | 0 | 509.6 | 1411.2 | 0 | 0 | 0 | 0
2022112719 | 1 | 0.53777 | 43021.6 | 0 | 0 | 0.06777 | 2371.95 | 0 | 0 | 40000 | 0 | 2371.95 | 0 | 0 | 0 | 0 | 649.65 | 0 | 0 | 649.65
2022112720 | 1 | 0.53685 | 42948 | 0 | 0 | 0.07744 | 2710.4 | 0 | 0 | 40000 | 0 | 2710.4 | 0 | 0 | 0 | 0 | 237.6 | 0 | 0 | 237.6
2022112721 | 1 | 0.53231 | 42584.8 | 0 | 0 | 0.08585 | 3004.75 | 0 | 0 | 40000 | 0 | 2584.8 | 419.95 | 0 | 0 | 419.95 | 0 | 0 | 0 | 0
2022112722 | 1 | 0.52122 | 41697.6 | 0 | 0 | 0.09609 | 3363.15 | 0 | 0 | 40000 | 0 | 1697.6 | 1665.55 | 0 | 0 | 1665.55 | 0 | 0 | 0 | 0
2022112723 | 1 | 0.49914 | 39931.2 | 0 | 0 | 0.11663 | 4082.05 | 0 | 0 | 39931.2 | 68.8 | 0 | 4082.05 | 0 | 0 | 4150.85 | 0 | 0 | 0 | 0
2022112724 | 1 | 0.47667 | 38133.6 | 0 | 0 | 0.14803 | 5181.05 | 0 | 0 | 38133.6 | 1866.4 | 0 | 5181.05 | 0 | 0 | 7047.45 | 0 | 0 | 0 | 0
2022112801 | 2 | 0.46192 | 36953.6 | 0 | 0 | 0.18299 | 6404.65 | 0 | 0 | 36953.6 | 3046.4 | 0 | 6404.65 | 0 | 0 | 9451.05 | 0 | 0 | 0 | 0
2022112802 | 2 | 0.45969 | 36775.2 | 0 | 0 | 0.24229 | 8480.15 | 0 | 0 | 36775.2 | 3224.8 | 0 | 8480.15 | 0 | 0 | 11704.95 | 0 | 0 | 0 | 0
2022112803 | 2 | 0.46644 | 37315.2 | 0 | 0 | 0.30646 | 10726.1 | 0 | 0 | 37315.2 | 2684.8 | 0 | 10726.1 | 0 | 0 | 13410.9 | 0 | 0 | 0 | 0
2022112804 | 2 | 0.47599 | 38079.2 | 0 | 0 | 0.36954 | 12933.9 | 0 | 0 | 38079.2 | 1920.8 | 0 | 12933.9 | 0 | 0 | 14854.7 | 0 | 0 | 0 | 0
2022112805 | 2 | 0.49299 | 39439.2 | 0 | 0 | 0.42293 | 14802.55 | 0 | 0 | 39439.2 | 560.8 | 0 | 14802.55 | 0 | 0 | 15363.35 | 0 | 0 | 0 | 0
2022112806 | 2 | 0.52768 | 42214.4 | 0 | 0 | 0.47302 | 16555.7 | 0 | 0 | 40000 | 0 | 2214.4 | 14341.3 | 0 | 0 | 14341.3 | 0 | 0 | 0 | 0
2022112807 | 2 | 0.57659 | 46127.2 | 0 | 0 | 0.49625 | 17368.75 | 0 | 0 | 40000 | 0 | 6127.2 | 11241.55 | 0 | 0 | 11241.55 | 0 | 0 | 0 | 0
2022112808 | 2 | 0.59753 | 47802.4 | 0 | 0 | 0.50056 | 17519.6 | 0.03742 | 523.88 | 40000 | 0 | 7802.4 | 9717.2 | 0 | 523.88 | 10241.08 | 0 | 0 | 0 | 0
2022112809 | 2 | 0.5843 | 46744 | 0 | 0 | 0.47548 | 16641.8 | 0.26719 | 3740.66 | 40000 | 0 | 6744 | 9897.8 | 0 | 3740.66 | 13638.46 | 0 | 0 | 0 | 0
2022112810 | 2 | 0.56659 | 45327.2 | 0 | 0 | 0.4199 | 14696.5 | 0.46826 | 6555.64 | 40000 | 0 | 5327.2 | 9369.3 | 0 | 6555.64 | 15924.94 | 0 | 0 | 0 | 0
2022112811 | 2 | 0.55019 | 44015.2 | 0 | 0 | 0.37986 | 13295.1 | 0.5496 | 7694.4 | 40000 | 0 | 4015.2 | 9279.9 | 0 | 7694.4 | 16974.3 | 0 | 0 | 0 | 0
2022112812 | 2 | 0.53925 | 43140 | 0 | 0 | 0.39654 | 13878.9 | 0.51891 | 7264.74 | 40000 | 0 | 3140 | 10738.9 | 0 | 7264.74 | 18003.64 | 0 | 0 | 0 | 0
2022112813 | 2 | 0.53314 | 42651.2 | 0 | 0 | 0.44855 | 15699.25 | 0.39676 | 5554.64 | 40000 | 0 | 2651.2 | 13048.05 | 0 | 5554.64 | 18602.69 | 0 | 0 | 0 | 0
2022112814 | 2 | 0.53364 | 42691.2 | 0 | 0 | 0.47397 | 16588.95 | 0.34417 | 4818.38 | 40000 | 0 | 2691.2 | 13897.75 | 0 | 4818.38 | 18716.13 | 0 | 0 | 0 | 0
2022112815 | 2 | 0.53473 | 42778.4 | 0 | 0 | 0.48198 | 16869.3 | 0.34361 | 4810.54 | 40000 | 0 | 2778.4 | 14090.9 | 0 | 4810.54 | 18901.44 | 0 | 0 | 0 | 0
2022112816 | 2 | 0.53613 | 42890.4 | 0 | 0 | 0.48638 | 17023.3 | 0.34201 | 4788.14 | 40000 | 0 | 2890.4 | 14132.9 | 0 | 4788.14 | 18921.04 | 0 | 0 | 0 | 0
2022112817 | 2 | 0.53858 | 43086.4 | 0 | 0 | 0.47606 | 16662.1 | 0.23607 | 3304.98 | 40000 | 0 | 3086.4 | 13575.7 | 0 | 3304.98 | 16880.68 | 0 | 0 | 0 | 0
2022112818 | 2 | 0.55093 | 44074.4 | 0 | 0 | 0.48716 | 17050.6 | 0.03321 | 464.94 | 40000 | 0 | 4074.4 | 12976.2 | 0 | 464.94 | 13441.14 | 0 | 0 | 0 | 0
2022112819 | 2 | 0.56814 | 45451.2 | 0 | 0 | 0.56057 | 19619.95 | 0 | 0 | 40000 | 0 | 5451.2 | 14168.75 | 0 | 0 | 14168.75 | 0 | 0 | 0 | 0
2022112820 | 2 | 0.56415 | 45132 | 0 | 0 | 0.59485 | 20819.75 | 0 | 0 | 40000 | 0 | 5132 | 15687.75 | 0 | 0 | 15687.75 | 0 | 0 | 0 | 0
2022112821 | 2 | 0.55389 | 44311.2 | 0 | 0 | 0.59794 | 20927.9 | 0 | 0 | 40000 | 0 | 4311.2 | 16616.7 | 0 | 0 | 16616.7 | 0 | 0 | 0 | 0
2022112822 | 2 | 0.53824 | 43059.2 | 0 | 0 | 0.60969 | 21339.15 | 0 | 0 | 40000 | 0 | 3059.2 | 18279.95 | 0 | 0 | 18279.95 | 0 | 0 | 0 | 0
2022112823 | 2 | 0.51297 | 41037.6 | 0 | 0 | 0.62266 | 21793.1 | 0 | 0 | 40000 | 0 | 1037.6 | 20755.5 | 0 | 0 | 20755.5 | 0 | 0 | 0 | 0
2022112824 | 2 | 0.48632 | 38905.6 | 0 | 0 | 0.64137 | 22447.95 | 0 | 0 | 38905.6 | 1094.4 | 0 | 22447.95 | 0 | 0 | 23542.35 | 0 | 0 | 0 | 0
2022112901 | 3 | 0.46626 | 37300.8 | 0 | 0 | 0.6421 | 22473.5 | 0 | 0 | 37300.8 | 2699.2 | 0 | 22473.5 | 0 | 0 | 25172.7 | 0 | 0 | 0 | 0
2022112902 | 3 | 0.45395 | 36316 | 0 | 0 | 0.62961 | 22036.35 | 0 | 0 | 36316 | 3684 | 0 | 22036.35 | 0 | 0 | 25720.35 | 0 | 0 | 0 | 0
2022112903 | 3 | 0.44599 | 35679.2 | 0 | 0 | 0.62253 | 21788.55 | 0 | 0 | 35679.2 | 4320.8 | 0 | 21788.55 | 0 | 0 | 26109.35 | 0 | 0 | 0 | 0
2022112904 | 3 | 0.44512 | 35609.6 | 0 | 0 | 0.62044 | 21715.4 | 0 | 0 | 35609.6 | 4390.4 | 0 | 21715.4 | 0 | 0 | 26105.8 | 0 | 0 | 0 | 0
2022112905 | 3 | 0.45321 | 36256.8 | 0 | 0 | 0.61686 | 21590.1 | 0 | 0 | 36256.8 | 3743.2 | 0 | 21590.1 | 0 | 0 | 25333.3 | 0 | 0 | 0 | 0
2022112906 | 3 | 0.47454 | 37963.2 | 0 | 0 | 0.60797 | 21278.95 | 0 | 0 | 37963.2 | 2036.8 | 0 | 21278.95 | 0 | 0 | 23315.75 | 0 | 0 | 0 | 0
2022112907 | 3 | 0.51083 | 40866.4 | 0 | 0 | 0.6098 | 21343 | 0 | 0 | 40000 | 0 | 866.4 | 20476.6 | 0 | 0 | 20476.6 | 0 | 0 | 0 | 0
2022112908 | 3 | 0.52895 | 42316 | 0 | 0 | 0.60117 | 21040.95 | 0.01299 | 181.86 | 40000 | 0 | 2316 | 18724.95 | 0 | 181.86 | 18906.81 | 0 | 0 | 0 | 0
2022112909 | 3 | 0.53296 | 42636.8 | 0 | 0 | 0.55025 | 19258.75 | 0.18412 | 2577.68 | 40000 | 0 | 2636.8 | 16621.95 | 0 | 2577.68 | 19199.63 | 0 | 0 | 0 | 0
2022112910 | 3 | 0.54214 | 43371.2 | 0 | 0 | 0.49056 | 17169.6 | 0.35159 | 4922.26 | 40000 | 0 | 3371.2 | 13798.4 | 0 | 4922.26 | 18720.66 | 0 | 0 | 0 | 0
2022112911 | 3 | 0.55084 | 44067.2 | 0 | 0 | 0.46507 | 16277.45 | 0.47664 | 6672.96 | 40000 | 0 | 4067.2 | 12210.25 | 0 | 6672.96 | 18883.21 | 0 | 0 | 0 | 0
2022112912 | 3 | 0.56109 | 44887.2 | 0 | 0 | 0.4712 | 16492 | 0.47843 | 6698.02 | 40000 | 0 | 4887.2 | 11604.8 | 0 | 6698.02 | 18302.82 | 0 | 0 | 0 | 0
2022112913 | 3 | 0.56844 | 45475.2 | 0 | 0 | 0.50299 | 17604.65 | 0.39179 | 5485.06 | 40000 | 0 | 5475.2 | 12129.45 | 0 | 5485.06 | 17614.51 | 0 | 0 | 0 | 0
2022112914 | 3 | 0.57617 | 46093.6 | 0 | 0 | 0.51206 | 17922.1 | 0.32246 | 4514.44 | 40000 | 0 | 6093.6 | 11828.5 | 0 | 4514.44 | 16342.94 | 0 | 0 | 0 | 0
2022112915 | 3 | 0.58394 | 46715.2 | 0 | 0 | 0.49598 | 17359.3 | 0.30519 | 4272.66 | 40000 | 0 | 6715.2 | 10644.1 | 0 | 4272.66 | 14916.76 | 0 | 0 | 0 | 0
2022112916 | 3 | 0.58994 | 47195.2 | 0 | 0 | 0.48085 | 16829.75 | 0.2728 | 3819.2 | 40000 | 0 | 7195.2 | 9634.55 | 0 | 3819.2 | 13453.75 | 0 | 0 | 0 | 0
2022112917 | 3 | 0.59197 | 47357.6 | 0 | 0 | 0.42632 | 14921.2 | 0.20771 | 2907.94 | 40000 | 0 | 7357.6 | 7563.6 | 0 | 2907.94 | 10471.54 | 0 | 0 | 0 | 0
2022112918 | 3 | 0.59896 | 47916.8 | 0 | 0 | 0.38976 | 13641.6 | 0.03499 | 489.86 | 40000 | 0 | 7916.8 | 5724.8 | 0 | 489.86 | 6214.66 | 0 | 0 | 0 | 0
2022112919 | 3 | 0.60369 | 48295.2 | 0 | 0 | 0.40285 | 14099.75 | 0.0043 | 60.2 | 40000 | 0 | 8295.2 | 5804.55 | 0 | 60.2 | 5864.75 | 0 | 0 | 0 | 0
2022112920 | 3 | 0.59074 | 47259.2 | 0 | 0 | 0.4774 | 16709 | 0.00431 | 60.34 | 40000 | 0 | 7259.2 | 9449.8 | 0 | 60.34 | 9510.14 | 0 | 0 | 0 | 0
2022112921 | 3 | 0.578 | 46240 | 0 | 0 | 0.54082 | 18928.7 | 0.00431 | 60.34 | 40000 | 0 | 6240 | 12688.7 | 0 | 60.34 | 12749.04 | 0 | 0 | 0 | 0
2022112922 | 3 | 0.55769 | 44615.2 | 0 | 0 | 0.55419 | 19396.65 | 0.00431 | 60.34 | 40000 | 0 | 4615.2 | 14781.45 | 0 | 60.34 | 14841.79 | 0 | 0 | 0 | 0
2022112923 | 3 | 0.53013 | 42410.4 | 0 | 0 | 0.5455 | 19092.5 | 0.00431 | 60.34 | 40000 | 0 | 2410.4 | 16682.1 | 0 | 60.34 | 16742.44 | 0 | 0 | 0 | 0
2022112924 | 3 | 0.50281 | 40224.8 | 0 | 0 | 0.52988 | 18545.8 | 0.00393 | 55.02 | 40000 | 0 | 224.8 | 18321 | 0 | 55.02 | 18376.02 | 0 | 0 | 0 | 0
2022113001 | 4 | 0.48004 | 38403.2 | 0 | 0 | 0.49109 | 17188.15 | 0 | 0 | 38403.2 | 1596.8 | 0 | 17188.15 | 0 | 0 | 18784.95 | 0 | 0 | 0 | 0
2022113002 | 4 | 0.47116 | 37692.8 | 0 | 0 | 0.44441 | 15554.35 | 0 | 0 | 37692.8 | 2307.2 | 0 | 15554.35 | 0 | 0 | 17861.55 | 0 | 0 | 0 | 0
2022113003 | 4 | 0.46893 | 37514.4 | 0 | 0 | 0.38601 | 13510.35 | 0 | 0 | 37514.4 | 2485.6 | 0 | 13510.35 | 0 | 0 | 15995.95 | 0 | 0 | 0 | 0
2022113004 | 4 | 0.46919 | 37535.2 | 0 | 0 | 0.34358 | 12025.3 | 0 | 0 | 37535.2 | 2464.8 | 0 | 12025.3 | 0 | 0 | 14490.1 | 0 | 0 | 0 | 0
2022113005 | 4 | 0.48197 | 38557.6 | 0 | 0 | 0.33391 | 11686.85 | 0 | 0 | 38557.6 | 1442.4 | 0 | 11686.85 | 0 | 0 | 13129.25 | 0 | 0 | 0 | 0
2022113006 | 4 | 0.51346 | 41076.8 | 0 | 0 | 0.34439 | 12053.65 | 0 | 0 | 40000 | 0 | 1076.8 | 10976.85 | 0 | 0 | 10976.85 | 0 | 0 | 0 | 0
2022113007 | 4 | 0.56483 | 45186.4 | 0 | 0 | 0.30542 | 10689.7 | 0 | 0 | 40000 | 0 | 5186.4 | 5503.3 | 0 | 0 | 5503.3 | 0 | 0 | 0 | 0
2022113008 | 4 | 0.59179 | 47343.2 | 0 | 0 | 0.28579 | 10002.65 | 0.03626 | 507.64 | 40000 | 0 | 7343.2 | 2659.45 | 0 | 507.64 | 3167.09 | 0 | 0 | 0 | 0
2022113009 | 4 | 0.59217 | 47373.6 | 0 | 0 | 0.25328 | 8864.8 | 0.35754 | 5005.56 | 40000 | 0 | 7373.6 | 1491.2 | 0 | 5005.56 | 6496.76 | 0 | 0 | 0 | 0
2022113010 | 4 | 0.58533 | 46826.4 | 0 | 0 | 0.23665 | 8282.75 | 0.58489 | 8188.46 | 40000 | 0 | 6826.4 | 1456.35 | 0 | 8188.46 | 9644.81 | 0 | 0 | 0 | 0
2022113011 | 4 | 0.57342 | 45873.6 | 0 | 0 | 0.21456 | 7509.6 | 0.59343 | 8308.02 | 40000 | 0 | 5873.6 | 1636 | 0 | 8308.02 | 9944.02 | 0 | 0 | 0 | 0
2022113012 | 4 | 0.5624 | 44992 | 0 | 0 | 0.19393 | 6787.55 | 0.58702 | 8218.28 | 40000 | 0 | 4992 | 1795.55 | 0 | 8218.28 | 10013.83 | 0 | 0 | 0 | 0
2022113013 | 4 | 0.55045 | 44036 | 0 | 0 | 0.1868 | 6538 | 0.58087 | 8132.18 | 40000 | 0 | 4036 | 2502 | 0 | 8132.18 | 10634.18 | 0 | 0 | 0 | 0
2022113014 | 4 | 0.5395 | 43160 | 0 | 0 | 0.18583 | 6504.05 | 0.58797 | 8231.58 | 40000 | 0 | 3160 | 3344.05 | 0 | 8231.58 | 11575.63 | 0 | 0 | 0 | 0
2022113015 | 4 | 0.53313 | 42650.4 | 0 | 0 | 0.19991 | 6996.85 | 0.59613 | 8345.82 | 40000 | 0 | 2650.4 | 4346.45 | 0 | 8345.82 | 12692.27 | 0 | 0 | 0 | 0
2022113016 | 4 | 0.53174 | 42539.2 | 0 | 0 | 0.22005 | 7701.75 | 0.55282 | 7739.48 | 40000 | 0 | 2539.2 | 5162.55 | 0 | 7739.48 | 12902.03 | 0 | 0 | 0 | 0
2022113017 | 4 | 0.54263 | 43410.4 | 0 | 0 | 0.23742 | 8309.7 | 0.28491 | 3988.74 | 40000 | 0 | 3410.4 | 4899.3 | 0 | 3988.74 | 8888.04 | 0 | 0 | 0 | 0
2022113018 | 4 | 0.57221 | 45776.8 | 0 | 0 | 0.2337 | 8179.5 | 0.02486 | 348.04 | 40000 | 0 | 5776.8 | 2402.7 | 0 | 348.04 | 2750.74 | 0 | 0 | 0 | 0
2022113019 | 4 | 0.59569 | 47655.2 | 0 | 0 | 0.26356 | 9224.6 | 0 | 0 | 40000 | 0 | 7655.2 | 1569.4 | 0 | 0 | 1569.4 | 0 | 0 | 0 | 0
2022113020 | 4 | 0.60143 | 48114.4 | 0 | 0 | 0.29792 | 10427.2 | 0 | 0 | 40000 | 0 | 8114.4 | 2312.8 | 0 | 0 | 2312.8 | 0 | 0 | 0 | 0
2022113021 | 4 | 0.60363 | 48290.4 | 0 | 0 | 0.33926 | 11874.1 | 0 | 0 | 40000 | 0 | 8290.4 | 3583.7 | 0 | 0 | 3583.7 | 0 | 0 | 0 | 0
2022113022 | 4 | 0.59369 | 47495.2 | 0 | 0 | 0.35665 | 12482.75 | 0 | 0 | 40000 | 0 | 7495.2 | 4987.55 | 0 | 0 | 4987.55 | 0 | 0 | 0 | 0
2022113023 | 4 | 0.57146 | 45716.8 | 0 | 0 | 0.36125 | 12643.75 | 0 | 0 | 40000 | 0 | 5716.8 | 6926.95 | 0 | 0 | 6926.95 | 0 | 0 | 0 | 0
2022113024 | 4 | 0.54661 | 43728.8 | 0 | 0 | 0.35661 | 12481.35 | 0 | 0 | 40000 | 0 | 3728.8 | 8752.55 | 0 | 0 | 8752.55 | 0 | 0 | 0 | 0
2022120101 | 5 | 0.53326 | 42660.8 | 0 | 0 | 0.33469 | 11714.15 | 0 | 0 | 40000 | 0 | 2660.8 | 9053.35 | 0 | 0 | 9053.35 | 0 | 0 | 0 | 0
2022120102 | 5 | 0.52668 | 42134.4 | 0 | 0 | 0.32473 | 11365.55 | 0 | 0 | 40000 | 0 | 2134.4 | 9231.15 | 0 | 0 | 9231.15 | 0 | 0 | 0 | 0
2022120103 | 5 | 0.52668 | 42134.4 | 0 | 0 | 0.33328 | 11664.8 | 0 | 0 | 40000 | 0 | 2134.4 | 9530.4 | 0 | 0 | 9530.4 | 0 | 0 | 0 | 0
2022120104 | 5 | 0.53095 | 42476 | 0 | 0 | 0.33243 | 11635.05 | 0 | 0 | 40000 | 0 | 2476 | 9159.05 | 0 | 0 | 9159.05 | 0 | 0 | 0 | 0
2022120105 | 5 | 0.54796 | 43836.8 | 0 | 0 | 0.32687 | 11440.45 | 0 | 0 | 40000 | 0 | 3836.8 | 7603.65 | 0 | 0 | 7603.65 | 0 | 0 | 0 | 0
2022120106 | 5 | 0.57862 | 46289.6 | 0 | 0 | 0.31592 | 11057.2 | 0 | 0 | 40000 | 0 | 6289.6 | 4767.6 | 0 | 0 | 4767.6 | 0 | 0 | 0 | 0
2022120107 | 5 | 0.62259 | 49807.2 | 0 | 0 | 0.31998 | 11199.3 | 0 | 0 | 40000 | 0 | 9807.2 | 1392.1 | 0 | 0 | 1392.1 | 0 | 0 | 0 | 0
2022120108 | 5 | 0.63969 | 51175.2 | 0 | 0 | 0.34839 | 12193.65 | 0.02477 | 346.78 | 40000 | 0 | 11175.2 | 1018.45 | 0 | 346.78 | 1365.23 | 0 | 0 | 0 | 0
2022120109 | 5 | 0.63155 | 50524 | 0 | 0 | 0.33853 | 11848.55 | 0.20838 | 2917.32 | 40000 | 0 | 10524 | 1324.55 | 0 | 2917.32 | 4241.87 | 0 | 0 | 0 | 0
2022120110 | 5 | 0.61765 | 49412 | 0 | 0 | 0.3559 | 12456.5 | 0.36308 | 5083.12 | 40000 | 0 | 9412 | 3044.5 | 0 | 5083.12 | 8127.62 | 0 | 0 | 0 | 0
2022120111 | 5 | 0.60089 | 48071.2 | 0 | 0 | 0.35236 | 12332.6 | 0.36828 | 5155.92 | 40000 | 0 | 8071.2 | 4261.4 | 0 | 5155.92 | 9417.32 | 0 | 0 | 0 | 0
2022120112 | 5 | 0.5879 | 47032 | 0 | 0 | 0.34138 | 11948.3 | 0.40024 | 5603.36 | 40000 | 0 | 7032 | 4916.3 | 0 | 5603.36 | 10519.66 | 0 | 0 | 0 | 0
2022120113 | 5 | 0.57828 | 46262.4 | 0 | 0 | 0.30652 | 10728.2 | 0.39872 | 5582.08 | 40000 | 0 | 6262.4 | 4465.8 | 0 | 5582.08 | 10047.88 | 0 | 0 | 0 | 0
2022120114 | 5 | 0.57297 | 45837.6 | 0 | 0 | 0.29617 | 10365.95 | 0.38009 | 5321.26 | 40000 | 0 | 5837.6 | 4528.35 | 0 | 5321.26 | 9849.61 | 0 | 0 | 0 | 0
2022120115 | 5 | 0.5712 | 45696 | 0 | 0 | 0.32769 | 11469.15 | 0.39606 | 5544.84 | 40000 | 0 | 5696 | 5773.15 | 0 | 5544.84 | 11317.99 | 0 | 0 | 0 | 0
2022120116 | 5 | 0.57081 | 45664.8 | 0 | 0 | 0.35579 | 12452.65 | 0.35534 | 4974.76 | 40000 | 0 | 5664.8 | 6787.85 | 0 | 4974.76 | 11762.61 | 0 | 0 | 0 | 0
2022120117 | 5 | 0.57566 | 46052.8 | 0 | 0 | 0.36043 | 12615.05 | 0.22036 | 3085.04 | 40000 | 0 | 6052.8 | 6562.25 | 0 | 3085.04 | 9647.29 | 0 | 0 | 0 | 0
2022120118 | 5 | 0.58944 | 47155.2 | 0 | 0 | 0.36234 | 12681.9 | 0.02594 | 363.16 | 40000 | 0 | 7155.2 | 5526.7 | 0 | 363.16 | 5889.86 | 0 | 0 | 0 | 0
2022120119 | 5 | 0.6048 | 48384 | 0 | 0 | 0.44135 | 15447.25 | 0.00137 | 19.18 | 40000 | 0 | 8384 | 7063.25 | 0 | 19.18 | 7082.43 | 0 | 0 | 0 | 0
2022120120 | 5 | 0.60503 | 48402.4 | 0 | 0 | 0.50405 | 17641.75 | 0.00046 | 6.44 | 40000 | 0 | 8402.4 | 9239.35 | 0 | 6.44 | 9245.79 | 0 | 0 | 0 | 0
2022120121 | 5 | 0.59805 | 47844 | 0 | 0 | 0.51372 | 17980.2 | 0 | 0 | 40000 | 0 | 7844 | 10136.2 | 0 | 0 | 10136.2 | 0 | 0 | 0 | 0
2022120122 | 5 | 0.57979 | 46383.2 | 0 | 0 | 0.51083 | 17879.05 | 0 | 0 | 40000 | 0 | 6383.2 | 11495.85 | 0 | 0 | 11495.85 | 0 | 0 | 0 | 0
2022120123 | 5 | 0.55143 | 44114.4 | 0 | 0 | 0.52338 | 18318.3 | 0 | 0 | 40000 | 0 | 4114.4 | 14203.9 | 0 | 0 | 14203.9 | 0 | 0 | 0 | 0
2022120124 | 5 | 0.52269 | 41815.2 | 0 | 0 | 0.52688 | 18440.8 | 4e-05 | 0.56 | 40000 | 0 | 1815.2 | 16625.6 | 0 | 0.56 | 16626.16 | 0 | 0 | 0 | 0
2022120201 | 6 | 0.50061 | 40048.8 | 0 | 0 | 0.51522 | 18032.7 | 4e-05 | 0.56 | 40000 | 0 | 48.8 | 17983.9 | 0 | 0.56 | 17984.46 | 0 | 0 | 0 | 0
2022120202 | 6 | 0.48919 | 39135.2 | 0 | 0 | 0.51849 | 18147.15 | 0 | 0 | 39135.2 | 864.8 | 0 | 18147.15 | 0 | 0 | 19011.95 | 0 | 0 | 0 | 0
2022120203 | 6 | 0.48209 | 38567.2 | 0 | 0 | 0.51337 | 17967.95 | 0 | 0 | 38567.2 | 1432.8 | 0 | 17967.95 | 0 | 0 | 19400.75 | 0 | 0 | 0 | 0
2022120204 | 6 | 0.48225 | 38580 | 0 | 0 | 0.51265 | 17942.75 | 4e-05 | 0.56 | 38580 | 1420 | 0 | 17942.75 | 0 | 0.56 | 19363.31 | 0 | 0 | 0 | 0
2022120205 | 6 | 0.49013 | 39210.4 | 0 | 0 | 0.51485 | 18019.75 | 4e-05 | 0.56 | 39210.4 | 789.6 | 0 | 18019.75 | 0 | 0.56 | 18809.91 | 0 | 0 | 0 | 0
2022120206 | 6 | 0.5139 | 41112 | 0 | 0 | 0.52094 | 18232.9 | 4e-05 | 0.56 | 40000 | 0 | 1112 | 17120.9 | 0 | 0.56 | 17121.46 | 0 | 0 | 0 | 0
2022120207 | 6 | 0.54955 | 43964 | 0 | 0 | 0.51208 | 17922.8 | 4e-05 | 0.56 | 40000 | 0 | 3964 | 13958.8 | 0 | 0.56 | 13959.36 | 0 | 0 | 0 | 0
2022120208 | 6 | 0.56619 | 45295.2 | 0 | 0 | 0.50436 | 17652.6 | 0.00665 | 93.1 | 40000 | 0 | 5295.2 | 12357.4 | 0 | 93.1 | 12450.5 | 0 | 0 | 0 | 0
2022120209 | 6 | 0.5669 | 45352 | 0 | 0 | 0.48477 | 16966.95 | 0.08577 | 1200.78 | 40000 | 0 | 5352 | 11614.95 | 0 | 1200.78 | 12815.73 | 0 | 0 | 0 | 0
2022120210 | 6 | 0.56916 | 45532.8 | 0 | 0 | 0.45326 | 15864.1 | 0.18046 | 2526.44 | 40000 | 0 | 5532.8 | 10331.3 | 0 | 2526.44 | 12857.74 | 0 | 0 | 0 | 0
2022120211 | 6 | 0.56599 | 45279.2 | 0 | 0 | 0.41821 | 14637.35 | 0.28852 | 4039.28 | 40000 | 0 | 5279.2 | 9358.15 | 0 | 4039.28 | 13397.43 | 0 | 0 | 0 | 0
2022120212 | 6 | 0.56266 | 45012.8 | 0 | 0 | 0.40037 | 14012.95 | 0.35716 | 5000.24 | 40000 | 0 | 5012.8 | 9000.15 | 0 | 5000.24 | 14000.39 | 0 | 0 | 0 | 0
2022120213 | 6 | 0.55834 | 44667.2 | 0 | 0 | 0.40711 | 14248.85 | 0.34151 | 4781.14 | 40000 | 0 | 4667.2 | 9581.65 | 0 | 4781.14 | 14362.79 | 0 | 0 | 0 | 0
2022120214 | 6 | 0.55363 | 44290.4 | 0 | 0 | 0.43581 | 15253.35 | 0.29104 | 4074.56 | 40000 | 0 | 4290.4 | 10962.95 | 0 | 4074.56 | 15037.51 | 0 | 0 | 0 | 0
2022120215 | 6 | 0.54906 | 43924.8 | 0 | 0 | 0.45096 | 15783.6 | 0.23618 | 3306.52 | 40000 | 0 | 3924.8 | 11858.8 | 0 | 3306.52 | 15165.32 | 0 | 0 | 0 | 0
2022120216 | 6 | 0.54597 | 43677.6 | 0 | 0 | 0.44692 | 15642.2 | 0.22191 | 3106.74 | 40000 | 0 | 3677.6 | 11964.6 | 0 | 3106.74 | 15071.34 | 0 | 0 | 0 | 0
2022120217 | 6 | 0.54272 | 43417.6 | 0 | 0 | 0.40756 | 14264.6 | 0.16986 | 2378.04 | 40000 | 0 | 3417.6 | 10847 | 0 | 2378.04 | 13225.04 | 0 | 0 | 0 | 0
2022120218 | 6 | 0.54645 | 43716 | 0 | 0 | 0.36127 | 12644.45 | 0.02116 | 296.24 | 40000 | 0 | 3716 | 8928.45 | 0 | 296.24 | 9224.69 | 0 | 0 | 0 | 0
2022120219 | 6 | 0.55345 | 44276 | 0 | 0 | 0.36078 | 12627.3 | 0 | 0 | 40000 | 0 | 4276 | 8351.3 | 0 | 0 | 8351.3 | 0 | 0 | 0 | 0
2022120220 | 6 | 0.54746 | 43796.8 | 0 | 0 | 0.36891 | 12911.85 | 0 | 0 | 40000 | 0 | 3796.8 | 9115.05 | 0 | 0 | 9115.05 | 0 | 0 | 0 | 0
2022120221 | 6 | 0.53764 | 43011.2 | 0 | 0 | 0.34299 | 12004.65 | 0 | 0 | 40000 | 0 | 3011.2 | 8993.45 | 0 | 0 | 8993.45 | 0 | 0 | 0 | 0
2022120222 | 6 | 0.52293 | 41834.4 | 0 | 0 | 0.31351 | 10972.85 | 0 | 0 | 40000 | 0 | 1834.4 | 9138.45 | 0 | 0 | 9138.45 | 0 | 0 | 0 | 0
2022120223 | 6 | 0.50503 | 40402.4 | 0 | 0 | 0.29007 | 10152.45 | 0 | 0 | 40000 | 0 | 402.4 | 9750.05 | 0 | 0 | 9750.05 | 0 | 0 | 0 | 0
2022120224 | 6 | 0.48306 | 38644.8 | 0 | 0 | 0.26758 | 9365.3 | 0 | 0 | 38644.8 | 1355.2 | 0 | 9365.3 | 0 | 0 | 10720.5 | 0 | 0 | 0 | 0
2022120301 | 7 | 0.46411 | 37128.8 | 0 | 0 | 0.26788 | 9375.8 | 0 | 0 | 37128.8 | 2871.2 | 0 | 9375.8 | 0 | 0 | 12247 | 0 | 0 | 0 | 0
2022120302 | 7 | 0.44995 | 35996 | 0 | 0 | 0.32078 | 11227.3 | 0 | 0 | 35996 | 4004 | 0 | 11227.3 | 0 | 0 | 15231.3 | 0 | 0 | 0 | 0
2022120303 | 7 | 0.44205 | 35364 | 0 | 0 | 0.38114 | 13339.9 | 0 | 0 | 35364 | 4636 | 0 | 13339.9 | 0 | 0 | 17975.9 | 0 | 0 | 0 | 0
2022120304 | 7 | 0.44234 | 35387.2 | 0 | 0 | 0.43974 | 15390.9 | 0 | 0 | 35387.2 | 4612.8 | 0 | 15390.9 | 0 | 0 | 20003.7 | 0 | 0 | 0 | 0
2022120305 | 7 | 0.44947 | 35957.6 | 0 | 0 | 0.46267 | 16193.45 | 0 | 0 | 35957.6 | 4042.4 | 0 | 16193.45 | 0 | 0 | 20235.85 | 0 | 0 | 0 | 0
2022120306 | 7 | 0.46115 | 36892 | 0 | 0 | 0.47034 | 16461.9 | 0 | 0 | 36892 | 3108 | 0 | 16461.9 | 0 | 0 | 19569.9 | 0 | 0 | 0 | 0
2022120307 | 7 | 0.47939 | 38351.2 | 0 | 0 | 0.46027 | 16109.45 | 0 | 0 | 38351.2 | 1648.8 | 0 | 16109.45 | 0 | 0 | 17758.25 | 0 | 0 | 0 | 0
2022120308 | 7 | 0.4992 | 39936 | 0 | 0 | 0.45176 | 15811.6 | 0.01096 | 153.44 | 39936 | 64 | 0 | 15811.6 | 0 | 153.44 | 16029.04 | 0 | 0 | 0 | 0
2022120309 | 7 | 0.52354 | 41883.2 | 0 | 0 | 0.41392 | 14487.2 | 0.17046 | 2386.44 | 40000 | 0 | 1883.2 | 12604 | 0 | 2386.44 | 14990.44 | 0 | 0 | 0 | 0
2022120310 | 7 | 0.53784 | 43027.2 | 0 | 0 | 0.3881 | 13583.5 | 0.28296 | 3961.44 | 40000 | 0 | 3027.2 | 10556.3 | 0 | 3961.44 | 14517.74 | 0 | 0 | 0 | 0
2022120311 | 7 | 0.54446 | 43556.8 | 0 | 0 | 0.3272 | 11452 | 0.39448 | 5522.72 | 40000 | 0 | 3556.8 | 7895.2 | 0 | 5522.72 | 13417.92 | 0 | 0 | 0 | 0
2022120312 | 7 | 0.54255 | 43404 | 0 | 0 | 0.23571 | 8249.85 | 0.46426 | 6499.64 | 40000 | 0 | 3404 | 4845.85 | 0 | 6499.64 | 11345.49 | 0 | 0 | 0 | 0
2022120313 | 7 | 0.53868 | 43094.4 | 0 | 0 | 0.17205 | 6021.75 | 0.48287 | 6760.18 | 40000 | 0 | 3094.4 | 2927.35 | 0 | 6760.18 | 9687.53 | 0 | 0 | 0 | 0
2022120314 | 7 | 0.53399 | 42719.2 | 0 | 0 | 0.14665 | 5132.75 | 0.47379 | 6633.06 | 40000 | 0 | 2719.2 | 2413.55 | 0 | 6633.06 | 9046.61 | 0 | 0 | 0 | 0
2022120315 | 7 | 0.53181 | 42544.8 | 0 | 0 | 0.1441 | 5043.5 | 0.46546 | 6516.44 | 40000 | 0 | 2544.8 | 2498.7 | 0 | 6516.44 | 9015.14 | 0 | 0 | 0 | 0
2022120316 | 7 | 0.5318 | 42544 | 0 | 0 | 0.13773 | 4820.55 | 0.43895 | 6145.3 | 40000 | 0 | 2544 | 2276.55 | 0 | 6145.3 | 8421.85 | 0 | 0 | 0 | 0
2022120317 | 7 | 0.53397 | 42717.6 | 0 | 0 | 0.12923 | 4523.05 | 0.24833 | 3476.62 | 40000 | 0 | 2717.6 | 1805.45 | 0 | 3476.62 | 5282.07 | 0 | 0 | 0 | 0
2022120318 | 7 | 0.54921 | 43936.8 | 0 | 0 | 0.11677 | 4086.95 | 0.01965 | 275.1 | 40000 | 0 | 3936.8 | 150.15 | 0 | 275.1 | 425.25 | 0 | 0 | 0 | 0
2022120319 | 7 | 0.55614 | 44491.2 | 0 | 0 | 0.12542 | 4389.7 | 0 | 0 | 40000 | 0 | 4389.7 | 0 | 0 | 0 | 0 | 101.5 | 0 | 0 | 101.5
2022120320 | 7 | 0.55339 | 44271.2 | 0 | 0 | 0.11567 | 4048.45 | 0 | 0 | 40000 | 0 | 4048.45 | 0 | 0 | 0 | 0 | 222.75 | 0 | 0 | 222.75
2022120321 | 7 | 0.54755 | 43804 | 0 | 0 | 0.11419 | 3996.65 | 0 | 0 | 40000 | 0 | 3804 | 192.65 | 0 | 0 | 192.65 | 0 | 0 | 0 | 0
2022120322 | 7 | 0.53744 | 42995.2 | 0 | 0 | 0.10685 | 3739.75 | 0 | 0 | 40000 | 0 | 2995.2 | 744.55 | 0 | 0 | 744.55 | 0 | 0 | 0 | 0
2022120323 | 7 | 0.51843 | 41474.4 | 0 | 0 | 0.09102 | 3185.7 | 0 | 0 | 40000 | 0 | 1474.4 | 1711.3 | 0 | 0 | 1711.3 | 0 | 0 | 0 | 0
2022120324 | 7 | 0.49839 | 39871.2 | 0 | 0 | 0.09373 | 3280.55 | 0 | 0 | 39871.2 | 128.8 | 0 | 3280.55 | 0 | 0 | 3409.35 | 0 | 0 | 0 | 0
2022120401 | 1 | 0.47892 | 38313.6 | 0 | 0 | 0.08901 | 3115.35 | 0 | 0 | 38313.6 | 1686.4 | 0 | 3115.35 | 0 | 0 | 4801.75 | 0 | 0 | 0 | 0
2022120402 | 1 | 0.4639 | 37112 | 0 | 0 | 0.0947 | 3314.5 | 0 | 0 | 37112 | 2888 | 0 | 3314.5 | 0 | 0 | 6202.5 | 0 | 0 | 0 | 0
2022120403 | 1 | 0.45427 | 36341.6 | 0 | 0 | 0.10484 | 3669.4 | 0 | 0 | 36341.6 | 3658.4 | 0 | 3669.4 | 0 | 0 | 7327.8 | 0 | 0 | 0 | 0
2022120404 | 1 | 0.45146 | 36116.8 | 0 | 0 | 0.11393 | 3987.55 | 0 | 0 | 36116.8 | 3883.2 | 0 | 3987.55 | 0 | 0 | 7870.75 | 0 | 0 | 0 | 0
2022120405 | 1 | 0.45328 | 36262.4 | 0 | 0 | 0.11316 | 3960.6 | 0 | 0 | 36262.4 | 3737.6 | 0 | 3960.6 | 0 | 0 | 7698.2 | 0 | 0 | 0 | 0
2022120406 | 1 | 0.45835 | 36668 | 0 | 0 | 0.13394 | 4687.9 | 0 | 0 | 36668 | 3332 | 0 | 4687.9 | 0 | 0 | 8019.9 | 0 | 0 | 0 | 0
2022120407 | 1 | 0.47089 | 37671.2 | 0 | 0 | 0.15204 | 5321.4 | 0 | 0 | 37671.2 | 2328.8 | 0 | 5321.4 | 0 | 0 | 7650.2 | 0 | 0 | 0 | 0
2022120408 | 1 | 0.48433 | 38746.4 | 0 | 0 | 0.17801 | 6230.35 | 0.00695 | 97.3 | 38746.4 | 1253.6 | 0 | 6230.35 | 0 | 97.3 | 7581.25 | 0 | 0 | 0 | 0
2022120409 | 1 | 0.50201 | 40160.8 | 0 | 0 | 0.1576 | 5516 | 0.10545 | 1476.3 | 40000 | 0 | 160.8 | 5355.2 | 0 | 1476.3 | 6831.5 | 0 | 0 | 0 | 0
2022120410 | 1 | 0.51557 | 41245.6 | 0 | 0 | 0.13217 | 4625.95 | 0.29096 | 4073.44 | 40000 | 0 | 1245.6 | 3380.35 | 0 | 4073.44 | 7453.79 | 0 | 0 | 0 | 0
2022120411 | 1 | 0.5218 | 41744 | 0 | 0 | 0.13151 | 4602.85 | 0.37285 | 5219.9 | 40000 | 0 | 1744 | 2858.85 | 0 | 5219.9 | 8078.75 | 0 | 0 | 0 | 0
2022120412 | 1 | 0.52152 | 41721.6 | 0 | 0 | 0.13464 | 4712.4 | 0.4223 | 5912.2 | 40000 | 0 | 1721.6 | 2990.8 | 0 | 5912.2 | 8903 | 0 | 0 | 0 | 0
2022120413 | 1 | 0.51896 | 41516.8 | 0 | 0 | 0.16309 | 5708.15 | 0.43395 | 6075.3 | 40000 | 0 | 1516.8 | 4191.35 | 0 | 6075.3 | 10266.65 | 0 | 0 | 0 | 0
2022120414 | 1 | 0.51609 | 41287.2 | 0 | 0 | 0.17294 | 6052.9 | 0.41111 | 5755.54 | 40000 | 0 | 1287.2 | 4765.7 | 0 | 5755.54 | 10521.24 | 0 | 0 | 0 | 0
2022120415 | 1 | 0.51741 | 41392.8 | 0 | 0 | 0.14345 | 5020.75 | 0.3727 | 5217.8 | 40000 | 0 | 1392.8 | 3627.95 | 0 | 5217.8 | 8845.75 | 0 | 0 | 0 | 0
2022120416 | 1 | 0.52025 | 41620 | 0 | 0 | 0.13111 | 4588.85 | 0.31538 | 4415.32 | 40000 | 0 | 1620 | 2968.85 | 0 | 4415.32 | 7384.17 | 0 | 0 | 0 | 0
2022120417 | 1 | 0.52654 | 42123.2 | 0 | 0 | 0.12046 | 4216.1 | 0.15952 | 2233.28 | 40000 | 0 | 2123.2 | 2092.9 | 0 | 2233.28 | 4326.18 | 0 | 0 | 0 | 0
2022120418 | 1 | 0.5488 | 43904 | 0 | 0 | 0.14925 | 5223.75 | 0.01048 | 146.72 | 40000 | 0 | 3904 | 1319.75 | 0 | 146.72 | 1466.47 | 0 | 0 | 0 | 0
2022120419 | 1 | 0.56338 | 45070.4 | 0 | 0 | 0.21148 | 7401.8 | 0 | 0 | 40000 | 0 | 5070.4 | 2331.4 | 0 | 0 | 2331.4 | 0 | 0 | 0 | 0
2022120420 | 1 | 0.56094 | 44875.2 | 0 | 0 | 0.27385 | 9584.75 | 0 | 0 | 40000 | 0 | 4875.2 | 4709.55 | 0 | 0 | 4709.55 | 0 | 0 | 0 | 0
2022120421 | 1 | 0.55447 | 44357.6 | 0 | 0 | 0.34504 | 12076.4 | 0 | 0 | 40000 | 0 | 4357.6 | 7718.8 | 0 | 0 | 7718.8 | 0 | 0 | 0 | 0
2022120422 | 1 | 0.5431 | 43448 | 0 | 0 | 0.39919 | 13971.65 | 0 | 0 | 40000 | 0 | 3448 | 10523.65 | 0 | 0 | 10523.65 | 0 | 0 | 0 | 0
2022120423 | 1 | 0.52147 | 41717.6 | 0 | 0 | 0.44197 | 15468.95 | 0 | 0 | 40000 | 0 | 1717.6 | 13751.35 | 0 | 0 | 13751.35 | 0 | 0 | 0 | 0
2022120424 | 1 | 0.49426 | 39540.8 | 0 | 0 | 0.47051 | 16467.85 | 0 | 0 | 39540.8 | 459.2 | 0 | 16467.85 | 0 | 0 | 16927.05 | 0 | 0 | 0 | 0
2022120501 | 2 | 0.47046 | 37636.8 | 0 | 0 | 0.49445 | 17305.75 | 0 | 0 | 37636.8 | 2363.2 | 0 | 17305.75 | 0 | 0 | 19668.95 | 0 | 0 | 0 | 0
2022120502 | 2 | 0.4542 | 36336 | 0 | 0 | 0.49887 | 17460.45 | 0 | 0 | 36336 | 3664 | 0 | 17460.45 | 0 | 0 | 21124.45 | 0 | 0 | 0 | 0
2022120503 | 2 | 0.44854 | 35883.2 | 0 | 0 | 0.49921 | 17472.35 | 0 | 0 | 35883.2 | 4116.8 | 0 | 17472.35 | 0 | 0 | 21589.15 | 0 | 0 | 0 | 0
2022120504 | 2 | 0.4455 | 35640 | 0 | 0 | 0.48912 | 17119.2 | 0 | 0 | 35640 | 4360 | 0 | 17119.2 | 0 | 0 | 21479.2 | 0 | 0 | 0 | 0
2022120505 | 2 | 0.45408 | 36326.4 | 0 | 0 | 0.48342 | 16919.7 | 0 | 0 | 36326.4 | 3673.6 | 0 | 16919.7 | 0 | 0 | 20593.3 | 0 | 0 | 0 | 0
2022120506 | 2 | 0.47636 | 38108.8 | 0 | 0 | 0.46702 | 16345.7 | 0 | 0 | 38108.8 | 1891.2 | 0 | 16345.7 | 0 | 0 | 18236.9 | 0 | 0 | 0 | 0
2022120507 | 2 | 0.51286 | 41028.8 | 0 | 0 | 0.46047 | 16116.45 | 0 | 0 | 40000 | 0 | 1028.8 | 15087.65 | 0 | 0 | 15087.65 | 0 | 0 | 0 | 0
2022120508 | 2 | 0.52839 | 42271.2 | 0 | 0 | 0.4467 | 15634.5 | 0.00498 | 69.72 | 40000 | 0 | 2271.2 | 13363.3 | 0 | 69.72 | 13433.02 | 0 | 0 | 0 | 0
2022120509 | 2 | 0.53631 | 42904.8 | 0 | 0 | 0.44012 | 15404.2 | 0.10257 | 1435.98 | 40000 | 0 | 2904.8 | 12499.4 | 0 | 1435.98 | 13935.38 | 0 | 0 | 0 | 0
2022120510 | 2 | 0.54536 | 43628.8 | 0 | 0 | 0.40928 | 14324.8 | 0.25848 | 3618.72 | 40000 | 0 | 3628.8 | 10696 | 0 | 3618.72 | 14314.72 | 0 | 0 | 0 | 0
2022120511 | 2 | 0.55047 | 44037.6 | 0 | 0 | 0.4278 | 14973 | 0.33503 | 4690.42 | 40000 | 0 | 4037.6 | 10935.4 | 0 | 4690.42 | 15625.82 | 0 | 0 | 0 | 0
2022120512 | 2 | 0.55474 | 44379.2 | 0 | 0 | 0.42342 | 14819.7 | 0.37013 | 5181.82 | 40000 | 0 | 4379.2 | 10440.5 | 0 | 5181.82 | 15622.32 | 0 | 0 | 0 | 0
2022120513 | 2 | 0.55818 | 44654.4 | 0 | 0 | 0.42914 | 15019.9 | 0.35724 | 5001.36 | 40000 | 0 | 4654.4 | 10365.5 | 0 | 5001.36 | 15366.86 | 0 | 0 | 0 | 0
2022120514 | 2 | 0.56375 | 45100 | 0 | 0 | 0.42749 | 14962.15 | 0.36789 | 5150.46 | 40000 | 0 | 5100 | 9862.15 | 0 | 5150.46 | 15012.61 | 0 | 0 | 0 | 0
2022120515 | 2 | 0.57057 | 45645.6 | 0 | 0 | 0.43733 | 15306.55 | 0.33749 | 4724.86 | 40000 | 0 | 5645.6 | 9660.95 | 0 | 4724.86 | 14385.81 | 0 | 0 | 0 | 0
2022120516 | 2 | 0.57355 | 45884 | 0 | 0 | 0.44816 | 15685.6 | 0.29955 | 4193.7 | 40000 | 0 | 5884 | 9801.6 | 0 | 4193.7 | 13995.3 | 0 | 0 | 0 | 0
2022120517 | 2 | 0.57604 | 46083.2 | 0 | 0 | 0.44727 | 15654.45 | 0.18239 | 2553.46 | 40000 | 0 | 6083.2 | 9571.25 | 0 | 2553.46 | 12124.71 | 0 | 0 | 0 | 0
2022120518 | 2 | 0.58803 | 47042.4 | 0 | 0 | 0.44743 | 15660.05 | 0.01029 | 144.06 | 40000 | 0 | 7042.4 | 8617.65 | 0 | 144.06 | 8761.71 | 0 | 0 | 0 | 0
2022120519 | 2 | 0.59854 | 47883.2 | 0 | 0 | 0.4945 | 17307.5 | 0 | 0 | 40000 | 0 | 7883.2 | 9424.3 | 0 | 0 | 9424.3 | 0 | 0 | 0 | 0
2022120520 | 2 | 0.59248 | 47398.4 | 0 | 0 | 0.52106 | 18237.1 | 0 | 0 | 40000 | 0 | 7398.4 | 10838.7 | 0 | 0 | 10838.7 | 0 | 0 | 0 | 0
2022120521 | 2 | 0.57974 | 46379.2 | 0 | 0 | 0.54015 | 18905.25 | 0 | 0 | 40000 | 0 | 6379.2 | 12526.05 | 0 | 0 | 12526.05 | 0 | 0 | 0 | 0
2022120522 | 2 | 0.56106 | 44884.8 | 0 | 0 | 0.53758 | 18815.3 | 0 | 0 | 40000 | 0 | 4884.8 | 13930.5 | 0 | 0 | 13930.5 | 0 | 0 | 0 | 0
2022120523 | 2 | 0.52879 | 42303.2 | 0 | 0 | 0.51114 | 17889.9 | 0 | 0 | 40000 | 0 | 2303.2 | 15586.7 | 0 | 0 | 15586.7 | 0 | 0 | 0 | 0
2022120524 | 2 | 0.49229 | 39383.2 | 0 | 0 | 0.48645 | 17025.75 | 0 | 0 | 39383.2 | 616.8 | 0 | 17025.75 | 0 | 0 | 17642.55 | 0 | 0 | 0 | 0
2022120601 | 3 | 0.46883 | 37506.4 | 0 | 0 | 0.45626 | 15969.1 | 0 | 0 | 37506.4 | 2493.6 | 0 | 15969.1 | 0 | 0 | 18462.7 | 0 | 0 | 0 | 0
2022120602 | 3 | 0.45027 | 36021.6 | 0 | 0 | 0.4334 | 15169 | 0 | 0 | 36021.6 | 3978.4 | 0 | 15169 | 0 | 0 | 19147.4 | 0 | 0 | 0 | 0
2022120603 | 3 | 0.44041 | 35232.8 | 0 | 0 | 0.41313 | 14459.55 | 0 | 0 | 35232.8 | 4767.2 | 0 | 14459.55 | 0 | 0 | 19226.75 | 0 | 0 | 0 | 0
2022120604 | 3 | 0.43789 | 35031.2 | 0 | 0 | 0.38781 | 13573.35 | 0 | 0 | 35031.2 | 4968.8 | 0 | 13573.35 | 0 | 0 | 18542.15 | 0 | 0 | 0 | 0
2022120605 | 3 | 0.44272 | 35417.6 | 0 | 0 | 0.37316 | 13060.6 | 0 | 0 | 35417.6 | 4582.4 | 0 | 13060.6 | 0 | 0 | 17643 | 0 | 0 | 0 | 0
2022120606 | 3 | 0.46349 | 37079.2 | 0 | 0 | 0.34378 | 12032.3 | 0 | 0 | 37079.2 | 2920.8 | 0 | 12032.3 | 0 | 0 | 14953.1 | 0 | 0 | 0 | 0
2022120607 | 3 | 0.50238 | 40190.4 | 0 | 0 | 0.31351 | 10972.85 | 0 | 0 | 40000 | 0 | 190.4 | 10782.45 | 0 | 0 | 10782.45 | 0 | 0 | 0 | 0
2022120608 | 3 | 0.51861 | 41488.8 | 0 | 0 | 0.28111 | 9838.85 | 0.00924 | 129.36 | 40000 | 0 | 1488.8 | 8350.05 | 0 | 129.36 | 8479.41 | 0 | 0 | 0 | 0
2022120609 | 3 | 0.52292 | 41833.6 | 0 | 0 | 0.23411 | 8193.85 | 0.0737 | 1031.8 | 40000 | 0 | 1833.6 | 6360.25 | 0 | 1031.8 | 7392.05 | 0 | 0 | 0 | 0
2022120610 | 3 | 0.53235 | 42588 | 0 | 0 | 0.20853 | 7298.55 | 0.13763 | 1926.82 | 40000 | 0 | 2588 | 4710.55 | 0 | 1926.82 | 6637.37 | 0 | 0 | 0 | 0
2022120611 | 3 | 0.54627 | 43701.6 | 0 | 0 | 0.20327 | 7114.45 | 0.20728 | 2901.92 | 40000 | 0 | 3701.6 | 3412.85 | 0 | 2901.92 | 6314.77 | 0 | 0 | 0 | 0
2022120612 | 3 | 0.55509 | 44407.2 | 0 | 0 | 0.18986 | 6645.1 | 0.26162 | 3662.68 | 40000 | 0 | 4407.2 | 2237.9 | 0 | 3662.68 | 5900.58 | 0 | 0 | 0 | 0
2022120613 | 3 | 0.56485 | 45188 | 0 | 0 | 0.19189 | 6716.15 | 0.30453 | 4263.42 | 40000 | 0 | 5188 | 1528.15 | 0 | 4263.42 | 5791.57 | 0 | 0 | 0 | 0
2022120614 | 3 | 0.57761 | 46208.8 | 0 | 0 | 0.20447 | 7156.45 | 0.30712 | 4299.68 | 40000 | 0 | 6208.8 | 947.65 | 0 | 4299.68 | 5247.33 | 0 | 0 | 0 | 0
2022120615 | 3 | 0.58391 | 46712.8 | 0 | 0 | 0.2149 | 7521.5 | 0.26014 | 3641.96 | 40000 | 0 | 6712.8 | 808.7 | 0 | 3641.96 | 4450.66 | 0 | 0 | 0 | 0
2022120616 | 3 | 0.586 | 46880 | 0 | 0 | 0.21392 | 7487.2 | 0.16163 | 2262.82 | 40000 | 0 | 6880 | 607.2 | 0 | 2262.82 | 2870.02 | 0 | 0 | 0 | 0
2022120617 | 3 | 0.58227 | 46581.6 | 0 | 0 | 0.21303 | 7456.05 | 0.0611 | 855.4 | 40000 | 0 | 6581.6 | 874.45 | 0 | 855.4 | 1729.85 | 0 | 0 | 0 | 0
2022120618 | 3 | 0.59063 | 47250.4 | 0 | 0 | 0.2218 | 7763 | 0.00518 | 72.52 | 40000 | 0 | 7250.4 | 512.6 | 0 | 72.52 | 585.12 | 0 | 0 | 0 | 0
2022120619 | 3 | 0.59964 | 47971.2 | 0 | 0 | 0.25648 | 8976.8 | 0 | 0 | 40000 | 0 | 7971.2 | 1005.6 | 0 | 0 | 1005.6 | 0 | 0 | 0 | 0
2022120620 | 3 | 0.59495 | 47596 | 0 | 0 | 0.29754 | 10413.9 | 0 | 0 | 40000 | 0 | 7596 | 2817.9 | 0 | 0 | 2817.9 | 0 | 0 | 0 | 0
2022120621 | 3 | 0.58318 | 46654.4 | 0 | 0 | 0.32546 | 11391.1 | 0 | 0 | 40000 | 0 | 6654.4 | 4736.7 | 0 | 0 | 4736.7 | 0 | 0 | 0 | 0
2022120622 | 3 | 0.56921 | 45536.8 | 0 | 0 | 0.36937 | 12927.95 | 0 | 0 | 40000 | 0 | 5536.8 | 7391.15 | 0 | 0 | 7391.15 | 0 | 0 | 0 | 0
2022120623 | 3 | 0.53801 | 43040.8 | 0 | 0 | 0.39714 | 13899.9 | 0 | 0 | 40000 | 0 | 3040.8 | 10859.1 | 0 | 0 | 10859.1 | 0 | 0 | 0 | 0
2022120624 | 3 | 0.50091 | 40072.8 | 0 | 0 | 0.3834 | 13419 | 0 | 0 | 40000 | 0 | 72.8 | 13346.2 | 0 | 0 | 13346.2 | 0 | 0 | 0 | 0
2022120701 | 4 | 0.47309 | 37847.2 | 0 | 0 | 0.35518 | 12431.3 | 0 | 0 | 37847.2 | 2152.8 | 0 | 12431.3 | 0 | 0 | 14584.1 | 0 | 0 | 0 | 0
2022120702 | 4 | 0.45691 | 36552.8 | 0 | 0 | 0.32525 | 11383.75 | 0 | 0 | 36552.8 | 3447.2 | 0 | 11383.75 | 0 | 0 | 14830.95 | 0 | 0 | 0 | 0
2022120703 | 4 | 0.44787 | 35829.6 | 0 | 0 | 0.28773 | 10070.55 | 0 | 0 | 35829.6 | 4170.4 | 0 | 10070.55 | 0 | 0 | 14240.95 | 0 | 0 | 0 | 0
2022120704 | 4 | 0.44124 | 35299.2 | 0 | 0 | 0.24198 | 8469.3 | 0 | 0 | 35299.2 | 4700.8 | 0 | 8469.3 | 0 | 0 | 13170.1 | 0 | 0 | 0 | 0
2022120705 | 4 | 0.4312 | 34496 | 0 | 0 | 0.21887 | 7660.45 | 0 | 0 | 34496 | 5504 | 0 | 7660.45 | 0 | 0 | 13164.45 | 0 | 0 | 0 | 0
2022120706 | 4 | 0.45886 | 36708.8 | 0 | 0 | 0.18787 | 6575.45 | 0 | 0 | 36708.8 | 3291.2 | 0 | 6575.45 | 0 | 0 | 9866.65 | 0 | 0 | 0 | 0
2022120707 | 4 | 0.4997 | 39976 | 0 | 0 | 0.17028 | 5959.8 | 0 | 0 | 39976 | 24 | 0 | 5959.8 | 0 | 0 | 5983.8 | 0 | 0 | 0 | 0
2022120708 | 4 | 0.51819 | 41455.2 | 0 | 0 | 0.16432 | 5751.2 | 0.00468 | 65.52 | 40000 | 0 | 1455.2 | 4296 | 0 | 65.52 | 4361.52 | 0 | 0 | 0 | 0
2022120709 | 4 | 0.52722 | 42177.6 | 0 | 0 | 0.16255 | 5689.25 | 0.05369 | 751.66 | 40000 | 0 | 2177.6 | 3511.65 | 0 | 751.66 | 4263.31 | 0 | 0 | 0 | 0
2022120710 | 4 | 0.54189 | 43351.2 | 0 | 0 | 0.16654 | 5828.9 | 0.17207 | 2408.98 | 40000 | 0 | 3351.2 | 2477.7 | 0 | 2408.98 | 4886.68 | 0 | 0 | 0 | 0
2022120711 | 4 | 0.55612 | 44489.6 | 0 | 0 | 0.1983 | 6940.5 | 0.27205 | 3808.7 | 40000 | 0 | 4489.6 | 2450.9 | 0 | 3808.7 | 6259.6 | 0 | 0 | 0 | 0
2022120712 | 4 | 0.56987 | 45589.6 | 0 | 0 | 0.20805 | 7281.75 | 0.30641 | 4289.74 | 40000 | 0 | 5589.6 | 1692.15 | 0 | 4289.74 | 5981.89 | 0 | 0 | 0 | 0
2022120713 | 4 | 0.5819 | 46552 | 0 | 0 | 0.20233 | 7081.55 | 0.31844 | 4458.16 | 40000 | 0 | 6552 | 529.55 | 0 | 4458.16 | 4987.71 | 0 | 0 | 0 | 0
2022120714 | 4 | 0.58813 | 47050.4 | 0 | 0 | 0.2024 | 7084 | 0.30727 | 4301.78 | 40000 | 0 | 7050.4 | 33.6 | 0 | 4301.78 | 4335.38 | 0 | 0 | 0 | 0
2022120715 | 4 | 0.58941 | 47152.8 | 0 | 0 | 0.19934 | 6976.9 | 0.22103 | 3094.42 | 40000 | 0 | 6976.9 | 0 | 175.9 | 2918.52 | 2918.52 | 0 | 0 | 0 | 0
2022120716 | 4 | 0.58934 | 47147.2 | 0 | 0 | 0.20115 | 7040.25 | 0.17669 | 2473.66 | 40000 | 0 | 7040.25 | 0 | 106.95 | 2366.71 | 2366.71 | 0 | 0 | 0 | 0
2022120717 | 4 | 0.58998 | 47198.4 | 0 | 0 | 0.2029 | 7101.5 | 0.08321 | 1164.94 | 40000 | 0 | 7101.5 | 0 | 96.9 | 1068.04 | 1068.04 | 0 | 0 | 0 | 0
2022120718 | 4 | 0.59641 | 47712.8 | 0 | 0 | 0.2042 | 7147 | 0.0076 | 106.4 | 40000 | 0 | 7147 | 0 | 106.4 | 0 | 0 | 459.4 | 0 | 0 | 459.4
2022120719 | 4 | 0.60099 | 48079.2 | 0 | 0 | 0.2201 | 7703.5 | 0 | 0 | 40000 | 0 | 7703.5 | 0 | 0 | 0 | 0 | 375.7 | 0 | 0 | 375.7
2022120720 | 4 | 0.59373 | 47498.4 | 0 | 0 | 0.23003 | 8051.05 | 0 | 0 | 40000 | 0 | 7498.4 | 552.65 | 0 | 0 | 552.65 | 0 | 0 | 0 | 0
2022120721 | 4 | 0.58222 | 46577.6 | 0 | 0 | 0.23944 | 8380.4 | 0 | 0 | 40000 | 0 | 6577.6 | 1802.8 | 0 | 0 | 1802.8 | 0 | 0 | 0 | 0
2022120722 | 4 | 0.56501 | 45200.8 | 0 | 0 | 0.25476 | 8916.6 | 0 | 0 | 40000 | 0 | 5200.8 | 3715.8 | 0 | 0 | 3715.8 | 0 | 0 | 0 | 0
2022120723 | 4 | 0.53792 | 43033.6 | 0 | 0 | 0.2567 | 8984.5 | 0 | 0 | 40000 | 0 | 3033.6 | 5950.9 | 0 | 0 | 5950.9 | 0 | 0 | 0 | 0
2022120724 | 4 | 0.50796 | 40636.8 | 0 | 0 | 0.25893 | 9062.55 | 0 | 0 | 40000 | 0 | 636.8 | 8425.75 | 0 | 0 | 8425.75 | 0 | 0 | 0 | 0
2022120801 | 5 | 0.48322 | 38657.6 | 0 | 0 | 0.26968 | 9438.8 | 0 | 0 | 38657.6 | 1342.4 | 0 | 9438.8 | 0 | 0 | 10781.2 | 0 | 0 | 0 | 0
2022120802 | 5 | 0.46748 | 37398.4 | 0 | 0 | 0.26444 | 9255.4 | 0 | 0 | 37398.4 | 2601.6 | 0 | 9255.4 | 0 | 0 | 11857 | 0 | 0 | 0 | 0
2022120803 | 5 | 0.45855 | 36684 | 0 | 0 | 0.24289 | 8501.15 | 0 | 0 | 36684 | 3316 | 0 | 8501.15 | 0 | 0 | 11817.15 | 0 | 0 | 0 | 0
2022120804 | 5 | 0.45361 | 36288.8 | 0 | 0 | 0.23777 | 8321.95 | 0 | 0 | 36288.8 | 3711.2 | 0 | 8321.95 | 0 | 0 | 12033.15 | 0 | 0 | 0 | 0
2022120805 | 5 | 0.45693 | 36554.4 | 0 | 0 | 0.25355 | 8874.25 | 0 | 0 | 36554.4 | 3445.6 | 0 | 8874.25 | 0 | 0 | 12319.85 | 0 | 0 | 0 | 0
2022120806 | 5 | 0.47746 | 38196.8 | 0 | 0 | 0.26002 | 9100.7 | 0 | 0 | 38196.8 | 1803.2 | 0 | 9100.7 | 0 | 0 | 10903.9 | 0 | 0 | 0 | 0
2022120807 | 5 | 0.51562 | 41249.6 | 0 | 0 | 0.24862 | 8701.7 | 0 | 0 | 40000 | 0 | 1249.6 | 7452.1 | 0 | 0 | 7452.1 | 0 | 0 | 0 | 0
2022120808 | 5 | 0.53162 | 42529.6 | 0 | 0 | 0.24963 | 8737.05 | 0.005 | 70 | 40000 | 0 | 2529.6 | 6207.45 | 0 | 70 | 6277.45 | 0 | 0 | 0 | 0
2022120809 | 5 | 0.53608 | 42886.4 | 0 | 0 | 0.22586 | 7905.1 | 0.11815 | 1654.1 | 40000 | 0 | 2886.4 | 5018.7 | 0 | 1654.1 | 6672.8 | 0 | 0 | 0 | 0
2022120810 | 5 | 0.54996 | 43996.8 | 0 | 0 | 0.22489 | 7871.15 | 0.30103 | 4214.42 | 40000 | 0 | 3996.8 | 3874.35 | 0 | 4214.42 | 8088.77 | 0 | 0 | 0 | 0
2022120811 | 5 | 0.56365 | 45092 | 0 | 0 | 0.23939 | 8378.65 | 0.3929 | 5500.6 | 40000 | 0 | 5092 | 3286.65 | 0 | 5500.6 | 8787.25 | 0 | 0 | 0 | 0
2022120812 | 5 | 0.57537 | 46029.6 | 0 | 0 | 0.23385 | 8184.75 | 0.41569 | 5819.66 | 40000 | 0 | 6029.6 | 2155.15 | 0 | 5819.66 | 7974.81 | 0 | 0 | 0 | 0
2022120813 | 5 | 0.58595 | 46876 | 0 | 0 | 0.21269 | 7444.15 | 0.42107 | 5894.98 | 40000 | 0 | 6876 | 568.15 | 0 | 5894.98 | 6463.13 | 0 | 0 | 0 | 0
2022120814 | 5 | 0.59749 | 47799.2 | 0 | 0 | 0.19587 | 6855.45 | 0.42357 | 5929.98 | 40000 | 0 | 6855.45 | 0 | 943.75 | 4986.23 | 4986.23 | 0 | 0 | 0 | 0
2022120815 | 5 | 0.60164 | 48131.2 | 0 | 0 | 0.18478 | 6467.3 | 0.41321 | 5784.94 | 40000 | 0 | 6467.3 | 0 | 1663.9 | 4121.04 | 4121.04 | 0 | 0 | 0 | 0
2022120816 | 5 | 0.60269 | 48215.2 | 0 | 0 | 0.17865 | 6252.75 | 0.41483 | 5807.62 | 40000 | 0 | 6252.75 | 0 | 1962.45 | 3845.17 | 3845.17 | 0 | 0 | 0 | 0
2022120817 | 5 | 0.60199 | 48159.2 | 0 | 0 | 0.14891 | 5211.85 | 0.25888 | 3624.32 | 40000 | 0 | 5211.85 | 0 | 2947.35 | 676.97 | 676.97 | 0 | 0 | 0 | 0
2022120818 | 5 | 0.60304 | 48243.2 | 0 | 0 | 0.1309 | 4581.5 | 0.02601 | 364.14 | 40000 | 0 | 4581.5 | 0 | 364.14 | 0 | 0 | 3297.56 | 0 | 0 | 3297.56
2022120819 | 5 | 0.60646 | 48516.8 | 0 | 0 | 0.14055 | 4919.25 | 0.00171 | 23.94 | 40000 | 0 | 4919.25 | 0 | 23.94 | 0 | 0 | 3573.61 | 0 | 0 | 3573.61
2022120820 | 5 | 0.59479 | 47583.2 | 0 | 0 | 0.14189 | 4966.15 | 0.0009 | 12.6 | 40000 | 0 | 4966.15 | 0 | 12.6 | 0 | 0 | 2604.45 | 0 | 0 | 2604.45
2022120821 | 5 | 0.58648 | 46918.4 | 0 | 0 | 0.14773 | 5170.55 | 0 | 0 | 40000 | 0 | 5170.55 | 0 | 0 | 0 | 0 | 1747.85 | 0 | 0 | 1747.85
2022120822 | 5 | 0.56932 | 45545.6 | 0 | 0 | 0.1541 | 5393.5 | 0 | 0 | 40000 | 0 | 5393.5 | 0 | 0 | 0 | 0 | 152.1 | 0 | 0 | 152.1
2022120823 | 5 | 0.53983 | 43186.4 | 0 | 0 | 0.16013 | 5604.55 | 0 | 0 | 40000 | 0 | 3186.4 | 2418.15 | 0 | 0 | 2418.15 | 0 | 0 | 0 | 0
2022120824 | 5 | 0.5089 | 40712 | 0 | 0 | 0.15797 | 5528.95 | 0 | 0 | 40000 | 0 | 712 | 4816.95 | 0 | 0 | 4816.95 | 0 | 0 | 0 | 0
2022120901 | 6 | 0.48223 | 38578.4 | 0 | 0 | 0.14422 | 5047.7 | 0 | 0 | 38578.4 | 1421.6 | 0 | 5047.7 | 0 | 0 | 6469.3 | 0 | 0 | 0 | 0
2022120902 | 6 | 0.46595 | 37276 | 0 | 0 | 0.13262 | 4641.7 | 0 | 0 | 37276 | 2724 | 0 | 4641.7 | 0 | 0 | 7365.7 | 0 | 0 | 0 | 0
2022120903 | 6 | 0.45333 | 36266.4 | 0 | 0 | 0.12223 | 4278.05 | 0 | 0 | 36266.4 | 3733.6 | 0 | 4278.05 | 0 | 0 | 8011.65 | 0 | 0 | 0 | 0
2022120904 | 6 | 0.44859 | 35887.2 | 0 | 0 | 0.11298 | 3954.3 | 0 | 0 | 35887.2 | 4112.8 | 0 | 3954.3 | 0 | 0 | 8067.1 | 0 | 0 | 0 | 0
2022120905 | 6 | 0.45497 | 36397.6 | 0 | 0 | 0.10475 | 3666.25 | 0 | 0 | 36397.6 | 3602.4 | 0 | 3666.25 | 0 | 0 | 7268.65 | 0 | 0 | 0 | 0
2022120906 | 6 | 0.47141 | 37712.8 | 0 | 0 | 0.11276 | 3946.6 | 0 | 0 | 37712.8 | 2287.2 | 0 | 3946.6 | 0 | 0 | 6233.8 | 0 | 0 | 0 | 0
2022120907 | 6 | 0.5085 | 40680 | 0 | 0 | 0.11786 | 4125.1 | 0 | 0 | 40000 | 0 | 680 | 3445.1 | 0 | 0 | 3445.1 | 0 | 0 | 0 | 0
2022120908 | 6 | 0.52584 | 42067.2 | 0 | 0 | 0.11024 | 3858.4 | 0.00333 | 46.62 | 40000 | 0 | 2067.2 | 1791.2 | 0 | 46.62 | 1837.82 | 0 | 0 | 0 | 0
2022120909 | 6 | 0.53114 | 42491.2 | 0 | 0 | 0.09964 | 3487.4 | 0.04044 | 566.16 | 40000 | 0 | 2491.2 | 996.2 | 0 | 566.16 | 1562.36 | 0 | 0 | 0 | 0
2022120910 | 6 | 0.54231 | 43384.8 | 0 | 0 | 0.09342 | 3269.7 | 0.11243 | 1574.02 | 40000 | 0 | 3269.7 | 0 | 115.1 | 1458.92 | 1458.92 | 0 | 0 | 0 | 0
2022120911 | 6 | 0.55543 | 44434.4 | 0 | 0 | 0.10486 | 3670.1 | 0.17284 | 2419.76 | 40000 | 0 | 3670.1 | 0 | 764.3 | 1655.46 | 1655.46 | 0 | 0 | 0 | 0
2022120912 | 6 | 0.56566 | 45252.8 | 0 | 0 | 0.12082 | 4228.7 | 0.21385 | 2993.9 | 40000 | 0 | 4228.7 | 0 | 1024.1 | 1969.8 | 1969.8 | 0 | 0 | 0 | 0
2022120913 | 6 | 0.57751 | 46200.8 | 0 | 0 | 0.13343 | 4670.05 | 0.24929 | 3490.06 | 40000 | 0 | 4670.05 | 0 | 1530.75 | 1959.31 | 1959.31 | 0 | 0 | 0 | 0
2022120914 | 6 | 0.58726 | 46980.8 | 0 | 0 | 0.14923 | 5223.05 | 0.26436 | 3701.04 | 40000 | 0 | 5223.05 | 0 | 1757.75 | 1943.29 | 1943.29 | 0 | 0 | 0 | 0
2022120915 | 6 | 0.59479 | 47583.2 | 0 | 0 | 0.17367 | 6078.45 | 0.24823 | 3475.22 | 40000 | 0 | 6078.45 | 0 | 1504.75 | 1970.47 | 1970.47 | 0 | 0 | 0 | 0
2022120916 | 6 | 0.59491 | 47592.8 | 0 | 0 | 0.19516 | 6830.6 | 0.22072 | 3090.08 | 40000 | 0 | 6830.6 | 0 | 762.2 | 2327.88 | 2327.88 | 0 | 0 | 0 | 0
2022120917 | 6 | 0.58986 | 47188.8 | 0 | 0 | 0.19647 | 6876.45 | 0.09624 | 1347.36 | 40000 | 0 | 6876.45 | 0 | 312.35 | 1035.01 | 1035.01 | 0 | 0 | 0 | 0
2022120918 | 6 | 0.59217 | 47373.6 | 0 | 0 | 0.19594 | 6857.9 | 0.00697 | 97.58 | 40000 | 0 | 6857.9 | 0 | 97.58 | 0 | 0 | 418.12 | 0 | 0 | 418.12
2022120919 | 6 | 0.59168 | 47334.4 | 0 | 0 | 0.2057 | 7199.5 | 0 | 0 | 40000 | 0 | 7199.5 | 0 | 0 | 0 | 0 | 134.9 | 0 | 0 | 134.9
2022120920 | 6 | 0.57828 | 46262.4 | 0 | 0 | 0.21454 | 7508.9 | 0 | 0 | 40000 | 0 | 6262.4 | 1246.5 | 0 | 0 | 1246.5 | 0 | 0 | 0 | 0
2022120921 | 6 | 0.56387 | 45109.6 | 0 | 0 | 0.21982 | 7693.7 | 0 | 0 | 40000 | 0 | 5109.6 | 2584.1 | 0 | 0 | 2584.1 | 0 | 0 | 0 | 0
2022120922 | 6 | 0.55033 | 44026.4 | 0 | 0 | 0.2433 | 8515.5 | 0 | 0 | 40000 | 0 | 4026.4 | 4489.1 | 0 | 0 | 4489.1 | 0 | 0 | 0 | 0
2022120923 | 6 | 0.52875 | 42300 | 0 | 0 | 0.2953 | 10335.5 | 0 | 0 | 40000 | 0 | 2300 | 8035.5 | 0 | 0 | 8035.5 | 0 | 0 | 0 | 0
2022120924 | 6 | 0.49934 | 39947.2 | 0 | 0 | 0.29455 | 10309.25 | 0 | 0 | 39947.2 | 52.8 | 0 | 10309.25 | 0 | 0 | 10362.05 | 0 | 0 | 0 | 0
2022121001 | 7 | 0.47478 | 37982.4 | 0 | 0 | 0.25821 | 9037.35 | 0 | 0 | 37982.4 | 2017.6 | 0 | 9037.35 | 0 | 0 | 11054.95 | 0 | 0 | 0 | 0
2022121002 | 7 | 0.45999 | 36799.2 | 0 | 0 | 0.24431 | 8550.85 | 0 | 0 | 36799.2 | 3200.8 | 0 | 8550.85 | 0 | 0 | 11751.65 | 0 | 0 | 0 | 0
2022121003 | 7 | 0.4508 | 36064 | 0 | 0 | 0.22665 | 7932.75 | 0 | 0 | 36064 | 3936 | 0 | 7932.75 | 0 | 0 | 11868.75 | 0 | 0 | 0 | 0
2022121004 | 7 | 0.44045 | 35236 | 0 | 0 | 0.19406 | 6792.1 | 0 | 0 | 35236 | 4764 | 0 | 6792.1 | 0 | 0 | 11556.1 | 0 | 0 | 0 | 0
2022121005 | 7 | 0.43891 | 35112.8 | 0 | 0 | 0.17337 | 6067.95 | 0 | 0 | 35112.8 | 4887.2 | 0 | 6067.95 | 0 | 0 | 10955.15 | 0 | 0 | 0 | 0
2022121006 | 7 | 0.44328 | 35462.4 | 0 | 0 | 0.16477 | 5766.95 | 0 | 0 | 35462.4 | 4537.6 | 0 | 5766.95 | 0 | 0 | 10304.55 | 0 | 0 | 0 | 0
2022121007 | 7 | 0.45702 | 36561.6 | 0 | 0 | 0.16002 | 5600.7 | 0 | 0 | 36561.6 | 3438.4 | 0 | 5600.7 | 0 | 0 | 9039.1 | 0 | 0 | 0 | 0
2022121008 | 7 | 0.47462 | 37969.6 | 0 | 0 | 0.14722 | 5152.7 | 0.00643 | 90.02 | 37969.6 | 2030.4 | 0 | 5152.7 | 0 | 90.02 | 7273.12 | 0 | 0 | 0 | 0
2022121009 | 7 | 0.49438 | 39550.4 | 0 | 0 | 0.13537 | 4737.95 | 0.06318 | 884.52 | 39550.4 | 449.6 | 0 | 4737.95 | 0 | 884.52 | 6072.07 | 0 | 0 | 0 | 0
2022121010 | 7 | 0.5205 | 41640 | 0 | 0 | 0.13948 | 4881.8 | 0.1326 | 1856.4 | 40000 | 0 | 1640 | 3241.8 | 0 | 1856.4 | 5098.2 | 0 | 0 | 0 | 0
2022121011 | 7 | 0.54243 | 43394.4 | 0 | 0 | 0.18121 | 6342.35 | 0.16595 | 2323.3 | 40000 | 0 | 3394.4 | 2947.95 | 0 | 2323.3 | 5271.25 | 0 | 0 | 0 | 0
2022121012 | 7 | 0.55593 | 44474.4 | 0 | 0 | 0.22157 | 7754.95 | 0.18716 | 2620.24 | 40000 | 0 | 4474.4 | 3280.55 | 0 | 2620.24 | 5900.79 | 0 | 0 | 0 | 0
2022121013 | 7 | 0.56328 | 45062.4 | 0 | 0 | 0.23818 | 8336.3 | 0.19059 | 2668.26 | 40000 | 0 | 5062.4 | 3273.9 | 0 | 2668.26 | 5942.16 | 0 | 0 | 0 | 0
2022121014 | 7 | 0.56767 | 45413.6 | 0 | 0 | 0.2453 | 8585.5 | 0.19684 | 2755.76 | 40000 | 0 | 5413.6 | 3171.9 | 0 | 2755.76 | 5927.66 | 0 | 0 | 0 | 0
2022121015 | 7 | 0.56683 | 45346.4 | 0 | 0 | 0.22782 | 7973.7 | 0.19588 | 2742.32 | 40000 | 0 | 5346.4 | 2627.3 | 0 | 2742.32 | 5369.62 | 0 | 0 | 0 | 0
2022121016 | 7 | 0.56392 | 45113.6 | 0 | 0 | 0.22613 | 7914.55 | 0.13675 | 1914.5 | 40000 | 0 | 5113.6 | 2800.95 | 0 | 1914.5 | 4715.45 | 0 | 0 | 0 | 0
2022121017 | 7 | 0.56135 | 44908 | 0 | 0 | 0.22201 | 7770.35 | 0.09984 | 1397.76 | 40000 | 0 | 4908 | 2862.35 | 0 | 1397.76 | 4260.11 | 0 | 0 | 0 | 0
2022121018 | 7 | 0.56712 | 45369.6 | 0 | 0 | 0.22296 | 7803.6 | 0.01805 | 252.7 | 40000 | 0 | 5369.6 | 2434 | 0 | 252.7 | 2686.7 | 0 | 0 | 0 | 0
2022121019 | 7 | 0.56594 | 45275.2 | 0 | 0 | 0.24036 | 8412.6 | 0 | 0 | 40000 | 0 | 5275.2 | 3137.4 | 0 | 0 | 3137.4 | 0 | 0 | 0 | 0
2022121020 | 7 | 0.55724 | 44579.2 | 0 | 0 | 0.23677 | 8286.95 | 0 | 0 | 40000 | 0 | 4579.2 | 3707.75 | 0 | 0 | 3707.75 | 0 | 0 | 0 | 0
2022121021 | 7 | 0.54702 | 43761.6 | 0 | 0 | 0.20846 | 7296.1 | 0 | 0 | 40000 | 0 | 3761.6 | 3534.5 | 0 | 0 | 3534.5 | 0 | 0 | 0 | 0
2022121022 | 7 | 0.53586 | 42868.8 | 0 | 0 | 0.17285 | 6049.75 | 0 | 0 | 40000 | 0 | 2868.8 | 3180.95 | 0 | 0 | 3180.95 | 0 | 0 | 0 | 0
2022121023 | 7 | 0.51689 | 41351.2 | 0 | 0 | 0.1518 | 5313 | 0 | 0 | 40000 | 0 | 1351.2 | 3961.8 | 0 | 0 | 3961.8 | 0 | 0 | 0 | 0
2022121024 | 7 | 0.49689 | 39751.2 | 0 | 0 | 0.12503 | 4376.05 | 0 | 0 | 39751.2 | 248.8 | 0 | 4376.05 | 0 | 0 | 4624.85 | 0 | 0 | 0 | 0
2022121101 | 1 | 0.47388 | 37910.4 | 0 | 0 | 0.10113 | 3539.55 | 0 | 0 | 37910.4 | 2089.6 | 0 | 3539.55 | 0 | 0 | 5629.15 | 0 | 0 | 0 | 0
2022121102 | 1 | 0.45607 | 36485.6 | 0 | 0 | 0.09094 | 3182.9 | 0 | 0 | 36485.6 | 3514.4 | 0 | 3182.9 | 0 | 0 | 6697.3 | 0 | 0 | 0 | 0
2022121103 | 1 | 0.44499 | 35599.2 | 0 | 0 | 0.08567 | 2998.45 | 0 | 0 | 35599.2 | 4400.8 | 0 | 2998.45 | 0 | 0 | 7399.25 | 0 | 0 | 0 | 0
2022121104 | 1 | 0.43801 | 35040.8 | 0 | 0 | 0.07731 | 2705.85 | 0 | 0 | 35040.8 | 4959.2 | 0 | 2705.85 | 0 | 0 | 7665.05 | 0 | 0 | 0 | 0
2022121105 | 1 | 0.43315 | 34652 | 0 | 0 | 0.07703 | 2696.05 | 0 | 0 | 34652 | 5348 | 0 | 2696.05 | 0 | 0 | 8044.05 | 0 | 0 | 0 | 0
2022121106 | 1 | 0.43481 | 34784.8 | 0 | 0 | 0.07175 | 2511.25 | 0 | 0 | 34784.8 | 5215.2 | 0 | 2511.25 | 0 | 0 | 7726.45 | 0 | 0 | 0 | 0
2022121107 | 1 | 0.44057 | 35245.6 | 0 | 0 | 0.06328 | 2214.8 | 0 | 0 | 35245.6 | 4754.4 | 0 | 2214.8 | 0 | 0 | 6969.2 | 0 | 0 | 0 | 0
2022121108 | 1 | 0.45444 | 36355.2 | 0 | 0 | 0.06016 | 2105.6 | 0.00153 | 21.42 | 36355.2 | 3644.8 | 0 | 2105.6 | 0 | 21.42 | 5771.82 | 0 | 0 | 0 | 0
2022121109 | 1 | 0.47296 | 37836.8 | 0 | 0 | 0.06557 | 2294.95 | 0.02602 | 364.28 | 37836.8 | 2163.2 | 0 | 2294.95 | 0 | 364.28 | 4822.43 | 0 | 0 | 0 | 0
2022121110 | 1 | 0.49397 | 39517.6 | 0 | 0 | 0.05565 | 1947.75 | 0.07778 | 1088.92 | 39517.6 | 482.4 | 0 | 1947.75 | 0 | 1088.92 | 3519.07 | 0 | 0 | 0 | 0
2022121111 | 1 | 0.50924 | 40739.2 | 0 | 0 | 0.04684 | 1639.4 | 0.16738 | 2343.32 | 40000 | 0 | 739.2 | 900.2 | 0 | 2343.32 | 3243.52 | 0 | 0 | 0 | 0
2022121112 | 1 | 0.52405 | 41924 | 0 | 0 | 0.05669 | 1984.15 | 0.2378 | 3329.2 | 40000 | 0 | 1924 | 60.15 | 0 | 3329.2 | 3389.35 | 0 | 0 | 0 | 0
2022121113 | 1 | 0.52994 | 42395.2 | 0 | 0 | 0.06137 | 2147.95 | 0.28918 | 4048.52 | 40000 | 0 | 2147.95 | 0 | 247.25 | 3801.27 | 3801.27 | 0 | 0 | 0 | 0
2022121114 | 1 | 0.53236 | 42588.8 | 0 | 0 | 0.07339 | 2568.65 | 0.30228 | 4231.92 | 40000 | 0 | 2568.65 | 0 | 20.15 | 4211.77 | 4211.77 | 0 | 0 | 0 | 0
2022121115 | 1 | 0.53139 | 42511.2 | 0 | 0 | 0.09163 | 3207.05 | 0.30974 | 4336.36 | 40000 | 0 | 2511.2 | 695.85 | 0 | 4336.36 | 5032.21 | 0 | 0 | 0 | 0
2022121116 | 1 | 0.53125 | 42500 | 0 | 0 | 0.11655 | 4079.25 | 0.28693 | 4017.02 | 40000 | 0 | 2500 | 1579.25 | 0 | 4017.02 | 5596.27 | 0 | 0 | 0 | 0
2022121117 | 1 | 0.53589 | 42871.2 | 0 | 0 | 0.13457 | 4709.95 | 0.16412 | 2297.68 | 40000 | 0 | 2871.2 | 1838.75 | 0 | 2297.68 | 4136.43 | 0 | 0 | 0 | 0
2022121118 | 1 | 0.54851 | 43880.8 | 0 | 0 | 0.13679 | 4787.65 | 0.02025 | 283.5 | 40000 | 0 | 3880.8 | 906.85 | 0 | 283.5 | 1190.35 | 0 | 0 | 0 | 0
2022121119 | 1 | 0.55974 | 44779.2 | 0 | 0 | 0.14921 | 5222.35 | 0 | 0 | 40000 | 0 | 4779.2 | 443.15 | 0 | 0 | 443.15 | 0 | 0 | 0 | 0
2022121120 | 1 | 0.55571 | 44456.8 | 0 | 0 | 0.17293 | 6052.55 | 0 | 0 | 40000 | 0 | 4456.8 | 1595.75 | 0 | 0 | 1595.75 | 0 | 0 | 0 | 0
2022121121 | 1 | 0.54938 | 43950.4 | 0 | 0 | 0.2096 | 7336 | 0 | 0 | 40000 | 0 | 3950.4 | 3385.6 | 0 | 0 | 3385.6 | 0 | 0 | 0 | 0
2022121122 | 1 | 0.53678 | 42942.4 | 0 | 0 | 0.24621 | 8617.35 | 0 | 0 | 40000 | 0 | 2942.4 | 5674.95 | 0 | 0 | 5674.95 | 0 | 0 | 0 | 0
2022121123 | 1 | 0.51161 | 40928.8 | 0 | 0 | 0.26896 | 9413.6 | 0 | 0 | 40000 | 0 | 928.8 | 8484.8 | 0 | 0 | 8484.8 | 0 | 0 | 0 | 0
2022121124 | 1 | 0.48171 | 38536.8 | 0 | 0 | 0.30872 | 10805.2 | 0 | 0 | 38536.8 | 1463.2 | 0 | 10805.2 | 0 | 0 | 12268.4 | 0 | 0 | 0 | 0
2022121201 | 2 | 0.45844 | 36675.2 | 0 | 0 | 0.33612 | 11764.2 | 0 | 0 | 36675.2 | 3324.8 | 0 | 11764.2 | 0 | 0 | 15089 | 0 | 0 | 0 | 0
2022121202 | 2 | 0.44308 | 35446.4 | 0 | 0 | 0.34531 | 12085.85 | 0 | 0 | 35446.4 | 4553.6 | 0 | 12085.85 | 0 | 0 | 16639.45 | 0 | 0 | 0 | 0
2022121203 | 2 | 0.43578 | 34862.4 | 0 | 0 | 0.35303 | 12356.05 | 0 | 0 | 34862.4 | 5137.6 | 0 | 12356.05 | 0 | 0 | 17493.65 | 0 | 0 | 0 | 0
2022121204 | 2 | 0.43489 | 34791.2 | 0 | 0 | 0.35897 | 12563.95 | 0 | 0 | 34791.2 | 5208.8 | 0 | 12563.95 | 0 | 0 | 17772.75 | 0 | 0 | 0 | 0
2022121205 | 2 | 0.44464 | 35571.2 | 0 | 0 | 0.37716 | 13200.6 | 0 | 0 | 35571.2 | 4428.8 | 0 | 13200.6 | 0 | 0 | 17629.4 | 0 | 0 | 0 | 0
2022121206 | 2 | 0.46926 | 37540.8 | 0 | 0 | 0.40574 | 14200.9 | 0 | 0 | 37540.8 | 2459.2 | 0 | 14200.9 | 0 | 0 | 16660.1 | 0 | 0 | 0 | 0
2022121207 | 2 | 0.50877 | 40701.6 | 0 | 0 | 0.43357 | 15174.95 | 0 | 0 | 40000 | 0 | 701.6 | 14473.35 | 0 | 0 | 14473.35 | 0 | 0 | 0 | 0
2022121208 | 2 | 0.52965 | 42372 | 0 | 0 | 0.45368 | 15878.8 | 0.00244 | 34.16 | 40000 | 0 | 2372 | 13506.8 | 0 | 34.16 | 13540.96 | 0 | 0 | 0 | 0
2022121209 | 2 | 0.53801 | 43040.8 | 0 | 0 | 0.45612 | 15964.2 | 0.06399 | 895.86 | 40000 | 0 | 3040.8 | 12923.4 | 0 | 895.86 | 13819.26 | 0 | 0 | 0 | 0
2022121210 | 2 | 0.55155 | 44124 | 0 | 0 | 0.46573 | 16300.55 | 0.17029 | 2384.06 | 40000 | 0 | 4124 | 12176.55 | 0 | 2384.06 | 14560.61 | 0 | 0 | 0 | 0
2022121211 | 2 | 0.55513 | 44410.4 | 0 | 0 | 0.49527 | 17334.45 | 0.20427 | 2859.78 | 40000 | 0 | 4410.4 | 12924.05 | 0 | 2859.78 | 15783.83 | 0 | 0 | 0 | 0
2022121212 | 2 | 0.56255 | 45004 | 0 | 0 | 0.53831 | 18840.85 | 0.19047 | 2666.58 | 40000 | 0 | 5004 | 13836.85 | 0 | 2666.58 | 16503.43 | 0 | 0 | 0 | 0
2022121213 | 2 | 0.56232 | 44985.6 | 0 | 0 | 0.5553 | 19435.5 | 0.14888 | 2084.32 | 40000 | 0 | 4985.6 | 14449.9 | 0 | 2084.32 | 16534.22 | 0 | 0 | 0 | 0
2022121214 | 2 | 0.56287 | 45029.6 | 0 | 0 | 0.5571 | 19498.5 | 0.12661 | 1772.54 | 40000 | 0 | 5029.6 | 14468.9 | 0 | 1772.54 | 16241.44 | 0 | 0 | 0 | 0
2022121215 | 2 | 0.56085 | 44868 | 0 | 0 | 0.58104 | 20336.4 | 0.1087 | 1521.8 | 40000 | 0 | 4868 | 15468.4 | 0 | 1521.8 | 16990.2 | 0 | 0 | 0 | 0
2022121216 | 2 | 0.56156 | 44924.8 | 0 | 0 | 0.60089 | 21031.15 | 0.08348 | 1168.72 | 40000 | 0 | 4924.8 | 16106.35 | 0 | 1168.72 | 17275.07 | 0 | 0 | 0 | 0
2022121217 | 2 | 0.56832 | 45465.6 | 0 | 0 | 0.60911 | 21318.85 | 0.04673 | 654.22 | 40000 | 0 | 5465.6 | 15853.25 | 0 | 654.22 | 16507.47 | 0 | 0 | 0 | 0
2022121218 | 2 | 0.58365 | 46692 | 0 | 0 | 0.61545 | 21540.75 | 0.01052 | 147.28 | 40000 | 0 | 6692 | 14848.75 | 0 | 147.28 | 14996.03 | 0 | 0 | 0 | 0
2022121219 | 2 | 0.59425 | 47540 | 0 | 0 | 0.63455 | 22209.25 | 0 | 0 | 40000 | 0 | 7540 | 14669.25 | 0 | 0 | 14669.25 | 0 | 0 | 0 | 0
2022121220 | 2 | 0.58562 | 46849.6 | 0 | 0 | 0.65847 | 23046.45 | 0 | 0 | 40000 | 0 | 6849.6 | 16196.85 | 0 | 0 | 16196.85 | 0 | 0 | 0 | 0
2022121221 | 2 | 0.57876 | 46300.8 | 0 | 0 | 0.6662 | 23317 | 0 | 0 | 40000 | 0 | 6300.8 | 17016.2 | 0 | 0 | 17016.2 | 0 | 0 | 0 | 0
2022121222 | 2 | 0.56306 | 45044.8 | 0 | 0 | 0.66618 | 23316.3 | 0 | 0 | 40000 | 0 | 5044.8 | 18271.5 | 0 | 0 | 18271.5 | 0 | 0 | 0 | 0
2022121223 | 2 | 0.53501 | 42800.8 | 0 | 0 | 0.65681 | 22988.35 | 0 | 0 | 40000 | 0 | 2800.8 | 20187.55 | 0 | 0 | 20187.55 | 0 | 0 | 0 | 0
2022121224 | 2 | 0.50582 | 40465.6 | 0 | 0 | 0.65083 | 22779.05 | 0 | 0 | 40000 | 0 | 465.6 | 22313.45 | 0 | 0 | 22313.45 | 0 | 0 | 0 | 0
2022121301 | 3 | 0.48163 | 38530.4 | 0 | 0 | 0.63345 | 22170.75 | 0 | 0 | 38530.4 | 1469.6 | 0 | 22170.75 | 0 | 0 | 23640.35 | 0 | 0 | 0 | 0
2022121302 | 3 | 0.46573 | 37258.4 | 0 | 0 | 0.61456 | 21509.6 | 0 | 0 | 37258.4 | 2741.6 | 0 | 21509.6 | 0 | 0 | 24251.2 | 0 | 0 | 0 | 0
2022121303 | 3 | 0.45626 | 36500.8 | 0 | 0 | 0.60516 | 21180.6 | 0 | 0 | 36500.8 | 3499.2 | 0 | 21180.6 | 0 | 0 | 24679.8 | 0 | 0 | 0 | 0
2022121304 | 3 | 0.45294 | 36235.2 | 0 | 0 | 0.58155 | 20354.25 | 0 | 0 | 36235.2 | 3764.8 | 0 | 20354.25 | 0 | 0 | 24119.05 | 0 | 0 | 0 | 0
2022121305 | 3 | 0.45975 | 36780 | 0 | 0 | 0.54928 | 19224.8 | 0 | 0 | 36780 | 3220 | 0 | 19224.8 | 0 | 0 | 22444.8 | 0 | 0 | 0 | 0
2022121306 | 3 | 0.4798 | 38384 | 0 | 0 | 0.52738 | 18458.3 | 0 | 0 | 38384 | 1616 | 0 | 18458.3 | 0 | 0 | 20074.3 | 0 | 0 | 0 | 0
2022121307 | 3 | 0.51499 | 41199.2 | 0 | 0 | 0.50551 | 17692.85 | 0 | 0 | 40000 | 0 | 1199.2 | 16493.65 | 0 | 0 | 16493.65 | 0 | 0 | 0 | 0
2022121308 | 3 | 0.53502 | 42801.6 | 0 | 0 | 0.51683 | 18089.05 | 0.00645 | 90.3 | 40000 | 0 | 2801.6 | 15287.45 | 0 | 90.3 | 15377.75 | 0 | 0 | 0 | 0
2022121309 | 3 | 0.54592 | 43673.6 | 0 | 0 | 0.4786 | 16751 | 0.16099 | 2253.86 | 40000 | 0 | 3673.6 | 13077.4 | 0 | 2253.86 | 15331.26 | 0 | 0 | 0 | 0
2022121310 | 3 | 0.55623 | 44498.4 | 0 | 0 | 0.41266 | 14443.1 | 0.38024 | 5323.36 | 40000 | 0 | 4498.4 | 9944.7 | 0 | 5323.36 | 15268.06 | 0 | 0 | 0 | 0
2022121311 | 3 | 0.56553 | 45242.4 | 0 | 0 | 0.42409 | 14843.15 | 0.42192 | 5906.88 | 40000 | 0 | 5242.4 | 9600.75 | 0 | 5906.88 | 15507.63 | 0 | 0 | 0 | 0
2022121312 | 3 | 0.57355 | 45884 | 0 | 0 | 0.48463 | 16962.05 | 0.35305 | 4942.7 | 40000 | 0 | 5884 | 11078.05 | 0 | 4942.7 | 16020.75 | 0 | 0 | 0 | 0
2022121313 | 3 | 0.57809 | 46247.2 | 0 | 0 | 0.54285 | 18999.75 | 0.24222 | 3391.08 | 40000 | 0 | 6247.2 | 12752.55 | 0 | 3391.08 | 16143.63 | 0 | 0 | 0 | 0
2022121314 | 3 | 0.58521 | 46816.8 | 0 | 0 | 0.54058 | 18920.3 | 0.18692 | 2616.88 | 40000 | 0 | 6816.8 | 12103.5 | 0 | 2616.88 | 14720.38 | 0 | 0 | 0 | 0
2022121315 | 3 | 0.58414 | 46731.2 | 0 | 0 | 0.52774 | 18470.9 | 0.17828 | 2495.92 | 40000 | 0 | 6731.2 | 11739.7 | 0 | 2495.92 | 14235.62 | 0 | 0 | 0 | 0
2022121316 | 3 | 0.58228 | 46582.4 | 0 | 0 | 0.52937 | 18527.95 | 0.14008 | 1961.12 | 40000 | 0 | 6582.4 | 11945.55 | 0 | 1961.12 | 13906.67 | 0 | 0 | 0 | 0
2022121317 | 3 | 0.58417 | 46733.6 | 0 | 0 | 0.53953 | 18883.55 | 0.07522 | 1053.08 | 40000 | 0 | 6733.6 | 12149.95 | 0 | 1053.08 | 13203.03 | 0 | 0 | 0 | 0
2022121318 | 3 | 0.59156 | 47324.8 | 0 | 0 | 0.48914 | 17119.9 | 0.02369 | 331.66 | 40000 | 0 | 7324.8 | 9795.1 | 0 | 331.66 | 10126.76 | 0 | 0 | 0 | 0
2022121319 | 3 | 0.59982 | 47985.6 | 0 | 0 | 0.43226 | 15129.1 | 0 | 0 | 40000 | 0 | 7985.6 | 7143.5 | 0 | 0 | 7143.5 | 0 | 0 | 0 | 0
2022121320 | 3 | 0.58941 | 47152.8 | 0 | 0 | 0.39451 | 13807.85 | 0 | 0 | 40000 | 0 | 7152.8 | 6655.05 | 0 | 0 | 6655.05 | 0 | 0 | 0 | 0
2022121321 | 3 | 0.57609 | 46087.2 | 0 | 0 | 0.38104 | 13336.4 | 0 | 0 | 40000 | 0 | 6087.2 | 7249.2 | 0 | 0 | 7249.2 | 0 | 0 | 0 | 0
2022121322 | 3 | 0.5636 | 45088 | 0 | 0 | 0.39728 | 13904.8 | 0 | 0 | 40000 | 0 | 5088 | 8816.8 | 0 | 0 | 8816.8 | 0 | 0 | 0 | 0
2022121323 | 3 | 0.53353 | 42682.4 | 0 | 0 | 0.39441 | 13804.35 | 0 | 0 | 40000 | 0 | 2682.4 | 11121.95 | 0 | 0 | 11121.95 | 0 | 0 | 0 | 0
2022121324 | 3 | 0.50466 | 40372.8 | 0 | 0 | 0.39534 | 13836.9 | 0 | 0 | 40000 | 0 | 372.8 | 13464.1 | 0 | 0 | 13464.1 | 0 | 0 | 0 | 0
2022121401 | 4 | 0.47872 | 38297.6 | 0 | 0 | 0.39635 | 13872.25 | 0 | 0 | 38297.6 | 1702.4 | 0 | 13872.25 | 0 | 0 | 15574.65 | 0 | 0 | 0 | 0
2022121402 | 4 | 0.46176 | 36940.8 | 0 | 0 | 0.37006 | 12952.1 | 0 | 0 | 36940.8 | 3059.2 | 0 | 12952.1 | 0 | 0 | 16011.3 | 0 | 0 | 0 | 0
2022121403 | 4 | 0.45124 | 36099.2 | 0 | 0 | 0.35283 | 12349.05 | 0 | 0 | 36099.2 | 3900.8 | 0 | 12349.05 | 0 | 0 | 16249.85 | 0 | 0 | 0 | 0
2022121404 | 4 | 0.44684 | 35747.2 | 0 | 0 | 0.3672 | 12852 | 0 | 0 | 35747.2 | 4252.8 | 0 | 12852 | 0 | 0 | 17104.8 | 0 | 0 | 0 | 0
2022121405 | 4 | 0.45352 | 36281.6 | 0 | 0 | 0.35511 | 12428.85 | 0 | 0 | 36281.6 | 3718.4 | 0 | 12428.85 | 0 | 0 | 16147.25 | 0 | 0 | 0 | 0
2022121406 | 4 | 0.4733 | 37864 | 0 | 0 | 0.33637 | 11772.95 | 0 | 0 | 37864 | 2136 | 0 | 11772.95 | 0 | 0 | 13908.95 | 0 | 0 | 0 | 0
2022121407 | 4 | 0.51233 | 40986.4 | 0 | 0 | 0.36633 | 12821.55 | 0 | 0 | 40000 | 0 | 986.4 | 11835.15 | 0 | 0 | 11835.15 | 0 | 0 | 0 | 0
2022121408 | 4 | 0.53268 | 42614.4 | 0 | 0 | 0.40787 | 14275.45 | 0.00314 | 43.96 | 40000 | 0 | 2614.4 | 11661.05 | 0 | 43.96 | 11705.01 | 0 | 0 | 0 | 0
2022121409 | 4 | 0.53432 | 42745.6 | 0 | 0 | 0.40074 | 14025.9 | 0.1705 | 2387 | 40000 | 0 | 2745.6 | 11280.3 | 0 | 2387 | 13667.3 | 0 | 0 | 0 | 0
2022121410 | 4 | 0.53576 | 42860.8 | 0 | 0 | 0.3863 | 13520.5 | 0.33227 | 4651.78 | 40000 | 0 | 2860.8 | 10659.7 | 0 | 4651.78 | 15311.48 | 0 | 0 | 0 | 0
2022121411 | 4 | 0.53011 | 42408.8 | 0 | 0 | 0.44358 | 15525.3 | 0.26477 | 3706.78 | 40000 | 0 | 2408.8 | 13116.5 | 0 | 3706.78 | 16823.28 | 0 | 0 | 0 | 0
2022121412 | 4 | 0.52683 | 42146.4 | 0 | 0 | 0.45156 | 15804.6 | 0.25409 | 3557.26 | 40000 | 0 | 2146.4 | 13658.2 | 0 | 3557.26 | 17215.46 | 0 | 0 | 0 | 0
2022121413 | 4 | 0.52307 | 41845.6 | 0 | 0 | 0.44108 | 15437.8 | 0.28023 | 3923.22 | 40000 | 0 | 1845.6 | 13592.2 | 0 | 3923.22 | 17515.42 | 0 | 0 | 0 | 0
2022121414 | 4 | 0.52226 | 41780.8 | 0 | 0 | 0.41361 | 14476.35 | 0.34864 | 4880.96 | 40000 | 0 | 1780.8 | 12695.55 | 0 | 4880.96 | 17576.51 | 0 | 0 | 0 | 0
2022121415 | 4 | 0.52065 | 41652 | 0 | 0 | 0.37004 | 12951.4 | 0.42408 | 5937.12 | 40000 | 0 | 1652 | 11299.4 | 0 | 5937.12 | 17236.52 | 0 | 0 | 0 | 0
2022121416 | 4 | 0.52362 | 41889.6 | 0 | 0 | 0.30463 | 10662.05 | 0.51576 | 7220.64 | 40000 | 0 | 1889.6 | 8772.45 | 0 | 7220.64 | 15993.09 | 0 | 0 | 0 | 0
2022121417 | 4 | 0.53014 | 42411.2 | 0 | 0 | 0.23634 | 8271.9 | 0.35295 | 4941.3 | 40000 | 0 | 2411.2 | 5860.7 | 0 | 4941.3 | 10802 | 0 | 0 | 0 | 0
2022121418 | 4 | 0.55261 | 44208.8 | 0 | 0 | 0.14303 | 5006.05 | 0.03937 | 551.18 | 40000 | 0 | 4208.8 | 797.25 | 0 | 551.18 | 1348.43 | 0 | 0 | 0 | 0
2022121419 | 4 | 0.5725 | 45800 | 0 | 0 | 0.12339 | 4318.65 | 0 | 0 | 40000 | 0 | 4318.65 | 0 | 0 | 0 | 0 | 1481.35 | 0 | 0 | 1481.35
2022121420 | 4 | 0.57139 | 45711.2 | 0 | 0 | 0.13189 | 4616.15 | 0 | 0 | 40000 | 0 | 4616.15 | 0 | 0 | 0 | 0 | 1095.05 | 0 | 0 | 1095.05
2022121421 | 4 | 0.57032 | 45625.6 | 0 | 0 | 0.13726 | 4804.1 | 0 | 0 | 40000 | 0 | 4804.1 | 0 | 0 | 0 | 0 | 821.5 | 0 | 0 | 821.5
2022121422 | 4 | 0.55919 | 44735.2 | 0 | 0 | 0.16342 | 5719.7 | 0 | 0 | 40000 | 0 | 4735.2 | 984.5 | 0 | 0 | 984.5 | 0 | 0 | 0 | 0
2022121423 | 4 | 0.53982 | 43185.6 | 0 | 0 | 0.18704 | 6546.4 | 0 | 0 | 40000 | 0 | 3185.6 | 3360.8 | 0 | 0 | 3360.8 | 0 | 0 | 0 | 0
2022121424 | 4 | 0.51647 | 41317.6 | 0 | 0 | 0.19182 | 6713.7 | 0 | 0 | 40000 | 0 | 1317.6 | 5396.1 | 0 | 0 | 5396.1 | 0 | 0 | 0 | 0
2022121501 | 5 | 0.4999 | 39992 | 0 | 0 | 0.18584 | 6504.4 | 0 | 0 | 39992 | 8 | 0 | 6504.4 | 0 | 0 | 6512.4 | 0 | 0 | 0 | 0
2022121502 | 5 | 0.49241 | 39392.8 | 0 | 0 | 0.17975 | 6291.25 | 0 | 0 | 39392.8 | 607.2 | 0 | 6291.25 | 0 | 0 | 6898.45 | 0 | 0 | 0 | 0
2022121503 | 5 | 0.49004 | 39203.2 | 0 | 0 | 0.17657 | 6179.95 | 0 | 0 | 39203.2 | 796.8 | 0 | 6179.95 | 0 | 0 | 6976.75 | 0 | 0 | 0 | 0
2022121504 | 5 | 0.496 | 39680 | 0 | 0 | 0.16605 | 5811.75 | 0 | 0 | 39680 | 320 | 0 | 5811.75 | 0 | 0 | 6131.75 | 0 | 0 | 0 | 0
2022121505 | 5 | 0.51462 | 41169.6 | 0 | 0 | 0.16013 | 5604.55 | 0 | 0 | 40000 | 0 | 1169.6 | 4434.95 | 0 | 0 | 4434.95 | 0 | 0 | 0 | 0
2022121506 | 5 | 0.54994 | 43995.2 | 0 | 0 | 0.1572 | 5502 | 0 | 0 | 40000 | 0 | 3995.2 | 1506.8 | 0 | 0 | 1506.8 | 0 | 0 | 0 | 0
2022121507 | 5 | 0.60495 | 48396 | 0 | 0 | 0.15133 | 5296.55 | 0 | 0 | 40000 | 0 | 5296.55 | 0 | 0 | 0 | 0 | 3099.45 | 0 | 0 | 3099.45
2022121508 | 5 | 0.62996 | 50396.8 | 0 | 0 | 0.14374 | 5030.9 | 0.01952 | 273.28 | 40000 | 0 | 5030.9 | 0 | 273.28 | 0 | 0 | 5092.62 | 0 | 0 | 5092.62
2022121509 | 5 | 0.61899 | 49519.2 | 0 | 0 | 0.13218 | 4626.3 | 0.3172 | 4440.8 | 40000 | 0 | 4626.3 | 0 | 4440.8 | 0 | 0 | 452.1 | 0 | 0 | 452.1
2022121510 | 5 | 0.59571 | 47656.8 | 0 | 0 | 0.08034 | 2811.9 | 0.61581 | 8621.34 | 40000 | 0 | 2811.9 | 0 | 4844.9 | 3776.44 | 3776.44 | 0 | 0 | 0 | 0
2022121511 | 5 | 0.56961 | 45568.8 | 0 | 0 | 0.10111 | 3538.85 | 0.63439 | 8881.46 | 40000 | 0 | 3538.85 | 0 | 2029.95 | 6851.51 | 6851.51 | 0 | 0 | 0 | 0
2022121512 | 5 | 0.5469 | 43752 | 0 | 0 | 0.12214 | 4274.9 | 0.60984 | 8537.76 | 40000 | 0 | 3752 | 522.9 | 0 | 8537.76 | 9060.66 | 0 | 0 | 0 | 0
2022121513 | 5 | 0.53167 | 42533.6 | 0 | 0 | 0.10201 | 3570.35 | 0.59541 | 8335.74 | 40000 | 0 | 2533.6 | 1036.75 | 0 | 8335.74 | 9372.49 | 0 | 0 | 0 | 0
2022121514 | 5 | 0.52734 | 42187.2 | 0 | 0 | 0.08258 | 2890.3 | 0.60633 | 8488.62 | 40000 | 0 | 2187.2 | 703.1 | 0 | 8488.62 | 9191.72 | 0 | 0 | 0 | 0
2022121515 | 5 | 0.52307 | 41845.6 | 0 | 0 | 0.07341 | 2569.35 | 0.63201 | 8848.14 | 40000 | 0 | 1845.6 | 723.75 | 0 | 8848.14 | 9571.89 | 0 | 0 | 0 | 0
2022121516 | 5 | 0.52269 | 41815.2 | 0 | 0 | 0.07752 | 2713.2 | 0.60811 | 8513.54 | 40000 | 0 | 1815.2 | 898 | 0 | 8513.54 | 9411.54 | 0 | 0 | 0 | 0
2022121517 | 5 | 0.53095 | 42476 | 0 | 0 | 0.07997 | 2798.95 | 0.3689 | 5164.6 | 40000 | 0 | 2476 | 322.95 | 0 | 5164.6 | 5487.55 | 0 | 0 | 0 | 0
2022121518 | 5 | 0.55252 | 44201.6 | 0 | 0 | 0.07565 | 2647.75 | 0.03768 | 527.52 | 40000 | 0 | 2647.75 | 0 | 527.52 | 0 | 0 | 1026.33 | 0 | 0 | 1026.33
2022121519 | 5 | 0.57613 | 46090.4 | 0 | 0 | 0.11671 | 4084.85 | 0 | 0 | 40000 | 0 | 4084.85 | 0 | 0 | 0 | 0 | 2005.55 | 0 | 0 | 2005.55
2022121520 | 5 | 0.58011 | 46408.8 | 0 | 0 | 0.17252 | 6038.2 | 0 | 0 | 40000 | 0 | 6038.2 | 0 | 0 | 0 | 0 | 370.6 | 0 | 0 | 370.6
2022121521 | 5 | 0.58151 | 46520.8 | 0 | 0 | 0.20622 | 7217.7 | 0 | 0 | 40000 | 0 | 6520.8 | 696.9 | 0 | 0 | 696.9 | 0 | 0 | 0 | 0
2022121522 | 5 | 0.57715 | 46172 | 0 | 0 | 0.2312 | 8092 | 0 | 0 | 40000 | 0 | 6172 | 1920 | 0 | 0 | 1920 | 0 | 0 | 0 | 0
2022121523 | 5 | 0.55881 | 44704.8 | 0 | 0 | 0.25223 | 8828.05 | 0 | 0 | 40000 | 0 | 4704.8 | 4123.25 | 0 | 0 | 4123.25 | 0 | 0 | 0 | 0
2022121524 | 5 | 0.53914 | 43131.2 | 0 | 0 | 0.26583 | 9304.05 | 0 | 0 | 40000 | 0 | 3131.2 | 6172.85 | 0 | 0 | 6172.85 | 0 | 0 | 0 | 0
2022121601 | 6 | 0.52484 | 41987.2 | 0 | 0 | 0.25993 | 9097.55 | 0 | 0 | 40000 | 0 | 1987.2 | 7110.35 | 0 | 0 | 7110.35 | 0 | 0 | 0 | 0
2022121602 | 6 | 0.51933 | 41546.4 | 0 | 0 | 0.26015 | 9105.25 | 0 | 0 | 40000 | 0 | 1546.4 | 7558.85 | 0 | 0 | 7558.85 | 0 | 0 | 0 | 0
2022121603 | 6 | 0.51577 | 41261.6 | 0 | 0 | 0.25722 | 9002.7 | 0 | 0 | 40000 | 0 | 1261.6 | 7741.1 | 0 | 0 | 7741.1 | 0 | 0 | 0 | 0
2022121604 | 6 | 0.51696 | 41356.8 | 0 | 0 | 0.26602 | 9310.7 | 0 | 0 | 40000 | 0 | 1356.8 | 7953.9 | 0 | 0 | 7953.9 | 0 | 0 | 0 | 0
2022121605 | 6 | 0.53007 | 42405.6 | 0 | 0 | 0.28973 | 10140.55 | 0 | 0 | 40000 | 0 | 2405.6 | 7734.95 | 0 | 0 | 7734.95 | 0 | 0 | 0 | 0
2022121606 | 6 | 0.55949 | 44759.2 | 0 | 0 | 0.27492 | 9622.2 | 0 | 0 | 40000 | 0 | 4759.2 | 4863 | 0 | 0 | 4863 | 0 | 0 | 0 | 0
2022121607 | 6 | 0.60656 | 48524.8 | 0 | 0 | 0.27607 | 9662.45 | 0 | 0 | 40000 | 0 | 8524.8 | 1137.65 | 0 | 0 | 1137.65 | 0 | 0 | 0 | 0
2022121608 | 6 | 0.62431 | 49944.8 | 0 | 0 | 0.30037 | 10512.95 | 0.01073 | 150.22 | 40000 | 0 | 9944.8 | 568.15 | 0 | 150.22 | 718.37 | 0 | 0 | 0 | 0
2022121609 | 6 | 0.61622 | 49297.6 | 0 | 0 | 0.2813 | 9845.5 | 0.18335 | 2566.9 | 40000 | 0 | 9297.6 | 547.9 | 0 | 2566.9 | 3114.8 | 0 | 0 | 0 | 0
2022121610 | 6 | 0.6061 | 48488 | 0 | 0 | 0.23967 | 8388.45 | 0.42564 | 5958.96 | 40000 | 0 | 8388.45 | 0 | 99.55 | 5859.41 | 5859.41 | 0 | 0 | 0 | 0
2022121611 | 6 | 0.60157 | 48125.6 | 0 | 0 | 0.26586 | 9305.1 | 0.49585 | 6941.9 | 40000 | 0 | 8125.6 | 1179.5 | 0 | 6941.9 | 8121.4 | 0 | 0 | 0 | 0
2022121612 | 6 | 0.5908 | 47264 | 0 | 0 | 0.23068 | 8073.8 | 0.45045 | 6306.3 | 40000 | 0 | 7264 | 809.8 | 0 | 6306.3 | 7116.1 | 0 | 0 | 0 | 0
2022121613 | 6 | 0.57837 | 46269.6 | 0 | 0 | 0.17568 | 6148.8 | 0.40927 | 5729.78 | 40000 | 0 | 6148.8 | 0 | 120.8 | 5608.98 | 5608.98 | 0 | 0 | 0 | 0
2022121614 | 6 | 0.57115 | 45692 | 0 | 0 | 0.13182 | 4613.7 | 0.38405 | 5376.7 | 40000 | 0 | 4613.7 | 0 | 1078.3 | 4298.4 | 4298.4 | 0 | 0 | 0 | 0
2022121615 | 6 | 0.56623 | 45298.4 | 0 | 0 | 0.1046 | 3661 | 0.36256 | 5075.84 | 40000 | 0 | 3661 | 0 | 1637.4 | 3438.44 | 3438.44 | 0 | 0 | 0 | 0
2022121616 | 6 | 0.56869 | 45495.2 | 0 | 0 | 0.10247 | 3586.45 | 0.29358 | 4110.12 | 40000 | 0 | 3586.45 | 0 | 1908.75 | 2201.37 | 2201.37 | 0 | 0 | 0 | 0
2022121617 | 6 | 0.57487 | 45989.6 | 0 | 0 | 0.09966 | 3488.1 | 0.1512 | 2116.8 | 40000 | 0 | 3488.1 | 0 | 2116.8 | 0 | 0 | 384.7 | 0 | 0 | 384.7
2022121618 | 6 | 0.59638 | 47710.4 | 0 | 0 | 0.08444 | 2955.4 | 0.01636 | 229.04 | 40000 | 0 | 2955.4 | 0 | 229.04 | 0 | 0 | 4525.96 | 0 | 0 | 4525.96
2022121619 | 6 | 0.61153 | 48922.4 | 0 | 0 | 0.10081 | 3528.35 | 0 | 0 | 40000 | 0 | 3528.35 | 0 | 0 | 0 | 0 | 5394.05 | 0 | 0 | 5394.05
2022121620 | 6 | 0.60922 | 48737.6 | 0 | 0 | 0.13771 | 4819.85 | 0 | 0 | 40000 | 0 | 4819.85 | 0 | 0 | 0 | 0 | 3917.75 | 0 | 0 | 3917.75
2022121621 | 6 | 0.60375 | 48300 | 0 | 0 | 0.17516 | 6130.6 | 0 | 0 | 40000 | 0 | 6130.6 | 0 | 0 | 0 | 0 | 2169.4 | 0 | 0 | 2169.4
2022121622 | 6 | 0.5942 | 47536 | 0 | 0 | 0.19983 | 6994.05 | 0 | 0 | 40000 | 0 | 6994.05 | 0 | 0 | 0 | 0 | 541.95 | 0 | 0 | 541.95
2022121623 | 6 | 0.57975 | 46380 | 0 | 0 | 0.2284 | 7994 | 0 | 0 | 40000 | 0 | 6380 | 1614 | 0 | 0 | 1614 | 0 | 0 | 0 | 0
2022121624 | 6 | 0.55779 | 44623.2 | 0 | 0 | 0.23599 | 8259.65 | 0 | 0 | 40000 | 0 | 4623.2 | 3636.45 | 0 | 0 | 3636.45 | 0 | 0 | 0 | 0
2022121701 | 7 | 0.54152 | 43321.6 | 0 | 0 | 0.24163 | 8457.05 | 0 | 0 | 40000 | 0 | 3321.6 | 5135.45 | 0 | 0 | 5135.45 | 0 | 0 | 0 | 0
2022121702 | 7 | 0.53035 | 42428 | 0 | 0 | 0.24074 | 8425.9 | 0 | 0 | 40000 | 0 | 2428 | 5997.9 | 0 | 0 | 5997.9 | 0 | 0 | 0 | 0
2022121703 | 7 | 0.52636 | 42108.8 | 0 | 0 | 0.23056 | 8069.6 | 0 | 0 | 40000 | 0 | 2108.8 | 5960.8 | 0 | 0 | 5960.8 | 0 | 0 | 0 | 0
2022121704 | 7 | 0.52691 | 42152.8 | 0 | 0 | 0.21489 | 7521.15 | 0 | 0 | 40000 | 0 | 2152.8 | 5368.35 | 0 | 0 | 5368.35 | 0 | 0 | 0 | 0
2022121705 | 7 | 0.53677 | 42941.6 | 0 | 0 | 0.21438 | 7503.3 | 0 | 0 | 40000 | 0 | 2941.6 | 4561.7 | 0 | 0 | 4561.7 | 0 | 0 | 0 | 0
2022121706 | 7 | 0.55353 | 44282.4 | 0 | 0 | 0.21896 | 7663.6 | 0 | 0 | 40000 | 0 | 4282.4 | 3381.2 | 0 | 0 | 3381.2 | 0 | 0 | 0 | 0
2022121707 | 7 | 0.57825 | 46260 | 0 | 0 | 0.21031 | 7360.85 | 0 | 0 | 40000 | 0 | 6260 | 1100.85 | 0 | 0 | 1100.85 | 0 | 0 | 0 | 0
2022121708 | 7 | 0.59769 | 47815.2 | 0 | 0 | 0.17894 | 6262.9 | 0.00639 | 89.46 | 40000 | 0 | 6262.9 | 0 | 89.46 | 0 | 0 | 1462.84 | 0 | 0 | 1462.84
2022121709 | 7 | 0.61697 | 49357.6 | 0 | 0 | 0.16225 | 5678.75 | 0.22408 | 3137.12 | 40000 | 0 | 5678.75 | 0 | 3137.12 | 0 | 0 | 541.73 | 0 | 0 | 541.73
2022121710 | 7 | 0.61656 | 49324.8 | 0 | 0 | 0.1271 | 4448.5 | 0.50277 | 7038.78 | 40000 | 0 | 4448.5 | 0 | 4876.3 | 2162.48 | 2162.48 | 0 | 0 | 0 | 0
2022121711 | 7 | 0.60121 | 48096.8 | 0 | 0 | 0.12536 | 4387.6 | 0.55084 | 7711.76 | 40000 | 0 | 4387.6 | 0 | 3709.2 | 4002.56 | 4002.56 | 0 | 0 | 0 | 0
2022121712 | 7 | 0.58211 | 46568.8 | 0 | 0 | 0.12813 | 4484.55 | 0.55769 | 7807.66 | 40000 | 0 | 4484.55 | 0 | 2084.25 | 5723.41 | 5723.41 | 0 | 0 | 0 | 0
2022121713 | 7 | 0.55791 | 44632.8 | 0 | 0 | 0.13283 | 4649.05 | 0.55735 | 7802.9 | 40000 | 0 | 4632.8 | 16.25 | 0 | 7802.9 | 7819.15 | 0 | 0 | 0 | 0
2022121714 | 7 | 0.53885 | 43108 | 0 | 0 | 0.12877 | 4506.95 | 0.56437 | 7901.18 | 40000 | 0 | 3108 | 1398.95 | 0 | 7901.18 | 9300.13 | 0 | 0 | 0 | 0
2022121715 | 7 | 0.52387 | 41909.6 | 0 | 0 | 0.11934 | 4176.9 | 0.58479 | 8187.06 | 40000 | 0 | 1909.6 | 2267.3 | 0 | 8187.06 | 10454.36 | 0 | 0 | 0 | 0
2022121716 | 7 | 0.51631 | 41304.8 | 0 | 0 | 0.10345 | 3620.75 | 0.58598 | 8203.72 | 40000 | 0 | 1304.8 | 2315.95 | 0 | 8203.72 | 10519.67 | 0 | 0 | 0 | 0
2022121717 | 7 | 0.52356 | 41884.8 | 0 | 0 | 0.09143 | 3200.05 | 0.35884 | 5023.76 | 40000 | 0 | 1884.8 | 1315.25 | 0 | 5023.76 | 6339.01 | 0 | 0 | 0 | 0
2022121718 | 7 | 0.54924 | 43939.2 | 0 | 0 | 0.08404 | 2941.4 | 0.03928 | 549.92 | 40000 | 0 | 2941.4 | 0 | 549.92 | 0 | 0 | 447.88 | 0 | 0 | 447.88
2022121719 | 7 | 0.57456 | 45964.8 | 0 | 0 | 0.11508 | 4027.8 | 0 | 0 | 40000 | 0 | 4027.8 | 0 | 0 | 0 | 0 | 1937 | 0 | 0 | 1937
2022121720 | 7 | 0.58345 | 46676 | 0 | 0 | 0.15719 | 5501.65 | 4e-05 | 0.56 | 40000 | 0 | 5501.65 | 0 | 0.56 | 0 | 0 | 1173.79 | 0 | 0 | 1173.79
2022121721 | 7 | 0.59442 | 47553.6 | 0 | 0 | 0.19599 | 6859.65 | 0 | 0 | 40000 | 0 | 6859.65 | 0 | 0 | 0 | 0 | 693.95 | 0 | 0 | 693.95
2022121722 | 7 | 0.59932 | 47945.6 | 0 | 0 | 0.23122 | 8092.7 | 0 | 0 | 40000 | 0 | 7945.6 | 147.1 | 0 | 0 | 147.1 | 0 | 0 | 0 | 0
2022121723 | 7 | 0.59742 | 47793.6 | 0 | 0 | 0.28824 | 10088.4 | 0 | 0 | 40000 | 0 | 7793.6 | 2294.8 | 0 | 0 | 2294.8 | 0 | 0 | 0 | 0
2022121724 | 7 | 0.58923 | 47138.4 | 0 | 0 | 0.34321 | 12012.35 | 0 | 0 | 40000 | 0 | 7138.4 | 4873.95 | 0 | 0 | 4873.95 | 0 | 0 | 0 | 0
2022121801 | 1 | 0.57975 | 46380 | 0 | 0 | 0.38233 | 13381.55 | 0 | 0 | 40000 | 0 | 6380 | 7001.55 | 0 | 0 | 7001.55 | 0 | 0 | 0 | 0
2022121802 | 1 | 0.57464 | 45971.2 | 0 | 0 | 0.41094 | 14382.9 | 0 | 0 | 40000 | 0 | 5971.2 | 8411.7 | 0 | 0 | 8411.7 | 0 | 0 | 0 | 0
2022121803 | 1 | 0.57566 | 46052.8 | 0 | 0 | 0.42652 | 14928.2 | 0 | 0 | 40000 | 0 | 6052.8 | 8875.4 | 0 | 0 | 8875.4 | 0 | 0 | 0 | 0
2022121804 | 1 | 0.57947 | 46357.6 | 0 | 0 | 0.44649 | 15627.15 | 0 | 0 | 40000 | 0 | 6357.6 | 9269.55 | 0 | 0 | 9269.55 | 0 | 0 | 0 | 0
2022121805 | 1 | 0.58908 | 47126.4 | 0 | 0 | 0.47093 | 16482.55 | 0 | 0 | 40000 | 0 | 7126.4 | 9356.15 | 0 | 0 | 9356.15 | 0 | 0 | 0 | 0
2022121806 | 1 | 0.60368 | 48294.4 | 0 | 0 | 0.48951 | 17132.85 | 0 | 0 | 40000 | 0 | 8294.4 | 8838.45 | 0 | 0 | 8838.45 | 0 | 0 | 0 | 0
2022121807 | 1 | 0.62338 | 49870.4 | 0 | 0 | 0.49088 | 17180.8 | 0 | 0 | 40000 | 0 | 9870.4 | 7310.4 | 0 | 0 | 7310.4 | 0 | 0 | 0 | 0
2022121808 | 1 | 0.64156 | 51324.8 | 0 | 0 | 0.49051 | 17167.85 | 0.0145 | 203 | 40000 | 0 | 11324.8 | 5843.05 | 0 | 203 | 6046.05 | 0 | 0 | 0 | 0
2022121809 | 1 | 0.64469 | 51575.2 | 0 | 0 | 0.47872 | 16755.2 | 0.21564 | 3018.96 | 40000 | 0 | 11575.2 | 5180 | 0 | 3018.96 | 8198.96 | 0 | 0 | 0 | 0
2022121810 | 1 | 0.62584 | 50067.2 | 0 | 0 | 0.41204 | 14421.4 | 0.39774 | 5568.36 | 40000 | 0 | 10067.2 | 4354.2 | 0 | 5568.36 | 9922.56 | 0 | 0 | 0 | 0
2022121811 | 1 | 0.60226 | 48180.8 | 0 | 0 | 0.41321 | 14462.35 | 0.42863 | 6000.82 | 40000 | 0 | 8180.8 | 6281.55 | 0 | 6000.82 | 12282.37 | 0 | 0 | 0 | 0
2022121812 | 1 | 0.57758 | 46206.4 | 0 | 0 | 0.45641 | 15974.35 | 0.41597 | 5823.58 | 40000 | 0 | 6206.4 | 9767.95 | 0 | 5823.58 | 15591.53 | 0 | 0 | 0 | 0
2022121813 | 1 | 0.56162 | 44929.6 | 0 | 0 | 0.48521 | 16982.35 | 0.33959 | 4754.26 | 40000 | 0 | 4929.6 | 12052.75 | 0 | 4754.26 | 16807.01 | 0 | 0 | 0 | 0
2022121814 | 1 | 0.54805 | 43844 | 0 | 0 | 0.49028 | 17159.8 | 0.26034 | 3644.76 | 40000 | 0 | 3844 | 13315.8 | 0 | 3644.76 | 16960.56 | 0 | 0 | 0 | 0
2022121815 | 1 | 0.54022 | 43217.6 | 0 | 0 | 0.50243 | 17585.05 | 0.2185 | 3059 | 40000 | 0 | 3217.6 | 14367.45 | 0 | 3059 | 17426.45 | 0 | 0 | 0 | 0
2022121816 | 1 | 0.5397 | 43176 | 0 | 0 | 0.52562 | 18396.7 | 0.14179 | 1985.06 | 40000 | 0 | 3176 | 15220.7 | 0 | 1985.06 | 17205.76 | 0 | 0 | 0 | 0
2022121817 | 1 | 0.55048 | 44038.4 | 0 | 0 | 0.53531 | 18735.85 | 0.08797 | 1231.58 | 40000 | 0 | 4038.4 | 14697.45 | 0 | 1231.58 | 15929.03 | 0 | 0 | 0 | 0
2022121818 | 1 | 0.58046 | 46436.8 | 0 | 0 | 0.53681 | 18788.35 | 0.01275 | 178.5 | 40000 | 0 | 6436.8 | 12351.55 | 0 | 178.5 | 12530.05 | 0 | 0 | 0 | 0
2022121819 | 1 | 0.59982 | 47985.6 | 0 | 0 | 0.55356 | 19374.6 | 0 | 0 | 40000 | 0 | 7985.6 | 11389 | 0 | 0 | 11389 | 0 | 0 | 0 | 0
2022121820 | 1 | 0.5992 | 47936 | 0 | 0 | 0.57474 | 20115.9 | 0 | 0 | 40000 | 0 | 7936 | 12179.9 | 0 | 0 | 12179.9 | 0 | 0 | 0 | 0
2022121821 | 1 | 0.59411 | 47528.8 | 0 | 0 | 0.57463 | 20112.05 | 0 | 0 | 40000 | 0 | 7528.8 | 12583.25 | 0 | 0 | 12583.25 | 0 | 0 | 0 | 0
2022121822 | 1 | 0.58228 | 46582.4 | 0 | 0 | 0.56458 | 19760.3 | 0 | 0 | 40000 | 0 | 6582.4 | 13177.9 | 0 | 0 | 13177.9 | 0 | 0 | 0 | 0
2022121823 | 1 | 0.55994 | 44795.2 | 0 | 0 | 0.55801 | 19530.35 | 0 | 0 | 40000 | 0 | 4795.2 | 14735.15 | 0 | 0 | 14735.15 | 0 | 0 | 0 | 0
2022121824 | 1 | 0.536 | 42880 | 0 | 0 | 0.54518 | 19081.3 | 0 | 0 | 40000 | 0 | 2880 | 16201.3 | 0 | 0 | 16201.3 | 0 | 0 | 0 | 0
2022121901 | 2 | 0.51766 | 41412.8 | 0 | 0 | 0.54321 | 19012.35 | 0 | 0 | 40000 | 0 | 1412.8 | 17599.55 | 0 | 0 | 17599.55 | 0 | 0 | 0 | 0
2022121902 | 2 | 0.50731 | 40584.8 | 0 | 0 | 0.54575 | 19101.25 | 0 | 0 | 40000 | 0 | 584.8 | 18516.45 | 0 | 0 | 18516.45 | 0 | 0 | 0 | 0
2022121903 | 2 | 0.50233 | 40186.4 | 0 | 0 | 0.54075 | 18926.25 | 0 | 0 | 40000 | 0 | 186.4 | 18739.85 | 0 | 0 | 18739.85 | 0 | 0 | 0 | 0
2022121904 | 2 | 0.50399 | 40319.2 | 0 | 0 | 0.52926 | 18524.1 | 0 | 0 | 40000 | 0 | 319.2 | 18204.9 | 0 | 0 | 18204.9 | 0 | 0 | 0 | 0
2022121905 | 2 | 0.51675 | 41340 | 0 | 0 | 0.52043 | 18215.05 | 0 | 0 | 40000 | 0 | 1340 | 16875.05 | 0 | 0 | 16875.05 | 0 | 0 | 0 | 0
2022121906 | 2 | 0.54106 | 43284.8 | 0 | 0 | 0.50485 | 17669.75 | 0 | 0 | 40000 | 0 | 3284.8 | 14384.95 | 0 | 0 | 14384.95 | 0 | 0 | 0 | 0
2022121907 | 2 | 0.57502 | 46001.6 | 0 | 0 | 0.47576 | 16651.6 | 0 | 0 | 40000 | 0 | 6001.6 | 10650 | 0 | 0 | 10650 | 0 | 0 | 0 | 0
2022121908 | 2 | 0.60103 | 48082.4 | 0 | 0 | 0.42953 | 15033.55 | 0.00113 | 15.82 | 40000 | 0 | 8082.4 | 6951.15 | 0 | 15.82 | 6966.97 | 0 | 0 | 0 | 0
2022121909 | 2 | 0.61557 | 49245.6 | 0 | 0 | 0.38544 | 13490.4 | 0.11788 | 1650.32 | 40000 | 0 | 9245.6 | 4244.8 | 0 | 1650.32 | 5895.12 | 0 | 0 | 0 | 0
2022121910 | 2 | 0.62811 | 50248.8 | 0 | 0 | 0.3414 | 11949 | 0.3327 | 4657.8 | 40000 | 0 | 10248.8 | 1700.2 | 0 | 4657.8 | 6358 | 0 | 0 | 0 | 0
2022121911 | 2 | 0.63268 | 50614.4 | 0 | 0 | 0.3274 | 11459 | 0.38501 | 5390.14 | 40000 | 0 | 10614.4 | 844.6 | 0 | 5390.14 | 6234.74 | 0 | 0 | 0 | 0
2022121912 | 2 | 0.63086 | 50468.8 | 0 | 0 | 0.29591 | 10356.85 | 0.38674 | 5414.36 | 40000 | 0 | 10356.85 | 0 | 111.95 | 5302.41 | 5302.41 | 0 | 0 | 0 | 0
2022121913 | 2 | 0.62462 | 49969.6 | 0 | 0 | 0.27535 | 9637.25 | 0.3902 | 5462.8 | 40000 | 0 | 9637.25 | 0 | 332.35 | 5130.45 | 5130.45 | 0 | 0 | 0 | 0
2022121914 | 2 | 0.61818 | 49454.4 | 0 | 0 | 0.26503 | 9276.05 | 0.40701 | 5698.14 | 40000 | 0 | 9276.05 | 0 | 178.35 | 5519.79 | 5519.79 | 0 | 0 | 0 | 0
2022121915 | 2 | 0.61231 | 48984.8 | 0 | 0 | 0.24973 | 8740.55 | 0.4162 | 5826.8 | 40000 | 0 | 8740.55 | 0 | 244.25 | 5582.55 | 5582.55 | 0 | 0 | 0 | 0
2022121916 | 2 | 0.61132 | 48905.6 | 0 | 0 | 0.24523 | 8583.05 | 0.40303 | 5642.42 | 40000 | 0 | 8583.05 | 0 | 322.55 | 5319.87 | 5319.87 | 0 | 0 | 0 | 0
2022121917 | 2 | 0.61476 | 49180.8 | 0 | 0 | 0.23114 | 8089.9 | 0.2703 | 3784.2 | 40000 | 0 | 8089.9 | 0 | 1090.9 | 2693.3 | 2693.3 | 0 | 0 | 0 | 0
2022121918 | 2 | 0.63132 | 50505.6 | 0 | 0 | 0.20711 | 7248.85 | 0.03419 | 478.66 | 40000 | 0 | 7248.85 | 0 | 478.66 | 0 | 0 | 2778.09 | 0 | 0 | 2778.09
2022121919 | 2 | 0.64309 | 51447.2 | 0 | 0 | 0.24622 | 8617.7 | 0 | 0 | 40000 | 0 | 8617.7 | 0 | 0 | 0 | 0 | 2829.5 | 0 | 0 | 2829.5
2022121920 | 2 | 0.63685 | 50948 | 0 | 0 | 0.26629 | 9320.15 | 0 | 0 | 40000 | 0 | 9320.15 | 0 | 0 | 0 | 0 | 1627.85 | 0 | 0 | 1627.85
2022121921 | 2 | 0.62651 | 50120.8 | 0 | 0 | 0.26689 | 9341.15 | 0 | 0 | 40000 | 0 | 9341.15 | 0 | 0 | 0 | 0 | 779.65 | 0 | 0 | 779.65
2022121922 | 2 | 0.6088 | 48704 | 0 | 0 | 0.26244 | 9185.4 | 0 | 0 | 40000 | 0 | 8704 | 481.4 | 0 | 0 | 481.4 | 0 | 0 | 0 | 0
2022121923 | 2 | 0.5811 | 46488 | 0 | 0 | 0.27812 | 9734.2 | 0 | 0 | 40000 | 0 | 6488 | 3246.2 | 0 | 0 | 3246.2 | 0 | 0 | 0 | 0
2022121924 | 2 | 0.55602 | 44481.6 | 0 | 0 | 0.29123 | 10193.05 | 0 | 0 | 40000 | 0 | 4481.6 | 5711.45 | 0 | 0 | 5711.45 | 0 | 0 | 0 | 0
2022122001 | 3 | 0.53509 | 42807.2 | 0 | 0 | 0.31765 | 11117.75 | 0 | 0 | 40000 | 0 | 2807.2 | 8310.55 | 0 | 0 | 8310.55 | 0 | 0 | 0 | 0
2022122002 | 3 | 0.52437 | 41949.6 | 0 | 0 | 0.32214 | 11274.9 | 0 | 0 | 40000 | 0 | 1949.6 | 9325.3 | 0 | 0 | 9325.3 | 0 | 0 | 0 | 0
2022122003 | 3 | 0.51745 | 41396 | 0 | 0 | 0.33168 | 11608.8 | 0 | 0 | 40000 | 0 | 1396 | 10212.8 | 0 | 0 | 10212.8 | 0 | 0 | 0 | 0
2022122004 | 3 | 0.51475 | 41180 | 0 | 0 | 0.35795 | 12528.25 | 0 | 0 | 40000 | 0 | 1180 | 11348.25 | 0 | 0 | 11348.25 | 0 | 0 | 0 | 0
2022122005 | 3 | 0.52778 | 42222.4 | 0 | 0 | 0.3776 | 13216 | 0 | 0 | 40000 | 0 | 2222.4 | 10993.6 | 0 | 0 | 10993.6 | 0 | 0 | 0 | 0
2022122006 | 3 | 0.5548 | 44384 | 0 | 0 | 0.3834 | 13419 | 0 | 0 | 40000 | 0 | 4384 | 9035 | 0 | 0 | 9035 | 0 | 0 | 0 | 0
2022122007 | 3 | 0.58936 | 47148.8 | 0 | 0 | 0.37364 | 13077.4 | 0 | 0 | 40000 | 0 | 7148.8 | 5928.6 | 0 | 0 | 5928.6 | 0 | 0 | 0 | 0
2022122008 | 3 | 0.61198 | 48958.4 | 0 | 0 | 0.34558 | 12095.3 | 0.00204 | 28.56 | 40000 | 0 | 8958.4 | 3136.9 | 0 | 28.56 | 3165.46 | 0 | 0 | 0 | 0
2022122009 | 3 | 0.62079 | 49663.2 | 0 | 0 | 0.29276 | 10246.6 | 0.13419 | 1878.66 | 40000 | 0 | 9663.2 | 583.4 | 0 | 1878.66 | 2462.06 | 0 | 0 | 0 | 0
2022122010 | 3 | 0.62172 | 49737.6 | 0 | 0 | 0.22784 | 7974.4 | 0.34666 | 4853.24 | 40000 | 0 | 7974.4 | 0 | 1763.2 | 3090.04 | 3090.04 | 0 | 0 | 0 | 0
2022122011 | 3 | 0.61241 | 48992.8 | 0 | 0 | 0.17935 | 6277.25 | 0.39859 | 5580.26 | 40000 | 0 | 6277.25 | 0 | 2715.55 | 2864.71 | 2864.71 | 0 | 0 | 0 | 0
2022122012 | 3 | 0.60178 | 48142.4 | 0 | 0 | 0.14556 | 5094.6 | 0.41916 | 5868.24 | 40000 | 0 | 5094.6 | 0 | 3047.8 | 2820.44 | 2820.44 | 0 | 0 | 0 | 0
2022122013 | 3 | 0.58799 | 47039.2 | 0 | 0 | 0.1293 | 4525.5 | 0.42448 | 5942.72 | 40000 | 0 | 4525.5 | 0 | 2513.7 | 3429.02 | 3429.02 | 0 | 0 | 0 | 0
2022122014 | 3 | 0.57865 | 46292 | 0 | 0 | 0.12221 | 4277.35 | 0.42983 | 6017.62 | 40000 | 0 | 4277.35 | 0 | 2014.65 | 4002.97 | 4002.97 | 0 | 0 | 0 | 0
2022122015 | 3 | 0.57168 | 45734.4 | 0 | 0 | 0.11779 | 4122.65 | 0.43104 | 6034.56 | 40000 | 0 | 4122.65 | 0 | 1611.75 | 4422.81 | 4422.81 | 0 | 0 | 0 | 0
2022122016 | 3 | 0.56818 | 45454.4 | 0 | 0 | 0.11535 | 4037.25 | 0.37956 | 5313.84 | 40000 | 0 | 4037.25 | 0 | 1417.15 | 3896.69 | 3896.69 | 0 | 0 | 0 | 0
2022122017 | 3 | 0.57425 | 45940 | 0 | 0 | 0.11675 | 4086.25 | 0.19514 | 2731.96 | 40000 | 0 | 4086.25 | 0 | 1853.75 | 878.21 | 878.21 | 0 | 0 | 0 | 0
2022122018 | 3 | 0.59985 | 47988 | 0 | 0 | 0.12429 | 4350.15 | 0.01917 | 268.38 | 40000 | 0 | 4350.15 | 0 | 268.38 | 0 | 0 | 3369.47 | 0 | 0 | 3369.47
2022122019 | 3 | 0.62329 | 49863.2 | 0 | 0 | 0.15418 | 5396.3 | 0 | 0 | 40000 | 0 | 5396.3 | 0 | 0 | 0 | 0 | 4466.9 | 0 | 0 | 4466.9
2022122020 | 3 | 0.62786 | 50228.8 | 0 | 0 | 0.16361 | 5726.35 | 0 | 0 | 40000 | 0 | 5726.35 | 0 | 0 | 0 | 0 | 4502.45 | 0 | 0 | 4502.45
2022122021 | 3 | 0.62415 | 49932 | 0 | 0 | 0.15861 | 5551.35 | 0 | 0 | 40000 | 0 | 5551.35 | 0 | 0 | 0 | 0 | 4380.65 | 0 | 0 | 4380.65
2022122022 | 3 | 0.61689 | 49351.2 | 0 | 0 | 0.15641 | 5474.35 | 0 | 0 | 40000 | 0 | 5474.35 | 0 | 0 | 0 | 0 | 3876.85 | 0 | 0 | 3876.85
2022122023 | 3 | 0.5985 | 47880 | 0 | 0 | 0.14774 | 5170.9 | 0 | 0 | 40000 | 0 | 5170.9 | 0 | 0 | 0 | 0 | 2709.1 | 0 | 0 | 2709.1
2022122024 | 3 | 0.57937 | 46349.6 | 0 | 0 | 0.14766 | 5168.1 | 0 | 0 | 40000 | 0 | 5168.1 | 0 | 0 | 0 | 0 | 1181.5 | 0 | 0 | 1181.5
2022122101 | 4 | 0.56491 | 45192.8 | 0 | 0 | 0.15554 | 5443.9 | 0 | 0 | 40000 | 0 | 5192.8 | 251.1 | 0 | 0 | 251.1 | 0 | 0 | 0 | 0
2022122102 | 4 | 0.56024 | 44819.2 | 0 | 0 | 0.16911 | 5918.85 | 0 | 0 | 40000 | 0 | 4819.2 | 1099.65 | 0 | 0 | 1099.65 | 0 | 0 | 0 | 0
2022122103 | 4 | 0.56017 | 44813.6 | 0 | 0 | 0.17738 | 6208.3 | 0 | 0 | 40000 | 0 | 4813.6 | 1394.7 | 0 | 0 | 1394.7 | 0 | 0 | 0 | 0
2022122104 | 4 | 0.56771 | 45416.8 | 0 | 0 | 0.17937 | 6277.95 | 0 | 0 | 40000 | 0 | 5416.8 | 861.15 | 0 | 0 | 861.15 | 0 | 0 | 0 | 0
2022122105 | 4 | 0.58597 | 46877.6 | 0 | 0 | 0.17653 | 6178.55 | 0 | 0 | 40000 | 0 | 6178.55 | 0 | 0 | 0 | 0 | 699.05 | 0 | 0 | 699.05
2022122106 | 4 | 0.6158 | 49264 | 0 | 0 | 0.19613 | 6864.55 | 0 | 0 | 40000 | 0 | 6864.55 | 0 | 0 | 0 | 0 | 2399.45 | 0 | 0 | 2399.45
2022122107 | 4 | 0.6566 | 52528 | 0 | 0 | 0.20887 | 7310.45 | 0 | 0 | 40000 | 0 | 7310.45 | 0 | 0 | 0 | 0 | 5217.55 | 0 | 0 | 5217.55
2022122108 | 4 | 0.67705 | 54164 | 0 | 0 | 0.21953 | 7683.55 | 0.00594 | 83.16 | 40000 | 0 | 7683.55 | 0 | 83.16 | 0 | 0 | 6397.29 | 0 | 0 | 6397.29
2022122109 | 4 | 0.6781 | 54248 | 0 | 0 | 0.23207 | 8122.45 | 0.06727 | 941.78 | 40000 | 0 | 8122.45 | 0 | 941.78 | 0 | 0 | 5183.77 | 0 | 0 | 5183.77
2022122110 | 4 | 0.67245 | 53796 | 0 | 0 | 0.26876 | 9406.6 | 0.14769 | 2067.66 | 40000 | 0 | 9406.6 | 0 | 2067.66 | 0 | 0 | 2321.74 | 0 | 0 | 2321.74
2022122111 | 4 | 0.65223 | 52178.4 | 0 | 0 | 0.28468 | 9963.8 | 0.25266 | 3537.24 | 40000 | 0 | 9963.8 | 0 | 2214.6 | 1322.64 | 1322.64 | 0 | 0 | 0 | 0
2022122112 | 4 | 0.62993 | 50394.4 | 0 | 0 | 0.30905 | 10816.75 | 0.36486 | 5108.04 | 40000 | 0 | 10394.4 | 422.35 | 0 | 5108.04 | 5530.39 | 0 | 0 | 0 | 0
2022122113 | 4 | 0.61215 | 48972 | 0 | 0 | 0.36402 | 12740.7 | 0.39806 | 5572.84 | 40000 | 0 | 8972 | 3768.7 | 0 | 5572.84 | 9341.54 | 0 | 0 | 0 | 0
2022122114 | 4 | 0.59742 | 47793.6 | 0 | 0 | 0.37587 | 13155.45 | 0.41798 | 5851.72 | 40000 | 0 | 7793.6 | 5361.85 | 0 | 5851.72 | 11213.57 | 0 | 0 | 0 | 0
2022122115 | 4 | 0.58498 | 46798.4 | 0 | 0 | 0.36906 | 12917.1 | 0.44065 | 6169.1 | 40000 | 0 | 6798.4 | 6118.7 | 0 | 6169.1 | 12287.8 | 0 | 0 | 0 | 0
2022122116 | 4 | 0.58202 | 46561.6 | 0 | 0 | 0.36491 | 12771.85 | 0.44976 | 6296.64 | 40000 | 0 | 6561.6 | 6210.25 | 0 | 6296.64 | 12506.89 | 0 | 0 | 0 | 0
2022122117 | 4 | 0.5874 | 46992 | 0 | 0 | 0.35355 | 12374.25 | 0.29597 | 4143.58 | 40000 | 0 | 6992 | 5382.25 | 0 | 4143.58 | 9525.83 | 0 | 0 | 0 | 0
2022122118 | 4 | 0.61272 | 49017.6 | 0 | 0 | 0.34582 | 12103.7 | 0.04233 | 592.62 | 40000 | 0 | 9017.6 | 3086.1 | 0 | 592.62 | 3678.72 | 0 | 0 | 0 | 0
2022122119 | 4 | 0.63943 | 51154.4 | 0 | 0 | 0.41473 | 14515.55 | 0 | 0 | 40000 | 0 | 11154.4 | 3361.15 | 0 | 0 | 3361.15 | 0 | 0 | 0 | 0
2022122120 | 4 | 0.64257 | 51405.6 | 0 | 0 | 0.49356 | 17274.6 | 0 | 0 | 40000 | 0 | 11405.6 | 5869 | 0 | 0 | 5869 | 0 | 0 | 0 | 0
2022122121 | 4 | 0.64628 | 51702.4 | 0 | 0 | 0.54658 | 19130.3 | 0 | 0 | 40000 | 0 | 11702.4 | 7427.9 | 0 | 0 | 7427.9 | 0 | 0 | 0 | 0
2022122122 | 4 | 0.63963 | 51170.4 | 0 | 0 | 0.56196 | 19668.6 | 0 | 0 | 40000 | 0 | 11170.4 | 8498.2 | 0 | 0 | 8498.2 | 0 | 0 | 0 | 0
2022122123 | 4 | 0.62334 | 49867.2 | 0 | 0 | 0.56043 | 19615.05 | 0 | 0 | 40000 | 0 | 9867.2 | 9747.85 | 0 | 0 | 9747.85 | 0 | 0 | 0 | 0
2022122124 | 4 | 0.60168 | 48134.4 | 0 | 0 | 0.55978 | 19592.3 | 0 | 0 | 40000 | 0 | 8134.4 | 11457.9 | 0 | 0 | 11457.9 | 0 | 0 | 0 | 0
2022122201 | 5 | 0.58339 | 46671.2 | 0 | 0 | 0.55202 | 19320.7 | 0 | 0 | 40000 | 0 | 6671.2 | 12649.5 | 0 | 0 | 12649.5 | 0 | 0 | 0 | 0
2022122202 | 5 | 0.57197 | 45757.6 | 0 | 0 | 0.54293 | 19002.55 | 0 | 0 | 40000 | 0 | 5757.6 | 13244.95 | 0 | 0 | 13244.95 | 0 | 0 | 0 | 0
2022122203 | 5 | 0.56247 | 44997.6 | 0 | 0 | 0.52857 | 18499.95 | 0 | 0 | 40000 | 0 | 4997.6 | 13502.35 | 0 | 0 | 13502.35 | 0 | 0 | 0 | 0
2022122204 | 5 | 0.55786 | 44628.8 | 0 | 0 | 0.52237 | 18282.95 | 0 | 0 | 40000 | 0 | 4628.8 | 13654.15 | 0 | 0 | 13654.15 | 0 | 0 | 0 | 0
2022122205 | 5 | 0.56382 | 45105.6 | 0 | 0 | 0.52367 | 18328.45 | 0 | 0 | 40000 | 0 | 5105.6 | 13222.85 | 0 | 0 | 13222.85 | 0 | 0 | 0 | 0
2022122206 | 5 | 0.58285 | 46628 | 0 | 0 | 0.50851 | 17797.85 | 0 | 0 | 40000 | 0 | 6628 | 11169.85 | 0 | 0 | 11169.85 | 0 | 0 | 0 | 0
2022122207 | 5 | 0.61057 | 48845.6 | 0 | 0 | 0.52079 | 18227.65 | 0 | 0 | 40000 | 0 | 8845.6 | 9382.05 | 0 | 0 | 9382.05 | 0 | 0 | 0 | 0
2022122208 | 5 | 0.6322 | 50576 | 0 | 0 | 0.53565 | 18747.75 | 0.00322 | 45.08 | 40000 | 0 | 10576 | 8171.75 | 0 | 45.08 | 8216.83 | 0 | 0 | 0 | 0
2022122209 | 5 | 0.65211 | 52168.8 | 0 | 0 | 0.52153 | 18253.55 | 0.10539 | 1475.46 | 40000 | 0 | 12168.8 | 6084.75 | 0 | 1475.46 | 7560.21 | 0 | 0 | 0 | 0
2022122210 | 5 | 0.67689 | 54151.2 | 0 | 0 | 0.54518 | 19081.3 | 0.14201 | 1988.14 | 40000 | 0 | 14151.2 | 4930.1 | 0 | 1988.14 | 6918.24 | 0 | 0 | 0 | 0
2022122211 | 5 | 0.69448 | 55558.4 | 0 | 0 | 0.56366 | 19728.1 | 0.16812 | 2353.68 | 40000 | 0 | 15558.4 | 4169.7 | 0 | 2353.68 | 6523.38 | 0 | 0 | 0 | 0
2022122212 | 5 | 0.70736 | 56588.8 | 0 | 0 | 0.55318 | 19361.3 | 0.22327 | 3125.78 | 40000 | 0 | 16588.8 | 2772.5 | 0 | 3125.78 | 5898.28 | 0 | 0 | 0 | 0
2022122213 | 5 | 0.71702 | 57361.6 | 0 | 0 | 0.54778 | 19172.3 | 0.21909 | 3067.26 | 40000 | 0 | 17361.6 | 1810.7 | 0 | 3067.26 | 4877.96 | 0 | 0 | 0 | 0
2022122214 | 5 | 0.73091 | 58472.8 | 0 | 0 | 0.55235 | 19332.25 | 0.19436 | 2721.04 | 40000 | 0 | 18472.8 | 859.45 | 0 | 2721.04 | 3580.49 | 0 | 0 | 0 | 0
2022122215 | 5 | 0.74345 | 59476 | 0 | 0 | 0.55021 | 19257.35 | 0.19359 | 2710.26 | 40000 | 0 | 19257.35 | 0 | 218.65 | 2491.61 | 2491.61 | 0 | 0 | 0 | 0
2022122216 | 5 | 0.76065 | 60852 | 0 | 0 | 0.56093 | 19632.55 | 0.18755 | 2625.7 | 40000 | 0 | 19632.55 | 0 | 1219.45 | 1406.25 | 1406.25 | 0 | 0 | 0 | 0
2022122217 | 5 | 0.78548 | 62838.4 | 0 | 0 | 0.60024 | 21008.4 | 0.12524 | 1753.36 | 40000 | 0 | 21008.4 | 0 | 1753.36 | 0 | 0 | 76.64 | 0 | 0 | 76.64
2022122218 | 5 | 0.83785 | 67028 | 0 | 0 | 0.6532 | 22862 | 0.01821 | 254.94 | 40000 | 0 | 22862 | 0 | 254.94 | 0 | 0 | 3911.06 | 0 | 0 | 3911.06
2022122219 | 5 | 0.88285 | 70628 | 0 | 0 | 0.66483 | 23269.05 | 0 | 0 | 40000 | 0 | 23269.05 | 0 | 0 | 0 | 0 | 7358.95 | 0 | 0 | 7358.95
2022122220 | 5 | 0.90326 | 72260.8 | 0 | 0 | 0.65158 | 22805.3 | 0 | 0 | 40000 | 0 | 22805.3 | 0 | 0 | 0 | 0 | 9455.5 | 0 | 0 | 9455.5
2022122221 | 5 | 0.91795 | 73436 | 0 | 0 | 0.64341 | 22519.35 | 0 | 0 | 40000 | 0 | 22519.35 | 0 | 0 | 0 | 0 | 10916.65 | 0 | 0 | 10916.65
2022122222 | 5 | 0.92266 | 73812.8 | 0 | 0 | 0.63087 | 22080.45 | 0 | 0 | 40000 | 0 | 22080.45 | 0 | 0 | 0 | 0 | 11732.35 | 0 | 0 | 11732.35
2022122223 | 5 | 0.91159 | 72927.2 | 0 | 0 | 0.61135 | 21397.25 | 0 | 0 | 40000 | 0 | 21397.25 | 0 | 0 | 0 | 0 | 11529.95 | 0 | 0 | 11529.95
2022122224 | 5 | 0.89802 | 71841.6 | 0 | 0 | 0.58189 | 20366.15 | 0 | 0 | 40000 | 0 | 20366.15 | 0 | 0 | 0 | 0 | 11475.45 | 0 | 0 | 11475.45
2022122301 | 6 | 0.889 | 71120 | 0 | 0 | 0.53966 | 18888.1 | 0 | 0 | 40000 | 0 | 18888.1 | 0 | 0 | 0 | 0 | 12231.9 | 0 | 0 | 12231.9
2022122302 | 6 | 0.88335 | 70668 | 0 | 0 | 0.4872 | 17052 | 0 | 0 | 40000 | 0 | 17052 | 0 | 0 | 0 | 0 | 13616 | 0 | 0 | 13616
2022122303 | 6 | 0.87904 | 70323.2 | 0 | 0 | 0.44825 | 15688.75 | 0 | 0 | 40000 | 0 | 15688.75 | 0 | 0 | 0 | 0 | 14634.45 | 0 | 0 | 14634.45
2022122304 | 6 | 0.88116 | 70492.8 | 0 | 0 | 0.41718 | 14601.3 | 0 | 0 | 40000 | 0 | 14601.3 | 0 | 0 | 0 | 0 | 15891.5 | 0 | 0 | 15891.5
2022122305 | 6 | 0.88786 | 71028.8 | 0 | 0 | 0.40525 | 14183.75 | 0 | 0 | 40000 | 0 | 14183.75 | 0 | 0 | 0 | 0 | 16845.05 | 0 | 0 | 16845.05
2022122306 | 6 | 0.89945 | 71956 | 0 | 0 | 0.38485 | 13469.75 | 0 | 0 | 40000 | 0 | 13469.75 | 0 | 0 | 0 | 0 | 18486.25 | 0 | 0 | 18486.25
2022122307 | 6 | 0.91481 | 73184.8 | 0 | 0 | 0.36202 | 12670.7 | 0 | 0 | 40000 | 0 | 12670.7 | 0 | 0 | 0 | 0 | 20514.1 | 0 | 0 | 20514.1
2022122308 | 6 | 0.92667 | 74133.6 | 0 | 0 | 0.32533 | 11386.55 | 0.01136 | 159.04 | 40000 | 0 | 11386.55 | 0 | 159.04 | 0 | 0 | 22588.01 | 0 | 0 | 22588.01
2022122309 | 6 | 0.92578 | 74062.4 | 0 | 0 | 0.27958 | 9785.3 | 0.16697 | 2337.58 | 40000 | 0 | 9785.3 | 0 | 2337.58 | 0 | 0 | 21939.52 | 0 | 0 | 21939.52
2022122310 | 6 | 0.92283 | 73826.4 | 0 | 0 | 0.28332 | 9916.2 | 0.4456 | 6238.4 | 40000 | 0 | 9916.2 | 0 | 6238.4 | 0 | 0 | 17671.8 | 0 | 0 | 17671.8
2022122311 | 6 | 0.90423 | 72338.4 | 0 | 0 | 0.27317 | 9560.95 | 0.52716 | 7380.24 | 40000 | 0 | 9560.95 | 0 | 7380.24 | 0 | 0 | 15397.21 | 0 | 0 | 15397.21
2022122312 | 6 | 0.87661 | 70128.8 | 0 | 0 | 0.25638 | 8973.3 | 0.52841 | 7397.74 | 40000 | 0 | 8973.3 | 0 | 7397.74 | 0 | 0 | 13757.76 | 0 | 0 | 13757.76
2022122313 | 6 | 0.84466 | 67572.8 | 0 | 0 | 0.23875 | 8356.25 | 0.53703 | 7518.42 | 40000 | 0 | 8356.25 | 0 | 7518.42 | 0 | 0 | 11698.13 | 0 | 0 | 11698.13
2022122314 | 6 | 0.82039 | 65631.2 | 0 | 0 | 0.22862 | 8001.7 | 0.53791 | 7530.74 | 40000 | 0 | 8001.7 | 0 | 7530.74 | 0 | 0 | 10098.76 | 0 | 0 | 10098.76
2022122315 | 6 | 0.79951 | 63960.8 | 0 | 0 | 0.19959 | 6985.65 | 0.51877 | 7262.78 | 40000 | 0 | 6985.65 | 0 | 7262.78 | 0 | 0 | 9712.37 | 0 | 0 | 9712.37
2022122316 | 6 | 0.79419 | 63535.2 | 0 | 0 | 0.17766 | 6218.1 | 0.50683 | 7095.62 | 40000 | 0 | 6218.1 | 0 | 7095.62 | 0 | 0 | 10221.48 | 0 | 0 | 10221.48
2022122317 | 6 | 0.80538 | 64430.4 | 0 | 0 | 0.1592 | 5572 | 0.27447 | 3842.58 | 40000 | 0 | 5572 | 0 | 3842.58 | 0 | 0 | 15015.82 | 0 | 0 | 15015.82
2022122318 | 6 | 0.83408 | 66726.4 | 0 | 0 | 0.12615 | 4415.25 | 0.03244 | 454.16 | 40000 | 0 | 4415.25 | 0 | 454.16 | 0 | 0 | 21856.99 | 0 | 0 | 21856.99
2022122319 | 6 | 0.85116 | 68092.8 | 0 | 0 | 0.09739 | 3408.65 | 0 | 0 | 40000 | 0 | 3408.65 | 0 | 0 | 0 | 0 | 24684.15 | 0 | 0 | 24684.15
2022122320 | 6 | 0.85155 | 68124 | 0 | 0 | 0.08366 | 2928.1 | 0 | 0 | 40000 | 0 | 2928.1 | 0 | 0 | 0 | 0 | 25195.9 | 0 | 0 | 25195.9
2022122321 | 6 | 0.8499 | 67992 | 0 | 0 | 0.07454 | 2608.9 | 0 | 0 | 40000 | 0 | 2608.9 | 0 | 0 | 0 | 0 | 25383.1 | 0 | 0 | 25383.1
2022122322 | 6 | 0.8434 | 67472 | 0 | 0 | 0.07309 | 2558.15 | 0 | 0 | 40000 | 0 | 2558.15 | 0 | 0 | 0 | 0 | 24913.85 | 0 | 0 | 24913.85
2022122323 | 6 | 0.83046 | 66436.8 | 0 | 0 | 0.07103 | 2486.05 | 0 | 0 | 40000 | 0 | 2486.05 | 0 | 0 | 0 | 0 | 23950.75 | 0 | 0 | 23950.75
2022122324 | 6 | 0.81157 | 64925.6 | 0 | 0 | 0.07502 | 2625.7 | 0 | 0 | 40000 | 0 | 2625.7 | 0 | 0 | 0 | 0 | 22299.9 | 0 | 0 | 22299.9
2022122401 | 7 | 0.79473 | 63578.4 | 0 | 0 | 0.09238 | 3233.3 | 0 | 0 | 40000 | 0 | 3233.3 | 0 | 0 | 0 | 0 | 20345.1 | 0 | 0 | 20345.1
2022122402 | 7 | 0.78702 | 62961.6 | 0 | 0 | 0.11314 | 3959.9 | 0 | 0 | 40000 | 0 | 3959.9 | 0 | 0 | 0 | 0 | 19001.7 | 0 | 0 | 19001.7
2022122403 | 7 | 0.78413 | 62730.4 | 0 | 0 | 0.11989 | 4196.15 | 0 | 0 | 40000 | 0 | 4196.15 | 0 | 0 | 0 | 0 | 18534.25 | 0 | 0 | 18534.25
2022122404 | 7 | 0.78507 | 62805.6 | 0 | 0 | 0.12419 | 4346.65 | 0 | 0 | 40000 | 0 | 4346.65 | 0 | 0 | 0 | 0 | 18458.95 | 0 | 0 | 18458.95
2022122405 | 7 | 0.78874 | 63099.2 | 0 | 0 | 0.12949 | 4532.15 | 0 | 0 | 40000 | 0 | 4532.15 | 0 | 0 | 0 | 0 | 18567.05 | 0 | 0 | 18567.05
2022122406 | 7 | 0.79598 | 63678.4 | 0 | 0 | 0.12653 | 4428.55 | 0 | 0 | 40000 | 0 | 4428.55 | 0 | 0 | 0 | 0 | 19249.85 | 0 | 0 | 19249.85
2022122407 | 7 | 0.80939 | 64751.2 | 0 | 0 | 0.13007 | 4552.45 | 0 | 0 | 40000 | 0 | 4552.45 | 0 | 0 | 0 | 0 | 20198.75 | 0 | 0 | 20198.75
2022122408 | 7 | 0.82158 | 65726.4 | 0 | 0 | 0.13397 | 4688.95 | 0.00893 | 125.02 | 40000 | 0 | 4688.95 | 0 | 125.02 | 0 | 0 | 20912.43 | 0 | 0 | 20912.43
2022122409 | 7 | 0.81711 | 65368.8 | 0 | 0 | 0.13293 | 4652.55 | 0.22532 | 3154.48 | 40000 | 0 | 4652.55 | 0 | 3154.48 | 0 | 0 | 17561.77 | 0 | 0 | 17561.77
2022122410 | 7 | 0.80075 | 64060 | 0 | 0 | 0.12139 | 4248.65 | 0.53049 | 7426.86 | 40000 | 0 | 4248.65 | 0 | 7426.86 | 0 | 0 | 12384.49 | 0 | 0 | 12384.49
2022122411 | 7 | 0.76943 | 61554.4 | 0 | 0 | 0.13085 | 4579.75 | 0.60453 | 8463.42 | 40000 | 0 | 4579.75 | 0 | 8463.42 | 0 | 0 | 8511.23 | 0 | 0 | 8511.23
2022122412 | 7 | 0.73272 | 58617.6 | 0 | 0 | 0.12916 | 4520.6 | 0.59563 | 8338.82 | 40000 | 0 | 4520.6 | 0 | 8338.82 | 0 | 0 | 5758.18 | 0 | 0 | 5758.18
2022122413 | 7 | 0.69445 | 55556 | 0 | 0 | 0.12176 | 4261.6 | 0.58432 | 8180.48 | 40000 | 0 | 4261.6 | 0 | 8180.48 | 0 | 0 | 3113.92 | 0 | 0 | 3113.92
2022122414 | 7 | 0.6602 | 52816 | 0 | 0 | 0.09947 | 3481.45 | 0.59876 | 8382.64 | 40000 | 0 | 3481.45 | 0 | 8382.64 | 0 | 0 | 951.91 | 0 | 0 | 951.91
2022122415 | 7 | 0.6344 | 50752 | 0 | 0 | 0.08019 | 2806.65 | 0.62168 | 8703.52 | 40000 | 0 | 2806.65 | 0 | 7945.35 | 758.17 | 758.17 | 0 | 0 | 0 | 0
2022122416 | 7 | 0.62321 | 49856.8 | 0 | 0 | 0.06755 | 2364.25 | 0.60823 | 8515.22 | 40000 | 0 | 2364.25 | 0 | 7492.55 | 1022.67 | 1022.67 | 0 | 0 | 0 | 0
2022122417 | 7 | 0.62772 | 50217.6 | 0 | 0 | 0.05009 | 1753.15 | 0.39954 | 5593.56 | 40000 | 0 | 1753.15 | 0 | 5593.56 | 0 | 0 | 2870.89 | 0 | 0 | 2870.89
2022122418 | 7 | 0.66501 | 53200.8 | 0 | 0 | 0.04449 | 1557.15 | 0.04994 | 699.16 | 40000 | 0 | 1557.15 | 0 | 699.16 | 0 | 0 | 10944.49 | 0 | 0 | 10944.49
2022122419 | 7 | 0.70159 | 56127.2 | 0 | 0 | 0.04445 | 1555.75 | 0 | 0 | 40000 | 0 | 1555.75 | 0 | 0 | 0 | 0 | 14571.45 | 0 | 0 | 14571.45
2022122420 | 7 | 0.71426 | 57140.8 | 0 | 0 | 0.05803 | 2031.05 | 0 | 0 | 40000 | 0 | 2031.05 | 0 | 0 | 0 | 0 | 15109.75 | 0 | 0 | 15109.75
2022122421 | 7 | 0.72224 | 57779.2 | 0 | 0 | 0.07204 | 2521.4 | 0 | 0 | 40000 | 0 | 2521.4 | 0 | 0 | 0 | 0 | 15257.8 | 0 | 0 | 15257.8
2022122422 | 7 | 0.72634 | 58107.2 | 0 | 0 | 0.10042 | 3514.7 | 0 | 0 | 40000 | 0 | 3514.7 | 0 | 0 | 0 | 0 | 14592.5 | 0 | 0 | 14592.5
2022122423 | 7 | 0.72283 | 57826.4 | 0 | 0 | 0.14502 | 5075.7 | 0 | 0 | 40000 | 0 | 5075.7 | 0 | 0 | 0 | 0 | 12750.7 | 0 | 0 | 12750.7
2022122424 | 7 | 0.71896 | 57516.8 | 0 | 0 | 0.17363 | 6077.05 | 0 | 0 | 40000 | 0 | 6077.05 | 0 | 0 | 0 | 0 | 11439.75 | 0 | 0 | 11439.75
2022122501 | 1 | 0.71661 | 57328.8 | 0 | 0 | 0.19704 | 6896.4 | 0 | 0 | 40000 | 0 | 6896.4 | 0 | 0 | 0 | 0 | 10432.4 | 0 | 0 | 10432.4
2022122502 | 1 | 0.71666 | 57332.8 | 0 | 0 | 0.21475 | 7516.25 | 0 | 0 | 40000 | 0 | 7516.25 | 0 | 0 | 0 | 0 | 9816.55 | 0 | 0 | 9816.55
2022122503 | 1 | 0.71963 | 57570.4 | 0 | 0 | 0.21846 | 7646.1 | 0 | 0 | 40000 | 0 | 7646.1 | 0 | 0 | 0 | 0 | 9924.3 | 0 | 0 | 9924.3
2022122504 | 1 | 0.72158 | 57726.4 | 0 | 0 | 0.22017 | 7705.95 | 0 | 0 | 40000 | 0 | 7705.95 | 0 | 0 | 0 | 0 | 10020.45 | 0 | 0 | 10020.45
2022122505 | 1 | 0.7251 | 58008 | 0 | 0 | 0.21493 | 7522.55 | 0 | 0 | 40000 | 0 | 7522.55 | 0 | 0 | 0 | 0 | 10485.45 | 0 | 0 | 10485.45
2022122506 | 1 | 0.73636 | 58908.8 | 0 | 0 | 0.19702 | 6895.7 | 0 | 0 | 40000 | 0 | 6895.7 | 0 | 0 | 0 | 0 | 12013.1 | 0 | 0 | 12013.1
2022122507 | 1 | 0.74997 | 59997.6 | 0 | 0 | 0.17577 | 6151.95 | 0 | 0 | 40000 | 0 | 6151.95 | 0 | 0 | 0 | 0 | 13845.65 | 0 | 0 | 13845.65
2022122508 | 1 | 0.76264 | 61011.2 | 0 | 0 | 0.1583 | 5540.5 | 0.01219 | 170.66 | 40000 | 0 | 5540.5 | 0 | 170.66 | 0 | 0 | 15300.04 | 0 | 0 | 15300.04
2022122509 | 1 | 0.74809 | 59847.2 | 0 | 0 | 0.14151 | 4952.85 | 0.24509 | 3431.26 | 40000 | 0 | 4952.85 | 0 | 3431.26 | 0 | 0 | 11463.09 | 0 | 0 | 11463.09
2022122510 | 1 | 0.7063 | 56504 | 0 | 0 | 0.08383 | 2934.05 | 0.57947 | 8112.58 | 40000 | 0 | 2934.05 | 0 | 8112.58 | 0 | 0 | 5457.37 | 0 | 0 | 5457.37
2022122511 | 1 | 0.65628 | 52502.4 | 0 | 0 | 0.05586 | 1955.1 | 0.61268 | 8577.52 | 40000 | 0 | 1955.1 | 0 | 8577.52 | 0 | 0 | 1969.78 | 0 | 0 | 1969.78
2022122512 | 1 | 0.61109 | 48887.2 | 0 | 0 | 0.0785 | 2747.5 | 0.58818 | 8234.52 | 40000 | 0 | 2747.5 | 0 | 6139.7 | 2094.82 | 2094.82 | 0 | 0 | 0 | 0
2022122513 | 1 | 0.57211 | 45768.8 | 0 | 0 | 0.13373 | 4680.55 | 0.49956 | 6993.84 | 40000 | 0 | 4680.55 | 0 | 1088.25 | 5905.59 | 5905.59 | 0 | 0 | 0 | 0
2022122514 | 1 | 0.53872 | 43097.6 | 0 | 0 | 0.17148 | 6001.8 | 0.32757 | 4585.98 | 40000 | 0 | 3097.6 | 2904.2 | 0 | 4585.98 | 7490.18 | 0 | 0 | 0 | 0
2022122515 | 1 | 0.51645 | 41316 | 0 | 0 | 0.18149 | 6352.15 | 0.21926 | 3069.64 | 40000 | 0 | 1316 | 5036.15 | 0 | 3069.64 | 8105.79 | 0 | 0 | 0 | 0
2022122516 | 1 | 0.50633 | 40506.4 | 0 | 0 | 0.19121 | 6692.35 | 0.14571 | 2039.94 | 40000 | 0 | 506.4 | 6185.95 | 0 | 2039.94 | 8225.89 | 0 | 0 | 0 | 0
2022122517 | 1 | 0.51181 | 40944.8 | 0 | 0 | 0.21092 | 7382.2 | 0.12992 | 1818.88 | 40000 | 0 | 944.8 | 6437.4 | 0 | 1818.88 | 8256.28 | 0 | 0 | 0 | 0
2022122518 | 1 | 0.54729 | 43783.2 | 0 | 0 | 0.25348 | 8871.8 | 0.0327 | 457.8 | 40000 | 0 | 3783.2 | 5088.6 | 0 | 457.8 | 5546.4 | 0 | 0 | 0 | 0
2022122519 | 1 | 0.58773 | 47018.4 | 0 | 0 | 0.37184 | 13014.4 | 0 | 0 | 40000 | 0 | 7018.4 | 5996 | 0 | 0 | 5996 | 0 | 0 | 0 | 0
2022122520 | 1 | 0.60696 | 48556.8 | 0 | 0 | 0.4367 | 15284.5 | 0 | 0 | 40000 | 0 | 8556.8 | 6727.7 | 0 | 0 | 6727.7 | 0 | 0 | 0 | 0
2022122521 | 1 | 0.62133 | 49706.4 | 0 | 0 | 0.46086 | 16130.1 | 0 | 0 | 40000 | 0 | 9706.4 | 6423.7 | 0 | 0 | 6423.7 | 0 | 0 | 0 | 0
2022122522 | 1 | 0.62794 | 50235.2 | 0 | 0 | 0.46667 | 16333.45 | 0 | 0 | 40000 | 0 | 10235.2 | 6098.25 | 0 | 0 | 6098.25 | 0 | 0 | 0 | 0
2022122523 | 1 | 0.62615 | 50092 | 0 | 0 | 0.48988 | 17145.8 | 0 | 0 | 40000 | 0 | 10092 | 7053.8 | 0 | 0 | 7053.8 | 0 | 0 | 0 | 0
2022122524 | 1 | 0.622 | 49760 | 0 | 0 | 0.50961 | 17836.35 | 0 | 0 | 40000 | 0 | 9760 | 8076.35 | 0 | 0 | 8076.35 | 0 | 0 | 0 | 0
2022122601 | 2 | 0.61415 | 49132 | 0 | 0 | 0.4975 | 17412.5 | 0 | 0 | 40000 | 0 | 9132 | 8280.5 | 0 | 0 | 8280.5 | 0 | 0 | 0 | 0
2022122602 | 2 | 0.61271 | 49016.8 | 0 | 0 | 0.47732 | 16706.2 | 0 | 0 | 40000 | 0 | 9016.8 | 7689.4 | 0 | 0 | 7689.4 | 0 | 0 | 0 | 0
2022122603 | 2 | 0.6137 | 49096 | 0 | 0 | 0.42098 | 14734.3 | 0 | 0 | 40000 | 0 | 9096 | 5638.3 | 0 | 0 | 5638.3 | 0 | 0 | 0 | 0
2022122604 | 2 | 0.62021 | 49616.8 | 0 | 0 | 0.36274 | 12695.9 | 0 | 0 | 40000 | 0 | 9616.8 | 3079.1 | 0 | 0 | 3079.1 | 0 | 0 | 0 | 0
2022122605 | 2 | 0.63246 | 50596.8 | 0 | 0 | 0.33405 | 11691.75 | 0 | 0 | 40000 | 0 | 10596.8 | 1094.95 | 0 | 0 | 1094.95 | 0 | 0 | 0 | 0
2022122606 | 2 | 0.65085 | 52068 | 0 | 0 | 0.29372 | 10280.2 | 0 | 0 | 40000 | 0 | 10280.2 | 0 | 0 | 0 | 0 | 1787.8 | 0 | 0 | 1787.8
2022122607 | 2 | 0.67078 | 53662.4 | 0 | 0 | 0.29032 | 10161.2 | 0 | 0 | 40000 | 0 | 10161.2 | 0 | 0 | 0 | 0 | 3501.2 | 0 | 0 | 3501.2
2022122608 | 2 | 0.68308 | 54646.4 | 0 | 0 | 0.33613 | 11764.55 | 0.00953 | 133.42 | 40000 | 0 | 11764.55 | 0 | 133.42 | 0 | 0 | 2748.43 | 0 | 0 | 2748.43
2022122609 | 2 | 0.67528 | 54022.4 | 0 | 0 | 0.37907 | 13267.45 | 0.22424 | 3139.36 | 40000 | 0 | 13267.45 | 0 | 754.95 | 2384.41 | 2384.41 | 0 | 0 | 0 | 0
2022122610 | 2 | 0.65415 | 52332 | 0 | 0 | 0.34839 | 12193.65 | 0.51415 | 7198.1 | 40000 | 0 | 12193.65 | 0 | 138.35 | 7059.75 | 7059.75 | 0 | 0 | 0 | 0
2022122611 | 2 | 0.6295 | 50360 | 0 | 0 | 0.37585 | 13154.75 | 0.4758 | 6661.2 | 40000 | 0 | 10360 | 2794.75 | 0 | 6661.2 | 9455.95 | 0 | 0 | 0 | 0
2022122612 | 2 | 0.60113 | 48090.4 | 0 | 0 | 0.42757 | 14964.95 | 0.25099 | 3513.86 | 40000 | 0 | 8090.4 | 6874.55 | 0 | 3513.86 | 10388.41 | 0 | 0 | 0 | 0
2022122613 | 2 | 0.57164 | 45731.2 | 0 | 0 | 0.41481 | 14518.35 | 0.13467 | 1885.38 | 40000 | 0 | 5731.2 | 8787.15 | 0 | 1885.38 | 10672.53 | 0 | 0 | 0 | 0
2022122614 | 2 | 0.54185 | 43348 | 0 | 0 | 0.37577 | 13151.95 | 0.09111 | 1275.54 | 40000 | 0 | 3348 | 9803.95 | 0 | 1275.54 | 11079.49 | 0 | 0 | 0 | 0
2022122615 | 2 | 0.51862 | 41489.6 | 0 | 0 | 0.33194 | 11617.9 | 0.08906 | 1246.84 | 40000 | 0 | 1489.6 | 10128.3 | 0 | 1246.84 | 11375.14 | 0 | 0 | 0 | 0
2022122616 | 2 | 0.50925 | 40740 | 0 | 0 | 0.27448 | 9606.8 | 0.18338 | 2567.32 | 40000 | 0 | 740 | 8866.8 | 0 | 2567.32 | 11434.12 | 0 | 0 | 0 | 0
2022122617 | 2 | 0.51255 | 41004 | 0 | 0 | 0.22329 | 7815.15 | 0.25622 | 3587.08 | 40000 | 0 | 1004 | 6811.15 | 0 | 3587.08 | 10398.23 | 0 | 0 | 0 | 0
2022122618 | 2 | 0.54261 | 43408.8 | 0 | 0 | 0.16899 | 5914.65 | 0.04933 | 690.62 | 40000 | 0 | 3408.8 | 2505.85 | 0 | 690.62 | 3196.47 | 0 | 0 | 0 | 0
2022122619 | 2 | 0.57673 | 46138.4 | 0 | 0 | 0.15986 | 5595.1 | 0 | 0 | 40000 | 0 | 5595.1 | 0 | 0 | 0 | 0 | 543.3 | 0 | 0 | 543.3
2022122620 | 2 | 0.58622 | 46897.6 | 0 | 0 | 0.16113 | 5639.55 | 0 | 0 | 40000 | 0 | 5639.55 | 0 | 0 | 0 | 0 | 1258.05 | 0 | 0 | 1258.05
2022122621 | 2 | 0.59547 | 47637.6 | 0 | 0 | 0.15913 | 5569.55 | 0 | 0 | 40000 | 0 | 5569.55 | 0 | 0 | 0 | 0 | 2068.05 | 0 | 0 | 2068.05
2022122622 | 2 | 0.60113 | 48090.4 | 0 | 0 | 0.1491 | 5218.5 | 0 | 0 | 40000 | 0 | 5218.5 | 0 | 0 | 0 | 0 | 2871.9 | 0 | 0 | 2871.9
2022122623 | 2 | 0.60067 | 48053.6 | 0 | 0 | 0.14339 | 5018.65 | 0 | 0 | 40000 | 0 | 5018.65 | 0 | 0 | 0 | 0 | 3034.95 | 0 | 0 | 3034.95
2022122624 | 2 | 0.59401 | 47520.8 | 0 | 0 | 0.14476 | 5066.6 | 0 | 0 | 40000 | 0 | 5066.6 | 0 | 0 | 0 | 0 | 2454.2 | 0 | 0 | 2454.2
2022122701 | 3 | 0.58235 | 46588 | 0 | 0 | 0.14809 | 5183.15 | 0 | 0 | 40000 | 0 | 5183.15 | 0 | 0 | 0 | 0 | 1404.85 | 0 | 0 | 1404.85
2022122702 | 3 | 0.58459 | 46767.2 | 0 | 0 | 0.16888 | 5910.8 | 0 | 0 | 40000 | 0 | 5910.8 | 0 | 0 | 0 | 0 | 856.4 | 0 | 0 | 856.4
2022122703 | 3 | 0.59513 | 47610.4 | 0 | 0 | 0.19807 | 6932.45 | 0 | 0 | 40000 | 0 | 6932.45 | 0 | 0 | 0 | 0 | 677.95 | 0 | 0 | 677.95
2022122704 | 3 | 0.60643 | 48514.4 | 0 | 0 | 0.24303 | 8506.05 | 0 | 0 | 40000 | 0 | 8506.05 | 0 | 0 | 0 | 0 | 8.35 | 0 | 0 | 8.35
2022122705 | 3 | 0.62743 | 50194.4 | 0 | 0 | 0.30364 | 10627.4 | 0 | 0 | 40000 | 0 | 10194.4 | 433 | 0 | 0 | 433 | 0 | 0 | 0 | 0
2022122706 | 3 | 0.65978 | 52782.4 | 0 | 0 | 0.36751 | 12862.85 | 0 | 0 | 40000 | 0 | 12782.4 | 80.45 | 0 | 0 | 80.45 | 0 | 0 | 0 | 0
2022122707 | 3 | 0.69903 | 55922.4 | 0 | 0 | 0.43925 | 15373.75 | 0 | 0 | 40000 | 0 | 15373.75 | 0 | 0 | 0 | 0 | 548.65 | 0 | 0 | 548.65
2022122708 | 3 | 0.72547 | 58037.6 | 0 | 0 | 0.51044 | 17865.4 | 0.01077 | 150.78 | 40000 | 0 | 17865.4 | 0 | 150.78 | 0 | 0 | 21.42 | 0 | 0 | 21.42
2022122709 | 3 | 0.72046 | 57636.8 | 0 | 0 | 0.51907 | 18167.45 | 0.22684 | 3175.76 | 40000 | 0 | 17636.8 | 530.65 | 0 | 3175.76 | 3706.41 | 0 | 0 | 0 | 0
2022122710 | 3 | 0.69281 | 55424.8 | 0 | 0 | 0.45336 | 15867.6 | 0.44718 | 6260.52 | 40000 | 0 | 15424.8 | 442.8 | 0 | 6260.52 | 6703.32 | 0 | 0 | 0 | 0
2022122711 | 3 | 0.65768 | 52614.4 | 0 | 0 | 0.44404 | 15541.4 | 0.45677 | 6394.78 | 40000 | 0 | 12614.4 | 2927 | 0 | 6394.78 | 9321.78 | 0 | 0 | 0 | 0
2022122712 | 3 | 0.6246 | 49968 | 0 | 0 | 0.46891 | 16411.85 | 0.40411 | 5657.54 | 40000 | 0 | 9968 | 6443.85 | 0 | 5657.54 | 12101.39 | 0 | 0 | 0 | 0
2022122713 | 3 | 0.59374 | 47499.2 | 0 | 0 | 0.49605 | 17361.75 | 0.34293 | 4801.02 | 40000 | 0 | 7499.2 | 9862.55 | 0 | 4801.02 | 14663.57 | 0 | 0 | 0 | 0
2022122714 | 3 | 0.56963 | 45570.4 | 0 | 0 | 0.50033 | 17511.55 | 0.30586 | 4282.04 | 40000 | 0 | 5570.4 | 11941.15 | 0 | 4282.04 | 16223.19 | 0 | 0 | 0 | 0
2022122715 | 3 | 0.55419 | 44335.2 | 0 | 0 | 0.50629 | 17720.15 | 0.21341 | 2987.74 | 40000 | 0 | 4335.2 | 13384.95 | 0 | 2987.74 | 16372.69 | 0 | 0 | 0 | 0
2022122716 | 3 | 0.54657 | 43725.6 | 0 | 0 | 0.50837 | 17792.95 | 0.17365 | 2431.1 | 40000 | 0 | 3725.6 | 14067.35 | 0 | 2431.1 | 16498.45 | 0 | 0 | 0 | 0
2022122717 | 3 | 0.55411 | 44328.8 | 0 | 0 | 0.53463 | 18712.05 | 0.12325 | 1725.5 | 40000 | 0 | 4328.8 | 14383.25 | 0 | 1725.5 | 16108.75 | 0 | 0 | 0 | 0
2022122718 | 3 | 0.58629 | 46903.2 | 0 | 0 | 0.57147 | 20001.45 | 0.01604 | 224.56 | 40000 | 0 | 6903.2 | 13098.25 | 0 | 224.56 | 13322.81 | 0 | 0 | 0 | 0
2022122719 | 3 | 0.61845 | 49476 | 0 | 0 | 0.59988 | 20995.8 | 0 | 0 | 40000 | 0 | 9476 | 11519.8 | 0 | 0 | 11519.8 | 0 | 0 | 0 | 0
2022122720 | 3 | 0.62479 | 49983.2 | 0 | 0 | 0.62117 | 21740.95 | 0 | 0 | 40000 | 0 | 9983.2 | 11757.75 | 0 | 0 | 11757.75 | 0 | 0 | 0 | 0
2022122721 | 3 | 0.62616 | 50092.8 | 0 | 0 | 0.62489 | 21871.15 | 0 | 0 | 40000 | 0 | 10092.8 | 11778.35 | 0 | 0 | 11778.35 | 0 | 0 | 0 | 0
2022122722 | 3 | 0.61931 | 49544.8 | 0 | 0 | 0.62971 | 22039.85 | 0 | 0 | 40000 | 0 | 9544.8 | 12495.05 | 0 | 0 | 12495.05 | 0 | 0 | 0 | 0
2022122723 | 3 | 0.6003 | 48024 | 0 | 0 | 0.63582 | 22253.7 | 0 | 0 | 40000 | 0 | 8024 | 14229.7 | 0 | 0 | 14229.7 | 0 | 0 | 0 | 0
2022122724 | 3 | 0.58212 | 46569.6 | 0 | 0 | 0.65574 | 22950.9 | 0 | 0 | 40000 | 0 | 6569.6 | 16381.3 | 0 | 0 | 16381.3 | 0 | 0 | 0 | 0
2022122801 | 4 | 0.56754 | 45403.2 | 0 | 0 | 0.67087 | 23480.45 | 0 | 0 | 40000 | 0 | 5403.2 | 18077.25 | 0 | 0 | 18077.25 | 0 | 0 | 0 | 0
2022122802 | 4 | 0.56208 | 44966.4 | 0 | 0 | 0.68269 | 23894.15 | 0 | 0 | 40000 | 0 | 4966.4 | 18927.75 | 0 | 0 | 18927.75 | 0 | 0 | 0 | 0
2022122803 | 4 | 0.56028 | 44822.4 | 0 | 0 | 0.68631 | 24020.85 | 0 | 0 | 40000 | 0 | 4822.4 | 19198.45 | 0 | 0 | 19198.45 | 0 | 0 | 0 | 0
2022122804 | 4 | 0.56414 | 45131.2 | 0 | 0 | 0.68569 | 23999.15 | 0 | 0 | 40000 | 0 | 5131.2 | 18867.95 | 0 | 0 | 18867.95 | 0 | 0 | 0 | 0
2022122805 | 4 | 0.57498 | 45998.4 | 0 | 0 | 0.68688 | 24040.8 | 0 | 0 | 40000 | 0 | 5998.4 | 18042.4 | 0 | 0 | 18042.4 | 0 | 0 | 0 | 0
2022122806 | 4 | 0.59636 | 47708.8 | 0 | 0 | 0.68775 | 24071.25 | 0 | 0 | 40000 | 0 | 7708.8 | 16362.45 | 0 | 0 | 16362.45 | 0 | 0 | 0 | 0
2022122807 | 4 | 0.62158 | 49726.4 | 0 | 0 | 0.68861 | 24101.35 | 0 | 0 | 40000 | 0 | 9726.4 | 14374.95 | 0 | 0 | 14374.95 | 0 | 0 | 0 | 0
2022122808 | 4 | 0.63483 | 50786.4 | 0 | 0 | 0.69028 | 24159.8 | 0.00829 | 116.06 | 40000 | 0 | 10786.4 | 13373.4 | 0 | 116.06 | 13489.46 | 0 | 0 | 0 | 0
2022122809 | 4 | 0.62605 | 50084 | 0 | 0 | 0.67463 | 23612.05 | 0.14285 | 1999.9 | 40000 | 0 | 10084 | 13528.05 | 0 | 1999.9 | 15527.95 | 0 | 0 | 0 | 0
2022122810 | 4 | 0.59755 | 47804 | 0 | 0 | 0.64161 | 22456.35 | 0.27183 | 3805.62 | 40000 | 0 | 7804 | 14652.35 | 0 | 3805.62 | 18457.97 | 0 | 0 | 0 | 0
2022122811 | 4 | 0.56718 | 45374.4 | 0 | 0 | 0.64042 | 22414.7 | 0.27621 | 3866.94 | 40000 | 0 | 5374.4 | 17040.3 | 0 | 3866.94 | 20907.24 | 0 | 0 | 0 | 0
2022122812 | 4 | 0.54244 | 43395.2 | 0 | 0 | 0.64063 | 22422.05 | 0.2111 | 2955.4 | 40000 | 0 | 3395.2 | 19026.85 | 0 | 2955.4 | 21982.25 | 0 | 0 | 0 | 0
2022122813 | 4 | 0.52387 | 41909.6 | 0 | 0 | 0.61829 | 21640.15 | 0.2074 | 2903.6 | 40000 | 0 | 1909.6 | 19730.55 | 0 | 2903.6 | 22634.15 | 0 | 0 | 0 | 0
2022122814 | 4 | 0.51403 | 41122.4 | 0 | 0 | 0.59896 | 20963.6 | 0.22198 | 3107.72 | 40000 | 0 | 1122.4 | 19841.2 | 0 | 3107.72 | 22948.92 | 0 | 0 | 0 | 0
2022122815 | 4 | 0.50873 | 40698.4 | 0 | 0 | 0.57629 | 20170.15 | 0.24166 | 3383.24 | 40000 | 0 | 698.4 | 19471.75 | 0 | 3383.24 | 22854.99 | 0 | 0 | 0 | 0
2022122816 | 4 | 0.50772 | 40617.6 | 0 | 0 | 0.56081 | 19628.35 | 0.25987 | 3638.18 | 40000 | 0 | 617.6 | 19010.75 | 0 | 3638.18 | 22648.93 | 0 | 0 | 0 | 0
2022122817 | 4 | 0.51109 | 40887.2 | 0 | 0 | 0.56062 | 19621.7 | 0.1438 | 2013.2 | 40000 | 0 | 887.2 | 18734.5 | 0 | 2013.2 | 20747.7 | 0 | 0 | 0 | 0
2022122818 | 4 | 0.52369 | 41895.2 | 0 | 0 | 0.58227 | 20379.45 | 0.01275 | 178.5 | 40000 | 0 | 1895.2 | 18484.25 | 0 | 178.5 | 18662.75 | 0 | 0 | 0 | 0
2022122819 | 4 | 0.5415 | 43320 | 0 | 0 | 0.65646 | 22976.1 | 0 | 0 | 40000 | 0 | 3320 | 19656.1 | 0 | 0 | 19656.1 | 0 | 0 | 0 | 0
2022122820 | 4 | 0.53988 | 43190.4 | 0 | 0 | 0.69236 | 24232.6 | 4e-05 | 0.56 | 40000 | 0 | 3190.4 | 21042.2 | 0 | 0.56 | 21042.76 | 0 | 0 | 0 | 0
2022122821 | 4 | 0.53231 | 42584.8 | 0 | 0 | 0.68431 | 23950.85 | 4e-05 | 0.56 | 40000 | 0 | 2584.8 | 21366.05 | 0 | 0.56 | 21366.61 | 0 | 0 | 0 | 0
2022122822 | 4 | 0.52165 | 41732 | 0 | 0 | 0.67583 | 23654.05 | 0 | 0 | 40000 | 0 | 1732 | 21922.05 | 0 | 0 | 21922.05 | 0 | 0 | 0 | 0
2022122823 | 4 | 0.50272 | 40217.6 | 0 | 0 | 0.64391 | 22536.85 | 0 | 0 | 40000 | 0 | 217.6 | 22319.25 | 0 | 0 | 22319.25 | 0 | 0 | 0 | 0
2022122824 | 4 | 0.4759 | 38072 | 0 | 0 | 0.5905 | 20667.5 | 0 | 0 | 38072 | 1928 | 0 | 20667.5 | 0 | 0 | 22595.5 | 0 | 0 | 0 | 0
2022122901 | 5 | 0.4539 | 36312 | 0 | 0 | 0.55886 | 19560.1 | 0 | 0 | 36312 | 3688 | 0 | 19560.1 | 0 | 0 | 23248.1 | 0 | 0 | 0 | 0
2022122902 | 5 | 0.43753 | 35002.4 | 0 | 0 | 0.52334 | 18316.9 | 0 | 0 | 35002.4 | 4997.6 | 0 | 18316.9 | 0 | 0 | 23314.5 | 0 | 0 | 0 | 0
2022122903 | 5 | 0.42545 | 34036 | 0 | 0 | 0.4967 | 17384.5 | 0 | 0 | 34036 | 5964 | 0 | 17384.5 | 0 | 0 | 23348.5 | 0 | 0 | 0 | 0
2022122904 | 5 | 0.42077 | 33661.6 | 0 | 0 | 0.47907 | 16767.45 | 4e-05 | 0.56 | 33661.6 | 6338.4 | 0 | 16767.45 | 0 | 0.56 | 23106.41 | 0 | 0 | 0 | 0
2022122905 | 5 | 0.42311 | 33848.8 | 0 | 0 | 0.47598 | 16659.3 | 4e-05 | 0.56 | 33848.8 | 6151.2 | 0 | 16659.3 | 0 | 0.56 | 22811.06 | 0 | 0 | 0 | 0
2022122906 | 5 | 0.4379 | 35032 | 0 | 0 | 0.47402 | 16590.7 | 4e-05 | 0.56 | 35032 | 4968 | 0 | 16590.7 | 0 | 0.56 | 21559.26 | 0 | 0 | 0 | 0
2022122907 | 5 | 0.45898 | 36718.4 | 0 | 0 | 0.45623 | 15968.05 | 4e-05 | 0.56 | 36718.4 | 3281.6 | 0 | 15968.05 | 0 | 0.56 | 19250.21 | 0 | 0 | 0 | 0
2022122908 | 5 | 0.47657 | 38125.6 | 0 | 0 | 0.46778 | 16372.3 | 0.00416 | 58.24 | 38125.6 | 1874.4 | 0 | 16372.3 | 0 | 58.24 | 18304.94 | 0 | 0 | 0 | 0
2022122909 | 5 | 0.48973 | 39178.4 | 0 | 0 | 0.45517 | 15930.95 | 0.08377 | 1172.78 | 39178.4 | 821.6 | 0 | 15930.95 | 0 | 1172.78 | 17925.33 | 0 | 0 | 0 | 0
2022122910 | 5 | 0.50514 | 40411.2 | 0 | 0 | 0.4126 | 14441 | 0.22403 | 3136.42 | 40000 | 0 | 411.2 | 14029.8 | 0 | 3136.42 | 17166.22 | 0 | 0 | 0 | 0
2022122911 | 5 | 0.50906 | 40724.8 | 0 | 0 | 0.35633 | 12471.55 | 0.28226 | 3951.64 | 40000 | 0 | 724.8 | 11746.75 | 0 | 3951.64 | 15698.39 | 0 | 0 | 0 | 0
2022122912 | 5 | 0.5136 | 41088 | 0 | 0 | 0.3436 | 12026 | 0.33301 | 4662.14 | 40000 | 0 | 1088 | 10938 | 0 | 4662.14 | 15600.14 | 0 | 0 | 0 | 0
2022122913 | 5 | 0.51599 | 41279.2 | 0 | 0 | 0.32494 | 11372.9 | 0.32707 | 4578.98 | 40000 | 0 | 1279.2 | 10093.7 | 0 | 4578.98 | 14672.68 | 0 | 0 | 0 | 0
2022122914 | 5 | 0.51798 | 41438.4 | 0 | 0 | 0.29158 | 10205.3 | 0.29256 | 4095.84 | 40000 | 0 | 1438.4 | 8766.9 | 0 | 4095.84 | 12862.74 | 0 | 0 | 0 | 0
2022122915 | 5 | 0.51642 | 41313.6 | 0 | 0 | 0.2544 | 8904 | 0.26865 | 3761.1 | 40000 | 0 | 1313.6 | 7590.4 | 0 | 3761.1 | 11351.5 | 0 | 0 | 0 | 0
2022122916 | 5 | 0.51258 | 41006.4 | 0 | 0 | 0.22711 | 7948.85 | 0.18409 | 2577.26 | 40000 | 0 | 1006.4 | 6942.45 | 0 | 2577.26 | 9519.71 | 0 | 0 | 0 | 0
2022122917 | 5 | 0.51142 | 40913.6 | 0 | 0 | 0.20087 | 7030.45 | 0.09485 | 1327.9 | 40000 | 0 | 913.6 | 6116.85 | 0 | 1327.9 | 7444.75 | 0 | 0 | 0 | 0
2022122918 | 5 | 0.525 | 42000 | 0 | 0 | 0.18108 | 6337.8 | 0.02289 | 320.46 | 40000 | 0 | 2000 | 4337.8 | 0 | 320.46 | 4658.26 | 0 | 0 | 0 | 0
2022122919 | 5 | 0.53604 | 42883.2 | 0 | 0 | 0.16612 | 5814.2 | 0 | 0 | 40000 | 0 | 2883.2 | 2931 | 0 | 0 | 2931 | 0 | 0 | 0 | 0
2022122920 | 5 | 0.52819 | 42255.2 | 0 | 0 | 0.15696 | 5493.6 | 0 | 0 | 40000 | 0 | 2255.2 | 3238.4 | 0 | 0 | 3238.4 | 0 | 0 | 0 | 0
2022122921 | 5 | 0.51856 | 41484.8 | 0 | 0 | 0.17555 | 6144.25 | 0 | 0 | 40000 | 0 | 1484.8 | 4659.45 | 0 | 0 | 4659.45 | 0 | 0 | 0 | 0
2022122922 | 5 | 0.50618 | 40494.4 | 0 | 0 | 0.19383 | 6784.05 | 0 | 0 | 40000 | 0 | 494.4 | 6289.65 | 0 | 0 | 6289.65 | 0 | 0 | 0 | 0
2022122923 | 5 | 0.487 | 38960 | 0 | 0 | 0.17176 | 6011.6 | 0 | 0 | 38960 | 1040 | 0 | 6011.6 | 0 | 0 | 7051.6 | 0 | 0 | 0 | 0
2022122924 | 5 | 0.46456 | 37164.8 | 0 | 0 | 0.14892 | 5212.2 | 0 | 0 | 37164.8 | 2835.2 | 0 | 5212.2 | 0 | 0 | 8047.4 | 0 | 0 | 0 | 0
2022123001 | 6 | 0.44471 | 35576.8 | 0 | 0 | 0.11791 | 4126.85 | 0 | 0 | 35576.8 | 4423.2 | 0 | 4126.85 | 0 | 0 | 8550.05 | 0 | 0 | 0 | 0
2022123002 | 6 | 0.43122 | 34497.6 | 0 | 0 | 0.0997 | 3489.5 | 0 | 0 | 34497.6 | 5502.4 | 0 | 3489.5 | 0 | 0 | 8991.9 | 0 | 0 | 0 | 0
2022123003 | 6 | 0.42498 | 33998.4 | 0 | 0 | 0.08715 | 3050.25 | 0 | 0 | 33998.4 | 6001.6 | 0 | 3050.25 | 0 | 0 | 9051.85 | 0 | 0 | 0 | 0
2022123004 | 6 | 0.42517 | 34013.6 | 0 | 0 | 0.06878 | 2407.3 | 0 | 0 | 34013.6 | 5986.4 | 0 | 2407.3 | 0 | 0 | 8393.7 | 0 | 0 | 0 | 0
2022123005 | 6 | 0.43065 | 34452 | 0 | 0 | 0.0792 | 2772 | 0 | 0 | 34452 | 5548 | 0 | 2772 | 0 | 0 | 8320 | 0 | 0 | 0 | 0
2022123006 | 6 | 0.44647 | 35717.6 | 0 | 0 | 0.10314 | 3609.9 | 0 | 0 | 35717.6 | 4282.4 | 0 | 3609.9 | 0 | 0 | 7892.3 | 0 | 0 | 0 | 0
2022123007 | 6 | 0.47115 | 37692 | 0 | 0 | 0.12335 | 4317.25 | 0 | 0 | 37692 | 2308 | 0 | 4317.25 | 0 | 0 | 6625.25 | 0 | 0 | 0 | 0
2022123008 | 6 | 0.49302 | 39441.6 | 0 | 0 | 0.12489 | 4371.15 | 0.00205 | 28.7 | 39441.6 | 558.4 | 0 | 4371.15 | 0 | 28.7 | 4958.25 | 0 | 0 | 0 | 0
2022123009 | 6 | 0.50692 | 40553.6 | 0 | 0 | 0.11155 | 3904.25 | 0.06046 | 846.44 | 40000 | 0 | 553.6 | 3350.65 | 0 | 846.44 | 4197.09 | 0 | 0 | 0 | 0
2022123010 | 6 | 0.51583 | 41266.4 | 0 | 0 | 0.08416 | 2945.6 | 0.14116 | 1976.24 | 40000 | 0 | 1266.4 | 1679.2 | 0 | 1976.24 | 3655.44 | 0 | 0 | 0 | 0
2022123011 | 6 | 0.51471 | 41176.8 | 0 | 0 | 0.06793 | 2377.55 | 0.22102 | 3094.28 | 40000 | 0 | 1176.8 | 1200.75 | 0 | 3094.28 | 4295.03 | 0 | 0 | 0 | 0
2022123012 | 6 | 0.50983 | 40786.4 | 0 | 0 | 0.07165 | 2507.75 | 0.23554 | 3297.56 | 40000 | 0 | 786.4 | 1721.35 | 0 | 3297.56 | 5018.91 | 0 | 0 | 0 | 0
2022123013 | 6 | 0.5088 | 40704 | 0 | 0 | 0.0942 | 3297 | 0.27118 | 3796.52 | 40000 | 0 | 704 | 2593 | 0 | 3796.52 | 6389.52 | 0 | 0 | 0 | 0
2022123014 | 6 | 0.5056 | 40448 | 0 | 0 | 0.13373 | 4680.55 | 0.24954 | 3493.56 | 40000 | 0 | 448 | 4232.55 | 0 | 3493.56 | 7726.11 | 0 | 0 | 0 | 0
2022123015 | 6 | 0.49922 | 39937.6 | 0 | 0 | 0.15173 | 5310.55 | 0.27515 | 3852.1 | 39937.6 | 62.4 | 0 | 5310.55 | 0 | 3852.1 | 9225.05 | 0 | 0 | 0 | 0
2022123016 | 6 | 0.50216 | 40172.8 | 0 | 0 | 0.15546 | 5441.1 | 0.28443 | 3982.02 | 40000 | 0 | 172.8 | 5268.3 | 0 | 3982.02 | 9250.32 | 0 | 0 | 0 | 0
2022123017 | 6 | 0.50286 | 40228.8 | 0 | 0 | 0.16068 | 5623.8 | 0.21777 | 3048.78 | 40000 | 0 | 228.8 | 5395 | 0 | 3048.78 | 8443.78 | 0 | 0 | 0 | 0
2022123018 | 6 | 0.51408 | 41126.4 | 0 | 0 | 0.17923 | 6273.05 | 0.03258 | 456.12 | 40000 | 0 | 1126.4 | 5146.65 | 0 | 456.12 | 5602.77 | 0 | 0 | 0 | 0
2022123019 | 6 | 0.53086 | 42468.8 | 0 | 0 | 0.23595 | 8258.25 | 0 | 0 | 40000 | 0 | 2468.8 | 5789.45 | 0 | 0 | 5789.45 | 0 | 0 | 0 | 0
2022123020 | 6 | 0.52872 | 42297.6 | 0 | 0 | 0.27178 | 9512.3 | 0 | 0 | 40000 | 0 | 2297.6 | 7214.7 | 0 | 0 | 7214.7 | 0 | 0 | 0 | 0
2022123021 | 6 | 0.52187 | 41749.6 | 0 | 0 | 0.29488 | 10320.8 | 0 | 0 | 40000 | 0 | 1749.6 | 8571.2 | 0 | 0 | 8571.2 | 0 | 0 | 0 | 0
2022123022 | 6 | 0.51515 | 41212 | 0 | 0 | 0.32816 | 11485.6 | 0 | 0 | 40000 | 0 | 1212 | 10273.6 | 0 | 0 | 10273.6 | 0 | 0 | 0 | 0
2022123023 | 6 | 0.50102 | 40081.6 | 0 | 0 | 0.37562 | 13146.7 | 0 | 0 | 40000 | 0 | 81.6 | 13065.1 | 0 | 0 | 13065.1 | 0 | 0 | 0 | 0
2022123024 | 6 | 0.48502 | 38801.6 | 0 | 0 | 0.41847 | 14646.45 | 0 | 0 | 38801.6 | 1198.4 | 0 | 14646.45 | 0 | 0 | 15844.85 | 0 | 0 | 0 | 0
2022123101 | 7 | 0.46837 | 37469.6 | 0 | 0 | 0.43556 | 15244.6 | 0 | 0 | 37469.6 | 2530.4 | 0 | 15244.6 | 0 | 0 | 17775 | 0 | 0 | 0 | 0
2022123102 | 7 | 0.45691 | 36552.8 | 0 | 0 | 0.43971 | 15389.85 | 0 | 0 | 36552.8 | 3447.2 | 0 | 15389.85 | 0 | 0 | 18837.05 | 0 | 0 | 0 | 0
2022123103 | 7 | 0.45079 | 36063.2 | 0 | 0 | 0.44593 | 15607.55 | 0 | 0 | 36063.2 | 3936.8 | 0 | 15607.55 | 0 | 0 | 19544.35 | 0 | 0 | 0 | 0
2022123104 | 7 | 0.44952 | 35961.6 | 0 | 0 | 0.45638 | 15973.3 | 0 | 0 | 35961.6 | 4038.4 | 0 | 15973.3 | 0 | 0 | 20011.7 | 0 | 0 | 0 | 0
2022123105 | 7 | 0.45592 | 36473.6 | 0 | 0 | 0.47974 | 16790.9 | 0 | 0 | 36473.6 | 3526.4 | 0 | 16790.9 | 0 | 0 | 20317.3 | 0 | 0 | 0 | 0
2022123106 | 7 | 0.46622 | 37297.6 | 0 | 0 | 0.50384 | 17634.4 | 0 | 0 | 37297.6 | 2702.4 | 0 | 17634.4 | 0 | 0 | 20336.8 | 0 | 0 | 0 | 0
2022123107 | 7 | 0.4828 | 38624 | 0 | 0 | 0.52958 | 18535.3 | 0 | 0 | 38624 | 1376 | 0 | 18535.3 | 0 | 0 | 19911.3 | 0 | 0 | 0 | 0
2022123108 | 7 | 0.49744 | 39795.2 | 0 | 0 | 0.56093 | 19632.55 | 0.00418 | 58.52 | 39795.2 | 204.8 | 0 | 19632.55 | 0 | 58.52 | 19895.87 | 0 | 0 | 0 | 0
2022123109 | 7 | 0.50467 | 40373.6 | 0 | 0 | 0.5546 | 19411 | 0.11751 | 1645.14 | 40000 | 0 | 373.6 | 19037.4 | 0 | 1645.14 | 20682.54 | 0 | 0 | 0 | 0
2022123110 | 7 | 0.50418 | 40334.4 | 0 | 0 | 0.50764 | 17767.4 | 0.27875 | 3902.5 | 40000 | 0 | 334.4 | 17433 | 0 | 3902.5 | 21335.5 | 0 | 0 | 0 | 0
2022123111 | 7 | 0.49987 | 39989.6 | 0 | 0 | 0.48376 | 16931.6 | 0.33331 | 4666.34 | 39989.6 | 10.4 | 0 | 16931.6 | 0 | 4666.34 | 21608.34 | 0 | 0 | 0 | 0
2022123112 | 7 | 0.49543 | 39634.4 | 0 | 0 | 0.50258 | 17590.3 | 0.27203 | 3808.42 | 39634.4 | 365.6 | 0 | 17590.3 | 0 | 3808.42 | 21764.32 | 0 | 0 | 0 | 0
2022123113 | 7 | 0.49251 | 39400.8 | 0 | 0 | 0.51625 | 18068.75 | 0.2265 | 3171 | 39400.8 | 599.2 | 0 | 18068.75 | 0 | 3171 | 21838.95 | 0 | 0 | 0 | 0
2022123114 | 7 | 0.49348 | 39478.4 | 0 | 0 | 0.51415 | 17995.25 | 0.24063 | 3368.82 | 39478.4 | 521.6 | 0 | 17995.25 | 0 | 3368.82 | 21885.67 | 0 | 0 | 0 | 0
2022123115 | 7 | 0.49615 | 39692 | 0 | 0 | 0.48941 | 17129.35 | 0.33032 | 4624.48 | 39692 | 308 | 0 | 17129.35 | 0 | 4624.48 | 22061.83 | 0 | 0 | 0 | 0
2022123116 | 7 | 0.50041 | 40032.8 | 0 | 0 | 0.47015 | 16455.25 | 0.39045 | 5466.3 | 40000 | 0 | 32.8 | 16422.45 | 0 | 5466.3 | 21888.75 | 0 | 0 | 0 | 0
2022123117 | 7 | 0.50569 | 40455.2 | 0 | 0 | 0.44868 | 15703.8 | 0.25989 | 3638.46 | 40000 | 0 | 455.2 | 15248.6 | 0 | 3638.46 | 18887.06 | 0 | 0 | 0 | 0
2022123118 | 7 | 0.51101 | 40880.8 | 0 | 0 | 0.40532 | 14186.2 | 0.03042 | 425.88 | 40000 | 0 | 880.8 | 13305.4 | 0 | 425.88 | 13731.28 | 0 | 0 | 0 | 0
2022123119 | 7 | 0.52427 | 41941.6 | 0 | 0 | 0.4822 | 16877 | 0 | 0 | 40000 | 0 | 1941.6 | 14935.4 | 0 | 0 | 14935.4 | 0 | 0 | 0 | 0
2022123120 | 7 | 0.51503 | 41202.4 | 0 | 0 | 0.56302 | 19705.7 | 0 | 0 | 40000 | 0 | 1202.4 | 18503.3 | 0 | 0 | 18503.3 | 0 | 0 | 0 | 0
2022123121 | 7 | 0.49985 | 39988 | 0 | 0 | 0.58325 | 20413.75 | 0 | 0 | 39988 | 12 | 0 | 20413.75 | 0 | 0 | 20425.75 | 0 | 0 | 0 | 0
2022123122 | 7 | 0.4872 | 38976 | 0 | 0 | 0.60108 | 21037.8 | 0 | 0 | 38976 | 1024 | 0 | 21037.8 | 0 | 0 | 22061.8 | 0 | 0 | 0 | 0
2022123123 | 7 | 0.47265 | 37812 | 0 | 0 | 0.60861 | 21301.35 | 0 | 0 | 37812 | 2188 | 0 | 21301.35 | 0 | 0 | 23489.35 | 0 | 0 | 0 | 0
2022123124 | 7 | 0.45911 | 36728.8 | 0 | 0 | 0.59735 | 20907.25 | 0 | 0 | 36728.8 | 3271.2 | 0 | 20907.25 | 0 | 0 | 24178.45 | 0 | 0 | 0 | 0
Note on W4: ERCOT 2022 hourly demand wind and solar. This file is used to create all the variable resources input data for this spreadsheet.
Note on C17: Base loaded nuclear net maximum power output in MW, i.e. the total nameplate MWs.
Note on D18: New annual peak demand forecast.
Note on F18: Installed nameplate MW generation capacity of either offshore wind or hydro generation capacity.
Note on H18: Installed nameplate MW generation capacity of onshore wind.
Note on J18: Installed nameplate MW generation capacity of solar.
Note on A19: This integer format of year month day hour allows for easy sorting of the date time stamp in text editors.
Note on B19: D is the day of the week Sunday is day 1
Note on C19: The historical test year 2022 hourly loads profile is in per unit with the annual peak having 1 per unit. See reference 1.
Note on D19: The per unit loads to the left are multiplied times the annual peak forecast for this simulation which is simply scaling up the historical data to the new load forecast.
Note on E19: OSW is off shore wind. It could be relabled Hydro. In either case this column is the per unit profile of historcal data for the test year of 2022. Its important the same test year be used for all historical weather and load data.
Note on F19: The per unit OSW values to the left are multiplied times the installed nameplate OSW capacity to produce hourly MWs. Its important this column's values are always less than the hourly load MWs because this column is assumed to be 100% dispatched.
Note on G19: On shore wind per unit hourly profile for the historical 2022 year from actual data posted by ERCOT. See Reference 1.
Note on H19: The per unit on shore wind values to the left are multiplied times the on shore wind capacity.
Note on I19: Solar per unit hourly profile for the historical 2022 year from actual data posted by ERCOT. See Reference 1.
Note on J19: The per unit solar values to the left are multiplied times the solar MW capacity.
Note on L19: If (Demand - OSW > Nucl Pmax, then Nucl Pmax, otherwise Demand - OSW).
Note on M19: Unused Nuclear MWHs
Note on N19: If (Demand - OSW - Nucl > Wind, then Wind, otherwise Demand - OSW - Nuclear).
Note on O19: Unused Wind MWHs
Note on P19: If (Demand - OSW - Nucl - Wind> Solar, then Solar, otherwise Demand - OSW - Nucl - Wind).
Note on Q19: Unused Solar MWHs
Note on R19: Sum of Unused MWHs
Note on S19: Demand - OSW - Nucl - Wind - Solar, i.e. the remaining unserved load.
Note on T19: Battery Storage in MWh. See Reference 3 for details.
Note on U19: IF (Battery MWh out - Shunt Loss is > 0, then use this formula, otherwise 0).
Note on V19: Remaining unserved load of Demand - OSW - Nuclear - Wind - Solar - Battery, is served by GTs.
Note on AA52: Battery storage is shared between Nuclear, Wind, and Solar in proportion to their excess MWHs compared to the total excess MWHs.