## 2021
PJM 64 GW base loaded nuclear 30 GW 45 hour thermal nuclear 12.5 GW on shore wind, 80 GW solar. Energy cost is 10.5 cents/kWh.
[19 empty] | Input | Calculated | Yellow per unit (pu) header means the column is input data.
References:
[18 empty] | 1 | https://dataminer2.pjm.com/feed/wind_gen/definition | [5 empty] | Variable Data
[18 empty] | 2 | https://www.futureofenergyinitiative.org/Pubs/46_CostInputsForToyModels.pdf
[18 empty] | 3 | https://egpreston.com/ExcelStorage.pdf |  |  |  | has more info on programming storage.
If storage drops down to the zero level gas generation will be automatically added.
[18 empty] | 4 | https://egpreston.com/ANS2022FallLongDurationCRUSHFinalDraft.pdf
[19 empty] | Zero fossil fuels are achieved when the MW Gas goes to zero. | [5 empty] | MWHt ~= 3*MWHe
OSW is Off Shore Wind. The OSW column could be used for hydro instead of wind.
The OSW MWs must be less than demand every hour since OSW is 100% dispatched.
If you have excess wind put it in the wind column where excess is treated correctly.
[19 empty] | System Energy Cost= |  | 10.4557 | cent/kWh | 0 | MW Gas
|  | Hourly Demand and Variable Resources Input | [7 empty] | Hourly Dispatching of All Resources and Thermal Storage | [8 empty] | Costs and Performance of Individual Sources
Base Nucl MW = |  | 64000 |  | Pmax is the installed nameplate MW of each resource. | [9 empty] | 30000 | MW Nucl hrs: | 45
|  | PeakMW= | 150000 | OSWPmx= | 0 | WinPmx= | 12500 | SolPmax= | 80000 | Nuclear | Wind | Solar | Peaking | Ramp | Therm MWh | Thermal | Fossil |  | Hourly Load Stats
YYYYMMDDHH | D | load pu | loadMW | OSW pu | OSW MW | wind pu | windMW | solar pu | solarMW | MW | MW | MW | MW | MW/hr | 1350000 | MW | MW |  | 150000 | MW Peak | 90.0859 | GW Avg | 15 | %Reserve
2021010101 | 6 | 0.55013 | 82519.5 | 0.16964 | 0 | 0.40403 | 5050.375 | 0 | 0 | 64000 | 5050.375 | 0 | 13469.125 | 0 | 1350000 | 13469.125 | 0 |  | 59170.5 | MW Min | 789152.6295 | GWh | 60.0573 | %CF
2021010102 | 6 | 0.53778 | 80667 | 0.20206 | 0 | 0.40762 | 5095.25 | 0 | 0 | 64000 | 5095.25 | 0 | 11571.75 | -1897.375 | 1350000 | 11571.75 | 0
2021010103 | 6 | 0.53062 | 79593 | 0.25204 | 0 | 0.35653 | 4456.625 | 0 | 0 | 64000 | 4456.625 | 0 | 11136.375 | -435.375 | 1350000 | 11136.375 | 0 |  | Nuclear Thermal Storage |  |  | CAPEX B$
2021010104 | 6 | 0.52809 | 79213.5 | 0.35618 | 0 | 0.31079 | 3884.875 | 0 | 0 | 64000 | 3884.875 | 0 | 11328.625 | 192.25 | 1350000 | 11328.625 | 0 |  | power | $/kW nucl | 6518 | 195.54 | 1350 | GWh | 0.06 | % loss/day
2021010105 | 6 | 0.53194 | 79791 | 0.4437 | 0 | 0.32456 | 4057 | 0 | 0 | 64000 | 4057 | 0 | 11734 | 405.375 | 1350000 | 11734 | 0 |  | power | $/kW gen | 922 | 27.66 | 78.1549 | GW | 33.75 | MWh/hr
2021010106 | 6 | 0.54356 | 81534 | 0.56338 | 0 | 0.34798 | 4349.75 | 0 | 0 | 64000 | 4349.75 | 0 | 13184.25 | 1450.25 | 1350000 | 13184.25 | 0 |  | energy | $/kWh | 43 | 58.05 | 45 | Hrs | 0.85 | efficiency
2021010107 | 6 | 0.5585 | 83775 | 0.65787 | 0 | 0.31093 | 3886.625 | 0 | 0 | 64000 | 3886.625 | 0 | 15888.375 | 2704.125 | 1350000 | 15888.375 | 0
2021010108 | 6 | 0.57023 | 85534.5 | 0.72162 | 0 | 0.25329 | 3166.125 | 0.01699 | 1359.2 | 64000 | 3166.125 | 1359.2 | 17009.175 | 1120.8 | 1350000 | 17009.175 | 0 |  | Annual Costs |  |  |  | per year | annual | uplifted
2021010109 | 6 | 0.5783 | 86745 | 0.79296 | 0 | 0.27197 | 3399.625 | 0.10394 | 8315.2 | 64000 | 3399.625 | 8315.2 | 11030.175 | -5979 | 1350000 | 11030.175 | 0 |  | Off Shore Wind |  |  |  | capt cost | cost M$ | cent/kWh
2021010110 | 6 | 0.59015 | 88522.5 | 0.83313 | 0 | 0.32617 | 4077.125 | 0.17257 | 13805.6 | 64000 | 4077.125 | 13805.6 | 6639.775 | -4390.4 | 1350000 | 6639.775 | 0 |  | 0 | MW OSW | 4730 | $/kW | 0.089 | 0 | 0
2021010111 | 6 | 0.60634 | 90951 | 0.8545 | 0 | 0.28274 | 3534.25 | 0.22158 | 17726.4 | 64000 | 3534.25 | 17726.4 | 5690.35 | -949.425 | 1350000 | 5690.35 | 0 |  |  | OSWO&M | 113 | $/kW/yr |  | 0 | 0
2021010112 | 6 | 0.61894 | 92841 | 0.76972 | 0 | 0.21985 | 2748.125 | 0.25216 | 20172.8 | 64000 | 2748.125 | 20172.8 | 5920.075 | 229.725 | 1350000 | 5920.075 | 0 |  | Base Loaded Nuclear
2021010113 | 6 | 0.62611 | 93916.5 | 0.65174 | 0 | 0.20825 | 2603.125 | 0.18459 | 14767.2 | 64000 | 2603.125 | 14767.2 | 12546.175 | 6626.1 | 1350000 | 12546.175 | 0 |  | 64000 | MW nucl | 7440 | $/kW | 0.064 | 30474.24 | 3.8616
2021010114 | 6 | 0.62544 | 93816 | 0.5741 | 0 | 0.16515 | 2064.375 | 0.11486 | 9188.8 | 64000 | 2064.375 | 9188.8 | 18562.825 | 6016.65 | 1350000 | 18562.825 | 0 |  |  | Nucl O&M | 146 | $/kW/yr |  | 9344 | 1.1841
2021010115 | 6 | 0.62281 | 93421.5 | 0.47594 | 0 | 0.1324 | 1655 | 0.07441 | 5952.8 | 64000 | 1655 | 5952.8 | 21813.7 | 3250.875 | 1350000 | 21813.7 | 0 |  |  | Vari O&M | 10 | $/MWh/yr |  | 5604.1456 | 0.71015
2021010116 | 6 | 0.62412 | 93618 | 0.32972 | 0 | 0.10733 | 1341.625 | 0.03935 | 3148 | 64000 | 1341.625 | 3148 | 25128.375 | 3314.675 | 1350000 | 25128.375 | 0 |  | On Shore Wind
2021010117 | 6 | 0.63667 | 95500.5 | 0.22782 | 0 | 0.08409 | 1051.125 | 0.00322 | 257.6 | 64000 | 1051.125 | 257.6 | 30191.775 | 5063.4 | 1345274.475 | 30191.775 | 0 |  | 12500 | MW wind | 1460 | $/kW | 0.089 | 1624.25 | 0.20582
2021010118 | 6 | 0.65514 | 98271 | 0.10705 | 0 | 0.08336 | 1042 | 0 | 0 | 64000 | 1042 | 0 | 33229 | 3037.225 | 1337511.725 | 33229 | 0 |  |  | WndO&M | 43 | $/kW/yr |  | 537.5 | 0.068111
2021010119 | 6 | 0.65058 | 97587 | 0.09169 | 0 | 0.09942 | 1242.75 | 0 | 0 | 64000 | 1242.75 | 0 | 32344.25 | -884.75 | 1330633.725 | 32344.25 | 0 |  | Solar
2021010120 | 6 | 0.63776 | 95664 | 0.08299 | 0 | 0.0994 | 1242.5 | 0 | 0 | 64000 | 1242.5 | 0 | 30421.5 | -1922.75 | 1325678.475 | 30421.5 | 0 |  | 80000 | MW solar | 1330 | $/kW | 0.074 | 7873.6 | 0.99773
2021010121 | 6 | 0.62299 | 93448.5 | 0.07998 | 0 | 0.10069 | 1258.625 | 0 | 0 | 64000 | 1258.625 | 0 | 28189.875 | -2231.625 | 1322954.85 | 28189.875 | 0 |  |  | solarO&M | 23 | $/kW/yr |  | 1840 | 0.23316
2021010122 | 6 | 0.60297 | 90445.5 | 0.10485 | 0 | 0.12774 | 1596.75 | 0 | 0 | 64000 | 1596.75 | 0 | 24848.75 | -3341.125 | 1323572.35 | 24848.75 | 0 |  | Nuclear Thermal Storage
2021010123 | 6 | 0.5802 | 87030 | 0.11969 | 0 | 0.14396 | 1799.5 | 0 | 0 | 64000 | 1799.5 | 0 | 21230.5 | -3618.25 | 1327808.1 | 21230.5 | 0 |  | 30000 | MW nucl | 6518 | $/kW | 0.064 | 12514.56 | 1.5858
2021010124 | 6 | 0.55232 | 82848 | 0.17976 | 0 | 0.14873 | 1859.125 | 0 | 0 | 64000 | 1859.125 | 0 | 16988.875 | -4241.625 | 1336285.475 | 16988.875 | 0 |  | 78154.925 | MW genr | 922 | $/kW |  | 4611.7658 | 0.58439
2021010201 | 7 | 0.52932 | 79398 | 0.26677 | 0 | 0.13311 | 1663.875 | 0 | 0 | 64000 | 1663.875 | 0 | 13734.125 | -3254.75 | 1348017.6 | 13734.125 | 0 |  | 1350 | GWh ther | 43 | $/kWh | 0.074 | 4295.7 | 0.54434
2021010202 | 7 | 0.5124 | 76860 | 0.42608 | 0 | 0.10477 | 1309.625 | 0 | 0 | 64000 | 1309.625 | 0 | 11550.375 | -2183.75 | 1350000 | 11550.375 | 0 |  |  | Thm O&M | 21 | $/kW/yr |  | 630 | 0.079832
2021010203 | 7 | 0.50237 | 75355.5 | 0.57274 | 0 | 0.09329 | 1166.125 | 0 | 0 | 64000 | 1166.125 | 0 | 10189.375 | -1361 | 1350000 | 10189.375 | 0 |  |  | Vari O&M | 10 | $/MWh/yr |  | 1153.7679 | 0.1462
2021010204 | 7 | 0.49898 | 74847 | 0.65858 | 0 | 0.09221 | 1152.625 | 0 | 0 | 64000 | 1152.625 | 0 | 9694.375 | -495 | 1350000 | 9694.375 | 0 |  | Gas Peaking
2021010205 | 7 | 0.50124 | 75186 | 0.75755 | 0 | 0.09576 | 1197 | 0 | 0 | 64000 | 1197 | 0 | 9989 | 294.625 | 1350000 | 9989 | 0 |  | 0 | MW Gas | 922 | $/kW | 0.074 | 0 | 0
2021010206 | 7 | 0.51 | 76500 | 0.84939 | 0 | 0.09404 | 1175.5 | 0 | 0 | 64000 | 1175.5 | 0 | 11324.5 | 1335.5 | 1350000 | 11324.5 | 0 |  |  | Gas O&M | 21 | $/kW/yr |  | 0 | 0
2021010207 | 7 | 0.52529 | 78793.5 | 0.90707 | 0 | 0.08126 | 1015.75 | 0 | 0 | 64000 | 1015.75 | 0 | 13777.75 | 2453.25 | 1350000 | 13777.75 | 0 |  |  | Vari O&M | 39 | $/MWh/yr |  | 0 | 0
2021010208 | 7 | 0.5435 | 81525 | 0.90013 | 0 | 0.06114 | 764.25 | 0.00597 | 477.6 | 64000 | 764.25 | 477.6 | 16283.15 | 2505.4 | 1350000 | 16283.15 | 0 |  | 0 | AvgGasMW | 24 | $/MWh fuel cost |  | 0 | 0
2021010209 | 7 | 0.55495 | 83242.5 | 0.91552 | 0 | 0.03878 | 484.75 | 0.03563 | 2850.4 | 64000 | 484.75 | 2850.4 | 15907.35 | -375.8 | 1350000 | 15907.35 | 0 |  | 22500 | MW Gas Reserve Capacity |  |  |  | 2007.63 | 0.2544
2021010210 | 7 | 0.56135 | 84202.5 | 0.95666 | 0 | 0.02378 | 297.25 | 0.06711 | 5368.8 | 64000 | 297.25 | 5368.8 | 14536.45 | -1370.9 | 1350000 | 14536.45 | 0 | [5 empty] | total | 82511.1593 | 10.4557
2021010211 | 7 | 0.56296 | 84444 | 0.96953 | 0 | 0.02554 | 319.25 | 0.11542 | 9233.6 | 64000 | 319.25 | 9233.6 | 10891.15 | -3645.3 | 1350000 | 10891.15 | 0
2021010212 | 7 | 0.56078 | 84117 | 0.95168 | 0 | 0.01966 | 245.75 | 0.14426 | 11540.8 | 64000 | 245.75 | 11540.8 | 8330.45 | -2560.7 | 1350000 | 8330.45 | 0 |  |  | Annual Costs |  |  |  | annual | source
2021010213 | 7 | 0.55336 | 83004 | 0.90315 | 0 | 0.01636 | 204.5 | 0.14415 | 11532 | 64000 | 204.5 | 11532 | 7267.5 | -1062.95 | 1350000 | 7267.5 | 0 |  |  |  | max % CF | act % CF | unused% | cost M$ | cent/kWh
2021010214 | 7 | 0.54761 | 82141.5 | 0.79237 | 0 | 0.01549 | 193.625 | 0.10449 | 8359.2 | 64000 | 193.625 | 8359.2 | 9588.675 | 2321.175 | 1350000 | 9588.675 | 0 |  |  | OSW | 0 | 0 | 0 | 0 | 0
2021010215 | 7 | 0.54406 | 81609 | 0.6386 | 0 | 0.02149 | 268.625 | 0.06407 | 5125.6 | 64000 | 268.625 | 5125.6 | 12214.775 | 2626.1 | 1350000 | 12214.775 | 0 |  |  | Nuclear | 100 | 99.9598 | 0.040212 | 45422.3856 | 8.1051
2021010216 | 7 | 0.54824 | 82236 | 0.54833 | 0 | 0.03129 | 391.125 | 0.02576 | 2060.8 | 64000 | 391.125 | 2060.8 | 15784.075 | 3569.3 | 1350000 | 15784.075 | 0 |  |  | Wind | 30 | 28.6354 | 1.3646 | 2161.75 | 6.8943
2021010217 | 7 | 0.56616 | 84924 | 0.36306 | 0 | 0.03782 | 472.75 | 0.0008 | 64 | 64000 | 472.75 | 64 | 20387.25 | 4603.175 | 1350000 | 20387.25 | 0 |  |  | Solar | 17.0496 | 11.7017 | 5.3479 | 9713.6 | 11.8451
2021010218 | 7 | 0.60182 | 90273 | 0.28124 | 0 | 0.04454 | 556.75 | 0 | 0 | 64000 | 556.75 | 0 | 25716.25 | 5329 | 1349750 | 25716.25 | 0 |  |  | Th Nucl | 100 | 43.9029 | %CF Nucl | 23205.7937 | 20.1131
2021010219 | 7 | 0.61062 | 91593 | 0.17986 | 0 | 0.05145 | 643.125 | 0 | 0 | 64000 | 643.125 | 0 | 26949.875 | 1233.625 | 1348266.375 | 26949.875 | 0 |  |  | Th Genr | 100 | 16.8523 | %CF Genr
2021010220 | 7 | 0.60504 | 90756 | 0.08811 | 0 | 0.05833 | 729.125 | 0 | 0 | 64000 | 729.125 | 0 | 26026.875 | -923 | 1347705.75 | 26026.875 | 0 |  |  | Fossil | 100 | 0 | 100 | 0 | 0
2021010221 | 7 | 0.59644 | 89466 | 0.08262 | 0 | 0.08174 | 1021.75 | 0 | 0 | 64000 | 1021.75 | 0 | 24444.25 | -1582.625 | 1348727.75 | 24444.25 | 0 |  |  | Reserve |  |  |  | 2007.63 | 0.2544
2021010222 | 7 | 0.58266 | 87399 | 0.20865 | 0 | 0.10739 | 1342.375 | 0 | 0 | 64000 | 1342.375 | 0 | 22056.625 | -2387.625 | 1350000 | 22056.625 | 0 | [5 empty] | total | 82511.1593
2021010223 | 7 | 0.56386 | 84579 | 0.26092 | 0 | 0.12641 | 1580.125 | 0 | 0 | 64000 | 1580.125 | 0 | 18998.875 | -3057.75 | 1350000 | 18998.875 | 0
2021010224 | 7 | 0.54086 | 81129 | 0.33611 | 0 | 0.18782 | 2347.75 | 0 | 0 | 64000 | 2347.75 | 0 | 14781.25 | -4217.625 | 1350000 | 14781.25 | 0
2021010301 | 1 | 0.52123 | 78184.5 | 0.45458 | 0 | 0.22032 | 2754 | 0 | 0 | 64000 | 2754 | 0 | 11430.5 | -3350.75 | 1350000 | 11430.5 | 0
2021010302 | 1 | 0.50833 | 76249.5 | 0.58276 | 0 | 0.19007 | 2375.875 | 0 | 0 | 64000 | 2375.875 | 0 | 9873.625 | -1556.875 | 1350000 | 9873.625 | 0
2021010303 | 1 | 0.50114 | 75171 | 0.6899 | 0 | 0.1078 | 1347.5 | 0 | 0 | 64000 | 1347.5 | 0 | 9823.5 | -50.125 | 1350000 | 9823.5 | 0
2021010304 | 1 | 0.4988 | 74820 | 0.65543 | 0 | 0.09972 | 1246.5 | 0 | 0 | 64000 | 1246.5 | 0 | 9573.5 | -250 | 1350000 | 9573.5 | 0
2021010305 | 1 | 0.50057 | 75085.5 | 0.50492 | 0 | 0.07138 | 892.25 | 0 | 0 | 64000 | 892.25 | 0 | 10193.25 | 619.75 | 1350000 | 10193.25 | 0
2021010306 | 1 | 0.50747 | 76120.5 | 0.57746 | 0 | 0.04692 | 586.5 | 0 | 0 | 64000 | 586.5 | 0 | 11534 | 1340.75 | 1350000 | 11534 | 0
2021010307 | 1 | 0.51945 | 77917.5 | 0.69623 | 0 | 0.04866 | 608.25 | 0 | 0 | 64000 | 608.25 | 0 | 13309.25 | 1775.25 | 1350000 | 13309.25 | 0
2021010308 | 1 | 0.53639 | 80458.5 | 0.77512 | 0 | 0.05422 | 677.75 | 0.01033 | 826.4 | 64000 | 677.75 | 826.4 | 14954.35 | 1645.1 | 1350000 | 14954.35 | 0
2021010309 | 1 | 0.55255 | 82882.5 | 0.86256 | 0 | 0.0672 | 840 | 0.0599 | 4792 | 64000 | 840 | 4792 | 13250.5 | -1703.85 | 1350000 | 13250.5 | 0
2021010310 | 1 | 0.57176 | 85764 | 0.83722 | 0 | 0.08377 | 1047.125 | 0.11447 | 9157.6 | 64000 | 1047.125 | 9157.6 | 11559.275 | -1691.225 | 1350000 | 11559.275 | 0
2021010311 | 1 | 0.58604 | 87906 | 0.71596 | 0 | 0.10673 | 1334.125 | 0.15232 | 12185.6 | 64000 | 1334.125 | 12185.6 | 10386.275 | -1173 | 1350000 | 10386.275 | 0
2021010312 | 1 | 0.59606 | 89409 | 0.48682 | 0 | 0.13379 | 1672.375 | 0.18027 | 14421.6 | 64000 | 1672.375 | 14421.6 | 9315.025 | -1071.25 | 1350000 | 9315.025 | 0
2021010313 | 1 | 0.60367 | 90550.5 | 0.30695 | 0 | 0.16257 | 2032.125 | 0.19596 | 15676.8 | 64000 | 2032.125 | 15676.8 | 8841.575 | -473.45 | 1350000 | 8841.575 | 0
2021010314 | 1 | 0.60356 | 90534 | 0.29071 | 0 | 0.18786 | 2348.25 | 0.1703 | 13624 | 64000 | 2348.25 | 13624 | 10561.75 | 1720.175 | 1350000 | 10561.75 | 0
2021010315 | 1 | 0.60216 | 90324 | 0.35054 | 0 | 0.22014 | 2751.75 | 0.14708 | 11766.4 | 64000 | 2751.75 | 11766.4 | 11805.85 | 1244.1 | 1350000 | 11805.85 | 0
2021010316 | 1 | 0.60469 | 90703.5 | 0.37765 | 0 | 0.19477 | 2434.625 | 0.10065 | 8052 | 64000 | 2434.625 | 8052 | 16216.875 | 4411.025 | 1350000 | 16216.875 | 0
2021010317 | 1 | 0.62002 | 93003 | 0.3659 | 0 | 0.20345 | 2543.125 | 0.00937 | 749.6 | 64000 | 2543.125 | 749.6 | 25710.275 | 9493.4 | 1349755.975 | 25710.275 | 0
2021010318 | 1 | 0.64868 | 97302 | 0.38085 | 0 | 0.22435 | 2804.375 | 0 | 0 | 64000 | 2804.375 | 0 | 30497.625 | 4787.35 | 1344724.6 | 30497.625 | 0
2021010319 | 1 | 0.65255 | 97882.5 | 0.42448 | 0 | 0.28692 | 3586.5 | 0 | 0 | 64000 | 3586.5 | 0 | 30296 | -201.625 | 1339894.85 | 30296 | 0
2021010320 | 1 | 0.64396 | 96594 | 0.38701 | 0 | 0.31531 | 3941.375 | 0 | 0 | 64000 | 3941.375 | 0 | 28652.625 | -1643.375 | 1336708.475 | 28652.625 | 0
2021010321 | 1 | 0.63148 | 94722 | 0.36833 | 0 | 0.36297 | 4537.125 | 0 | 0 | 64000 | 4537.125 | 0 | 26184.875 | -2467.75 | 1335989.85 | 26184.875 | 0
2021010322 | 1 | 0.61162 | 91743 | 0.31616 | 0 | 0.36303 | 4537.875 | 0 | 0 | 64000 | 4537.875 | 0 | 23205.125 | -2979.75 | 1338250.975 | 23205.125 | 0
2021010323 | 1 | 0.58746 | 88119 | 0.187 | 0 | 0.30322 | 3790.25 | 0 | 0 | 64000 | 3790.25 | 0 | 20328.75 | -2876.375 | 1343388.475 | 20328.75 | 0
2021010324 | 1 | 0.56344 | 84516 | 0.14772 | 0 | 0.25422 | 3177.75 | 0 | 0 | 64000 | 3177.75 | 0 | 17338.25 | -2990.5 | 1350000 | 17338.25 | 0
2021010401 | 2 | 0.54602 | 81903 | 0.13996 | 0 | 0.21451 | 2681.375 | 0 | 0 | 64000 | 2681.375 | 0 | 15221.625 | -2116.625 | 1350000 | 15221.625 | 0
2021010402 | 2 | 0.53746 | 80619 | 0.12574 | 0 | 0.19582 | 2447.75 | 0 | 0 | 64000 | 2447.75 | 0 | 14171.25 | -1050.375 | 1350000 | 14171.25 | 0
2021010403 | 2 | 0.53512 | 80268 | 0.12515 | 0 | 0.15882 | 1985.25 | 0 | 0 | 64000 | 1985.25 | 0 | 14282.75 | 111.5 | 1350000 | 14282.75 | 0
2021010404 | 2 | 0.53996 | 80994 | 0.11482 | 0 | 0.15992 | 1999 | 0 | 0 | 64000 | 1999 | 0 | 14995 | 712.25 | 1350000 | 14995 | 0
2021010405 | 2 | 0.55333 | 82999.5 | 0.12542 | 0 | 0.19196 | 2399.5 | 0 | 0 | 64000 | 2399.5 | 0 | 16600 | 1605 | 1350000 | 16600 | 0
2021010406 | 2 | 0.58405 | 87607.5 | 0.14434 | 0 | 0.28567 | 3570.875 | 0 | 0 | 64000 | 3570.875 | 0 | 20036.625 | 3436.625 | 1350000 | 20036.625 | 0
2021010407 | 2 | 0.63012 | 94518 | 0.11411 | 0 | 0.397 | 4962.5 | 0 | 0 | 64000 | 4962.5 | 0 | 25555.5 | 5518.875 | 1349910.75 | 25555.5 | 0
2021010408 | 2 | 0.66979 | 100468.5 | 0.09366 | 0 | 0.48669 | 6083.625 | 0.01911 | 1528.8 | 64000 | 6083.625 | 1528.8 | 28856.075 | 3300.575 | 1346520.925 | 28856.075 | 0
2021010409 | 2 | 0.68176 | 102264 | 0.05486 | 0 | 0.57432 | 7179 | 0.173 | 13840 | 64000 | 7179 | 13840 | 17245 | -11611.075 | 1350000 | 17245 | 0
2021010410 | 2 | 0.67743 | 101614.5 | 0.03624 | 0 | 0.56409 | 7051.125 | 0.32701 | 26160.8 | 64000 | 7051.125 | 26160.8 | 4402.575 | -12842.425 | 1350000 | 4402.575 | 0
2021010411 | 2 | 0.67118 | 100677 | 0.01381 | 0 | 0.49596 | 6199.5 | 0.38109 | 30487.2 | 64000 | 6199.5 | 30477.5 | 0 | -4402.575 | 1350000 | 0 | 0
2021010412 | 2 | 0.66483 | 99724.5 | 0.00825 | 0 | 0.44385 | 5548.125 | 0.36946 | 29556.8 | 64000 | 5548.125 | 29556.8 | 619.575 | 619.575 | 1350000 | 619.575 | 0
2021010413 | 2 | 0.6609 | 99135 | 0.0059 | 0 | 0.43139 | 5392.375 | 0.35157 | 28125.6 | 64000 | 5392.375 | 28125.6 | 1617.025 | 997.45 | 1350000 | 1617.025 | 0
2021010414 | 2 | 0.65663 | 98494.5 | 0.0011 | 0 | 0.36215 | 4526.875 | 0.33173 | 26538.4 | 64000 | 4526.875 | 26538.4 | 3429.225 | 1812.2 | 1350000 | 3429.225 | 0
2021010415 | 2 | 0.65248 | 97872 | 0.00592 | 0 | 0.38375 | 4796.875 | 0.34566 | 27652.8 | 64000 | 4796.875 | 27652.8 | 1422.325 | -2006.9 | 1350000 | 1422.325 | 0
2021010416 | 2 | 0.65144 | 97716 | 0.00937 | 0 | 0.4199 | 5248.75 | 0.16328 | 13062.4 | 64000 | 5248.75 | 13062.4 | 15404.85 | 13982.525 | 1350000 | 15404.85 | 0
2021010417 | 2 | 0.66148 | 99222 | 0.00697 | 0 | 0.40274 | 5034.25 | 0.01426 | 1140.8 | 64000 | 5034.25 | 1140.8 | 29046.95 | 13642.1 | 1346419.3 | 29046.95 | 0
2021010418 | 2 | 0.69193 | 103789.5 | 0.00671 | 0 | 0.31891 | 3986.375 | 0 | 0 | 64000 | 3986.375 | 0 | 35803.125 | 6756.175 | 1336082.425 | 35803.125 | 0
2021010419 | 2 | 0.69733 | 104599.5 | 0.00507 | 0 | 0.25103 | 3137.875 | 0 | 0 | 64000 | 3137.875 | 0 | 37461.625 | 1658.5 | 1324087.05 | 37461.625 | 0
2021010420 | 2 | 0.68533 | 102799.5 | 0.00665 | 0 | 0.21665 | 2708.125 | 0 | 0 | 64000 | 2708.125 | 0 | 36091.375 | -1370.25 | 1313461.925 | 36091.375 | 0
2021010421 | 2 | 0.67099 | 100648.5 | 0.00625 | 0 | 0.24578 | 3072.25 | 0 | 0 | 64000 | 3072.25 | 0 | 33576.25 | -2515.125 | 1305351.925 | 33576.25 | 0
2021010422 | 2 | 0.64834 | 97251 | 0.00753 | 0 | 0.27109 | 3388.625 | 0 | 0 | 64000 | 3388.625 | 0 | 29862.375 | -3713.875 | 1300955.8 | 29862.375 | 0
2021010423 | 2 | 0.61836 | 92754 | 0.00678 | 0 | 0.26722 | 3340.25 | 0 | 0 | 64000 | 3340.25 | 0 | 25413.75 | -4448.625 | 1301008.3 | 25413.75 | 0
2021010424 | 2 | 0.58793 | 88189.5 | 0.00684 | 0 | 0.25054 | 3131.75 | 0 | 0 | 64000 | 3131.75 | 0 | 21057.75 | -4356 | 1305416.8 | 21057.75 | 0
2021010501 | 3 | 0.56503 | 84754.5 | 0.00658 | 0 | 0.2791 | 3488.75 | 0 | 0 | 64000 | 3488.75 | 0 | 17265.75 | -3792 | 1313617.3 | 17265.75 | 0
2021010502 | 3 | 0.55292 | 82938 | 0.0059 | 0 | 0.34265 | 4283.125 | 0 | 0 | 64000 | 4283.125 | 0 | 14654.875 | -2610.875 | 1324428.675 | 14654.875 | 0
2021010503 | 3 | 0.5474 | 82110 | 0.00689 | 0 | 0.46452 | 5806.5 | 0 | 0 | 64000 | 5806.5 | 0 | 12303.5 | -2351.375 | 1337591.425 | 12303.5 | 0
2021010504 | 3 | 0.54738 | 82107 | 0.00675 | 0 | 0.59089 | 7386.125 | 0 | 0 | 64000 | 7386.125 | 0 | 10720.875 | -1582.625 | 1350000 | 10720.875 | 0
2021010505 | 3 | 0.55823 | 83734.5 | 0.00767 | 0 | 0.67137 | 8392.125 | 0 | 0 | 64000 | 8392.125 | 0 | 11342.375 | 621.5 | 1350000 | 11342.375 | 0
2021010506 | 3 | 0.58442 | 87663 | 0.00797 | 0 | 0.68768 | 8596 | 0 | 0 | 64000 | 8596 | 0 | 15067 | 3724.625 | 1350000 | 15067 | 0
2021010507 | 3 | 0.62517 | 93775.5 | 0.00749 | 0 | 0.68596 | 8574.5 | 0.00646 | 516.8 | 64000 | 8574.5 | 516.8 | 20684.2 | 5617.2 | 1350000 | 20684.2 | 0
2021010508 | 3 | 0.66239 | 99358.5 | 0.0071 | 0 | 0.67456 | 8432 | 0.03393 | 2714.4 | 64000 | 8432 | 2714.4 | 24212.1 | 3527.9 | 1350000 | 24212.1 | 0
2021010509 | 3 | 0.67544 | 101316 | 0.0075 | 0 | 0.64656 | 8082 | 0.09762 | 7809.6 | 64000 | 8082 | 7809.6 | 21424.4 | -2787.7 | 1350000 | 21424.4 | 0
2021010510 | 3 | 0.67565 | 101347.5 | 0.00787 | 0 | 0.59353 | 7419.125 | 0.12041 | 9632.8 | 64000 | 7419.125 | 9632.8 | 20295.575 | -1128.825 | 1350000 | 20295.575 | 0
2021010511 | 3 | 0.67547 | 101320.5 | 0.00653 | 0 | 0.54211 | 6776.375 | 0.18715 | 14972 | 64000 | 6776.375 | 14972 | 15572.125 | -4723.45 | 1350000 | 15572.125 | 0
2021010512 | 3 | 0.673 | 100950 | 0.0049 | 0 | 0.4837 | 6046.25 | 0.23486 | 18788.8 | 64000 | 6046.25 | 18788.8 | 12114.95 | -3457.175 | 1350000 | 12114.95 | 0
2021010513 | 3 | 0.67004 | 100506 | 0.00327 | 0 | 0.39761 | 4970.125 | 0.2453 | 19624 | 64000 | 4970.125 | 19624 | 11911.875 | -203.075 | 1350000 | 11911.875 | 0
2021010514 | 3 | 0.66605 | 99907.5 | 0.00477 | 0 | 0.32807 | 4100.875 | 0.20885 | 16708 | 64000 | 4100.875 | 16708 | 15098.625 | 3186.75 | 1350000 | 15098.625 | 0
2021010515 | 3 | 0.66208 | 99312 | 0.00411 | 0 | 0.30412 | 3801.5 | 0.13627 | 10901.6 | 64000 | 3801.5 | 10901.6 | 20608.9 | 5510.275 | 1350000 | 20608.9 | 0
2021010516 | 3 | 0.66181 | 99271.5 | 0.03816 | 0 | 0.34075 | 4259.375 | 0.09444 | 7555.2 | 64000 | 4259.375 | 7555.2 | 23456.925 | 2848.025 | 1350000 | 23456.925 | 0
2021010517 | 3 | 0.67465 | 101197.5 | 0.08886 | 0 | 0.39944 | 4993 | 0.01041 | 832.8 | 64000 | 4993 | 832.8 | 31371.7 | 7914.775 | 1344094.55 | 31371.7 | 0
2021010518 | 3 | 0.70414 | 105621 | 0.14523 | 0 | 0.40459 | 5057.375 | 0 | 0 | 64000 | 5057.375 | 0 | 36563.625 | 5191.925 | 1332997.175 | 36563.625 | 0
2021010519 | 3 | 0.70672 | 106008 | 0.14184 | 0 | 0.4399 | 5498.75 | 0 | 0 | 64000 | 5498.75 | 0 | 36509.25 | -54.375 | 1321954.175 | 36509.25 | 0
2021010520 | 3 | 0.69405 | 104107.5 | 0.14281 | 0 | 0.44814 | 5601.75 | 0 | 0 | 64000 | 5601.75 | 0 | 34505.75 | -2003.5 | 1312914.675 | 34505.75 | 0
2021010521 | 3 | 0.67898 | 101847 | 0.13029 | 0 | 0.52375 | 6546.875 | 0 | 0 | 64000 | 6546.875 | 0 | 31300.125 | -3205.625 | 1307080.8 | 31300.125 | 0
2021010522 | 3 | 0.6563 | 98445 | 0.12697 | 0 | 0.55222 | 6902.75 | 0 | 0 | 64000 | 6902.75 | 0 | 27542.25 | -3757.875 | 1305004.8 | 27542.25 | 0
2021010523 | 3 | 0.62676 | 94014 | 0.13411 | 0 | 0.56378 | 7047.25 | 0 | 0 | 64000 | 7047.25 | 0 | 22966.75 | -4575.5 | 1307504.3 | 22966.75 | 0
2021010524 | 3 | 0.59578 | 89367 | 0.18026 | 0 | 0.58143 | 7267.875 | 0 | 0 | 64000 | 7267.875 | 0 | 18099.125 | -4867.625 | 1314871.425 | 18099.125 | 0
2021010601 | 4 | 0.57352 | 86028 | 0.21296 | 0 | 0.63982 | 7997.75 | 0 | 0 | 64000 | 7997.75 | 0 | 14030.25 | -4068.875 | 1326307.425 | 14030.25 | 0
2021010602 | 4 | 0.56055 | 84082.5 | 0.26232 | 0 | 0.65752 | 8219 | 0 | 0 | 64000 | 8219 | 0 | 11863.5 | -2166.75 | 1339910.175 | 11863.5 | 0
2021010603 | 4 | 0.55472 | 83208 | 0.28987 | 0 | 0.66833 | 8354.125 | 0 | 0 | 64000 | 8354.125 | 0 | 10853.875 | -1009.625 | 1350000 | 10853.875 | 0
2021010604 | 4 | 0.55481 | 83221.5 | 0.32851 | 0 | 0.62545 | 7818.125 | 0 | 0 | 64000 | 7818.125 | 0 | 11403.375 | 549.5 | 1350000 | 11403.375 | 0
2021010605 | 4 | 0.56622 | 84933 | 0.37132 | 0 | 0.59014 | 7376.75 | 0 | 0 | 64000 | 7376.75 | 0 | 13556.25 | 2152.875 | 1350000 | 13556.25 | 0
2021010606 | 4 | 0.59164 | 88746 | 0.41514 | 0 | 0.55594 | 6949.25 | 0 | 0 | 64000 | 6949.25 | 0 | 17796.75 | 4240.5 | 1350000 | 17796.75 | 0
2021010607 | 4 | 0.63306 | 94959 | 0.43346 | 0 | 0.47058 | 5882.25 | 0 | 0 | 64000 | 5882.25 | 0 | 25076.75 | 7280 | 1350000 | 25076.75 | 0
2021010608 | 4 | 0.66833 | 100249.5 | 0.45767 | 0 | 0.36482 | 4560.25 | 0.05222 | 4177.6 | 64000 | 4560.25 | 4177.6 | 27511.65 | 2434.9 | 1347954.6 | 27511.65 | 0
2021010609 | 4 | 0.67994 | 101991 | 0.47752 | 0 | 0.29729 | 3716.125 | 0.32262 | 25809.6 | 64000 | 3716.125 | 25809.6 | 8465.275 | -19046.375 | 1350000 | 8465.275 | 0
2021010610 | 4 | 0.67977 | 101965.5 | 0.49543 | 0 | 0.24176 | 3022 | 0.50442 | 40353.6 | 64000 | 3022 | 34943.5 | 0 | -8465.275 | 1350000 | 0 | 0
2021010611 | 4 | 0.6765 | 101475 | 0.51754 | 0 | 0.19112 | 2389 | 0.53913 | 43130.4 | 64000 | 2389 | 35086 | 0 | 0 | 1350000 | 0 | 0
2021010612 | 4 | 0.67295 | 100942.5 | 0.58203 | 0 | 0.14597 | 1824.625 | 0.53987 | 43189.6 | 64000 | 1824.625 | 35117.875 | 0 | 0 | 1350000 | 0 | 0
2021010613 | 4 | 0.66897 | 100345.5 | 0.59744 | 0 | 0.14099 | 1762.375 | 0.56296 | 45036.8 | 64000 | 1762.375 | 34583.125 | 0 | 0 | 1350000 | 0 | 0
2021010614 | 4 | 0.6653 | 99795 | 0.62168 | 0 | 0.12983 | 1622.875 | 0.57757 | 46205.6 | 64000 | 1622.875 | 34172.125 | 0 | 0 | 1350000 | 0 | 0
2021010615 | 4 | 0.6625 | 99375 | 0.63395 | 0 | 0.11414 | 1426.75 | 0.52759 | 42207.2 | 64000 | 1426.75 | 33948.25 | 0 | 0 | 1350000 | 0 | 0
2021010616 | 4 | 0.66391 | 99586.5 | 0.70418 | 0 | 0.12082 | 1510.25 | 0.25436 | 20348.8 | 64000 | 1510.25 | 20348.8 | 13727.45 | 13727.45 | 1350000 | 13727.45 | 0
2021010617 | 4 | 0.67707 | 101560.5 | 0.70742 | 0 | 0.13384 | 1673 | 0.01811 | 1448.8 | 64000 | 1673 | 1448.8 | 34438.7 | 20711.25 | 1341027.55 | 34438.7 | 0
2021010618 | 4 | 0.70804 | 106206 | 0.68604 | 0 | 0.14666 | 1833.25 | 0 | 0 | 64000 | 1833.25 | 0 | 40372.75 | 5934.05 | 1326121.05 | 40372.75 | 0
2021010619 | 4 | 0.71264 | 106896 | 0.72384 | 0 | 0.14396 | 1799.5 | 0 | 0 | 64000 | 1799.5 | 0 | 41096.5 | 723.75 | 1310490.8 | 41096.5 | 0
2021010620 | 4 | 0.70159 | 105238.5 | 0.81056 | 0 | 0.16269 | 2033.625 | 0 | 0 | 64000 | 2033.625 | 0 | 39204.875 | -1891.625 | 1296752.175 | 39204.875 | 0
2021010621 | 4 | 0.68616 | 102924 | 0.81691 | 0 | 0.17552 | 2194 | 0 | 0 | 64000 | 2194 | 0 | 36730 | -2474.875 | 1285488.425 | 36730 | 0
2021010622 | 4 | 0.66381 | 99571.5 | 0.79818 | 0 | 0.18163 | 2270.375 | 0 | 0 | 64000 | 2270.375 | 0 | 33301.125 | -3428.875 | 1277653.55 | 33301.125 | 0
2021010623 | 4 | 0.63369 | 95053.5 | 0.73624 | 0 | 0.1853 | 2316.25 | 0 | 0 | 64000 | 2316.25 | 0 | 28737.25 | -4563.875 | 1274382.55 | 28737.25 | 0
2021010624 | 4 | 0.60503 | 90754.5 | 0.70288 | 0 | 0.19904 | 2488 | 0 | 0 | 64000 | 2488 | 0 | 24266.5 | -4470.75 | 1275582.3 | 24266.5 | 0
2021010701 | 5 | 0.58559 | 87838.5 | 0.69561 | 0 | 0.20798 | 2599.75 | 0 | 0 | 64000 | 2599.75 | 0 | 21238.75 | -3027.75 | 1279809.8 | 21238.75 | 0
2021010702 | 5 | 0.57371 | 86056.5 | 0.69064 | 0 | 0.2093 | 2616.25 | 0 | 0 | 64000 | 2616.25 | 0 | 19440.25 | -1798.5 | 1285835.8 | 19440.25 | 0
2021010703 | 5 | 0.56975 | 85462.5 | 0.68817 | 0 | 0.1951 | 2438.75 | 0 | 0 | 64000 | 2438.75 | 0 | 19023.75 | -416.5 | 1292278.3 | 19023.75 | 0
2021010704 | 5 | 0.57094 | 85641 | 0.69828 | 0 | 0.1713 | 2141.25 | 0 | 0 | 64000 | 2141.25 | 0 | 19499.75 | 476 | 1298244.8 | 19499.75 | 0
2021010705 | 5 | 0.58519 | 87778.5 | 0.71317 | 0 | 0.15551 | 1943.875 | 0 | 0 | 64000 | 1943.875 | 0 | 21834.625 | 2334.875 | 1301876.425 | 21834.625 | 0
2021010706 | 5 | 0.61279 | 91918.5 | 0.73584 | 0 | 0.16958 | 2119.75 | 0 | 0 | 64000 | 2119.75 | 0 | 25798.75 | 3964.125 | 1301543.925 | 25798.75 | 0
2021010707 | 5 | 0.65826 | 98739 | 0.71364 | 0 | 0.19244 | 2405.5 | 0.00048 | 38.4 | 64000 | 2405.5 | 38.4 | 32295.1 | 6496.35 | 1294715.075 | 32295.1 | 0
2021010708 | 5 | 0.69524 | 104286 | 0.64642 | 0 | 0.22329 | 2791.125 | 0.04077 | 3261.6 | 64000 | 2791.125 | 3261.6 | 34233.275 | 1938.175 | 1285948.05 | 34233.275 | 0
2021010709 | 5 | 0.70032 | 105048 | 0.60979 | 0 | 0.25978 | 3247.25 | 0.24486 | 19588.8 | 64000 | 3247.25 | 19588.8 | 18211.95 | -16021.325 | 1293202.35 | 18211.95 | 0
2021010710 | 5 | 0.68403 | 102604.5 | 0.53807 | 0 | 0.25042 | 3130.25 | 0.37577 | 30061.6 | 64000 | 3130.25 | 30061.6 | 5412.65 | -12799.3 | 1313255.95 | 5412.65 | 0
2021010711 | 5 | 0.67051 | 100576.5 | 0.49509 | 0 | 0.29595 | 3699.375 | 0.39188 | 31350.4 | 64000 | 3699.375 | 31350.4 | 1526.725 | -3885.925 | 1337195.475 | 1526.725 | 0
2021010712 | 5 | 0.66009 | 99013.5 | 0.41886 | 0 | 0.36107 | 4513.375 | 0.36428 | 29142.4 | 64000 | 4513.375 | 29142.4 | 1357.725 | -169 | 1350000 | 1357.725 | 0
2021010713 | 5 | 0.65055 | 97582.5 | 0.40992 | 0 | 0.45706 | 5713.25 | 0.35729 | 28583.2 | 64000 | 5713.25 | 27869.25 | 0 | -1357.725 | 1350000 | 0 | 0
2021010714 | 5 | 0.64326 | 96489 | 0.42457 | 0 | 0.52077 | 6509.625 | 0.31418 | 25134.4 | 64000 | 6509.625 | 25134.4 | 844.975 | 844.975 | 1350000 | 844.975 | 0
2021010715 | 5 | 0.63772 | 95658 | 0.39301 | 0 | 0.55043 | 6880.375 | 0.22299 | 17839.2 | 64000 | 6880.375 | 17839.2 | 6938.425 | 6093.45 | 1350000 | 6938.425 | 0
2021010716 | 5 | 0.64212 | 96318 | 0.39472 | 0 | 0.49044 | 6130.5 | 0.06027 | 4821.6 | 64000 | 6130.5 | 4821.6 | 21365.9 | 14427.475 | 1350000 | 21365.9 | 0
2021010717 | 5 | 0.65908 | 98862 | 0.44973 | 0 | 0.44682 | 5585.25 | 0.00383 | 306.4 | 64000 | 5585.25 | 306.4 | 28970.35 | 7604.45 | 1346495.9 | 28970.35 | 0
2021010718 | 5 | 0.69728 | 104592 | 0.49941 | 0 | 0.46283 | 5785.375 | 0 | 0 | 64000 | 5785.375 | 0 | 34806.625 | 5836.275 | 1337155.525 | 34806.625 | 0
2021010719 | 5 | 0.70682 | 106023 | 0.51473 | 0 | 0.5014 | 6267.5 | 0 | 0 | 64000 | 6267.5 | 0 | 35755.5 | 948.875 | 1326866.275 | 35755.5 | 0
2021010720 | 5 | 0.69965 | 104947.5 | 0.47877 | 0 | 0.54566 | 6820.75 | 0 | 0 | 64000 | 6820.75 | 0 | 34126.75 | -1628.75 | 1318205.775 | 34126.75 | 0
2021010721 | 5 | 0.68839 | 103258.5 | 0.44471 | 0 | 0.59733 | 7466.625 | 0 | 0 | 64000 | 7466.625 | 0 | 31791.875 | -2334.875 | 1311880.15 | 31791.875 | 0
2021010722 | 5 | 0.66859 | 100288.5 | 0.45296 | 0 | 0.68012 | 8501.5 | 0 | 0 | 64000 | 8501.5 | 0 | 27787 | -4004.875 | 1309559.4 | 27787 | 0
2021010723 | 5 | 0.64064 | 96096 | 0.43979 | 0 | 0.6677 | 8346.25 | 0 | 0 | 64000 | 8346.25 | 0 | 23749.75 | -4037.25 | 1311275.9 | 23749.75 | 0
2021010724 | 5 | 0.61246 | 91869 | 0.40653 | 0 | 0.68899 | 8612.375 | 0 | 0 | 64000 | 8612.375 | 0 | 19256.625 | -4493.125 | 1317485.525 | 19256.625 | 0
2021010801 | 6 | 0.59281 | 88921.5 | 0.30729 | 0 | 0.64659 | 8082.375 | 0 | 0 | 64000 | 8082.375 | 0 | 16839.125 | -2417.5 | 1326112.65 | 16839.125 | 0
2021010802 | 6 | 0.58136 | 87204 | 0.29528 | 0 | 0.64798 | 8099.75 | 0 | 0 | 64000 | 8099.75 | 0 | 15104.25 | -1734.875 | 1336474.65 | 15104.25 | 0
2021010803 | 6 | 0.57709 | 86563.5 | 0.25161 | 0 | 0.65796 | 8224.5 | 0 | 0 | 64000 | 8224.5 | 0 | 14339 | -765.25 | 1347601.9 | 14339 | 0
2021010804 | 6 | 0.57741 | 86611.5 | 0.19159 | 0 | 0.6481 | 8101.25 | 0 | 0 | 64000 | 8101.25 | 0 | 14510.25 | 171.25 | 1350000 | 14510.25 | 0
2021010805 | 6 | 0.5873 | 88095 | 0.21413 | 0 | 0.6392 | 7990 | 0 | 0 | 64000 | 7990 | 0 | 16105 | 1594.75 | 1350000 | 16105 | 0
2021010806 | 6 | 0.61369 | 92053.5 | 0.18289 | 0 | 0.62567 | 7820.875 | 0 | 0 | 64000 | 7820.875 | 0 | 20232.625 | 4127.625 | 1350000 | 20232.625 | 0
2021010807 | 6 | 0.65543 | 98314.5 | 0.19154 | 0 | 0.60464 | 7558 | 0 | 0 | 64000 | 7558 | 0 | 26756.5 | 6523.875 | 1348709.75 | 26756.5 | 0
2021010808 | 6 | 0.69277 | 103915.5 | 0.19758 | 0 | 0.59628 | 7453.5 | 0.02438 | 1950.4 | 64000 | 7453.5 | 1950.4 | 30511.6 | 3755.1 | 1343664.4 | 30511.6 | 0
2021010809 | 6 | 0.70644 | 105966 | 0.16467 | 0 | 0.57656 | 7207 | 0.21492 | 17193.6 | 64000 | 7207 | 17193.6 | 17565.4 | -12946.2 | 1350000 | 17565.4 | 0
2021010810 | 6 | 0.70836 | 106254 | 0.15247 | 0 | 0.60126 | 7515.75 | 0.408 | 32640 | 64000 | 7515.75 | 32640 | 2098.25 | -15467.15 | 1350000 | 2098.25 | 0
2021010811 | 6 | 0.70539 | 105808.5 | 0.1069 | 0 | 0.60783 | 7597.875 | 0.48695 | 38956 | 64000 | 7597.875 | 34210.625 | 0 | -2098.25 | 1350000 | 0 | 0
2021010812 | 6 | 0.70101 | 105151.5 | 0.12013 | 0 | 0.63703 | 7962.875 | 0.47714 | 38171.2 | 64000 | 7962.875 | 33188.625 | 0 | 0 | 1350000 | 0 | 0
2021010813 | 6 | 0.69596 | 104394 | 0.13006 | 0 | 0.65167 | 8145.875 | 0.48298 | 38638.4 | 64000 | 8145.875 | 32248.125 | 0 | 0 | 1350000 | 0 | 0
2021010814 | 6 | 0.68662 | 102993 | 0.13354 | 0 | 0.68253 | 8531.625 | 0.45678 | 36542.4 | 64000 | 8531.625 | 30461.375 | 0 | 0 | 1350000 | 0 | 0
2021010815 | 6 | 0.67973 | 101959.5 | 0.23832 | 0 | 0.71448 | 8931 | 0.29827 | 23861.6 | 64000 | 8931 | 23861.6 | 5166.9 | 5166.9 | 1350000 | 5166.9 | 0
2021010816 | 6 | 0.67746 | 101619 | 0.28379 | 0 | 0.71146 | 8893.25 | 0.09571 | 7656.8 | 64000 | 8893.25 | 7656.8 | 21068.95 | 15902.05 | 1350000 | 21068.95 | 0
2021010817 | 6 | 0.68626 | 102939 | 0.38642 | 0 | 0.69076 | 8634.5 | 0.00733 | 586.4 | 64000 | 8634.5 | 586.4 | 29718.1 | 8649.15 | 1345748.15 | 29718.1 | 0
2021010818 | 6 | 0.71203 | 106804.5 | 0.46494 | 0 | 0.66617 | 8327.125 | 0 | 0 | 64000 | 8327.125 | 0 | 34477.375 | 4759.275 | 1336737.025 | 34477.375 | 0
2021010819 | 6 | 0.71345 | 107017.5 | 0.50177 | 0 | 0.6058 | 7572.5 | 0 | 0 | 64000 | 7572.5 | 0 | 35445 | 967.625 | 1326758.275 | 35445 | 0
2021010820 | 6 | 0.70243 | 105364.5 | 0.52264 | 0 | 0.59536 | 7442 | 0 | 0 | 64000 | 7442 | 0 | 33922.5 | -1522.5 | 1318302.025 | 33922.5 | 0
2021010821 | 6 | 0.68944 | 103416 | 0.53278 | 0 | 0.5693 | 7116.25 | 0 | 0 | 64000 | 7116.25 | 0 | 32299.75 | -1622.75 | 1311468.525 | 32299.75 | 0
2021010822 | 6 | 0.67145 | 100717.5 | 0.59749 | 0 | 0.57092 | 7136.5 | 0 | 0 | 64000 | 7136.5 | 0 | 29581 | -2718.75 | 1307353.775 | 29581 | 0
2021010823 | 6 | 0.64574 | 96861 | 0.63635 | 0 | 0.55761 | 6970.125 | 0 | 0 | 64000 | 6970.125 | 0 | 25890.875 | -3690.125 | 1306929.15 | 25890.875 | 0
2021010824 | 6 | 0.61966 | 92949 | 0.66185 | 0 | 0.52621 | 6577.625 | 0 | 0 | 64000 | 6577.625 | 0 | 22371.375 | -3519.5 | 1310024.025 | 22371.375 | 0
2021010901 | 7 | 0.59954 | 89931 | 0.68924 | 0 | 0.53105 | 6638.125 | 0 | 0 | 64000 | 6638.125 | 0 | 19292.875 | -3078.5 | 1316197.4 | 19292.875 | 0
2021010902 | 7 | 0.5872 | 88080 | 0.66754 | 0 | 0.55756 | 6969.5 | 0 | 0 | 64000 | 6969.5 | 0 | 17110.5 | -2182.375 | 1324553.15 | 17110.5 | 0
2021010903 | 7 | 0.5813 | 87195 | 0.6858 | 0 | 0.54914 | 6864.25 | 0 | 0 | 64000 | 6864.25 | 0 | 16330.75 | -779.75 | 1333688.65 | 16330.75 | 0
2021010904 | 7 | 0.58175 | 87262.5 | 0.69759 | 0 | 0.51517 | 6439.625 | 0 | 0 | 64000 | 6439.625 | 0 | 16822.875 | 492.125 | 1342332.025 | 16822.875 | 0
2021010905 | 7 | 0.58753 | 88129.5 | 0.71724 | 0 | 0.48457 | 6057.125 | 0 | 0 | 64000 | 6057.125 | 0 | 18072.375 | 1249.5 | 1349725.9 | 18072.375 | 0
2021010906 | 7 | 0.60131 | 90196.5 | 0.71948 | 0 | 0.48109 | 6013.625 | 0 | 0 | 64000 | 6013.625 | 0 | 20182.875 | 2110.5 | 1350000 | 20182.875 | 0
2021010907 | 7 | 0.62247 | 93370.5 | 0.70068 | 0 | 0.45934 | 5741.75 | 0 | 0 | 64000 | 5741.75 | 0 | 23628.75 | 3445.875 | 1350000 | 23628.75 | 0
2021010908 | 7 | 0.64402 | 96603 | 0.73292 | 0 | 0.46623 | 5827.875 | 0.05257 | 4205.6 | 64000 | 5827.875 | 4205.6 | 22569.525 | -1059.225 | 1350000 | 22569.525 | 0
2021010909 | 7 | 0.65401 | 98101.5 | 0.7486 | 0 | 0.52962 | 6620.25 | 0.34053 | 27242.4 | 64000 | 6620.25 | 27242.4 | 238.85 | -22330.675 | 1350000 | 238.85 | 0
2021010910 | 7 | 0.65014 | 97521 | 0.75382 | 0 | 0.55144 | 6893 | 0.52389 | 41911.2 | 64000 | 6893 | 26628 | 0 | -238.85 | 1350000 | 0 | 0
2021010911 | 7 | 0.64048 | 96072 | 0.75649 | 0 | 0.56238 | 7029.75 | 0.55969 | 44775.2 | 64000 | 7029.75 | 25042.25 | 0 | 0 | 1350000 | 0 | 0
2021010912 | 7 | 0.62871 | 94306.5 | 0.74052 | 0 | 0.54974 | 6871.75 | 0.5736 | 45888 | 64000 | 6871.75 | 23434.75 | 0 | 0 | 1350000 | 0 | 0
2021010913 | 7 | 0.61536 | 92304 | 0.74625 | 0 | 0.56832 | 7104 | 0.60332 | 48265.6 | 64000 | 7104 | 21200 | 0 | 0 | 1350000 | 0 | 0
2021010914 | 7 | 0.60247 | 90370.5 | 0.76171 | 0 | 0.55436 | 6929.5 | 0.61387 | 49109.6 | 64000 | 6929.5 | 19441 | 0 | 0 | 1350000 | 0 | 0
2021010915 | 7 | 0.59426 | 89139 | 0.81448 | 0 | 0.53757 | 6719.625 | 0.55696 | 44556.8 | 64000 | 6719.625 | 18419.375 | 0 | 0 | 1350000 | 0 | 0
2021010916 | 7 | 0.59452 | 89178 | 0.83843 | 0 | 0.54527 | 6815.875 | 0.27668 | 22134.4 | 64000 | 6815.875 | 18362.125 | 0 | 0 | 1350000 | 0 | 0
2021010917 | 7 | 0.61193 | 91789.5 | 0.81664 | 0 | 0.54274 | 6784.25 | 0.02305 | 1844 | 64000 | 6784.25 | 1844 | 19161.25 | 19161.25 | 1350000 | 19161.25 | 0
2021010918 | 7 | 0.65268 | 97902 | 0.88699 | 0 | 0.53549 | 6693.625 | 0 | 0 | 64000 | 6693.625 | 0 | 27208.375 | 8047.125 | 1348257.875 | 27208.375 | 0
2021010919 | 7 | 0.66786 | 100179 | 0.91253 | 0 | 0.51073 | 6384.125 | 0 | 0 | 64000 | 6384.125 | 0 | 29794.875 | 2586.5 | 1343929.25 | 29794.875 | 0
2021010920 | 7 | 0.66339 | 99508.5 | 0.9065 | 0 | 0.51296 | 6412 | 0 | 0 | 64000 | 6412 | 0 | 29096.5 | -698.375 | 1340299 | 29096.5 | 0
2021010921 | 7 | 0.6546 | 98190 | 0.92496 | 0 | 0.48419 | 6052.375 | 0 | 0 | 64000 | 6052.375 | 0 | 28137.625 | -958.875 | 1337627.625 | 28137.625 | 0
2021010922 | 7 | 0.64032 | 96048 | 0.94661 | 0 | 0.49 | 6125 | 0 | 0 | 64000 | 6125 | 0 | 25923 | -2214.625 | 1337170.875 | 25923 | 0
2021010923 | 7 | 0.62092 | 93138 | 0.92116 | 0 | 0.48299 | 6037.375 | 0 | 0 | 64000 | 6037.375 | 0 | 23100.625 | -2822.375 | 1339536.5 | 23100.625 | 0
2021010924 | 7 | 0.59882 | 89823 | 0.91177 | 0 | 0.47665 | 5958.125 | 0 | 0 | 64000 | 5958.125 | 0 | 19864.875 | -3235.75 | 1345137.875 | 19864.875 | 0
2021011001 | 1 | 0.58158 | 87237 | 0.89852 | 0 | 0.4726 | 5907.5 | 0 | 0 | 64000 | 5907.5 | 0 | 17329.5 | -2535.375 | 1350000 | 17329.5 | 0
2021011002 | 1 | 0.57016 | 85524 | 0.83655 | 0 | 0.49204 | 6150.5 | 0 | 0 | 64000 | 6150.5 | 0 | 15373.5 | -1956 | 1350000 | 15373.5 | 0
2021011003 | 1 | 0.56555 | 84832.5 | 0.80546 | 0 | 0.50997 | 6374.625 | 0 | 0 | 64000 | 6374.625 | 0 | 14457.875 | -915.625 | 1350000 | 14457.875 | 0
2021011004 | 1 | 0.5669 | 85035 | 0.79898 | 0 | 0.46683 | 5835.375 | 0 | 0 | 64000 | 5835.375 | 0 | 15199.625 | 741.75 | 1350000 | 15199.625 | 0
2021011005 | 1 | 0.5715 | 85725 | 0.86366 | 0 | 0.35944 | 4493 | 0 | 0 | 64000 | 4493 | 0 | 17232 | 2032.375 | 1350000 | 17232 | 0
2021011006 | 1 | 0.58301 | 87451.5 | 0.84167 | 0 | 0.27339 | 3417.375 | 0 | 0 | 64000 | 3417.375 | 0 | 20034.125 | 2802.125 | 1350000 | 20034.125 | 0
2021011007 | 1 | 0.59997 | 89995.5 | 0.83531 | 0 | 0.24454 | 3056.75 | 0 | 0 | 64000 | 3056.75 | 0 | 22938.75 | 2904.625 | 1350000 | 22938.75 | 0
2021011008 | 1 | 0.61927 | 92890.5 | 0.82456 | 0 | 0.28622 | 3577.75 | 0.05318 | 4254.4 | 64000 | 3577.75 | 4254.4 | 21058.35 | -1880.4 | 1350000 | 21058.35 | 0
2021011009 | 1 | 0.62544 | 93816 | 0.70633 | 0 | 0.31395 | 3924.375 | 0.34286 | 27428.8 | 64000 | 3924.375 | 25891.625 | 0 | -21058.35 | 1350000 | 0 | 0
2021011010 | 1 | 0.61662 | 92493 | 0.59593 | 0 | 0.30839 | 3854.875 | 0.56033 | 44826.4 | 64000 | 3854.875 | 24638.125 | 0 | 0 | 1350000 | 0 | 0
2021011011 | 1 | 0.60303 | 90454.5 | 0.47074 | 0 | 0.28637 | 3579.625 | 0.57184 | 45747.2 | 64000 | 3579.625 | 22874.875 | 0 | 0 | 1350000 | 0 | 0
2021011012 | 1 | 0.59125 | 88687.5 | 0.28779 | 0 | 0.26573 | 3321.625 | 0.55843 | 44674.4 | 64000 | 3321.625 | 21365.875 | 0 | 0 | 1350000 | 0 | 0
2021011013 | 1 | 0.58152 | 87228 | 0.16948 | 0 | 0.28053 | 3506.625 | 0.52779 | 42223.2 | 64000 | 3506.625 | 19721.375 | 0 | 0 | 1350000 | 0 | 0
2021011014 | 1 | 0.57092 | 85638 | 0.12517 | 0 | 0.33618 | 4202.25 | 0.49492 | 39593.6 | 64000 | 4202.25 | 17435.75 | 0 | 0 | 1350000 | 0 | 0
2021011015 | 1 | 0.56413 | 84619.5 | 0.09798 | 0 | 0.3751 | 4688.75 | 0.33776 | 27020.8 | 64000 | 4688.75 | 15930.75 | 0 | 0 | 1350000 | 0 | 0
2021011016 | 1 | 0.56686 | 85029 | 0.05842 | 0 | 0.45248 | 5656 | 0.11464 | 9171.2 | 64000 | 5656 | 9171.2 | 6201.8 | 6201.8 | 1350000 | 6201.8 | 0
2021011017 | 1 | 0.59165 | 88747.5 | 0.06886 | 0 | 0.52131 | 6516.375 | 0.0066 | 528 | 64000 | 6516.375 | 528 | 17703.125 | 11501.325 | 1350000 | 17703.125 | 0
2021011018 | 1 | 0.63842 | 95763 | 0.15436 | 0 | 0.53696 | 6712 | 0 | 0 | 64000 | 6712 | 0 | 25051 | 7347.875 | 1350000 | 25051 | 0
2021011019 | 1 | 0.66076 | 99114 | 0.23184 | 0 | 0.54375 | 6796.875 | 0 | 0 | 64000 | 6796.875 | 0 | 28317.125 | 3266.125 | 1347149.125 | 28317.125 | 0
2021011020 | 1 | 0.66316 | 99474 | 0.16336 | 0 | 0.59064 | 7383 | 0 | 0 | 64000 | 7383 | 0 | 28091 | -226.125 | 1344524.375 | 28091 | 0
2021011021 | 1 | 0.65863 | 98794.5 | 0.09501 | 0 | 0.64303 | 8037.875 | 0 | 0 | 64000 | 8037.875 | 0 | 26756.625 | -1334.375 | 1343234 | 26756.625 | 0
2021011022 | 1 | 0.64491 | 96736.5 | 0.0563 | 0 | 0.6934 | 8667.5 | 0 | 0 | 64000 | 8667.5 | 0 | 24069 | -2687.625 | 1344631.25 | 24069 | 0
2021011023 | 1 | 0.62801 | 94201.5 | 0.05135 | 0 | 0.73865 | 9233.125 | 0 | 0 | 64000 | 9233.125 | 0 | 20968.375 | -3100.625 | 1349129.125 | 20968.375 | 0
2021011024 | 1 | 0.60837 | 91255.5 | 0.04794 | 0 | 0.73703 | 9212.875 | 0 | 0 | 64000 | 9212.875 | 0 | 18042.625 | -2925.75 | 1350000 | 18042.625 | 0
2021011101 | 2 | 0.59558 | 89337 | 0.02904 | 0 | 0.73009 | 9126.125 | 0 | 0 | 64000 | 9126.125 | 0 | 16210.875 | -1831.75 | 1350000 | 16210.875 | 0
2021011102 | 2 | 0.59119 | 88678.5 | 0.04071 | 0 | 0.69573 | 8696.625 | 0 | 0 | 64000 | 8696.625 | 0 | 15981.875 | -229 | 1350000 | 15981.875 | 0
2021011103 | 2 | 0.59041 | 88561.5 | 0.0814 | 0 | 0.66489 | 8311.125 | 0 | 0 | 64000 | 8311.125 | 0 | 16250.375 | 268.5 | 1350000 | 16250.375 | 0
2021011104 | 2 | 0.59758 | 89637 | 0.12623 | 0 | 0.66203 | 8275.375 | 0 | 0 | 64000 | 8275.375 | 0 | 17361.625 | 1111.25 | 1350000 | 17361.625 | 0
2021011105 | 2 | 0.61247 | 91870.5 | 0.13587 | 0 | 0.63424 | 7928 | 0 | 0 | 64000 | 7928 | 0 | 19942.5 | 2580.875 | 1350000 | 19942.5 | 0
2021011106 | 2 | 0.64363 | 96544.5 | 0.17825 | 0 | 0.62143 | 7767.875 | 0 | 0 | 64000 | 7767.875 | 0 | 24776.625 | 4834.125 | 1350000 | 24776.625 | 0
2021011107 | 2 | 0.68782 | 103173 | 0.17727 | 0 | 0.59789 | 7473.625 | 0 | 0 | 64000 | 7473.625 | 0 | 31699.375 | 6922.75 | 1343766.875 | 31699.375 | 0
2021011108 | 2 | 0.72295 | 108442.5 | 0.20366 | 0 | 0.5607 | 7008.75 | 0.01527 | 1221.6 | 64000 | 7008.75 | 1221.6 | 36212.15 | 4512.775 | 1333020.975 | 36212.15 | 0
2021011109 | 2 | 0.73357 | 110035.5 | 0.22535 | 0 | 0.56549 | 7068.625 | 0.07972 | 6377.6 | 64000 | 7068.625 | 6377.6 | 32589.275 | -3622.875 | 1325897.95 | 32589.275 | 0
2021011110 | 2 | 0.72979 | 109468.5 | 0.2952 | 0 | 0.55716 | 6964.5 | 0.12961 | 10368.8 | 64000 | 6964.5 | 10368.8 | 28135.2 | -4454.075 | 1323229 | 28135.2 | 0
2021011111 | 2 | 0.71977 | 107965.5 | 0.24348 | 0 | 0.5255 | 6568.75 | 0.17667 | 14133.6 | 64000 | 6568.75 | 14133.6 | 23263.15 | -4872.05 | 1325432.1 | 23263.15 | 0
2021011112 | 2 | 0.71042 | 106563 | 0.1912 | 0 | 0.4252 | 5315 | 0.21914 | 17531.2 | 64000 | 5315 | 17531.2 | 19716.8 | -3546.35 | 1331181.55 | 19716.8 | 0
2021011113 | 2 | 0.70445 | 105667.5 | 0.23118 | 0 | 0.27297 | 3412.125 | 0.2161 | 17288 | 64000 | 3412.125 | 17288 | 20967.375 | 1250.575 | 1335680.425 | 20967.375 | 0
2021011114 | 2 | 0.69696 | 104544 | 0.29902 | 0 | 0.18178 | 2272.25 | 0.18751 | 15000.8 | 64000 | 2272.25 | 15000.8 | 23270.95 | 2303.575 | 1337875.725 | 23270.95 | 0
2021011115 | 2 | 0.6884 | 103260 | 0.40891 | 0 | 0.17077 | 2134.625 | 0.12223 | 9778.4 | 64000 | 2134.625 | 9778.4 | 27346.975 | 4076.025 | 1335995 | 27346.975 | 0
2021011116 | 2 | 0.68302 | 102453 | 0.37574 | 0 | 0.12342 | 1542.75 | 0.05101 | 4080.8 | 64000 | 1542.75 | 4080.8 | 32829.45 | 5482.475 | 1328631.8 | 32829.45 | 0
2021011117 | 2 | 0.69083 | 103624.5 | 0.34913 | 0 | 0.1054 | 1317.5 | 0.00435 | 348 | 64000 | 1317.5 | 348 | 37959 | 5129.55 | 1316139.05 | 37959 | 0
2021011118 | 2 | 0.71934 | 107901 | 0.39681 | 0 | 0.10725 | 1340.625 | 0 | 0 | 64000 | 1340.625 | 0 | 42560.375 | 4601.375 | 1299044.925 | 42560.375 | 0
2021011119 | 2 | 0.72624 | 108936 | 0.42737 | 0 | 0.10578 | 1322.25 | 0 | 0 | 64000 | 1322.25 | 0 | 43613.75 | 1053.375 | 1280897.425 | 43613.75 | 0
2021011120 | 2 | 0.71689 | 107533.5 | 0.54504 | 0 | 0.13263 | 1657.875 | 0 | 0 | 64000 | 1657.875 | 0 | 41875.625 | -1738.125 | 1264488.05 | 41875.625 | 0
2021011121 | 2 | 0.70198 | 105297 | 0.55199 | 0 | 0.15308 | 1913.5 | 0 | 0 | 64000 | 1913.5 | 0 | 39383.5 | -2492.125 | 1250570.8 | 39383.5 | 0
2021011122 | 2 | 0.68128 | 102192 | 0.53316 | 0 | 0.16105 | 2013.125 | 0 | 0 | 64000 | 2013.125 | 0 | 36178.875 | -3204.625 | 1239858.175 | 36178.875 | 0
2021011123 | 2 | 0.65479 | 98218.5 | 0.57343 | 0 | 0.1727 | 2158.75 | 0 | 0 | 64000 | 2158.75 | 0 | 32059.75 | -4119.125 | 1233264.675 | 32059.75 | 0
2021011124 | 2 | 0.62866 | 94299 | 0.6476 | 0 | 0.19706 | 2463.25 | 0 | 0 | 64000 | 2463.25 | 0 | 27835.75 | -4224 | 1230895.175 | 27835.75 | 0
2021011201 | 3 | 0.609 | 91350 | 0.71062 | 0 | 0.23982 | 2997.75 | 0 | 0 | 64000 | 2997.75 | 0 | 24352.25 | -3483.5 | 1232009.175 | 24352.25 | 0
2021011202 | 3 | 0.59992 | 89988 | 0.69171 | 0 | 0.27315 | 3414.375 | 0 | 0 | 64000 | 3414.375 | 0 | 22573.625 | -1778.625 | 1234901.8 | 22573.625 | 0
2021011203 | 3 | 0.59728 | 89592 | 0.66107 | 0 | 0.29516 | 3689.5 | 0 | 0 | 64000 | 3689.5 | 0 | 21902.5 | -671.125 | 1238465.55 | 21902.5 | 0
2021011204 | 3 | 0.59997 | 89995.5 | 0.57392 | 0 | 0.31535 | 3941.875 | 0 | 0 | 64000 | 3941.875 | 0 | 22053.625 | 151.125 | 1241878.175 | 22053.625 | 0
2021011205 | 3 | 0.61435 | 92152.5 | 0.53617 | 0 | 0.28702 | 3587.75 | 0 | 0 | 64000 | 3587.75 | 0 | 24564.75 | 2511.125 | 1242779.675 | 24564.75 | 0
2021011206 | 3 | 0.6446 | 96690 | 0.47669 | 0 | 0.27001 | 3375.125 | 0 | 0 | 64000 | 3375.125 | 0 | 29314.875 | 4750.125 | 1238931.05 | 29314.875 | 0
2021011207 | 3 | 0.69076 | 103614 | 0.50458 | 0 | 0.26128 | 3266 | 0 | 0 | 64000 | 3266 | 0 | 36348 | 7033.125 | 1228049.3 | 36348 | 0
2021011208 | 3 | 0.72908 | 109362 | 0.55315 | 0 | 0.2795 | 3493.75 | 0.05053 | 4042.4 | 64000 | 3493.75 | 4042.4 | 37825.85 | 1477.85 | 1215689.7 | 37825.85 | 0
2021011209 | 3 | 0.73435 | 110152.5 | 0.4841 | 0 | 0.33863 | 4232.875 | 0.30481 | 24384.8 | 64000 | 4232.875 | 24384.8 | 17534.825 | -20291.025 | 1223621.125 | 17534.825 | 0
2021011210 | 3 | 0.7153 | 107295 | 0.39014 | 0 | 0.37328 | 4666 | 0.49693 | 39754.4 | 64000 | 4666 | 38629 | 0 | -17534.825 | 1249087.375 | 0 | 0
2021011211 | 3 | 0.69399 | 104098.5 | 0.34023 | 0 | 0.40418 | 5052.25 | 0.56003 | 44802.4 | 64000 | 5052.25 | 35046.25 | 0 | 0 | 1274553.625 | 0 | 0
2021011212 | 3 | 0.67692 | 101538 | 0.28246 | 0 | 0.45176 | 5647 | 0.5736 | 45888 | 64000 | 5647 | 31891 | 0 | 0 | 1300019.875 | 0 | 0
2021011213 | 3 | 0.66348 | 99522 | 0.26578 | 0 | 0.4596 | 5745 | 0.59832 | 47865.6 | 64000 | 5745 | 29777 | 0 | 0 | 1325486.125 | 0 | 0
2021011214 | 3 | 0.64902 | 97353 | 0.24372 | 0 | 0.42966 | 5370.75 | 0.62282 | 49825.6 | 64000 | 5370.75 | 27982.25 | 0 | 0 | 1350000 | 0 | 0
2021011215 | 3 | 0.63679 | 95518.5 | 0.27633 | 0 | 0.4241 | 5301.25 | 0.56757 | 45405.6 | 64000 | 5301.25 | 26217.25 | 0 | 0 | 1350000 | 0 | 0
2021011216 | 3 | 0.63488 | 95232 | 0.33348 | 0 | 0.44361 | 5545.125 | 0.29152 | 23321.6 | 64000 | 5545.125 | 23321.6 | 2365.275 | 2365.275 | 1350000 | 2365.275 | 0
2021011217 | 3 | 0.65059 | 97588.5 | 0.33454 | 0 | 0.44591 | 5573.875 | 0.02562 | 2049.6 | 64000 | 5573.875 | 2049.6 | 25965.025 | 23599.75 | 1349501.225 | 25965.025 | 0
2021011218 | 3 | 0.69089 | 103633.5 | 0.296 | 0 | 0.46893 | 5861.625 | 0 | 0 | 64000 | 5861.625 | 0 | 33771.875 | 7806.85 | 1341195.6 | 33771.875 | 0
2021011219 | 3 | 0.7095 | 106425 | 0.32278 | 0 | 0.44489 | 5561.125 | 0 | 0 | 64000 | 5561.125 | 0 | 36863.875 | 3092 | 1329797.975 | 36863.875 | 0
2021011220 | 3 | 0.70507 | 105760.5 | 0.35019 | 0 | 0.43357 | 5419.625 | 0 | 0 | 64000 | 5419.625 | 0 | 36340.875 | -523 | 1318923.35 | 36340.875 | 0
2021011221 | 3 | 0.69467 | 104200.5 | 0.40057 | 0 | 0.40527 | 5065.875 | 0 | 0 | 64000 | 5065.875 | 0 | 35134.625 | -1206.25 | 1309254.975 | 35134.625 | 0
2021011222 | 3 | 0.67622 | 101433 | 0.4589 | 0 | 0.38163 | 4770.375 | 0 | 0 | 64000 | 4770.375 | 0 | 32662.625 | -2472 | 1302058.6 | 32662.625 | 0
2021011223 | 3 | 0.64883 | 97324.5 | 0.5424 | 0 | 0.37137 | 4642.125 | 0 | 0 | 64000 | 4642.125 | 0 | 28682.375 | -3980.25 | 1298842.475 | 28682.375 | 0
2021011224 | 3 | 0.62385 | 93577.5 | 0.54346 | 0 | 0.38219 | 4777.375 | 0 | 0 | 64000 | 4777.375 | 0 | 24800.125 | -3882.25 | 1299508.6 | 24800.125 | 0
2021011301 | 4 | 0.60677 | 91015.5 | 0.52933 | 0 | 0.37324 | 4665.5 | 0 | 0 | 64000 | 4665.5 | 0 | 22350 | -2450.125 | 1302624.85 | 22350 | 0
2021011302 | 4 | 0.59848 | 89772 | 0.56708 | 0 | 0.37535 | 4691.875 | 0 | 0 | 64000 | 4691.875 | 0 | 21080.125 | -1269.875 | 1307010.975 | 21080.125 | 0
2021011303 | 4 | 0.59596 | 89394 | 0.53689 | 0 | 0.34991 | 4373.875 | 0 | 0 | 64000 | 4373.875 | 0 | 21020.125 | -60 | 1311457.1 | 21020.125 | 0
2021011304 | 4 | 0.59945 | 89917.5 | 0.42507 | 0 | 0.31306 | 3913.25 | 0 | 0 | 64000 | 3913.25 | 0 | 22004.25 | 984.125 | 1314919.1 | 22004.25 | 0
2021011305 | 4 | 0.61312 | 91968 | 0.37898 | 0 | 0.26433 | 3304.125 | 0 | 0 | 64000 | 3304.125 | 0 | 24663.875 | 2659.625 | 1315721.475 | 24663.875 | 0
2021011306 | 4 | 0.64277 | 96415.5 | 0.39938 | 0 | 0.20338 | 2542.25 | 0 | 0 | 64000 | 2542.25 | 0 | 29873.25 | 5209.375 | 1311314.475 | 29873.25 | 0
2021011307 | 4 | 0.68866 | 103299 | 0.43336 | 0 | 0.15534 | 1941.75 | 0 | 0 | 64000 | 1941.75 | 0 | 37357.25 | 7484 | 1299423.475 | 37357.25 | 0
2021011308 | 4 | 0.72386 | 108579 | 0.48883 | 0 | 0.13884 | 1735.5 | 0.02534 | 2027.2 | 64000 | 1735.5 | 2027.2 | 40816.3 | 3459.05 | 1284073.425 | 40816.3 | 0
2021011309 | 4 | 0.72695 | 109042.5 | 0.44145 | 0 | 0.13248 | 1656 | 0.12543 | 10034.4 | 64000 | 1656 | 10034.4 | 33352.1 | -7464.2 | 1276187.575 | 33352.1 | 0
2021011310 | 4 | 0.70302 | 105453 | 0.4101 | 0 | 0.12454 | 1556.75 | 0.16501 | 13200.8 | 64000 | 1556.75 | 13200.8 | 26695.45 | -6656.65 | 1274958.375 | 26695.45 | 0
2021011311 | 4 | 0.67634 | 101451 | 0.51913 | 0 | 0.10865 | 1358.125 | 0.13463 | 10770.4 | 64000 | 1358.125 | 10770.4 | 25322.475 | -1372.975 | 1275102.15 | 25322.475 | 0
2021011312 | 4 | 0.65319 | 97978.5 | 0.63091 | 0 | 0.12428 | 1553.5 | 0.13036 | 10428.8 | 64000 | 1553.5 | 10428.8 | 21996.2 | -3326.275 | 1278572.2 | 21996.2 | 0
2021011313 | 4 | 0.63758 | 95637 | 0.62383 | 0 | 0.13408 | 1676 | 0.11628 | 9302.4 | 64000 | 1676 | 9302.4 | 20658.6 | -1337.6 | 1283379.85 | 20658.6 | 0
2021011314 | 4 | 0.62505 | 93757.5 | 0.57842 | 0 | 0.14137 | 1767.125 | 0.0817 | 6536 | 64000 | 1767.125 | 6536 | 21454.375 | 795.775 | 1287391.725 | 21454.375 | 0
2021011315 | 4 | 0.61542 | 92313 | 0.53991 | 0 | 0.14527 | 1815.875 | 0.04628 | 3702.4 | 64000 | 1815.875 | 3702.4 | 22794.725 | 1340.35 | 1290063.25 | 22794.725 | 0
2021011316 | 4 | 0.61375 | 92062.5 | 0.46231 | 0 | 0.14771 | 1846.375 | 0.01539 | 1231.2 | 64000 | 1846.375 | 1231.2 | 24984.925 | 2190.2 | 1290544.575 | 24984.925 | 0
2021011317 | 4 | 0.62948 | 94422 | 0.46248 | 0 | 0.1488 | 1860 | 0.00015 | 12 | 64000 | 1860 | 12 | 28550 | 3565.075 | 1287460.825 | 28550 | 0
2021011318 | 4 | 0.66771 | 100156.5 | 0.58921 | 0 | 0.15575 | 1946.875 | 0 | 0 | 64000 | 1946.875 | 0 | 34209.625 | 5659.625 | 1278717.45 | 34209.625 | 0
2021011319 | 4 | 0.685 | 102750 | 0.67145 | 0 | 0.17502 | 2187.75 | 0 | 0 | 64000 | 2187.75 | 0 | 36562.25 | 2352.625 | 1267621.45 | 36562.25 | 0
2021011320 | 4 | 0.68 | 102000 | 0.7116 | 0 | 0.17418 | 2177.25 | 0 | 0 | 64000 | 2177.25 | 0 | 35822.75 | -739.5 | 1257264.95 | 35822.75 | 0
2021011321 | 4 | 0.66842 | 100263 | 0.73126 | 0 | 0.18598 | 2324.75 | 0 | 0 | 64000 | 2324.75 | 0 | 33938.25 | -1884.5 | 1248792.95 | 33938.25 | 0
2021011322 | 4 | 0.64955 | 97432.5 | 0.77059 | 0 | 0.21555 | 2694.375 | 0 | 0 | 64000 | 2694.375 | 0 | 30738.125 | -3200.125 | 1243521.075 | 30738.125 | 0
2021011323 | 4 | 0.62307 | 93460.5 | 0.74173 | 0 | 0.24714 | 3089.25 | 0 | 0 | 64000 | 3089.25 | 0 | 26371.25 | -4366.875 | 1242616.075 | 26371.25 | 0
2021011324 | 4 | 0.59578 | 89367 | 0.68492 | 0 | 0.26509 | 3313.625 | 0 | 0 | 64000 | 3313.625 | 0 | 22053.375 | -4317.875 | 1246028.95 | 22053.375 | 0
2021011401 | 5 | 0.57834 | 86751 | 0.71179 | 0 | 0.27851 | 3481.375 | 0 | 0 | 64000 | 3481.375 | 0 | 19269.625 | -2783.75 | 1252225.575 | 19269.625 | 0
2021011402 | 5 | 0.56879 | 85318.5 | 0.70133 | 0 | 0.30786 | 3848.25 | 0 | 0 | 64000 | 3848.25 | 0 | 17470.25 | -1799.375 | 1260221.575 | 17470.25 | 0
2021011403 | 5 | 0.5653 | 84795 | 0.64284 | 0 | 0.31615 | 3951.875 | 0 | 0 | 64000 | 3951.875 | 0 | 16843.125 | -627.125 | 1268844.7 | 16843.125 | 0
2021011404 | 5 | 0.56815 | 85222.5 | 0.62703 | 0 | 0.37224 | 4653 | 0 | 0 | 64000 | 4653 | 0 | 16569.5 | -273.625 | 1277741.45 | 16569.5 | 0
2021011405 | 5 | 0.58009 | 87013.5 | 0.60791 | 0 | 0.39884 | 4985.5 | 0 | 0 | 64000 | 4985.5 | 0 | 18028 | 1458.5 | 1285179.7 | 18028 | 0
2021011406 | 5 | 0.60958 | 91437 | 0.50616 | 0 | 0.41697 | 5212.125 | 0 | 0 | 64000 | 5212.125 | 0 | 22224.875 | 4196.875 | 1288421.075 | 22224.875 | 0
2021011407 | 5 | 0.65413 | 98119.5 | 0.4101 | 0 | 0.41664 | 5208 | 0 | 0 | 64000 | 5208 | 0 | 28911.5 | 6686.625 | 1284975.825 | 28911.5 | 0
2021011408 | 5 | 0.6913 | 103695 | 0.32325 | 0 | 0.45023 | 5627.875 | 0.01012 | 809.6 | 64000 | 5627.875 | 809.6 | 33257.525 | 4346.025 | 1277184.55 | 33257.525 | 0
2021011409 | 5 | 0.69687 | 104530.5 | 0.24616 | 0 | 0.45632 | 5704 | 0.04494 | 3595.2 | 64000 | 5704 | 3595.2 | 31231.3 | -2026.225 | 1271419.5 | 31231.3 | 0
2021011410 | 5 | 0.67973 | 101959.5 | 0.19954 | 0 | 0.45258 | 5657.25 | 0.06649 | 5319.2 | 64000 | 5657.25 | 5319.2 | 26983.05 | -4248.25 | 1269902.7 | 26983.05 | 0
2021011411 | 5 | 0.66154 | 99231 | 0.14732 | 0 | 0.44843 | 5605.375 | 0.09857 | 7885.6 | 64000 | 5605.375 | 7885.6 | 21740.025 | -5243.025 | 1273628.925 | 21740.025 | 0
2021011412 | 5 | 0.64306 | 96459 | 0.0542 | 0 | 0.41494 | 5186.75 | 0.15671 | 12536.8 | 64000 | 5186.75 | 12536.8 | 14735.45 | -7004.575 | 1284359.725 | 14735.45 | 0
2021011413 | 5 | 0.62687 | 94030.5 | 0.03682 | 0 | 0.35543 | 4442.875 | 0.15982 | 12785.6 | 64000 | 4442.875 | 12785.6 | 12802.025 | -1933.425 | 1297023.95 | 12802.025 | 0
2021011414 | 5 | 0.61232 | 91848 | 0.02304 | 0 | 0.30831 | 3853.875 | 0.12734 | 10187.2 | 64000 | 3853.875 | 10187.2 | 13806.925 | 1004.9 | 1308683.275 | 13806.925 | 0
2021011415 | 5 | 0.60217 | 90325.5 | 0.00495 | 0 | 0.29118 | 3639.75 | 0.08049 | 6439.2 | 64000 | 3639.75 | 6439.2 | 16246.55 | 2439.625 | 1317902.975 | 16246.55 | 0
2021011416 | 5 | 0.60112 | 90168 | 0.00623 | 0 | 0.27258 | 3407.25 | 0.04041 | 3232.8 | 64000 | 3407.25 | 3232.8 | 19527.95 | 3281.4 | 1323841.275 | 19527.95 | 0
2021011417 | 5 | 0.61608 | 92412 | 0.00625 | 0 | 0.26854 | 3356.75 | 0.00307 | 245.6 | 64000 | 3356.75 | 245.6 | 24809.65 | 5281.7 | 1324497.875 | 24809.65 | 0
2021011418 | 5 | 0.65156 | 97734 | 0.00668 | 0 | 0.24585 | 3073.125 | 0 | 0 | 64000 | 3073.125 | 0 | 30660.875 | 5851.225 | 1319303.25 | 30660.875 | 0
2021011419 | 5 | 0.66615 | 99922.5 | 0.02021 | 0 | 0.22221 | 2777.625 | 0 | 0 | 64000 | 2777.625 | 0 | 33144.875 | 2484 | 1311624.625 | 33144.875 | 0
2021011420 | 5 | 0.6595 | 98925 | 0.09847 | 0 | 0.25622 | 3202.75 | 0 | 0 | 64000 | 3202.75 | 0 | 31722.25 | -1422.625 | 1305368.625 | 31722.25 | 0
2021011421 | 5 | 0.65044 | 97566 | 0.20096 | 0 | 0.25411 | 3176.375 | 0 | 0 | 64000 | 3176.375 | 0 | 30389.625 | -1332.625 | 1300445.25 | 30389.625 | 0
2021011422 | 5 | 0.63216 | 94824 | 0.28598 | 0 | 0.259 | 3237.5 | 0 | 0 | 64000 | 3237.5 | 0 | 27586.5 | -2803.125 | 1298325 | 27586.5 | 0
2021011423 | 5 | 0.60649 | 90973.5 | 0.41029 | 0 | 0.26737 | 3342.125 | 0 | 0 | 64000 | 3342.125 | 0 | 23631.375 | -3955.125 | 1300159.875 | 23631.375 | 0
2021011424 | 5 | 0.58004 | 87006 | 0.48832 | 0 | 0.26032 | 3254 | 0 | 0 | 64000 | 3254 | 0 | 19752 | -3879.375 | 1305874.125 | 19752 | 0
2021011501 | 6 | 0.56264 | 84396 | 0.51429 | 0 | 0.25894 | 3236.75 | 0 | 0 | 64000 | 3236.75 | 0 | 17159.25 | -2592.75 | 1314181.125 | 17159.25 | 0
2021011502 | 6 | 0.55342 | 83013 | 0.5963 | 0 | 0.26714 | 3339.25 | 0 | 0 | 64000 | 3339.25 | 0 | 15673.75 | -1485.5 | 1323973.625 | 15673.75 | 0
2021011503 | 6 | 0.55029 | 82543.5 | 0.6753 | 0 | 0.29792 | 3724 | 0 | 0 | 64000 | 3724 | 0 | 14819.5 | -854.25 | 1334620.375 | 14819.5 | 0
2021011504 | 6 | 0.55367 | 83050.5 | 0.71515 | 0 | 0.28522 | 3565.25 | 0 | 0 | 64000 | 3565.25 | 0 | 15485.25 | 665.75 | 1344601.375 | 15485.25 | 0
2021011505 | 6 | 0.56675 | 85012.5 | 0.73083 | 0 | 0.25877 | 3234.625 | 0 | 0 | 64000 | 3234.625 | 0 | 17777.875 | 2292.625 | 1350000 | 17777.875 | 0
2021011506 | 6 | 0.59447 | 89170.5 | 0.81233 | 0 | 0.22181 | 2772.625 | 0 | 0 | 64000 | 2772.625 | 0 | 22397.875 | 4620 | 1350000 | 22397.875 | 0
2021011507 | 6 | 0.63565 | 95347.5 | 0.82397 | 0 | 0.17057 | 2132.125 | 0 | 0 | 64000 | 2132.125 | 0 | 29215.375 | 6817.5 | 1346250.875 | 29215.375 | 0
2021011508 | 6 | 0.67113 | 100669.5 | 0.86861 | 0 | 0.12236 | 1529.5 | 0.01828 | 1462.4 | 64000 | 1529.5 | 1462.4 | 33677.6 | 4462.225 | 1338039.525 | 33677.6 | 0
2021011509 | 6 | 0.68086 | 102129 | 0.92154 | 0 | 0.10687 | 1335.875 | 0.12711 | 10168.8 | 64000 | 1335.875 | 10168.8 | 26624.325 | -7053.275 | 1336881.45 | 26624.325 | 0
2021011510 | 6 | 0.6719 | 100785 | 0.95187 | 0 | 0.09796 | 1224.5 | 0.24945 | 19956 | 64000 | 1224.5 | 19956 | 15604.5 | -11019.825 | 1346743.2 | 15604.5 | 0
2021011511 | 6 | 0.66146 | 99219 | 0.947 | 0 | 0.08083 | 1010.375 | 0.36001 | 28800.8 | 64000 | 1010.375 | 28800.8 | 5407.825 | -10196.675 | 1350000 | 5407.825 | 0
2021011512 | 6 | 0.65123 | 97684.5 | 0.9553 | 0 | 0.07431 | 928.875 | 0.41035 | 32828 | 64000 | 928.875 | 32755.625 | 0 | -5407.825 | 1350000 | 0 | 0
2021011513 | 6 | 0.6421 | 96315 | 0.97927 | 0 | 0.08456 | 1057 | 0.43383 | 34706.4 | 64000 | 1057 | 31258 | 0 | 0 | 1350000 | 0 | 0
2021011514 | 6 | 0.63623 | 95434.5 | 0.97696 | 0 | 0.10306 | 1288.25 | 0.42902 | 34321.6 | 64000 | 1288.25 | 30146.25 | 0 | 0 | 1350000 | 0 | 0
2021011515 | 6 | 0.63108 | 94662 | 0.96424 | 0 | 0.12239 | 1529.875 | 0.3664 | 29312 | 64000 | 1529.875 | 29132.125 | 0 | 0 | 1350000 | 0 | 0
2021011516 | 6 | 0.62978 | 94467 | 0.89722 | 0 | 0.13948 | 1743.5 | 0.14504 | 11603.2 | 64000 | 1743.5 | 11603.2 | 17120.3 | 17120.3 | 1350000 | 17120.3 | 0
2021011517 | 6 | 0.63643 | 95464.5 | 0.73214 | 0 | 0.17101 | 2137.625 | 0.01532 | 1225.6 | 64000 | 2137.625 | 1225.6 | 28101.275 | 10980.975 | 1347364.975 | 28101.275 | 0
2021011518 | 6 | 0.65682 | 98523 | 0.63243 | 0 | 0.18585 | 2323.125 | 0 | 0 | 64000 | 2323.125 | 0 | 32199.875 | 4098.6 | 1340631.35 | 32199.875 | 0
2021011519 | 6 | 0.66082 | 99123 | 0.59167 | 0 | 0.21146 | 2643.25 | 0 | 0 | 64000 | 2643.25 | 0 | 32479.75 | 279.875 | 1333617.85 | 32479.75 | 0
2021011520 | 6 | 0.6499 | 97485 | 0.57292 | 0 | 0.23908 | 2988.5 | 0 | 0 | 64000 | 2988.5 | 0 | 30496.5 | -1983.25 | 1328587.6 | 30496.5 | 0
2021011521 | 6 | 0.63557 | 95335.5 | 0.5794 | 0 | 0.25016 | 3127 | 0 | 0 | 64000 | 3127 | 0 | 28208.5 | -2288 | 1325845.35 | 28208.5 | 0
2021011522 | 6 | 0.61689 | 92533.5 | 0.5787 | 0 | 0.31013 | 3876.625 | 0 | 0 | 64000 | 3876.625 | 0 | 24656.875 | -3551.625 | 1326654.725 | 24656.875 | 0
2021011523 | 6 | 0.59209 | 88813.5 | 0.48854 | 0 | 0.41128 | 5141 | 0 | 0 | 64000 | 5141 | 0 | 19672.5 | -4984.375 | 1332448.475 | 19672.5 | 0
2021011524 | 6 | 0.5657 | 84855 | 0.40371 | 0 | 0.52984 | 6623 | 0 | 0 | 64000 | 6623 | 0 | 14232 | -5440.5 | 1343682.725 | 14232 | 0
2021011601 | 7 | 0.54666 | 81999 | 0.45469 | 0 | 0.63725 | 7965.625 | 0 | 0 | 64000 | 7965.625 | 0 | 10033.375 | -4198.625 | 1350000 | 10033.375 | 0
2021011602 | 7 | 0.53592 | 80388 | 0.43656 | 0 | 0.67165 | 8395.625 | 0 | 0 | 64000 | 8395.625 | 0 | 7992.375 | -2041 | 1350000 | 7992.375 | 0
2021011603 | 7 | 0.52972 | 79458 | 0.30869 | 0 | 0.66279 | 8284.875 | 0 | 0 | 64000 | 8284.875 | 0 | 7173.125 | -819.25 | 1350000 | 7173.125 | 0
2021011604 | 7 | 0.52923 | 79384.5 | 0.28527 | 0 | 0.62261 | 7782.625 | 0 | 0 | 64000 | 7782.625 | 0 | 7601.875 | 428.75 | 1350000 | 7601.875 | 0
2021011605 | 7 | 0.53473 | 80209.5 | 0.32328 | 0 | 0.57409 | 7176.125 | 0 | 0 | 64000 | 7176.125 | 0 | 9033.375 | 1431.5 | 1350000 | 9033.375 | 0
2021011606 | 7 | 0.54899 | 82348.5 | 0.29342 | 0 | 0.56217 | 7027.125 | 0 | 0 | 64000 | 7027.125 | 0 | 11321.375 | 2288 | 1350000 | 11321.375 | 0
2021011607 | 7 | 0.56899 | 85348.5 | 0.29857 | 0 | 0.61825 | 7728.125 | 0 | 0 | 64000 | 7728.125 | 0 | 13620.375 | 2299 | 1350000 | 13620.375 | 0
2021011608 | 7 | 0.59279 | 88918.5 | 0.31594 | 0 | 0.70269 | 8783.625 | 0.03524 | 2819.2 | 64000 | 8783.625 | 2819.2 | 13315.675 | -304.7 | 1350000 | 13315.675 | 0
2021011609 | 7 | 0.60729 | 91093.5 | 0.25156 | 0 | 0.75279 | 9409.875 | 0.23374 | 18699.2 | 64000 | 9409.875 | 17683.625 | 0 | -13315.675 | 1350000 | 0 | 0
2021011610 | 7 | 0.61403 | 92104.5 | 0.23205 | 0 | 0.77054 | 9631.75 | 0.42426 | 33940.8 | 64000 | 9631.75 | 18472.75 | 0 | 0 | 1350000 | 0 | 0
2021011611 | 7 | 0.61564 | 92346 | 0.20889 | 0 | 0.77233 | 9654.125 | 0.46941 | 37552.8 | 64000 | 9654.125 | 18691.875 | 0 | 0 | 1350000 | 0 | 0
2021011612 | 7 | 0.60988 | 91482 | 0.23556 | 0 | 0.76148 | 9518.5 | 0.48902 | 39121.6 | 64000 | 9518.5 | 17963.5 | 0 | 0 | 1350000 | 0 | 0
2021011613 | 7 | 0.60361 | 90541.5 | 0.28571 | 0 | 0.77594 | 9699.25 | 0.48647 | 38917.6 | 64000 | 9699.25 | 16842.25 | 0 | 0 | 1350000 | 0 | 0
2021011614 | 7 | 0.59859 | 89788.5 | 0.29372 | 0 | 0.77818 | 9727.25 | 0.50054 | 40043.2 | 64000 | 9727.25 | 16061.25 | 0 | 0 | 1350000 | 0 | 0
2021011615 | 7 | 0.59694 | 89541 | 0.42616 | 0 | 0.79679 | 9959.875 | 0.48939 | 39151.2 | 64000 | 9959.875 | 15581.125 | 0 | 0 | 1350000 | 0 | 0
2021011616 | 7 | 0.60161 | 90241.5 | 0.59792 | 0 | 0.79336 | 9917 | 0.25676 | 20540.8 | 64000 | 9917 | 16324.5 | 0 | 0 | 1350000 | 0 | 0
2021011617 | 7 | 0.61758 | 92637 | 0.61634 | 0 | 0.77431 | 9678.875 | 0.02436 | 1948.8 | 64000 | 9678.875 | 1948.8 | 17009.325 | 17009.325 | 1350000 | 17009.325 | 0
2021011618 | 7 | 0.64755 | 97132.5 | 0.68323 | 0 | 0.75839 | 9479.875 | 0 | 0 | 64000 | 9479.875 | 0 | 23652.625 | 6643.3 | 1350000 | 23652.625 | 0
2021011619 | 7 | 0.65738 | 98607 | 0.7488 | 0 | 0.77099 | 9637.375 | 0 | 0 | 64000 | 9637.375 | 0 | 24969.625 | 1317 | 1350000 | 24969.625 | 0
2021011620 | 7 | 0.65071 | 97606.5 | 0.77995 | 0 | 0.76086 | 9510.75 | 0 | 0 | 64000 | 9510.75 | 0 | 24095.75 | -873.875 | 1350000 | 24095.75 | 0
2021011621 | 7 | 0.6413 | 96195 | 0.81475 | 0 | 0.7479 | 9348.75 | 0 | 0 | 64000 | 9348.75 | 0 | 22846.25 | -1249.5 | 1350000 | 22846.25 | 0
2021011622 | 7 | 0.6263 | 93945 | 0.86192 | 0 | 0.73952 | 9244 | 0 | 0 | 64000 | 9244 | 0 | 20701 | -2145.25 | 1350000 | 20701 | 0
2021011623 | 7 | 0.60497 | 90745.5 | 0.89668 | 0 | 0.67225 | 8403.125 | 0 | 0 | 64000 | 8403.125 | 0 | 18342.375 | -2358.625 | 1350000 | 18342.375 | 0
2021011624 | 7 | 0.58218 | 87327 | 0.92074 | 0 | 0.61066 | 7633.25 | 0 | 0 | 64000 | 7633.25 | 0 | 15693.75 | -2648.625 | 1350000 | 15693.75 | 0
2021011701 | 1 | 0.56403 | 84604.5 | 0.94208 | 0 | 0.58177 | 7272.125 | 0 | 0 | 64000 | 7272.125 | 0 | 13332.375 | -2361.375 | 1350000 | 13332.375 | 0
2021011702 | 1 | 0.55247 | 82870.5 | 0.95292 | 0 | 0.60773 | 7596.625 | 0 | 0 | 64000 | 7596.625 | 0 | 11273.875 | -2058.5 | 1350000 | 11273.875 | 0
2021011703 | 1 | 0.54518 | 81777 | 0.96186 | 0 | 0.68985 | 8623.125 | 0 | 0 | 64000 | 8623.125 | 0 | 9153.875 | -2120 | 1350000 | 9153.875 | 0
2021011704 | 1 | 0.54308 | 81462 | 0.93405 | 0 | 0.72563 | 9070.375 | 0 | 0 | 64000 | 9070.375 | 0 | 8391.625 | -762.25 | 1350000 | 8391.625 | 0
2021011705 | 1 | 0.54646 | 81969 | 0.90812 | 0 | 0.77291 | 9661.375 | 0 | 0 | 64000 | 9661.375 | 0 | 8307.625 | -84 | 1350000 | 8307.625 | 0
2021011706 | 1 | 0.55563 | 83344.5 | 0.89304 | 0 | 0.78902 | 9862.75 | 0 | 0 | 64000 | 9862.75 | 0 | 9481.75 | 1174.125 | 1350000 | 9481.75 | 0
2021011707 | 1 | 0.56986 | 85479 | 0.89847 | 0 | 0.78777 | 9847.125 | 0 | 0 | 64000 | 9847.125 | 0 | 11631.875 | 2150.125 | 1350000 | 11631.875 | 0
2021011708 | 1 | 0.5854 | 87810 | 0.90176 | 0 | 0.77642 | 9705.25 | 0.04018 | 3214.4 | 64000 | 9705.25 | 3214.4 | 10890.35 | -741.525 | 1350000 | 10890.35 | 0
2021011709 | 1 | 0.59635 | 89452.5 | 0.87075 | 0 | 0.76199 | 9524.875 | 0.23256 | 18604.8 | 64000 | 9524.875 | 15927.625 | 0 | -10890.35 | 1350000 | 0 | 0
2021011710 | 1 | 0.60185 | 90277.5 | 0.85318 | 0 | 0.76452 | 9556.5 | 0.3741 | 29928 | 64000 | 9556.5 | 16721 | 0 | 0 | 1350000 | 0 | 0
2021011711 | 1 | 0.59962 | 89943 | 0.85197 | 0 | 0.76246 | 9530.75 | 0.44234 | 35387.2 | 64000 | 9530.75 | 16412.25 | 0 | 0 | 1350000 | 0 | 0
2021011712 | 1 | 0.59514 | 89271 | 0.81505 | 0 | 0.78132 | 9766.5 | 0.47631 | 38104.8 | 64000 | 9766.5 | 15504.5 | 0 | 0 | 1350000 | 0 | 0
2021011713 | 1 | 0.59282 | 88923 | 0.76163 | 0 | 0.79209 | 9901.125 | 0.49227 | 39381.6 | 64000 | 9901.125 | 15021.875 | 0 | 0 | 1350000 | 0 | 0
2021011714 | 1 | 0.591 | 88650 | 0.70635 | 0 | 0.80254 | 10031.75 | 0.49734 | 39787.2 | 64000 | 10031.75 | 14618.25 | 0 | 0 | 1350000 | 0 | 0
2021011715 | 1 | 0.58999 | 88498.5 | 0.59221 | 0 | 0.81112 | 10139 | 0.4284 | 34272 | 64000 | 10139 | 14359.5 | 0 | 0 | 1350000 | 0 | 0
2021011716 | 1 | 0.594 | 89100 | 0.53036 | 0 | 0.81562 | 10195.25 | 0.19044 | 15235.2 | 64000 | 10195.25 | 14904.75 | 0 | 0 | 1350000 | 0 | 0
2021011717 | 1 | 0.60915 | 91372.5 | 0.46913 | 0 | 0.81612 | 10201.5 | 0.0185 | 1480 | 64000 | 10201.5 | 1480 | 15691 | 15691 | 1350000 | 15691 | 0
2021011718 | 1 | 0.63693 | 95539.5 | 0.37303 | 0 | 0.77785 | 9723.125 | 0 | 0 | 64000 | 9723.125 | 0 | 21816.375 | 6125.375 | 1350000 | 21816.375 | 0
2021011719 | 1 | 0.64836 | 97254 | 0.35903 | 0 | 0.73851 | 9231.375 | 0 | 0 | 64000 | 9231.375 | 0 | 24022.625 | 2206.25 | 1350000 | 24022.625 | 0
2021011720 | 1 | 0.64013 | 96019.5 | 0.40454 | 0 | 0.73832 | 9229 | 0 | 0 | 64000 | 9229 | 0 | 22790.5 | -1232.125 | 1350000 | 22790.5 | 0
2021011721 | 1 | 0.62973 | 94459.5 | 0.39459 | 0 | 0.73739 | 9217.375 | 0 | 0 | 64000 | 9217.375 | 0 | 21242.125 | -1548.375 | 1350000 | 21242.125 | 0
2021011722 | 1 | 0.61231 | 91846.5 | 0.44171 | 0 | 0.7515 | 9393.75 | 0 | 0 | 64000 | 9393.75 | 0 | 18452.75 | -2789.375 | 1350000 | 18452.75 | 0
2021011723 | 1 | 0.59203 | 88804.5 | 0.46437 | 0 | 0.75679 | 9459.875 | 0 | 0 | 64000 | 9459.875 | 0 | 15344.625 | -3108.125 | 1350000 | 15344.625 | 0
2021011724 | 1 | 0.56955 | 85432.5 | 0.45371 | 0 | 0.76713 | 9589.125 | 0 | 0 | 64000 | 9589.125 | 0 | 11843.375 | -3501.25 | 1350000 | 11843.375 | 0
2021011801 | 2 | 0.55451 | 83176.5 | 0.50105 | 0 | 0.77511 | 9688.875 | 0 | 0 | 64000 | 9688.875 | 0 | 9487.625 | -2355.75 | 1350000 | 9487.625 | 0
2021011802 | 2 | 0.54676 | 82014 | 0.55894 | 0 | 0.75702 | 9462.75 | 0 | 0 | 64000 | 9462.75 | 0 | 8551.25 | -936.375 | 1350000 | 8551.25 | 0
2021011803 | 2 | 0.54362 | 81543 | 0.52307 | 0 | 0.71612 | 8951.5 | 0 | 0 | 64000 | 8951.5 | 0 | 8591.5 | 40.25 | 1350000 | 8591.5 | 0
2021011804 | 2 | 0.54785 | 82177.5 | 0.57779 | 0 | 0.67854 | 8481.75 | 0 | 0 | 64000 | 8481.75 | 0 | 9695.75 | 1104.25 | 1350000 | 9695.75 | 0
2021011805 | 2 | 0.56126 | 84189 | 0.51319 | 0 | 0.65361 | 8170.125 | 0 | 0 | 64000 | 8170.125 | 0 | 12018.875 | 2323.125 | 1350000 | 12018.875 | 0
2021011806 | 2 | 0.58659 | 87988.5 | 0.4741 | 0 | 0.60811 | 7601.375 | 0 | 0 | 64000 | 7601.375 | 0 | 16387.125 | 4368.25 | 1350000 | 16387.125 | 0
2021011807 | 2 | 0.62472 | 93708 | 0.44799 | 0 | 0.51437 | 6429.625 | 0 | 0 | 64000 | 6429.625 | 0 | 23278.375 | 6891.25 | 1350000 | 23278.375 | 0
2021011808 | 2 | 0.65714 | 98571 | 0.48397 | 0 | 0.39122 | 4890.25 | 0.04163 | 3330.4 | 64000 | 4890.25 | 3330.4 | 26350.35 | 3071.975 | 1349115.9 | 26350.35 | 0
2021011809 | 2 | 0.66794 | 100191 | 0.55819 | 0 | 0.25691 | 3211.375 | 0.31402 | 25121.6 | 64000 | 3211.375 | 25121.6 | 7858.025 | -18492.325 | 1350000 | 7858.025 | 0
2021011810 | 2 | 0.66749 | 100123.5 | 0.56952 | 0 | 0.20113 | 2514.125 | 0.53741 | 42992.8 | 64000 | 2514.125 | 33609.375 | 0 | -7858.025 | 1350000 | 0 | 0
2021011811 | 2 | 0.66388 | 99582 | 0.56867 | 0 | 0.21901 | 2737.625 | 0.57904 | 46323.2 | 64000 | 2737.625 | 32844.375 | 0 | 0 | 1350000 | 0 | 0
2021011812 | 2 | 0.66185 | 99277.5 | 0.60566 | 0 | 0.21569 | 2696.125 | 0.57478 | 45982.4 | 64000 | 2696.125 | 32581.375 | 0 | 0 | 1350000 | 0 | 0
2021011813 | 2 | 0.66004 | 99006 | 0.64108 | 0 | 0.22224 | 2778 | 0.5898 | 47184 | 64000 | 2778 | 32228 | 0 | 0 | 1350000 | 0 | 0
2021011814 | 2 | 0.65994 | 98991 | 0.66811 | 0 | 0.32693 | 4086.625 | 0.6174 | 49392 | 64000 | 4086.625 | 30904.375 | 0 | 0 | 1350000 | 0 | 0
2021011815 | 2 | 0.65814 | 98721 | 0.63863 | 0 | 0.43632 | 5454 | 0.57753 | 46202.4 | 64000 | 5454 | 29267 | 0 | 0 | 1350000 | 0 | 0
2021011816 | 2 | 0.65973 | 98959.5 | 0.61847 | 0 | 0.41146 | 5143.25 | 0.30865 | 24692 | 64000 | 5143.25 | 24692 | 5124.25 | 5124.25 | 1350000 | 5124.25 | 0
2021011817 | 2 | 0.67179 | 100768.5 | 0.6083 | 0 | 0.34924 | 4365.5 | 0.03359 | 2687.2 | 64000 | 4365.5 | 2687.2 | 29715.8 | 24591.55 | 1345750.45 | 29715.8 | 0
2021011818 | 2 | 0.70338 | 105507 | 0.59699 | 0 | 0.27141 | 3392.625 | 0 | 0 | 64000 | 3392.625 | 0 | 38114.375 | 8398.575 | 1333102.325 | 38114.375 | 0
2021011819 | 2 | 0.71211 | 106816.5 | 0.58813 | 0 | 0.23238 | 2904.75 | 0 | 0 | 64000 | 2904.75 | 0 | 39911.75 | 1797.375 | 1318656.825 | 39911.75 | 0
2021011820 | 2 | 0.7023 | 105345 | 0.60925 | 0 | 0.2298 | 2872.5 | 0 | 0 | 64000 | 2872.5 | 0 | 38472.5 | -1439.25 | 1305650.575 | 38472.5 | 0
2021011821 | 2 | 0.6868 | 103020 | 0.67028 | 0 | 0.25154 | 3144.25 | 0 | 0 | 64000 | 3144.25 | 0 | 35875.75 | -2596.75 | 1295241.075 | 35875.75 | 0
2021011822 | 2 | 0.66443 | 99664.5 | 0.70813 | 0 | 0.27016 | 3377 | 0 | 0 | 64000 | 3377 | 0 | 32287.5 | -3588.25 | 1288419.825 | 32287.5 | 0
2021011823 | 2 | 0.63512 | 95268 | 0.78676 | 0 | 0.24817 | 3102.125 | 0 | 0 | 64000 | 3102.125 | 0 | 28165.875 | -4121.625 | 1285720.2 | 28165.875 | 0
2021011824 | 2 | 0.60646 | 90969 | 0.77649 | 0 | 0.24254 | 3031.75 | 0 | 0 | 64000 | 3031.75 | 0 | 23937.25 | -4228.625 | 1287249.2 | 23937.25 | 0
2021011901 | 3 | 0.5879 | 88185 | 0.66951 | 0 | 0.25956 | 3244.5 | 0 | 0 | 64000 | 3244.5 | 0 | 20940.5 | -2996.75 | 1291774.95 | 20940.5 | 0
2021011902 | 3 | 0.57871 | 86806.5 | 0.71657 | 0 | 0.26782 | 3347.75 | 0 | 0 | 64000 | 3347.75 | 0 | 19458.75 | -1481.75 | 1297782.45 | 19458.75 | 0
2021011903 | 3 | 0.57612 | 86418 | 0.75483 | 0 | 0.25506 | 3188.25 | 0 | 0 | 64000 | 3188.25 | 0 | 19229.75 | -229 | 1304018.95 | 19229.75 | 0
2021011904 | 3 | 0.57926 | 86889 | 0.81634 | 0 | 0.2344 | 2930 | 0 | 0 | 64000 | 2930 | 0 | 19959 | 729.25 | 1309526.2 | 19959 | 0
2021011905 | 3 | 0.59127 | 88690.5 | 0.83353 | 0 | 0.21072 | 2634 | 0 | 0 | 64000 | 2634 | 0 | 22056.5 | 2097.5 | 1312935.95 | 22056.5 | 0
2021011906 | 3 | 0.62129 | 93193.5 | 0.75072 | 0 | 0.17155 | 2144.375 | 0 | 0 | 64000 | 2144.375 | 0 | 27049.125 | 4992.625 | 1311353.075 | 27049.125 | 0
2021011907 | 3 | 0.66847 | 100270.5 | 0.66965 | 0 | 0.13879 | 1734.875 | 0.00024 | 19.2 | 64000 | 1734.875 | 19.2 | 34516.425 | 7467.3 | 1302302.9 | 34516.425 | 0
2021011908 | 3 | 0.70489 | 105733.5 | 0.65388 | 0 | 0.1256 | 1570 | 0.05194 | 4155.2 | 64000 | 1570 | 4155.2 | 36008.3 | 1491.875 | 1291760.85 | 36008.3 | 0
2021011909 | 3 | 0.71139 | 106708.5 | 0.7246 | 0 | 0.14307 | 1788.375 | 0.35767 | 28613.6 | 64000 | 1788.375 | 28613.6 | 12306.525 | -23701.775 | 1304920.575 | 12306.525 | 0
2021011910 | 3 | 0.69598 | 104397 | 0.79853 | 0 | 0.16137 | 2017.125 | 0.56906 | 45524.8 | 64000 | 2017.125 | 38379.875 | 0 | -12306.525 | 1330386.825 | 0 | 0
2021011911 | 3 | 0.6805 | 102075 | 0.79462 | 0 | 0.19445 | 2430.625 | 0.5953 | 47624 | 64000 | 2430.625 | 35644.375 | 0 | 0 | 1350000 | 0 | 0
2021011912 | 3 | 0.66516 | 99774 | 0.78012 | 0 | 0.26537 | 3317.125 | 0.59451 | 47560.8 | 64000 | 3317.125 | 32456.875 | 0 | 0 | 1350000 | 0 | 0
2021011913 | 3 | 0.65542 | 98313 | 0.75116 | 0 | 0.34599 | 4324.875 | 0.60994 | 48795.2 | 64000 | 4324.875 | 29988.125 | 0 | 0 | 1350000 | 0 | 0
2021011914 | 3 | 0.6429 | 96435 | 0.80076 | 0 | 0.4529 | 5661.25 | 0.63256 | 50604.8 | 64000 | 5661.25 | 26773.75 | 0 | 0 | 1350000 | 0 | 0
2021011915 | 3 | 0.63133 | 94699.5 | 0.823 | 0 | 0.59492 | 7436.5 | 0.58752 | 47001.6 | 64000 | 7436.5 | 23263 | 0 | 0 | 1350000 | 0 | 0
2021011916 | 3 | 0.62943 | 94414.5 | 0.83423 | 0 | 0.6705 | 8381.25 | 0.31824 | 25459.2 | 64000 | 8381.25 | 22033.25 | 0 | 0 | 1350000 | 0 | 0
2021011917 | 3 | 0.64249 | 96373.5 | 0.77159 | 0 | 0.65689 | 8211.125 | 0.03605 | 2884 | 64000 | 8211.125 | 2884 | 21278.375 | 21278.375 | 1350000 | 21278.375 | 0
2021011918 | 3 | 0.67797 | 101695.5 | 0.68708 | 0 | 0.66856 | 8357 | 0 | 0 | 64000 | 8357 | 0 | 29338.5 | 8060.125 | 1346127.75 | 29338.5 | 0
2021011919 | 3 | 0.69633 | 104449.5 | 0.73913 | 0 | 0.66525 | 8315.625 | 0 | 0 | 64000 | 8315.625 | 0 | 32133.875 | 2795.375 | 1339460.125 | 32133.875 | 0
2021011920 | 3 | 0.69067 | 103600.5 | 0.74468 | 0 | 0.67273 | 8409.125 | 0 | 0 | 64000 | 8409.125 | 0 | 31191.375 | -942.5 | 1333735 | 31191.375 | 0
2021011921 | 3 | 0.67935 | 101902.5 | 0.65266 | 0 | 0.68048 | 8506 | 0 | 0 | 64000 | 8506 | 0 | 29396.5 | -1794.875 | 1329804.75 | 29396.5 | 0
2021011922 | 3 | 0.66056 | 99084 | 0.62316 | 0 | 0.69386 | 8673.25 | 0 | 0 | 64000 | 8673.25 | 0 | 26410.75 | -2985.75 | 1328860.25 | 26410.75 | 0
2021011923 | 3 | 0.63289 | 94933.5 | 0.6031 | 0 | 0.71739 | 8967.375 | 0 | 0 | 64000 | 8967.375 | 0 | 21966.125 | -4444.625 | 1332360.375 | 21966.125 | 0
2021011924 | 3 | 0.60763 | 91144.5 | 0.58812 | 0 | 0.73582 | 9197.75 | 0 | 0 | 64000 | 9197.75 | 0 | 17946.75 | -4019.375 | 1339879.875 | 17946.75 | 0
2021012001 | 4 | 0.58819 | 88228.5 | 0.58777 | 0 | 0.75157 | 9394.625 | 0 | 0 | 64000 | 9394.625 | 0 | 14833.875 | -3112.875 | 1350000 | 14833.875 | 0
2021012002 | 4 | 0.57614 | 86421 | 0.65667 | 0 | 0.77766 | 9720.75 | 0 | 0 | 64000 | 9720.75 | 0 | 12700.25 | -2133.625 | 1350000 | 12700.25 | 0
2021012003 | 4 | 0.57165 | 85747.5 | 0.57244 | 0 | 0.77732 | 9716.5 | 0 | 0 | 64000 | 9716.5 | 0 | 12031 | -669.25 | 1350000 | 12031 | 0
2021012004 | 4 | 0.57063 | 85594.5 | 0.66215 | 0 | 0.77943 | 9742.875 | 0 | 0 | 64000 | 9742.875 | 0 | 11851.625 | -179.375 | 1350000 | 11851.625 | 0
2021012005 | 4 | 0.58151 | 87226.5 | 0.75031 | 0 | 0.77572 | 9696.5 | 0 | 0 | 64000 | 9696.5 | 0 | 13530 | 1678.375 | 1350000 | 13530 | 0
2021012006 | 4 | 0.6091 | 91365 | 0.79655 | 0 | 0.74094 | 9261.75 | 0 | 0 | 64000 | 9261.75 | 0 | 18103.25 | 4573.25 | 1350000 | 18103.25 | 0
2021012007 | 4 | 0.6514 | 97710 | 0.84465 | 0 | 0.69702 | 8712.75 | 0 | 0 | 64000 | 8712.75 | 0 | 24997.25 | 6894 | 1350000 | 24997.25 | 0
2021012008 | 4 | 0.68754 | 103131 | 0.90269 | 0 | 0.65424 | 8178 | 0.05268 | 4214.4 | 64000 | 8178 | 4214.4 | 26738.6 | 1741.35 | 1348727.65 | 26738.6 | 0
2021012009 | 4 | 0.69379 | 104068.5 | 0.93323 | 0 | 0.65662 | 8207.75 | 0.36001 | 28800.8 | 64000 | 8207.75 | 28800.8 | 3059.95 | -23678.65 | 1350000 | 3059.95 | 0
2021012010 | 4 | 0.68812 | 103218 | 0.9519 | 0 | 0.67187 | 8398.375 | 0.5931 | 47448 | 64000 | 8398.375 | 30819.625 | 0 | -3059.95 | 1350000 | 0 | 0
2021012011 | 4 | 0.68079 | 102118.5 | 0.97384 | 0 | 0.64046 | 8005.75 | 0.62063 | 49650.4 | 64000 | 8005.75 | 30112.75 | 0 | 0 | 1350000 | 0 | 0
2021012012 | 4 | 0.67307 | 100960.5 | 0.97588 | 0 | 0.60754 | 7594.25 | 0.60825 | 48660 | 64000 | 7594.25 | 29366.25 | 0 | 0 | 1350000 | 0 | 0
2021012013 | 4 | 0.66458 | 99687 | 0.95551 | 0 | 0.60764 | 7595.5 | 0.61847 | 49477.6 | 64000 | 7595.5 | 28091.5 | 0 | 0 | 1350000 | 0 | 0
2021012014 | 4 | 0.6594 | 98910 | 0.96356 | 0 | 0.64373 | 8046.625 | 0.63894 | 51115.2 | 64000 | 8046.625 | 26863.375 | 0 | 0 | 1350000 | 0 | 0
2021012015 | 4 | 0.6491 | 97365 | 0.97351 | 0 | 0.66725 | 8340.625 | 0.59038 | 47230.4 | 64000 | 8340.625 | 25024.375 | 0 | 0 | 1350000 | 0 | 0
2021012016 | 4 | 0.64892 | 97338 | 0.9562 | 0 | 0.67643 | 8455.375 | 0.2641 | 21128 | 64000 | 8455.375 | 21128 | 3754.625 | 3754.625 | 1350000 | 3754.625 | 0
2021012017 | 4 | 0.66599 | 99898.5 | 0.82789 | 0 | 0.68372 | 8546.5 | 0.01795 | 1436 | 64000 | 8546.5 | 1436 | 25916 | 22161.375 | 1349550.25 | 25916 | 0
2021012018 | 4 | 0.70354 | 105531 | 0.56491 | 0 | 0.68969 | 8621.125 | 0 | 0 | 64000 | 8621.125 | 0 | 32909.875 | 6993.875 | 1342106.625 | 32909.875 | 0
2021012019 | 4 | 0.72566 | 108849 | 0.3241 | 0 | 0.69849 | 8731.125 | 0 | 0 | 64000 | 8731.125 | 0 | 36117.875 | 3208 | 1331455 | 36117.875 | 0
2021012020 | 4 | 0.72047 | 108070.5 | 0.21562 | 0 | 0.68151 | 8518.875 | 0 | 0 | 64000 | 8518.875 | 0 | 35551.625 | -566.25 | 1321369.625 | 35551.625 | 0
2021012021 | 4 | 0.71267 | 106900.5 | 0.31912 | 0 | 0.69595 | 8699.375 | 0 | 0 | 64000 | 8699.375 | 0 | 34201.125 | -1350.5 | 1312634.75 | 34201.125 | 0
2021012022 | 4 | 0.69377 | 104065.5 | 0.35405 | 0 | 0.72268 | 9033.5 | 0 | 0 | 64000 | 9033.5 | 0 | 31032 | -3169.125 | 1307069 | 31032 | 0
2021012023 | 4 | 0.66644 | 99966 | 0.47752 | 0 | 0.73153 | 9144.125 | 0 | 0 | 64000 | 9144.125 | 0 | 26821.875 | -4210.125 | 1305713.375 | 26821.875 | 0
2021012024 | 4 | 0.64029 | 96043.5 | 0.60159 | 0 | 0.70719 | 8839.875 | 0 | 0 | 64000 | 8839.875 | 0 | 23203.625 | -3618.25 | 1307976 | 23203.625 | 0
2021012101 | 5 | 0.62231 | 93346.5 | 0.73034 | 0 | 0.67753 | 8469.125 | 0 | 0 | 64000 | 8469.125 | 0 | 20877.375 | -2326.25 | 1312564.875 | 20877.375 | 0
2021012102 | 5 | 0.61241 | 91861.5 | 0.80393 | 0 | 0.64114 | 8014.25 | 0 | 0 | 64000 | 8014.25 | 0 | 19847.25 | -1030.125 | 1318183.875 | 19847.25 | 0
2021012103 | 5 | 0.61002 | 91503 | 0.8756 | 0 | 0.64616 | 8077 | 0 | 0 | 64000 | 8077 | 0 | 19426 | -421.25 | 1324224.125 | 19426 | 0
2021012104 | 5 | 0.61228 | 91842 | 0.89929 | 0 | 0.66092 | 8261.5 | 0 | 0 | 64000 | 8261.5 | 0 | 19580.5 | 154.5 | 1330109.875 | 19580.5 | 0
2021012105 | 5 | 0.62372 | 93558 | 0.89414 | 0 | 0.6555 | 8193.75 | 0 | 0 | 64000 | 8193.75 | 0 | 21364.25 | 1783.75 | 1334211.875 | 21364.25 | 0
2021012106 | 5 | 0.64818 | 97227 | 0.91426 | 0 | 0.66365 | 8295.625 | 0 | 0 | 64000 | 8295.625 | 0 | 24931.375 | 3567.125 | 1334746.75 | 24931.375 | 0
2021012107 | 5 | 0.68976 | 103464 | 0.92905 | 0 | 0.72541 | 9067.625 | 0 | 0 | 64000 | 9067.625 | 0 | 30396.375 | 5465 | 1329816.625 | 30396.375 | 0
2021012108 | 5 | 0.71873 | 107809.5 | 0.9655 | 0 | 0.79664 | 9958 | 0.01545 | 1236 | 64000 | 9958 | 1236 | 32615.5 | 2219.125 | 1322667.375 | 32615.5 | 0
2021012109 | 5 | 0.72243 | 108364.5 | 0.96601 | 0 | 0.81754 | 10219.25 | 0.06406 | 5124.8 | 64000 | 10219.25 | 5124.8 | 29020.45 | -3595.05 | 1319113.175 | 29020.45 | 0
2021012110 | 5 | 0.70654 | 105981 | 0.94666 | 0 | 0.81812 | 10226.5 | 0.12256 | 9804.8 | 64000 | 10226.5 | 9804.8 | 21949.7 | -7070.75 | 1322629.725 | 21949.7 | 0
2021012111 | 5 | 0.68301 | 102451.5 | 0.90445 | 0 | 0.8085 | 10106.25 | 0.17235 | 13788 | 64000 | 10106.25 | 13788 | 14557.25 | -7392.45 | 1333538.725 | 14557.25 | 0
2021012112 | 5 | 0.66149 | 99223.5 | 0.82533 | 0 | 0.76911 | 9613.875 | 0.18605 | 14884 | 64000 | 9613.875 | 14884 | 10725.625 | -3831.625 | 1348279.35 | 10725.625 | 0
2021012113 | 5 | 0.64544 | 96816 | 0.777 | 0 | 0.73451 | 9181.375 | 0.16889 | 13511.2 | 64000 | 9181.375 | 13511.2 | 10123.425 | -602.2 | 1350000 | 10123.425 | 0
2021012114 | 5 | 0.63303 | 94954.5 | 0.82757 | 0 | 0.74239 | 9279.875 | 0.13594 | 10875.2 | 64000 | 9279.875 | 10875.2 | 10799.425 | 676 | 1350000 | 10799.425 | 0
2021012115 | 5 | 0.62172 | 93258 | 0.81135 | 0 | 0.76011 | 9501.375 | 0.10409 | 8327.2 | 64000 | 9501.375 | 8327.2 | 11429.425 | 630 | 1350000 | 11429.425 | 0
2021012116 | 5 | 0.61676 | 92514 | 0.77387 | 0 | 0.76507 | 9563.375 | 0.05923 | 4738.4 | 64000 | 9563.375 | 4738.4 | 14212.225 | 2782.8 | 1350000 | 14212.225 | 0
2021012117 | 5 | 0.6273 | 94095 | 0.74162 | 0 | 0.75642 | 9455.25 | 0.00804 | 643.2 | 64000 | 9455.25 | 643.2 | 19996.55 | 5784.325 | 1350000 | 19996.55 | 0
2021012118 | 5 | 0.66138 | 99207 | 0.8079 | 0 | 0.71568 | 8946 | 0 | 0 | 64000 | 8946 | 0 | 26261 | 6264.45 | 1349205.25 | 26261 | 0
2021012119 | 5 | 0.68326 | 102489 | 0.89424 | 0 | 0.74672 | 9334 | 0 | 0 | 64000 | 9334 | 0 | 29155 | 2894 | 1345516.5 | 29155 | 0
2021012120 | 5 | 0.67931 | 101896.5 | 0.90562 | 0 | 0.7589 | 9486.25 | 0 | 0 | 64000 | 9486.25 | 0 | 28410.25 | -744.75 | 1342572.5 | 28410.25 | 0
2021012121 | 5 | 0.66827 | 100240.5 | 0.91119 | 0 | 0.76593 | 9574.125 | 0 | 0 | 64000 | 9574.125 | 0 | 26666.375 | -1743.875 | 1341372.375 | 26666.375 | 0
2021012122 | 5 | 0.64779 | 97168.5 | 0.91742 | 0 | 0.75556 | 9444.5 | 0 | 0 | 64000 | 9444.5 | 0 | 23724 | -2942.375 | 1343114.625 | 23724 | 0
2021012123 | 5 | 0.62015 | 93022.5 | 0.94785 | 0 | 0.74082 | 9260.25 | 0 | 0 | 64000 | 9260.25 | 0 | 19762.25 | -3961.75 | 1348818.625 | 19762.25 | 0
2021012124 | 5 | 0.59231 | 88846.5 | 0.9481 | 0 | 0.76663 | 9582.875 | 0 | 0 | 64000 | 9582.875 | 0 | 15263.625 | -4498.625 | 1350000 | 15263.625 | 0
2021012201 | 6 | 0.57195 | 85792.5 | 0.9196 | 0 | 0.75169 | 9396.125 | 0 | 0 | 64000 | 9396.125 | 0 | 12396.375 | -2867.25 | 1350000 | 12396.375 | 0
2021012202 | 6 | 0.56182 | 84273 | 0.93319 | 0 | 0.69288 | 8661 | 0 | 0 | 64000 | 8661 | 0 | 11612 | -784.375 | 1350000 | 11612 | 0
2021012203 | 6 | 0.55685 | 83527.5 | 0.93382 | 0 | 0.71043 | 8880.375 | 0 | 0 | 64000 | 8880.375 | 0 | 10647.125 | -964.875 | 1350000 | 10647.125 | 0
2021012204 | 6 | 0.55997 | 83995.5 | 0.91923 | 0 | 0.67091 | 8386.375 | 0 | 0 | 64000 | 8386.375 | 0 | 11609.125 | 962 | 1350000 | 11609.125 | 0
2021012205 | 6 | 0.57323 | 85984.5 | 0.93844 | 0 | 0.64308 | 8038.5 | 0 | 0 | 64000 | 8038.5 | 0 | 13946 | 2336.875 | 1350000 | 13946 | 0
2021012206 | 6 | 0.60275 | 90412.5 | 0.92856 | 0 | 0.57614 | 7201.75 | 0 | 0 | 64000 | 7201.75 | 0 | 19210.75 | 5264.75 | 1350000 | 19210.75 | 0
2021012207 | 6 | 0.64951 | 97426.5 | 0.9015 | 0 | 0.54549 | 6818.625 | 0 | 0 | 64000 | 6818.625 | 0 | 26607.875 | 7397.125 | 1348858.375 | 26607.875 | 0
2021012208 | 6 | 0.68529 | 102793.5 | 0.876 | 0 | 0.51769 | 6471.125 | 0.0073 | 584 | 64000 | 6471.125 | 584 | 31738.375 | 5130.5 | 1342586.25 | 31738.375 | 0
2021012209 | 6 | 0.69169 | 103753.5 | 0.84466 | 0 | 0.47039 | 5879.875 | 0.0618 | 4944 | 64000 | 5879.875 | 4944 | 28929.625 | -2808.75 | 1339122.875 | 28929.625 | 0
2021012210 | 6 | 0.68006 | 102009 | 0.87047 | 0 | 0.37501 | 4687.625 | 0.14646 | 11716.8 | 64000 | 4687.625 | 11716.8 | 21604.575 | -7325.05 | 1342984.55 | 21604.575 | 0
2021012211 | 6 | 0.66753 | 100129.5 | 0.86702 | 0 | 0.29539 | 3692.375 | 0.18459 | 14767.2 | 64000 | 3692.375 | 14767.2 | 17669.925 | -3934.65 | 1350000 | 17669.925 | 0
2021012212 | 6 | 0.6562 | 98430 | 0.89824 | 0 | 0.24493 | 3061.625 | 0.18342 | 14673.6 | 64000 | 3061.625 | 14673.6 | 16694.775 | -975.15 | 1350000 | 16694.775 | 0
2021012213 | 6 | 0.64804 | 97206 | 0.91107 | 0 | 0.2289 | 2861.25 | 0.1922 | 15376 | 64000 | 2861.25 | 15376 | 14968.75 | -1726.025 | 1350000 | 14968.75 | 0
2021012214 | 6 | 0.63983 | 95974.5 | 0.91861 | 0 | 0.20115 | 2514.375 | 0.16268 | 13014.4 | 64000 | 2514.375 | 13014.4 | 16445.725 | 1476.975 | 1350000 | 16445.725 | 0
2021012215 | 6 | 0.62931 | 94396.5 | 0.90877 | 0 | 0.20638 | 2579.75 | 0.14873 | 11898.4 | 64000 | 2579.75 | 11898.4 | 15918.35 | -527.375 | 1350000 | 15918.35 | 0
2021012216 | 6 | 0.62658 | 93987 | 0.92421 | 0 | 0.19733 | 2466.625 | 0.08282 | 6625.6 | 64000 | 2466.625 | 6625.6 | 20894.775 | 4976.425 | 1350000 | 20894.775 | 0
2021012217 | 6 | 0.63911 | 95866.5 | 0.91715 | 0 | 0.16965 | 2120.625 | 0.01407 | 1125.6 | 64000 | 2120.625 | 1125.6 | 28620.275 | 7725.5 | 1346845.975 | 28620.275 | 0
2021012218 | 6 | 0.66891 | 100336.5 | 0.9076 | 0 | 0.12725 | 1590.625 | 0 | 0 | 64000 | 1590.625 | 0 | 34745.875 | 6125.6 | 1337566.35 | 34745.875 | 0
2021012219 | 6 | 0.68747 | 103120.5 | 0.90024 | 0 | 0.13059 | 1632.375 | 0 | 0 | 64000 | 1632.375 | 0 | 37488.125 | 2742.25 | 1325544.475 | 37488.125 | 0
2021012220 | 6 | 0.68206 | 102309 | 0.90814 | 0 | 0.18285 | 2285.625 | 0 | 0 | 64000 | 2285.625 | 0 | 36023.375 | -1464.75 | 1314987.35 | 36023.375 | 0
2021012221 | 6 | 0.67224 | 100836 | 0.93373 | 0 | 0.26229 | 3278.625 | 0 | 0 | 64000 | 3278.625 | 0 | 33557.375 | -2466 | 1306896.225 | 33557.375 | 0
2021012222 | 6 | 0.65663 | 98494.5 | 0.95881 | 0 | 0.31284 | 3910.5 | 0 | 0 | 64000 | 3910.5 | 0 | 30584 | -2973.375 | 1301778.475 | 30584 | 0
2021012223 | 6 | 0.63474 | 95211 | 0.96444 | 0 | 0.30423 | 3802.875 | 0 | 0 | 64000 | 3802.875 | 0 | 27408.125 | -3175.875 | 1299836.6 | 27408.125 | 0
2021012224 | 6 | 0.61189 | 91783.5 | 0.94991 | 0 | 0.2973 | 3716.25 | 0 | 0 | 64000 | 3716.25 | 0 | 24067.25 | -3340.875 | 1301235.6 | 24067.25 | 0
2021012301 | 7 | 0.59516 | 89274 | 0.95066 | 0 | 0.33807 | 4225.875 | 0 | 0 | 64000 | 4225.875 | 0 | 21048.125 | -3019.125 | 1305653.725 | 21048.125 | 0
2021012302 | 7 | 0.58678 | 88017 | 0.93754 | 0 | 0.37322 | 4665.25 | 0 | 0 | 64000 | 4665.25 | 0 | 19351.75 | -1696.375 | 1311768.225 | 19351.75 | 0
2021012303 | 7 | 0.58438 | 87657 | 0.93904 | 0 | 0.42538 | 5317.25 | 0 | 0 | 64000 | 5317.25 | 0 | 18339.75 | -1012 | 1318894.725 | 18339.75 | 0
2021012304 | 7 | 0.58744 | 88116 | 0.94919 | 0 | 0.45123 | 5640.375 | 0 | 0 | 64000 | 5640.375 | 0 | 18475.625 | 135.875 | 1325885.35 | 18475.625 | 0
2021012305 | 7 | 0.5964 | 89460 | 0.96081 | 0 | 0.43113 | 5389.125 | 0 | 0 | 64000 | 5389.125 | 0 | 20070.875 | 1595.25 | 1331280.725 | 20070.875 | 0
2021012306 | 7 | 0.61459 | 92188.5 | 0.96756 | 0 | 0.38453 | 4806.625 | 0 | 0 | 64000 | 4806.625 | 0 | 23381.875 | 3311 | 1333365.1 | 23381.875 | 0
2021012307 | 7 | 0.63945 | 95917.5 | 0.97563 | 0 | 0.32996 | 4124.5 | 0 | 0 | 64000 | 4124.5 | 0 | 27793 | 4411.125 | 1331038.35 | 27793 | 0
2021012308 | 7 | 0.66476 | 99714 | 0.98431 | 0 | 0.37797 | 4724.625 | 0.02594 | 2075.2 | 64000 | 4724.625 | 2075.2 | 28914.175 | 1121.175 | 1327590.425 | 28914.175 | 0
2021012309 | 7 | 0.67918 | 101877 | 0.98935 | 0 | 0.48009 | 6001.125 | 0.11754 | 9403.2 | 64000 | 6001.125 | 9403.2 | 22472.675 | -6441.5 | 1330584 | 22472.675 | 0
2021012310 | 7 | 0.67611 | 101416.5 | 0.98994 | 0 | 0.53971 | 6746.375 | 0.16313 | 13050.4 | 64000 | 6746.375 | 13050.4 | 17619.725 | -4852.95 | 1338430.525 | 17619.725 | 0
2021012311 | 7 | 0.66758 | 100137 | 0.98896 | 0 | 0.57437 | 7179.625 | 0.26636 | 21308.8 | 64000 | 7179.625 | 21308.8 | 7648.575 | -9971.15 | 1350000 | 7648.575 | 0
2021012312 | 7 | 0.65593 | 98389.5 | 0.97879 | 0 | 0.57444 | 7180.5 | 0.36533 | 29226.4 | 64000 | 7180.5 | 27209 | 0 | -7648.575 | 1350000 | 0 | 0
2021012313 | 7 | 0.64156 | 96234 | 0.97748 | 0 | 0.58338 | 7292.25 | 0.41871 | 33496.8 | 64000 | 7292.25 | 24941.75 | 0 | 0 | 1350000 | 0 | 0
2021012314 | 7 | 0.62521 | 93781.5 | 0.9717 | 0 | 0.59713 | 7464.125 | 0.4059 | 32472 | 64000 | 7464.125 | 22317.375 | 0 | 0 | 1350000 | 0 | 0
2021012315 | 7 | 0.61484 | 92226 | 0.97067 | 0 | 0.57122 | 7140.25 | 0.3883 | 31064 | 64000 | 7140.25 | 21085.75 | 0 | 0 | 1350000 | 0 | 0
2021012316 | 7 | 0.61635 | 92452.5 | 0.97331 | 0 | 0.56207 | 7025.875 | 0.2439 | 19512 | 64000 | 7025.875 | 19512 | 1914.625 | 1914.625 | 1350000 | 1914.625 | 0
2021012317 | 7 | 0.63579 | 95368.5 | 0.96944 | 0 | 0.55021 | 6877.625 | 0.03996 | 3196.8 | 64000 | 6877.625 | 3196.8 | 21294.075 | 19379.45 | 1350000 | 21294.075 | 0
2021012318 | 7 | 0.67708 | 101562 | 0.96221 | 0 | 0.54389 | 6798.625 | 0 | 0 | 64000 | 6798.625 | 0 | 30763.375 | 9469.3 | 1344702.875 | 30763.375 | 0
2021012319 | 7 | 0.70322 | 105483 | 0.94458 | 0 | 0.5311 | 6638.75 | 0 | 0 | 64000 | 6638.75 | 0 | 34844.25 | 4080.875 | 1335324.875 | 34844.25 | 0
2021012320 | 7 | 0.70232 | 105348 | 0.93664 | 0 | 0.51248 | 6406 | 0 | 0 | 64000 | 6406 | 0 | 34942 | 97.75 | 1325849.125 | 34942 | 0
2021012321 | 7 | 0.69624 | 104436 | 0.9221 | 0 | 0.4987 | 6233.75 | 0 | 0 | 64000 | 6233.75 | 0 | 34202.25 | -739.75 | 1317113.125 | 34202.25 | 0
2021012322 | 7 | 0.68385 | 102577.5 | 0.92505 | 0 | 0.44992 | 5624 | 0 | 0 | 64000 | 5624 | 0 | 32953.5 | -1248.75 | 1309625.875 | 32953.5 | 0
2021012323 | 7 | 0.66326 | 99489 | 0.92404 | 0 | 0.35949 | 4493.625 | 0 | 0 | 64000 | 4493.625 | 0 | 30995.375 | -1958.125 | 1304096.75 | 30995.375 | 0
2021012324 | 7 | 0.64308 | 96462 | 0.92389 | 0 | 0.27379 | 3422.375 | 0 | 0 | 64000 | 3422.375 | 0 | 29039.625 | -1955.75 | 1300523.375 | 29039.625 | 0
2021012401 | 1 | 0.6259 | 93885 | 0.93037 | 0 | 0.22138 | 2767.25 | 0 | 0 | 64000 | 2767.25 | 0 | 27117.75 | -1921.875 | 1298871.875 | 27117.75 | 0
2021012402 | 1 | 0.61592 | 92388 | 0.87123 | 0 | 0.20359 | 2544.875 | 0 | 0 | 64000 | 2544.875 | 0 | 25843.125 | -1274.625 | 1298495 | 25843.125 | 0
2021012403 | 1 | 0.61038 | 91557 | 0.81653 | 0 | 0.17363 | 2170.375 | 0 | 0 | 64000 | 2170.375 | 0 | 25386.625 | -456.5 | 1298574.625 | 25386.625 | 0
2021012404 | 1 | 0.60856 | 91284 | 0.7651 | 0 | 0.14885 | 1860.625 | 0 | 0 | 64000 | 1860.625 | 0 | 25423.375 | 36.75 | 1298617.5 | 25423.375 | 0
2021012405 | 1 | 0.61303 | 91954.5 | 0.74115 | 0 | 0.15024 | 1878 | 0 | 0 | 64000 | 1878 | 0 | 26076.5 | 653.125 | 1298007.25 | 26076.5 | 0
2021012406 | 1 | 0.62212 | 93318 | 0.66992 | 0 | 0.16016 | 2002 | 0 | 0 | 64000 | 2002 | 0 | 27316 | 1239.5 | 1296157.5 | 27316 | 0
2021012407 | 1 | 0.63883 | 95824.5 | 0.61981 | 0 | 0.1576 | 1970 | 0 | 0 | 64000 | 1970 | 0 | 29854.5 | 2538.5 | 1291769.25 | 29854.5 | 0
2021012408 | 1 | 0.65581 | 98371.5 | 0.60324 | 0 | 0.18073 | 2259.125 | 0.03333 | 2666.4 | 64000 | 2259.125 | 2666.4 | 29445.975 | -408.525 | 1287789.525 | 29445.975 | 0
2021012409 | 1 | 0.66134 | 99201 | 0.52371 | 0 | 0.21749 | 2718.625 | 0.20558 | 16446.4 | 64000 | 2718.625 | 16446.4 | 16035.975 | -13410 | 1297219.8 | 16035.975 | 0
2021012410 | 1 | 0.65578 | 98367 | 0.51751 | 0 | 0.26024 | 3253 | 0.24366 | 19492.8 | 64000 | 3253 | 19492.8 | 11621.2 | -4414.775 | 1311064.85 | 11621.2 | 0
2021012411 | 1 | 0.6475 | 97125 | 0.42366 | 0 | 0.29317 | 3664.625 | 0.22447 | 17957.6 | 64000 | 3664.625 | 17957.6 | 11502.775 | -118.425 | 1325028.325 | 11502.775 | 0
2021012412 | 1 | 0.64032 | 96048 | 0.3307 | 0 | 0.29297 | 3662.125 | 0.15437 | 12349.6 | 64000 | 3662.125 | 12349.6 | 16036.275 | 4533.5 | 1334458.3 | 16036.275 | 0
2021012413 | 1 | 0.63536 | 95304 | 0.26414 | 0 | 0.3083 | 3853.75 | 0.1244 | 9952 | 64000 | 3853.75 | 9952 | 17498.25 | 1461.975 | 1342426.3 | 17498.25 | 0
2021012414 | 1 | 0.63022 | 94533 | 0.21652 | 0 | 0.31245 | 3905.625 | 0.09574 | 7659.2 | 64000 | 3905.625 | 7659.2 | 18968.175 | 1469.925 | 1348924.375 | 18968.175 | 0
2021012415 | 1 | 0.62913 | 94369.5 | 0.17745 | 0 | 0.27296 | 3412 | 0.05541 | 4432.8 | 64000 | 3412 | 4432.8 | 22524.7 | 3556.525 | 1350000 | 22524.7 | 0
2021012416 | 1 | 0.63484 | 95226 | 0.13275 | 0 | 0.28713 | 3589.125 | 0.0174 | 1392 | 64000 | 3589.125 | 1392 | 26244.875 | 3720.175 | 1349221.375 | 26244.875 | 0
2021012417 | 1 | 0.65167 | 97750.5 | 0.1464 | 0 | 0.26104 | 3263 | 0.00075 | 60 | 64000 | 3263 | 60 | 30427.5 | 4182.625 | 1344260.125 | 30427.5 | 0
2021012418 | 1 | 0.68059 | 102088.5 | 0.14342 | 0 | 0.26192 | 3274 | 0 | 0 | 64000 | 3274 | 0 | 34814.5 | 4387 | 1334911.875 | 34814.5 | 0
2021012419 | 1 | 0.69207 | 103810.5 | 0.16589 | 0 | 0.29021 | 3627.625 | 0 | 0 | 64000 | 3627.625 | 0 | 36182.875 | 1368.375 | 1324195.25 | 36182.875 | 0
2021012420 | 1 | 0.68528 | 102792 | 0.14165 | 0 | 0.29924 | 3740.5 | 0 | 0 | 64000 | 3740.5 | 0 | 35051.5 | -1131.375 | 1314610 | 35051.5 | 0
2021012421 | 1 | 0.67096 | 100644 | 0.15371 | 0 | 0.29127 | 3640.875 | 0 | 0 | 64000 | 3640.875 | 0 | 33003.125 | -2048.375 | 1307073.125 | 33003.125 | 0
2021012422 | 1 | 0.64933 | 97399.5 | 0.17125 | 0 | 0.28248 | 3531 | 0 | 0 | 64000 | 3531 | 0 | 29868.5 | -3134.625 | 1302670.875 | 29868.5 | 0
2021012423 | 1 | 0.62152 | 93228 | 0.15521 | 0 | 0.26301 | 3287.625 | 0 | 0 | 64000 | 3287.625 | 0 | 25940.375 | -3928.125 | 1302196.75 | 25940.375 | 0
2021012424 | 1 | 0.59595 | 89392.5 | 0.09501 | 0 | 0.25232 | 3154 | 0 | 0 | 64000 | 3154 | 0 | 22238.5 | -3701.875 | 1305424.5 | 22238.5 | 0
2021012501 | 2 | 0.57773 | 86659.5 | 0.05601 | 0 | 0.23731 | 2966.375 | 0 | 0 | 64000 | 2966.375 | 0 | 19693.125 | -2545.375 | 1311197.625 | 19693.125 | 0
2021012502 | 2 | 0.56826 | 85239 | 0.04577 | 0 | 0.2342 | 2927.5 | 0 | 0 | 64000 | 2927.5 | 0 | 18311.5 | -1381.625 | 1318352.375 | 18311.5 | 0
2021012503 | 2 | 0.56432 | 84648 | 0.0431 | 0 | 0.19939 | 2492.375 | 0 | 0 | 64000 | 2492.375 | 0 | 18155.625 | -155.875 | 1325663 | 18155.625 | 0
2021012504 | 2 | 0.56645 | 84967.5 | 0.05311 | 0 | 0.18913 | 2364.125 | 0 | 0 | 64000 | 2364.125 | 0 | 18603.375 | 447.75 | 1332525.875 | 18603.375 | 0
2021012505 | 2 | 0.58019 | 87028.5 | 0.04703 | 0 | 0.18216 | 2277 | 0 | 0 | 64000 | 2277 | 0 | 20751.5 | 2148.125 | 1337240.625 | 20751.5 | 0
2021012506 | 2 | 0.6102 | 91530 | 0.02418 | 0 | 0.16305 | 2038.125 | 0 | 0 | 64000 | 2038.125 | 0 | 25491.875 | 4740.375 | 1337215 | 25491.875 | 0
2021012507 | 2 | 0.6571 | 98565 | 0.02415 | 0 | 0.11727 | 1465.875 | 0 | 0 | 64000 | 1465.875 | 0 | 33099.125 | 7607.25 | 1329582.125 | 33099.125 | 0
2021012508 | 2 | 0.69571 | 104356.5 | 0.02609 | 0 | 0.0919 | 1148.75 | 0.02707 | 2165.6 | 64000 | 1148.75 | 2165.6 | 37042.15 | 3943.025 | 1318006.225 | 37042.15 | 0
2021012509 | 2 | 0.7115 | 106725 | 0.00626 | 0 | 0.06075 | 759.375 | 0.25013 | 20010.4 | 64000 | 759.375 | 20010.4 | 21955.225 | -15086.925 | 1321517.25 | 21955.225 | 0
2021012510 | 2 | 0.71512 | 107268 | 0.00475 | 0 | 0.05787 | 723.375 | 0.42849 | 34279.2 | 64000 | 723.375 | 34279.2 | 8265.425 | -13689.8 | 1338718.075 | 8265.425 | 0
2021012511 | 2 | 0.71464 | 107196 | 0.00945 | 0 | 0.05124 | 640.5 | 0.44339 | 35471.2 | 64000 | 640.5 | 35471.2 | 7084.3 | -1181.125 | 1350000 | 7084.3 | 0
2021012512 | 2 | 0.71035 | 106552.5 | 0.00232 | 0 | 0.04442 | 555.25 | 0.48125 | 38500 | 64000 | 555.25 | 38500 | 3497.25 | -3587.05 | 1350000 | 3497.25 | 0
2021012513 | 2 | 0.70657 | 105985.5 | 0.00799 | 0 | 0.03333 | 416.625 | 0.50488 | 40390.4 | 64000 | 416.625 | 40390.4 | 1178.475 | -2318.775 | 1350000 | 1178.475 | 0
2021012514 | 2 | 0.70199 | 105298.5 | 0.00624 | 0 | 0.03047 | 380.875 | 0.49953 | 39962.4 | 64000 | 380.875 | 39962.4 | 955.225 | -223.25 | 1350000 | 955.225 | 0
2021012515 | 2 | 0.69676 | 104514 | 0.00714 | 0 | 0.04299 | 537.375 | 0.36117 | 28893.6 | 64000 | 537.375 | 28893.6 | 11083.025 | 10127.8 | 1350000 | 11083.025 | 0
2021012516 | 2 | 0.69567 | 104350.5 | 0.02513 | 0 | 0.05304 | 663 | 0.14948 | 11958.4 | 64000 | 663 | 11958.4 | 27729.1 | 16646.075 | 1347737.15 | 27729.1 | 0
2021012517 | 2 | 0.7031 | 105465 | 0.03572 | 0 | 0.08064 | 1008 | 0.02484 | 1987.2 | 64000 | 1008 | 1987.2 | 38469.8 | 10740.7 | 1334733.6 | 38469.8 | 0
2021012518 | 2 | 0.72685 | 109027.5 | 0.10079 | 0 | 0.11333 | 1416.625 | 0 | 0 | 64000 | 1416.625 | 0 | 43610.875 | 5141.075 | 1316588.975 | 43610.875 | 0
2021012519 | 2 | 0.7306 | 109590 | 0.2055 | 0 | 0.16888 | 2111 | 0 | 0 | 64000 | 2111 | 0 | 43479 | -131.875 | 1298576.225 | 43479 | 0
2021012520 | 2 | 0.71748 | 107622 | 0.22865 | 0 | 0.20759 | 2594.875 | 0 | 0 | 64000 | 2594.875 | 0 | 41027.125 | -2451.875 | 1283015.35 | 41027.125 | 0
2021012521 | 2 | 0.69969 | 104953.5 | 0.30993 | 0 | 0.2739 | 3423.75 | 0 | 0 | 64000 | 3423.75 | 0 | 37529.75 | -3497.375 | 1270951.85 | 37529.75 | 0
2021012522 | 2 | 0.67534 | 101301 | 0.34762 | 0 | 0.3263 | 4078.75 | 0 | 0 | 64000 | 4078.75 | 0 | 33222.25 | -4307.5 | 1263195.85 | 33222.25 | 0
2021012523 | 2 | 0.64282 | 96423 | 0.38709 | 0 | 0.42082 | 5260.25 | 0 | 0 | 64000 | 5260.25 | 0 | 27162.75 | -6059.5 | 1261499.35 | 27162.75 | 0
2021012524 | 2 | 0.61203 | 91804.5 | 0.42004 | 0 | 0.51076 | 6384.5 | 0 | 0 | 64000 | 6384.5 | 0 | 21420 | -5742.75 | 1265545.6 | 21420 | 0
2021012601 | 3 | 0.58962 | 88443 | 0.37945 | 0 | 0.59166 | 7395.75 | 0 | 0 | 64000 | 7395.75 | 0 | 17047.25 | -4372.75 | 1273964.6 | 17047.25 | 0
2021012602 | 3 | 0.57797 | 86695.5 | 0.29644 | 0 | 0.6776 | 8470 | 0 | 0 | 64000 | 8470 | 0 | 14225.5 | -2821.75 | 1285205.35 | 14225.5 | 0
2021012603 | 3 | 0.57155 | 85732.5 | 0.28753 | 0 | 0.75038 | 9379.75 | 0 | 0 | 64000 | 9379.75 | 0 | 12352.75 | -1872.75 | 1298318.85 | 12352.75 | 0
2021012604 | 3 | 0.57191 | 85786.5 | 0.29884 | 0 | 0.78338 | 9792.25 | 0 | 0 | 64000 | 9792.25 | 0 | 11994.25 | -358.5 | 1311790.85 | 11994.25 | 0
2021012605 | 3 | 0.58169 | 87253.5 | 0.35837 | 0 | 0.77681 | 9710.125 | 0 | 0 | 64000 | 9710.125 | 0 | 13543.375 | 1549.125 | 1323713.725 | 13543.375 | 0
2021012606 | 3 | 0.60955 | 91432.5 | 0.46466 | 0 | 0.78764 | 9845.5 | 0 | 0 | 64000 | 9845.5 | 0 | 17587 | 4043.625 | 1331592.975 | 17587 | 0
2021012607 | 3 | 0.64998 | 97497 | 0.54481 | 0 | 0.7983 | 9978.75 | 0 | 0 | 64000 | 9978.75 | 0 | 23518.25 | 5931.25 | 1333540.975 | 23518.25 | 0
2021012608 | 3 | 0.68644 | 102966 | 0.54674 | 0 | 0.84521 | 10565.125 | 0.02043 | 1634.4 | 64000 | 10565.125 | 1634.4 | 26766.475 | 3248.225 | 1332240.75 | 26766.475 | 0
2021012609 | 3 | 0.70097 | 105145.5 | 0.53376 | 0 | 0.84774 | 10596.75 | 0.15371 | 12296.8 | 64000 | 10596.75 | 12296.8 | 18251.95 | -8514.525 | 1339455.05 | 18251.95 | 0
2021012610 | 3 | 0.70492 | 105738 | 0.53356 | 0 | 0.84244 | 10530.5 | 0.33261 | 26608.8 | 64000 | 10530.5 | 26608.8 | 4598.7 | -13653.25 | 1350000 | 4598.7 | 0
2021012611 | 3 | 0.70665 | 105997.5 | 0.5342 | 0 | 0.82762 | 10345.25 | 0.39884 | 31907.2 | 64000 | 10345.25 | 31652.25 | 0 | -4598.7 | 1350000 | 0 | 0
2021012612 | 3 | 0.7043 | 105645 | 0.5632 | 0 | 0.82353 | 10294.125 | 0.46032 | 36825.6 | 64000 | 10294.125 | 31350.875 | 0 | 0 | 1350000 | 0 | 0
2021012613 | 3 | 0.70095 | 105142.5 | 0.60358 | 0 | 0.79014 | 9876.75 | 0.45118 | 36094.4 | 64000 | 9876.75 | 31265.75 | 0 | 0 | 1350000 | 0 | 0
2021012614 | 3 | 0.69391 | 104086.5 | 0.5366 | 0 | 0.78077 | 9759.625 | 0.39022 | 31217.6 | 64000 | 9759.625 | 30326.875 | 0 | 0 | 1350000 | 0 | 0
2021012615 | 3 | 0.6851 | 102765 | 0.49996 | 0 | 0.7805 | 9756.25 | 0.24122 | 19297.6 | 64000 | 9756.25 | 19297.6 | 9711.15 | 9711.15 | 1350000 | 9711.15 | 0
2021012616 | 3 | 0.68066 | 102099 | 0.62018 | 0 | 0.77984 | 9748 | 0.0828 | 6624 | 64000 | 9748 | 6624 | 21727 | 12015.85 | 1350000 | 21727 | 0
2021012617 | 3 | 0.68333 | 102499.5 | 0.68885 | 0 | 0.7778 | 9722.5 | 0.01512 | 1209.6 | 64000 | 9722.5 | 1209.6 | 27567.4 | 5840.4 | 1347898.85 | 27567.4 | 0
2021012618 | 3 | 0.70209 | 105313.5 | 0.71601 | 0 | 0.76371 | 9546.375 | 0 | 0 | 64000 | 9546.375 | 0 | 31767.125 | 4199.725 | 1341597.975 | 31767.125 | 0
2021012619 | 3 | 0.70753 | 106129.5 | 0.58496 | 0 | 0.76195 | 9524.375 | 0 | 0 | 64000 | 9524.375 | 0 | 32605.125 | 838 | 1334459.1 | 32605.125 | 0
2021012620 | 3 | 0.69526 | 104289 | 0.70317 | 0 | 0.71197 | 8899.625 | 0 | 0 | 64000 | 8899.625 | 0 | 31389.375 | -1215.75 | 1328535.975 | 31389.375 | 0
2021012621 | 3 | 0.67735 | 101602.5 | 0.7117 | 0 | 0.66195 | 8274.375 | 0 | 0 | 64000 | 8274.375 | 0 | 29328.125 | -2061.25 | 1324674.1 | 29328.125 | 0
2021012622 | 3 | 0.65386 | 98079 | 0.67096 | 0 | 0.62732 | 7841.5 | 0 | 0 | 64000 | 7841.5 | 0 | 26237.5 | -3090.625 | 1323902.85 | 26237.5 | 0
2021012623 | 3 | 0.62276 | 93414 | 0.68292 | 0 | 0.61224 | 7653 | 0 | 0 | 64000 | 7653 | 0 | 21761 | -4476.5 | 1327608.1 | 21761 | 0
2021012624 | 3 | 0.5943 | 89145 | 0.72457 | 0 | 0.67659 | 8457.375 | 0 | 0 | 64000 | 8457.375 | 0 | 16687.625 | -5073.375 | 1336386.725 | 16687.625 | 0
2021012701 | 4 | 0.57238 | 85857 | 0.73386 | 0 | 0.67508 | 8438.5 | 0 | 0 | 64000 | 8438.5 | 0 | 13418.5 | -3269.125 | 1348434.475 | 13418.5 | 0
2021012702 | 4 | 0.55992 | 83988 | 0.73982 | 0 | 0.71331 | 8916.375 | 0 | 0 | 64000 | 8916.375 | 0 | 11071.625 | -2346.875 | 1350000 | 11071.625 | 0
2021012703 | 4 | 0.55599 | 83398.5 | 0.74558 | 0 | 0.72033 | 9004.125 | 0 | 0 | 64000 | 9004.125 | 0 | 10394.375 | -677.25 | 1350000 | 10394.375 | 0
2021012704 | 4 | 0.55692 | 83538 | 0.78303 | 0 | 0.70887 | 8860.875 | 0 | 0 | 64000 | 8860.875 | 0 | 10677.125 | 282.75 | 1350000 | 10677.125 | 0
2021012705 | 4 | 0.56916 | 85374 | 0.77005 | 0 | 0.68603 | 8575.375 | 0 | 0 | 64000 | 8575.375 | 0 | 12798.625 | 2121.5 | 1350000 | 12798.625 | 0
2021012706 | 4 | 0.59782 | 89673 | 0.77139 | 0 | 0.63295 | 7911.875 | 0 | 0 | 64000 | 7911.875 | 0 | 17761.125 | 4962.5 | 1350000 | 17761.125 | 0
2021012707 | 4 | 0.64167 | 96250.5 | 0.72163 | 0 | 0.60185 | 7523.125 | 0 | 0 | 64000 | 7523.125 | 0 | 24727.375 | 6966.25 | 1350000 | 24727.375 | 0
2021012708 | 4 | 0.67835 | 101752.5 | 0.70835 | 0 | 0.58261 | 7282.625 | 0.01409 | 1127.2 | 64000 | 7282.625 | 1127.2 | 29342.675 | 4615.3 | 1346123.575 | 29342.675 | 0
2021012709 | 4 | 0.69044 | 103566 | 0.5903 | 0 | 0.53867 | 6733.375 | 0.12411 | 9928.8 | 64000 | 6733.375 | 9928.8 | 22903.825 | -6438.85 | 1348686 | 22903.825 | 0
2021012710 | 4 | 0.6917 | 103755 | 0.44968 | 0 | 0.51332 | 6416.5 | 0.26672 | 21337.6 | 64000 | 6416.5 | 21337.6 | 12000.9 | -10902.925 | 1350000 | 12000.9 | 0
2021012711 | 4 | 0.68878 | 103317 | 0.48808 | 0 | 0.58873 | 7359.125 | 0.34981 | 27984.8 | 64000 | 7359.125 | 27984.8 | 3973.075 | -8027.825 | 1350000 | 3973.075 | 0
2021012712 | 4 | 0.68514 | 102771 | 0.44831 | 0 | 0.63444 | 7930.5 | 0.3948 | 31584 | 64000 | 7930.5 | 30840.5 | 0 | -3973.075 | 1350000 | 0 | 0
2021012713 | 4 | 0.67953 | 101929.5 | 0.35393 | 0 | 0.64273 | 8034.125 | 0.44023 | 35218.4 | 64000 | 8034.125 | 29895.375 | 0 | 0 | 1350000 | 0 | 0
2021012714 | 4 | 0.67485 | 101227.5 | 0.32822 | 0 | 0.64461 | 8057.625 | 0.48325 | 38660 | 64000 | 8057.625 | 29169.875 | 0 | 0 | 1350000 | 0 | 0
2021012715 | 4 | 0.66979 | 100468.5 | 0.35647 | 0 | 0.61115 | 7639.375 | 0.43797 | 35037.6 | 64000 | 7639.375 | 28829.125 | 0 | 0 | 1350000 | 0 | 0
2021012716 | 4 | 0.66718 | 100077 | 0.29365 | 0 | 0.60984 | 7623 | 0.22967 | 18373.6 | 64000 | 7623 | 18373.6 | 10080.4 | 10080.4 | 1350000 | 10080.4 | 0
2021012717 | 4 | 0.67877 | 101815.5 | 0.31652 | 0 | 0.61336 | 7667 | 0.038 | 3040 | 64000 | 7667 | 3040 | 27108.5 | 17028.1 | 1348357.75 | 27108.5 | 0
2021012718 | 4 | 0.70807 | 106210.5 | 0.31903 | 0 | 0.59368 | 7421 | 0 | 0 | 64000 | 7421 | 0 | 34789.5 | 7681 | 1339034.5 | 34789.5 | 0
2021012719 | 4 | 0.72337 | 108505.5 | 0.28711 | 0 | 0.54413 | 6801.625 | 0 | 0 | 64000 | 6801.625 | 0 | 37703.875 | 2914.375 | 1326796.875 | 37703.875 | 0
2021012720 | 4 | 0.71625 | 107437.5 | 0.33633 | 0 | 0.45602 | 5700.25 | 0 | 0 | 64000 | 5700.25 | 0 | 37737.25 | 33.375 | 1314525.875 | 37737.25 | 0
2021012721 | 4 | 0.70406 | 105609 | 0.3272 | 0 | 0.41546 | 5193.25 | 0 | 0 | 64000 | 5193.25 | 0 | 36415.75 | -1321.5 | 1303576.375 | 36415.75 | 0
2021012722 | 4 | 0.68468 | 102702 | 0.35513 | 0 | 0.40489 | 5061.125 | 0 | 0 | 64000 | 5061.125 | 0 | 33640.875 | -2774.875 | 1295401.75 | 33640.875 | 0
2021012723 | 4 | 0.65576 | 98364 | 0.45424 | 0 | 0.37113 | 4639.125 | 0 | 0 | 64000 | 4639.125 | 0 | 29724.875 | -3916 | 1291143.125 | 29724.875 | 0
2021012724 | 4 | 0.62887 | 94330.5 | 0.57048 | 0 | 0.29299 | 3662.375 | 0 | 0 | 64000 | 3662.375 | 0 | 26668.125 | -3056.75 | 1289941.25 | 26668.125 | 0
2021012801 | 5 | 0.61092 | 91638 | 0.61504 | 0 | 0.22141 | 2767.625 | 0 | 0 | 64000 | 2767.625 | 0 | 24870.375 | -1797.75 | 1290537.125 | 24870.375 | 0
2021012802 | 5 | 0.60233 | 90349.5 | 0.6258 | 0 | 0.19681 | 2460.125 | 0 | 0 | 64000 | 2460.125 | 0 | 23889.375 | -981 | 1292114 | 23889.375 | 0
2021012803 | 5 | 0.60071 | 90106.5 | 0.63108 | 0 | 0.18135 | 2266.875 | 0 | 0 | 64000 | 2266.875 | 0 | 23839.625 | -49.75 | 1293740.625 | 23839.625 | 0
2021012804 | 5 | 0.60661 | 90991.5 | 0.68949 | 0 | 0.19907 | 2488.375 | 0 | 0 | 64000 | 2488.375 | 0 | 24503.125 | 663.5 | 1294703.75 | 24503.125 | 0
2021012805 | 5 | 0.62269 | 93403.5 | 0.78099 | 0 | 0.20646 | 2580.75 | 0 | 0 | 64000 | 2580.75 | 0 | 26822.75 | 2319.625 | 1293347.25 | 26822.75 | 0
2021012806 | 5 | 0.65473 | 98209.5 | 0.81988 | 0 | 0.18552 | 2319 | 0 | 0 | 64000 | 2319 | 0 | 31890.5 | 5067.75 | 1286923 | 31890.5 | 0
2021012807 | 5 | 0.70249 | 105373.5 | 0.87111 | 0 | 0.18332 | 2291.5 | 0 | 0 | 64000 | 2291.5 | 0 | 39082 | 7191.5 | 1273307.25 | 39082 | 0
2021012808 | 5 | 0.74479 | 111718.5 | 0.92603 | 0 | 0.19025 | 2378.125 | 0.02954 | 2363.2 | 64000 | 2378.125 | 2363.2 | 42977.175 | 3895.175 | 1255796.325 | 42977.175 | 0
2021012809 | 5 | 0.76077 | 114115.5 | 0.94524 | 0 | 0.2022 | 2527.5 | 0.17101 | 13680.8 | 64000 | 2527.5 | 13680.8 | 33907.2 | -9069.975 | 1247355.375 | 33907.2 | 0
2021012810 | 5 | 0.75843 | 113764.5 | 0.95108 | 0 | 0.20761 | 2595.125 | 0.32672 | 26137.6 | 64000 | 2595.125 | 26137.6 | 21031.775 | -12875.425 | 1251789.85 | 21031.775 | 0
2021012811 | 5 | 0.7456 | 111840 | 0.95843 | 0 | 0.19682 | 2460.25 | 0.40526 | 32420.8 | 64000 | 2460.25 | 32420.8 | 12958.95 | -8072.825 | 1264297.15 | 12958.95 | 0
2021012812 | 5 | 0.73038 | 109557 | 0.96449 | 0 | 0.14565 | 1820.625 | 0.41567 | 33253.6 | 64000 | 1820.625 | 33253.6 | 10482.775 | -2476.175 | 1279280.625 | 10482.775 | 0
2021012813 | 5 | 0.71826 | 107739 | 0.97578 | 0 | 0.09682 | 1210.25 | 0.42905 | 34324 | 64000 | 1210.25 | 34324 | 8204.75 | -2278.025 | 1296542.125 | 8204.75 | 0
2021012814 | 5 | 0.71115 | 106672.5 | 0.98221 | 0 | 0.09391 | 1173.875 | 0.45018 | 36014.4 | 64000 | 1173.875 | 36014.4 | 5484.225 | -2720.525 | 1316524.15 | 5484.225 | 0
2021012815 | 5 | 0.70437 | 105655.5 | 0.98497 | 0 | 0.11956 | 1494.5 | 0.39733 | 31786.4 | 64000 | 1494.5 | 31786.4 | 8374.6 | 2890.375 | 1333615.8 | 8374.6 | 0
2021012816 | 5 | 0.70433 | 105649.5 | 0.98704 | 0 | 0.13709 | 1713.625 | 0.20306 | 16244.8 | 64000 | 1713.625 | 16244.8 | 23691.075 | 15316.475 | 1335390.975 | 23691.075 | 0
2021012817 | 5 | 0.72019 | 108028.5 | 0.98812 | 0 | 0.12996 | 1624.5 | 0.03477 | 2781.6 | 64000 | 1624.5 | 2781.6 | 39622.4 | 15931.325 | 1321234.825 | 39622.4 | 0
2021012818 | 5 | 0.75792 | 113688 | 0.98325 | 0 | 0.11426 | 1428.25 | 0 | 0 | 64000 | 1428.25 | 0 | 48259.75 | 8637.35 | 1298441.325 | 48259.75 | 0
2021012819 | 5 | 0.7806 | 117090 | 0.97741 | 0 | 0.12996 | 1624.5 | 0 | 0 | 64000 | 1624.5 | 0 | 51465.5 | 3205.75 | 1272442.075 | 51465.5 | 0
2021012820 | 5 | 0.77618 | 116427 | 0.98201 | 0 | 0.16167 | 2020.875 | 0 | 0 | 64000 | 2020.875 | 0 | 50406.125 | -1059.375 | 1247502.2 | 50406.125 | 0
2021012821 | 5 | 0.76462 | 114693 | 0.98184 | 0 | 0.19172 | 2396.5 | 0 | 0 | 64000 | 2396.5 | 0 | 48296.5 | -2109.625 | 1224671.95 | 48296.5 | 0
2021012822 | 5 | 0.744 | 111600 | 0.98192 | 0 | 0.22552 | 2819 | 0 | 0 | 64000 | 2819 | 0 | 44781 | -3515.5 | 1205357.2 | 44781 | 0
2021012823 | 5 | 0.71532 | 107298 | 0.97651 | 0 | 0.27417 | 3427.125 | 0 | 0 | 64000 | 3427.125 | 0 | 39870.875 | -4910.125 | 1190952.575 | 39870.875 | 0
2021012824 | 5 | 0.6886 | 103290 | 0.96778 | 0 | 0.29241 | 3655.125 | 0 | 0 | 64000 | 3655.125 | 0 | 35634.875 | -4236 | 1180783.95 | 35634.875 | 0
2021012901 | 6 | 0.67135 | 100702.5 | 0.97223 | 0 | 0.31129 | 3891.125 | 0 | 0 | 64000 | 3891.125 | 0 | 32811.375 | -2823.5 | 1173438.825 | 32811.375 | 0
2021012902 | 6 | 0.6617 | 99255 | 0.97067 | 0 | 0.28303 | 3537.875 | 0 | 0 | 64000 | 3537.875 | 0 | 31717.125 | -1094.25 | 1167187.95 | 31717.125 | 0
2021012903 | 6 | 0.65928 | 98892 | 0.97685 | 0 | 0.26517 | 3314.625 | 0 | 0 | 64000 | 3314.625 | 0 | 31577.375 | -139.75 | 1161076.825 | 31577.375 | 0
2021012904 | 6 | 0.66356 | 99534 | 0.97294 | 0 | 0.24107 | 3013.375 | 0 | 0 | 64000 | 3013.375 | 0 | 32520.625 | 943.25 | 1154022.45 | 32520.625 | 0
2021012905 | 6 | 0.67702 | 101553 | 0.9751 | 0 | 0.22639 | 2829.875 | 0 | 0 | 64000 | 2829.875 | 0 | 34723.125 | 2202.5 | 1144765.575 | 34723.125 | 0
2021012906 | 6 | 0.70764 | 106146 | 0.9747 | 0 | 0.20954 | 2619.25 | 0 | 0 | 64000 | 2619.25 | 0 | 39526.75 | 4803.625 | 1130705.075 | 39526.75 | 0
2021012907 | 6 | 0.75376 | 113064 | 0.97626 | 0 | 0.1774 | 2217.5 | 0 | 0 | 64000 | 2217.5 | 0 | 46846.5 | 7319.75 | 1109324.825 | 46846.5 | 0
2021012908 | 6 | 0.78761 | 118141.5 | 0.97654 | 0 | 0.11402 | 1425.25 | 0.04217 | 3373.6 | 64000 | 1425.25 | 3373.6 | 49342.65 | 2496.15 | 1085448.425 | 49342.65 | 0
2021012909 | 6 | 0.78901 | 118351.5 | 0.97684 | 0 | 0.08303 | 1037.875 | 0.31571 | 25256.8 | 64000 | 1037.875 | 25256.8 | 28056.825 | -21285.825 | 1082857.85 | 28056.825 | 0
2021012910 | 6 | 0.77373 | 116059.5 | 0.95651 | 0 | 0.10496 | 1312 | 0.51861 | 41488.8 | 64000 | 1312 | 41488.8 | 9258.7 | -18798.125 | 1099065.4 | 9258.7 | 0
2021012911 | 6 | 0.7592 | 113880 | 0.9627 | 0 | 0.14191 | 1773.875 | 0.54705 | 43764 | 64000 | 1773.875 | 43764 | 4342.125 | -4916.575 | 1120189.525 | 4342.125 | 0
2021012912 | 6 | 0.7447 | 111705 | 0.96246 | 0 | 0.17167 | 2145.875 | 0.54688 | 43750.4 | 64000 | 2145.875 | 43750.4 | 1808.725 | -2533.4 | 1143847.05 | 1808.725 | 0
2021012913 | 6 | 0.73252 | 109878 | 0.98032 | 0 | 0.19268 | 2408.5 | 0.54332 | 43465.6 | 64000 | 2408.5 | 43465.6 | 3.9 | -1804.825 | 1169309.4 | 3.9 | 0
2021012914 | 6 | 0.71989 | 107983.5 | 0.97811 | 0 | 0.23391 | 2923.875 | 0.5558 | 44464 | 64000 | 2923.875 | 41059.625 | 0 | -3.9 | 1194775.65 | 0 | 0
2021012915 | 6 | 0.70951 | 106426.5 | 0.97775 | 0 | 0.36706 | 4588.25 | 0.52393 | 41914.4 | 64000 | 4588.25 | 37838.25 | 0 | 0 | 1220241.9 | 0 | 0
2021012916 | 6 | 0.70657 | 105985.5 | 0.96605 | 0 | 0.41683 | 5210.375 | 0.29895 | 23916 | 64000 | 5210.375 | 23916 | 12859.125 | 12859.125 | 1232849.025 | 12859.125 | 0
2021012917 | 6 | 0.7176 | 107640 | 0.94427 | 0 | 0.40485 | 5060.625 | 0.04217 | 3373.6 | 64000 | 5060.625 | 3373.6 | 35205.775 | 22346.65 | 1223109.5 | 35205.775 | 0
2021012918 | 6 | 0.7468 | 112020 | 0.91839 | 0 | 0.36979 | 4622.375 | 0 | 0 | 64000 | 4622.375 | 0 | 43397.625 | 8191.85 | 1205178.125 | 43397.625 | 0
2021012919 | 6 | 0.76613 | 114919.5 | 0.90217 | 0 | 0.32943 | 4117.875 | 0 | 0 | 64000 | 4117.875 | 0 | 46801.625 | 3404 | 1183842.75 | 46801.625 | 0
2021012920 | 6 | 0.76006 | 114009 | 0.88243 | 0 | 0.29417 | 3677.125 | 0 | 0 | 64000 | 3677.125 | 0 | 46331.875 | -469.75 | 1162977.125 | 46331.875 | 0
2021012921 | 6 | 0.74733 | 112099.5 | 0.8385 | 0 | 0.25202 | 3150.25 | 0 | 0 | 64000 | 3150.25 | 0 | 44949.25 | -1382.625 | 1143494.125 | 44949.25 | 0
2021012922 | 6 | 0.72975 | 109462.5 | 0.86288 | 0 | 0.21379 | 2672.375 | 0 | 0 | 64000 | 2672.375 | 0 | 42790.125 | -2159.125 | 1126170.25 | 42790.125 | 0
2021012923 | 6 | 0.70523 | 105784.5 | 0.82191 | 0 | 0.19319 | 2414.875 | 0 | 0 | 64000 | 2414.875 | 0 | 39369.625 | -3420.5 | 1112266.875 | 39369.625 | 0
2021012924 | 6 | 0.68 | 102000 | 0.79661 | 0 | 0.1926 | 2407.5 | 0 | 0 | 64000 | 2407.5 | 0 | 35592.5 | -3777.125 | 1102140.625 | 35592.5 | 0
2021013001 | 7 | 0.66299 | 99448.5 | 0.82601 | 0 | 0.21095 | 2636.875 | 0 | 0 | 64000 | 2636.875 | 0 | 32811.625 | -2780.875 | 1094795.25 | 32811.625 | 0
2021013002 | 7 | 0.65179 | 97768.5 | 0.8308 | 0 | 0.23311 | 2913.875 | 0 | 0 | 64000 | 2913.875 | 0 | 30854.625 | -1957 | 1089406.875 | 30854.625 | 0
2021013003 | 7 | 0.64878 | 97317 | 0.82257 | 0 | 0.31065 | 3883.125 | 0 | 0 | 64000 | 3883.125 | 0 | 29433.875 | -1420.75 | 1085439.25 | 29433.875 | 0
2021013004 | 7 | 0.64925 | 97387.5 | 0.7935 | 0 | 0.4233 | 5291.25 | 0 | 0 | 64000 | 5291.25 | 0 | 28096.25 | -1337.625 | 1082809.25 | 28096.25 | 0
2021013005 | 7 | 0.65615 | 98422.5 | 0.77914 | 0 | 0.49297 | 6162.125 | 0 | 0 | 64000 | 6162.125 | 0 | 28260.375 | 164.125 | 1080015.125 | 28260.375 | 0
2021013006 | 7 | 0.67146 | 100719 | 0.7022 | 0 | 0.5061 | 6326.25 | 0 | 0 | 64000 | 6326.25 | 0 | 30392.75 | 2132.375 | 1075088.625 | 30392.75 | 0
2021013007 | 7 | 0.6948 | 104220 | 0.6143 | 0 | 0.54769 | 6846.125 | 0 | 0 | 64000 | 6846.125 | 0 | 33373.875 | 2981.125 | 1067181 | 33373.875 | 0
2021013008 | 7 | 0.71678 | 107517 | 0.50262 | 0 | 0.57505 | 7188.125 | 0.03314 | 2651.2 | 64000 | 7188.125 | 2651.2 | 33677.675 | 303.8 | 1058969.575 | 33677.675 | 0
2021013009 | 7 | 0.71833 | 107749.5 | 0.45402 | 0 | 0.64006 | 8000.75 | 0.25125 | 20100 | 64000 | 8000.75 | 20100 | 15648.75 | -18028.925 | 1068787.075 | 15648.75 | 0
2021013010 | 7 | 0.70373 | 105559.5 | 0.36657 | 0 | 0.69265 | 8658.125 | 0.42232 | 33785.6 | 64000 | 8658.125 | 32901.375 | 0 | -15648.75 | 1094253.325 | 0 | 0
2021013011 | 7 | 0.68557 | 102835.5 | 0.21611 | 0 | 0.70154 | 8769.25 | 0.46211 | 36968.8 | 64000 | 8769.25 | 30066.25 | 0 | 0 | 1119719.575 | 0 | 0
2021013012 | 7 | 0.6688 | 100320 | 0.18113 | 0 | 0.66679 | 8334.875 | 0.41807 | 33445.6 | 64000 | 8334.875 | 27985.125 | 0 | 0 | 1145185.825 | 0 | 0
2021013013 | 7 | 0.65058 | 97587 | 0.15921 | 0 | 0.65437 | 8179.625 | 0.41826 | 33460.8 | 64000 | 8179.625 | 25407.375 | 0 | 0 | 1170652.075 | 0 | 0
2021013014 | 7 | 0.63421 | 95131.5 | 0.15413 | 0 | 0.66541 | 8317.625 | 0.3952 | 31616 | 64000 | 8317.625 | 22813.875 | 0 | 0 | 1196118.325 | 0 | 0
2021013015 | 7 | 0.6254 | 93810 | 0.16098 | 0 | 0.72118 | 9014.75 | 0.35251 | 28200.8 | 64000 | 9014.75 | 20795.25 | 0 | 0 | 1221584.575 | 0 | 0
2021013016 | 7 | 0.62572 | 93858 | 0.15876 | 0 | 0.74087 | 9260.875 | 0.28032 | 22425.6 | 64000 | 9260.875 | 20597.125 | 0 | 0 | 1247050.825 | 0 | 0
2021013017 | 7 | 0.64148 | 96222 | 0.14592 | 0 | 0.71978 | 8997.25 | 0.04501 | 3600.8 | 64000 | 8997.25 | 3600.8 | 19623.95 | 19623.95 | 1252893.125 | 19623.95 | 0
2021013018 | 7 | 0.67828 | 101742 | 0.12985 | 0 | 0.71046 | 8880.75 | 0 | 0 | 64000 | 8880.75 | 0 | 28861.25 | 9237.3 | 1249498.125 | 28861.25 | 0
2021013019 | 7 | 0.7009 | 105135 | 0.18963 | 0 | 0.71502 | 8937.75 | 0 | 0 | 64000 | 8937.75 | 0 | 32197.25 | 3336 | 1242767.125 | 32197.25 | 0
2021013020 | 7 | 0.69907 | 104860.5 | 0.21895 | 0 | 0.72732 | 9091.5 | 0 | 0 | 64000 | 9091.5 | 0 | 31769 | -428.25 | 1236464.375 | 31769 | 0
2021013021 | 7 | 0.69168 | 103752 | 0.24006 | 0 | 0.7649 | 9561.25 | 0 | 0 | 64000 | 9561.25 | 0 | 30190.75 | -1578.25 | 1231739.875 | 30190.75 | 0
2021013022 | 7 | 0.6774 | 101610 | 0.35269 | 0 | 0.76574 | 9571.75 | 0 | 0 | 64000 | 9571.75 | 0 | 28038.25 | -2152.5 | 1229167.875 | 28038.25 | 0
2021013023 | 7 | 0.65437 | 98155.5 | 0.44969 | 0 | 0.75923 | 9490.375 | 0 | 0 | 64000 | 9490.375 | 0 | 24665.125 | -3373.125 | 1229969 | 24665.125 | 0
2021013024 | 7 | 0.62963 | 94444.5 | 0.4619 | 0 | 0.75255 | 9406.875 | 0 | 0 | 64000 | 9406.875 | 0 | 21037.625 | -3627.5 | 1234397.625 | 21037.625 | 0
2021013101 | 1 | 0.60846 | 91269 | 0.38616 | 0 | 0.69426 | 8678.25 | 0 | 0 | 64000 | 8678.25 | 0 | 18590.75 | -2446.875 | 1241273.125 | 18590.75 | 0
2021013102 | 1 | 0.59573 | 89359.5 | 0.41325 | 0 | 0.65745 | 8218.125 | 0 | 0 | 64000 | 8218.125 | 0 | 17141.375 | -1449.375 | 1249598 | 17141.375 | 0
2021013103 | 1 | 0.58811 | 88216.5 | 0.46171 | 0 | 0.60453 | 7556.625 | 0 | 0 | 64000 | 7556.625 | 0 | 16659.875 | -481.5 | 1258404.375 | 16659.875 | 0
2021013104 | 1 | 0.58605 | 87907.5 | 0.49759 | 0 | 0.54185 | 6773.125 | 0 | 0 | 64000 | 6773.125 | 0 | 17134.375 | 474.5 | 1266736.25 | 17134.375 | 0
2021013105 | 1 | 0.58776 | 88164 | 0.52697 | 0 | 0.43531 | 5441.375 | 0 | 0 | 64000 | 5441.375 | 0 | 18722.625 | 1588.25 | 1273479.875 | 18722.625 | 0
2021013106 | 1 | 0.59665 | 89497.5 | 0.52553 | 0 | 0.30799 | 3849.875 | 0 | 0 | 64000 | 3849.875 | 0 | 21647.625 | 2925 | 1277298.5 | 21647.625 | 0
2021013107 | 1 | 0.61072 | 91608 | 0.62946 | 0 | 0.22455 | 2806.875 | 0 | 0 | 64000 | 2806.875 | 0 | 24801.125 | 3153.5 | 1277963.625 | 24801.125 | 0
2021013108 | 1 | 0.62849 | 94273.5 | 0.66875 | 0 | 0.18433 | 2304.125 | 0.02103 | 1682.4 | 64000 | 2304.125 | 1682.4 | 26286.975 | 1485.85 | 1277142.9 | 26286.975 | 0
2021013109 | 1 | 0.6463 | 96945 | 0.76343 | 0 | 0.19197 | 2399.625 | 0.17599 | 14079.2 | 64000 | 2399.625 | 14079.2 | 16466.175 | -9820.8 | 1286142.975 | 16466.175 | 0
2021013110 | 1 | 0.66439 | 99658.5 | 0.73922 | 0 | 0.18829 | 2353.625 | 0.35837 | 28669.6 | 64000 | 2353.625 | 28669.6 | 4635.275 | -11830.9 | 1306973.95 | 4635.275 | 0
2021013111 | 1 | 0.67331 | 100996.5 | 0.75982 | 0 | 0.22119 | 2764.875 | 0.39604 | 31683.2 | 64000 | 2764.875 | 31683.2 | 2548.425 | -2086.85 | 1329891.775 | 2548.425 | 0
2021013112 | 1 | 0.67859 | 101788.5 | 0.77975 | 0 | 0.22715 | 2839.375 | 0.45721 | 36576.8 | 64000 | 2839.375 | 34949.125 | 0 | -2548.425 | 1350000 | 0 | 0
2021013113 | 1 | 0.68233 | 102349.5 | 0.78317 | 0 | 0.28551 | 3568.875 | 0.49811 | 39848.8 | 64000 | 3568.875 | 34780.625 | 0 | 0 | 1350000 | 0 | 0
2021013114 | 1 | 0.68094 | 102141 | 0.76886 | 0 | 0.35851 | 4481.375 | 0.51724 | 41379.2 | 64000 | 4481.375 | 33659.625 | 0 | 0 | 1350000 | 0 | 0
2021013115 | 1 | 0.67808 | 101712 | 0.79797 | 0 | 0.37104 | 4638 | 0.51338 | 41070.4 | 64000 | 4638 | 33074 | 0 | 0 | 1350000 | 0 | 0
2021013116 | 1 | 0.67984 | 101976 | 0.81142 | 0 | 0.36347 | 4543.375 | 0.34022 | 27217.6 | 64000 | 4543.375 | 27217.6 | 6215.025 | 6215.025 | 1350000 | 6215.025 | 0
2021013117 | 1 | 0.69059 | 103588.5 | 0.80699 | 0 | 0.33594 | 4199.25 | 0.06168 | 4934.4 | 64000 | 4199.25 | 4934.4 | 30454.85 | 24239.825 | 1345011.4 | 30454.85 | 0
2021013118 | 1 | 0.71363 | 107044.5 | 0.73557 | 0 | 0.24277 | 3034.625 | 0 | 0 | 64000 | 3034.625 | 0 | 40009.875 | 9555.025 | 1330467.775 | 40009.875 | 0
2021013119 | 1 | 0.72461 | 108691.5 | 0.69478 | 0 | 0.16013 | 2001.625 | 0 | 0 | 64000 | 2001.625 | 0 | 42689.875 | 2680 | 1313244.15 | 42689.875 | 0
2021013120 | 1 | 0.71466 | 107199 | 0.76807 | 0 | 0.14612 | 1826.5 | 0 | 0 | 64000 | 1826.5 | 0 | 41372.5 | -1317.375 | 1297337.9 | 41372.5 | 0
2021013121 | 1 | 0.69904 | 104856 | 0.79563 | 0 | 0.15632 | 1954 | 0 | 0 | 64000 | 1954 | 0 | 38902 | -2470.5 | 1283902.15 | 38902 | 0
2021013122 | 1 | 0.67767 | 101650.5 | 0.8462 | 0 | 0.15154 | 1894.25 | 0 | 0 | 64000 | 1894.25 | 0 | 35756.25 | -3145.75 | 1273612.15 | 35756.25 | 0
2021013123 | 1 | 0.65122 | 97683 | 0.84827 | 0 | 0.1763 | 2203.75 | 0 | 0 | 64000 | 2203.75 | 0 | 31479.25 | -4277 | 1267599.15 | 31479.25 | 0
2021013124 | 1 | 0.6275 | 94125 | 0.8422 | 0 | 0.22 | 2750 | 0 | 0 | 64000 | 2750 | 0 | 27375 | -4104.25 | 1265690.4 | 27375 | 0
2021020101 | 2 | 0.60909 | 91363.5 | 0.83475 | 0 | 0.25708 | 3213.5 | 0 | 0 | 64000 | 3213.5 | 0 | 24150 | -3225 | 1267006.65 | 24150 | 0
2021020102 | 2 | 0.60165 | 90247.5 | 0.82835 | 0 | 0.27318 | 3414.75 | 0 | 0 | 64000 | 3414.75 | 0 | 22832.75 | -1317.25 | 1269640.15 | 22832.75 | 0
2021020103 | 2 | 0.59927 | 89890.5 | 0.808 | 0 | 0.2897 | 3621.25 | 0 | 0 | 64000 | 3621.25 | 0 | 22269.25 | -563.5 | 1272837.15 | 22269.25 | 0
2021020104 | 2 | 0.60291 | 90436.5 | 0.80865 | 0 | 0.32285 | 4035.625 | 0 | 0 | 64000 | 4035.625 | 0 | 22400.875 | 131.625 | 1275902.525 | 22400.875 | 0
2021020105 | 2 | 0.6148 | 92220 | 0.78761 | 0 | 0.33645 | 4205.625 | 0 | 0 | 64000 | 4205.625 | 0 | 24014.375 | 1613.5 | 1277354.4 | 24014.375 | 0
2021020106 | 2 | 0.64116 | 96174 | 0.70735 | 0 | 0.36347 | 4543.375 | 0 | 0 | 64000 | 4543.375 | 0 | 27630.625 | 3616.25 | 1275190.025 | 27630.625 | 0
2021020107 | 2 | 0.67934 | 101901 | 0.62682 | 0 | 0.3549 | 4436.25 | 0 | 0 | 64000 | 4436.25 | 0 | 33464.75 | 5834.125 | 1267191.525 | 33464.75 | 0
2021020108 | 2 | 0.71368 | 107052 | 0.60644 | 0 | 0.34684 | 4335.5 | 0.04714 | 3771.2 | 64000 | 4335.5 | 3771.2 | 34945.3 | 1480.55 | 1257712.475 | 34945.3 | 0
2021020109 | 2 | 0.73306 | 109959 | 0.60441 | 0 | 0.35323 | 4415.375 | 0.32687 | 26149.6 | 64000 | 4415.375 | 26149.6 | 15394.025 | -19551.275 | 1267784.7 | 15394.025 | 0
2021020110 | 2 | 0.74178 | 111267 | 0.57589 | 0 | 0.3426 | 4282.5 | 0.52371 | 41896.8 | 64000 | 4282.5 | 41896.8 | 1087.7 | -14306.325 | 1292163.25 | 1087.7 | 0
2021020111 | 2 | 0.7435 | 111525 | 0.49918 | 0 | 0.30682 | 3835.25 | 0.52214 | 41771.2 | 64000 | 3835.25 | 41771.2 | 1918.55 | 830.85 | 1315710.95 | 1918.55 | 0
2021020112 | 2 | 0.74236 | 111354 | 0.42017 | 0 | 0.2365 | 2956.25 | 0.48528 | 38822.4 | 64000 | 2956.25 | 38822.4 | 5575.35 | 3656.8 | 1335601.85 | 5575.35 | 0
2021020113 | 2 | 0.73971 | 110956.5 | 0.35896 | 0 | 0.21034 | 2629.25 | 0.48015 | 38412 | 64000 | 2629.25 | 38412 | 5915.25 | 339.9 | 1350000 | 5915.25 | 0
2021020114 | 2 | 0.73367 | 110050.5 | 0.36802 | 0 | 0.23108 | 2888.5 | 0.43889 | 35111.2 | 64000 | 2888.5 | 35111.2 | 8050.8 | 2135.55 | 1350000 | 8050.8 | 0
2021020115 | 2 | 0.7264 | 108960 | 0.39468 | 0 | 0.31729 | 3966.125 | 0.38422 | 30737.6 | 64000 | 3966.125 | 30737.6 | 10256.275 | 2205.475 | 1350000 | 10256.275 | 0
2021020116 | 2 | 0.72258 | 108387 | 0.43778 | 0 | 0.42628 | 5328.5 | 0.23855 | 19084 | 64000 | 5328.5 | 19084 | 19974.5 | 9718.225 | 1350000 | 19974.5 | 0
2021020117 | 2 | 0.72931 | 109396.5 | 0.51423 | 0 | 0.45697 | 5712.125 | 0.04485 | 3588 | 64000 | 5712.125 | 3588 | 36096.375 | 16121.875 | 1339369.875 | 36096.375 | 0
2021020118 | 2 | 0.75139 | 112708.5 | 0.57085 | 0 | 0.46103 | 5762.875 | 9e-05 | 7.2 | 64000 | 5762.875 | 7.2 | 42938.425 | 6842.05 | 1321897.7 | 42938.425 | 0
2021020119 | 2 | 0.76423 | 114634.5 | 0.60838 | 0 | 0.48264 | 6033 | 0 | 0 | 64000 | 6033 | 0 | 44601.5 | 1663.075 | 1302762.45 | 44601.5 | 0
2021020120 | 2 | 0.75281 | 112921.5 | 0.64354 | 0 | 0.51831 | 6478.875 | 0 | 0 | 64000 | 6478.875 | 0 | 42442.625 | -2158.875 | 1285786.075 | 42442.625 | 0
2021020121 | 2 | 0.73457 | 110185.5 | 0.66431 | 0 | 0.50354 | 6294.25 | 0 | 0 | 64000 | 6294.25 | 0 | 39891.25 | -2551.375 | 1271361.075 | 39891.25 | 0
2021020122 | 2 | 0.70787 | 106180.5 | 0.69897 | 0 | 0.53514 | 6689.25 | 0 | 0 | 64000 | 6689.25 | 0 | 35491.25 | -4400 | 1261336.075 | 35491.25 | 0
2021020123 | 2 | 0.67514 | 101271 | 0.76349 | 0 | 0.59352 | 7419 | 0 | 0 | 64000 | 7419 | 0 | 29852 | -5639.25 | 1256950.325 | 29852 | 0
2021020124 | 2 | 0.64605 | 96907.5 | 0.78448 | 0 | 0.60796 | 7599.5 | 0 | 0 | 64000 | 7599.5 | 0 | 25308 | -4544 | 1257108.575 | 25308 | 0
2021020201 | 3 | 0.62588 | 93882 | 0.81425 | 0 | 0.57491 | 7186.375 | 0 | 0 | 64000 | 7186.375 | 0 | 22695.625 | -2612.375 | 1259879.2 | 22695.625 | 0
2021020202 | 3 | 0.61434 | 92151 | 0.82553 | 0 | 0.54038 | 6754.75 | 0 | 0 | 64000 | 6754.75 | 0 | 21396.25 | -1299.375 | 1263949.2 | 21396.25 | 0
2021020203 | 3 | 0.61082 | 91623 | 0.84115 | 0 | 0.50101 | 6262.625 | 0 | 0 | 64000 | 6262.625 | 0 | 21360.375 | -35.875 | 1268055.075 | 21360.375 | 0
2021020204 | 3 | 0.61142 | 91713 | 0.85051 | 0 | 0.4953 | 6191.25 | 0 | 0 | 64000 | 6191.25 | 0 | 21521.75 | 161.375 | 1271999.575 | 21521.75 | 0
2021020205 | 3 | 0.62376 | 93564 | 0.87471 | 0 | 0.47511 | 5938.875 | 0 | 0 | 64000 | 5938.875 | 0 | 23625.125 | 2103.375 | 1273840.7 | 23625.125 | 0
2021020206 | 3 | 0.65062 | 97593 | 0.88238 | 0 | 0.4828 | 6035 | 0 | 0 | 64000 | 6035 | 0 | 27558 | 3932.875 | 1271748.95 | 27558 | 0
2021020207 | 3 | 0.69027 | 103540.5 | 0.89438 | 0 | 0.5202 | 6502.5 | 0 | 0 | 64000 | 6502.5 | 0 | 33038 | 5480 | 1264177.2 | 33038 | 0
2021020208 | 3 | 0.72208 | 108312 | 0.88756 | 0 | 0.54814 | 6851.75 | 0.04765 | 3812 | 64000 | 6851.75 | 3812 | 33648.25 | 610.25 | 1255995.2 | 33648.25 | 0
2021020209 | 3 | 0.73618 | 110427 | 0.89315 | 0 | 0.56228 | 7028.5 | 0.30098 | 24078.4 | 64000 | 7028.5 | 24078.4 | 15320.1 | -18328.15 | 1266141.35 | 15320.1 | 0
2021020210 | 3 | 0.73674 | 110511 | 0.91541 | 0 | 0.54506 | 6813.25 | 0.47389 | 37911.2 | 64000 | 6813.25 | 37911.2 | 1786.55 | -13533.55 | 1289821.05 | 1786.55 | 0
2021020211 | 3 | 0.73223 | 109834.5 | 0.91272 | 0 | 0.55478 | 6934.75 | 0.49764 | 39811.2 | 64000 | 6934.75 | 38899.75 | 0 | -1786.55 | 1315287.3 | 0 | 0
2021020212 | 3 | 0.72406 | 108609 | 0.90738 | 0 | 0.52302 | 6537.75 | 0.48904 | 39123.2 | 64000 | 6537.75 | 38071.25 | 0 | 0 | 1340753.55 | 0 | 0
2021020213 | 3 | 0.71693 | 107539.5 | 0.91393 | 0 | 0.46997 | 5874.625 | 0.5327 | 42616 | 64000 | 5874.625 | 37664.875 | 0 | 0 | 1350000 | 0 | 0
2021020214 | 3 | 0.70966 | 106449 | 0.96621 | 0 | 0.37957 | 4744.625 | 0.58197 | 46557.6 | 64000 | 4744.625 | 37704.375 | 0 | 0 | 1350000 | 0 | 0
2021020215 | 3 | 0.70307 | 105460.5 | 0.98767 | 0 | 0.35737 | 4467.125 | 0.60064 | 48051.2 | 64000 | 4467.125 | 36993.375 | 0 | 0 | 1350000 | 0 | 0
2021020216 | 3 | 0.70194 | 105291 | 0.9945 | 0 | 0.33279 | 4159.875 | 0.35976 | 28780.8 | 64000 | 4159.875 | 28780.8 | 8350.325 | 8350.325 | 1350000 | 8350.325 | 0
2021020217 | 3 | 0.71039 | 106558.5 | 0.99805 | 0 | 0.2773 | 3466.25 | 0.04986 | 3988.8 | 64000 | 3466.25 | 3988.8 | 35103.45 | 26753.125 | 1340362.8 | 35103.45 | 0
2021020218 | 3 | 0.73817 | 110725.5 | 0.99923 | 0 | 0.22817 | 2852.125 | 0 | 0 | 64000 | 2852.125 | 0 | 43873.375 | 8769.925 | 1321955.675 | 43873.375 | 0
2021020219 | 3 | 0.75855 | 113782.5 | 0.99659 | 0 | 0.19932 | 2491.5 | 0 | 0 | 64000 | 2491.5 | 0 | 47291 | 3417.625 | 1300130.925 | 47291 | 0
2021020220 | 3 | 0.75042 | 112563 | 0.99327 | 0 | 0.19093 | 2386.625 | 0 | 0 | 64000 | 2386.625 | 0 | 46176.375 | -1114.625 | 1279420.8 | 46176.375 | 0
2021020221 | 3 | 0.73396 | 110094 | 0.99085 | 0 | 0.19736 | 2467 | 0 | 0 | 64000 | 2467 | 0 | 43627 | -2549.375 | 1261260.05 | 43627 | 0
2021020222 | 3 | 0.71112 | 106668 | 0.98619 | 0 | 0.21948 | 2743.5 | 0 | 0 | 64000 | 2743.5 | 0 | 39924.5 | -3702.5 | 1246801.8 | 39924.5 | 0
2021020223 | 3 | 0.68062 | 102093 | 0.98551 | 0 | 0.22488 | 2811 | 0 | 0 | 64000 | 2811 | 0 | 35282 | -4642.5 | 1236986.05 | 35282 | 0
2021020224 | 3 | 0.65215 | 97822.5 | 0.98929 | 0 | 0.23958 | 2994.75 | 0 | 0 | 64000 | 2994.75 | 0 | 30827.75 | -4454.25 | 1231624.55 | 30827.75 | 0
2021020301 | 4 | 0.6331 | 94965 | 0.98943 | 0 | 0.27654 | 3456.75 | 0 | 0 | 64000 | 3456.75 | 0 | 27508.25 | -3319.5 | 1229582.55 | 27508.25 | 0
2021020302 | 4 | 0.62422 | 93633 | 0.98679 | 0 | 0.33904 | 4238 | 0 | 0 | 64000 | 4238 | 0 | 25395 | -2113.25 | 1229653.8 | 25395 | 0
2021020303 | 4 | 0.62105 | 93157.5 | 0.98529 | 0 | 0.40904 | 5113 | 0 | 0 | 64000 | 5113 | 0 | 24044.5 | -1350.5 | 1231075.55 | 24044.5 | 0
2021020304 | 4 | 0.62262 | 93393 | 0.98547 | 0 | 0.45147 | 5643.375 | 0 | 0 | 64000 | 5643.375 | 0 | 23749.625 | -294.875 | 1232792.175 | 23749.625 | 0
2021020305 | 4 | 0.63577 | 95365.5 | 0.98918 | 0 | 0.47413 | 5926.625 | 0 | 0 | 64000 | 5926.625 | 0 | 25438.875 | 1689.25 | 1232819.55 | 25438.875 | 0
2021020306 | 4 | 0.66403 | 99604.5 | 0.98898 | 0 | 0.48694 | 6086.75 | 0 | 0 | 64000 | 6086.75 | 0 | 29517.75 | 4078.875 | 1228768.05 | 29517.75 | 0
2021020307 | 4 | 0.70838 | 106257 | 0.99095 | 0 | 0.48801 | 6100.125 | 0 | 0 | 64000 | 6100.125 | 0 | 36156.875 | 6639.125 | 1218077.425 | 36156.875 | 0
2021020308 | 4 | 0.74343 | 111514.5 | 0.99333 | 0 | 0.61197 | 7649.625 | 0.02894 | 2315.2 | 64000 | 7649.625 | 2315.2 | 37549.675 | 1392.8 | 1205994 | 37549.675 | 0
2021020309 | 4 | 0.74978 | 112467 | 0.99092 | 0 | 0.67502 | 8437.75 | 0.17252 | 13801.6 | 64000 | 8437.75 | 13801.6 | 26227.65 | -11322.025 | 1205232.6 | 26227.65 | 0
2021020310 | 4 | 0.73916 | 110874 | 0.98934 | 0 | 0.69491 | 8686.375 | 0.32159 | 25727.2 | 64000 | 8686.375 | 25727.2 | 12460.425 | -13767.225 | 1218238.425 | 12460.425 | 0
2021020311 | 4 | 0.72701 | 109051.5 | 0.98814 | 0 | 0.7188 | 8985 | 0.42151 | 33720.8 | 64000 | 8985 | 33720.8 | 2345.7 | -10114.725 | 1241358.975 | 2345.7 | 0
2021020312 | 4 | 0.71418 | 107127 | 0.98761 | 0 | 0.71764 | 8970.5 | 0.46735 | 37388 | 64000 | 8970.5 | 34156.5 | 0 | -2345.7 | 1266825.225 | 0 | 0
2021020313 | 4 | 0.70087 | 105130.5 | 0.98225 | 0 | 0.703 | 8787.5 | 0.48093 | 38474.4 | 64000 | 8787.5 | 32343 | 0 | 0 | 1292291.475 | 0 | 0
2021020314 | 4 | 0.68882 | 103323 | 0.98421 | 0 | 0.63675 | 7959.375 | 0.50876 | 40700.8 | 64000 | 7959.375 | 31363.625 | 0 | 0 | 1317757.725 | 0 | 0
2021020315 | 4 | 0.67678 | 101517 | 0.98899 | 0 | 0.55313 | 6914.125 | 0.51202 | 40961.6 | 64000 | 6914.125 | 30602.875 | 0 | 0 | 1343223.975 | 0 | 0
2021020316 | 4 | 0.67038 | 100557 | 0.98876 | 0 | 0.59376 | 7422 | 0.30892 | 24713.6 | 64000 | 7422 | 24713.6 | 4421.4 | 4421.4 | 1350000 | 4421.4 | 0
2021020317 | 4 | 0.67787 | 101680.5 | 0.98845 | 0 | 0.5902 | 7377.5 | 0.0474 | 3792 | 64000 | 7377.5 | 3792 | 26511 | 22089.6 | 1348955.25 | 26511 | 0
2021020318 | 4 | 0.70872 | 106308 | 0.98714 | 0 | 0.56681 | 7085.125 | 0 | 0 | 64000 | 7085.125 | 0 | 35222.875 | 8711.875 | 1339198.625 | 35222.875 | 0
2021020319 | 4 | 0.73519 | 110278.5 | 0.98191 | 0 | 0.54853 | 6856.625 | 0 | 0 | 64000 | 6856.625 | 0 | 39421.875 | 4199 | 1325243 | 39421.875 | 0
2021020320 | 4 | 0.73403 | 110104.5 | 0.98028 | 0 | 0.53724 | 6715.5 | 0 | 0 | 64000 | 6715.5 | 0 | 39389 | -32.875 | 1311320.25 | 39389 | 0
2021020321 | 4 | 0.72328 | 108492 | 0.97388 | 0 | 0.50788 | 6348.5 | 0 | 0 | 64000 | 6348.5 | 0 | 38143.5 | -1245.5 | 1298643 | 38143.5 | 0
2021020322 | 4 | 0.70443 | 105664.5 | 0.97856 | 0 | 0.54551 | 6818.875 | 0 | 0 | 64000 | 6818.875 | 0 | 34845.625 | -3297.875 | 1289263.625 | 34845.625 | 0
2021020323 | 4 | 0.67543 | 101314.5 | 0.98531 | 0 | 0.57514 | 7189.25 | 0 | 0 | 64000 | 7189.25 | 0 | 30125.25 | -4720.375 | 1284604.625 | 30125.25 | 0
2021020324 | 4 | 0.65068 | 97602 | 0.9831 | 0 | 0.60856 | 7607 | 0 | 0 | 64000 | 7607 | 0 | 25995 | -4130.25 | 1284075.875 | 25995 | 0
2021020401 | 5 | 0.63435 | 95152.5 | 0.97689 | 0 | 0.61277 | 7659.625 | 0 | 0 | 64000 | 7659.625 | 0 | 23492.875 | -2502.125 | 1286049.25 | 23492.875 | 0
2021020402 | 5 | 0.62686 | 94029 | 0.97042 | 0 | 0.59238 | 7404.75 | 0 | 0 | 64000 | 7404.75 | 0 | 22624.25 | -868.625 | 1288891.25 | 22624.25 | 0
2021020403 | 5 | 0.62434 | 93651 | 0.95999 | 0 | 0.56159 | 7019.875 | 0 | 0 | 64000 | 7019.875 | 0 | 22631.125 | 6.875 | 1291726.375 | 22631.125 | 0
2021020404 | 5 | 0.62976 | 94464 | 0.93794 | 0 | 0.52001 | 6500.125 | 0 | 0 | 64000 | 6500.125 | 0 | 23963.875 | 1332.75 | 1293228.75 | 23963.875 | 0
2021020405 | 5 | 0.64476 | 96714 | 0.92751 | 0 | 0.44517 | 5564.625 | 0 | 0 | 64000 | 5564.625 | 0 | 27149.375 | 3185.5 | 1291545.625 | 27149.375 | 0
2021020406 | 5 | 0.677 | 101550 | 0.92415 | 0 | 0.41373 | 5171.625 | 0 | 0 | 64000 | 5171.625 | 0 | 32378.375 | 5229 | 1284633.5 | 32378.375 | 0
2021020407 | 5 | 0.72544 | 108816 | 0.93605 | 0 | 0.38074 | 4759.25 | 0 | 0 | 64000 | 4759.25 | 0 | 40056.75 | 7678.375 | 1270043 | 40056.75 | 0
2021020408 | 5 | 0.75794 | 113691 | 0.94735 | 0 | 0.34932 | 4366.5 | 0.0406 | 3248 | 64000 | 4366.5 | 3248 | 42076.5 | 2019.75 | 1253432.75 | 42076.5 | 0
2021020409 | 5 | 0.75727 | 113590.5 | 0.94365 | 0 | 0.33057 | 4132.125 | 0.31902 | 25521.6 | 64000 | 4132.125 | 25521.6 | 19936.775 | -22139.725 | 1258962.225 | 19936.775 | 0
2021020410 | 5 | 0.73448 | 110172 | 0.86445 | 0 | 0.28585 | 3573.125 | 0.54342 | 43473.6 | 64000 | 3573.125 | 42598.875 | 0 | -19936.775 | 1284428.475 | 0 | 0
2021020411 | 5 | 0.71172 | 106758 | 0.55906 | 0 | 0.27669 | 3458.625 | 0.58311 | 46648.8 | 64000 | 3458.625 | 39299.375 | 0 | 0 | 1309894.725 | 0 | 0
2021020412 | 5 | 0.69206 | 103809 | 0.31412 | 0 | 0.25053 | 3131.625 | 0.57227 | 45781.6 | 64000 | 3131.625 | 36677.375 | 0 | 0 | 1335360.975 | 0 | 0
2021020413 | 5 | 0.67518 | 101277 | 0.26605 | 0 | 0.22498 | 2812.25 | 0.5793 | 46344 | 64000 | 2812.25 | 34464.75 | 0 | 0 | 1350000 | 0 | 0
2021020414 | 5 | 0.66317 | 99475.5 | 0.19533 | 0 | 0.25226 | 3153.25 | 0.57861 | 46288.8 | 64000 | 3153.25 | 32322.25 | 0 | 0 | 1350000 | 0 | 0
2021020415 | 5 | 0.65334 | 98001 | 0.11592 | 0 | 0.30452 | 3806.5 | 0.5462 | 43696 | 64000 | 3806.5 | 30194.5 | 0 | 0 | 1350000 | 0 | 0
2021020416 | 5 | 0.65016 | 97524 | 0.12822 | 0 | 0.37865 | 4733.125 | 0.37322 | 29857.6 | 64000 | 4733.125 | 28790.875 | 0 | 0 | 1350000 | 0 | 0
2021020417 | 5 | 0.66285 | 99427.5 | 0.21935 | 0 | 0.3803 | 4753.75 | 0.06951 | 5560.8 | 64000 | 4753.75 | 5560.8 | 25112.95 | 25112.95 | 1350000 | 25112.95 | 0
2021020418 | 5 | 0.69383 | 104074.5 | 0.42877 | 0 | 0.39018 | 4877.25 | 0 | 0 | 64000 | 4877.25 | 0 | 35197.25 | 10084.3 | 1340269 | 35197.25 | 0
2021020419 | 5 | 0.71458 | 107187 | 0.64077 | 0 | 0.36595 | 4574.375 | 0 | 0 | 64000 | 4574.375 | 0 | 38612.625 | 3415.375 | 1327122.625 | 38612.625 | 0
2021020420 | 5 | 0.70857 | 106285.5 | 0.70243 | 0 | 0.3499 | 4373.75 | 0 | 0 | 64000 | 4373.75 | 0 | 37911.75 | -700.875 | 1314677.125 | 37911.75 | 0
2021020421 | 5 | 0.69429 | 104143.5 | 0.74966 | 0 | 0.34717 | 4339.625 | 0 | 0 | 64000 | 4339.625 | 0 | 35803.875 | -2107.875 | 1304339.5 | 35803.875 | 0
2021020422 | 5 | 0.67016 | 100524 | 0.80537 | 0 | 0.38107 | 4763.375 | 0 | 0 | 64000 | 4763.375 | 0 | 31760.625 | -4043.25 | 1298045.125 | 31760.625 | 0
2021020423 | 5 | 0.63887 | 95830.5 | 0.90066 | 0 | 0.37563 | 4695.375 | 0 | 0 | 64000 | 4695.375 | 0 | 27135.125 | -4625.5 | 1296376.25 | 27135.125 | 0
2021020424 | 5 | 0.60914 | 91371 | 0.9564 | 0 | 0.34995 | 4374.375 | 0 | 0 | 64000 | 4374.375 | 0 | 22996.625 | -4138.5 | 1298845.875 | 22996.625 | 0
2021020501 | 6 | 0.58939 | 88408.5 | 0.95719 | 0 | 0.3653 | 4566.25 | 0 | 0 | 64000 | 4566.25 | 0 | 19842.25 | -3154.375 | 1304469.875 | 19842.25 | 0
2021020502 | 6 | 0.5762 | 86430 | 0.93822 | 0 | 0.37896 | 4737 | 0 | 0 | 64000 | 4737 | 0 | 17693 | -2149.25 | 1312243.125 | 17693 | 0
2021020503 | 6 | 0.57136 | 85704 | 0.90844 | 0 | 0.3597 | 4496.25 | 0 | 0 | 64000 | 4496.25 | 0 | 17207.75 | -485.25 | 1320501.625 | 17207.75 | 0
2021020504 | 6 | 0.57293 | 85939.5 | 0.90823 | 0 | 0.34763 | 4345.375 | 0 | 0 | 64000 | 4345.375 | 0 | 17594.125 | 386.375 | 1328373.75 | 17594.125 | 0
2021020505 | 6 | 0.58508 | 87762 | 0.91116 | 0 | 0.35389 | 4423.625 | 0 | 0 | 64000 | 4423.625 | 0 | 19338.375 | 1744.25 | 1334501.625 | 19338.375 | 0
2021020506 | 6 | 0.61309 | 91963.5 | 0.9191 | 0 | 0.32289 | 4036.125 | 0 | 0 | 64000 | 4036.125 | 0 | 23927.375 | 4589 | 1336040.5 | 23927.375 | 0
2021020507 | 6 | 0.65696 | 98544 | 0.95698 | 0 | 0.29307 | 3663.375 | 0 | 0 | 64000 | 3663.375 | 0 | 30880.625 | 6953.25 | 1330626.125 | 30880.625 | 0
2021020508 | 6 | 0.69318 | 103977 | 0.95398 | 0 | 0.27913 | 3489.125 | 0.03385 | 2708 | 64000 | 3489.125 | 2708 | 33779.875 | 2899.25 | 1322312.5 | 33779.875 | 0
2021020509 | 6 | 0.70324 | 105486 | 0.89917 | 0 | 0.26184 | 3273 | 0.24794 | 19835.2 | 64000 | 3273 | 19835.2 | 18377.8 | -15402.075 | 1329400.95 | 18377.8 | 0
2021020510 | 6 | 0.6949 | 104235 | 0.83478 | 0 | 0.27798 | 3474.75 | 0.51587 | 41269.6 | 64000 | 3474.75 | 36760.25 | 0 | -18377.8 | 1350000 | 0 | 0
2021020511 | 6 | 0.68155 | 102232.5 | 0.85879 | 0 | 0.26659 | 3332.375 | 0.53064 | 42451.2 | 64000 | 3332.375 | 34900.125 | 0 | 0 | 1350000 | 0 | 0
2021020512 | 6 | 0.66867 | 100300.5 | 0.8316 | 0 | 0.27022 | 3377.75 | 0.52762 | 42209.6 | 64000 | 3377.75 | 32922.75 | 0 | 0 | 1350000 | 0 | 0
2021020513 | 6 | 0.65871 | 98806.5 | 0.85091 | 0 | 0.26595 | 3324.375 | 0.53908 | 43126.4 | 64000 | 3324.375 | 31482.125 | 0 | 0 | 1350000 | 0 | 0
2021020514 | 6 | 0.65009 | 97513.5 | 0.86088 | 0 | 0.27043 | 3380.375 | 0.51804 | 41443.2 | 64000 | 3380.375 | 30133.125 | 0 | 0 | 1350000 | 0 | 0
2021020515 | 6 | 0.64294 | 96441 | 0.88964 | 0 | 0.2994 | 3742.5 | 0.43528 | 34822.4 | 64000 | 3742.5 | 28698.5 | 0 | 0 | 1350000 | 0 | 0
2021020516 | 6 | 0.63845 | 95767.5 | 0.90672 | 0 | 0.30791 | 3848.875 | 0.25729 | 20583.2 | 64000 | 3848.875 | 20583.2 | 7335.425 | 7335.425 | 1350000 | 7335.425 | 0
2021020517 | 6 | 0.64523 | 96784.5 | 0.92297 | 0 | 0.33919 | 4239.875 | 0.03179 | 2543.2 | 64000 | 4239.875 | 2543.2 | 26001.425 | 18666 | 1349464.825 | 26001.425 | 0
2021020518 | 6 | 0.66793 | 100189.5 | 0.95385 | 0 | 0.39173 | 4896.625 | 0 | 0 | 64000 | 4896.625 | 0 | 31292.875 | 5291.45 | 1343638.2 | 31292.875 | 0
2021020519 | 6 | 0.69117 | 103675.5 | 0.93453 | 0 | 0.39902 | 4987.75 | 0 | 0 | 64000 | 4987.75 | 0 | 34687.75 | 3394.875 | 1334416.7 | 34687.75 | 0
2021020520 | 6 | 0.68701 | 103051.5 | 0.90335 | 0 | 0.42002 | 5250.25 | 0 | 0 | 64000 | 5250.25 | 0 | 33801.25 | -886.5 | 1326081.7 | 33801.25 | 0
2021020521 | 6 | 0.67557 | 101335.5 | 0.93841 | 0 | 0.4773 | 5966.25 | 0 | 0 | 64000 | 5966.25 | 0 | 31369.25 | -2432 | 1320178.7 | 31369.25 | 0
2021020522 | 6 | 0.65978 | 98967 | 0.95718 | 0 | 0.50384 | 6298 | 0 | 0 | 64000 | 6298 | 0 | 28669 | -2700.25 | 1316975.95 | 28669 | 0
2021020523 | 6 | 0.63712 | 95568 | 0.88414 | 0 | 0.528 | 6600 | 0 | 0 | 64000 | 6600 | 0 | 24968 | -3701 | 1317474.2 | 24968 | 0
2021020524 | 6 | 0.61248 | 91872 | 0.75482 | 0 | 0.53889 | 6736.125 | 0 | 0 | 64000 | 6736.125 | 0 | 21135.875 | -3832.125 | 1321804.575 | 21135.875 | 0
2021020601 | 7 | 0.59444 | 89166 | 0.71054 | 0 | 0.54521 | 6815.125 | 0 | 0 | 64000 | 6815.125 | 0 | 18350.875 | -2785 | 1328919.95 | 18350.875 | 0
2021020602 | 7 | 0.5872 | 88080 | 0.79189 | 0 | 0.56798 | 7099.75 | 0 | 0 | 64000 | 7099.75 | 0 | 16980.25 | -1370.625 | 1337405.95 | 16980.25 | 0
2021020603 | 7 | 0.58472 | 87708 | 0.85488 | 0 | 0.61559 | 7694.875 | 0 | 0 | 64000 | 7694.875 | 0 | 16013.125 | -967.125 | 1346859.075 | 16013.125 | 0
2021020604 | 7 | 0.58598 | 87897 | 0.88606 | 0 | 0.6347 | 7933.75 | 0 | 0 | 64000 | 7933.75 | 0 | 15963.25 | -49.875 | 1350000 | 15963.25 | 0
2021020605 | 7 | 0.59422 | 89133 | 0.91234 | 0 | 0.67408 | 8426 | 0 | 0 | 64000 | 8426 | 0 | 16707 | 743.75 | 1350000 | 16707 | 0
2021020606 | 7 | 0.61008 | 91512 | 0.92291 | 0 | 0.67276 | 8409.5 | 0 | 0 | 64000 | 8409.5 | 0 | 19102.5 | 2395.5 | 1350000 | 19102.5 | 0
2021020607 | 7 | 0.63219 | 94828.5 | 0.89871 | 0 | 0.68355 | 8544.375 | 0 | 0 | 64000 | 8544.375 | 0 | 22284.125 | 3181.625 | 1350000 | 22284.125 | 0
2021020608 | 7 | 0.65259 | 97888.5 | 0.88515 | 0 | 0.68864 | 8608 | 0.04016 | 3212.8 | 64000 | 8608 | 3212.8 | 22067.7 | -216.425 | 1350000 | 22067.7 | 0
2021020609 | 7 | 0.65867 | 98800.5 | 0.89671 | 0 | 0.67291 | 8411.375 | 0.31164 | 24931.2 | 64000 | 8411.375 | 24931.2 | 1457.925 | -20609.775 | 1350000 | 1457.925 | 0
2021020610 | 7 | 0.65183 | 97774.5 | 0.92373 | 0 | 0.65348 | 8168.5 | 0.52138 | 41710.4 | 64000 | 8168.5 | 25606 | 0 | -1457.925 | 1350000 | 0 | 0
2021020611 | 7 | 0.64011 | 96016.5 | 0.97188 | 0 | 0.65539 | 8192.375 | 0.5503 | 44024 | 64000 | 8192.375 | 23824.125 | 0 | 0 | 1350000 | 0 | 0
2021020612 | 7 | 0.62708 | 94062 | 0.97516 | 0 | 0.63938 | 7992.25 | 0.52792 | 42233.6 | 64000 | 7992.25 | 22069.75 | 0 | 0 | 1350000 | 0 | 0
2021020613 | 7 | 0.61596 | 92394 | 0.97836 | 0 | 0.59318 | 7414.75 | 0.51628 | 41302.4 | 64000 | 7414.75 | 20979.25 | 0 | 0 | 1350000 | 0 | 0
2021020614 | 7 | 0.60289 | 90433.5 | 0.96562 | 0 | 0.55708 | 6963.5 | 0.51204 | 40963.2 | 64000 | 6963.5 | 19470 | 0 | 0 | 1350000 | 0 | 0
2021020615 | 7 | 0.59351 | 89026.5 | 0.92826 | 0 | 0.56859 | 7107.375 | 0.47219 | 37775.2 | 64000 | 7107.375 | 17919.125 | 0 | 0 | 1350000 | 0 | 0
2021020616 | 7 | 0.59287 | 88930.5 | 0.80764 | 0 | 0.60175 | 7521.875 | 0.28469 | 22775.2 | 64000 | 7521.875 | 17408.625 | 0 | 0 | 1350000 | 0 | 0
2021020617 | 7 | 0.60643 | 90964.5 | 0.59945 | 0 | 0.57386 | 7173.25 | 0.06491 | 5192.8 | 64000 | 7173.25 | 5192.8 | 14598.45 | 14598.45 | 1350000 | 14598.45 | 0
2021020618 | 7 | 0.63636 | 95454 | 0.28107 | 0 | 0.58904 | 7363 | 0 | 0 | 64000 | 7363 | 0 | 24091 | 9492.55 | 1350000 | 24091 | 0
2021020619 | 7 | 0.6626 | 99390 | 0.22521 | 0 | 0.5676 | 7095 | 0 | 0 | 64000 | 7095 | 0 | 28295 | 4204 | 1347171.25 | 28295 | 0
2021020620 | 7 | 0.66434 | 99651 | 0.31972 | 0 | 0.53205 | 6650.625 | 0 | 0 | 64000 | 6650.625 | 0 | 29000.375 | 705.375 | 1343637.125 | 29000.375 | 0
2021020621 | 7 | 0.65637 | 98455.5 | 0.37692 | 0 | 0.48725 | 6090.625 | 0 | 0 | 64000 | 6090.625 | 0 | 28364.875 | -635.5 | 1340738.5 | 28364.875 | 0
2021020622 | 7 | 0.64189 | 96283.5 | 0.45369 | 0 | 0.49745 | 6218.125 | 0 | 0 | 64000 | 6218.125 | 0 | 26065.375 | -2299.5 | 1340139.375 | 26065.375 | 0
2021020623 | 7 | 0.62235 | 93352.5 | 0.47369 | 0 | 0.51229 | 6403.625 | 0 | 0 | 64000 | 6403.625 | 0 | 22948.875 | -3116.5 | 1342656.75 | 22948.875 | 0
2021020624 | 7 | 0.60117 | 90175.5 | 0.44442 | 0 | 0.52513 | 6564.125 | 0 | 0 | 64000 | 6564.125 | 0 | 19611.375 | -3337.5 | 1348511.625 | 19611.375 | 0
2021020701 | 1 | 0.5834 | 87510 | 0.46769 | 0 | 0.52673 | 6584.125 | 0 | 0 | 64000 | 6584.125 | 0 | 16925.875 | -2685.5 | 1350000 | 16925.875 | 0
2021020702 | 1 | 0.57387 | 86080.5 | 0.54755 | 0 | 0.52905 | 6613.125 | 0 | 0 | 64000 | 6613.125 | 0 | 15467.375 | -1458.5 | 1350000 | 15467.375 | 0
2021020703 | 1 | 0.56896 | 85344 | 0.68732 | 0 | 0.53147 | 6643.375 | 0 | 0 | 64000 | 6643.375 | 0 | 14700.625 | -766.75 | 1350000 | 14700.625 | 0
2021020704 | 1 | 0.56843 | 85264.5 | 0.74571 | 0 | 0.5718 | 7147.5 | 0 | 0 | 64000 | 7147.5 | 0 | 14117 | -583.625 | 1350000 | 14117 | 0
2021020705 | 1 | 0.57269 | 85903.5 | 0.71714 | 0 | 0.54784 | 6848 | 0 | 0 | 64000 | 6848 | 0 | 15055.5 | 938.5 | 1350000 | 15055.5 | 0
2021020706 | 1 | 0.58264 | 87396 | 0.64699 | 0 | 0.53948 | 6743.5 | 0 | 0 | 64000 | 6743.5 | 0 | 16652.5 | 1597 | 1350000 | 16652.5 | 0
2021020707 | 1 | 0.60114 | 90171 | 0.60211 | 0 | 0.52447 | 6555.875 | 0 | 0 | 64000 | 6555.875 | 0 | 19615.125 | 2962.625 | 1350000 | 19615.125 | 0
2021020708 | 1 | 0.622 | 93300 | 0.55911 | 0 | 0.55399 | 6924.875 | 0.04418 | 3534.4 | 64000 | 6924.875 | 3534.4 | 18840.725 | -774.4 | 1350000 | 18840.725 | 0
2021020709 | 1 | 0.64475 | 96712.5 | 0.49648 | 0 | 0.59133 | 7391.625 | 0.31754 | 25403.2 | 64000 | 7391.625 | 25320.875 | 0 | -18840.725 | 1350000 | 0 | 0
2021020710 | 1 | 0.66361 | 99541.5 | 0.45046 | 0 | 0.61818 | 7727.25 | 0.56399 | 45119.2 | 64000 | 7727.25 | 27814.25 | 0 | 0 | 1350000 | 0 | 0
2021020711 | 1 | 0.67516 | 101274 | 0.47733 | 0 | 0.62486 | 7810.75 | 0.60646 | 48516.8 | 64000 | 7810.75 | 29463.25 | 0 | 0 | 1350000 | 0 | 0
2021020712 | 1 | 0.67794 | 101691 | 0.50545 | 0 | 0.63251 | 7906.375 | 0.60237 | 48189.6 | 64000 | 7906.375 | 29784.625 | 0 | 0 | 1350000 | 0 | 0
2021020713 | 1 | 0.67577 | 101365.5 | 0.49073 | 0 | 0.62416 | 7802 | 0.60907 | 48725.6 | 64000 | 7802 | 29563.5 | 0 | 0 | 1350000 | 0 | 0
2021020714 | 1 | 0.66495 | 99742.5 | 0.57819 | 0 | 0.61025 | 7628.125 | 0.63495 | 50796 | 64000 | 7628.125 | 28114.375 | 0 | 0 | 1350000 | 0 | 0
2021020715 | 1 | 0.65365 | 98047.5 | 0.75319 | 0 | 0.61883 | 7735.375 | 0.62442 | 49953.6 | 64000 | 7735.375 | 26312.125 | 0 | 0 | 1350000 | 0 | 0
2021020716 | 1 | 0.64746 | 97119 | 0.81807 | 0 | 0.65172 | 8146.5 | 0.42844 | 34275.2 | 64000 | 8146.5 | 24972.5 | 0 | 0 | 1350000 | 0 | 0
2021020717 | 1 | 0.65813 | 98719.5 | 0.90266 | 0 | 0.65915 | 8239.375 | 0.08846 | 7076.8 | 64000 | 8239.375 | 7076.8 | 19403.325 | 19403.325 | 1350000 | 19403.325 | 0
2021020718 | 1 | 0.68947 | 103420.5 | 0.92278 | 0 | 0.65285 | 8160.625 | 0.00056 | 44.8 | 64000 | 8160.625 | 44.8 | 31215.075 | 11811.75 | 1344251.175 | 31215.075 | 0
2021020719 | 1 | 0.71634 | 107451 | 0.95516 | 0 | 0.64021 | 8002.625 | 0 | 0 | 64000 | 8002.625 | 0 | 35448.375 | 4233.3 | 1334269.05 | 35448.375 | 0
2021020720 | 1 | 0.70857 | 106285.5 | 0.96075 | 0 | 0.63725 | 7965.625 | 0 | 0 | 64000 | 7965.625 | 0 | 34319.875 | -1128.5 | 1325415.425 | 34319.875 | 0
2021020721 | 1 | 0.7044 | 105660 | 0.93479 | 0 | 0.65134 | 8141.75 | 0 | 0 | 64000 | 8141.75 | 0 | 33518.25 | -801.625 | 1317363.425 | 33518.25 | 0
2021020722 | 1 | 0.69403 | 104104.5 | 0.91843 | 0 | 0.67308 | 8413.5 | 0 | 0 | 64000 | 8413.5 | 0 | 31691 | -1827.25 | 1311138.675 | 31691 | 0
2021020723 | 1 | 0.67854 | 101781 | 0.85315 | 0 | 0.67088 | 8386 | 0 | 0 | 64000 | 8386 | 0 | 29395 | -2296 | 1307209.925 | 29395 | 0
2021020724 | 1 | 0.66009 | 99013.5 | 0.86215 | 0 | 0.674 | 8425 | 0 | 0 | 64000 | 8425 | 0 | 26588.5 | -2806.5 | 1306087.675 | 26588.5 | 0
2021020801 | 2 | 0.6458 | 96870 | 0.78473 | 0 | 0.66729 | 8341.125 | 0 | 0 | 64000 | 8341.125 | 0 | 24528.875 | -2059.625 | 1307025.05 | 24528.875 | 0
2021020802 | 2 | 0.6404 | 96060 | 0.65057 | 0 | 0.66095 | 8261.875 | 0 | 0 | 64000 | 8261.875 | 0 | 23798.125 | -730.75 | 1308693.175 | 23798.125 | 0
2021020803 | 2 | 0.64277 | 96415.5 | 0.58459 | 0 | 0.65712 | 8214 | 0 | 0 | 64000 | 8214 | 0 | 24201.5 | 403.375 | 1309957.925 | 24201.5 | 0
2021020804 | 2 | 0.64911 | 97366.5 | 0.43857 | 0 | 0.62142 | 7767.75 | 0 | 0 | 64000 | 7767.75 | 0 | 25598.75 | 1397.25 | 1309825.425 | 25598.75 | 0
2021020805 | 2 | 0.66719 | 100078.5 | 0.35997 | 0 | 0.60464 | 7558 | 0 | 0 | 64000 | 7558 | 0 | 28520.5 | 2921.75 | 1306771.175 | 28520.5 | 0
2021020806 | 2 | 0.70104 | 105156 | 0.36441 | 0 | 0.5697 | 7121.25 | 0 | 0 | 64000 | 7121.25 | 0 | 34034.75 | 5514.25 | 1298202.675 | 34034.75 | 0
2021020807 | 2 | 0.74897 | 112345.5 | 0.24123 | 0 | 0.51701 | 6462.625 | 0 | 0 | 64000 | 6462.625 | 0 | 41882.875 | 7848.125 | 1281786.05 | 41882.875 | 0
2021020808 | 2 | 0.78311 | 117466.5 | 0.19502 | 0 | 0.49001 | 6125.125 | 0.05577 | 4461.6 | 64000 | 6125.125 | 4461.6 | 42879.775 | 996.9 | 1264372.525 | 42879.775 | 0
2021020809 | 2 | 0.78426 | 117639 | 0.12262 | 0 | 0.43983 | 5497.875 | 0.36508 | 29206.4 | 64000 | 5497.875 | 29206.4 | 18934.725 | -23945.05 | 1270904.05 | 18934.725 | 0
2021020810 | 2 | 0.76812 | 115218 | 0.04358 | 0 | 0.37731 | 4716.375 | 0.57703 | 46162.4 | 64000 | 4716.375 | 46162.4 | 339.225 | -18595.5 | 1296031.075 | 339.225 | 0
2021020811 | 2 | 0.74967 | 112450.5 | 0.00993 | 0 | 0.33926 | 4240.75 | 0.5915 | 47320 | 64000 | 4240.75 | 44209.75 | 0 | -339.225 | 1321497.325 | 0 | 0
2021020812 | 2 | 0.72933 | 109399.5 | 0.00598 | 0 | 0.31212 | 3901.5 | 0.59642 | 47713.6 | 64000 | 3901.5 | 41498 | 0 | 0 | 1346963.575 | 0 | 0
2021020813 | 2 | 0.71072 | 106608 | 0.00767 | 0 | 0.27825 | 3478.125 | 0.61272 | 49017.6 | 64000 | 3478.125 | 39129.875 | 0 | 0 | 1350000 | 0 | 0
2021020814 | 2 | 0.69357 | 104035.5 | 0.0058 | 0 | 0.2097 | 2621.25 | 0.64518 | 51614.4 | 64000 | 2621.25 | 37414.25 | 0 | 0 | 1350000 | 0 | 0
2021020815 | 2 | 0.68254 | 102381 | 0.02766 | 0 | 0.1991 | 2488.75 | 0.63762 | 51009.6 | 64000 | 2488.75 | 35892.25 | 0 | 0 | 1350000 | 0 | 0
2021020816 | 2 | 0.67835 | 101752.5 | 0.03134 | 0 | 0.16219 | 2027.375 | 0.42944 | 34355.2 | 64000 | 2027.375 | 34355.2 | 1369.925 | 1369.925 | 1350000 | 1369.925 | 0
2021020817 | 2 | 0.69033 | 103549.5 | 0.0809 | 0 | 0.13505 | 1688.125 | 0.08566 | 6852.8 | 64000 | 1688.125 | 6852.8 | 31008.575 | 29638.65 | 1344457.675 | 31008.575 | 0
2021020818 | 2 | 0.72279 | 108418.5 | 0.18998 | 0 | 0.13314 | 1664.25 | 0 | 0 | 64000 | 1664.25 | 0 | 42754.25 | 11745.675 | 1327169.675 | 42754.25 | 0
2021020819 | 2 | 0.75215 | 112822.5 | 0.355 | 0 | 0.1612 | 2015 | 0 | 0 | 64000 | 2015 | 0 | 46807.5 | 4053.25 | 1305828.425 | 46807.5 | 0
2021020820 | 2 | 0.74982 | 112473 | 0.51251 | 0 | 0.16277 | 2034.625 | 0 | 0 | 64000 | 2034.625 | 0 | 46438.375 | -369.125 | 1284856.3 | 46438.375 | 0
2021020821 | 2 | 0.73731 | 110596.5 | 0.63616 | 0 | 0.18289 | 2286.125 | 0 | 0 | 64000 | 2286.125 | 0 | 44310.375 | -2128 | 1266012.175 | 44310.375 | 0
2021020822 | 2 | 0.71555 | 107332.5 | 0.72147 | 0 | 0.21544 | 2693 | 0 | 0 | 64000 | 2693 | 0 | 40639.5 | -3670.875 | 1250838.925 | 40639.5 | 0
2021020823 | 2 | 0.68748 | 103122 | 0.7083 | 0 | 0.25254 | 3156.75 | 0 | 0 | 64000 | 3156.75 | 0 | 35965.25 | -4674.25 | 1240339.925 | 35965.25 | 0
2021020824 | 2 | 0.65966 | 98949 | 0.64646 | 0 | 0.28895 | 3611.875 | 0 | 0 | 64000 | 3611.875 | 0 | 31337.125 | -4628.125 | 1234469.05 | 31337.125 | 0
2021020901 | 3 | 0.64039 | 96058.5 | 0.63965 | 0 | 0.27725 | 3465.625 | 0 | 0 | 64000 | 3465.625 | 0 | 28592.875 | -2744.25 | 1231342.425 | 28592.875 | 0
2021020902 | 3 | 0.63008 | 94512 | 0.63923 | 0 | 0.28418 | 3552.25 | 0 | 0 | 64000 | 3552.25 | 0 | 26959.75 | -1633.125 | 1229848.925 | 26959.75 | 0
2021020903 | 3 | 0.62401 | 93601.5 | 0.6343 | 0 | 0.30462 | 3807.75 | 0 | 0 | 64000 | 3807.75 | 0 | 25793.75 | -1166 | 1229521.425 | 25793.75 | 0
2021020904 | 3 | 0.62312 | 93468 | 0.62839 | 0 | 0.30086 | 3760.75 | 0 | 0 | 64000 | 3760.75 | 0 | 25707.25 | -86.5 | 1229280.425 | 25707.25 | 0
2021020905 | 3 | 0.63361 | 95041.5 | 0.59018 | 0 | 0.28176 | 3522 | 0 | 0 | 64000 | 3522 | 0 | 27519.5 | 1812.25 | 1227227.175 | 27519.5 | 0
2021020906 | 3 | 0.66053 | 99079.5 | 0.54433 | 0 | 0.29076 | 3634.5 | 0 | 0 | 64000 | 3634.5 | 0 | 31445 | 3925.5 | 1221248.425 | 31445 | 0
2021020907 | 3 | 0.70254 | 105381 | 0.50547 | 0 | 0.31166 | 3895.75 | 0 | 0 | 64000 | 3895.75 | 0 | 37485.25 | 6040.25 | 1209229.425 | 37485.25 | 0
2021020908 | 3 | 0.73408 | 110112 | 0.49658 | 0 | 0.38315 | 4789.375 | 0.02788 | 2230.4 | 64000 | 4789.375 | 2230.4 | 39092.225 | 1606.975 | 1195603.45 | 39092.225 | 0
2021020909 | 3 | 0.74244 | 111366 | 0.46357 | 0 | 0.41738 | 5217.25 | 0.11828 | 9462.4 | 64000 | 5217.25 | 9462.4 | 32686.35 | -6405.875 | 1188383.35 | 32686.35 | 0
2021020910 | 3 | 0.73888 | 110832 | 0.2934 | 0 | 0.39284 | 4910.5 | 0.15456 | 12364.8 | 64000 | 4910.5 | 12364.8 | 29556.7 | -3129.65 | 1184292.9 | 29556.7 | 0
2021020911 | 3 | 0.72631 | 108946.5 | 0.19679 | 0 | 0.34483 | 4310.375 | 0.17396 | 13916.8 | 64000 | 4310.375 | 13916.8 | 26719.325 | -2837.375 | 1183039.825 | 26719.325 | 0
2021020912 | 3 | 0.71292 | 106938 | 0.07668 | 0 | 0.29233 | 3654.125 | 0.1709 | 13672 | 64000 | 3654.125 | 13672 | 25611.875 | -1107.45 | 1182894.2 | 25611.875 | 0
2021020913 | 3 | 0.69939 | 104908.5 | 0.02995 | 0 | 0.27016 | 3377 | 0.14519 | 11615.2 | 64000 | 3377 | 11615.2 | 25916.3 | 304.425 | 1182444.15 | 25916.3 | 0
2021020914 | 3 | 0.68632 | 102948 | 0.09105 | 0 | 0.30091 | 3761.375 | 0.11204 | 8963.2 | 64000 | 3761.375 | 8963.2 | 26223.425 | 307.125 | 1181686.975 | 26223.425 | 0
2021020915 | 3 | 0.67519 | 101278.5 | 0.24735 | 0 | 0.32986 | 4123.25 | 0.09251 | 7400.8 | 64000 | 4123.25 | 7400.8 | 25754.45 | -468.975 | 1181398.775 | 25754.45 | 0
2021020916 | 3 | 0.66763 | 100144.5 | 0.22965 | 0 | 0.35653 | 4456.625 | 0.05335 | 4268 | 64000 | 4456.625 | 4268 | 27419.875 | 1665.425 | 1179445.15 | 27419.875 | 0
2021020917 | 3 | 0.67517 | 101275.5 | 0.20831 | 0 | 0.38782 | 4847.75 | 0.01019 | 815.2 | 64000 | 4847.75 | 815.2 | 31612.55 | 4192.675 | 1173298.85 | 31612.55 | 0
2021020918 | 3 | 0.69925 | 104887.5 | 0.31868 | 0 | 0.39878 | 4984.75 | 0 | 0 | 64000 | 4984.75 | 0 | 35902.75 | 4290.2 | 1162862.35 | 35902.75 | 0
2021020919 | 3 | 0.72237 | 108355.5 | 0.31718 | 0 | 0.43092 | 5386.5 | 0 | 0 | 64000 | 5386.5 | 0 | 38969 | 3066.25 | 1149359.6 | 38969 | 0
2021020920 | 3 | 0.72012 | 108018 | 0.30583 | 0 | 0.44974 | 5621.75 | 0 | 0 | 64000 | 5621.75 | 0 | 38396.25 | -572.75 | 1136429.6 | 38396.25 | 0
2021020921 | 3 | 0.70748 | 106122 | 0.35064 | 0 | 0.47091 | 5886.375 | 0 | 0 | 64000 | 5886.375 | 0 | 36235.625 | -2160.625 | 1125660.225 | 36235.625 | 0
2021020922 | 3 | 0.6869 | 103035 | 0.39968 | 0 | 0.55683 | 6960.375 | 0 | 0 | 64000 | 6960.375 | 0 | 32074.625 | -4161 | 1119051.85 | 32074.625 | 0
2021020923 | 3 | 0.65682 | 98523 | 0.39026 | 0 | 0.60415 | 7551.875 | 0 | 0 | 64000 | 7551.875 | 0 | 26971.125 | -5103.5 | 1117546.975 | 26971.125 | 0
2021020924 | 3 | 0.6304 | 94560 | 0.37458 | 0 | 0.65205 | 8150.625 | 0 | 0 | 64000 | 8150.625 | 0 | 22409.375 | -4561.75 | 1120603.85 | 22409.375 | 0
2021021001 | 4 | 0.61247 | 91870.5 | 0.38569 | 0 | 0.69596 | 8699.5 | 0 | 0 | 64000 | 8699.5 | 0 | 19171 | -3238.375 | 1126899.1 | 19171 | 0
2021021002 | 4 | 0.60537 | 90805.5 | 0.37406 | 0 | 0.71031 | 8878.875 | 0 | 0 | 64000 | 8878.875 | 0 | 17926.625 | -1244.375 | 1134438.725 | 17926.625 | 0
2021021003 | 4 | 0.60356 | 90534 | 0.34633 | 0 | 0.72553 | 9069.125 | 0 | 0 | 64000 | 9069.125 | 0 | 17464.875 | -461.75 | 1142440.1 | 17464.875 | 0
2021021004 | 4 | 0.60826 | 91239 | 0.22637 | 0 | 0.73256 | 9157 | 0 | 0 | 64000 | 9157 | 0 | 18082 | 617.125 | 1149824.35 | 18082 | 0
2021021005 | 4 | 0.62202 | 93303 | 0.17679 | 0 | 0.71827 | 8978.375 | 0 | 0 | 64000 | 8978.375 | 0 | 20324.625 | 2242.625 | 1154965.975 | 20324.625 | 0
2021021006 | 4 | 0.65219 | 97828.5 | 0.16252 | 0 | 0.64729 | 8091.125 | 0 | 0 | 64000 | 8091.125 | 0 | 25737.375 | 5412.75 | 1154694.85 | 25737.375 | 0
2021021007 | 4 | 0.69862 | 104793 | 0.1981 | 0 | 0.56531 | 7066.375 | 0 | 0 | 64000 | 7066.375 | 0 | 33726.625 | 7989.25 | 1146434.475 | 33726.625 | 0
2021021008 | 4 | 0.73276 | 109914 | 0.2101 | 0 | 0.48173 | 6021.625 | 0.01364 | 1091.2 | 64000 | 6021.625 | 1091.2 | 38801.175 | 5074.55 | 1133099.55 | 38801.175 | 0
2021021009 | 4 | 0.7413 | 111195 | 0.14136 | 0 | 0.4776 | 5970 | 0.07559 | 6047.2 | 64000 | 5970 | 6047.2 | 35177.8 | -3623.375 | 1123388 | 35177.8 | 0
2021021010 | 4 | 0.73355 | 110032.5 | 0.07975 | 0 | 0.46781 | 5847.625 | 0.14603 | 11682.4 | 64000 | 5847.625 | 11682.4 | 28502.475 | -6675.325 | 1120351.775 | 28502.475 | 0
2021021011 | 4 | 0.72049 | 108073.5 | 0.05082 | 0 | 0.37832 | 4729 | 0.27196 | 21756.8 | 64000 | 4729 | 21756.8 | 17587.7 | -10914.775 | 1128230.325 | 17587.7 | 0
2021021012 | 4 | 0.70956 | 106434 | 0.02909 | 0 | 0.28475 | 3559.375 | 0.36511 | 29208.8 | 64000 | 3559.375 | 29208.8 | 9665.825 | -7921.875 | 1144030.75 | 9665.825 | 0
2021021013 | 4 | 0.70286 | 105429 | 0.01218 | 0 | 0.20139 | 2517.375 | 0.42739 | 34191.2 | 64000 | 2517.375 | 34191.2 | 4720.425 | -4945.4 | 1164776.575 | 4720.425 | 0
2021021014 | 4 | 0.69794 | 104691 | 0.01145 | 0 | 0.16822 | 2102.75 | 0.42928 | 34342.4 | 64000 | 2102.75 | 34342.4 | 4245.85 | -474.575 | 1185996.975 | 4245.85 | 0
2021021015 | 4 | 0.69531 | 104296.5 | 0.00142 | 0 | 0.15165 | 1895.625 | 0.38902 | 31121.6 | 64000 | 1895.625 | 31121.6 | 7279.275 | 3033.425 | 1204183.95 | 7279.275 | 0
2021021016 | 4 | 0.69877 | 104815.5 | 0.0073 | 0 | 0.15768 | 1971 | 0.24843 | 19874.4 | 64000 | 1971 | 19874.4 | 18970.1 | 11690.825 | 1210680.1 | 18970.1 | 0
2021021017 | 4 | 0.70835 | 106252.5 | 0.02983 | 0 | 0.18169 | 2271.125 | 0.07423 | 5938.4 | 64000 | 2271.125 | 5938.4 | 34042.975 | 15072.875 | 1202103.375 | 34042.975 | 0
2021021018 | 4 | 0.73235 | 109852.5 | 0.10676 | 0 | 0.14622 | 1827.75 | 0.00141 | 112.8 | 64000 | 1827.75 | 112.8 | 43911.95 | 9868.975 | 1183657.675 | 43911.95 | 0
2021021019 | 4 | 0.74991 | 112486.5 | 0.16656 | 0 | 0.14094 | 1761.75 | 0 | 0 | 64000 | 1761.75 | 0 | 46724.75 | 2812.8 | 1162399.175 | 46724.75 | 0
2021021020 | 4 | 0.74256 | 111384 | 0.22755 | 0 | 0.16556 | 2069.5 | 0 | 0 | 64000 | 2069.5 | 0 | 45314.5 | -1410.25 | 1142550.925 | 45314.5 | 0
2021021021 | 4 | 0.72762 | 109143 | 0.2622 | 0 | 0.20349 | 2543.625 | 0 | 0 | 64000 | 2543.625 | 0 | 42599.375 | -2715.125 | 1125417.8 | 42599.375 | 0
2021021022 | 4 | 0.70529 | 105793.5 | 0.28968 | 0 | 0.18245 | 2280.625 | 0 | 0 | 64000 | 2280.625 | 0 | 39512.875 | -3086.5 | 1111371.175 | 39512.875 | 0
2021021023 | 4 | 0.67339 | 101008.5 | 0.26064 | 0 | 0.15974 | 1996.75 | 0 | 0 | 64000 | 1996.75 | 0 | 35011.75 | -4501.125 | 1101825.675 | 35011.75 | 0
2021021024 | 4 | 0.64496 | 96744 | 0.21523 | 0 | 0.15038 | 1879.75 | 0 | 0 | 64000 | 1879.75 | 0 | 30864.25 | -4147.5 | 1096427.675 | 30864.25 | 0
2021021101 | 5 | 0.62482 | 93723 | 0.16142 | 0 | 0.16562 | 2070.25 | 0 | 0 | 64000 | 2070.25 | 0 | 27652.75 | -3211.5 | 1094241.175 | 27652.75 | 0
2021021102 | 5 | 0.61341 | 92011.5 | 0.0834 | 0 | 0.21027 | 2628.375 | 0 | 0 | 64000 | 2628.375 | 0 | 25383.125 | -2269.625 | 1094324.3 | 25383.125 | 0
2021021103 | 5 | 0.60999 | 91498.5 | 0.03402 | 0 | 0.22445 | 2805.625 | 0 | 0 | 64000 | 2805.625 | 0 | 24692.875 | -690.25 | 1095097.675 | 24692.875 | 0
2021021104 | 5 | 0.6108 | 91620 | 0.0104 | 0 | 0.22565 | 2820.625 | 0 | 0 | 64000 | 2820.625 | 0 | 24799.375 | 106.5 | 1095764.55 | 24799.375 | 0
2021021105 | 5 | 0.62263 | 93394.5 | 0.00684 | 0 | 0.20262 | 2532.75 | 0 | 0 | 64000 | 2532.75 | 0 | 26861.75 | 2062.375 | 1094369.05 | 26861.75 | 0
2021021106 | 5 | 0.65242 | 97863 | 0.00029 | 0 | 0.17742 | 2217.75 | 0 | 0 | 64000 | 2217.75 | 0 | 31645.25 | 4783.5 | 1088190.05 | 31645.25 | 0
2021021107 | 5 | 0.69315 | 103972.5 | 0.00043 | 0 | 0.16382 | 2047.75 | 0 | 0 | 64000 | 2047.75 | 0 | 37924.75 | 6279.5 | 1075731.55 | 37924.75 | 0
2021021108 | 5 | 0.72729 | 109093.5 | 7e-05 | 0 | 0.17596 | 2199.5 | 0.04244 | 3395.2 | 64000 | 2199.5 | 3395.2 | 39498.8 | 1574.05 | 1061699 | 39498.8 | 0
2021021109 | 5 | 0.74383 | 111574.5 | 0.00275 | 0 | 0.21648 | 2706 | 0.23752 | 19001.6 | 64000 | 2706 | 19001.6 | 25866.9 | -13631.9 | 1061298.35 | 25866.9 | 0
2021021110 | 5 | 0.74916 | 112374 | 0.00141 | 0 | 0.2291 | 2863.75 | 0.43962 | 35169.6 | 64000 | 2863.75 | 35169.6 | 10340.65 | -15526.25 | 1076423.95 | 10340.65 | 0
2021021111 | 5 | 0.74914 | 112371 | 0.05137 | 0 | 0.2638 | 3297.5 | 0.45234 | 36187.2 | 64000 | 3297.5 | 36187.2 | 8886.3 | -1454.35 | 1093003.9 | 8886.3 | 0
2021021112 | 5 | 0.74526 | 111789 | 0.10812 | 0 | 0.35002 | 4375.25 | 0.46092 | 36873.6 | 64000 | 4375.25 | 36873.6 | 6540.15 | -2346.15 | 1111930 | 6540.15 | 0
2021021113 | 5 | 0.73991 | 110986.5 | 0.16639 | 0 | 0.41729 | 5216.125 | 0.49979 | 39983.2 | 64000 | 5216.125 | 39983.2 | 1787.175 | -4752.975 | 1135609.075 | 1787.175 | 0
2021021114 | 5 | 0.73468 | 110202 | 0.20685 | 0 | 0.46854 | 5856.75 | 0.52744 | 42195.2 | 64000 | 5856.75 | 40345.25 | 0 | -1787.175 | 1161075.325 | 0 | 0
2021021115 | 5 | 0.72949 | 109423.5 | 0.27078 | 0 | 0.50389 | 6298.625 | 0.55656 | 44524.8 | 64000 | 6298.625 | 39124.875 | 0 | 0 | 1186541.575 | 0 | 0
2021021116 | 5 | 0.72801 | 109201.5 | 0.31144 | 0 | 0.53738 | 6717.25 | 0.42622 | 34097.6 | 64000 | 6717.25 | 34097.6 | 4386.65 | 4386.65 | 1207621.175 | 4386.65 | 0
2021021117 | 5 | 0.7356 | 110340 | 0.3266 | 0 | 0.55975 | 6996.875 | 0.11107 | 8885.6 | 64000 | 6996.875 | 8885.6 | 30457.525 | 26070.875 | 1202629.9 | 30457.525 | 0
2021021118 | 5 | 0.75394 | 113091 | 0.25957 | 0 | 0.55285 | 6910.625 | 0.00386 | 308.8 | 64000 | 6910.625 | 308.8 | 41871.575 | 11414.05 | 1186224.575 | 41871.575 | 0
2021021119 | 5 | 0.76909 | 115363.5 | 0.25193 | 0 | 0.56817 | 7102.125 | 0 | 0 | 64000 | 7102.125 | 0 | 44261.375 | 2389.8 | 1167429.45 | 44261.375 | 0
2021021120 | 5 | 0.76054 | 114081 | 0.24291 | 0 | 0.51999 | 6499.875 | 0 | 0 | 64000 | 6499.875 | 0 | 43581.125 | -680.25 | 1149314.575 | 43581.125 | 0
2021021121 | 5 | 0.74558 | 111837 | 0.24301 | 0 | 0.51151 | 6393.875 | 0 | 0 | 64000 | 6393.875 | 0 | 41443.125 | -2138 | 1133337.7 | 41443.125 | 0
2021021122 | 5 | 0.72344 | 108516 | 0.23841 | 0 | 0.52625 | 6578.125 | 0 | 0 | 64000 | 6578.125 | 0 | 37937.875 | -3505.25 | 1120866.075 | 37937.875 | 0
2021021123 | 5 | 0.6937 | 104055 | 0.31245 | 0 | 0.50878 | 6359.75 | 0 | 0 | 64000 | 6359.75 | 0 | 33695.25 | -4242.625 | 1112637.075 | 33695.25 | 0
2021021124 | 5 | 0.66669 | 100003.5 | 0.36201 | 0 | 0.51711 | 6463.875 | 0 | 0 | 64000 | 6463.875 | 0 | 29539.625 | -4155.625 | 1108563.7 | 29539.625 | 0
2021021201 | 6 | 0.64681 | 97021.5 | 0.42256 | 0 | 0.53938 | 6742.25 | 0 | 0 | 64000 | 6742.25 | 0 | 26279.25 | -3260.375 | 1107750.7 | 26279.25 | 0
2021021202 | 6 | 0.63709 | 95563.5 | 0.50612 | 0 | 0.53087 | 6635.875 | 0 | 0 | 64000 | 6635.875 | 0 | 24927.625 | -1351.625 | 1108289.325 | 24927.625 | 0
2021021203 | 6 | 0.6338 | 95070 | 0.5371 | 0 | 0.51548 | 6443.5 | 0 | 0 | 64000 | 6443.5 | 0 | 24626.5 | -301.125 | 1109129.075 | 24626.5 | 0
2021021204 | 6 | 0.63717 | 95575.5 | 0.52213 | 0 | 0.50122 | 6265.25 | 0 | 0 | 64000 | 6265.25 | 0 | 25310.25 | 683.75 | 1109285.075 | 25310.25 | 0
2021021205 | 6 | 0.64857 | 97285.5 | 0.52922 | 0 | 0.42279 | 5284.875 | 0 | 0 | 64000 | 5284.875 | 0 | 28000.625 | 2690.375 | 1106750.7 | 28000.625 | 0
2021021206 | 6 | 0.67596 | 101394 | 0.58979 | 0 | 0.3231 | 4038.75 | 0 | 0 | 64000 | 4038.75 | 0 | 33355.25 | 5354.625 | 1098861.7 | 33355.25 | 0
2021021207 | 6 | 0.71694 | 107541 | 0.63807 | 0 | 0.2425 | 3031.25 | 0 | 0 | 64000 | 3031.25 | 0 | 40509.75 | 7154.5 | 1083818.2 | 40509.75 | 0
2021021208 | 6 | 0.74885 | 112327.5 | 0.51879 | 0 | 0.19734 | 2466.75 | 0.06949 | 5559.2 | 64000 | 2466.75 | 5559.2 | 40301.55 | -208.2 | 1068982.9 | 40301.55 | 0
2021021209 | 6 | 0.76361 | 114541.5 | 0.48421 | 0 | 0.20399 | 2549.875 | 0.36985 | 29588 | 64000 | 2549.875 | 29588 | 18403.625 | -21897.925 | 1076045.525 | 18403.625 | 0
2021021210 | 6 | 0.76664 | 114996 | 0.39493 | 0 | 0.22444 | 2805.5 | 0.58591 | 46872.8 | 64000 | 2805.5 | 46872.8 | 1317.7 | -17085.925 | 1100194.075 | 1317.7 | 0
2021021211 | 6 | 0.7632 | 114480 | 0.31008 | 0 | 0.2361 | 2951.25 | 0.61131 | 48904.8 | 64000 | 2951.25 | 47528.75 | 0 | -1317.7 | 1125660.325 | 0 | 0
2021021212 | 6 | 0.7549 | 113235 | 0.18078 | 0 | 0.24405 | 3050.625 | 0.58432 | 46745.6 | 64000 | 3050.625 | 46184.375 | 0 | 0 | 1151126.575 | 0 | 0
2021021213 | 6 | 0.74496 | 111744 | 0.17997 | 0 | 0.2046 | 2557.5 | 0.59194 | 47355.2 | 64000 | 2557.5 | 45186.5 | 0 | 0 | 1176592.825 | 0 | 0
2021021214 | 6 | 0.7358 | 110370 | 0.09119 | 0 | 0.18133 | 2266.625 | 0.61632 | 49305.6 | 64000 | 2266.625 | 44103.375 | 0 | 0 | 1202059.075 | 0 | 0
2021021215 | 6 | 0.72723 | 109084.5 | 0.0073 | 0 | 0.18807 | 2350.875 | 0.59375 | 47500 | 64000 | 2350.875 | 42733.625 | 0 | 0 | 1227525.325 | 0 | 0
2021021216 | 6 | 0.72146 | 108219 | 0.05065 | 0 | 0.20055 | 2506.875 | 0.38105 | 30484 | 64000 | 2506.875 | 30484 | 11228.125 | 11228.125 | 1241763.45 | 11228.125 | 0
2021021217 | 6 | 0.72625 | 108937.5 | 0.02523 | 0 | 0.22384 | 2798 | 0.08184 | 6547.2 | 64000 | 2798 | 6547.2 | 35592.3 | 24364.175 | 1231637.4 | 35592.3 | 0
2021021218 | 6 | 0.74198 | 111297 | 0.00342 | 0 | 0.25545 | 3193.125 | 0 | 0 | 64000 | 3193.125 | 0 | 44103.875 | 8511.575 | 1212999.775 | 44103.875 | 0
2021021219 | 6 | 0.75606 | 113409 | 0.01033 | 0 | 0.29398 | 3674.75 | 0 | 0 | 64000 | 3674.75 | 0 | 45734.25 | 1630.375 | 1192731.775 | 45734.25 | 0
2021021220 | 6 | 0.74866 | 112299 | 0.0051 | 0 | 0.34444 | 4305.5 | 0 | 0 | 64000 | 4305.5 | 0 | 43993.5 | -1740.75 | 1174204.525 | 43993.5 | 0
2021021221 | 6 | 0.73283 | 109924.5 | 0.00758 | 0 | 0.39643 | 4955.375 | 0 | 0 | 64000 | 4955.375 | 0 | 40969.125 | -3024.375 | 1158701.65 | 40969.125 | 0
2021021222 | 6 | 0.71211 | 106816.5 | 0.00986 | 0 | 0.43738 | 5467.25 | 0 | 0 | 64000 | 5467.25 | 0 | 37349.25 | -3619.875 | 1146818.65 | 37349.25 | 0
2021021223 | 6 | 0.68417 | 102625.5 | 0.00648 | 0 | 0.4805 | 6006.25 | 0 | 0 | 64000 | 6006.25 | 0 | 32619.25 | -4730 | 1139665.65 | 32619.25 | 0
2021021224 | 6 | 0.65692 | 98538 | 0.00544 | 0 | 0.54184 | 6773 | 0 | 0 | 64000 | 6773 | 0 | 27765 | -4854.25 | 1137366.9 | 27765 | 0
2021021301 | 7 | 0.63686 | 95529 | 0.03407 | 0 | 0.60129 | 7516.125 | 0 | 0 | 64000 | 7516.125 | 0 | 24012.875 | -3752.125 | 1138820.275 | 24012.875 | 0
2021021302 | 7 | 0.62346 | 93519 | 0.08686 | 0 | 0.63721 | 7965.125 | 0 | 0 | 64000 | 7965.125 | 0 | 21553.875 | -2459 | 1142732.65 | 21553.875 | 0
2021021303 | 7 | 0.61627 | 92440.5 | 0.1495 | 0 | 0.67229 | 8403.625 | 0 | 0 | 64000 | 8403.625 | 0 | 20036.875 | -1517 | 1148162.025 | 20036.875 | 0
2021021304 | 7 | 0.61526 | 92289 | 0.25879 | 0 | 0.73641 | 9205.125 | 0 | 0 | 64000 | 9205.125 | 0 | 19083.875 | -953 | 1154544.4 | 19083.875 | 0
2021021305 | 7 | 0.6183 | 92745 | 0.35526 | 0 | 0.77647 | 9705.875 | 0 | 0 | 64000 | 9705.875 | 0 | 19039.125 | -44.75 | 1160971.525 | 19039.125 | 0
2021021306 | 7 | 0.6308 | 94620 | 0.3865 | 0 | 0.78876 | 9859.5 | 0 | 0 | 64000 | 9859.5 | 0 | 20760.5 | 1721.375 | 1165677.275 | 20760.5 | 0
2021021307 | 7 | 0.65133 | 97699.5 | 0.45684 | 0 | 0.79721 | 9965.125 | 0 | 0 | 64000 | 9965.125 | 0 | 23734.375 | 2973.875 | 1167409.15 | 23734.375 | 0
2021021308 | 7 | 0.67213 | 100819.5 | 0.46774 | 0 | 0.82626 | 10328.25 | 0.05113 | 4090.4 | 64000 | 10328.25 | 4090.4 | 22400.85 | -1333.525 | 1170474.55 | 22400.85 | 0
2021021309 | 7 | 0.69145 | 103717.5 | 0.4174 | 0 | 0.8363 | 10453.75 | 0.29452 | 23561.6 | 64000 | 10453.75 | 23561.6 | 5702.15 | -16698.7 | 1190238.65 | 5702.15 | 0
2021021310 | 7 | 0.70966 | 106449 | 0.33365 | 0 | 0.82283 | 10285.375 | 0.47726 | 38180.8 | 64000 | 10285.375 | 32163.625 | 0 | -5702.15 | 1215704.9 | 0 | 0
2021021311 | 7 | 0.71714 | 107571 | 0.21656 | 0 | 0.78548 | 9818.5 | 0.52955 | 42364 | 64000 | 9818.5 | 33752.5 | 0 | 0 | 1241171.15 | 0 | 0
2021021312 | 7 | 0.71705 | 107557.5 | 0.08499 | 0 | 0.7755 | 9693.75 | 0.53308 | 42646.4 | 64000 | 9693.75 | 33863.75 | 0 | 0 | 1266637.4 | 0 | 0
2021021313 | 7 | 0.71168 | 106752 | 0.02476 | 0 | 0.79089 | 9886.125 | 0.54043 | 43234.4 | 64000 | 9886.125 | 32865.875 | 0 | 0 | 1292103.65 | 0 | 0
2021021314 | 7 | 0.70375 | 105562.5 | 0.01555 | 0 | 0.78523 | 9815.375 | 0.57479 | 45983.2 | 64000 | 9815.375 | 31747.125 | 0 | 0 | 1317569.9 | 0 | 0
2021021315 | 7 | 0.6981 | 104715 | 0.029 | 0 | 0.72265 | 9033.125 | 0.56766 | 45412.8 | 64000 | 9033.125 | 31681.875 | 0 | 0 | 1343036.15 | 0 | 0
2021021316 | 7 | 0.69617 | 104425.5 | 0.04814 | 0 | 0.68008 | 8501 | 0.38823 | 31058.4 | 64000 | 8501 | 31058.4 | 866.1 | 866.1 | 1350000 | 866.1 | 0
2021021317 | 7 | 0.70226 | 105339 | 0.07502 | 0 | 0.64242 | 8030.25 | 0.09787 | 7829.6 | 64000 | 8030.25 | 7829.6 | 25479.15 | 24613.05 | 1349987.1 | 25479.15 | 0
2021021318 | 7 | 0.71789 | 107683.5 | 0.09593 | 0 | 0.58881 | 7360.125 | 0.00282 | 225.6 | 64000 | 7360.125 | 225.6 | 36097.775 | 10618.625 | 1339355.575 | 36097.775 | 0
2021021319 | 7 | 0.73278 | 109917 | 0.12143 | 0 | 0.5372 | 6715 | 0 | 0 | 64000 | 6715 | 0 | 39202 | 3104.225 | 1325619.825 | 39202 | 0
2021021320 | 7 | 0.7267 | 109005 | 0.17791 | 0 | 0.52405 | 6550.625 | 0 | 0 | 64000 | 6550.625 | 0 | 38454.375 | -747.625 | 1312631.7 | 38454.375 | 0
2021021321 | 7 | 0.7145 | 107175 | 0.18052 | 0 | 0.52751 | 6593.875 | 0 | 0 | 64000 | 6593.875 | 0 | 36581.125 | -1873.25 | 1301516.825 | 36581.125 | 0
2021021322 | 7 | 0.69595 | 104392.5 | 0.15339 | 0 | 0.56398 | 7049.75 | 0 | 0 | 64000 | 7049.75 | 0 | 33342.75 | -3238.375 | 1293640.325 | 33342.75 | 0
2021021323 | 7 | 0.67169 | 100753.5 | 0.2303 | 0 | 0.55352 | 6919 | 0 | 0 | 64000 | 6919 | 0 | 29834.5 | -3508.25 | 1289272.075 | 29834.5 | 0
2021021324 | 7 | 0.6488 | 97320 | 0.34044 | 0 | 0.60146 | 7518.25 | 0 | 0 | 64000 | 7518.25 | 0 | 25801.75 | -4032.75 | 1288936.575 | 25801.75 | 0
2021021401 | 1 | 0.63107 | 94660.5 | 0.27836 | 0 | 0.6319 | 7898.75 | 0 | 0 | 64000 | 7898.75 | 0 | 22761.75 | -3040 | 1291641.075 | 22761.75 | 0
2021021402 | 1 | 0.61855 | 92782.5 | 0.14127 | 0 | 0.62428 | 7803.5 | 0 | 0 | 64000 | 7803.5 | 0 | 20979 | -1782.75 | 1296128.325 | 20979 | 0
2021021403 | 1 | 0.61199 | 91798.5 | 0.12761 | 0 | 0.6003 | 7503.75 | 0 | 0 | 64000 | 7503.75 | 0 | 20294.75 | -684.25 | 1301299.825 | 20294.75 | 0
2021021404 | 1 | 0.61132 | 91698 | 0.08745 | 0 | 0.5827 | 7283.75 | 0 | 0 | 64000 | 7283.75 | 0 | 20414.25 | 119.5 | 1306351.825 | 20414.25 | 0
2021021405 | 1 | 0.61398 | 92097 | 0.0502 | 0 | 0.57164 | 7145.5 | 0 | 0 | 64000 | 7145.5 | 0 | 20951.5 | 537.25 | 1310866.575 | 20951.5 | 0
2021021406 | 1 | 0.62319 | 93478.5 | 0.00339 | 0 | 0.53854 | 6731.75 | 0 | 0 | 64000 | 6731.75 | 0 | 22746.75 | 1795.25 | 1313586.075 | 22746.75 | 0
2021021407 | 1 | 0.63715 | 95572.5 | 0.00643 | 0 | 0.5192 | 6490 | 0 | 0 | 64000 | 6490 | 0 | 25082.5 | 2335.75 | 1313969.825 | 25082.5 | 0
2021021408 | 1 | 0.6519 | 97785 | 0.00916 | 0 | 0.51904 | 6488 | 0.04613 | 3690.4 | 64000 | 6488 | 3690.4 | 23606.6 | -1475.9 | 1315829.475 | 23606.6 | 0
2021021409 | 1 | 0.67121 | 100681.5 | 0.00945 | 0 | 0.53592 | 6699 | 0.29797 | 23837.6 | 64000 | 6699 | 23837.6 | 6144.9 | -17461.7 | 1335150.825 | 6144.9 | 0
2021021410 | 1 | 0.68453 | 102679.5 | 0.01113 | 0 | 0.55398 | 6924.75 | 0.47648 | 38118.4 | 64000 | 6924.75 | 31754.75 | 0 | -6144.9 | 1350000 | 0 | 0
2021021411 | 1 | 0.68726 | 103089 | 0.00842 | 0 | 0.54676 | 6834.5 | 0.50104 | 40083.2 | 64000 | 6834.5 | 32254.5 | 0 | 0 | 1350000 | 0 | 0
2021021412 | 1 | 0.68303 | 102454.5 | 0.00742 | 0 | 0.54568 | 6821 | 0.50567 | 40453.6 | 64000 | 6821 | 31633.5 | 0 | 0 | 1350000 | 0 | 0
2021021413 | 1 | 0.67447 | 101170.5 | 0.00872 | 0 | 0.58798 | 7349.75 | 0.49622 | 39697.6 | 64000 | 7349.75 | 29820.75 | 0 | 0 | 1350000 | 0 | 0
2021021414 | 1 | 0.6657 | 99855 | 0.00712 | 0 | 0.58429 | 7303.625 | 0.48807 | 39045.6 | 64000 | 7303.625 | 28551.375 | 0 | 0 | 1350000 | 0 | 0
2021021415 | 1 | 0.66148 | 99222 | 0.0016 | 0 | 0.6006 | 7507.5 | 0.46438 | 37150.4 | 64000 | 7507.5 | 27714.5 | 0 | 0 | 1350000 | 0 | 0
2021021416 | 1 | 0.6647 | 99705 | 0.00446 | 0 | 0.62195 | 7774.375 | 0.33114 | 26491.2 | 64000 | 7774.375 | 26491.2 | 1439.425 | 1439.425 | 1350000 | 1439.425 | 0
2021021417 | 1 | 0.67516 | 101274 | 0.00253 | 0 | 0.62632 | 7829 | 0.08306 | 6644.8 | 64000 | 7829 | 6644.8 | 22800.2 | 21360.775 | 1350000 | 22800.2 | 0
2021021418 | 1 | 0.69674 | 104511 | 0.0085 | 0 | 0.62341 | 7792.625 | 0.0002 | 16 | 64000 | 7792.625 | 16 | 32702.375 | 9902.175 | 1342763.875 | 32702.375 | 0
2021021419 | 1 | 0.71634 | 107451 | 0.00914 | 0 | 0.62062 | 7757.75 | 0 | 0 | 64000 | 7757.75 | 0 | 35693.25 | 2990.875 | 1332536.875 | 35693.25 | 0
2021021420 | 1 | 0.7138 | 107070 | 0.01079 | 0 | 0.61763 | 7720.375 | 0 | 0 | 64000 | 7720.375 | 0 | 35349.625 | -343.625 | 1322653.5 | 35349.625 | 0
2021021421 | 1 | 0.70091 | 105136.5 | 0.0138 | 0 | 0.64161 | 8020.125 | 0 | 0 | 64000 | 8020.125 | 0 | 33116.375 | -2233.25 | 1315003.375 | 33116.375 | 0
2021021422 | 1 | 0.68402 | 102603 | 0.03755 | 0 | 0.64131 | 8016.375 | 0 | 0 | 64000 | 8016.375 | 0 | 30586.625 | -2529.75 | 1309883 | 30586.625 | 0
2021021423 | 1 | 0.66055 | 99082.5 | 0.03834 | 0 | 0.62367 | 7795.875 | 0 | 0 | 64000 | 7795.875 | 0 | 27286.625 | -3300 | 1308062.625 | 27286.625 | 0
2021021424 | 1 | 0.63891 | 95836.5 | 0.02785 | 0 | 0.64437 | 8054.625 | 0 | 0 | 64000 | 8054.625 | 0 | 23781.875 | -3504.75 | 1309747 | 23781.875 | 0
2021021501 | 2 | 0.62125 | 93187.5 | 0.00031 | 0 | 0.63987 | 7998.375 | 0 | 0 | 64000 | 7998.375 | 0 | 21189.125 | -2592.75 | 1314024.125 | 21189.125 | 0
2021021502 | 2 | 0.6121 | 91815 | 0.00021 | 0 | 0.63309 | 7913.625 | 0 | 0 | 64000 | 7913.625 | 0 | 19901.375 | -1287.75 | 1319589 | 19901.375 | 0
2021021503 | 2 | 0.6097 | 91455 | 0.00258 | 0 | 0.63263 | 7907.875 | 0 | 0 | 64000 | 7907.875 | 0 | 19547.125 | -354.25 | 1325508.125 | 19547.125 | 0
2021021504 | 2 | 0.61135 | 91702.5 | 0.00868 | 0 | 0.59256 | 7407 | 0 | 0 | 64000 | 7407 | 0 | 20295.5 | 748.375 | 1330678.875 | 20295.5 | 0
2021021505 | 2 | 0.62293 | 93439.5 | 0.00252 | 0 | 0.57639 | 7204.875 | 0 | 0 | 64000 | 7204.875 | 0 | 22234.625 | 1939.125 | 1333910.5 | 22234.625 | 0
2021021506 | 2 | 0.64686 | 97029 | 0.00063 | 0 | 0.521 | 6512.5 | 0 | 0 | 64000 | 6512.5 | 0 | 26516.5 | 4281.875 | 1332860.25 | 26516.5 | 0
2021021507 | 2 | 0.6836 | 102540 | 0.00218 | 0 | 0.49339 | 6167.375 | 0 | 0 | 64000 | 6167.375 | 0 | 32372.625 | 5856.125 | 1325953.875 | 32372.625 | 0
2021021508 | 2 | 0.71074 | 106611 | 0.006 | 0 | 0.42097 | 5262.125 | 0.06058 | 4846.4 | 64000 | 5262.125 | 4846.4 | 32502.475 | 129.85 | 1318917.65 | 32502.475 | 0
2021021509 | 2 | 0.72795 | 109192.5 | 0.00898 | 0 | 0.37275 | 4659.375 | 0.35754 | 28603.2 | 64000 | 4659.375 | 28603.2 | 11929.925 | -20572.55 | 1332453.975 | 11929.925 | 0
2021021510 | 2 | 0.7381 | 110715 | 0.0082 | 0 | 0.33362 | 4170.25 | 0.55216 | 44172.8 | 64000 | 4170.25 | 42544.75 | 0 | -11929.925 | 1350000 | 0 | 0
2021021511 | 2 | 0.73979 | 110968.5 | 0.00723 | 0 | 0.33665 | 4208.125 | 0.56921 | 45536.8 | 64000 | 4208.125 | 42760.375 | 0 | 0 | 1350000 | 0 | 0
2021021512 | 2 | 0.73853 | 110779.5 | 0.00778 | 0 | 0.32085 | 4010.625 | 0.56262 | 45009.6 | 64000 | 4010.625 | 42768.875 | 0 | 0 | 1350000 | 0 | 0
2021021513 | 2 | 0.73456 | 110184 | 0.00846 | 0 | 0.23687 | 2960.875 | 0.58086 | 46468.8 | 64000 | 2960.875 | 43223.125 | 0 | 0 | 1350000 | 0 | 0
2021021514 | 2 | 0.72975 | 109462.5 | 0.01015 | 0 | 0.17371 | 2171.375 | 0.57445 | 45956 | 64000 | 2171.375 | 43291.125 | 0 | 0 | 1350000 | 0 | 0
2021021515 | 2 | 0.72648 | 108972 | 0.01138 | 0 | 0.21496 | 2687 | 0.54104 | 43283.2 | 64000 | 2687 | 42285 | 0 | 0 | 1350000 | 0 | 0
2021021516 | 2 | 0.72525 | 108787.5 | 0.01029 | 0 | 0.25532 | 3191.5 | 0.40699 | 32559.2 | 64000 | 3191.5 | 32559.2 | 9036.8 | 9036.8 | 1350000 | 9036.8 | 0
2021021517 | 2 | 0.73337 | 110005.5 | 0.00846 | 0 | 0.24876 | 3109.5 | 0.11059 | 8847.2 | 64000 | 3109.5 | 8847.2 | 34048.8 | 25012 | 1341417.45 | 34048.8 | 0
2021021518 | 2 | 0.75194 | 112791 | 0.00731 | 0 | 0.24436 | 3054.5 | 0.00019 | 15.2 | 64000 | 3054.5 | 15.2 | 45721.3 | 11672.5 | 1321162.4 | 45721.3 | 0
2021021519 | 2 | 0.76286 | 114429 | 0.00239 | 0 | 0.23598 | 2949.75 | 0 | 0 | 64000 | 2949.75 | 0 | 47479.25 | 1757.95 | 1299149.4 | 47479.25 | 0
2021021520 | 2 | 0.75151 | 112726.5 | 0.0138 | 0 | 0.21587 | 2698.375 | 0 | 0 | 64000 | 2698.375 | 0 | 46028.125 | -1451.125 | 1278587.525 | 46028.125 | 0
2021021521 | 2 | 0.73277 | 109915.5 | 0.0201 | 0 | 0.20417 | 2552.125 | 0 | 0 | 64000 | 2552.125 | 0 | 43363.375 | -2664.75 | 1260690.4 | 43363.375 | 0
2021021522 | 2 | 0.70552 | 105828 | 0.02475 | 0 | 0.19832 | 2479 | 0 | 0 | 64000 | 2479 | 0 | 39349 | -4014.375 | 1246807.65 | 39349 | 0
2021021523 | 2 | 0.67224 | 100836 | 0.03052 | 0 | 0.21134 | 2641.75 | 0 | 0 | 64000 | 2641.75 | 0 | 34194.25 | -5154.75 | 1238079.65 | 34194.25 | 0
2021021524 | 2 | 0.64063 | 96094.5 | 0.03284 | 0 | 0.20623 | 2577.875 | 0 | 0 | 64000 | 2577.875 | 0 | 29516.625 | -4677.625 | 1234029.275 | 29516.625 | 0
2021021601 | 3 | 0.61852 | 92778 | 0.04753 | 0 | 0.21439 | 2679.875 | 0 | 0 | 64000 | 2679.875 | 0 | 26098.125 | -3418.5 | 1233397.4 | 26098.125 | 0
2021021602 | 3 | 0.60405 | 90607.5 | 0.0824 | 0 | 0.22789 | 2848.625 | 0 | 0 | 64000 | 2848.625 | 0 | 23758.875 | -2339.25 | 1235104.775 | 23758.875 | 0
2021021603 | 3 | 0.59524 | 89286 | 0.15558 | 0 | 0.22271 | 2783.875 | 0 | 0 | 64000 | 2783.875 | 0 | 22502.125 | -1256.75 | 1238068.9 | 22502.125 | 0
2021021604 | 3 | 0.59417 | 89125.5 | 0.18905 | 0 | 0.20843 | 2605.375 | 0 | 0 | 64000 | 2605.375 | 0 | 22520.125 | 18 | 1241015.025 | 22520.125 | 0
2021021605 | 3 | 0.60188 | 90282 | 0.30534 | 0 | 0.19157 | 2394.625 | 0 | 0 | 64000 | 2394.625 | 0 | 23887.375 | 1367.25 | 1242593.9 | 23887.375 | 0
2021021606 | 3 | 0.62597 | 93895.5 | 0.33813 | 0 | 0.19653 | 2456.625 | 0 | 0 | 64000 | 2456.625 | 0 | 27438.875 | 3551.5 | 1240621.275 | 27438.875 | 0
2021021607 | 3 | 0.66236 | 99354 | 0.40384 | 0 | 0.20309 | 2538.625 | 0.00268 | 214.4 | 64000 | 2538.625 | 214.4 | 32600.975 | 5162.1 | 1233486.55 | 32600.975 | 0
2021021608 | 3 | 0.69134 | 103701 | 0.59196 | 0 | 0.2171 | 2713.75 | 0.06113 | 4890.4 | 64000 | 2713.75 | 4890.4 | 32096.85 | -504.125 | 1226855.95 | 32096.85 | 0
2021021609 | 3 | 0.70176 | 105264 | 0.72101 | 0 | 0.28453 | 3556.625 | 0.34701 | 27760.8 | 64000 | 3556.625 | 27760.8 | 9946.575 | -22150.275 | 1242375.625 | 9946.575 | 0
2021021610 | 3 | 0.7002 | 105030 | 0.80309 | 0 | 0.31145 | 3893.125 | 0.54456 | 43564.8 | 64000 | 3893.125 | 37136.875 | 0 | -9946.575 | 1267841.875 | 0 | 0
2021021611 | 3 | 0.69182 | 103773 | 0.85406 | 0 | 0.31869 | 3983.625 | 0.55735 | 44588 | 64000 | 3983.625 | 35789.375 | 0 | 0 | 1293308.125 | 0 | 0
2021021612 | 3 | 0.68062 | 102093 | 0.84724 | 0 | 0.30486 | 3810.75 | 0.53636 | 42908.8 | 64000 | 3810.75 | 34282.25 | 0 | 0 | 1318774.375 | 0 | 0
2021021613 | 3 | 0.67409 | 101113.5 | 0.84862 | 0 | 0.2683 | 3353.75 | 0.55401 | 44320.8 | 64000 | 3353.75 | 33759.75 | 0 | 0 | 1344240.625 | 0 | 0
2021021614 | 3 | 0.66837 | 100255.5 | 0.88524 | 0 | 0.22071 | 2758.875 | 0.57206 | 45764.8 | 64000 | 2758.875 | 33496.625 | 0 | 0 | 1350000 | 0 | 0
2021021615 | 3 | 0.66429 | 99643.5 | 0.87996 | 0 | 0.19925 | 2490.625 | 0.54203 | 43362.4 | 64000 | 2490.625 | 33152.875 | 0 | 0 | 1350000 | 0 | 0
2021021616 | 3 | 0.66912 | 100368 | 0.88177 | 0 | 0.20738 | 2592.25 | 0.30878 | 24702.4 | 64000 | 2592.25 | 24702.4 | 9073.35 | 9073.35 | 1350000 | 9073.35 | 0
2021021617 | 3 | 0.68147 | 102220.5 | 0.89758 | 0 | 0.19914 | 2489.25 | 0.08947 | 7157.6 | 64000 | 2489.25 | 7157.6 | 28573.65 | 19500.3 | 1346892.6 | 28573.65 | 0
2021021618 | 3 | 0.70957 | 106435.5 | 0.89368 | 0 | 0.21374 | 2671.75 | 0.00016 | 12.8 | 64000 | 2671.75 | 12.8 | 39750.95 | 11177.3 | 1332607.9 | 39750.95 | 0
2021021619 | 3 | 0.7391 | 110865 | 0.87629 | 0 | 0.23395 | 2924.375 | 0 | 0 | 64000 | 2924.375 | 0 | 43940.625 | 4189.675 | 1314133.525 | 43940.625 | 0
2021021620 | 3 | 0.7439 | 111585 | 0.88431 | 0 | 0.2483 | 3103.75 | 0 | 0 | 64000 | 3103.75 | 0 | 44481.25 | 540.625 | 1295118.525 | 44481.25 | 0
2021021621 | 3 | 0.73538 | 110307 | 0.87851 | 0 | 0.27985 | 3498.125 | 0 | 0 | 64000 | 3498.125 | 0 | 42808.875 | -1672.375 | 1277775.9 | 42808.875 | 0
2021021622 | 3 | 0.7197 | 107955 | 0.86357 | 0 | 0.3422 | 4277.5 | 0 | 0 | 64000 | 4277.5 | 0 | 39677.5 | -3131.375 | 1263564.65 | 39677.5 | 0
2021021623 | 3 | 0.69452 | 104178 | 0.79561 | 0 | 0.43128 | 5391 | 0 | 0 | 64000 | 5391 | 0 | 34787 | -4890.5 | 1254243.9 | 34787 | 0
2021021624 | 3 | 0.6734 | 101010 | 0.74923 | 0 | 0.48874 | 6109.25 | 0 | 0 | 64000 | 6109.25 | 0 | 30900.75 | -3886.25 | 1248809.4 | 30900.75 | 0
2021021701 | 4 | 0.65771 | 98656.5 | 0.71947 | 0 | 0.51144 | 6393 | 0 | 0 | 64000 | 6393 | 0 | 28263.5 | -2637.25 | 1246012.15 | 28263.5 | 0
2021021702 | 4 | 0.65334 | 98001 | 0.69754 | 0 | 0.52503 | 6562.875 | 0 | 0 | 64000 | 6562.875 | 0 | 27438.125 | -825.375 | 1244040.275 | 27438.125 | 0
2021021703 | 4 | 0.65303 | 97954.5 | 0.66953 | 0 | 0.5968 | 7460 | 0 | 0 | 64000 | 7460 | 0 | 26494.5 | -943.625 | 1243012.025 | 26494.5 | 0
2021021704 | 4 | 0.65954 | 98931 | 0.67413 | 0 | 0.65497 | 8187.125 | 0 | 0 | 64000 | 8187.125 | 0 | 26743.875 | 249.375 | 1241734.4 | 26743.875 | 0
2021021705 | 4 | 0.6743 | 101145 | 0.58127 | 0 | 0.65822 | 8227.75 | 0 | 0 | 64000 | 8227.75 | 0 | 28917.25 | 2173.375 | 1238283.4 | 28917.25 | 0
2021021706 | 4 | 0.70529 | 105793.5 | 0.59186 | 0 | 0.64578 | 8072.25 | 0 | 0 | 64000 | 8072.25 | 0 | 33721.25 | 4804 | 1230028.4 | 33721.25 | 0
2021021707 | 4 | 0.75009 | 112513.5 | 0.53454 | 0 | 0.63133 | 7891.625 | 0 | 0 | 64000 | 7891.625 | 0 | 40621.875 | 6900.625 | 1214872.775 | 40621.875 | 0
2021021708 | 4 | 0.77913 | 116869.5 | 0.5127 | 0 | 0.64188 | 8023.5 | 0.04822 | 3857.6 | 64000 | 8023.5 | 3857.6 | 40988.4 | 366.525 | 1199350.625 | 40988.4 | 0
2021021709 | 4 | 0.77907 | 116860.5 | 0.37625 | 0 | 0.64149 | 8018.625 | 0.26213 | 20970.4 | 64000 | 8018.625 | 20970.4 | 23871.475 | -17116.925 | 1200945.4 | 23871.475 | 0
2021021710 | 4 | 0.75716 | 113574 | 0.28436 | 0 | 0.64763 | 8095.375 | 0.41915 | 33532 | 64000 | 8095.375 | 33532 | 7946.625 | -15924.85 | 1218465.025 | 7946.625 | 0
2021021711 | 4 | 0.7359 | 110385 | 0.21305 | 0 | 0.65432 | 8179 | 0.45102 | 36081.6 | 64000 | 8179 | 36081.6 | 2124.4 | -5822.225 | 1241806.875 | 2124.4 | 0
2021021712 | 4 | 0.72103 | 108154.5 | 0.09009 | 0 | 0.62555 | 7819.375 | 0.4642 | 37136 | 64000 | 7819.375 | 36335.125 | 0 | -2124.4 | 1267273.125 | 0 | 0
2021021713 | 4 | 0.70714 | 106071 | 0.01464 | 0 | 0.59574 | 7446.75 | 0.45748 | 36598.4 | 64000 | 7446.75 | 34624.25 | 0 | 0 | 1292739.375 | 0 | 0
2021021714 | 4 | 0.69441 | 104161.5 | 0.00949 | 0 | 0.57671 | 7208.875 | 0.45762 | 36609.6 | 64000 | 7208.875 | 32952.625 | 0 | 0 | 1318205.625 | 0 | 0
2021021715 | 4 | 0.68315 | 102472.5 | 0.01788 | 0 | 0.58856 | 7357 | 0.47989 | 38391.2 | 64000 | 7357 | 31115.5 | 0 | 0 | 1343671.875 | 0 | 0
2021021716 | 4 | 0.67943 | 101914.5 | 0.01588 | 0 | 0.57681 | 7210.125 | 0.39727 | 31781.6 | 64000 | 7210.125 | 30704.375 | 0 | 0 | 1350000 | 0 | 0
2021021717 | 4 | 0.69379 | 104068.5 | 0.01992 | 0 | 0.53202 | 6650.25 | 0.1208 | 9664 | 64000 | 6650.25 | 9664 | 23754.25 | 23754.25 | 1350000 | 23754.25 | 0
2021021718 | 4 | 0.72325 | 108487.5 | 0.02427 | 0 | 0.52594 | 6574.25 | 0.00142 | 113.6 | 64000 | 6574.25 | 113.6 | 37799.65 | 14045.4 | 1337666.6 | 37799.65 | 0
2021021719 | 4 | 0.75598 | 113397 | 0.06694 | 0 | 0.49966 | 6245.75 | 0 | 0 | 64000 | 6245.75 | 0 | 43151.25 | 5351.6 | 1319981.6 | 43151.25 | 0
2021021720 | 4 | 0.75866 | 113799 | 0.20812 | 0 | 0.46453 | 5806.625 | 0 | 0 | 64000 | 5806.625 | 0 | 43992.375 | 841.125 | 1301455.475 | 43992.375 | 0
2021021721 | 4 | 0.74756 | 112134 | 0.28273 | 0 | 0.47693 | 5961.625 | 0 | 0 | 64000 | 5961.625 | 0 | 42172.375 | -1820 | 1284749.35 | 42172.375 | 0
2021021722 | 4 | 0.72661 | 108991.5 | 0.3434 | 0 | 0.51337 | 6417.125 | 0 | 0 | 64000 | 6417.125 | 0 | 38574.375 | -3598 | 1271641.225 | 38574.375 | 0
2021021723 | 4 | 0.69636 | 104454 | 0.3818 | 0 | 0.52258 | 6532.25 | 0 | 0 | 64000 | 6532.25 | 0 | 33921.75 | -4652.625 | 1263185.725 | 33921.75 | 0
2021021724 | 4 | 0.66851 | 100276.5 | 0.3821 | 0 | 0.48676 | 6084.5 | 0 | 0 | 64000 | 6084.5 | 0 | 30192 | -3729.75 | 1258459.975 | 30192 | 0
2021021801 | 5 | 0.64796 | 97194 | 0.29495 | 0 | 0.40755 | 5094.375 | 0 | 0 | 64000 | 5094.375 | 0 | 28099.625 | -2092.375 | 1255826.6 | 28099.625 | 0
2021021802 | 5 | 0.63628 | 95442 | 0.25671 | 0 | 0.38034 | 4754.25 | 0 | 0 | 64000 | 4754.25 | 0 | 26687.75 | -1411.875 | 1254605.1 | 26687.75 | 0
2021021803 | 5 | 0.63094 | 94641 | 0.13318 | 0 | 0.41204 | 5150.5 | 0 | 0 | 64000 | 5150.5 | 0 | 25490.5 | -1197.25 | 1254580.85 | 25490.5 | 0
2021021804 | 5 | 0.63209 | 94813.5 | 0.08352 | 0 | 0.3782 | 4727.5 | 0 | 0 | 64000 | 4727.5 | 0 | 26086 | 595.5 | 1253961.1 | 26086 | 0
2021021805 | 5 | 0.64307 | 96460.5 | 0.15013 | 0 | 0.36638 | 4579.75 | 0 | 0 | 64000 | 4579.75 | 0 | 27880.75 | 1794.75 | 1251546.6 | 27880.75 | 0
2021021806 | 5 | 0.67081 | 100621.5 | 0.18564 | 0 | 0.36976 | 4622 | 0 | 0 | 64000 | 4622 | 0 | 31999.5 | 4118.75 | 1245013.35 | 31999.5 | 0
2021021807 | 5 | 0.71072 | 106608 | 0.27041 | 0 | 0.41362 | 5170.25 | 0 | 0 | 64000 | 5170.25 | 0 | 37437.75 | 5438.25 | 1233041.85 | 37437.75 | 0
2021021808 | 5 | 0.7444 | 111660 | 0.41197 | 0 | 0.46064 | 5758 | 0.06426 | 5140.8 | 64000 | 5758 | 5140.8 | 36761.2 | -676.55 | 1221746.9 | 36761.2 | 0
2021021809 | 5 | 0.76199 | 114298.5 | 0.43737 | 0 | 0.50373 | 6296.625 | 0.36324 | 29059.2 | 64000 | 6296.625 | 29059.2 | 14942.675 | -21818.525 | 1232270.475 | 14942.675 | 0
2021021810 | 5 | 0.77105 | 115657.5 | 0.52455 | 0 | 0.54412 | 6801.5 | 0.53402 | 42721.6 | 64000 | 6801.5 | 42721.6 | 2134.4 | -12808.275 | 1255602.325 | 2134.4 | 0
2021021811 | 5 | 0.77155 | 115732.5 | 0.53059 | 0 | 0.59009 | 7376.125 | 0.54205 | 43364 | 64000 | 7376.125 | 43364 | 992.375 | -1142.025 | 1280076.2 | 992.375 | 0
2021021812 | 5 | 0.76565 | 114847.5 | 0.55627 | 0 | 0.62736 | 7842 | 0.52593 | 42074.4 | 64000 | 7842 | 42074.4 | 931.1 | -61.275 | 1304611.35 | 931.1 | 0
2021021813 | 5 | 0.75713 | 113569.5 | 0.32678 | 0 | 0.61337 | 7667.125 | 0.52463 | 41970.4 | 64000 | 7667.125 | 41902.375 | 0 | -931.1 | 1330077.6 | 0 | 0
2021021814 | 5 | 0.74696 | 112044 | 0.13877 | 0 | 0.61616 | 7702 | 0.49125 | 39300 | 64000 | 7702 | 39300 | 1042 | 1042 | 1350000 | 1042 | 0
2021021815 | 5 | 0.73966 | 110949 | 0.09672 | 0 | 0.57162 | 7145.25 | 0.47487 | 37989.6 | 64000 | 7145.25 | 37989.6 | 1814.15 | 772.15 | 1350000 | 1814.15 | 0
2021021816 | 5 | 0.73357 | 110035.5 | 0.08004 | 0 | 0.54182 | 6772.75 | 0.35646 | 28516.8 | 64000 | 6772.75 | 28516.8 | 10745.95 | 8931.8 | 1350000 | 10745.95 | 0
2021021817 | 5 | 0.73784 | 110676 | 0.10259 | 0 | 0.54964 | 6870.5 | 0.10922 | 8737.6 | 64000 | 6870.5 | 8737.6 | 31067.9 | 20321.95 | 1344398.35 | 31067.9 | 0
2021021818 | 5 | 0.75401 | 113101.5 | 0.11018 | 0 | 0.58313 | 7289.125 | 0.00113 | 90.4 | 64000 | 7289.125 | 90.4 | 41721.975 | 10654.075 | 1328142.625 | 41721.975 | 0
2021021819 | 5 | 0.76921 | 115381.5 | 0.11085 | 0 | 0.56252 | 7031.5 | 0 | 0 | 64000 | 7031.5 | 0 | 44350 | 2628.025 | 1309258.875 | 44350 | 0
2021021820 | 5 | 0.76187 | 114280.5 | 0.11949 | 0 | 0.56994 | 7124.25 | 0 | 0 | 64000 | 7124.25 | 0 | 43156.25 | -1193.75 | 1291568.875 | 43156.25 | 0
2021021821 | 5 | 0.7457 | 111855 | 0.11625 | 0 | 0.54842 | 6855.25 | 0 | 0 | 64000 | 6855.25 | 0 | 40999.75 | -2156.5 | 1276035.375 | 40999.75 | 0
2021021822 | 5 | 0.72191 | 108286.5 | 0.13065 | 0 | 0.51526 | 6440.75 | 0 | 0 | 64000 | 6440.75 | 0 | 37845.75 | -3154 | 1263655.875 | 37845.75 | 0
2021021823 | 5 | 0.69065 | 103597.5 | 0.11607 | 0 | 0.5473 | 6841.25 | 0 | 0 | 64000 | 6841.25 | 0 | 32756.25 | -5089.5 | 1256365.875 | 32756.25 | 0
2021021824 | 5 | 0.66161 | 99241.5 | 0.09382 | 0 | 0.5729 | 7161.25 | 0 | 0 | 64000 | 7161.25 | 0 | 28080.25 | -4676 | 1253751.875 | 28080.25 | 0
2021021901 | 6 | 0.64154 | 96231 | 0.14916 | 0 | 0.56812 | 7101.5 | 0 | 0 | 64000 | 7101.5 | 0 | 25129.5 | -2950.75 | 1254088.625 | 25129.5 | 0
2021021902 | 6 | 0.62974 | 94461 | 0.14426 | 0 | 0.58532 | 7316.5 | 0 | 0 | 64000 | 7316.5 | 0 | 23144.5 | -1985 | 1256410.375 | 23144.5 | 0
2021021903 | 6 | 0.62666 | 93999 | 0.13017 | 0 | 0.5852 | 7315 | 0 | 0 | 64000 | 7315 | 0 | 22684 | -460.5 | 1259192.625 | 22684 | 0
2021021904 | 6 | 0.6304 | 94560 | 0.11264 | 0 | 0.57273 | 7159.125 | 0 | 0 | 64000 | 7159.125 | 0 | 23400.875 | 716.875 | 1261258 | 23400.875 | 0
2021021905 | 6 | 0.64333 | 96499.5 | 0.12326 | 0 | 0.56402 | 7050.25 | 0 | 0 | 64000 | 7050.25 | 0 | 25449.25 | 2048.375 | 1261275 | 25449.25 | 0
2021021906 | 6 | 0.66907 | 100360.5 | 0.15033 | 0 | 0.56582 | 7072.75 | 0 | 0 | 64000 | 7072.75 | 0 | 29287.75 | 3838.5 | 1257453.5 | 29287.75 | 0
2021021907 | 6 | 0.70775 | 106162.5 | 0.11107 | 0 | 0.60296 | 7537 | 0 | 0 | 64000 | 7537 | 0 | 34625.5 | 5337.75 | 1248294.25 | 34625.5 | 0
2021021908 | 6 | 0.74006 | 111009 | 0.11281 | 0 | 0.62377 | 7797.125 | 0.07561 | 6048.8 | 64000 | 7797.125 | 6048.8 | 33163.075 | -1462.425 | 1240597.425 | 33163.075 | 0
2021021909 | 6 | 0.75795 | 113692.5 | 0.08697 | 0 | 0.68067 | 8508.375 | 0.38078 | 30462.4 | 64000 | 8508.375 | 30462.4 | 10721.725 | -22441.35 | 1255341.95 | 10721.725 | 0
2021021910 | 6 | 0.76228 | 114342 | 0.04911 | 0 | 0.7001 | 8751.25 | 0.55755 | 44604 | 64000 | 8751.25 | 41590.75 | 0 | -10721.725 | 1280808.2 | 0 | 0
2021021911 | 6 | 0.75916 | 113874 | 0.03963 | 0 | 0.70252 | 8781.5 | 0.55489 | 44391.2 | 64000 | 8781.5 | 41092.5 | 0 | 0 | 1306274.45 | 0 | 0
2021021912 | 6 | 0.75113 | 112669.5 | 0.05076 | 0 | 0.69044 | 8630.5 | 0.51511 | 41208.8 | 64000 | 8630.5 | 40039 | 0 | 0 | 1331740.7 | 0 | 0
2021021913 | 6 | 0.74008 | 111012 | 0.04997 | 0 | 0.68307 | 8538.375 | 0.46854 | 37483.2 | 64000 | 8538.375 | 37483.2 | 990.425 | 990.425 | 1350000 | 990.425 | 0
2021021914 | 6 | 0.72779 | 109168.5 | 0.0534 | 0 | 0.67477 | 8434.625 | 0.42868 | 34294.4 | 64000 | 8434.625 | 34294.4 | 2439.475 | 1449.05 | 1350000 | 2439.475 | 0
2021021915 | 6 | 0.71752 | 107628 | 0.07224 | 0 | 0.6591 | 8238.75 | 0.26376 | 21100.8 | 64000 | 8238.75 | 21100.8 | 14288.45 | 11848.975 | 1350000 | 14288.45 | 0
2021021916 | 6 | 0.7088 | 106320 | 0.11034 | 0 | 0.63444 | 7930.5 | 0.15505 | 12404 | 64000 | 7930.5 | 12404 | 21985.5 | 7697.05 | 1350000 | 21985.5 | 0
2021021917 | 6 | 0.70821 | 106231.5 | 0.21133 | 0 | 0.65721 | 8215.125 | 0.03965 | 3172 | 64000 | 8215.125 | 3172 | 30844.375 | 8858.875 | 1344621.875 | 30844.375 | 0
2021021918 | 6 | 0.72282 | 108423 | 0.23571 | 0 | 0.65234 | 8154.25 | 0 | 0 | 64000 | 8154.25 | 0 | 36268.75 | 5424.375 | 1333819.375 | 36268.75 | 0
2021021919 | 6 | 0.74464 | 111696 | 0.22387 | 0 | 0.68825 | 8603.125 | 0 | 0 | 64000 | 8603.125 | 0 | 39092.875 | 2824.125 | 1320192.75 | 39092.875 | 0
2021021920 | 6 | 0.74269 | 111403.5 | 0.23056 | 0 | 0.67432 | 8429 | 0 | 0 | 64000 | 8429 | 0 | 38974.5 | -118.375 | 1306684.5 | 38974.5 | 0
2021021921 | 6 | 0.73052 | 109578 | 0.3126 | 0 | 0.65659 | 8207.375 | 0 | 0 | 64000 | 8207.375 | 0 | 37370.625 | -1603.875 | 1294780.125 | 37370.625 | 0
2021021922 | 6 | 0.71397 | 107095.5 | 0.36707 | 0 | 0.65029 | 8128.625 | 0 | 0 | 64000 | 8128.625 | 0 | 34966.875 | -2403.75 | 1285279.5 | 34966.875 | 0
2021021923 | 6 | 0.69076 | 103614 | 0.40295 | 0 | 0.60778 | 7597.25 | 0 | 0 | 64000 | 7597.25 | 0 | 32016.75 | -2950.125 | 1278729 | 32016.75 | 0
2021021924 | 6 | 0.66687 | 100030.5 | 0.4765 | 0 | 0.65478 | 8184.75 | 0 | 0 | 64000 | 8184.75 | 0 | 27845.75 | -4171 | 1276349.5 | 27845.75 | 0
2021022001 | 7 | 0.64963 | 97444.5 | 0.57933 | 0 | 0.65199 | 8149.875 | 0 | 0 | 64000 | 8149.875 | 0 | 25294.625 | -2551.125 | 1276521.125 | 25294.625 | 0
2021022002 | 7 | 0.64102 | 96153 | 0.59766 | 0 | 0.62857 | 7857.125 | 0 | 0 | 64000 | 7857.125 | 0 | 24295.875 | -998.75 | 1277691.5 | 24295.875 | 0
2021022003 | 7 | 0.63705 | 95557.5 | 0.5853 | 0 | 0.61697 | 7712.125 | 0 | 0 | 64000 | 7712.125 | 0 | 23845.375 | -450.5 | 1279312.375 | 23845.375 | 0
2021022004 | 7 | 0.63788 | 95682 | 0.58334 | 0 | 0.62857 | 7857.125 | 0 | 0 | 64000 | 7857.125 | 0 | 23824.875 | -20.5 | 1280953.75 | 23824.875 | 0
2021022005 | 7 | 0.64505 | 96757.5 | 0.58988 | 0 | 0.61221 | 7652.625 | 0 | 0 | 64000 | 7652.625 | 0 | 25104.875 | 1280 | 1281315.125 | 25104.875 | 0
2021022006 | 7 | 0.66331 | 99496.5 | 0.53858 | 0 | 0.60196 | 7524.5 | 0 | 0 | 64000 | 7524.5 | 0 | 27972 | 2867.125 | 1278809.375 | 27972 | 0
2021022007 | 7 | 0.68647 | 102970.5 | 0.53711 | 0 | 0.68137 | 8517.125 | 0 | 0 | 64000 | 8517.125 | 0 | 30453.375 | 2481.375 | 1273822.25 | 30453.375 | 0
2021022008 | 7 | 0.70537 | 105805.5 | 0.51191 | 0 | 0.71527 | 8940.875 | 0.05068 | 4054.4 | 64000 | 8940.875 | 4054.4 | 28810.225 | -1643.15 | 1270478.275 | 28810.225 | 0
2021022009 | 7 | 0.71183 | 106774.5 | 0.44582 | 0 | 0.74121 | 9265.125 | 0.24561 | 19648.8 | 64000 | 9265.125 | 19648.8 | 13860.575 | -14949.65 | 1282083.95 | 13860.575 | 0
2021022010 | 7 | 0.70539 | 105808.5 | 0.44749 | 0 | 0.74195 | 9274.375 | 0.38721 | 30976.8 | 64000 | 9274.375 | 30976.8 | 1557.325 | -12303.25 | 1305992.875 | 1557.325 | 0
2021022011 | 7 | 0.69533 | 104299.5 | 0.43965 | 0 | 0.74372 | 9296.5 | 0.42656 | 34124.8 | 64000 | 9296.5 | 31003 | 0 | -1557.325 | 1331459.125 | 0 | 0
2021022012 | 7 | 0.68255 | 102382.5 | 0.47009 | 0 | 0.75496 | 9437 | 0.45931 | 36744.8 | 64000 | 9437 | 28945.5 | 0 | 0 | 1350000 | 0 | 0
2021022013 | 7 | 0.66881 | 100321.5 | 0.54563 | 0 | 0.75029 | 9378.625 | 0.45764 | 36611.2 | 64000 | 9378.625 | 26942.875 | 0 | 0 | 1350000 | 0 | 0
2021022014 | 7 | 0.65522 | 98283 | 0.61871 | 0 | 0.74313 | 9289.125 | 0.4939 | 39512 | 64000 | 9289.125 | 24993.875 | 0 | 0 | 1350000 | 0 | 0
2021022015 | 7 | 0.64449 | 96673.5 | 0.6434 | 0 | 0.74085 | 9260.625 | 0.46823 | 37458.4 | 64000 | 9260.625 | 23412.875 | 0 | 0 | 1350000 | 0 | 0
2021022016 | 7 | 0.64311 | 96466.5 | 0.7027 | 0 | 0.74514 | 9314.25 | 0.32881 | 26304.8 | 64000 | 9314.25 | 23152.25 | 0 | 0 | 1350000 | 0 | 0
2021022017 | 7 | 0.65464 | 98196 | 0.69406 | 0 | 0.72861 | 9107.625 | 0.10748 | 8598.4 | 64000 | 9107.625 | 8598.4 | 16489.975 | 16489.975 | 1350000 | 16489.975 | 0
2021022018 | 7 | 0.68263 | 102394.5 | 0.71454 | 0 | 0.67418 | 8427.25 | 0.00217 | 173.6 | 64000 | 8427.25 | 173.6 | 29793.65 | 13303.675 | 1345672.6 | 29793.65 | 0
2021022019 | 7 | 0.71983 | 107974.5 | 0.74592 | 0 | 0.62844 | 7855.5 | 0 | 0 | 64000 | 7855.5 | 0 | 36119 | 6325.35 | 1335019.85 | 36119 | 0
2021022020 | 7 | 0.72956 | 109434 | 0.77886 | 0 | 0.63499 | 7937.375 | 0 | 0 | 64000 | 7937.375 | 0 | 37496.625 | 1377.625 | 1322989.475 | 37496.625 | 0
2021022021 | 7 | 0.72461 | 108691.5 | 0.78147 | 0 | 0.64281 | 8035.125 | 0 | 0 | 64000 | 8035.125 | 0 | 36656.375 | -840.25 | 1311799.35 | 36656.375 | 0
2021022022 | 7 | 0.71271 | 106906.5 | 0.77345 | 0 | 0.61977 | 7747.125 | 0 | 0 | 64000 | 7747.125 | 0 | 35159.375 | -1497 | 1302106.225 | 35159.375 | 0
2021022023 | 7 | 0.69391 | 104086.5 | 0.75237 | 0 | 0.6341 | 7926.25 | 0 | 0 | 64000 | 7926.25 | 0 | 32160.25 | -2999.125 | 1295412.225 | 32160.25 | 0
2021022024 | 7 | 0.67602 | 101403 | 0.74027 | 0 | 0.61665 | 7708.125 | 0 | 0 | 64000 | 7708.125 | 0 | 29694.875 | -2465.375 | 1291183.6 | 29694.875 | 0
2021022101 | 1 | 0.66106 | 99159 | 0.69322 | 0 | 0.61202 | 7650.25 | 0 | 0 | 64000 | 7650.25 | 0 | 27508.75 | -2186.125 | 1289141.1 | 27508.75 | 0
2021022102 | 1 | 0.65458 | 98187 | 0.66681 | 0 | 0.59117 | 7389.625 | 0 | 0 | 64000 | 7389.625 | 0 | 26797.375 | -711.375 | 1287809.975 | 26797.375 | 0
2021022103 | 1 | 0.65443 | 98164.5 | 0.63792 | 0 | 0.55945 | 6993.125 | 0 | 0 | 64000 | 6993.125 | 0 | 27171.375 | 374 | 1286104.85 | 27171.375 | 0
2021022104 | 1 | 0.65685 | 98527.5 | 0.5882 | 0 | 0.5136 | 6420 | 0 | 0 | 64000 | 6420 | 0 | 28107.5 | 936.125 | 1283463.6 | 28107.5 | 0
2021022105 | 1 | 0.66399 | 99598.5 | 0.53136 | 0 | 0.44518 | 5564.75 | 0 | 0 | 64000 | 5564.75 | 0 | 30033.75 | 1926.25 | 1278896.1 | 30033.75 | 0
2021022106 | 1 | 0.6773 | 101595 | 0.48766 | 0 | 0.42078 | 5259.75 | 0 | 0 | 64000 | 5259.75 | 0 | 32335.25 | 2301.5 | 1272027.1 | 32335.25 | 0
2021022107 | 1 | 0.69676 | 104514 | 0.43678 | 0 | 0.37346 | 4668.25 | 0 | 0 | 64000 | 4668.25 | 0 | 35845.75 | 3510.5 | 1261647.6 | 35845.75 | 0
2021022108 | 1 | 0.70708 | 106062 | 0.39529 | 0 | 0.30919 | 3864.875 | 0.0719 | 5752 | 64000 | 3864.875 | 5752 | 32445.125 | -3400.625 | 1254668.725 | 32445.125 | 0
2021022109 | 1 | 0.69796 | 104694 | 0.27355 | 0 | 0.25046 | 3130.75 | 0.37715 | 30172 | 64000 | 3130.75 | 30172 | 7391.25 | -25053.875 | 1272743.725 | 7391.25 | 0
2021022110 | 1 | 0.68166 | 102249 | 0.13399 | 0 | 0.18911 | 2363.875 | 0.57627 | 46101.6 | 64000 | 2363.875 | 35885.125 | 0 | -7391.25 | 1298209.975 | 0 | 0
2021022111 | 1 | 0.66141 | 99211.5 | 0.0935 | 0 | 0.18944 | 2368 | 0.60853 | 48682.4 | 64000 | 2368 | 32843.5 | 0 | 0 | 1323676.225 | 0 | 0
2021022112 | 1 | 0.64345 | 96517.5 | 0.06248 | 0 | 0.20499 | 2562.375 | 0.60702 | 48561.6 | 64000 | 2562.375 | 29955.125 | 0 | 0 | 1349142.475 | 0 | 0
2021022113 | 1 | 0.62763 | 94144.5 | 0.04138 | 0 | 0.20191 | 2523.875 | 0.61262 | 49009.6 | 64000 | 2523.875 | 27620.625 | 0 | 0 | 1350000 | 0 | 0
2021022114 | 1 | 0.61112 | 91668 | 0.02276 | 0 | 0.20115 | 2514.375 | 0.6253 | 50024 | 64000 | 2514.375 | 25153.625 | 0 | 0 | 1350000 | 0 | 0
2021022115 | 1 | 0.59926 | 89889 | 0.01779 | 0 | 0.24928 | 3116 | 0.57689 | 46151.2 | 64000 | 3116 | 22773 | 0 | 0 | 1350000 | 0 | 0
2021022116 | 1 | 0.59871 | 89806.5 | 0.07747 | 0 | 0.32221 | 4027.625 | 0.40734 | 32587.2 | 64000 | 4027.625 | 21778.875 | 0 | 0 | 1350000 | 0 | 0
2021022117 | 1 | 0.61543 | 92314.5 | 0.14976 | 0 | 0.33858 | 4232.25 | 0.08503 | 6802.4 | 64000 | 4232.25 | 6802.4 | 17279.85 | 17279.85 | 1350000 | 17279.85 | 0
2021022118 | 1 | 0.64936 | 97404 | 0.19363 | 0 | 0.3057 | 3821.25 | 0.00048 | 38.4 | 64000 | 3821.25 | 38.4 | 29544.35 | 12264.5 | 1345921.9 | 29544.35 | 0
2021022119 | 1 | 0.68466 | 102699 | 0.35399 | 0 | 0.2902 | 3627.5 | 0 | 0 | 64000 | 3627.5 | 0 | 35071.5 | 5527.15 | 1336316.65 | 35071.5 | 0
2021022120 | 1 | 0.69366 | 104049 | 0.533 | 0 | 0.29879 | 3734.875 | 0 | 0 | 64000 | 3734.875 | 0 | 36314.125 | 1242.625 | 1325468.775 | 36314.125 | 0
2021022121 | 1 | 0.68523 | 102784.5 | 0.72069 | 0 | 0.26435 | 3304.375 | 0 | 0 | 64000 | 3304.375 | 0 | 35480.125 | -834 | 1315454.9 | 35480.125 | 0
2021022122 | 1 | 0.6675 | 100125 | 0.79239 | 0 | 0.2777 | 3471.25 | 0 | 0 | 64000 | 3471.25 | 0 | 32653.75 | -2826.375 | 1308267.4 | 32653.75 | 0
2021022123 | 1 | 0.64279 | 96418.5 | 0.85657 | 0 | 0.29682 | 3710.25 | 0 | 0 | 64000 | 3710.25 | 0 | 28708.25 | -3945.5 | 1305025.4 | 28708.25 | 0
2021022124 | 1 | 0.61846 | 92769 | 0.86487 | 0 | 0.30997 | 3874.625 | 0 | 0 | 64000 | 3874.625 | 0 | 24894.375 | -3813.875 | 1305597.275 | 24894.375 | 0
2021022201 | 2 | 0.60066 | 90099 | 0.84715 | 0 | 0.29728 | 3716 | 0 | 0 | 64000 | 3716 | 0 | 22383 | -2511.375 | 1308680.525 | 22383 | 0
2021022202 | 2 | 0.59229 | 88843.5 | 0.87428 | 0 | 0.26869 | 3358.625 | 0 | 0 | 64000 | 3358.625 | 0 | 21484.875 | -898.125 | 1312661.9 | 21484.875 | 0
2021022203 | 2 | 0.58888 | 88332 | 0.89209 | 0 | 0.21186 | 2648.25 | 0 | 0 | 64000 | 2648.25 | 0 | 21683.75 | 198.875 | 1316444.4 | 21683.75 | 0
2021022204 | 2 | 0.59116 | 88674 | 0.90555 | 0 | 0.18808 | 2351 | 0 | 0 | 64000 | 2351 | 0 | 22323 | 639.25 | 1319587.65 | 22323 | 0
2021022205 | 2 | 0.60538 | 90807 | 0.87522 | 0 | 0.1464 | 1830 | 0 | 0 | 64000 | 1830 | 0 | 24977 | 2654 | 1320076.9 | 24977 | 0
2021022206 | 2 | 0.63359 | 95038.5 | 0.84349 | 0 | 0.0994 | 1242.5 | 0 | 0 | 64000 | 1242.5 | 0 | 29796 | 4819 | 1315747.15 | 29796 | 0
2021022207 | 2 | 0.67787 | 101680.5 | 0.87642 | 0 | 0.08489 | 1061.125 | 0 | 0 | 64000 | 1061.125 | 0 | 36619.375 | 6823.375 | 1304594.025 | 36619.375 | 0
2021022208 | 2 | 0.70998 | 106497 | 0.92492 | 0 | 0.08769 | 1096.125 | 0.07445 | 5956 | 64000 | 1096.125 | 5956 | 35444.875 | -1174.5 | 1294615.4 | 35444.875 | 0
2021022209 | 2 | 0.72436 | 108654 | 0.93563 | 0 | 0.11925 | 1490.625 | 0.38536 | 30828.8 | 64000 | 1490.625 | 30828.8 | 12334.575 | -23110.3 | 1307747.075 | 12334.575 | 0
2021022210 | 2 | 0.73151 | 109726.5 | 0.93055 | 0 | 0.1152 | 1440 | 0.56497 | 45197.6 | 64000 | 1440 | 44286.5 | 0 | -12334.575 | 1333213.325 | 0 | 0
2021022211 | 2 | 0.73579 | 110368.5 | 0.92637 | 0 | 0.09523 | 1190.375 | 0.59941 | 47952.8 | 64000 | 1190.375 | 45178.125 | 0 | 0 | 1350000 | 0 | 0
2021022212 | 2 | 0.73524 | 110286 | 0.89264 | 0 | 0.08459 | 1057.375 | 0.6105 | 48840 | 64000 | 1057.375 | 45228.625 | 0 | 0 | 1350000 | 0 | 0
2021022213 | 2 | 0.72832 | 109248 | 0.88158 | 0 | 0.08442 | 1055.25 | 0.61732 | 49385.6 | 64000 | 1055.25 | 44192.75 | 0 | 0 | 1350000 | 0 | 0
2021022214 | 2 | 0.71932 | 107898 | 0.9244 | 0 | 0.07398 | 924.75 | 0.63107 | 50485.6 | 64000 | 924.75 | 42973.25 | 0 | 0 | 1350000 | 0 | 0
2021022215 | 2 | 0.70876 | 106314 | 0.91618 | 0 | 0.08272 | 1034 | 0.63035 | 50428 | 64000 | 1034 | 41280 | 0 | 0 | 1350000 | 0 | 0
2021022216 | 2 | 0.69668 | 104502 | 0.83429 | 0 | 0.15291 | 1911.375 | 0.50597 | 40477.6 | 64000 | 1911.375 | 38590.625 | 0 | 0 | 1350000 | 0 | 0
2021022217 | 2 | 0.69281 | 103921.5 | 0.83054 | 0 | 0.20924 | 2615.5 | 0.15543 | 12434.4 | 64000 | 2615.5 | 12434.4 | 24871.6 | 24871.6 | 1350000 | 24871.6 | 0
2021022218 | 2 | 0.70222 | 105333 | 0.83213 | 0 | 0.25608 | 3201 | 0.00233 | 186.4 | 64000 | 3201 | 186.4 | 37945.6 | 13074 | 1337520.65 | 37945.6 | 0
2021022219 | 2 | 0.72168 | 108252 | 0.81288 | 0 | 0.271 | 3387.5 | 0 | 0 | 64000 | 3387.5 | 0 | 40864.5 | 2918.9 | 1322122.4 | 40864.5 | 0
2021022220 | 2 | 0.71996 | 107994 | 0.87725 | 0 | 0.29391 | 3673.875 | 0 | 0 | 64000 | 3673.875 | 0 | 40320.125 | -544.375 | 1307268.525 | 40320.125 | 0
2021022221 | 2 | 0.7042 | 105630 | 0.89598 | 0 | 0.31159 | 3894.875 | 0 | 0 | 64000 | 3894.875 | 0 | 37735.125 | -2585 | 1294999.65 | 37735.125 | 0
2021022222 | 2 | 0.6804 | 102060 | 0.91659 | 0 | 0.29447 | 3680.875 | 0 | 0 | 64000 | 3680.875 | 0 | 34379.125 | -3356 | 1286086.775 | 34379.125 | 0
2021022223 | 2 | 0.64948 | 97422 | 0.89871 | 0 | 0.27152 | 3394 | 0 | 0 | 64000 | 3394 | 0 | 30028 | -4351.125 | 1281525.025 | 30028 | 0
2021022224 | 2 | 0.62153 | 93229.5 | 0.87506 | 0 | 0.26833 | 3354.125 | 0 | 0 | 64000 | 3354.125 | 0 | 25875.375 | -4152.625 | 1281115.9 | 25875.375 | 0
2021022301 | 3 | 0.6005 | 90075 | 0.80109 | 0 | 0.28833 | 3604.125 | 0 | 0 | 64000 | 3604.125 | 0 | 22470.875 | -3404.5 | 1284111.275 | 22470.875 | 0
2021022302 | 3 | 0.58918 | 88377 | 0.78566 | 0 | 0.29861 | 3732.625 | 0 | 0 | 64000 | 3732.625 | 0 | 20644.375 | -1826.5 | 1288933.15 | 20644.375 | 0
2021022303 | 3 | 0.58416 | 87624 | 0.70645 | 0 | 0.33586 | 4198.25 | 0 | 0 | 64000 | 4198.25 | 0 | 19425.75 | -1218.625 | 1294973.65 | 19425.75 | 0
2021022304 | 3 | 0.58563 | 87844.5 | 0.77977 | 0 | 0.36987 | 4623.375 | 0 | 0 | 64000 | 4623.375 | 0 | 19221.125 | -204.625 | 1301218.775 | 19221.125 | 0
2021022305 | 3 | 0.59857 | 89785.5 | 0.81578 | 0 | 0.34868 | 4358.5 | 0 | 0 | 64000 | 4358.5 | 0 | 21427 | 2205.875 | 1305258.025 | 21427 | 0
2021022306 | 3 | 0.62858 | 94287 | 0.84595 | 0 | 0.32482 | 4060.25 | 0 | 0 | 64000 | 4060.25 | 0 | 26226.75 | 4799.75 | 1304497.525 | 26226.75 | 0
2021022307 | 3 | 0.67272 | 100908 | 0.83107 | 0 | 0.2589 | 3236.25 | 0 | 0 | 64000 | 3236.25 | 0 | 33671.75 | 7445 | 1296292.025 | 33671.75 | 0
2021022308 | 3 | 0.69824 | 104736 | 0.81544 | 0 | 0.22761 | 2845.125 | 0.08716 | 6972.8 | 64000 | 2845.125 | 6972.8 | 30918.075 | -2753.675 | 1290840.2 | 30918.075 | 0
2021022309 | 3 | 0.69274 | 103911 | 0.86284 | 0 | 0.24577 | 3072.125 | 0.41967 | 33573.6 | 64000 | 3072.125 | 33573.6 | 3265.275 | -27652.8 | 1313041.175 | 3265.275 | 0
2021022310 | 3 | 0.67383 | 101074.5 | 0.9176 | 0 | 0.23675 | 2959.375 | 0.61693 | 49354.4 | 64000 | 2959.375 | 34115.125 | 0 | -3265.275 | 1338507.425 | 0 | 0
2021022311 | 3 | 0.6566 | 98490 | 0.91044 | 0 | 0.24434 | 3054.25 | 0.63968 | 51174.4 | 64000 | 3054.25 | 31435.75 | 0 | 0 | 1350000 | 0 | 0
2021022312 | 3 | 0.64448 | 96672 | 0.89026 | 0 | 0.27146 | 3393.25 | 0.64383 | 51506.4 | 64000 | 3393.25 | 29278.75 | 0 | 0 | 1350000 | 0 | 0
2021022313 | 3 | 0.63282 | 94923 | 0.86961 | 0 | 0.33379 | 4172.375 | 0.65052 | 52041.6 | 64000 | 4172.375 | 26750.625 | 0 | 0 | 1350000 | 0 | 0
2021022314 | 3 | 0.61779 | 92668.5 | 0.89069 | 0 | 0.37161 | 4645.125 | 0.67048 | 53638.4 | 64000 | 4645.125 | 24023.375 | 0 | 0 | 1350000 | 0 | 0
2021022315 | 3 | 0.60204 | 90306 | 0.94278 | 0 | 0.44304 | 5538 | 0.67176 | 53740.8 | 64000 | 5538 | 20768 | 0 | 0 | 1350000 | 0 | 0
2021022316 | 3 | 0.59409 | 89113.5 | 0.94788 | 0 | 0.52465 | 6558.125 | 0.52514 | 42011.2 | 64000 | 6558.125 | 18555.375 | 0 | 0 | 1350000 | 0 | 0
2021022317 | 3 | 0.60073 | 90109.5 | 0.95835 | 0 | 0.57376 | 7172 | 0.15778 | 12622.4 | 64000 | 7172 | 12622.4 | 6315.1 | 6315.1 | 1350000 | 6315.1 | 0
2021022318 | 3 | 0.62015 | 93022.5 | 0.96446 | 0 | 0.57609 | 7201.125 | 0.00165 | 132 | 64000 | 7201.125 | 132 | 21689.375 | 15374.275 | 1350000 | 21689.375 | 0
2021022319 | 3 | 0.64811 | 97216.5 | 0.93493 | 0 | 0.5648 | 7060 | 0 | 0 | 64000 | 7060 | 0 | 26156.5 | 4467.125 | 1349309.75 | 26156.5 | 0
2021022320 | 3 | 0.65565 | 98347.5 | 0.91024 | 0 | 0.56468 | 7058.5 | 0 | 0 | 64000 | 7058.5 | 0 | 27289 | 1132.5 | 1347487 | 27289 | 0
2021022321 | 3 | 0.64623 | 96934.5 | 0.93528 | 0 | 0.57871 | 7233.875 | 0 | 0 | 64000 | 7233.875 | 0 | 25700.625 | -1588.375 | 1347252.625 | 25700.625 | 0
2021022322 | 3 | 0.6281 | 94215 | 0.95336 | 0 | 0.59534 | 7441.75 | 0 | 0 | 64000 | 7441.75 | 0 | 22773.25 | -2927.375 | 1349945.625 | 22773.25 | 0
2021022323 | 3 | 0.60257 | 90385.5 | 0.94086 | 0 | 0.6254 | 7817.5 | 0 | 0 | 64000 | 7817.5 | 0 | 18568 | -4205.25 | 1350000 | 18568 | 0
2021022324 | 3 | 0.57615 | 86422.5 | 0.92003 | 0 | 0.63242 | 7905.25 | 0 | 0 | 64000 | 7905.25 | 0 | 14517.25 | -4050.75 | 1350000 | 14517.25 | 0
2021022401 | 4 | 0.55896 | 83844 | 0.91056 | 0 | 0.62785 | 7848.125 | 0 | 0 | 64000 | 7848.125 | 0 | 11995.875 | -2521.375 | 1350000 | 11995.875 | 0
2021022402 | 4 | 0.55127 | 82690.5 | 0.87559 | 0 | 0.65289 | 8161.125 | 0 | 0 | 64000 | 8161.125 | 0 | 10529.375 | -1466.5 | 1350000 | 10529.375 | 0
2021022403 | 4 | 0.54985 | 82477.5 | 0.76056 | 0 | 0.65952 | 8244 | 0 | 0 | 64000 | 8244 | 0 | 10233.5 | -295.875 | 1350000 | 10233.5 | 0
2021022404 | 4 | 0.55476 | 83214 | 0.61898 | 0 | 0.6275 | 7843.75 | 0 | 0 | 64000 | 7843.75 | 0 | 11370.25 | 1136.75 | 1350000 | 11370.25 | 0
2021022405 | 4 | 0.5696 | 85440 | 0.50733 | 0 | 0.56018 | 7002.25 | 0 | 0 | 64000 | 7002.25 | 0 | 14437.75 | 3067.5 | 1350000 | 14437.75 | 0
2021022406 | 4 | 0.60159 | 90238.5 | 0.51755 | 0 | 0.49093 | 6136.625 | 0 | 0 | 64000 | 6136.625 | 0 | 20101.875 | 5664.125 | 1350000 | 20101.875 | 0
2021022407 | 4 | 0.64929 | 97393.5 | 0.56493 | 0 | 0.41279 | 5159.875 | 0 | 0 | 64000 | 5159.875 | 0 | 28233.625 | 8131.75 | 1347232.625 | 28233.625 | 0
2021022408 | 4 | 0.67297 | 100945.5 | 0.61773 | 0 | 0.38756 | 4844.5 | 0.07983 | 6386.4 | 64000 | 4844.5 | 6386.4 | 25714.6 | -2519.025 | 1346984.275 | 25714.6 | 0
2021022409 | 4 | 0.66188 | 99282 | 0.60847 | 0 | 0.41522 | 5190.25 | 0.27565 | 22052 | 64000 | 5190.25 | 22052 | 8039.75 | -17674.85 | 1350000 | 8039.75 | 0
2021022410 | 4 | 0.63504 | 95256 | 0.51139 | 0 | 0.39961 | 4995.125 | 0.39623 | 31698.4 | 64000 | 4995.125 | 26260.875 | 0 | -8039.75 | 1350000 | 0 | 0
2021022411 | 4 | 0.60919 | 91378.5 | 0.48113 | 0 | 0.31411 | 3926.375 | 0.41744 | 33395.2 | 64000 | 3926.375 | 23452.125 | 0 | 0 | 1350000 | 0 | 0
2021022412 | 4 | 0.59288 | 88932 | 0.63898 | 0 | 0.19198 | 2399.75 | 0.45658 | 36526.4 | 64000 | 2399.75 | 22532.25 | 0 | 0 | 1350000 | 0 | 0
2021022413 | 4 | 0.5809 | 87135 | 0.81646 | 0 | 0.10599 | 1324.875 | 0.4726 | 37808 | 64000 | 1324.875 | 21810.125 | 0 | 0 | 1350000 | 0 | 0
2021022414 | 4 | 0.57157 | 85735.5 | 0.89232 | 0 | 0.08729 | 1091.125 | 0.45765 | 36612 | 64000 | 1091.125 | 20644.375 | 0 | 0 | 1350000 | 0 | 0
2021022415 | 4 | 0.56497 | 84745.5 | 0.92915 | 0 | 0.13987 | 1748.375 | 0.3759 | 30072 | 64000 | 1748.375 | 18997.125 | 0 | 0 | 1350000 | 0 | 0
2021022416 | 4 | 0.56335 | 84502.5 | 0.92577 | 0 | 0.19628 | 2453.5 | 0.23019 | 18415.2 | 64000 | 2453.5 | 18049 | 0 | 0 | 1350000 | 0 | 0
2021022417 | 4 | 0.57429 | 86143.5 | 0.91509 | 0 | 0.20133 | 2516.625 | 0.0751 | 6008 | 64000 | 2516.625 | 6008 | 13618.875 | 13618.875 | 1350000 | 13618.875 | 0
2021022418 | 4 | 0.59288 | 88932 | 0.88168 | 0 | 0.228 | 2850 | 0.00446 | 356.8 | 64000 | 2850 | 356.8 | 21725.2 | 8106.325 | 1350000 | 21725.2 | 0
2021022419 | 4 | 0.61939 | 92908.5 | 0.95865 | 0 | 0.28492 | 3561.5 | 0 | 0 | 64000 | 3561.5 | 0 | 25347 | 3621.8 | 1350000 | 25347 | 0
2021022420 | 4 | 0.62243 | 93364.5 | 0.96955 | 0 | 0.32481 | 4060.125 | 0 | 0 | 64000 | 4060.125 | 0 | 25304.375 | -42.625 | 1350000 | 25304.375 | 0
2021022421 | 4 | 0.61265 | 91897.5 | 0.98122 | 0 | 0.34939 | 4367.375 | 0 | 0 | 64000 | 4367.375 | 0 | 23530.125 | -1774.25 | 1350000 | 23530.125 | 0
2021022422 | 4 | 0.59307 | 88960.5 | 0.98751 | 0 | 0.36007 | 4500.875 | 0 | 0 | 64000 | 4500.875 | 0 | 20459.625 | -3070.5 | 1350000 | 20459.625 | 0
2021022423 | 4 | 0.56503 | 84754.5 | 0.99264 | 0 | 0.39418 | 4927.25 | 0 | 0 | 64000 | 4927.25 | 0 | 15827.25 | -4632.375 | 1350000 | 15827.25 | 0
2021022424 | 4 | 0.53756 | 80634 | 0.99261 | 0 | 0.42883 | 5360.375 | 0 | 0 | 64000 | 5360.375 | 0 | 11273.625 | -4553.625 | 1350000 | 11273.625 | 0
2021022501 | 5 | 0.51909 | 77863.5 | 0.98897 | 0 | 0.46241 | 5780.125 | 0 | 0 | 64000 | 5780.125 | 0 | 8083.375 | -3190.25 | 1350000 | 8083.375 | 0
2021022502 | 5 | 0.50921 | 76381.5 | 0.98173 | 0 | 0.45408 | 5676 | 0 | 0 | 64000 | 5676 | 0 | 6705.5 | -1377.875 | 1350000 | 6705.5 | 0
2021022503 | 5 | 0.50689 | 76033.5 | 0.97311 | 0 | 0.4459 | 5573.75 | 0 | 0 | 64000 | 5573.75 | 0 | 6459.75 | -245.75 | 1350000 | 6459.75 | 0
2021022504 | 5 | 0.51146 | 76719 | 0.96788 | 0 | 0.43768 | 5471 | 0 | 0 | 64000 | 5471 | 0 | 7248 | 788.25 | 1350000 | 7248 | 0
2021022505 | 5 | 0.52631 | 78946.5 | 0.97424 | 0 | 0.40695 | 5086.875 | 0 | 0 | 64000 | 5086.875 | 0 | 9859.625 | 2611.625 | 1350000 | 9859.625 | 0
2021022506 | 5 | 0.55987 | 83980.5 | 0.92283 | 0 | 0.34208 | 4276 | 0 | 0 | 64000 | 4276 | 0 | 15704.5 | 5844.875 | 1350000 | 15704.5 | 0
2021022507 | 5 | 0.60784 | 91176 | 0.8065 | 0 | 0.25129 | 3141.125 | 0 | 0 | 64000 | 3141.125 | 0 | 24034.875 | 8330.375 | 1350000 | 24034.875 | 0
2021022508 | 5 | 0.63681 | 95521.5 | 0.78079 | 0 | 0.22699 | 2837.375 | 0.03157 | 2525.6 | 64000 | 2837.375 | 2525.6 | 26158.525 | 2123.65 | 1349307.725 | 26158.525 | 0
2021022509 | 5 | 0.63429 | 95143.5 | 0.7153 | 0 | 0.19504 | 2438 | 0.13322 | 10657.6 | 64000 | 2438 | 10657.6 | 18047.9 | -8110.625 | 1350000 | 18047.9 | 0
2021022510 | 5 | 0.61873 | 92809.5 | 0.619 | 0 | 0.18255 | 2281.875 | 0.26196 | 20956.8 | 64000 | 2281.875 | 20956.8 | 5570.825 | -12477.075 | 1350000 | 5570.825 | 0
2021022511 | 5 | 0.60548 | 90822 | 0.4822 | 0 | 0.18871 | 2358.875 | 0.33829 | 27063.2 | 64000 | 2358.875 | 24463.125 | 0 | -5570.825 | 1350000 | 0 | 0
2021022512 | 5 | 0.59457 | 89185.5 | 0.42705 | 0 | 0.19406 | 2425.75 | 0.41612 | 33289.6 | 64000 | 2425.75 | 22759.75 | 0 | 0 | 1350000 | 0 | 0
2021022513 | 5 | 0.58497 | 87745.5 | 0.39585 | 0 | 0.18492 | 2311.5 | 0.45696 | 36556.8 | 64000 | 2311.5 | 21434 | 0 | 0 | 1350000 | 0 | 0
2021022514 | 5 | 0.57547 | 86320.5 | 0.4401 | 0 | 0.17243 | 2155.375 | 0.46809 | 37447.2 | 64000 | 2155.375 | 20165.125 | 0 | 0 | 1350000 | 0 | 0
2021022515 | 5 | 0.56649 | 84973.5 | 0.5815 | 0 | 0.25285 | 3160.625 | 0.42275 | 33820 | 64000 | 3160.625 | 17812.875 | 0 | 0 | 1350000 | 0 | 0
2021022516 | 5 | 0.56322 | 84483 | 0.63998 | 0 | 0.37834 | 4729.25 | 0.26454 | 21163.2 | 64000 | 4729.25 | 15753.75 | 0 | 0 | 1350000 | 0 | 0
2021022517 | 5 | 0.57167 | 85750.5 | 0.55644 | 0 | 0.39747 | 4968.375 | 0.07761 | 6208.8 | 64000 | 4968.375 | 6208.8 | 10573.325 | 10573.325 | 1350000 | 10573.325 | 0
2021022518 | 5 | 0.5952 | 89280 | 0.39827 | 0 | 0.37387 | 4673.375 | 0.0007 | 56 | 64000 | 4673.375 | 56 | 20550.625 | 9977.3 | 1350000 | 20550.625 | 0
2021022519 | 5 | 0.62998 | 94497 | 0.31867 | 0 | 0.36016 | 4502 | 0 | 0 | 64000 | 4502 | 0 | 25995 | 5444.375 | 1349471.25 | 25995 | 0
2021022520 | 5 | 0.64145 | 96217.5 | 0.35488 | 0 | 0.33572 | 4196.5 | 0 | 0 | 64000 | 4196.5 | 0 | 28021 | 2026 | 1346916.5 | 28021 | 0
2021022521 | 5 | 0.63684 | 95526 | 0.38211 | 0 | 0.35841 | 4480.125 | 0 | 0 | 64000 | 4480.125 | 0 | 27045.875 | -975.125 | 1345336.875 | 27045.875 | 0
2021022522 | 5 | 0.62246 | 93369 | 0.38417 | 0 | 0.38607 | 4825.875 | 0 | 0 | 64000 | 4825.875 | 0 | 24543.125 | -2502.75 | 1346260 | 24543.125 | 0
2021022523 | 5 | 0.59763 | 89644.5 | 0.44039 | 0 | 0.41057 | 5132.125 | 0 | 0 | 64000 | 5132.125 | 0 | 20512.375 | -4030.75 | 1350000 | 20512.375 | 0
2021022524 | 5 | 0.57461 | 86191.5 | 0.47989 | 0 | 0.41477 | 5184.625 | 0 | 0 | 64000 | 5184.625 | 0 | 17006.875 | -3505.5 | 1350000 | 17006.875 | 0
2021022601 | 6 | 0.55801 | 83701.5 | 0.46042 | 0 | 0.4135 | 5168.75 | 0 | 0 | 64000 | 5168.75 | 0 | 14532.75 | -2474.125 | 1350000 | 14532.75 | 0
2021022602 | 6 | 0.54928 | 82392 | 0.40834 | 0 | 0.3839 | 4798.75 | 0 | 0 | 64000 | 4798.75 | 0 | 13593.25 | -939.5 | 1350000 | 13593.25 | 0
2021022603 | 6 | 0.54678 | 82017 | 0.37343 | 0 | 0.34493 | 4311.625 | 0 | 0 | 64000 | 4311.625 | 0 | 13705.375 | 112.125 | 1350000 | 13705.375 | 0
2021022604 | 6 | 0.54973 | 82459.5 | 0.31558 | 0 | 0.30648 | 3831 | 0 | 0 | 64000 | 3831 | 0 | 14628.5 | 923.125 | 1350000 | 14628.5 | 0
2021022605 | 6 | 0.56277 | 84415.5 | 0.32118 | 0 | 0.26309 | 3288.625 | 0 | 0 | 64000 | 3288.625 | 0 | 17126.875 | 2498.375 | 1350000 | 17126.875 | 0
2021022606 | 6 | 0.59297 | 88945.5 | 0.32134 | 0 | 0.1792 | 2240 | 0 | 0 | 64000 | 2240 | 0 | 22705.5 | 5578.625 | 1350000 | 22705.5 | 0
2021022607 | 6 | 0.63973 | 95959.5 | 0.29092 | 0 | 0.12477 | 1559.625 | 0 | 0 | 64000 | 1559.625 | 0 | 30399.875 | 7694.375 | 1345066.375 | 30399.875 | 0
2021022608 | 6 | 0.66748 | 100122 | 0.19643 | 0 | 0.12535 | 1566.875 | 0.06506 | 5204.8 | 64000 | 1566.875 | 5204.8 | 29350.325 | -1049.55 | 1341182.3 | 29350.325 | 0
2021022609 | 6 | 0.66408 | 99612 | 0.06652 | 0 | 0.14552 | 1819 | 0.3029 | 24232 | 64000 | 1819 | 24232 | 9561 | -19789.325 | 1350000 | 9561 | 0
2021022610 | 6 | 0.65114 | 97671 | 0.02402 | 0 | 0.16622 | 2077.75 | 0.50894 | 40715.2 | 64000 | 2077.75 | 31593.25 | 0 | -9561 | 1350000 | 0 | 0
2021022611 | 6 | 0.63845 | 95767.5 | 0.06576 | 0 | 0.17191 | 2148.875 | 0.57133 | 45706.4 | 64000 | 2148.875 | 29618.625 | 0 | 0 | 1350000 | 0 | 0
2021022612 | 6 | 0.62644 | 93966 | 0.22164 | 0 | 0.17019 | 2127.375 | 0.61137 | 48909.6 | 64000 | 2127.375 | 27838.625 | 0 | 0 | 1350000 | 0 | 0
2021022613 | 6 | 0.6178 | 92670 | 0.27674 | 0 | 0.16307 | 2038.375 | 0.63695 | 50956 | 64000 | 2038.375 | 26631.625 | 0 | 0 | 1350000 | 0 | 0
2021022614 | 6 | 0.61116 | 91674 | 0.23052 | 0 | 0.11549 | 1443.625 | 0.65099 | 52079.2 | 64000 | 1443.625 | 26230.375 | 0 | 0 | 1350000 | 0 | 0
2021022615 | 6 | 0.60777 | 91165.5 | 0.23294 | 0 | 0.14862 | 1857.75 | 0.61068 | 48854.4 | 64000 | 1857.75 | 25307.75 | 0 | 0 | 1350000 | 0 | 0
2021022616 | 6 | 0.6095 | 91425 | 0.30069 | 0 | 0.21205 | 2650.625 | 0.47686 | 38148.8 | 64000 | 2650.625 | 24774.375 | 0 | 0 | 1350000 | 0 | 0
2021022617 | 6 | 0.61841 | 92761.5 | 0.44057 | 0 | 0.20902 | 2612.75 | 0.15249 | 12199.2 | 64000 | 2612.75 | 12199.2 | 13949.55 | 13949.55 | 1350000 | 13949.55 | 0
2021022618 | 6 | 0.63578 | 95367 | 0.67891 | 0 | 0.19619 | 2452.375 | 0.00345 | 276 | 64000 | 2452.375 | 276 | 28638.625 | 14689.075 | 1346827.625 | 28638.625 | 0
2021022619 | 6 | 0.65347 | 98020.5 | 0.84448 | 0 | 0.18816 | 2352 | 0 | 0 | 64000 | 2352 | 0 | 31668.5 | 3029.875 | 1340625.375 | 31668.5 | 0
2021022620 | 6 | 0.65118 | 97677 | 0.91934 | 0 | 0.15563 | 1945.375 | 0 | 0 | 64000 | 1945.375 | 0 | 31731.625 | 63.125 | 1334360 | 31731.625 | 0
2021022621 | 6 | 0.63823 | 95734.5 | 0.95329 | 0 | 0.14332 | 1791.5 | 0 | 0 | 64000 | 1791.5 | 0 | 29943 | -1788.625 | 1329883.25 | 29943 | 0
2021022622 | 6 | 0.61946 | 92919 | 0.97668 | 0 | 0.14543 | 1817.875 | 0 | 0 | 64000 | 1817.875 | 0 | 27101.125 | -2841.875 | 1328248.375 | 27101.125 | 0
2021022623 | 6 | 0.59414 | 89121 | 0.97536 | 0 | 0.15613 | 1951.625 | 0 | 0 | 64000 | 1951.625 | 0 | 23169.375 | -3931.75 | 1330545.25 | 23169.375 | 0
2021022624 | 6 | 0.56757 | 85135.5 | 0.97667 | 0 | 0.16055 | 2006.875 | 0 | 0 | 64000 | 2006.875 | 0 | 19128.625 | -4040.75 | 1336882.875 | 19128.625 | 0
2021022701 | 7 | 0.54717 | 82075.5 | 0.95931 | 0 | 0.15509 | 1938.625 | 0 | 0 | 64000 | 1938.625 | 0 | 16136.875 | -2991.75 | 1346212.25 | 16136.875 | 0
2021022702 | 7 | 0.53325 | 79987.5 | 0.92039 | 0 | 0.12689 | 1586.125 | 0 | 0 | 64000 | 1586.125 | 0 | 14401.375 | -1735.5 | 1350000 | 14401.375 | 0
2021022703 | 7 | 0.52565 | 78847.5 | 0.88483 | 0 | 0.08772 | 1096.5 | 0 | 0 | 64000 | 1096.5 | 0 | 13751 | -650.375 | 1350000 | 13751 | 0
2021022704 | 7 | 0.52181 | 78271.5 | 0.85213 | 0 | 0.06034 | 754.25 | 0 | 0 | 64000 | 754.25 | 0 | 13517.25 | -233.75 | 1350000 | 13517.25 | 0
2021022705 | 7 | 0.52358 | 78537 | 0.83729 | 0 | 0.03977 | 497.125 | 0 | 0 | 64000 | 497.125 | 0 | 14039.875 | 522.625 | 1350000 | 14039.875 | 0
2021022706 | 7 | 0.53341 | 80011.5 | 0.8294 | 0 | 0.02739 | 342.375 | 0 | 0 | 64000 | 342.375 | 0 | 15669.125 | 1629.25 | 1350000 | 15669.125 | 0
2021022707 | 7 | 0.55144 | 82716 | 0.69725 | 0 | 0.02143 | 267.875 | 0 | 0 | 64000 | 267.875 | 0 | 18448.125 | 2779 | 1350000 | 18448.125 | 0
2021022708 | 7 | 0.56947 | 85420.5 | 0.56622 | 0 | 0.01912 | 239 | 0.04506 | 3604.8 | 64000 | 239 | 3604.8 | 17576.7 | -871.425 | 1350000 | 17576.7 | 0
2021022709 | 7 | 0.58858 | 88287 | 0.52329 | 0 | 0.01845 | 230.625 | 0.14025 | 11220 | 64000 | 230.625 | 11220 | 12836.375 | -4740.325 | 1350000 | 12836.375 | 0
2021022710 | 7 | 0.60003 | 90004.5 | 0.63837 | 0 | 0.01899 | 237.375 | 0.2005 | 16040 | 64000 | 237.375 | 16040 | 9727.125 | -3109.25 | 1350000 | 9727.125 | 0
2021022711 | 7 | 0.59835 | 89752.5 | 0.68261 | 0 | 0.02528 | 316 | 0.21186 | 16948.8 | 64000 | 316 | 16948.8 | 8487.7 | -1239.425 | 1350000 | 8487.7 | 0
2021022712 | 7 | 0.5868 | 88020 | 0.71913 | 0 | 0.02096 | 262 | 0.26107 | 20885.6 | 64000 | 262 | 20885.6 | 2872.4 | -5615.3 | 1350000 | 2872.4 | 0
2021022713 | 7 | 0.57188 | 85782 | 0.73668 | 0 | 0.01822 | 227.75 | 0.30362 | 24289.6 | 64000 | 227.75 | 21554.25 | 0 | -2872.4 | 1350000 | 0 | 0
2021022714 | 7 | 0.55362 | 83043 | 0.74868 | 0 | 0.02419 | 302.375 | 0.30791 | 24632.8 | 64000 | 302.375 | 18740.625 | 0 | 0 | 1350000 | 0 | 0
2021022715 | 7 | 0.53713 | 80569.5 | 0.76341 | 0 | 0.03245 | 405.625 | 0.26586 | 21268.8 | 64000 | 405.625 | 16163.875 | 0 | 0 | 1350000 | 0 | 0
2021022716 | 7 | 0.5275 | 79125 | 0.72201 | 0 | 0.03677 | 459.625 | 0.164 | 13120 | 64000 | 459.625 | 13120 | 1545.375 | 1545.375 | 1350000 | 1545.375 | 0
2021022717 | 7 | 0.53135 | 79702.5 | 0.77181 | 0 | 0.03669 | 458.625 | 0.05713 | 4570.4 | 64000 | 458.625 | 4570.4 | 10673.475 | 9128.1 | 1350000 | 10673.475 | 0
2021022718 | 7 | 0.54892 | 82338 | 0.7172 | 0 | 0.03443 | 430.375 | 0.00156 | 124.8 | 64000 | 430.375 | 124.8 | 17782.825 | 7109.35 | 1350000 | 17782.825 | 0
2021022719 | 7 | 0.57652 | 86478 | 0.68054 | 0 | 0.03174 | 396.75 | 0 | 0 | 64000 | 396.75 | 0 | 22081.25 | 4298.425 | 1350000 | 22081.25 | 0
2021022720 | 7 | 0.58238 | 87357 | 0.63392 | 0 | 0.03075 | 384.375 | 0 | 0 | 64000 | 384.375 | 0 | 22972.625 | 891.375 | 1350000 | 22972.625 | 0
2021022721 | 7 | 0.57495 | 86242.5 | 0.55876 | 0 | 0.028 | 350 | 0 | 0 | 64000 | 350 | 0 | 21892.5 | -1080.125 | 1350000 | 21892.5 | 0
2021022722 | 7 | 0.56235 | 84352.5 | 0.46347 | 0 | 0.02757 | 344.625 | 0 | 0 | 64000 | 344.625 | 0 | 20007.875 | -1884.625 | 1350000 | 20007.875 | 0
2021022723 | 7 | 0.5431 | 81465 | 0.35305 | 0 | 0.03089 | 386.125 | 0 | 0 | 64000 | 386.125 | 0 | 17078.875 | -2929 | 1350000 | 17078.875 | 0
2021022724 | 7 | 0.52183 | 78274.5 | 0.20975 | 0 | 0.0333 | 416.25 | 0 | 0 | 64000 | 416.25 | 0 | 13858.25 | -3220.625 | 1350000 | 13858.25 | 0
2021022801 | 1 | 0.50302 | 75453 | 0.18997 | 0 | 0.02544 | 318 | 0 | 0 | 64000 | 318 | 0 | 11135 | -2723.25 | 1350000 | 11135 | 0
2021022802 | 1 | 0.49072 | 73608 | 0.17453 | 0 | 0.02127 | 265.875 | 0 | 0 | 64000 | 265.875 | 0 | 9342.125 | -1792.875 | 1350000 | 9342.125 | 0
2021022803 | 1 | 0.48412 | 72618 | 0.31058 | 0 | 0.02509 | 313.625 | 0 | 0 | 64000 | 313.625 | 0 | 8304.375 | -1037.75 | 1350000 | 8304.375 | 0
2021022804 | 1 | 0.47967 | 71950.5 | 0.49808 | 0 | 0.02785 | 348.125 | 0 | 0 | 64000 | 348.125 | 0 | 7602.375 | -702 | 1350000 | 7602.375 | 0
2021022805 | 1 | 0.4819 | 72285 | 0.62686 | 0 | 0.03121 | 390.125 | 0 | 0 | 64000 | 390.125 | 0 | 7894.875 | 292.5 | 1350000 | 7894.875 | 0
2021022806 | 1 | 0.4893 | 73395 | 0.70789 | 0 | 0.02575 | 321.875 | 0 | 0 | 64000 | 321.875 | 0 | 9073.125 | 1178.25 | 1350000 | 9073.125 | 0
2021022807 | 1 | 0.50155 | 75232.5 | 0.78197 | 0 | 0.01918 | 239.75 | 0 | 0 | 64000 | 239.75 | 0 | 10992.75 | 1919.625 | 1350000 | 10992.75 | 0
2021022808 | 1 | 0.51576 | 77364 | 0.81506 | 0 | 0.02017 | 252.125 | 0.08343 | 6674.4 | 64000 | 252.125 | 6674.4 | 6437.475 | -4555.275 | 1350000 | 6437.475 | 0
2021022809 | 1 | 0.53577 | 80365.5 | 0.8118 | 0 | 0.02801 | 350.125 | 0.4041 | 32328 | 64000 | 350.125 | 16015.375 | 0 | -6437.475 | 1350000 | 0 | 0
2021022810 | 1 | 0.55406 | 83109 | 0.82856 | 0 | 0.03437 | 429.625 | 0.59253 | 47402.4 | 64000 | 429.625 | 18679.375 | 0 | 0 | 1350000 | 0 | 0
2021022811 | 1 | 0.56571 | 84856.5 | 0.88551 | 0 | 0.03663 | 457.875 | 0.63354 | 50683.2 | 64000 | 457.875 | 20398.625 | 0 | 0 | 1350000 | 0 | 0
2021022812 | 1 | 0.56885 | 85327.5 | 0.91504 | 0 | 0.04238 | 529.75 | 0.64136 | 51308.8 | 64000 | 529.75 | 20797.75 | 0 | 0 | 1350000 | 0 | 0
2021022813 | 1 | 0.56964 | 85446 | 0.90198 | 0 | 0.04968 | 621 | 0.62347 | 49877.6 | 64000 | 621 | 20825 | 0 | 0 | 1350000 | 0 | 0
2021022814 | 1 | 0.56719 | 85078.5 | 0.8964 | 0 | 0.06027 | 753.375 | 0.65389 | 52311.2 | 64000 | 753.375 | 20325.125 | 0 | 0 | 1350000 | 0 | 0
2021022815 | 1 | 0.56263 | 84394.5 | 0.95491 | 0 | 0.05207 | 650.875 | 0.62782 | 50225.6 | 64000 | 650.875 | 19743.625 | 0 | 0 | 1350000 | 0 | 0
2021022816 | 1 | 0.56187 | 84280.5 | 0.96215 | 0 | 0.04273 | 534.125 | 0.4684 | 37472 | 64000 | 534.125 | 19746.375 | 0 | 0 | 1350000 | 0 | 0
2021022817 | 1 | 0.57033 | 85549.5 | 0.94493 | 0 | 0.05602 | 700.25 | 0.13862 | 11089.6 | 64000 | 700.25 | 11089.6 | 9759.65 | 9759.65 | 1350000 | 9759.65 | 0
2021022818 | 1 | 0.58545 | 87817.5 | 0.93525 | 0 | 0.07241 | 905.125 | 0.00376 | 300.8 | 64000 | 905.125 | 300.8 | 22611.575 | 12851.925 | 1350000 | 22611.575 | 0
2021022819 | 1 | 0.60037 | 90055.5 | 0.90587 | 0 | 0.08557 | 1069.625 | 0 | 0 | 64000 | 1069.625 | 0 | 24985.875 | 2374.3 | 1350000 | 24985.875 | 0
2021022820 | 1 | 0.59922 | 89883 | 0.89086 | 0 | 0.09802 | 1225.25 | 0 | 0 | 64000 | 1225.25 | 0 | 24657.75 | -328.125 | 1350000 | 24657.75 | 0
2021022821 | 1 | 0.58367 | 87550.5 | 0.88171 | 0 | 0.10605 | 1325.625 | 0 | 0 | 64000 | 1325.625 | 0 | 22224.875 | -2432.875 | 1350000 | 22224.875 | 0
2021022822 | 1 | 0.56329 | 84493.5 | 0.87904 | 0 | 0.12234 | 1529.25 | 0 | 0 | 64000 | 1529.25 | 0 | 18964.25 | -3260.625 | 1350000 | 18964.25 | 0
2021022823 | 1 | 0.53758 | 80637 | 0.88561 | 0 | 0.12216 | 1527 | 0 | 0 | 64000 | 1527 | 0 | 15110 | -3854.25 | 1350000 | 15110 | 0
2021022824 | 1 | 0.5139 | 77085 | 0.859 | 0 | 0.12818 | 1602.25 | 0 | 0 | 64000 | 1602.25 | 0 | 11482.75 | -3627.25 | 1350000 | 11482.75 | 0
2021030101 | 2 | 0.49613 | 74419.5 | 0.82128 | 0 | 0.13644 | 1705.5 | 0 | 0 | 64000 | 1705.5 | 0 | 8714 | -2768.75 | 1350000 | 8714 | 0
2021030102 | 2 | 0.48628 | 72942 | 0.77399 | 0 | 0.13863 | 1732.875 | 0 | 0 | 64000 | 1732.875 | 0 | 7209.125 | -1504.875 | 1350000 | 7209.125 | 0
2021030103 | 2 | 0.48342 | 72513 | 0.78301 | 0 | 0.15749 | 1968.625 | 0 | 0 | 64000 | 1968.625 | 0 | 6544.375 | -664.75 | 1350000 | 6544.375 | 0
2021030104 | 2 | 0.48566 | 72849 | 0.79307 | 0 | 0.19604 | 2450.5 | 0 | 0 | 64000 | 2450.5 | 0 | 6398.5 | -145.875 | 1350000 | 6398.5 | 0
2021030105 | 2 | 0.49863 | 74794.5 | 0.83986 | 0 | 0.21805 | 2725.625 | 0 | 0 | 64000 | 2725.625 | 0 | 8068.875 | 1670.375 | 1350000 | 8068.875 | 0
2021030106 | 2 | 0.5292 | 79380 | 0.88743 | 0 | 0.2282 | 2852.5 | 0 | 0 | 64000 | 2852.5 | 0 | 12527.5 | 4458.625 | 1350000 | 12527.5 | 0
2021030107 | 2 | 0.5757 | 86355 | 0.88732 | 0 | 0.2526 | 3157.5 | 0 | 0 | 64000 | 3157.5 | 0 | 19197.5 | 6670 | 1350000 | 19197.5 | 0
2021030108 | 2 | 0.61025 | 91537.5 | 0.84565 | 0 | 0.28663 | 3582.875 | 0.02777 | 2221.6 | 64000 | 3582.875 | 2221.6 | 21733.025 | 2535.525 | 1350000 | 21733.025 | 0
2021030109 | 2 | 0.62766 | 94149 | 0.90433 | 0 | 0.30002 | 3750.25 | 0.07542 | 6033.6 | 64000 | 3750.25 | 6033.6 | 20365.15 | -1367.875 | 1350000 | 20365.15 | 0
2021030110 | 2 | 0.63439 | 95158.5 | 0.95474 | 0 | 0.2995 | 3743.75 | 0.12152 | 9721.6 | 64000 | 3743.75 | 9721.6 | 17693.15 | -2672 | 1350000 | 17693.15 | 0
2021030111 | 2 | 0.63657 | 95485.5 | 0.92446 | 0 | 0.27337 | 3417.125 | 0.21927 | 17541.6 | 64000 | 3417.125 | 17541.6 | 10526.775 | -7166.375 | 1350000 | 10526.775 | 0
2021030112 | 2 | 0.63536 | 95304 | 0.91695 | 0 | 0.26197 | 3274.625 | 0.27627 | 22101.6 | 64000 | 3274.625 | 22101.6 | 5927.775 | -4599 | 1350000 | 5927.775 | 0
2021030113 | 2 | 0.62935 | 94402.5 | 0.96031 | 0 | 0.19634 | 2454.25 | 0.30753 | 24602.4 | 64000 | 2454.25 | 24602.4 | 3345.85 | -2581.925 | 1350000 | 3345.85 | 0
2021030114 | 2 | 0.62356 | 93534 | 0.98116 | 0 | 0.1431 | 1788.75 | 0.2943 | 23544 | 64000 | 1788.75 | 23544 | 4201.25 | 855.4 | 1350000 | 4201.25 | 0
2021030115 | 2 | 0.61695 | 92542.5 | 0.99019 | 0 | 0.12286 | 1535.75 | 0.29916 | 23932.8 | 64000 | 1535.75 | 23932.8 | 3073.95 | -1127.3 | 1350000 | 3073.95 | 0
2021030116 | 2 | 0.61436 | 92154 | 0.99457 | 0 | 0.18581 | 2322.625 | 0.26184 | 20947.2 | 64000 | 2322.625 | 20947.2 | 4884.175 | 1810.225 | 1350000 | 4884.175 | 0
2021030117 | 2 | 0.61985 | 92977.5 | 0.99477 | 0 | 0.23862 | 2982.75 | 0.10944 | 8755.2 | 64000 | 2982.75 | 8755.2 | 17239.55 | 12355.375 | 1350000 | 17239.55 | 0
2021030118 | 2 | 0.6372 | 95580 | 0.98677 | 0 | 0.24968 | 3121 | 0.00251 | 200.8 | 64000 | 3121 | 200.8 | 28258.2 | 11018.65 | 1347208.05 | 28258.2 | 0
2021030119 | 2 | 0.66704 | 100056 | 0.9929 | 0 | 0.26354 | 3294.25 | 0 | 0 | 64000 | 3294.25 | 0 | 32761.75 | 4503.55 | 1339912.55 | 32761.75 | 0
2021030120 | 2 | 0.67539 | 101308.5 | 0.99565 | 0 | 0.29415 | 3676.875 | 0 | 0 | 64000 | 3676.875 | 0 | 33631.625 | 869.875 | 1331747.175 | 33631.625 | 0
2021030121 | 2 | 0.66677 | 100015.5 | 0.99343 | 0 | 0.30423 | 3802.875 | 0 | 0 | 64000 | 3802.875 | 0 | 32212.625 | -1419 | 1325000.8 | 32212.625 | 0
2021030122 | 2 | 0.64781 | 97171.5 | 0.99693 | 0 | 0.28533 | 3566.625 | 0 | 0 | 64000 | 3566.625 | 0 | 29604.875 | -2607.75 | 1320862.175 | 29604.875 | 0
2021030123 | 2 | 0.62233 | 93349.5 | 0.9959 | 0 | 0.29507 | 3688.375 | 0 | 0 | 64000 | 3688.375 | 0 | 25661.125 | -3943.75 | 1320667.3 | 25661.125 | 0
2021030124 | 2 | 0.59974 | 89961 | 0.99444 | 0 | 0.30503 | 3812.875 | 0 | 0 | 64000 | 3812.875 | 0 | 22148.125 | -3513 | 1323985.425 | 22148.125 | 0
2021030201 | 3 | 0.58398 | 87597 | 0.99652 | 0 | 0.30946 | 3868.25 | 0 | 0 | 64000 | 3868.25 | 0 | 19728.75 | -2419.375 | 1329722.925 | 19728.75 | 0
2021030202 | 3 | 0.57781 | 86671.5 | 0.99791 | 0 | 0.29832 | 3729 | 0 | 0 | 64000 | 3729 | 0 | 18942.5 | -786.25 | 1336246.675 | 18942.5 | 0
2021030203 | 3 | 0.57914 | 86871 | 0.99787 | 0 | 0.26538 | 3317.25 | 0 | 0 | 64000 | 3317.25 | 0 | 19553.75 | 611.25 | 1342159.175 | 19553.75 | 0
2021030204 | 3 | 0.58589 | 87883.5 | 0.99331 | 0 | 0.26588 | 3323.5 | 0 | 0 | 64000 | 3323.5 | 0 | 20560 | 1006.25 | 1347065.425 | 20560 | 0
2021030205 | 3 | 0.60449 | 90673.5 | 0.99106 | 0 | 0.23503 | 2937.875 | 0 | 0 | 64000 | 2937.875 | 0 | 23735.625 | 3175.625 | 1348796.05 | 23735.625 | 0
2021030206 | 3 | 0.64047 | 96070.5 | 0.98608 | 0 | 0.20713 | 2589.125 | 0 | 0 | 64000 | 2589.125 | 0 | 29481.375 | 5745.75 | 1344780.925 | 29481.375 | 0
2021030207 | 3 | 0.6916 | 103740 | 0.98066 | 0 | 0.21507 | 2688.375 | 0 | 0 | 64000 | 2688.375 | 0 | 37051.625 | 7570.25 | 1333195.55 | 37051.625 | 0
2021030208 | 3 | 0.71588 | 107382 | 0.96397 | 0 | 0.25029 | 3128.625 | 0.08939 | 7151.2 | 64000 | 3128.625 | 7151.2 | 33102.175 | -3949.45 | 1325559.625 | 33102.175 | 0
2021030209 | 3 | 0.70581 | 105871.5 | 0.89242 | 0 | 0.2808 | 3510 | 0.37355 | 29884 | 64000 | 3510 | 29884 | 8477.5 | -24624.675 | 1342548.375 | 8477.5 | 0
2021030210 | 3 | 0.68478 | 102717 | 0.83031 | 0 | 0.28383 | 3547.875 | 0.52221 | 41776.8 | 64000 | 3547.875 | 35169.125 | 0 | -8477.5 | 1350000 | 0 | 0
2021030211 | 3 | 0.6685 | 100275 | 0.69458 | 0 | 0.27397 | 3424.625 | 0.5514 | 44112 | 64000 | 3424.625 | 32850.375 | 0 | 0 | 1350000 | 0 | 0
2021030212 | 3 | 0.65285 | 97927.5 | 0.57746 | 0 | 0.23921 | 2990.125 | 0.58138 | 46510.4 | 64000 | 2990.125 | 30937.375 | 0 | 0 | 1350000 | 0 | 0
2021030213 | 3 | 0.63885 | 95827.5 | 0.46928 | 0 | 0.19688 | 2461 | 0.62575 | 50060 | 64000 | 2461 | 29366.5 | 0 | 0 | 1350000 | 0 | 0
2021030214 | 3 | 0.62729 | 94093.5 | 0.3964 | 0 | 0.15966 | 1995.75 | 0.65801 | 52640.8 | 64000 | 1995.75 | 28097.75 | 0 | 0 | 1350000 | 0 | 0
2021030215 | 3 | 0.61369 | 92053.5 | 0.34667 | 0 | 0.15341 | 1917.625 | 0.64954 | 51963.2 | 64000 | 1917.625 | 26135.875 | 0 | 0 | 1350000 | 0 | 0
2021030216 | 3 | 0.60677 | 91015.5 | 0.32361 | 0 | 0.1978 | 2472.5 | 0.5392 | 43136 | 64000 | 2472.5 | 24543 | 0 | 0 | 1350000 | 0 | 0
2021030217 | 3 | 0.61432 | 92148 | 0.30455 | 0 | 0.28135 | 3516.875 | 0.19568 | 15654.4 | 64000 | 3516.875 | 15654.4 | 8976.725 | 8976.725 | 1350000 | 8976.725 | 0
2021030218 | 3 | 0.63703 | 95554.5 | 0.29453 | 0 | 0.30322 | 3790.25 | 0.0056 | 448 | 64000 | 3790.25 | 448 | 27316.25 | 18339.525 | 1348150 | 27316.25 | 0
2021030219 | 3 | 0.67319 | 100978.5 | 0.29921 | 0 | 0.33783 | 4222.875 | 0 | 0 | 64000 | 4222.875 | 0 | 32755.625 | 5439.375 | 1340860.625 | 32755.625 | 0
2021030220 | 3 | 0.68783 | 103174.5 | 0.42751 | 0 | 0.3636 | 4545 | 0 | 0 | 64000 | 4545 | 0 | 34629.5 | 1873.875 | 1331697.375 | 34629.5 | 0
2021030221 | 3 | 0.68407 | 102610.5 | 0.6011 | 0 | 0.40503 | 5062.875 | 0 | 0 | 64000 | 5062.875 | 0 | 33547.625 | -1081.875 | 1323616 | 33547.625 | 0
2021030222 | 3 | 0.66651 | 99976.5 | 0.77622 | 0 | 0.42325 | 5290.625 | 0 | 0 | 64000 | 5290.625 | 0 | 30685.875 | -2861.75 | 1318396.375 | 30685.875 | 0
2021030223 | 3 | 0.63942 | 95913 | 0.8371 | 0 | 0.46185 | 5773.125 | 0 | 0 | 64000 | 5773.125 | 0 | 26139.875 | -4546 | 1317722.75 | 26139.875 | 0
2021030224 | 3 | 0.61405 | 92107.5 | 0.83052 | 0 | 0.48781 | 6097.625 | 0 | 0 | 64000 | 6097.625 | 0 | 22009.875 | -4130 | 1321179.125 | 22009.875 | 0
2021030301 | 4 | 0.59682 | 89523 | 0.86219 | 0 | 0.49917 | 6239.625 | 0 | 0 | 64000 | 6239.625 | 0 | 19283.375 | -2726.5 | 1327362 | 19283.375 | 0
2021030302 | 4 | 0.58819 | 88228.5 | 0.94678 | 0 | 0.51293 | 6411.625 | 0 | 0 | 64000 | 6411.625 | 0 | 17816.875 | -1466.5 | 1335011.375 | 17816.875 | 0
2021030303 | 4 | 0.58635 | 87952.5 | 0.97071 | 0 | 0.53353 | 6669.125 | 0 | 0 | 64000 | 6669.125 | 0 | 17283.375 | -533.5 | 1343194.25 | 17283.375 | 0
2021030304 | 4 | 0.59058 | 88587 | 0.97031 | 0 | 0.57584 | 7198 | 0 | 0 | 64000 | 7198 | 0 | 17389 | 105.625 | 1350000 | 17389 | 0
2021030305 | 4 | 0.60583 | 90874.5 | 0.96371 | 0 | 0.58847 | 7355.875 | 0 | 0 | 64000 | 7355.875 | 0 | 19518.625 | 2129.625 | 1350000 | 19518.625 | 0
2021030306 | 4 | 0.63758 | 95637 | 0.9625 | 0 | 0.57875 | 7234.375 | 0 | 0 | 64000 | 7234.375 | 0 | 24402.625 | 4884 | 1350000 | 24402.625 | 0
2021030307 | 4 | 0.68436 | 102654 | 0.95089 | 0 | 0.59139 | 7392.375 | 0 | 0 | 64000 | 7392.375 | 0 | 31261.625 | 6859 | 1344204.625 | 31261.625 | 0
2021030308 | 4 | 0.70133 | 105199.5 | 0.92217 | 0 | 0.61376 | 7672 | 0.07019 | 5615.2 | 64000 | 7672 | 5615.2 | 27912.3 | -3349.325 | 1341758.575 | 27912.3 | 0
2021030309 | 4 | 0.67991 | 101986.5 | 0.82 | 0 | 0.59603 | 7450.375 | 0.29773 | 23818.4 | 64000 | 7450.375 | 23818.4 | 6717.725 | -21194.575 | 1350000 | 6717.725 | 0
2021030310 | 4 | 0.64626 | 96939 | 0.72624 | 0 | 0.61497 | 7687.125 | 0.41907 | 33525.6 | 64000 | 7687.125 | 25251.875 | 0 | -6717.725 | 1350000 | 0 | 0
2021030311 | 4 | 0.62052 | 93078 | 0.64122 | 0 | 0.57991 | 7248.875 | 0.48684 | 38947.2 | 64000 | 7248.875 | 21829.125 | 0 | 0 | 1350000 | 0 | 0
2021030312 | 4 | 0.59996 | 89994 | 0.57979 | 0 | 0.53882 | 6735.25 | 0.51479 | 41183.2 | 64000 | 6735.25 | 19258.75 | 0 | 0 | 1350000 | 0 | 0
2021030313 | 4 | 0.58526 | 87789 | 0.55148 | 0 | 0.48744 | 6093 | 0.56589 | 45271.2 | 64000 | 6093 | 17696 | 0 | 0 | 1350000 | 0 | 0
2021030314 | 4 | 0.57361 | 86041.5 | 0.55705 | 0 | 0.44589 | 5573.625 | 0.61492 | 49193.6 | 64000 | 5573.625 | 16467.875 | 0 | 0 | 1350000 | 0 | 0
2021030315 | 4 | 0.56197 | 84295.5 | 0.59583 | 0 | 0.3775 | 4718.75 | 0.60925 | 48740 | 64000 | 4718.75 | 15576.75 | 0 | 0 | 1350000 | 0 | 0
2021030316 | 4 | 0.55618 | 83427 | 0.62396 | 0 | 0.37018 | 4627.25 | 0.49411 | 39528.8 | 64000 | 4627.25 | 14799.75 | 0 | 0 | 1350000 | 0 | 0
2021030317 | 4 | 0.56009 | 84013.5 | 0.64711 | 0 | 0.40236 | 5029.5 | 0.17208 | 13766.4 | 64000 | 5029.5 | 13766.4 | 1217.6 | 1217.6 | 1350000 | 1217.6 | 0
2021030318 | 4 | 0.57911 | 86866.5 | 0.58411 | 0 | 0.38018 | 4752.25 | 0.00578 | 462.4 | 64000 | 4752.25 | 462.4 | 17651.85 | 16434.25 | 1350000 | 17651.85 | 0
2021030319 | 4 | 0.60854 | 91281 | 0.54812 | 0 | 0.3422 | 4277.5 | 0 | 0 | 64000 | 4277.5 | 0 | 23003.5 | 5351.65 | 1350000 | 23003.5 | 0
2021030320 | 4 | 0.62278 | 93417 | 0.60543 | 0 | 0.30691 | 3836.375 | 0 | 0 | 64000 | 3836.375 | 0 | 25580.625 | 2577.125 | 1349885.625 | 25580.625 | 0
2021030321 | 4 | 0.61542 | 92313 | 0.66896 | 0 | 0.25551 | 3193.875 | 0 | 0 | 64000 | 3193.875 | 0 | 25119.125 | -461.5 | 1350000 | 25119.125 | 0
2021030322 | 4 | 0.60007 | 90010.5 | 0.69382 | 0 | 0.20632 | 2579 | 0 | 0 | 64000 | 2579 | 0 | 23431.5 | -1687.625 | 1350000 | 23431.5 | 0
2021030323 | 4 | 0.5748 | 86220 | 0.70097 | 0 | 0.15032 | 1879 | 0 | 0 | 64000 | 1879 | 0 | 20341 | -3090.5 | 1350000 | 20341 | 0
2021030324 | 4 | 0.55099 | 82648.5 | 0.59464 | 0 | 0.12561 | 1570.125 | 0 | 0 | 64000 | 1570.125 | 0 | 17078.375 | -3262.625 | 1350000 | 17078.375 | 0
2021030401 | 5 | 0.53662 | 80493 | 0.51803 | 0 | 0.10789 | 1348.625 | 0 | 0 | 64000 | 1348.625 | 0 | 15144.375 | -1934 | 1350000 | 15144.375 | 0
2021030402 | 5 | 0.52837 | 79255.5 | 0.53014 | 0 | 0.12026 | 1503.25 | 0 | 0 | 64000 | 1503.25 | 0 | 13752.25 | -1392.125 | 1350000 | 13752.25 | 0
2021030403 | 5 | 0.5268 | 79020 | 0.5209 | 0 | 0.12516 | 1564.5 | 0 | 0 | 64000 | 1564.5 | 0 | 13455.5 | -296.75 | 1350000 | 13455.5 | 0
2021030404 | 5 | 0.53049 | 79573.5 | 0.54311 | 0 | 0.11483 | 1435.375 | 0 | 0 | 64000 | 1435.375 | 0 | 14138.125 | 682.625 | 1350000 | 14138.125 | 0
2021030405 | 5 | 0.54612 | 81918 | 0.59592 | 0 | 0.11062 | 1382.75 | 0 | 0 | 64000 | 1382.75 | 0 | 16535.25 | 2397.125 | 1350000 | 16535.25 | 0
2021030406 | 5 | 0.57903 | 86854.5 | 0.65235 | 0 | 0.11856 | 1482 | 0 | 0 | 64000 | 1482 | 0 | 21372.5 | 4837.25 | 1350000 | 21372.5 | 0
2021030407 | 5 | 0.62607 | 93910.5 | 0.73429 | 0 | 0.13254 | 1656.75 | 0 | 0 | 64000 | 1656.75 | 0 | 28253.75 | 6881.25 | 1347212.5 | 28253.75 | 0
2021030408 | 5 | 0.6492 | 97380 | 0.79378 | 0 | 0.1721 | 2151.25 | 0.07125 | 5700 | 64000 | 2151.25 | 5700 | 25528.75 | -2725 | 1347150 | 25528.75 | 0
2021030409 | 5 | 0.6413 | 96195 | 0.84536 | 0 | 0.22158 | 2769.75 | 0.26462 | 21169.6 | 64000 | 2769.75 | 21169.6 | 8255.65 | -17273.1 | 1350000 | 8255.65 | 0
2021030410 | 5 | 0.62637 | 93955.5 | 0.89216 | 0 | 0.21464 | 2683 | 0.25997 | 20797.6 | 64000 | 2683 | 20797.6 | 6474.9 | -1780.75 | 1350000 | 6474.9 | 0
2021030411 | 5 | 0.61624 | 92436 | 0.91653 | 0 | 0.21835 | 2729.375 | 0.28321 | 22656.8 | 64000 | 2729.375 | 22656.8 | 3049.825 | -3425.075 | 1350000 | 3049.825 | 0
2021030412 | 5 | 0.60753 | 91129.5 | 0.94241 | 0 | 0.23396 | 2924.5 | 0.34994 | 27995.2 | 64000 | 2924.5 | 24205 | 0 | -3049.825 | 1350000 | 0 | 0
2021030413 | 5 | 0.59967 | 89950.5 | 0.94967 | 0 | 0.25579 | 3197.375 | 0.40347 | 32277.6 | 64000 | 3197.375 | 22753.125 | 0 | 0 | 1350000 | 0 | 0
2021030414 | 5 | 0.59406 | 89109 | 0.96932 | 0 | 0.29486 | 3685.75 | 0.43657 | 34925.6 | 64000 | 3685.75 | 21423.25 | 0 | 0 | 1350000 | 0 | 0
2021030415 | 5 | 0.59154 | 88731 | 0.98889 | 0 | 0.35176 | 4397 | 0.42569 | 34055.2 | 64000 | 4397 | 20334 | 0 | 0 | 1350000 | 0 | 0
2021030416 | 5 | 0.59178 | 88767 | 0.98997 | 0 | 0.41264 | 5158 | 0.38603 | 30882.4 | 64000 | 5158 | 19609 | 0 | 0 | 1350000 | 0 | 0
2021030417 | 5 | 0.60256 | 90384 | 0.99135 | 0 | 0.43643 | 5455.375 | 0.1511 | 12088 | 64000 | 5455.375 | 12088 | 8840.625 | 8840.625 | 1350000 | 8840.625 | 0
2021030418 | 5 | 0.62655 | 93982.5 | 0.98662 | 0 | 0.46418 | 5802.25 | 0.00511 | 408.8 | 64000 | 5802.25 | 408.8 | 23771.45 | 14930.825 | 1350000 | 23771.45 | 0
2021030419 | 5 | 0.65834 | 98751 | 0.98266 | 0 | 0.49461 | 6182.625 | 0 | 0 | 64000 | 6182.625 | 0 | 28568.375 | 4796.925 | 1346897.875 | 28568.375 | 0
2021030420 | 5 | 0.67082 | 100623 | 0.98811 | 0 | 0.50405 | 6300.625 | 0 | 0 | 64000 | 6300.625 | 0 | 30322.375 | 1754 | 1342041.75 | 30322.375 | 0
2021030421 | 5 | 0.66502 | 99753 | 0.99069 | 0 | 0.5124 | 6405 | 0 | 0 | 64000 | 6405 | 0 | 29348 | -974.375 | 1338160 | 29348 | 0
2021030422 | 5 | 0.64912 | 97368 | 0.99455 | 0 | 0.51937 | 6492.125 | 0 | 0 | 64000 | 6492.125 | 0 | 26875.875 | -2472.125 | 1336750.375 | 26875.875 | 0
2021030423 | 5 | 0.62469 | 93703.5 | 0.99485 | 0 | 0.52246 | 6530.75 | 0 | 0 | 64000 | 6530.75 | 0 | 23172.75 | -3703.125 | 1339043.875 | 23172.75 | 0
2021030424 | 5 | 0.60217 | 90325.5 | 0.99549 | 0 | 0.51979 | 6497.375 | 0 | 0 | 64000 | 6497.375 | 0 | 19828.125 | -3344.625 | 1344682 | 19828.125 | 0
2021030501 | 6 | 0.58887 | 88330.5 | 0.99393 | 0 | 0.53402 | 6675.25 | 0 | 0 | 64000 | 6675.25 | 0 | 17655.25 | -2172.875 | 1350000 | 17655.25 | 0
2021030502 | 6 | 0.58411 | 87616.5 | 0.98814 | 0 | 0.56501 | 7062.625 | 0 | 0 | 64000 | 7062.625 | 0 | 16553.875 | -1101.375 | 1350000 | 16553.875 | 0
2021030503 | 6 | 0.58535 | 87802.5 | 0.99314 | 0 | 0.54219 | 6777.375 | 0 | 0 | 64000 | 6777.375 | 0 | 17025.125 | 471.25 | 1350000 | 17025.125 | 0
2021030504 | 6 | 0.59181 | 88771.5 | 0.9952 | 0 | 0.55033 | 6879.125 | 0 | 0 | 64000 | 6879.125 | 0 | 17892.375 | 867.25 | 1350000 | 17892.375 | 0
2021030505 | 6 | 0.61092 | 91638 | 0.99434 | 0 | 0.55088 | 6886 | 0 | 0 | 64000 | 6886 | 0 | 20752 | 2859.625 | 1350000 | 20752 | 0
2021030506 | 6 | 0.64531 | 96796.5 | 0.99206 | 0 | 0.54638 | 6829.75 | 0 | 0 | 64000 | 6829.75 | 0 | 25966.75 | 5214.75 | 1349499.5 | 25966.75 | 0
2021030507 | 6 | 0.69253 | 103879.5 | 0.99187 | 0 | 0.51696 | 6462 | 0 | 0 | 64000 | 6462 | 0 | 33417.5 | 7450.75 | 1341548.25 | 33417.5 | 0
2021030508 | 6 | 0.71367 | 107050.5 | 0.99156 | 0 | 0.51631 | 6453.875 | 0.05599 | 4479.2 | 64000 | 6453.875 | 4479.2 | 32117.425 | -1300.075 | 1334897.075 | 32117.425 | 0
2021030509 | 6 | 0.70297 | 105445.5 | 0.98401 | 0 | 0.50497 | 6312.125 | 0.18402 | 14721.6 | 64000 | 6312.125 | 14721.6 | 20411.775 | -11705.65 | 1339951.55 | 20411.775 | 0
2021030510 | 6 | 0.68295 | 102442.5 | 0.96664 | 0 | 0.48762 | 6095.25 | 0.21724 | 17379.2 | 64000 | 6095.25 | 17379.2 | 14968.05 | -5443.725 | 1350000 | 14968.05 | 0
2021030511 | 6 | 0.66618 | 99927 | 0.96542 | 0 | 0.44708 | 5588.5 | 0.25108 | 20086.4 | 64000 | 5588.5 | 20086.4 | 10252.1 | -4715.95 | 1350000 | 10252.1 | 0
2021030512 | 6 | 0.65053 | 97579.5 | 0.96932 | 0 | 0.43826 | 5478.25 | 0.322 | 25760 | 64000 | 5478.25 | 25760 | 2341.25 | -7910.85 | 1350000 | 2341.25 | 0
2021030513 | 6 | 0.63632 | 95448 | 0.96859 | 0 | 0.41793 | 5224.125 | 0.31844 | 25475.2 | 64000 | 5224.125 | 25475.2 | 748.675 | -1592.575 | 1350000 | 748.675 | 0
2021030514 | 6 | 0.62188 | 93282 | 0.98536 | 0 | 0.42605 | 5325.625 | 0.26241 | 20992.8 | 64000 | 5325.625 | 20992.8 | 2963.575 | 2214.9 | 1350000 | 2963.575 | 0
2021030515 | 6 | 0.60918 | 91377 | 0.99218 | 0 | 0.39569 | 4946.125 | 0.19699 | 15759.2 | 64000 | 4946.125 | 15759.2 | 6671.675 | 3708.1 | 1350000 | 6671.675 | 0
2021030516 | 6 | 0.60039 | 90058.5 | 0.99646 | 0 | 0.39775 | 4971.875 | 0.07811 | 6248.8 | 64000 | 4971.875 | 6248.8 | 14837.825 | 8166.15 | 1350000 | 14837.825 | 0
2021030517 | 6 | 0.60808 | 91212 | 0.99598 | 0 | 0.39759 | 4969.875 | 0.02345 | 1876 | 64000 | 4969.875 | 1876 | 20366.125 | 5528.3 | 1350000 | 20366.125 | 0
2021030518 | 6 | 0.63049 | 94573.5 | 0.9887 | 0 | 0.38102 | 4762.75 | 0 | 0 | 64000 | 4762.75 | 0 | 25810.75 | 5444.625 | 1349655.5 | 25810.75 | 0
2021030519 | 6 | 0.66172 | 99258 | 0.98607 | 0 | 0.36075 | 4509.375 | 0 | 0 | 64000 | 4509.375 | 0 | 30748.625 | 4937.875 | 1344373.125 | 30748.625 | 0
2021030520 | 6 | 0.67167 | 100750.5 | 0.99365 | 0 | 0.35457 | 4432.125 | 0 | 0 | 64000 | 4432.125 | 0 | 32318.375 | 1569.75 | 1337521 | 32318.375 | 0
2021030521 | 6 | 0.66414 | 99621 | 0.99906 | 0 | 0.31607 | 3950.875 | 0 | 0 | 64000 | 3950.875 | 0 | 31670.125 | -648.25 | 1331317.125 | 31670.125 | 0
2021030522 | 6 | 0.64934 | 97401 | 0.99734 | 0 | 0.27378 | 3422.25 | 0 | 0 | 64000 | 3422.25 | 0 | 29978.75 | -1691.375 | 1326804.625 | 29978.75 | 0
2021030523 | 6 | 0.6271 | 94065 | 0.98124 | 0 | 0.23636 | 2954.5 | 0 | 0 | 64000 | 2954.5 | 0 | 27110.5 | -2868.25 | 1325160.375 | 27110.5 | 0
2021030524 | 6 | 0.60297 | 90445.5 | 0.9558 | 0 | 0.23306 | 2913.25 | 0 | 0 | 64000 | 2913.25 | 0 | 23532.25 | -3578.25 | 1327094.375 | 23532.25 | 0
2021030601 | 7 | 0.58514 | 87771 | 0.92572 | 0 | 0.2443 | 3053.75 | 0 | 0 | 64000 | 3053.75 | 0 | 20717.25 | -2815 | 1331843.375 | 20717.25 | 0
2021030602 | 7 | 0.57477 | 86215.5 | 0.87355 | 0 | 0.26586 | 3323.25 | 0 | 0 | 64000 | 3323.25 | 0 | 18892.25 | -1825 | 1338417.375 | 18892.25 | 0
2021030603 | 7 | 0.57091 | 85636.5 | 0.87244 | 0 | 0.27177 | 3397.125 | 0 | 0 | 64000 | 3397.125 | 0 | 18239.375 | -652.875 | 1345644.25 | 18239.375 | 0
2021030604 | 7 | 0.57199 | 85798.5 | 0.87237 | 0 | 0.27368 | 3421 | 0 | 0 | 64000 | 3421 | 0 | 18377.5 | 138.125 | 1350000 | 18377.5 | 0
2021030605 | 7 | 0.57845 | 86767.5 | 0.91959 | 0 | 0.2727 | 3408.75 | 0 | 0 | 64000 | 3408.75 | 0 | 19358.75 | 981.25 | 1350000 | 19358.75 | 0
2021030606 | 7 | 0.59368 | 89052 | 0.91363 | 0 | 0.28919 | 3614.875 | 0 | 0 | 64000 | 3614.875 | 0 | 21437.125 | 2078.375 | 1350000 | 21437.125 | 0
2021030607 | 7 | 0.61621 | 92431.5 | 0.87949 | 0 | 0.29302 | 3662.75 | 0 | 0 | 64000 | 3662.75 | 0 | 24768.75 | 3331.625 | 1350000 | 24768.75 | 0
2021030608 | 7 | 0.62618 | 93927 | 0.8172 | 0 | 0.30397 | 3799.625 | 0.0241 | 1928 | 64000 | 3799.625 | 1928 | 24199.375 | -569.375 | 1350000 | 24199.375 | 0
2021030609 | 7 | 0.62224 | 93336 | 0.81097 | 0 | 0.34264 | 4283 | 0.09931 | 7944.8 | 64000 | 4283 | 7944.8 | 17108.2 | -7091.175 | 1350000 | 17108.2 | 0
2021030610 | 7 | 0.61409 | 92113.5 | 0.8628 | 0 | 0.35362 | 4420.25 | 0.20173 | 16138.4 | 64000 | 4420.25 | 16138.4 | 7554.85 | -9553.35 | 1350000 | 7554.85 | 0
2021030611 | 7 | 0.60657 | 90985.5 | 0.88791 | 0 | 0.35027 | 4378.375 | 0.3044 | 24352 | 64000 | 4378.375 | 22607.125 | 0 | -7554.85 | 1350000 | 0 | 0
2021030612 | 7 | 0.59708 | 89562 | 0.87714 | 0 | 0.33411 | 4176.375 | 0.4284 | 34272 | 64000 | 4176.375 | 21385.625 | 0 | 0 | 1350000 | 0 | 0
2021030613 | 7 | 0.58447 | 87670.5 | 0.883 | 0 | 0.40003 | 5000.375 | 0.50395 | 40316 | 64000 | 5000.375 | 18670.125 | 0 | 0 | 1350000 | 0 | 0
2021030614 | 7 | 0.57144 | 85716 | 0.84918 | 0 | 0.45661 | 5707.625 | 0.4899 | 39192 | 64000 | 5707.625 | 16008.375 | 0 | 0 | 1350000 | 0 | 0
2021030615 | 7 | 0.56112 | 84168 | 0.82962 | 0 | 0.51776 | 6472 | 0.4646 | 37168 | 64000 | 6472 | 13696 | 0 | 0 | 1350000 | 0 | 0
2021030616 | 7 | 0.55735 | 83602.5 | 0.81506 | 0 | 0.51928 | 6491 | 0.38579 | 30863.2 | 64000 | 6491 | 13111.5 | 0 | 0 | 1350000 | 0 | 0
2021030617 | 7 | 0.56415 | 84622.5 | 0.80708 | 0 | 0.49087 | 6135.875 | 0.17319 | 13855.2 | 64000 | 6135.875 | 13855.2 | 631.425 | 631.425 | 1350000 | 631.425 | 0
2021030618 | 7 | 0.58342 | 87513 | 0.74708 | 0 | 0.4321 | 5401.25 | 0.00906 | 724.8 | 64000 | 5401.25 | 724.8 | 17386.95 | 16755.525 | 1350000 | 17386.95 | 0
2021030619 | 7 | 0.6164 | 92460 | 0.62696 | 0 | 0.43551 | 5443.875 | 0 | 0 | 64000 | 5443.875 | 0 | 23016.125 | 5629.175 | 1350000 | 23016.125 | 0
2021030620 | 7 | 0.63052 | 94578 | 0.59968 | 0 | 0.44763 | 5595.375 | 0 | 0 | 64000 | 5595.375 | 0 | 24982.625 | 1966.5 | 1350000 | 24982.625 | 0
2021030621 | 7 | 0.62696 | 94044 | 0.63574 | 0 | 0.42565 | 5320.625 | 0 | 0 | 64000 | 5320.625 | 0 | 24723.375 | -259.25 | 1350000 | 24723.375 | 0
2021030622 | 7 | 0.61889 | 92833.5 | 0.6994 | 0 | 0.39953 | 4994.125 | 0 | 0 | 64000 | 4994.125 | 0 | 23839.375 | -884 | 1350000 | 23839.375 | 0
2021030623 | 7 | 0.60316 | 90474 | 0.66886 | 0 | 0.4133 | 5166.25 | 0 | 0 | 64000 | 5166.25 | 0 | 21307.75 | -2531.625 | 1350000 | 21307.75 | 0
2021030624 | 7 | 0.58602 | 87903 | 0.53856 | 0 | 0.42492 | 5311.5 | 0 | 0 | 64000 | 5311.5 | 0 | 18591.5 | -2716.25 | 1350000 | 18591.5 | 0
2021030701 | 1 | 0.57307 | 85960.5 | 0.44482 | 0 | 0.47315 | 5914.375 | 0 | 0 | 64000 | 5914.375 | 0 | 16046.125 | -2545.375 | 1350000 | 16046.125 | 0
2021030702 | 1 | 0.56786 | 85179 | 0.40308 | 0 | 0.51408 | 6426 | 0 | 0 | 64000 | 6426 | 0 | 14753 | -1293.125 | 1350000 | 14753 | 0
2021030703 | 1 | 0.5675 | 85125 | 0.25492 | 0 | 0.50028 | 6253.5 | 0 | 0 | 64000 | 6253.5 | 0 | 14871.5 | 118.5 | 1350000 | 14871.5 | 0
2021030704 | 1 | 0.57023 | 85534.5 | 0.19294 | 0 | 0.46775 | 5846.875 | 0 | 0 | 64000 | 5846.875 | 0 | 15687.625 | 816.125 | 1350000 | 15687.625 | 0
2021030705 | 1 | 0.57834 | 86751 | 0.20005 | 0 | 0.44458 | 5557.25 | 0 | 0 | 64000 | 5557.25 | 0 | 17193.75 | 1506.125 | 1350000 | 17193.75 | 0
2021030706 | 1 | 0.59382 | 89073 | 0.24596 | 0 | 0.38795 | 4849.375 | 0 | 0 | 64000 | 4849.375 | 0 | 20223.625 | 3029.875 | 1350000 | 20223.625 | 0
2021030707 | 1 | 0.61075 | 91612.5 | 0.25486 | 0 | 0.30951 | 3868.875 | 0 | 0 | 64000 | 3868.875 | 0 | 23743.625 | 3520 | 1350000 | 23743.625 | 0
2021030708 | 1 | 0.6165 | 92475 | 0.19169 | 0 | 0.29858 | 3732.25 | 0.13138 | 10510.4 | 64000 | 3732.25 | 10510.4 | 14232.35 | -9511.275 | 1350000 | 14232.35 | 0
2021030709 | 1 | 0.60398 | 90597 | 0.152 | 0 | 0.31028 | 3878.5 | 0.40045 | 32036 | 64000 | 3878.5 | 22718.5 | 0 | -14232.35 | 1350000 | 0 | 0
2021030710 | 1 | 0.58829 | 88243.5 | 0.16472 | 0 | 0.29374 | 3671.75 | 0.52043 | 41634.4 | 64000 | 3671.75 | 20571.75 | 0 | 0 | 1350000 | 0 | 0
2021030711 | 1 | 0.57311 | 85966.5 | 0.21326 | 0 | 0.2642 | 3302.5 | 0.54048 | 43238.4 | 64000 | 3302.5 | 18664 | 0 | 0 | 1350000 | 0 | 0
2021030712 | 1 | 0.56036 | 84054 | 0.27865 | 0 | 0.24404 | 3050.5 | 0.53247 | 42597.6 | 64000 | 3050.5 | 17003.5 | 0 | 0 | 1350000 | 0 | 0
2021030713 | 1 | 0.54913 | 82369.5 | 0.38247 | 0 | 0.2411 | 3013.75 | 0.53077 | 42461.6 | 64000 | 3013.75 | 15355.75 | 0 | 0 | 1350000 | 0 | 0
2021030714 | 1 | 0.53777 | 80665.5 | 0.40366 | 0 | 0.23792 | 2974 | 0.54263 | 43410.4 | 64000 | 2974 | 13691.5 | 0 | 0 | 1350000 | 0 | 0
2021030715 | 1 | 0.52772 | 79158 | 0.37025 | 0 | 0.2069 | 2586.25 | 0.53601 | 42880.8 | 64000 | 2586.25 | 12571.75 | 0 | 0 | 1350000 | 0 | 0
2021030716 | 1 | 0.52605 | 78907.5 | 0.36042 | 0 | 0.26411 | 3301.375 | 0.43346 | 34676.8 | 64000 | 3301.375 | 11606.125 | 0 | 0 | 1350000 | 0 | 0
2021030717 | 1 | 0.53895 | 80842.5 | 0.38855 | 0 | 0.28375 | 3546.875 | 0.18878 | 15102.4 | 64000 | 3546.875 | 13295.625 | 0 | 0 | 1350000 | 0 | 0
2021030718 | 1 | 0.56782 | 85173 | 0.38794 | 0 | 0.284 | 3550 | 0.0152 | 1216 | 64000 | 3550 | 1216 | 16407 | 16407 | 1350000 | 16407 | 0
2021030719 | 1 | 0.6067 | 91005 | 0.29661 | 0 | 0.28325 | 3540.625 | 0 | 0 | 64000 | 3540.625 | 0 | 23464.375 | 7057.375 | 1350000 | 23464.375 | 0
2021030720 | 1 | 0.62863 | 94294.5 | 0.31903 | 0 | 0.30138 | 3767.25 | 0 | 0 | 64000 | 3767.25 | 0 | 26527.25 | 3062.875 | 1348939 | 26527.25 | 0
2021030721 | 1 | 0.62776 | 94164 | 0.30244 | 0 | 0.31992 | 3999 | 0 | 0 | 64000 | 3999 | 0 | 26165 | -362.25 | 1348240.25 | 26165 | 0
2021030722 | 1 | 0.61838 | 92757 | 0.25531 | 0 | 0.33044 | 4130.5 | 0 | 0 | 64000 | 4130.5 | 0 | 24626.5 | -1538.5 | 1349080 | 24626.5 | 0
2021030723 | 1 | 0.60218 | 90327 | 0.20962 | 0 | 0.35352 | 4419 | 0 | 0 | 64000 | 4419 | 0 | 21908 | -2718.5 | 1350000 | 21908 | 0
2021030724 | 1 | 0.5849 | 87735 | 0.1553 | 0 | 0.37033 | 4629.125 | 0 | 0 | 64000 | 4629.125 | 0 | 19105.875 | -2802.125 | 1350000 | 19105.875 | 0
2021030801 | 2 | 0.57636 | 86454 | 0.17229 | 0 | 0.37739 | 4717.375 | 0 | 0 | 64000 | 4717.375 | 0 | 17736.625 | -1369.25 | 1350000 | 17736.625 | 0
2021030802 | 2 | 0.57464 | 86196 | 0.19288 | 0 | 0.34874 | 4359.25 | 0 | 0 | 64000 | 4359.25 | 0 | 17836.75 | 100.125 | 1350000 | 17836.75 | 0
2021030803 | 2 | 0.57897 | 86845.5 | 0.25332 | 0 | 0.32657 | 4082.125 | 0 | 0 | 64000 | 4082.125 | 0 | 18763.375 | 926.625 | 1350000 | 18763.375 | 0
2021030804 | 2 | 0.58808 | 88212 | 0.43093 | 0 | 0.32663 | 4082.875 | 0 | 0 | 64000 | 4082.875 | 0 | 20129.125 | 1365.75 | 1350000 | 20129.125 | 0
2021030805 | 2 | 0.60787 | 91180.5 | 0.56612 | 0 | 0.2884 | 3605 | 0 | 0 | 64000 | 3605 | 0 | 23575.5 | 3446.375 | 1350000 | 23575.5 | 0
2021030806 | 2 | 0.64499 | 96748.5 | 0.65162 | 0 | 0.25784 | 3223 | 0 | 0 | 64000 | 3223 | 0 | 29525.5 | 5950 | 1345940.75 | 29525.5 | 0
2021030807 | 2 | 0.6949 | 104235 | 0.74634 | 0 | 0.24851 | 3106.375 | 0.00137 | 109.6 | 64000 | 3106.375 | 109.6 | 37019.025 | 7493.525 | 1334387.975 | 37019.025 | 0
2021030808 | 2 | 0.7116 | 106740 | 0.70944 | 0 | 0.25409 | 3176.125 | 0.13101 | 10480.8 | 64000 | 3176.125 | 10480.8 | 29083.075 | -7935.95 | 1330771.15 | 29083.075 | 0
2021030809 | 2 | 0.68887 | 103330.5 | 0.60638 | 0 | 0.2491 | 3113.75 | 0.36753 | 29402.4 | 64000 | 3113.75 | 29402.4 | 6814.35 | -22268.725 | 1349423.05 | 6814.35 | 0
2021030810 | 2 | 0.65688 | 98532 | 0.48621 | 0 | 0.2538 | 3172.5 | 0.39021 | 31216.8 | 64000 | 3172.5 | 31216.8 | 142.7 | -6671.65 | 1350000 | 142.7 | 0
2021030811 | 2 | 0.6332 | 94980 | 0.28581 | 0 | 0.24217 | 3027.125 | 0.41029 | 32823.2 | 64000 | 3027.125 | 27952.875 | 0 | -142.7 | 1350000 | 0 | 0
2021030812 | 2 | 0.61413 | 92119.5 | 0.18957 | 0 | 0.23424 | 2928 | 0.50263 | 40210.4 | 64000 | 2928 | 25191.5 | 0 | 0 | 1350000 | 0 | 0
2021030813 | 2 | 0.59862 | 89793 | 0.1942 | 0 | 0.22299 | 2787.375 | 0.54023 | 43218.4 | 64000 | 2787.375 | 23005.625 | 0 | 0 | 1350000 | 0 | 0
2021030814 | 2 | 0.58423 | 87634.5 | 0.25101 | 0 | 0.21178 | 2647.25 | 0.57965 | 46372 | 64000 | 2647.25 | 20987.25 | 0 | 0 | 1350000 | 0 | 0
2021030815 | 2 | 0.57071 | 85606.5 | 0.21869 | 0 | 0.21929 | 2741.125 | 0.51964 | 41571.2 | 64000 | 2741.125 | 18865.375 | 0 | 0 | 1350000 | 0 | 0
2021030816 | 2 | 0.56296 | 84444 | 0.20776 | 0 | 0.26965 | 3370.625 | 0.37841 | 30272.8 | 64000 | 3370.625 | 17073.375 | 0 | 0 | 1350000 | 0 | 0
2021030817 | 2 | 0.56764 | 85146 | 0.23466 | 0 | 0.2997 | 3746.25 | 0.14496 | 11596.8 | 64000 | 3746.25 | 11596.8 | 5802.95 | 5802.95 | 1350000 | 5802.95 | 0
2021030818 | 2 | 0.58664 | 87996 | 0.26365 | 0 | 0.29855 | 3731.875 | 0.00494 | 395.2 | 64000 | 3731.875 | 395.2 | 19868.925 | 14065.975 | 1350000 | 19868.925 | 0
2021030819 | 2 | 0.61699 | 92548.5 | 0.4693 | 0 | 0.3036 | 3795 | 0 | 0 | 64000 | 3795 | 0 | 24753.5 | 4884.575 | 1350000 | 24753.5 | 0
2021030820 | 2 | 0.63002 | 94503 | 0.74758 | 0 | 0.31928 | 3991 | 0 | 0 | 64000 | 3991 | 0 | 26512 | 1758.5 | 1348954.25 | 26512 | 0
2021030821 | 2 | 0.62095 | 93142.5 | 0.88944 | 0 | 0.33105 | 4138.125 | 0 | 0 | 64000 | 4138.125 | 0 | 25004.375 | -1507.625 | 1349416.125 | 25004.375 | 0
2021030822 | 2 | 0.60266 | 90399 | 0.94884 | 0 | 0.32836 | 4104.5 | 0 | 0 | 64000 | 4104.5 | 0 | 22294.5 | -2709.875 | 1350000 | 22294.5 | 0
2021030823 | 2 | 0.57576 | 86364 | 0.95735 | 0 | 0.31828 | 3978.5 | 0 | 0 | 64000 | 3978.5 | 0 | 18385.5 | -3909 | 1350000 | 18385.5 | 0
2021030824 | 2 | 0.55233 | 82849.5 | 0.95483 | 0 | 0.35161 | 4395.125 | 0 | 0 | 64000 | 4395.125 | 0 | 14454.375 | -3931.125 | 1350000 | 14454.375 | 0
2021030901 | 3 | 0.53517 | 80275.5 | 0.95441 | 0 | 0.35524 | 4440.5 | 0 | 0 | 64000 | 4440.5 | 0 | 11835 | -2619.375 | 1350000 | 11835 | 0
2021030902 | 3 | 0.52733 | 79099.5 | 0.95035 | 0 | 0.3543 | 4428.75 | 0 | 0 | 64000 | 4428.75 | 0 | 10670.75 | -1164.25 | 1350000 | 10670.75 | 0
2021030903 | 3 | 0.52532 | 78798 | 0.94489 | 0 | 0.37845 | 4730.625 | 0 | 0 | 64000 | 4730.625 | 0 | 10067.375 | -603.375 | 1350000 | 10067.375 | 0
2021030904 | 3 | 0.52797 | 79195.5 | 0.95003 | 0 | 0.41465 | 5183.125 | 0 | 0 | 64000 | 5183.125 | 0 | 10012.375 | -55 | 1350000 | 10012.375 | 0
2021030905 | 3 | 0.54215 | 81322.5 | 0.93376 | 0 | 0.43625 | 5453.125 | 0 | 0 | 64000 | 5453.125 | 0 | 11869.375 | 1857 | 1350000 | 11869.375 | 0
2021030906 | 3 | 0.57443 | 86164.5 | 0.90819 | 0 | 0.4726 | 5907.5 | 0 | 0 | 64000 | 5907.5 | 0 | 16257 | 4387.625 | 1350000 | 16257 | 0
2021030907 | 3 | 0.61881 | 92821.5 | 0.88096 | 0 | 0.50463 | 6307.875 | 0 | 0 | 64000 | 6307.875 | 0 | 22513.625 | 6256.625 | 1350000 | 22513.625 | 0
2021030908 | 3 | 0.6387 | 95805 | 0.80959 | 0 | 0.55161 | 6895.125 | 0.0477 | 3816 | 64000 | 6895.125 | 3816 | 21093.875 | -1419.75 | 1350000 | 21093.875 | 0
2021030909 | 3 | 0.62533 | 93799.5 | 0.68125 | 0 | 0.58768 | 7346 | 0.18126 | 14500.8 | 64000 | 7346 | 14500.8 | 7952.7 | -13141.175 | 1350000 | 7952.7 | 0
2021030910 | 3 | 0.60044 | 90066 | 0.59946 | 0 | 0.58041 | 7255.125 | 0.24342 | 19473.6 | 64000 | 7255.125 | 18810.875 | 0 | -7952.7 | 1350000 | 0 | 0
2021030911 | 3 | 0.58026 | 87039 | 0.5673 | 0 | 0.56349 | 7043.625 | 0.32605 | 26084 | 64000 | 7043.625 | 15995.375 | 0 | 0 | 1350000 | 0 | 0
2021030912 | 3 | 0.56556 | 84834 | 0.58566 | 0 | 0.56245 | 7030.625 | 0.36911 | 29528.8 | 64000 | 7030.625 | 13803.375 | 0 | 0 | 1350000 | 0 | 0
2021030913 | 3 | 0.55649 | 83473.5 | 0.53108 | 0 | 0.56534 | 7066.75 | 0.36894 | 29515.2 | 64000 | 7066.75 | 12406.75 | 0 | 0 | 1350000 | 0 | 0
2021030914 | 3 | 0.54913 | 82369.5 | 0.52157 | 0 | 0.50962 | 6370.25 | 0.35531 | 28424.8 | 64000 | 6370.25 | 11999.25 | 0 | 0 | 1350000 | 0 | 0
2021030915 | 3 | 0.54256 | 81384 | 0.50385 | 0 | 0.51393 | 6424.125 | 0.30818 | 24654.4 | 64000 | 6424.125 | 10959.875 | 0 | 0 | 1350000 | 0 | 0
2021030916 | 3 | 0.53836 | 80754 | 0.46532 | 0 | 0.51616 | 6452 | 0.18752 | 15001.6 | 64000 | 6452 | 10302 | 0 | 0 | 1350000 | 0 | 0
2021030917 | 3 | 0.54107 | 81160.5 | 0.31343 | 0 | 0.54398 | 6799.75 | 0.06615 | 5292 | 64000 | 6799.75 | 5292 | 5068.75 | 5068.75 | 1350000 | 5068.75 | 0
2021030918 | 3 | 0.5549 | 83235 | 0.16324 | 0 | 0.49925 | 6240.625 | 0.00283 | 226.4 | 64000 | 6240.625 | 226.4 | 12767.975 | 7699.225 | 1350000 | 12767.975 | 0
2021030919 | 3 | 0.57922 | 86883 | 0.0813 | 0 | 0.49315 | 6164.375 | 0 | 0 | 64000 | 6164.375 | 0 | 16718.625 | 3950.65 | 1350000 | 16718.625 | 0
2021030920 | 3 | 0.59061 | 88591.5 | 0.06032 | 0 | 0.48229 | 6028.625 | 0 | 0 | 64000 | 6028.625 | 0 | 18562.875 | 1844.25 | 1350000 | 18562.875 | 0
2021030921 | 3 | 0.57968 | 86952 | 0.08818 | 0 | 0.52409 | 6551.125 | 0 | 0 | 64000 | 6551.125 | 0 | 16400.875 | -2162 | 1350000 | 16400.875 | 0
2021030922 | 3 | 0.5602 | 84030 | 0.11013 | 0 | 0.52448 | 6556 | 0 | 0 | 64000 | 6556 | 0 | 13474 | -2926.875 | 1350000 | 13474 | 0
2021030923 | 3 | 0.53341 | 80011.5 | 0.1043 | 0 | 0.56899 | 7112.375 | 0 | 0 | 64000 | 7112.375 | 0 | 8899.125 | -4574.875 | 1350000 | 8899.125 | 0
2021030924 | 3 | 0.5096 | 76440 | 0.08277 | 0 | 0.54574 | 6821.75 | 0 | 0 | 64000 | 6821.75 | 0 | 5618.25 | -3280.875 | 1350000 | 5618.25 | 0
2021031001 | 4 | 0.49229 | 73843.5 | 0.11126 | 0 | 0.58968 | 7371 | 0 | 0 | 64000 | 7371 | 0 | 2472.5 | -3145.75 | 1350000 | 2472.5 | 0
2021031002 | 4 | 0.48568 | 72852 | 0.16381 | 0 | 0.63876 | 7984.5 | 0 | 0 | 64000 | 7984.5 | 0 | 867.5 | -1605 | 1350000 | 867.5 | 0
2021031003 | 4 | 0.48453 | 72679.5 | 0.1872 | 0 | 0.60387 | 7548.375 | 0 | 0 | 64000 | 7548.375 | 0 | 1131.125 | 263.625 | 1350000 | 1131.125 | 0
2021031004 | 4 | 0.48944 | 73416 | 0.27667 | 0 | 0.55765 | 6970.625 | 0 | 0 | 64000 | 6970.625 | 0 | 2445.375 | 1314.25 | 1350000 | 2445.375 | 0
2021031005 | 4 | 0.50342 | 75513 | 0.41312 | 0 | 0.52831 | 6603.875 | 0 | 0 | 64000 | 6603.875 | 0 | 4909.125 | 2463.75 | 1350000 | 4909.125 | 0
2021031006 | 4 | 0.53536 | 80304 | 0.58152 | 0 | 0.47047 | 5880.875 | 0 | 0 | 64000 | 5880.875 | 0 | 10423.125 | 5514 | 1350000 | 10423.125 | 0
2021031007 | 4 | 0.57987 | 86980.5 | 0.6567 | 0 | 0.49044 | 6130.5 | 0.00307 | 245.6 | 64000 | 6130.5 | 245.6 | 16604.4 | 6181.275 | 1350000 | 16604.4 | 0
2021031008 | 4 | 0.59989 | 89983.5 | 0.68745 | 0 | 0.42717 | 5339.625 | 0.13509 | 10807.2 | 64000 | 5339.625 | 10807.2 | 9836.675 | -6767.725 | 1350000 | 9836.675 | 0
2021031009 | 4 | 0.58994 | 88491 | 0.65494 | 0 | 0.33342 | 4167.75 | 0.43132 | 34505.6 | 64000 | 4167.75 | 20323.25 | 0 | -9836.675 | 1350000 | 0 | 0
2021031010 | 4 | 0.57293 | 85939.5 | 0.57047 | 0 | 0.30285 | 3785.625 | 0.55546 | 44436.8 | 64000 | 3785.625 | 18153.875 | 0 | 0 | 1350000 | 0 | 0
2021031011 | 4 | 0.55871 | 83806.5 | 0.50863 | 0 | 0.2902 | 3627.5 | 0.56404 | 45123.2 | 64000 | 3627.5 | 16179 | 0 | 0 | 1350000 | 0 | 0
2021031012 | 4 | 0.54897 | 82345.5 | 0.47807 | 0 | 0.26104 | 3263 | 0.55649 | 44519.2 | 64000 | 3263 | 15082.5 | 0 | 0 | 1350000 | 0 | 0
2021031013 | 4 | 0.54317 | 81475.5 | 0.44854 | 0 | 0.30575 | 3821.875 | 0.5407 | 43256 | 64000 | 3821.875 | 13653.625 | 0 | 0 | 1350000 | 0 | 0
2021031014 | 4 | 0.53802 | 80703 | 0.47919 | 0 | 0.28788 | 3598.5 | 0.52973 | 42378.4 | 64000 | 3598.5 | 13104.5 | 0 | 0 | 1350000 | 0 | 0
2021031015 | 4 | 0.53424 | 80136 | 0.55686 | 0 | 0.29735 | 3716.875 | 0.44311 | 35448.8 | 64000 | 3716.875 | 12419.125 | 0 | 0 | 1350000 | 0 | 0
2021031016 | 4 | 0.53395 | 80092.5 | 0.60354 | 0 | 0.34803 | 4350.375 | 0.31724 | 25379.2 | 64000 | 4350.375 | 11742.125 | 0 | 0 | 1350000 | 0 | 0
2021031017 | 4 | 0.5398 | 80970 | 0.67524 | 0 | 0.32816 | 4102 | 0.12277 | 9821.6 | 64000 | 4102 | 9821.6 | 3046.4 | 3046.4 | 1350000 | 3046.4 | 0
2021031018 | 4 | 0.55401 | 83101.5 | 0.73598 | 0 | 0.30387 | 3798.375 | 0.00701 | 560.8 | 64000 | 3798.375 | 560.8 | 14742.325 | 11695.925 | 1350000 | 14742.325 | 0
2021031019 | 4 | 0.57607 | 86410.5 | 0.79419 | 0 | 0.31492 | 3936.5 | 0 | 0 | 64000 | 3936.5 | 0 | 18474 | 3731.675 | 1350000 | 18474 | 0
2021031020 | 4 | 0.58257 | 87385.5 | 0.85967 | 0 | 0.28939 | 3617.375 | 0 | 0 | 64000 | 3617.375 | 0 | 19768.125 | 1294.125 | 1350000 | 19768.125 | 0
2021031021 | 4 | 0.56909 | 85363.5 | 0.88264 | 0 | 0.24257 | 3032.125 | 0 | 0 | 64000 | 3032.125 | 0 | 18331.375 | -1436.75 | 1350000 | 18331.375 | 0
2021031022 | 4 | 0.54666 | 81999 | 0.88387 | 0 | 0.22726 | 2840.75 | 0 | 0 | 64000 | 2840.75 | 0 | 15158.25 | -3173.125 | 1350000 | 15158.25 | 0
2021031023 | 4 | 0.51795 | 77692.5 | 0.87378 | 0 | 0.20522 | 2565.25 | 0 | 0 | 64000 | 2565.25 | 0 | 11127.25 | -4031 | 1350000 | 11127.25 | 0
2021031024 | 4 | 0.48961 | 73441.5 | 0.85959 | 0 | 0.1792 | 2240 | 0 | 0 | 64000 | 2240 | 0 | 7201.5 | -3925.75 | 1350000 | 7201.5 | 0
2021031101 | 5 | 0.47027 | 70540.5 | 0.84298 | 0 | 0.18631 | 2328.875 | 0 | 0 | 64000 | 2328.875 | 0 | 4211.625 | -2989.875 | 1350000 | 4211.625 | 0
2021031102 | 5 | 0.45845 | 68767.5 | 0.86572 | 0 | 0.18323 | 2290.375 | 0 | 0 | 64000 | 2290.375 | 0 | 2477.125 | -1734.5 | 1350000 | 2477.125 | 0
2021031103 | 5 | 0.45375 | 68062.5 | 0.87171 | 0 | 0.1619 | 2023.75 | 0 | 0 | 64000 | 2023.75 | 0 | 2038.75 | -438.375 | 1350000 | 2038.75 | 0
2021031104 | 5 | 0.45412 | 68118 | 0.89471 | 0 | 0.11112 | 1389 | 0 | 0 | 64000 | 1389 | 0 | 2729 | 690.25 | 1350000 | 2729 | 0
2021031105 | 5 | 0.46484 | 69726 | 0.94038 | 0 | 0.07849 | 981.125 | 0 | 0 | 64000 | 981.125 | 0 | 4744.875 | 2015.875 | 1350000 | 4744.875 | 0
2021031106 | 5 | 0.49346 | 74019 | 0.93597 | 0 | 0.05328 | 666 | 0 | 0 | 64000 | 666 | 0 | 9353 | 4608.125 | 1350000 | 9353 | 0
2021031107 | 5 | 0.53554 | 80331 | 0.9302 | 0 | 0.06208 | 776 | 0.00295 | 236 | 64000 | 776 | 236 | 15319 | 5966 | 1350000 | 15319 | 0
2021031108 | 5 | 0.56031 | 84046.5 | 0.89438 | 0 | 0.08075 | 1009.375 | 0.12921 | 10336.8 | 64000 | 1009.375 | 10336.8 | 8700.325 | -6618.675 | 1350000 | 8700.325 | 0
2021031109 | 5 | 0.56263 | 84394.5 | 0.8606 | 0 | 0.09788 | 1223.5 | 0.43415 | 34732 | 64000 | 1223.5 | 19171 | 0 | -8700.325 | 1350000 | 0 | 0
2021031110 | 5 | 0.55436 | 83154 | 0.82775 | 0 | 0.11625 | 1453.125 | 0.5567 | 44536 | 64000 | 1453.125 | 17700.875 | 0 | 0 | 1350000 | 0 | 0
2021031111 | 5 | 0.54568 | 81852 | 0.77494 | 0 | 0.11986 | 1498.25 | 0.54307 | 43445.6 | 64000 | 1498.25 | 16353.75 | 0 | 0 | 1350000 | 0 | 0
2021031112 | 5 | 0.54213 | 81319.5 | 0.80596 | 0 | 0.1049 | 1311.25 | 0.52305 | 41844 | 64000 | 1311.25 | 16008.25 | 0 | 0 | 1350000 | 0 | 0
2021031113 | 5 | 0.54034 | 81051 | 0.7738 | 0 | 0.0797 | 996.25 | 0.55276 | 44220.8 | 64000 | 996.25 | 16054.75 | 0 | 0 | 1350000 | 0 | 0
2021031114 | 5 | 0.53955 | 80932.5 | 0.73409 | 0 | 0.07111 | 888.875 | 0.54099 | 43279.2 | 64000 | 888.875 | 16043.625 | 0 | 0 | 1350000 | 0 | 0
2021031115 | 5 | 0.53807 | 80710.5 | 0.75374 | 0 | 0.05381 | 672.625 | 0.42117 | 33693.6 | 64000 | 672.625 | 16037.875 | 0 | 0 | 1350000 | 0 | 0
2021031116 | 5 | 0.53678 | 80517 | 0.74986 | 0 | 0.05323 | 665.375 | 0.31287 | 25029.6 | 64000 | 665.375 | 15851.625 | 0 | 0 | 1350000 | 0 | 0
2021031117 | 5 | 0.54046 | 81069 | 0.83291 | 0 | 0.04127 | 515.875 | 0.11247 | 8997.6 | 64000 | 515.875 | 8997.6 | 7555.525 | 7555.525 | 1350000 | 7555.525 | 0
2021031118 | 5 | 0.55172 | 82758 | 0.91785 | 0 | 0.02864 | 358 | 0.00622 | 497.6 | 64000 | 358 | 497.6 | 17902.4 | 10346.875 | 1350000 | 17902.4 | 0
2021031119 | 5 | 0.57071 | 85606.5 | 0.92262 | 0 | 0.03472 | 434 | 0 | 0 | 64000 | 434 | 0 | 21172.5 | 3270.1 | 1350000 | 21172.5 | 0
2021031120 | 5 | 0.57634 | 86451 | 0.88992 | 0 | 0.03917 | 489.625 | 0 | 0 | 64000 | 489.625 | 0 | 21961.375 | 788.875 | 1350000 | 21961.375 | 0
2021031121 | 5 | 0.56003 | 84004.5 | 0.93179 | 0 | 0.03761 | 470.125 | 0 | 0 | 64000 | 470.125 | 0 | 19534.375 | -2427 | 1350000 | 19534.375 | 0
2021031122 | 5 | 0.53807 | 80710.5 | 0.93377 | 0 | 0.04154 | 519.25 | 0 | 0 | 64000 | 519.25 | 0 | 16191.25 | -3343.125 | 1350000 | 16191.25 | 0
2021031123 | 5 | 0.50785 | 76177.5 | 0.93748 | 0 | 0.04311 | 538.875 | 0 | 0 | 64000 | 538.875 | 0 | 11638.625 | -4552.625 | 1350000 | 11638.625 | 0
2021031124 | 5 | 0.47855 | 71782.5 | 0.95491 | 0 | 0.06529 | 816.125 | 0 | 0 | 64000 | 816.125 | 0 | 6966.375 | -4672.25 | 1350000 | 6966.375 | 0
2021031201 | 6 | 0.4586 | 68790 | 0.95801 | 0 | 0.06266 | 783.25 | 0 | 0 | 64000 | 783.25 | 0 | 4006.75 | -2959.625 | 1350000 | 4006.75 | 0
2021031202 | 6 | 0.44531 | 66796.5 | 0.93378 | 0 | 0.06382 | 797.75 | 0 | 0 | 64000 | 797.75 | 0 | 1998.75 | -2008 | 1350000 | 1998.75 | 0
2021031203 | 6 | 0.43935 | 65902.5 | 0.90196 | 0 | 0.05703 | 712.875 | 0 | 0 | 64000 | 712.875 | 0 | 1189.625 | -809.125 | 1350000 | 1189.625 | 0
2021031204 | 6 | 0.43887 | 65830.5 | 0.88386 | 0 | 0.05739 | 717.375 | 0 | 0 | 64000 | 717.375 | 0 | 1113.125 | -76.5 | 1350000 | 1113.125 | 0
2021031205 | 6 | 0.44778 | 67167 | 0.7871 | 0 | 0.05918 | 739.75 | 0 | 0 | 64000 | 739.75 | 0 | 2427.25 | 1314.125 | 1350000 | 2427.25 | 0
2021031206 | 6 | 0.47361 | 71041.5 | 0.69434 | 0 | 0.06156 | 769.5 | 0 | 0 | 64000 | 769.5 | 0 | 6272 | 3844.75 | 1350000 | 6272 | 0
2021031207 | 6 | 0.51305 | 76957.5 | 0.62743 | 0 | 0.06246 | 780.75 | 0.00218 | 174.4 | 64000 | 780.75 | 174.4 | 12002.35 | 5730.35 | 1350000 | 12002.35 | 0
2021031208 | 6 | 0.54076 | 81114 | 0.51216 | 0 | 0.05188 | 648.5 | 0.07034 | 5627.2 | 64000 | 648.5 | 5627.2 | 10838.3 | -1164.05 | 1350000 | 10838.3 | 0
2021031209 | 6 | 0.55079 | 82618.5 | 0.41402 | 0 | 0.04969 | 621.125 | 0.22731 | 18184.8 | 64000 | 621.125 | 17997.375 | 0 | -10838.3 | 1350000 | 0 | 0
2021031210 | 6 | 0.55099 | 82648.5 | 0.3747 | 0 | 0.05444 | 680.5 | 0.33934 | 27147.2 | 64000 | 680.5 | 17968 | 0 | 0 | 1350000 | 0 | 0
2021031211 | 6 | 0.54906 | 82359 | 0.48483 | 0 | 0.05984 | 748 | 0.38375 | 30700 | 64000 | 748 | 17611 | 0 | 0 | 1350000 | 0 | 0
2021031212 | 6 | 0.545 | 81750 | 0.56779 | 0 | 0.05947 | 743.375 | 0.38992 | 31193.6 | 64000 | 743.375 | 17006.625 | 0 | 0 | 1350000 | 0 | 0
2021031213 | 6 | 0.53762 | 80643 | 0.71502 | 0 | 0.04216 | 527 | 0.40119 | 32095.2 | 64000 | 527 | 16116 | 0 | 0 | 1350000 | 0 | 0
2021031214 | 6 | 0.52963 | 79444.5 | 0.77862 | 0 | 0.04507 | 563.375 | 0.39748 | 31798.4 | 64000 | 563.375 | 14881.125 | 0 | 0 | 1350000 | 0 | 0
2021031215 | 6 | 0.52563 | 78844.5 | 0.8625 | 0 | 0.05348 | 668.5 | 0.30913 | 24730.4 | 64000 | 668.5 | 14176 | 0 | 0 | 1350000 | 0 | 0
2021031216 | 6 | 0.52237 | 78355.5 | 0.93233 | 0 | 0.06574 | 821.75 | 0.22085 | 17668 | 64000 | 821.75 | 13533.75 | 0 | 0 | 1350000 | 0 | 0
2021031217 | 6 | 0.5263 | 78945 | 0.96166 | 0 | 0.08331 | 1041.375 | 0.0862 | 6896 | 64000 | 1041.375 | 6896 | 7007.625 | 7007.625 | 1350000 | 7007.625 | 0
2021031218 | 6 | 0.53586 | 80379 | 0.96529 | 0 | 0.09784 | 1223 | 0.00859 | 687.2 | 64000 | 1223 | 687.2 | 14468.8 | 7461.175 | 1350000 | 14468.8 | 0
2021031219 | 6 | 0.55248 | 82872 | 0.96125 | 0 | 0.11513 | 1439.125 | 0 | 0 | 64000 | 1439.125 | 0 | 17432.875 | 2964.075 | 1350000 | 17432.875 | 0
2021031220 | 6 | 0.55901 | 83851.5 | 0.96335 | 0 | 0.12388 | 1548.5 | 0 | 0 | 64000 | 1548.5 | 0 | 18303 | 870.125 | 1350000 | 18303 | 0
2021031221 | 6 | 0.54753 | 82129.5 | 0.97451 | 0 | 0.1413 | 1766.25 | 0 | 0 | 64000 | 1766.25 | 0 | 16363.25 | -1939.75 | 1350000 | 16363.25 | 0
2021031222 | 6 | 0.53162 | 79743 | 0.98184 | 0 | 0.16411 | 2051.375 | 0 | 0 | 64000 | 2051.375 | 0 | 13691.625 | -2671.625 | 1350000 | 13691.625 | 0
2021031223 | 6 | 0.50899 | 76348.5 | 0.98979 | 0 | 0.18667 | 2333.375 | 0 | 0 | 64000 | 2333.375 | 0 | 10015.125 | -3676.5 | 1350000 | 10015.125 | 0
2021031224 | 6 | 0.48596 | 72894 | 0.99198 | 0 | 0.21662 | 2707.75 | 0 | 0 | 64000 | 2707.75 | 0 | 6186.25 | -3828.875 | 1350000 | 6186.25 | 0
2021031301 | 7 | 0.46826 | 70239 | 0.99479 | 0 | 0.24797 | 3099.625 | 0 | 0 | 64000 | 3099.625 | 0 | 3139.375 | -3046.875 | 1350000 | 3139.375 | 0
2021031302 | 7 | 0.45748 | 68622 | 0.98631 | 0 | 0.28873 | 3609.125 | 0 | 0 | 64000 | 3609.125 | 0 | 1012.875 | -2126.5 | 1350000 | 1012.875 | 0
2021031303 | 7 | 0.45584 | 68376 | 0.97359 | 0 | 0.35839 | 4479.875 | 0 | 0 | 64000 | 4376 | 0 | 0 | -1012.875 | 1350000 | 0 | 0
2021031304 | 7 | 0.45459 | 68188.5 | 0.97457 | 0 | 0.39692 | 4961.5 | 0 | 0 | 64000 | 4188.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021031305 | 7 | 0.46043 | 69064.5 | 0.9468 | 0 | 0.38478 | 4809.75 | 0 | 0 | 64000 | 4809.75 | 0 | 254.75 | 254.75 | 1350000 | 254.75 | 0
2021031306 | 7 | 0.47667 | 71500.5 | 0.9116 | 0 | 0.38714 | 4839.25 | 0 | 0 | 64000 | 4839.25 | 0 | 2661.25 | 2406.5 | 1350000 | 2661.25 | 0
2021031307 | 7 | 0.4981 | 74715 | 0.83615 | 0 | 0.41658 | 5207.25 | 0.0025 | 200 | 64000 | 5207.25 | 200 | 5307.75 | 2646.5 | 1350000 | 5307.75 | 0
2021031308 | 7 | 0.51382 | 77073 | 0.72126 | 0 | 0.47614 | 5951.75 | 0.14407 | 11525.6 | 64000 | 5951.75 | 7121.25 | 0 | -5307.75 | 1350000 | 0 | 0
2021031309 | 7 | 0.52327 | 78490.5 | 0.53907 | 0 | 0.53352 | 6669 | 0.48484 | 38787.2 | 64000 | 6669 | 7821.5 | 0 | 0 | 1350000 | 0 | 0
2021031310 | 7 | 0.52574 | 78861 | 0.3382 | 0 | 0.57554 | 7194.25 | 0.62611 | 50088.8 | 64000 | 7194.25 | 7666.75 | 0 | 0 | 1350000 | 0 | 0
2021031311 | 7 | 0.52129 | 78193.5 | 0.25968 | 0 | 0.59652 | 7456.5 | 0.64293 | 51434.4 | 64000 | 7456.5 | 6737 | 0 | 0 | 1350000 | 0 | 0
2021031312 | 7 | 0.51299 | 76948.5 | 0.24118 | 0 | 0.61265 | 7658.125 | 0.63273 | 50618.4 | 64000 | 7658.125 | 5290.375 | 0 | 0 | 1350000 | 0 | 0
2021031313 | 7 | 0.50158 | 75237 | 0.2721 | 0 | 0.60761 | 7595.125 | 0.63693 | 50954.4 | 64000 | 7595.125 | 3641.875 | 0 | 0 | 1350000 | 0 | 0
2021031314 | 7 | 0.49168 | 73752 | 0.36347 | 0 | 0.61765 | 7720.625 | 0.63099 | 50479.2 | 64000 | 7720.625 | 2031.375 | 0 | 0 | 1350000 | 0 | 0
2021031315 | 7 | 0.48513 | 72769.5 | 0.45517 | 0 | 0.54008 | 6751 | 0.63077 | 50461.6 | 64000 | 6751 | 2018.5 | 0 | 0 | 1350000 | 0 | 0
2021031316 | 7 | 0.48412 | 72618 | 0.52592 | 0 | 0.489 | 6112.5 | 0.5454 | 43632 | 64000 | 6112.5 | 2505.5 | 0 | 0 | 1350000 | 0 | 0
2021031317 | 7 | 0.49275 | 73912.5 | 0.60999 | 0 | 0.49329 | 6166.125 | 0.22556 | 18044.8 | 64000 | 6166.125 | 3746.375 | 0 | 0 | 1350000 | 0 | 0
2021031318 | 7 | 0.50651 | 75976.5 | 0.61059 | 0 | 0.5062 | 6327.5 | 0.02057 | 1645.6 | 64000 | 6327.5 | 1645.6 | 4003.4 | 4003.4 | 1350000 | 4003.4 | 0
2021031319 | 7 | 0.53417 | 80125.5 | 0.62847 | 0 | 0.48936 | 6117 | 0 | 0 | 64000 | 6117 | 0 | 10008.5 | 6005.1 | 1350000 | 10008.5 | 0
2021031320 | 7 | 0.55107 | 82660.5 | 0.74363 | 0 | 0.45881 | 5735.125 | 0 | 0 | 64000 | 5735.125 | 0 | 12925.375 | 2916.875 | 1350000 | 12925.375 | 0
2021031321 | 7 | 0.54792 | 82188 | 0.89271 | 0 | 0.50681 | 6335.125 | 0 | 0 | 64000 | 6335.125 | 0 | 11852.875 | -1072.5 | 1350000 | 11852.875 | 0
2021031322 | 7 | 0.53804 | 80706 | 0.92351 | 0 | 0.53864 | 6733 | 0 | 0 | 64000 | 6733 | 0 | 9973 | -1879.875 | 1350000 | 9973 | 0
2021031323 | 7 | 0.52207 | 78310.5 | 0.9354 | 0 | 0.59163 | 7395.375 | 0 | 0 | 64000 | 7395.375 | 0 | 6915.125 | -3057.875 | 1350000 | 6915.125 | 0
2021031324 | 7 | 0.50512 | 75768 | 0.96233 | 0 | 0.6251 | 7813.75 | 0 | 0 | 64000 | 7813.75 | 0 | 3954.25 | -2960.875 | 1350000 | 3954.25 | 0
2021031401 | 1 | 0.48929 | 73393.5 | 0.97372 | 0 | 0.65453 | 8181.625 | 0 | 0 | 64000 | 8181.625 | 0 | 1211.875 | -2742.375 | 1350000 | 1211.875 | 0
2021031403 | 1 | 0.44955 | 67432.5 | 0.97858 | 0 | 0.62921 | 7865.125 | 0 | 0 | 64000 | 3432.5 | 0 | 0 | -1211.875 | 1350000 | 0 | 0
2021031404 | 1 | 0.47925 | 71887.5 | 0.9809 | 0 | 0.60133 | 7516.625 | 0 | 0 | 64000 | 7516.625 | 0 | 370.875 | 370.875 | 1350000 | 370.875 | 0
2021031405 | 1 | 0.48142 | 72213 | 0.96785 | 0 | 0.5747 | 7183.75 | 0 | 0 | 64000 | 7183.75 | 0 | 1029.25 | 658.375 | 1350000 | 1029.25 | 0
2021031406 | 1 | 0.49166 | 73749 | 0.94318 | 0 | 0.55935 | 6991.875 | 0 | 0 | 64000 | 6991.875 | 0 | 2757.125 | 1727.875 | 1350000 | 2757.125 | 0
2021031407 | 1 | 0.50698 | 76047 | 0.91683 | 0 | 0.46836 | 5854.5 | 0 | 0 | 64000 | 5854.5 | 0 | 6192.5 | 3435.375 | 1350000 | 6192.5 | 0
2021031408 | 1 | 0.5203 | 78045 | 0.91556 | 0 | 0.48406 | 6050.75 | 0.00453 | 362.4 | 64000 | 6050.75 | 362.4 | 7631.85 | 1439.35 | 1350000 | 7631.85 | 0
2021031409 | 1 | 0.52571 | 78856.5 | 0.91214 | 0 | 0.55003 | 6875.375 | 0.17388 | 13910.4 | 64000 | 6875.375 | 7981.125 | 0 | -7631.85 | 1350000 | 0 | 0
2021031410 | 1 | 0.52063 | 78094.5 | 0.92303 | 0 | 0.5176 | 6470 | 0.48951 | 39160.8 | 64000 | 6470 | 7624.5 | 0 | 0 | 1350000 | 0 | 0
2021031411 | 1 | 0.51148 | 76722 | 0.95207 | 0 | 0.43749 | 5468.625 | 0.6174 | 49392 | 64000 | 5468.625 | 7253.375 | 0 | 0 | 1350000 | 0 | 0
2021031412 | 1 | 0.50353 | 75529.5 | 0.98449 | 0 | 0.33098 | 4137.25 | 0.63565 | 50852 | 64000 | 4137.25 | 7392.25 | 0 | 0 | 1350000 | 0 | 0
2021031413 | 1 | 0.49784 | 74676 | 0.99585 | 0 | 0.22816 | 2852 | 0.63741 | 50992.8 | 64000 | 2852 | 7824 | 0 | 0 | 1350000 | 0 | 0
2021031414 | 1 | 0.49183 | 73774.5 | 0.99899 | 0 | 0.19439 | 2429.875 | 0.64473 | 51578.4 | 64000 | 2429.875 | 7344.625 | 0 | 0 | 1350000 | 0 | 0
2021031415 | 1 | 0.48586 | 72879 | 0.99944 | 0 | 0.18245 | 2280.625 | 0.65843 | 52674.4 | 64000 | 2280.625 | 6598.375 | 0 | 0 | 1350000 | 0 | 0
2021031416 | 1 | 0.48424 | 72636 | 0.99786 | 0 | 0.17954 | 2244.25 | 0.65194 | 52155.2 | 64000 | 2244.25 | 6391.75 | 0 | 0 | 1350000 | 0 | 0
2021031417 | 1 | 0.49185 | 73777.5 | 0.99861 | 0 | 0.26437 | 3304.625 | 0.53465 | 42772 | 64000 | 3304.625 | 6472.875 | 0 | 0 | 1350000 | 0 | 0
2021031418 | 1 | 0.50756 | 76134 | 0.99831 | 0 | 0.36752 | 4594 | 0.19722 | 15777.6 | 64000 | 4594 | 7540 | 0 | 0 | 1350000 | 0 | 0
2021031419 | 1 | 0.5272 | 79080 | 0.99603 | 0 | 0.38405 | 4800.625 | 0.01953 | 1562.4 | 64000 | 4800.625 | 1562.4 | 8716.975 | 8716.975 | 1350000 | 8716.975 | 0
2021031420 | 1 | 0.55697 | 83545.5 | 0.9939 | 0 | 0.39743 | 4967.875 | 0 | 0 | 64000 | 4967.875 | 0 | 14577.625 | 5860.65 | 1350000 | 14577.625 | 0
2021031421 | 1 | 0.57198 | 85797 | 0.9917 | 0 | 0.44628 | 5578.5 | 0 | 0 | 64000 | 5578.5 | 0 | 16218.5 | 1640.875 | 1350000 | 16218.5 | 0
2021031422 | 1 | 0.56202 | 84303 | 0.98975 | 0 | 0.48431 | 6053.875 | 0 | 0 | 64000 | 6053.875 | 0 | 14249.125 | -1969.375 | 1350000 | 14249.125 | 0
2021031423 | 1 | 0.54445 | 81667.5 | 0.99129 | 0 | 0.49683 | 6210.375 | 0 | 0 | 64000 | 6210.375 | 0 | 11457.125 | -2792 | 1350000 | 11457.125 | 0
2021031424 | 1 | 0.52439 | 78658.5 | 0.9873 | 0 | 0.51329 | 6416.125 | 0 | 0 | 64000 | 6416.125 | 0 | 8242.375 | -3214.75 | 1350000 | 8242.375 | 0
2021031501 | 2 | 0.51157 | 76735.5 | 0.97639 | 0 | 0.52177 | 6522.125 | 0 | 0 | 64000 | 6522.125 | 0 | 6213.375 | -2029 | 1350000 | 6213.375 | 0
2021031502 | 2 | 0.50708 | 76062 | 0.94284 | 0 | 0.54382 | 6797.75 | 0 | 0 | 64000 | 6797.75 | 0 | 5264.25 | -949.125 | 1350000 | 5264.25 | 0
2021031503 | 2 | 0.50708 | 76062 | 0.89858 | 0 | 0.56589 | 7073.625 | 0 | 0 | 64000 | 7073.625 | 0 | 4988.375 | -275.875 | 1350000 | 4988.375 | 0
2021031504 | 2 | 0.51345 | 77017.5 | 0.8701 | 0 | 0.54491 | 6811.375 | 0 | 0 | 64000 | 6811.375 | 0 | 6206.125 | 1217.75 | 1350000 | 6206.125 | 0
2021031505 | 2 | 0.53255 | 79882.5 | 0.84069 | 0 | 0.51783 | 6472.875 | 0 | 0 | 64000 | 6472.875 | 0 | 9409.625 | 3203.5 | 1350000 | 9409.625 | 0
2021031506 | 2 | 0.56718 | 85077 | 0.79462 | 0 | 0.4394 | 5492.5 | 0 | 0 | 64000 | 5492.5 | 0 | 15584.5 | 6174.875 | 1350000 | 15584.5 | 0
2021031507 | 2 | 0.62118 | 93177 | 0.7943 | 0 | 0.33689 | 4211.125 | 0 | 0 | 64000 | 4211.125 | 0 | 24965.875 | 9381.375 | 1350000 | 24965.875 | 0
2021031508 | 2 | 0.66387 | 99580.5 | 0.78324 | 0 | 0.32483 | 4060.375 | 0.00483 | 386.4 | 64000 | 4060.375 | 386.4 | 31133.725 | 6167.85 | 1344332.525 | 31133.725 | 0
2021031509 | 2 | 0.67392 | 101088 | 0.73606 | 0 | 0.32678 | 4084.75 | 0.18506 | 14804.8 | 64000 | 4084.75 | 14804.8 | 18198.45 | -12935.275 | 1350000 | 18198.45 | 0
2021031510 | 2 | 0.66632 | 99948 | 0.66054 | 0 | 0.3323 | 4153.75 | 0.49424 | 39539.2 | 64000 | 4153.75 | 31794.25 | 0 | -18198.45 | 1350000 | 0 | 0
2021031511 | 2 | 0.65554 | 98331 | 0.63677 | 0 | 0.32881 | 4110.125 | 0.62504 | 50003.2 | 64000 | 4110.125 | 30220.875 | 0 | 0 | 1350000 | 0 | 0
2021031512 | 2 | 0.64213 | 96319.5 | 0.58845 | 0 | 0.34092 | 4261.5 | 0.64863 | 51890.4 | 64000 | 4261.5 | 28058 | 0 | 0 | 1350000 | 0 | 0
2021031513 | 2 | 0.63398 | 95097 | 0.51236 | 0 | 0.31727 | 3965.875 | 0.64994 | 51995.2 | 64000 | 3965.875 | 27131.125 | 0 | 0 | 1350000 | 0 | 0
2021031514 | 2 | 0.62475 | 93712.5 | 0.44135 | 0 | 0.26883 | 3360.375 | 0.65911 | 52728.8 | 64000 | 3360.375 | 26352.125 | 0 | 0 | 1350000 | 0 | 0
2021031515 | 2 | 0.61455 | 92182.5 | 0.40356 | 0 | 0.19719 | 2464.875 | 0.67422 | 53937.6 | 64000 | 2464.875 | 25717.625 | 0 | 0 | 1350000 | 0 | 0
2021031516 | 2 | 0.60603 | 90904.5 | 0.342 | 0 | 0.17285 | 2160.625 | 0.6662 | 53296 | 64000 | 2160.625 | 24743.875 | 0 | 0 | 1350000 | 0 | 0
2021031517 | 2 | 0.60943 | 91414.5 | 0.29193 | 0 | 0.24841 | 3105.125 | 0.56546 | 45236.8 | 64000 | 3105.125 | 24309.375 | 0 | 0 | 1350000 | 0 | 0
2021031518 | 2 | 0.62244 | 93366 | 0.28547 | 0 | 0.31565 | 3945.625 | 0.27461 | 21968.8 | 64000 | 3945.625 | 21968.8 | 3451.575 | 3451.575 | 1350000 | 3451.575 | 0
2021031519 | 2 | 0.63743 | 95614.5 | 0.2615 | 0 | 0.363 | 4537.5 | 0.02823 | 2258.4 | 64000 | 4537.5 | 2258.4 | 24818.6 | 21367.025 | 1350000 | 24818.6 | 0
2021031520 | 2 | 0.65534 | 98301 | 0.23489 | 0 | 0.43394 | 5424.25 | 0 | 0 | 64000 | 5424.25 | 0 | 28876.75 | 4058.15 | 1346589.5 | 28876.75 | 0
2021031521 | 2 | 0.65605 | 98407.5 | 0.26921 | 0 | 0.50979 | 6372.375 | 0 | 0 | 64000 | 6372.375 | 0 | 28035.125 | -841.625 | 1344020.625 | 28035.125 | 0
2021031522 | 2 | 0.63542 | 95313 | 0.33364 | 0 | 0.53777 | 6722.125 | 0 | 0 | 64000 | 6722.125 | 0 | 24590.875 | -3444.25 | 1344896 | 24590.875 | 0
2021031523 | 2 | 0.60348 | 90522 | 0.52499 | 0 | 0.53059 | 6632.375 | 0 | 0 | 64000 | 6632.375 | 0 | 19889.625 | -4701.25 | 1350000 | 19889.625 | 0
2021031524 | 2 | 0.57208 | 85812 | 0.61574 | 0 | 0.50553 | 6319.125 | 0 | 0 | 64000 | 6319.125 | 0 | 15492.875 | -4396.75 | 1350000 | 15492.875 | 0
2021031601 | 3 | 0.54877 | 82315.5 | 0.68452 | 0 | 0.49284 | 6160.5 | 0 | 0 | 64000 | 6160.5 | 0 | 12155 | -3337.875 | 1350000 | 12155 | 0
2021031602 | 3 | 0.53513 | 80269.5 | 0.59906 | 0 | 0.46809 | 5851.125 | 0 | 0 | 64000 | 5851.125 | 0 | 10418.375 | -1736.625 | 1350000 | 10418.375 | 0
2021031603 | 3 | 0.5296 | 79440 | 0.63062 | 0 | 0.45916 | 5739.5 | 0 | 0 | 64000 | 5739.5 | 0 | 9700.5 | -717.875 | 1350000 | 9700.5 | 0
2021031604 | 3 | 0.53013 | 79519.5 | 0.55736 | 0 | 0.43309 | 5413.625 | 0 | 0 | 64000 | 5413.625 | 0 | 10105.875 | 405.375 | 1350000 | 10105.875 | 0
2021031605 | 3 | 0.53917 | 80875.5 | 0.46633 | 0 | 0.35976 | 4497 | 0 | 0 | 64000 | 4497 | 0 | 12378.5 | 2272.625 | 1350000 | 12378.5 | 0
2021031606 | 3 | 0.56717 | 85075.5 | 0.53643 | 0 | 0.27654 | 3456.75 | 0 | 0 | 64000 | 3456.75 | 0 | 17618.75 | 5240.25 | 1350000 | 17618.75 | 0
2021031607 | 3 | 0.61032 | 91548 | 0.57577 | 0 | 0.20528 | 2566 | 0 | 0 | 64000 | 2566 | 0 | 24982 | 7363.25 | 1350000 | 24982 | 0
2021031608 | 3 | 0.64685 | 97027.5 | 0.63267 | 0 | 0.19717 | 2464.625 | 0.00739 | 591.2 | 64000 | 2464.625 | 591.2 | 29971.675 | 4989.675 | 1345494.575 | 29971.675 | 0
2021031609 | 3 | 0.65857 | 98785.5 | 0.73459 | 0 | 0.23128 | 2891 | 0.20229 | 16183.2 | 64000 | 2891 | 16183.2 | 15711.3 | -14260.375 | 1350000 | 15711.3 | 0
2021031610 | 3 | 0.65874 | 98811 | 0.71605 | 0 | 0.26228 | 3278.5 | 0.51464 | 41171.2 | 64000 | 3278.5 | 31532.5 | 0 | -15711.3 | 1350000 | 0 | 0
2021031611 | 3 | 0.65478 | 98217 | 0.656 | 0 | 0.26566 | 3320.75 | 0.62701 | 50160.8 | 64000 | 3320.75 | 30896.25 | 0 | 0 | 1350000 | 0 | 0
2021031612 | 3 | 0.6493 | 97395 | 0.71617 | 0 | 0.2456 | 3070 | 0.63568 | 50854.4 | 64000 | 3070 | 30325 | 0 | 0 | 1350000 | 0 | 0
2021031613 | 3 | 0.64225 | 96337.5 | 0.64368 | 0 | 0.21777 | 2722.125 | 0.60551 | 48440.8 | 64000 | 2722.125 | 29615.375 | 0 | 0 | 1350000 | 0 | 0
2021031614 | 3 | 0.63422 | 95133 | 0.61965 | 0 | 0.19636 | 2454.5 | 0.62841 | 50272.8 | 64000 | 2454.5 | 28678.5 | 0 | 0 | 1350000 | 0 | 0
2021031615 | 3 | 0.62268 | 93402 | 0.65042 | 0 | 0.18502 | 2312.75 | 0.66059 | 52847.2 | 64000 | 2312.75 | 27089.25 | 0 | 0 | 1350000 | 0 | 0
2021031616 | 3 | 0.61466 | 92199 | 0.64514 | 0 | 0.17216 | 2152 | 0.68057 | 54445.6 | 64000 | 2152 | 26047 | 0 | 0 | 1350000 | 0 | 0
2021031617 | 3 | 0.61173 | 91759.5 | 0.61018 | 0 | 0.18892 | 2361.5 | 0.59732 | 47785.6 | 64000 | 2361.5 | 25398 | 0 | 0 | 1350000 | 0 | 0
2021031618 | 3 | 0.6154 | 92310 | 0.63911 | 0 | 0.22623 | 2827.875 | 0.27584 | 22067.2 | 64000 | 2827.875 | 22067.2 | 3414.925 | 3414.925 | 1350000 | 3414.925 | 0
2021031619 | 3 | 0.6179 | 92685 | 0.5754 | 0 | 0.25782 | 3222.75 | 0.03676 | 2940.8 | 64000 | 3222.75 | 2940.8 | 22521.45 | 19106.525 | 1350000 | 22521.45 | 0
2021031620 | 3 | 0.62712 | 94068 | 0.44625 | 0 | 0.2675 | 3343.75 | 0.00016 | 12.8 | 64000 | 3343.75 | 12.8 | 26711.45 | 4190 | 1348754.8 | 26711.45 | 0
2021031621 | 3 | 0.62824 | 94236 | 0.45906 | 0 | 0.27617 | 3452.125 | 0 | 0 | 64000 | 3452.125 | 0 | 26783.875 | 72.425 | 1347437.175 | 26783.875 | 0
2021031622 | 3 | 0.60727 | 91090.5 | 0.46643 | 0 | 0.28115 | 3514.375 | 0 | 0 | 64000 | 3514.375 | 0 | 23576.125 | -3207.75 | 1349327.3 | 23576.125 | 0
2021031623 | 3 | 0.57582 | 86373 | 0.45332 | 0 | 0.28156 | 3519.5 | 0 | 0 | 64000 | 3519.5 | 0 | 18853.5 | -4722.625 | 1350000 | 18853.5 | 0
2021031624 | 3 | 0.54535 | 81802.5 | 0.41504 | 0 | 0.27219 | 3402.375 | 0 | 0 | 64000 | 3402.375 | 0 | 14400.125 | -4453.375 | 1350000 | 14400.125 | 0
2021031701 | 4 | 0.52236 | 78354 | 0.30898 | 0 | 0.25997 | 3249.625 | 0 | 0 | 64000 | 3249.625 | 0 | 11104.375 | -3295.75 | 1350000 | 11104.375 | 0
2021031702 | 4 | 0.5104 | 76560 | 0.25182 | 0 | 0.24849 | 3106.125 | 0 | 0 | 64000 | 3106.125 | 0 | 9453.875 | -1650.5 | 1350000 | 9453.875 | 0
2021031703 | 4 | 0.5045 | 75675 | 0.18583 | 0 | 0.24998 | 3124.75 | 0 | 0 | 64000 | 3124.75 | 0 | 8550.25 | -903.625 | 1350000 | 8550.25 | 0
2021031704 | 4 | 0.50434 | 75651 | 0.13104 | 0 | 0.26392 | 3299 | 0 | 0 | 64000 | 3299 | 0 | 8352 | -198.25 | 1350000 | 8352 | 0
2021031705 | 4 | 0.51581 | 77371.5 | 0.07824 | 0 | 0.27798 | 3474.75 | 0 | 0 | 64000 | 3474.75 | 0 | 9896.75 | 1544.75 | 1350000 | 9896.75 | 0
2021031706 | 4 | 0.54334 | 81501 | 0.03457 | 0 | 0.27711 | 3463.875 | 0 | 0 | 64000 | 3463.875 | 0 | 14037.125 | 4140.375 | 1350000 | 14037.125 | 0
2021031707 | 4 | 0.58921 | 88381.5 | 0.0155 | 0 | 0.26903 | 3362.875 | 0 | 0 | 64000 | 3362.875 | 0 | 21018.625 | 6981.5 | 1350000 | 21018.625 | 0
2021031708 | 4 | 0.62561 | 93841.5 | 0.00033 | 0 | 0.29132 | 3641.5 | 0.00812 | 649.6 | 64000 | 3641.5 | 649.6 | 25550.4 | 4531.775 | 1349915.85 | 25550.4 | 0
2021031709 | 4 | 0.6378 | 95670 | 0.00526 | 0 | 0.35428 | 4428.5 | 0.15732 | 12585.6 | 64000 | 4428.5 | 12585.6 | 14655.9 | -10894.5 | 1350000 | 14655.9 | 0
2021031710 | 4 | 0.63667 | 95500.5 | 0.00519 | 0 | 0.38513 | 4814.125 | 0.3715 | 29720 | 64000 | 4814.125 | 26686.375 | 0 | -14655.9 | 1350000 | 0 | 0
2021031711 | 4 | 0.62938 | 94407 | 0.00326 | 0 | 0.39718 | 4964.75 | 0.52145 | 41716 | 64000 | 4964.75 | 25442.25 | 0 | 0 | 1350000 | 0 | 0
2021031712 | 4 | 0.61834 | 92751 | 0.00755 | 0 | 0.36742 | 4592.75 | 0.57803 | 46242.4 | 64000 | 4592.75 | 24158.25 | 0 | 0 | 1350000 | 0 | 0
2021031713 | 4 | 0.60799 | 91198.5 | 0.00188 | 0 | 0.32649 | 4081.125 | 0.60009 | 48007.2 | 64000 | 4081.125 | 23117.375 | 0 | 0 | 1350000 | 0 | 0
2021031714 | 4 | 0.59641 | 89461.5 | 0.03303 | 0 | 0.29738 | 3717.25 | 0.64045 | 51236 | 64000 | 3717.25 | 21744.25 | 0 | 0 | 1350000 | 0 | 0
2021031715 | 4 | 0.58792 | 88188 | 0.10524 | 0 | 0.25258 | 3157.25 | 0.67803 | 54242.4 | 64000 | 3157.25 | 21030.75 | 0 | 0 | 1350000 | 0 | 0
2021031716 | 4 | 0.5795 | 86925 | 0.1311 | 0 | 0.2505 | 3131.25 | 0.68665 | 54932 | 64000 | 3131.25 | 19793.75 | 0 | 0 | 1350000 | 0 | 0
2021031717 | 4 | 0.57867 | 86800.5 | 0.17793 | 0 | 0.3296 | 4120 | 0.59736 | 47788.8 | 64000 | 4120 | 18680.5 | 0 | 0 | 1350000 | 0 | 0
2021031718 | 4 | 0.58095 | 87142.5 | 0.25443 | 0 | 0.41092 | 5136.5 | 0.29646 | 23716.8 | 64000 | 5136.5 | 18006 | 0 | 0 | 1350000 | 0 | 0
2021031719 | 4 | 0.58682 | 88023 | 0.41015 | 0 | 0.44919 | 5614.875 | 0.03368 | 2694.4 | 64000 | 5614.875 | 2694.4 | 15713.725 | 15713.725 | 1350000 | 15713.725 | 0
2021031720 | 4 | 0.59868 | 89802 | 0.5047 | 0 | 0.46968 | 5871 | 3e-05 | 2.4 | 64000 | 5871 | 2.4 | 19928.6 | 4214.875 | 1350000 | 19928.6 | 0
2021031721 | 4 | 0.59956 | 89934 | 0.47001 | 0 | 0.48784 | 6098 | 0 | 0 | 64000 | 6098 | 0 | 19836 | -92.6 | 1350000 | 19836 | 0
2021031722 | 4 | 0.57966 | 86949 | 0.46117 | 0 | 0.50382 | 6297.75 | 0 | 0 | 64000 | 6297.75 | 0 | 16651.25 | -3184.75 | 1350000 | 16651.25 | 0
2021031723 | 4 | 0.55122 | 82683 | 0.65841 | 0 | 0.50032 | 6254 | 0 | 0 | 64000 | 6254 | 0 | 12429 | -4222.25 | 1350000 | 12429 | 0
2021031724 | 4 | 0.52204 | 78306 | 0.81379 | 0 | 0.49227 | 6153.375 | 0 | 0 | 64000 | 6153.375 | 0 | 8152.625 | -4276.375 | 1350000 | 8152.625 | 0
2021031801 | 5 | 0.49881 | 74821.5 | 0.78357 | 0 | 0.50549 | 6318.625 | 0 | 0 | 64000 | 6318.625 | 0 | 4502.875 | -3649.75 | 1350000 | 4502.875 | 0
2021031802 | 5 | 0.48576 | 72864 | 0.73478 | 0 | 0.51285 | 6410.625 | 0 | 0 | 64000 | 6410.625 | 0 | 2453.375 | -2049.5 | 1350000 | 2453.375 | 0
2021031803 | 5 | 0.47941 | 71911.5 | 0.72298 | 0 | 0.52781 | 6597.625 | 0 | 0 | 64000 | 6597.625 | 0 | 1313.875 | -1139.5 | 1350000 | 1313.875 | 0
2021031804 | 5 | 0.47831 | 71746.5 | 0.70123 | 0 | 0.52181 | 6522.625 | 0 | 0 | 64000 | 6522.625 | 0 | 1223.875 | -90 | 1350000 | 1223.875 | 0
2021031805 | 5 | 0.4876 | 73140 | 0.72613 | 0 | 0.50001 | 6250.125 | 0 | 0 | 64000 | 6250.125 | 0 | 2889.875 | 1666 | 1350000 | 2889.875 | 0
2021031806 | 5 | 0.51313 | 76969.5 | 0.70963 | 0 | 0.45581 | 5697.625 | 0 | 0 | 64000 | 5697.625 | 0 | 7271.875 | 4382 | 1350000 | 7271.875 | 0
2021031807 | 5 | 0.55785 | 83677.5 | 0.67764 | 0 | 0.43643 | 5455.375 | 0 | 0 | 64000 | 5455.375 | 0 | 14222.125 | 6950.25 | 1350000 | 14222.125 | 0
2021031808 | 5 | 0.59635 | 89452.5 | 0.65477 | 0 | 0.54979 | 6872.375 | 0.00161 | 128.8 | 64000 | 6872.375 | 128.8 | 18451.325 | 4229.2 | 1350000 | 18451.325 | 0
2021031809 | 5 | 0.61249 | 91873.5 | 0.54171 | 0 | 0.65664 | 8208 | 0.0446 | 3568 | 64000 | 8208 | 3568 | 16097.5 | -2353.825 | 1350000 | 16097.5 | 0
2021031810 | 5 | 0.62017 | 93025.5 | 0.53377 | 0 | 0.66958 | 8369.75 | 0.18219 | 14575.2 | 64000 | 8369.75 | 14575.2 | 6080.55 | -10016.95 | 1350000 | 6080.55 | 0
2021031811 | 5 | 0.62679 | 94018.5 | 0.44517 | 0 | 0.68348 | 8543.5 | 0.32707 | 26165.6 | 64000 | 8543.5 | 21475 | 0 | -6080.55 | 1350000 | 0 | 0
2021031812 | 5 | 0.62809 | 94213.5 | 0.36968 | 0 | 0.69115 | 8639.375 | 0.40059 | 32047.2 | 64000 | 8639.375 | 21574.125 | 0 | 0 | 1350000 | 0 | 0
2021031813 | 5 | 0.62519 | 93778.5 | 0.32223 | 0 | 0.67207 | 8400.875 | 0.49611 | 39688.8 | 64000 | 8400.875 | 21377.625 | 0 | 0 | 1350000 | 0 | 0
2021031814 | 5 | 0.61996 | 92994 | 0.36289 | 0 | 0.62596 | 7824.5 | 0.53678 | 42942.4 | 64000 | 7824.5 | 21169.5 | 0 | 0 | 1350000 | 0 | 0
2021031815 | 5 | 0.61141 | 91711.5 | 0.41662 | 0 | 0.55228 | 6903.5 | 0.60563 | 48450.4 | 64000 | 6903.5 | 20808 | 0 | 0 | 1350000 | 0 | 0
2021031816 | 5 | 0.60336 | 90504 | 0.51485 | 0 | 0.45635 | 5704.375 | 0.56931 | 45544.8 | 64000 | 5704.375 | 20799.625 | 0 | 0 | 1350000 | 0 | 0
2021031817 | 5 | 0.60086 | 90129 | 0.57128 | 0 | 0.42742 | 5342.75 | 0.46469 | 37175.2 | 64000 | 5342.75 | 20786.25 | 0 | 0 | 1350000 | 0 | 0
2021031818 | 5 | 0.60543 | 90814.5 | 0.78839 | 0 | 0.42692 | 5336.5 | 0.22483 | 17986.4 | 64000 | 5336.5 | 17986.4 | 3491.6 | 3491.6 | 1350000 | 3491.6 | 0
2021031819 | 5 | 0.6066 | 90990 | 0.86916 | 0 | 0.42694 | 5336.75 | 0.02198 | 1758.4 | 64000 | 5336.75 | 1758.4 | 19894.85 | 16403.25 | 1350000 | 19894.85 | 0
2021031820 | 5 | 0.61405 | 92107.5 | 0.92208 | 0 | 0.41812 | 5226.5 | 0 | 0 | 64000 | 5226.5 | 0 | 22881 | 2986.15 | 1350000 | 22881 | 0
2021031821 | 5 | 0.61205 | 91807.5 | 0.8992 | 0 | 0.428 | 5350 | 0 | 0 | 64000 | 5350 | 0 | 22457.5 | -423.5 | 1350000 | 22457.5 | 0
2021031822 | 5 | 0.59453 | 89179.5 | 0.81766 | 0 | 0.46938 | 5867.25 | 0 | 0 | 64000 | 5867.25 | 0 | 19312.25 | -3145.25 | 1350000 | 19312.25 | 0
2021031823 | 5 | 0.56657 | 84985.5 | 0.83316 | 0 | 0.46983 | 5872.875 | 0 | 0 | 64000 | 5872.875 | 0 | 15112.625 | -4199.625 | 1350000 | 15112.625 | 0
2021031824 | 5 | 0.53765 | 80647.5 | 0.85211 | 0 | 0.46235 | 5779.375 | 0 | 0 | 64000 | 5779.375 | 0 | 10868.125 | -4244.5 | 1350000 | 10868.125 | 0
2021031901 | 6 | 0.51708 | 77562 | 0.823 | 0 | 0.45657 | 5707.125 | 0 | 0 | 64000 | 5707.125 | 0 | 7854.875 | -3013.25 | 1350000 | 7854.875 | 0
2021031902 | 6 | 0.50654 | 75981 | 0.82899 | 0 | 0.45726 | 5715.75 | 0 | 0 | 64000 | 5715.75 | 0 | 6265.25 | -1589.625 | 1350000 | 6265.25 | 0
2021031903 | 6 | 0.50322 | 75483 | 0.83527 | 0 | 0.3671 | 4588.75 | 0 | 0 | 64000 | 4588.75 | 0 | 6894.25 | 629 | 1350000 | 6894.25 | 0
2021031904 | 6 | 0.50518 | 75777 | 0.85241 | 0 | 0.2863 | 3578.75 | 0 | 0 | 64000 | 3578.75 | 0 | 8198.25 | 1304 | 1350000 | 8198.25 | 0
2021031905 | 6 | 0.51887 | 77830.5 | 0.8542 | 0 | 0.25736 | 3217 | 0 | 0 | 64000 | 3217 | 0 | 10613.5 | 2415.25 | 1350000 | 10613.5 | 0
2021031906 | 6 | 0.55003 | 82504.5 | 0.83669 | 0 | 0.21774 | 2721.75 | 0 | 0 | 64000 | 2721.75 | 0 | 15782.75 | 5169.25 | 1350000 | 15782.75 | 0
2021031907 | 6 | 0.60118 | 90177 | 0.83568 | 0 | 0.20893 | 2611.625 | 0 | 0 | 64000 | 2611.625 | 0 | 23565.375 | 7782.625 | 1350000 | 23565.375 | 0
2021031908 | 6 | 0.64056 | 96084 | 0.82192 | 0 | 0.23045 | 2880.625 | 0.00623 | 498.4 | 64000 | 2880.625 | 498.4 | 28704.975 | 5139.6 | 1346761.275 | 28704.975 | 0
2021031909 | 6 | 0.65382 | 98073 | 0.81755 | 0 | 0.25011 | 3126.375 | 0.16845 | 13476 | 64000 | 3126.375 | 13476 | 17470.625 | -11234.35 | 1350000 | 17470.625 | 0
2021031910 | 6 | 0.65018 | 97527 | 0.82871 | 0 | 0.22478 | 2809.75 | 0.41719 | 33375.2 | 64000 | 2809.75 | 30717.25 | 0 | -17470.625 | 1350000 | 0 | 0
2021031911 | 6 | 0.63825 | 95737.5 | 0.81614 | 0 | 0.20679 | 2584.875 | 0.47157 | 37725.6 | 64000 | 2584.875 | 29152.625 | 0 | 0 | 1350000 | 0 | 0
2021031912 | 6 | 0.62656 | 93984 | 0.74525 | 0 | 0.1841 | 2301.25 | 0.52724 | 42179.2 | 64000 | 2301.25 | 27682.75 | 0 | 0 | 1350000 | 0 | 0
2021031913 | 6 | 0.61079 | 91618.5 | 0.70486 | 0 | 0.14574 | 1821.75 | 0.55105 | 44084 | 64000 | 1821.75 | 25796.75 | 0 | 0 | 1350000 | 0 | 0
2021031914 | 6 | 0.59693 | 89539.5 | 0.65636 | 0 | 0.10178 | 1272.25 | 0.5439 | 43512 | 64000 | 1272.25 | 24267.25 | 0 | 0 | 1350000 | 0 | 0
2021031915 | 6 | 0.57967 | 86950.5 | 0.6281 | 0 | 0.08786 | 1098.25 | 0.54967 | 43973.6 | 64000 | 1098.25 | 21852.25 | 0 | 0 | 1350000 | 0 | 0
2021031916 | 6 | 0.5649 | 84735 | 0.57963 | 0 | 0.10123 | 1265.375 | 0.51566 | 41252.8 | 64000 | 1265.375 | 19469.625 | 0 | 0 | 1350000 | 0 | 0
2021031917 | 6 | 0.55685 | 83527.5 | 0.54923 | 0 | 0.10634 | 1329.25 | 0.46647 | 37317.6 | 64000 | 1329.25 | 18198.25 | 0 | 0 | 1350000 | 0 | 0
2021031918 | 6 | 0.55907 | 83860.5 | 0.50191 | 0 | 0.13161 | 1645.125 | 0.2091 | 16728 | 64000 | 1645.125 | 16728 | 1487.375 | 1487.375 | 1350000 | 1487.375 | 0
2021031919 | 6 | 0.57046 | 85569 | 0.50148 | 0 | 0.1146 | 1432.5 | 0.02147 | 1717.6 | 64000 | 1432.5 | 1717.6 | 18418.9 | 16931.525 | 1350000 | 18418.9 | 0
2021031920 | 6 | 0.59308 | 88962 | 0.45212 | 0 | 0.09775 | 1221.875 | 0 | 0 | 64000 | 1221.875 | 0 | 23740.125 | 5321.225 | 1350000 | 23740.125 | 0
2021031921 | 6 | 0.6102 | 91530 | 0.47294 | 0 | 0.09439 | 1179.875 | 0 | 0 | 64000 | 1179.875 | 0 | 26350.125 | 2610 | 1349116.125 | 26350.125 | 0
2021031922 | 6 | 0.60467 | 90700.5 | 0.47235 | 0 | 0.07691 | 961.375 | 0 | 0 | 64000 | 961.375 | 0 | 25739.125 | -611 | 1348843.25 | 25739.125 | 0
2021031923 | 6 | 0.58709 | 88063.5 | 0.45676 | 0 | 0.051 | 637.5 | 0 | 0 | 64000 | 637.5 | 0 | 23426 | -2313.125 | 1350000 | 23426 | 0
2021031924 | 6 | 0.56594 | 84891 | 0.41297 | 0 | 0.04278 | 534.75 | 0 | 0 | 64000 | 534.75 | 0 | 20356.25 | -3069.75 | 1350000 | 20356.25 | 0
2021032001 | 7 | 0.54871 | 82306.5 | 0.35514 | 0 | 0.03488 | 436 | 0 | 0 | 64000 | 436 | 0 | 17870.5 | -2485.75 | 1350000 | 17870.5 | 0
2021032002 | 7 | 0.53956 | 80934 | 0.30793 | 0 | 0.03084 | 385.5 | 0 | 0 | 64000 | 385.5 | 0 | 16548.5 | -1322 | 1350000 | 16548.5 | 0
2021032003 | 7 | 0.53729 | 80593.5 | 0.30478 | 0 | 0.02829 | 353.625 | 0 | 0 | 64000 | 353.625 | 0 | 16239.875 | -308.625 | 1350000 | 16239.875 | 0
2021032004 | 7 | 0.53961 | 80941.5 | 0.34006 | 0 | 0.02018 | 252.25 | 0 | 0 | 64000 | 252.25 | 0 | 16689.25 | 449.375 | 1350000 | 16689.25 | 0
2021032005 | 7 | 0.54689 | 82033.5 | 0.39787 | 0 | 0.01963 | 245.375 | 0 | 0 | 64000 | 245.375 | 0 | 17788.125 | 1098.875 | 1350000 | 17788.125 | 0
2021032006 | 7 | 0.5619 | 84285 | 0.44438 | 0 | 0.03083 | 385.375 | 0 | 0 | 64000 | 385.375 | 0 | 19899.625 | 2111.5 | 1350000 | 19899.625 | 0
2021032007 | 7 | 0.58619 | 87928.5 | 0.42048 | 0 | 0.031 | 387.5 | 0 | 0 | 64000 | 387.5 | 0 | 23541 | 3641.375 | 1350000 | 23541 | 0
2021032008 | 7 | 0.6085 | 91275 | 0.43143 | 0 | 0.05439 | 679.875 | 0.00883 | 706.4 | 64000 | 679.875 | 706.4 | 25888.725 | 2347.725 | 1349577.525 | 25888.725 | 0
2021032009 | 7 | 0.61052 | 91578 | 0.36404 | 0 | 0.07008 | 876 | 0.17011 | 13608.8 | 64000 | 876 | 13608.8 | 13093.2 | -12795.525 | 1350000 | 13093.2 | 0
2021032010 | 7 | 0.59236 | 88854 | 0.25063 | 0 | 0.0801 | 1001.25 | 0.40179 | 32143.2 | 64000 | 1001.25 | 23852.75 | 0 | -13093.2 | 1350000 | 0 | 0
2021032011 | 7 | 0.5693 | 85395 | 0.18953 | 0 | 0.1066 | 1332.5 | 0.51002 | 40801.6 | 64000 | 1332.5 | 20062.5 | 0 | 0 | 1350000 | 0 | 0
2021032012 | 7 | 0.54668 | 82002 | 0.17226 | 0 | 0.1369 | 1711.25 | 0.55205 | 44164 | 64000 | 1711.25 | 16290.75 | 0 | 0 | 1350000 | 0 | 0
2021032013 | 7 | 0.52615 | 78922.5 | 0.11761 | 0 | 0.12408 | 1551 | 0.57692 | 46153.6 | 64000 | 1551 | 13371.5 | 0 | 0 | 1350000 | 0 | 0
2021032014 | 7 | 0.50694 | 76041 | 0.05882 | 0 | 0.12092 | 1511.5 | 0.57759 | 46207.2 | 64000 | 1511.5 | 10529.5 | 0 | 0 | 1350000 | 0 | 0
2021032015 | 7 | 0.49119 | 73678.5 | 0.03557 | 0 | 0.13866 | 1733.25 | 0.58738 | 46990.4 | 64000 | 1733.25 | 7945.25 | 0 | 0 | 1350000 | 0 | 0
2021032016 | 7 | 0.48254 | 72381 | 0.03227 | 0 | 0.12179 | 1522.375 | 0.55793 | 44634.4 | 64000 | 1522.375 | 6858.625 | 0 | 0 | 1350000 | 0 | 0
2021032017 | 7 | 0.48234 | 72351 | 0.02226 | 0 | 0.15132 | 1891.5 | 0.43346 | 34676.8 | 64000 | 1891.5 | 6459.5 | 0 | 0 | 1350000 | 0 | 0
2021032018 | 7 | 0.49143 | 73714.5 | 0.00986 | 0 | 0.19748 | 2468.5 | 0.18778 | 15022.4 | 64000 | 2468.5 | 7246 | 0 | 0 | 1350000 | 0 | 0
2021032019 | 7 | 0.50294 | 75441 | 0.00978 | 0 | 0.21095 | 2636.875 | 0.01887 | 1509.6 | 64000 | 2636.875 | 1509.6 | 7294.525 | 7294.525 | 1350000 | 7294.525 | 0
2021032020 | 7 | 0.52478 | 78717 | 0.02667 | 0 | 0.27869 | 3483.625 | 0 | 0 | 64000 | 3483.625 | 0 | 11233.375 | 3938.85 | 1350000 | 11233.375 | 0
2021032021 | 7 | 0.54366 | 81549 | 0.04871 | 0 | 0.30534 | 3816.75 | 0 | 0 | 64000 | 3816.75 | 0 | 13732.25 | 2498.875 | 1350000 | 13732.25 | 0
2021032022 | 7 | 0.54007 | 81010.5 | 0.10878 | 0 | 0.31033 | 3879.125 | 0 | 0 | 64000 | 3879.125 | 0 | 13131.375 | -600.875 | 1350000 | 13131.375 | 0
2021032023 | 7 | 0.5287 | 79305 | 0.15205 | 0 | 0.31368 | 3921 | 0 | 0 | 64000 | 3921 | 0 | 11384 | -1747.375 | 1350000 | 11384 | 0
2021032024 | 7 | 0.51299 | 76948.5 | 0.15527 | 0 | 0.32017 | 4002.125 | 0 | 0 | 64000 | 4002.125 | 0 | 8946.375 | -2437.625 | 1350000 | 8946.375 | 0
2021032101 | 1 | 0.50158 | 75237 | 0.18868 | 0 | 0.3554 | 4442.5 | 0 | 0 | 64000 | 4442.5 | 0 | 6794.5 | -2151.875 | 1350000 | 6794.5 | 0
2021032102 | 1 | 0.49615 | 74422.5 | 0.18522 | 0 | 0.39737 | 4967.125 | 0 | 0 | 64000 | 4967.125 | 0 | 5455.375 | -1339.125 | 1350000 | 5455.375 | 0
2021032103 | 1 | 0.4954 | 74310 | 0.20733 | 0 | 0.45122 | 5640.25 | 0 | 0 | 64000 | 5640.25 | 0 | 4669.75 | -785.625 | 1350000 | 4669.75 | 0
2021032104 | 1 | 0.49809 | 74713.5 | 0.19235 | 0 | 0.48931 | 6116.375 | 0 | 0 | 64000 | 6116.375 | 0 | 4597.125 | -72.625 | 1350000 | 4597.125 | 0
2021032105 | 1 | 0.50638 | 75957 | 0.19476 | 0 | 0.45559 | 5694.875 | 0 | 0 | 64000 | 5694.875 | 0 | 6262.125 | 1665 | 1350000 | 6262.125 | 0
2021032106 | 1 | 0.51891 | 77836.5 | 0.23915 | 0 | 0.43569 | 5446.125 | 0 | 0 | 64000 | 5446.125 | 0 | 8390.375 | 2128.25 | 1350000 | 8390.375 | 0
2021032107 | 1 | 0.53933 | 80899.5 | 0.28251 | 0 | 0.42091 | 5261.375 | 0 | 0 | 64000 | 5261.375 | 0 | 11638.125 | 3247.75 | 1350000 | 11638.125 | 0
2021032108 | 1 | 0.55627 | 83440.5 | 0.33514 | 0 | 0.39849 | 4981.125 | 0.01071 | 856.8 | 64000 | 4981.125 | 856.8 | 13602.575 | 1964.45 | 1350000 | 13602.575 | 0
2021032109 | 1 | 0.55668 | 83502 | 0.35156 | 0 | 0.3382 | 4227.5 | 0.11138 | 8910.4 | 64000 | 4227.5 | 8910.4 | 6364.1 | -7238.475 | 1350000 | 6364.1 | 0
2021032110 | 1 | 0.5388 | 80820 | 0.32205 | 0 | 0.31051 | 3881.375 | 0.19657 | 15725.6 | 64000 | 3881.375 | 12938.625 | 0 | -6364.1 | 1350000 | 0 | 0
2021032111 | 1 | 0.51504 | 77256 | 0.29093 | 0 | 0.30084 | 3760.5 | 0.26054 | 20843.2 | 64000 | 3760.5 | 9495.5 | 0 | 0 | 1350000 | 0 | 0
2021032112 | 1 | 0.50049 | 75073.5 | 0.20308 | 0 | 0.31856 | 3982 | 0.31009 | 24807.2 | 64000 | 3982 | 7091.5 | 0 | 0 | 1350000 | 0 | 0
2021032113 | 1 | 0.4865 | 72975 | 0.09569 | 0 | 0.33361 | 4170.125 | 0.32418 | 25934.4 | 64000 | 4170.125 | 4804.875 | 0 | 0 | 1350000 | 0 | 0
2021032114 | 1 | 0.47387 | 71080.5 | 0.08429 | 0 | 0.34817 | 4352.125 | 0.37986 | 30388.8 | 64000 | 4352.125 | 2728.375 | 0 | 0 | 1350000 | 0 | 0
2021032115 | 1 | 0.46202 | 69303 | 0.08708 | 0 | 0.26713 | 3339.125 | 0.37616 | 30092.8 | 64000 | 3339.125 | 1963.875 | 0 | 0 | 1350000 | 0 | 0
2021032116 | 1 | 0.45934 | 68901 | 0.06457 | 0 | 0.22114 | 2764.25 | 0.35244 | 28195.2 | 64000 | 2764.25 | 2136.75 | 0 | 0 | 1350000 | 0 | 0
2021032117 | 1 | 0.46531 | 69796.5 | 0.07599 | 0 | 0.24462 | 3057.75 | 0.23705 | 18964 | 64000 | 3057.75 | 2738.75 | 0 | 0 | 1350000 | 0 | 0
2021032118 | 1 | 0.47858 | 71787 | 0.11401 | 0 | 0.2204 | 2755 | 0.08981 | 7184.8 | 64000 | 2755 | 5032 | 0 | 0 | 1350000 | 0 | 0
2021032119 | 1 | 0.49244 | 73866 | 0.1874 | 0 | 0.17596 | 2199.5 | 0.00804 | 643.2 | 64000 | 2199.5 | 643.2 | 7023.3 | 7023.3 | 1350000 | 7023.3 | 0
2021032120 | 1 | 0.51503 | 77254.5 | 0.3108 | 0 | 0.14166 | 1770.75 | 0 | 0 | 64000 | 1770.75 | 0 | 11483.75 | 4460.45 | 1350000 | 11483.75 | 0
2021032121 | 1 | 0.53453 | 80179.5 | 0.51884 | 0 | 0.12853 | 1606.625 | 0 | 0 | 64000 | 1606.625 | 0 | 14572.875 | 3089.125 | 1350000 | 14572.875 | 0
2021032122 | 1 | 0.5233 | 78495 | 0.60723 | 0 | 0.10054 | 1256.75 | 0 | 0 | 64000 | 1256.75 | 0 | 13238.25 | -1334.625 | 1350000 | 13238.25 | 0
2021032123 | 1 | 0.50383 | 75574.5 | 0.63765 | 0 | 0.07993 | 999.125 | 0 | 0 | 64000 | 999.125 | 0 | 10575.375 | -2662.875 | 1350000 | 10575.375 | 0
2021032124 | 1 | 0.48432 | 72648 | 0.68118 | 0 | 0.06909 | 863.625 | 0 | 0 | 64000 | 863.625 | 0 | 7784.375 | -2791 | 1350000 | 7784.375 | 0
2021032201 | 2 | 0.47103 | 70654.5 | 0.68627 | 0 | 0.05783 | 722.875 | 0 | 0 | 64000 | 722.875 | 0 | 5931.625 | -1852.75 | 1350000 | 5931.625 | 0
2021032202 | 2 | 0.46669 | 70003.5 | 0.67913 | 0 | 0.04691 | 586.375 | 0 | 0 | 64000 | 586.375 | 0 | 5417.125 | -514.5 | 1350000 | 5417.125 | 0
2021032203 | 2 | 0.46835 | 70252.5 | 0.6769 | 0 | 0.04124 | 515.5 | 0 | 0 | 64000 | 515.5 | 0 | 5737 | 319.875 | 1350000 | 5737 | 0
2021032204 | 2 | 0.4755 | 71325 | 0.6397 | 0 | 0.04598 | 574.75 | 0 | 0 | 64000 | 574.75 | 0 | 6750.25 | 1013.25 | 1350000 | 6750.25 | 0
2021032205 | 2 | 0.49377 | 74065.5 | 0.56147 | 0 | 0.05083 | 635.375 | 0 | 0 | 64000 | 635.375 | 0 | 9430.125 | 2679.875 | 1350000 | 9430.125 | 0
2021032206 | 2 | 0.52924 | 79386 | 0.54653 | 0 | 0.05013 | 626.625 | 0 | 0 | 64000 | 626.625 | 0 | 14759.375 | 5329.25 | 1350000 | 14759.375 | 0
2021032207 | 2 | 0.5824 | 87360 | 0.46949 | 0 | 0.05621 | 702.625 | 0 | 0 | 64000 | 702.625 | 0 | 22657.375 | 7898 | 1350000 | 22657.375 | 0
2021032208 | 2 | 0.61885 | 92827.5 | 0.38567 | 0 | 0.09148 | 1143.5 | 0.00631 | 504.8 | 64000 | 1143.5 | 504.8 | 27179.2 | 4521.825 | 1348287.05 | 27179.2 | 0
2021032209 | 2 | 0.61594 | 92391 | 0.26969 | 0 | 0.13956 | 1744.5 | 0.07787 | 6229.6 | 64000 | 1744.5 | 6229.6 | 20416.9 | -6762.3 | 1350000 | 20416.9 | 0
2021032210 | 2 | 0.59261 | 88891.5 | 0.14366 | 0 | 0.15926 | 1990.75 | 0.15061 | 12048.8 | 64000 | 1990.75 | 12048.8 | 10851.95 | -9564.95 | 1350000 | 10851.95 | 0
2021032211 | 2 | 0.57041 | 85561.5 | 0.07503 | 0 | 0.17797 | 2224.625 | 0.2062 | 16496 | 64000 | 2224.625 | 16496 | 2840.875 | -8011.075 | 1350000 | 2840.875 | 0
2021032212 | 2 | 0.55554 | 83331 | 0.05686 | 0 | 0.20945 | 2618.125 | 0.27708 | 22166.4 | 64000 | 2618.125 | 16712.875 | 0 | -2840.875 | 1350000 | 0 | 0
2021032213 | 2 | 0.54435 | 81652.5 | 0.07178 | 0 | 0.24956 | 3119.5 | 0.28011 | 22408.8 | 64000 | 3119.5 | 14533 | 0 | 0 | 1350000 | 0 | 0
2021032214 | 2 | 0.53556 | 80334 | 0.07696 | 0 | 0.28714 | 3589.25 | 0.24256 | 19404.8 | 64000 | 3589.25 | 12744.75 | 0 | 0 | 1350000 | 0 | 0
2021032215 | 2 | 0.52724 | 79086 | 0.07168 | 0 | 0.31329 | 3916.125 | 0.21327 | 17061.6 | 64000 | 3916.125 | 11169.875 | 0 | 0 | 1350000 | 0 | 0
2021032216 | 2 | 0.52097 | 78145.5 | 0.08625 | 0 | 0.33891 | 4236.375 | 0.15537 | 12429.6 | 64000 | 4236.375 | 9909.125 | 0 | 0 | 1350000 | 0 | 0
2021032217 | 2 | 0.52115 | 78172.5 | 0.11935 | 0 | 0.33544 | 4193 | 0.12324 | 9859.2 | 64000 | 4193 | 9859.2 | 120.3 | 120.3 | 1350000 | 120.3 | 0
2021032218 | 2 | 0.52817 | 79225.5 | 0.15521 | 0 | 0.31324 | 3915.5 | 0.05456 | 4364.8 | 64000 | 3915.5 | 4364.8 | 6945.2 | 6824.9 | 1350000 | 6945.2 | 0
2021032219 | 2 | 0.53506 | 80259 | 0.20948 | 0 | 0.29501 | 3687.625 | 0.00637 | 509.6 | 64000 | 3687.625 | 509.6 | 12061.775 | 5116.575 | 1350000 | 12061.775 | 0
2021032220 | 2 | 0.5515 | 82725 | 0.34337 | 0 | 0.34145 | 4268.125 | 0 | 0 | 64000 | 4268.125 | 0 | 14456.875 | 2395.1 | 1350000 | 14456.875 | 0
2021032221 | 2 | 0.56142 | 84213 | 0.52325 | 0 | 0.42411 | 5301.375 | 0 | 0 | 64000 | 5301.375 | 0 | 14911.625 | 454.75 | 1350000 | 14911.625 | 0
2021032222 | 2 | 0.54471 | 81706.5 | 0.62544 | 0 | 0.47681 | 5960.125 | 0 | 0 | 64000 | 5960.125 | 0 | 11746.375 | -3165.25 | 1350000 | 11746.375 | 0
2021032223 | 2 | 0.51623 | 77434.5 | 0.68055 | 0 | 0.52289 | 6536.125 | 0 | 0 | 64000 | 6536.125 | 0 | 6898.375 | -4848 | 1350000 | 6898.375 | 0
2021032224 | 2 | 0.48913 | 73369.5 | 0.64712 | 0 | 0.5101 | 6376.25 | 0 | 0 | 64000 | 6376.25 | 0 | 2993.25 | -3905.125 | 1350000 | 2993.25 | 0
2021032301 | 3 | 0.47011 | 70516.5 | 0.67054 | 0 | 0.51554 | 6444.25 | 0 | 0 | 64000 | 6444.25 | 0 | 72.25 | -2921 | 1350000 | 72.25 | 0
2021032302 | 3 | 0.46111 | 69166.5 | 0.63947 | 0 | 0.50228 | 6278.5 | 0 | 0 | 64000 | 5166.5 | 0 | 0 | -72.25 | 1350000 | 0 | 0
2021032303 | 3 | 0.45819 | 68728.5 | 0.60326 | 0 | 0.46757 | 5844.625 | 0 | 0 | 64000 | 4728.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032304 | 3 | 0.462 | 69300 | 0.60036 | 0 | 0.4842 | 6052.5 | 0 | 0 | 64000 | 5300 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032305 | 3 | 0.47533 | 71299.5 | 0.55409 | 0 | 0.50279 | 6284.875 | 0 | 0 | 64000 | 6284.875 | 0 | 1014.625 | 1014.625 | 1350000 | 1014.625 | 0
2021032306 | 3 | 0.50502 | 75753 | 0.54149 | 0 | 0.46429 | 5803.625 | 0 | 0 | 64000 | 5803.625 | 0 | 5949.375 | 4934.75 | 1350000 | 5949.375 | 0
2021032307 | 3 | 0.55276 | 82914 | 0.51821 | 0 | 0.52418 | 6552.25 | 0 | 0 | 64000 | 6552.25 | 0 | 12361.75 | 6412.375 | 1350000 | 12361.75 | 0
2021032308 | 3 | 0.58665 | 87997.5 | 0.48542 | 0 | 0.54812 | 6851.5 | 0.00536 | 428.8 | 64000 | 6851.5 | 428.8 | 16717.2 | 4355.45 | 1350000 | 16717.2 | 0
2021032309 | 3 | 0.59009 | 88513.5 | 0.42599 | 0 | 0.48029 | 6003.625 | 0.06092 | 4873.6 | 64000 | 6003.625 | 4873.6 | 13636.275 | -3080.925 | 1350000 | 13636.275 | 0
2021032310 | 3 | 0.58069 | 87103.5 | 0.36189 | 0 | 0.48136 | 6017 | 0.1236 | 9888 | 64000 | 6017 | 9888 | 7198.5 | -6437.775 | 1350000 | 7198.5 | 0
2021032311 | 3 | 0.56643 | 84964.5 | 0.3864 | 0 | 0.46173 | 5771.625 | 0.16884 | 13507.2 | 64000 | 5771.625 | 13507.2 | 1685.675 | -5512.825 | 1350000 | 1685.675 | 0
2021032312 | 3 | 0.55509 | 83263.5 | 0.40733 | 0 | 0.45162 | 5645.25 | 0.2148 | 17184 | 64000 | 5645.25 | 13618.25 | 0 | -1685.675 | 1350000 | 0 | 0
2021032313 | 3 | 0.54561 | 81841.5 | 0.41312 | 0 | 0.47334 | 5916.75 | 0.25668 | 20534.4 | 64000 | 5916.75 | 11924.75 | 0 | 0 | 1350000 | 0 | 0
2021032314 | 3 | 0.54022 | 81033 | 0.48955 | 0 | 0.50737 | 6342.125 | 0.24862 | 19889.6 | 64000 | 6342.125 | 10690.875 | 0 | 0 | 1350000 | 0 | 0
2021032315 | 3 | 0.53384 | 80076 | 0.54359 | 0 | 0.4648 | 5810 | 0.21438 | 17150.4 | 64000 | 5810 | 10266 | 0 | 0 | 1350000 | 0 | 0
2021032316 | 3 | 0.52953 | 79429.5 | 0.604 | 0 | 0.42847 | 5355.875 | 0.17386 | 13908.8 | 64000 | 5355.875 | 10073.625 | 0 | 0 | 1350000 | 0 | 0
2021032317 | 3 | 0.53223 | 79834.5 | 0.65637 | 0 | 0.37673 | 4709.125 | 0.13787 | 11029.6 | 64000 | 4709.125 | 11029.6 | 95.775 | 95.775 | 1350000 | 95.775 | 0
2021032318 | 3 | 0.53873 | 80809.5 | 0.66695 | 0 | 0.37093 | 4636.625 | 0.05338 | 4270.4 | 64000 | 4636.625 | 4270.4 | 7902.475 | 7806.7 | 1350000 | 7902.475 | 0
2021032319 | 3 | 0.54437 | 81655.5 | 0.61505 | 0 | 0.37016 | 4627 | 0.00509 | 407.2 | 64000 | 4627 | 407.2 | 12621.3 | 4718.825 | 1350000 | 12621.3 | 0
2021032320 | 3 | 0.55776 | 83664 | 0.57142 | 0 | 0.40389 | 5048.625 | 0 | 0 | 64000 | 5048.625 | 0 | 14615.375 | 1994.075 | 1350000 | 14615.375 | 0
2021032321 | 3 | 0.56223 | 84334.5 | 0.67268 | 0 | 0.46632 | 5829 | 0 | 0 | 64000 | 5829 | 0 | 14505.5 | -109.875 | 1350000 | 14505.5 | 0
2021032322 | 3 | 0.54333 | 81499.5 | 0.8061 | 0 | 0.54587 | 6823.375 | 0 | 0 | 64000 | 6823.375 | 0 | 10676.125 | -3829.375 | 1350000 | 10676.125 | 0
2021032323 | 3 | 0.51263 | 76894.5 | 0.90276 | 0 | 0.57411 | 7176.375 | 0 | 0 | 64000 | 7176.375 | 0 | 5718.125 | -4958 | 1350000 | 5718.125 | 0
2021032324 | 3 | 0.48208 | 72312 | 0.90196 | 0 | 0.60521 | 7565.125 | 0 | 0 | 64000 | 7565.125 | 0 | 746.875 | -4971.25 | 1350000 | 746.875 | 0
2021032401 | 4 | 0.45932 | 68898 | 0.90282 | 0 | 0.61179 | 7647.375 | 0 | 0 | 64000 | 4898 | 0 | 0 | -746.875 | 1350000 | 0 | 0
2021032402 | 4 | 0.44635 | 66952.5 | 0.93118 | 0 | 0.61409 | 7676.125 | 0 | 0 | 64000 | 2952.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032403 | 4 | 0.43847 | 65770.5 | 0.84912 | 0 | 0.60613 | 7576.625 | 0 | 0 | 64000 | 1770.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032404 | 4 | 0.43621 | 65431.5 | 0.87359 | 0 | 0.58011 | 7251.375 | 0 | 0 | 64000 | 1431.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032405 | 4 | 0.4443 | 66645 | 0.74637 | 0 | 0.55049 | 6881.125 | 0 | 0 | 64000 | 2645 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032406 | 4 | 0.46719 | 70078.5 | 0.73028 | 0 | 0.49863 | 6232.875 | 0 | 0 | 64000 | 6078.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032407 | 4 | 0.51002 | 76503 | 0.73814 | 0 | 0.41102 | 5137.75 | 0 | 0 | 64000 | 5137.75 | 0 | 7365.25 | 7365.25 | 1350000 | 7365.25 | 0
2021032408 | 4 | 0.54417 | 81625.5 | 0.70634 | 0 | 0.39222 | 4902.75 | 0.01538 | 1230.4 | 64000 | 4902.75 | 1230.4 | 11492.35 | 4127.1 | 1350000 | 11492.35 | 0
2021032409 | 4 | 0.55918 | 83877 | 0.66885 | 0 | 0.41476 | 5184.5 | 0.16745 | 13396 | 64000 | 5184.5 | 13396 | 1296.5 | -10195.85 | 1350000 | 1296.5 | 0
2021032410 | 4 | 0.56469 | 84703.5 | 0.63729 | 0 | 0.38941 | 4867.625 | 0.31203 | 24962.4 | 64000 | 4867.625 | 15835.875 | 0 | -1296.5 | 1350000 | 0 | 0
2021032411 | 4 | 0.56749 | 85123.5 | 0.54108 | 0 | 0.35431 | 4428.875 | 0.35006 | 28004.8 | 64000 | 4428.875 | 16694.625 | 0 | 0 | 1350000 | 0 | 0
2021032412 | 4 | 0.56972 | 85458 | 0.55325 | 0 | 0.31225 | 3903.125 | 0.3316 | 26528 | 64000 | 3903.125 | 17554.875 | 0 | 0 | 1350000 | 0 | 0
2021032413 | 4 | 0.56912 | 85368 | 0.47643 | 0 | 0.32954 | 4119.25 | 0.34141 | 27312.8 | 64000 | 4119.25 | 17248.75 | 0 | 0 | 1350000 | 0 | 0
2021032414 | 4 | 0.56873 | 85309.5 | 0.38028 | 0 | 0.41643 | 5205.375 | 0.33096 | 26476.8 | 64000 | 5205.375 | 16104.125 | 0 | 0 | 1350000 | 0 | 0
2021032415 | 4 | 0.56409 | 84613.5 | 0.33611 | 0 | 0.50909 | 6363.625 | 0.26257 | 21005.6 | 64000 | 6363.625 | 14249.875 | 0 | 0 | 1350000 | 0 | 0
2021032416 | 4 | 0.5585 | 83775 | 0.49125 | 0 | 0.50496 | 6312 | 0.18517 | 14813.6 | 64000 | 6312 | 13463 | 0 | 0 | 1350000 | 0 | 0
2021032417 | 4 | 0.55864 | 83796 | 0.61594 | 0 | 0.49604 | 6200.5 | 0.09573 | 7658.4 | 64000 | 6200.5 | 7658.4 | 5937.1 | 5937.1 | 1350000 | 5937.1 | 0
2021032418 | 4 | 0.56035 | 84052.5 | 0.57956 | 0 | 0.52235 | 6529.375 | 0.03091 | 2472.8 | 64000 | 6529.375 | 2472.8 | 11050.325 | 5113.225 | 1350000 | 11050.325 | 0
2021032419 | 4 | 0.55845 | 83767.5 | 0.65404 | 0 | 0.52375 | 6546.875 | 0.003 | 240 | 64000 | 6546.875 | 240 | 12980.625 | 1930.3 | 1350000 | 12980.625 | 0
2021032420 | 4 | 0.56221 | 84331.5 | 0.66867 | 0 | 0.51489 | 6436.125 | 0 | 0 | 64000 | 6436.125 | 0 | 13895.375 | 914.75 | 1350000 | 13895.375 | 0
2021032421 | 4 | 0.56498 | 84747 | 0.66462 | 0 | 0.51808 | 6476 | 0 | 0 | 64000 | 6476 | 0 | 14271 | 375.625 | 1350000 | 14271 | 0
2021032422 | 4 | 0.54447 | 81670.5 | 0.58466 | 0 | 0.50157 | 6269.625 | 0 | 0 | 64000 | 6269.625 | 0 | 11400.875 | -2870.125 | 1350000 | 11400.875 | 0
2021032423 | 4 | 0.51303 | 76954.5 | 0.53018 | 0 | 0.50285 | 6285.625 | 0 | 0 | 64000 | 6285.625 | 0 | 6668.875 | -4732 | 1350000 | 6668.875 | 0
2021032424 | 4 | 0.48163 | 72244.5 | 0.5035 | 0 | 0.48868 | 6108.5 | 0 | 0 | 64000 | 6108.5 | 0 | 2136 | -4532.875 | 1350000 | 2136 | 0
2021032501 | 5 | 0.45871 | 68806.5 | 0.44663 | 0 | 0.46432 | 5804 | 0 | 0 | 64000 | 4806.5 | 0 | 0 | -2136 | 1350000 | 0 | 0
2021032502 | 5 | 0.44424 | 66636 | 0.42771 | 0 | 0.51454 | 6431.75 | 0 | 0 | 64000 | 2636 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032503 | 5 | 0.43692 | 65538 | 0.42849 | 0 | 0.53723 | 6715.375 | 0 | 0 | 64000 | 1538 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032504 | 5 | 0.43426 | 65139 | 0.39923 | 0 | 0.52841 | 6605.125 | 0 | 0 | 64000 | 1139 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032505 | 5 | 0.44349 | 66523.5 | 0.33137 | 0 | 0.52615 | 6576.875 | 0 | 0 | 64000 | 2523.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032506 | 5 | 0.4682 | 70230 | 0.2603 | 0 | 0.4784 | 5980 | 0 | 0 | 64000 | 5980 | 0 | 250 | 250 | 1350000 | 250 | 0
2021032507 | 5 | 0.51087 | 76630.5 | 0.21067 | 0 | 0.36222 | 4527.75 | 0 | 0 | 64000 | 4527.75 | 0 | 8102.75 | 7852.75 | 1350000 | 8102.75 | 0
2021032508 | 5 | 0.54362 | 81543 | 0.20662 | 0 | 0.26815 | 3351.875 | 0.00682 | 545.6 | 64000 | 3351.875 | 545.6 | 13645.525 | 5542.775 | 1350000 | 13645.525 | 0
2021032509 | 5 | 0.55515 | 83272.5 | 0.20628 | 0 | 0.25833 | 3229.125 | 0.0492 | 3936 | 64000 | 3229.125 | 3936 | 12107.375 | -1538.15 | 1350000 | 12107.375 | 0
2021032510 | 5 | 0.55868 | 83802 | 0.13707 | 0 | 0.24387 | 3048.375 | 0.09284 | 7427.2 | 64000 | 3048.375 | 7427.2 | 9326.425 | -2780.95 | 1350000 | 9326.425 | 0
2021032511 | 5 | 0.55857 | 83785.5 | 0.05713 | 0 | 0.20772 | 2596.5 | 0.15147 | 12117.6 | 64000 | 2596.5 | 12117.6 | 5071.4 | -4255.025 | 1350000 | 5071.4 | 0
2021032512 | 5 | 0.5571 | 83565 | 0.03773 | 0 | 0.1893 | 2366.25 | 0.18787 | 15029.6 | 64000 | 2366.25 | 15029.6 | 2169.15 | -2902.25 | 1350000 | 2169.15 | 0
2021032513 | 5 | 0.55519 | 83278.5 | 0.11423 | 0 | 0.16691 | 2086.375 | 0.2325 | 18600 | 64000 | 2086.375 | 17192.125 | 0 | -2169.15 | 1350000 | 0 | 0
2021032514 | 5 | 0.5513 | 82695 | 0.1625 | 0 | 0.14214 | 1776.75 | 0.21815 | 17452 | 64000 | 1776.75 | 16918.25 | 0 | 0 | 1350000 | 0 | 0
2021032515 | 5 | 0.54654 | 81981 | 0.2116 | 0 | 0.11303 | 1412.875 | 0.20128 | 16102.4 | 64000 | 1412.875 | 16102.4 | 465.725 | 465.725 | 1350000 | 465.725 | 0
2021032516 | 5 | 0.54106 | 81159 | 0.33479 | 0 | 0.11144 | 1393 | 0.15903 | 12722.4 | 64000 | 1393 | 12722.4 | 3043.6 | 2577.875 | 1350000 | 3043.6 | 0
2021032517 | 5 | 0.53936 | 80904 | 0.41331 | 0 | 0.15931 | 1991.375 | 0.11734 | 9387.2 | 64000 | 1991.375 | 9387.2 | 5525.425 | 2481.825 | 1350000 | 5525.425 | 0
2021032518 | 5 | 0.54355 | 81532.5 | 0.42669 | 0 | 0.1614 | 2017.5 | 0.06069 | 4855.2 | 64000 | 2017.5 | 4855.2 | 10659.8 | 5134.375 | 1350000 | 10659.8 | 0
2021032519 | 5 | 0.54759 | 82138.5 | 0.52351 | 0 | 0.12281 | 1535.125 | 0.00447 | 357.6 | 64000 | 1535.125 | 357.6 | 16245.775 | 5585.975 | 1350000 | 16245.775 | 0
2021032520 | 5 | 0.55787 | 83680.5 | 0.62985 | 0 | 0.11391 | 1423.875 | 0 | 0 | 64000 | 1423.875 | 0 | 18256.625 | 2010.85 | 1350000 | 18256.625 | 0
2021032521 | 5 | 0.56071 | 84106.5 | 0.7195 | 0 | 0.10186 | 1273.25 | 0 | 0 | 64000 | 1273.25 | 0 | 18833.25 | 576.625 | 1350000 | 18833.25 | 0
2021032522 | 5 | 0.5432 | 81480 | 0.80609 | 0 | 0.101 | 1262.5 | 0 | 0 | 64000 | 1262.5 | 0 | 16217.5 | -2615.75 | 1350000 | 16217.5 | 0
2021032523 | 5 | 0.51301 | 76951.5 | 0.77204 | 0 | 0.12749 | 1593.625 | 0 | 0 | 64000 | 1593.625 | 0 | 11357.875 | -4859.625 | 1350000 | 11357.875 | 0
2021032524 | 5 | 0.48329 | 72493.5 | 0.79658 | 0 | 0.11512 | 1439 | 0 | 0 | 64000 | 1439 | 0 | 7054.5 | -4303.375 | 1350000 | 7054.5 | 0
2021032601 | 6 | 0.45829 | 68743.5 | 0.7998 | 0 | 0.09017 | 1127.125 | 0 | 0 | 64000 | 1127.125 | 0 | 3616.375 | -3438.125 | 1350000 | 3616.375 | 0
2021032602 | 6 | 0.44387 | 66580.5 | 0.67392 | 0 | 0.07159 | 894.875 | 0 | 0 | 64000 | 894.875 | 0 | 1685.625 | -1930.75 | 1350000 | 1685.625 | 0
2021032603 | 6 | 0.43463 | 65194.5 | 0.68378 | 0 | 0.05784 | 723 | 0 | 0 | 64000 | 723 | 0 | 471.5 | -1214.125 | 1350000 | 471.5 | 0
2021032604 | 6 | 0.43219 | 64828.5 | 0.75724 | 0 | 0.05094 | 636.75 | 0 | 0 | 64000 | 636.75 | 0 | 191.75 | -279.75 | 1350000 | 191.75 | 0
2021032605 | 6 | 0.43834 | 65751 | 0.88879 | 0 | 0.04992 | 624 | 0 | 0 | 64000 | 624 | 0 | 1127 | 935.25 | 1350000 | 1127 | 0
2021032606 | 6 | 0.45978 | 68967 | 0.94197 | 0 | 0.05074 | 634.25 | 0 | 0 | 64000 | 634.25 | 0 | 4332.75 | 3205.75 | 1350000 | 4332.75 | 0
2021032607 | 6 | 0.49781 | 74671.5 | 0.96561 | 0 | 0.05493 | 686.625 | 0 | 0 | 64000 | 686.625 | 0 | 9984.875 | 5652.125 | 1350000 | 9984.875 | 0
2021032608 | 6 | 0.53127 | 79690.5 | 0.98831 | 0 | 0.06085 | 760.625 | 0.00699 | 559.2 | 64000 | 760.625 | 559.2 | 14370.675 | 4385.8 | 1350000 | 14370.675 | 0
2021032609 | 6 | 0.54665 | 81997.5 | 0.98709 | 0 | 0.0615 | 768.75 | 0.07211 | 5768.8 | 64000 | 768.75 | 5768.8 | 11459.95 | -2910.725 | 1350000 | 11459.95 | 0
2021032610 | 6 | 0.55514 | 83271 | 0.96145 | 0 | 0.07878 | 984.75 | 0.18001 | 14400.8 | 64000 | 984.75 | 14400.8 | 3885.45 | -7574.5 | 1350000 | 3885.45 | 0
2021032611 | 6 | 0.55885 | 83827.5 | 0.91331 | 0 | 0.07387 | 923.375 | 0.28125 | 22500 | 64000 | 923.375 | 18904.125 | 0 | -3885.45 | 1350000 | 0 | 0
2021032612 | 6 | 0.55703 | 83554.5 | 0.85042 | 0 | 0.04374 | 546.75 | 0.38338 | 30670.4 | 64000 | 546.75 | 19007.75 | 0 | 0 | 1350000 | 0 | 0
2021032613 | 6 | 0.55178 | 82767 | 0.84423 | 0 | 0.02873 | 359.125 | 0.4128 | 33024 | 64000 | 359.125 | 18407.875 | 0 | 0 | 1350000 | 0 | 0
2021032614 | 6 | 0.55035 | 82552.5 | 0.91533 | 0 | 0.01393 | 174.125 | 0.41974 | 33579.2 | 64000 | 174.125 | 18378.375 | 0 | 0 | 1350000 | 0 | 0
2021032615 | 6 | 0.54507 | 81760.5 | 0.9651 | 0 | 0.01284 | 160.5 | 0.37852 | 30281.6 | 64000 | 160.5 | 17600 | 0 | 0 | 1350000 | 0 | 0
2021032616 | 6 | 0.54008 | 81012 | 0.97242 | 0 | 0.01461 | 182.625 | 0.35634 | 28507.2 | 64000 | 182.625 | 16829.375 | 0 | 0 | 1350000 | 0 | 0
2021032617 | 6 | 0.54095 | 81142.5 | 0.98351 | 0 | 0.01799 | 224.875 | 0.25167 | 20133.6 | 64000 | 224.875 | 16917.625 | 0 | 0 | 1350000 | 0 | 0
2021032618 | 6 | 0.54229 | 81343.5 | 0.95943 | 0 | 0.02796 | 349.5 | 0.12066 | 9652.8 | 64000 | 349.5 | 9652.8 | 7341.2 | 7341.2 | 1350000 | 7341.2 | 0
2021032619 | 6 | 0.54158 | 81237 | 0.9338 | 0 | 0.03119 | 389.875 | 0.01608 | 1286.4 | 64000 | 389.875 | 1286.4 | 15560.725 | 8219.525 | 1350000 | 15560.725 | 0
2021032620 | 6 | 0.54441 | 81661.5 | 0.86718 | 0 | 0.0246 | 307.5 | 0 | 0 | 64000 | 307.5 | 0 | 17354 | 1793.275 | 1350000 | 17354 | 0
2021032621 | 6 | 0.54752 | 82128 | 0.76673 | 0 | 0.02226 | 278.25 | 0 | 0 | 64000 | 278.25 | 0 | 17849.75 | 495.75 | 1350000 | 17849.75 | 0
2021032622 | 6 | 0.52897 | 79345.5 | 0.72645 | 0 | 0.02572 | 321.5 | 0 | 0 | 64000 | 321.5 | 0 | 15024 | -2825.75 | 1350000 | 15024 | 0
2021032623 | 6 | 0.50177 | 75265.5 | 0.68885 | 0 | 0.03211 | 401.375 | 0 | 0 | 64000 | 401.375 | 0 | 10864.125 | -4159.875 | 1350000 | 10864.125 | 0
2021032624 | 6 | 0.47389 | 71083.5 | 0.65235 | 0 | 0.04002 | 500.25 | 0 | 0 | 64000 | 500.25 | 0 | 6583.25 | -4280.875 | 1350000 | 6583.25 | 0
2021032701 | 7 | 0.45018 | 67527 | 0.70548 | 0 | 0.04453 | 556.625 | 0 | 0 | 64000 | 556.625 | 0 | 2970.375 | -3612.875 | 1350000 | 2970.375 | 0
2021032702 | 7 | 0.43508 | 65262 | 0.64014 | 0 | 0.05312 | 664 | 0 | 0 | 64000 | 664 | 0 | 598 | -2372.375 | 1350000 | 598 | 0
2021032703 | 7 | 0.42501 | 63751.5 | 0.50205 | 0 | 0.0572 | 715 | 0 | 0 | 63751.5 | 0 | 0 | 0 | -598 | 1350000 | 0 | 0
2021032704 | 7 | 0.42198 | 63297 | 0.39563 | 0 | 0.06089 | 761.125 | 0 | 0 | 63297 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032705 | 7 | 0.42365 | 63547.5 | 0.36216 | 0 | 0.06182 | 772.75 | 0 | 0 | 63547.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032706 | 7 | 0.43526 | 65289 | 0.35543 | 0 | 0.06895 | 861.875 | 0 | 0 | 64000 | 861.875 | 0 | 427.125 | 427.125 | 1350000 | 427.125 | 0
2021032707 | 7 | 0.45498 | 68247 | 0.37163 | 0 | 0.05172 | 646.5 | 0 | 0 | 64000 | 646.5 | 0 | 3600.5 | 3173.375 | 1350000 | 3600.5 | 0
2021032708 | 7 | 0.47378 | 71067 | 0.32386 | 0 | 0.05229 | 653.625 | 0.01243 | 994.4 | 64000 | 653.625 | 994.4 | 5418.975 | 1818.475 | 1350000 | 5418.975 | 0
2021032709 | 7 | 0.48773 | 73159.5 | 0.23052 | 0 | 0.06708 | 838.5 | 0.08861 | 7088.8 | 64000 | 838.5 | 7088.8 | 1232.2 | -4186.775 | 1350000 | 1232.2 | 0
2021032710 | 7 | 0.49053 | 73579.5 | 0.16101 | 0 | 0.07438 | 929.75 | 0.15648 | 12518.4 | 64000 | 929.75 | 8649.75 | 0 | -1232.2 | 1350000 | 0 | 0
2021032711 | 7 | 0.4898 | 73470 | 0.13376 | 0 | 0.06909 | 863.625 | 0.2476 | 19808 | 64000 | 863.625 | 8606.375 | 0 | 0 | 1350000 | 0 | 0
2021032712 | 7 | 0.48365 | 72547.5 | 0.06756 | 0 | 0.06015 | 751.875 | 0.32101 | 25680.8 | 64000 | 751.875 | 7795.625 | 0 | 0 | 1350000 | 0 | 0
2021032713 | 7 | 0.47894 | 71841 | 0.03231 | 0 | 0.05431 | 678.875 | 0.3233 | 25864 | 64000 | 678.875 | 7162.125 | 0 | 0 | 1350000 | 0 | 0
2021032714 | 7 | 0.47477 | 71215.5 | 0.03343 | 0 | 0.05547 | 693.375 | 0.36065 | 28852 | 64000 | 693.375 | 6522.125 | 0 | 0 | 1350000 | 0 | 0
2021032715 | 7 | 0.47053 | 70579.5 | 0.10694 | 0 | 0.05221 | 652.625 | 0.29982 | 23985.6 | 64000 | 652.625 | 5926.875 | 0 | 0 | 1350000 | 0 | 0
2021032716 | 7 | 0.47148 | 70722 | 0.15831 | 0 | 0.05163 | 645.375 | 0.2133 | 17064 | 64000 | 645.375 | 6076.625 | 0 | 0 | 1350000 | 0 | 0
2021032717 | 7 | 0.47765 | 71647.5 | 0.30376 | 0 | 0.04826 | 603.25 | 0.15973 | 12778.4 | 64000 | 603.25 | 7044.25 | 0 | 0 | 1350000 | 0 | 0
2021032718 | 7 | 0.4862 | 72930 | 0.26675 | 0 | 0.05608 | 701 | 0.0831 | 6648 | 64000 | 701 | 6648 | 1581 | 1581 | 1350000 | 1581 | 0
2021032719 | 7 | 0.49054 | 73581 | 0.24701 | 0 | 0.06209 | 776.125 | 0.01503 | 1202.4 | 64000 | 776.125 | 1202.4 | 7602.475 | 6021.475 | 1350000 | 7602.475 | 0
2021032720 | 7 | 0.49807 | 74710.5 | 0.37483 | 0 | 0.06592 | 824 | 0 | 0 | 64000 | 824 | 0 | 9886.5 | 2284.025 | 1350000 | 9886.5 | 0
2021032721 | 7 | 0.50599 | 75898.5 | 0.50849 | 0 | 0.07198 | 899.75 | 0 | 0 | 64000 | 899.75 | 0 | 10998.75 | 1112.25 | 1350000 | 10998.75 | 0
2021032722 | 7 | 0.4924 | 73860 | 0.60592 | 0 | 0.07986 | 998.25 | 0 | 0 | 64000 | 998.25 | 0 | 8861.75 | -2137 | 1350000 | 8861.75 | 0
2021032723 | 7 | 0.47295 | 70942.5 | 0.63502 | 0 | 0.11204 | 1400.5 | 0 | 0 | 64000 | 1400.5 | 0 | 5542 | -3319.75 | 1350000 | 5542 | 0
2021032724 | 7 | 0.44955 | 67432.5 | 0.69186 | 0 | 0.14466 | 1808.25 | 0 | 0 | 64000 | 1808.25 | 0 | 1624.25 | -3917.75 | 1350000 | 1624.25 | 0
2021032801 | 1 | 0.42929 | 64393.5 | 0.7464 | 0 | 0.17227 | 2153.375 | 0 | 0 | 64000 | 393.5 | 0 | 0 | -1624.25 | 1350000 | 0 | 0
2021032802 | 1 | 0.41547 | 62320.5 | 0.77123 | 0 | 0.17933 | 2241.625 | 0 | 0 | 62320.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032803 | 1 | 0.40841 | 61261.5 | 0.73663 | 0 | 0.18503 | 2312.875 | 0 | 0 | 61261.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032804 | 1 | 0.40339 | 60508.5 | 0.69409 | 0 | 0.18928 | 2366 | 0 | 0 | 60508.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032805 | 1 | 0.4038 | 60570 | 0.73904 | 0 | 0.18996 | 2374.5 | 0 | 0 | 60570 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032806 | 1 | 0.40928 | 61392 | 0.7866 | 0 | 0.1648 | 2060 | 0 | 0 | 61392 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032807 | 1 | 0.42197 | 63295.5 | 0.86272 | 0 | 0.16437 | 2054.625 | 0 | 0 | 63295.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032808 | 1 | 0.43818 | 65727 | 0.89284 | 0 | 0.17639 | 2204.875 | 0.01991 | 1592.8 | 64000 | 1727 | 0 | 0 | 0 | 1350000 | 0 | 0
2021032809 | 1 | 0.45946 | 68919 | 0.90851 | 0 | 0.17325 | 2165.625 | 0.12424 | 9939.2 | 64000 | 2165.625 | 2753.375 | 0 | 0 | 1350000 | 0 | 0
2021032810 | 1 | 0.48038 | 72057 | 0.92028 | 0 | 0.16891 | 2111.375 | 0.2273 | 18184 | 64000 | 2111.375 | 5945.625 | 0 | 0 | 1350000 | 0 | 0
2021032811 | 1 | 0.49422 | 74133 | 0.89836 | 0 | 0.14805 | 1850.625 | 0.24 | 19200 | 64000 | 1850.625 | 8282.375 | 0 | 0 | 1350000 | 0 | 0
2021032812 | 1 | 0.50181 | 75271.5 | 0.91462 | 0 | 0.14553 | 1819.125 | 0.27923 | 22338.4 | 64000 | 1819.125 | 9452.375 | 0 | 0 | 1350000 | 0 | 0
2021032813 | 1 | 0.50513 | 75769.5 | 0.8965 | 0 | 0.15892 | 1986.5 | 0.28455 | 22764 | 64000 | 1986.5 | 9783 | 0 | 0 | 1350000 | 0 | 0
2021032814 | 1 | 0.50322 | 75483 | 0.9076 | 0 | 0.16521 | 2065.125 | 0.2743 | 21944 | 64000 | 2065.125 | 9417.875 | 0 | 0 | 1350000 | 0 | 0
2021032815 | 1 | 0.50045 | 75067.5 | 0.94818 | 0 | 0.17309 | 2163.625 | 0.24849 | 19879.2 | 64000 | 2163.625 | 8903.875 | 0 | 0 | 1350000 | 0 | 0
2021032816 | 1 | 0.50024 | 75036 | 0.96371 | 0 | 0.18875 | 2359.375 | 0.18325 | 14660 | 64000 | 2359.375 | 8676.625 | 0 | 0 | 1350000 | 0 | 0
2021032817 | 1 | 0.50585 | 75877.5 | 0.96739 | 0 | 0.19461 | 2432.625 | 0.11767 | 9413.6 | 64000 | 2432.625 | 9413.6 | 31.275 | 31.275 | 1350000 | 31.275 | 0
2021032818 | 1 | 0.51686 | 77529 | 0.99074 | 0 | 0.20025 | 2503.125 | 0.06106 | 4884.8 | 64000 | 2503.125 | 4884.8 | 6141.075 | 6109.8 | 1350000 | 6141.075 | 0
2021032819 | 1 | 0.52428 | 78642 | 0.98888 | 0 | 0.18539 | 2317.375 | 0.01005 | 804 | 64000 | 2317.375 | 804 | 11520.625 | 5379.55 | 1350000 | 11520.625 | 0
2021032820 | 1 | 0.53293 | 79939.5 | 0.95801 | 0 | 0.19462 | 2432.75 | 0 | 0 | 64000 | 2432.75 | 0 | 13506.75 | 1986.125 | 1350000 | 13506.75 | 0
2021032821 | 1 | 0.54084 | 81126 | 0.97833 | 0 | 0.19285 | 2410.625 | 0 | 0 | 64000 | 2410.625 | 0 | 14715.375 | 1208.625 | 1350000 | 14715.375 | 0
2021032822 | 1 | 0.52755 | 79132.5 | 0.98579 | 0 | 0.19532 | 2441.5 | 0 | 0 | 64000 | 2441.5 | 0 | 12691 | -2024.375 | 1350000 | 12691 | 0
2021032823 | 1 | 0.50639 | 75958.5 | 0.99114 | 0 | 0.20827 | 2603.375 | 0 | 0 | 64000 | 2603.375 | 0 | 9355.125 | -3335.875 | 1350000 | 9355.125 | 0
2021032824 | 1 | 0.4841 | 72615 | 0.98529 | 0 | 0.23115 | 2889.375 | 0 | 0 | 64000 | 2889.375 | 0 | 5725.625 | -3629.5 | 1350000 | 5725.625 | 0
2021032901 | 2 | 0.46887 | 70330.5 | 0.99002 | 0 | 0.2509 | 3136.25 | 0 | 0 | 64000 | 3136.25 | 0 | 3194.25 | -2531.375 | 1350000 | 3194.25 | 0
2021032902 | 2 | 0.46098 | 69147 | 0.99004 | 0 | 0.2763 | 3453.75 | 0 | 0 | 64000 | 3453.75 | 0 | 1693.25 | -1501 | 1350000 | 1693.25 | 0
2021032903 | 2 | 0.46067 | 69100.5 | 0.9922 | 0 | 0.29761 | 3720.125 | 0 | 0 | 64000 | 3720.125 | 0 | 1380.375 | -312.875 | 1350000 | 1380.375 | 0
2021032904 | 2 | 0.46406 | 69609 | 0.9927 | 0 | 0.30294 | 3786.75 | 0 | 0 | 64000 | 3786.75 | 0 | 1822.25 | 441.875 | 1350000 | 1822.25 | 0
2021032905 | 2 | 0.47961 | 71941.5 | 0.9942 | 0 | 0.27967 | 3495.875 | 0 | 0 | 64000 | 3495.875 | 0 | 4445.625 | 2623.375 | 1350000 | 4445.625 | 0
2021032906 | 2 | 0.51017 | 76525.5 | 0.98282 | 0 | 0.23071 | 2883.875 | 0 | 0 | 64000 | 2883.875 | 0 | 9641.625 | 5196 | 1350000 | 9641.625 | 0
2021032907 | 2 | 0.56101 | 84151.5 | 0.96914 | 0 | 0.18615 | 2326.875 | 0 | 0 | 64000 | 2326.875 | 0 | 17824.625 | 8183 | 1350000 | 17824.625 | 0
2021032908 | 2 | 0.59716 | 89574 | 0.98209 | 0 | 0.15387 | 1923.375 | 0.01495 | 1196 | 64000 | 1923.375 | 1196 | 22454.625 | 4630 | 1350000 | 22454.625 | 0
2021032909 | 2 | 0.60379 | 90568.5 | 0.97749 | 0 | 0.12727 | 1590.875 | 0.15653 | 12522.4 | 64000 | 1590.875 | 12522.4 | 12455.225 | -9999.4 | 1350000 | 12455.225 | 0
2021032910 | 2 | 0.59383 | 89074.5 | 0.98102 | 0 | 0.11282 | 1410.25 | 0.31963 | 25570.4 | 64000 | 1410.25 | 23664.25 | 0 | -12455.225 | 1350000 | 0 | 0
2021032911 | 2 | 0.5815 | 87225 | 0.9546 | 0 | 0.09987 | 1248.375 | 0.36357 | 29085.6 | 64000 | 1248.375 | 21976.625 | 0 | 0 | 1350000 | 0 | 0
2021032912 | 2 | 0.56787 | 85180.5 | 0.92734 | 0 | 0.09623 | 1202.875 | 0.35563 | 28450.4 | 64000 | 1202.875 | 19977.625 | 0 | 0 | 1350000 | 0 | 0
2021032913 | 2 | 0.55615 | 83422.5 | 0.89588 | 0 | 0.09912 | 1239 | 0.41261 | 33008.8 | 64000 | 1239 | 18183.5 | 0 | 0 | 1350000 | 0 | 0
2021032914 | 2 | 0.54636 | 81954 | 0.76134 | 0 | 0.09416 | 1177 | 0.44854 | 35883.2 | 64000 | 1177 | 16777 | 0 | 0 | 1350000 | 0 | 0
2021032915 | 2 | 0.53394 | 80091 | 0.63911 | 0 | 0.10251 | 1281.375 | 0.49081 | 39264.8 | 64000 | 1281.375 | 14809.625 | 0 | 0 | 1350000 | 0 | 0
2021032916 | 2 | 0.5249 | 78735 | 0.55439 | 0 | 0.09668 | 1208.5 | 0.46415 | 37132 | 64000 | 1208.5 | 13526.5 | 0 | 0 | 1350000 | 0 | 0
2021032917 | 2 | 0.52353 | 78529.5 | 0.44596 | 0 | 0.07992 | 999 | 0.36705 | 29364 | 64000 | 999 | 13530.5 | 0 | 0 | 1350000 | 0 | 0
2021032918 | 2 | 0.52883 | 79324.5 | 0.28597 | 0 | 0.07157 | 894.625 | 0.1722 | 13776 | 64000 | 894.625 | 13776 | 653.875 | 653.875 | 1350000 | 653.875 | 0
2021032919 | 2 | 0.53684 | 80526 | 0.20412 | 0 | 0.06029 | 753.625 | 0.01917 | 1533.6 | 64000 | 753.625 | 1533.6 | 14238.775 | 13584.9 | 1350000 | 14238.775 | 0
2021032920 | 2 | 0.55232 | 82848 | 0.12926 | 0 | 0.05512 | 689 | 0 | 0 | 64000 | 689 | 0 | 18159 | 3920.225 | 1350000 | 18159 | 0
2021032921 | 2 | 0.56934 | 85401 | 0.11343 | 0 | 0.05208 | 651 | 0 | 0 | 64000 | 651 | 0 | 20750 | 2591 | 1350000 | 20750 | 0
2021032922 | 2 | 0.55758 | 83637 | 0.05157 | 0 | 0.04721 | 590.125 | 0 | 0 | 64000 | 590.125 | 0 | 19046.875 | -1703.125 | 1350000 | 19046.875 | 0
2021032923 | 2 | 0.53291 | 79936.5 | 0.06707 | 0 | 0.04117 | 514.625 | 0 | 0 | 64000 | 514.625 | 0 | 15421.875 | -3625 | 1350000 | 15421.875 | 0
2021032924 | 2 | 0.50872 | 76308 | 0.21718 | 0 | 0.05259 | 657.375 | 0 | 0 | 64000 | 657.375 | 0 | 11650.625 | -3771.25 | 1350000 | 11650.625 | 0
2021033001 | 3 | 0.49152 | 73728 | 0.50258 | 0 | 0.06256 | 782 | 0 | 0 | 64000 | 782 | 0 | 8946 | -2704.625 | 1350000 | 8946 | 0
2021033002 | 3 | 0.48189 | 72283.5 | 0.68213 | 0 | 0.06347 | 793.375 | 0 | 0 | 64000 | 793.375 | 0 | 7490.125 | -1455.875 | 1350000 | 7490.125 | 0
2021033003 | 3 | 0.47852 | 71778 | 0.77834 | 0 | 0.0672 | 840 | 0 | 0 | 64000 | 840 | 0 | 6938 | -552.125 | 1350000 | 6938 | 0
2021033004 | 3 | 0.48131 | 72196.5 | 0.81441 | 0 | 0.07713 | 964.125 | 0 | 0 | 64000 | 964.125 | 0 | 7232.375 | 294.375 | 1350000 | 7232.375 | 0
2021033005 | 3 | 0.49606 | 74409 | 0.80885 | 0 | 0.09527 | 1190.875 | 0 | 0 | 64000 | 1190.875 | 0 | 9218.125 | 1985.75 | 1350000 | 9218.125 | 0
2021033006 | 3 | 0.52551 | 78826.5 | 0.82118 | 0 | 0.10961 | 1370.125 | 0 | 0 | 64000 | 1370.125 | 0 | 13456.375 | 4238.25 | 1350000 | 13456.375 | 0
2021033007 | 3 | 0.57294 | 85941 | 0.86429 | 0 | 0.11505 | 1438.125 | 0 | 0 | 64000 | 1438.125 | 0 | 20502.875 | 7046.5 | 1350000 | 20502.875 | 0
2021033008 | 3 | 0.601 | 90150 | 0.89455 | 0 | 0.12043 | 1505.375 | 0.01707 | 1365.6 | 64000 | 1505.375 | 1365.6 | 23279.025 | 2776.15 | 1350000 | 23279.025 | 0
2021033009 | 3 | 0.59294 | 88941 | 0.86531 | 0 | 0.10576 | 1322 | 0.12511 | 10008.8 | 64000 | 1322 | 10008.8 | 13610.2 | -9668.825 | 1350000 | 13610.2 | 0
2021033010 | 3 | 0.57231 | 85846.5 | 0.79952 | 0 | 0.07035 | 879.375 | 0.26722 | 21377.6 | 64000 | 879.375 | 20967.125 | 0 | -13610.2 | 1350000 | 0 | 0
2021033011 | 3 | 0.55607 | 83410.5 | 0.75125 | 0 | 0.0625 | 781.25 | 0.36466 | 29172.8 | 64000 | 781.25 | 18629.25 | 0 | 0 | 1350000 | 0 | 0
2021033012 | 3 | 0.54382 | 81573 | 0.70305 | 0 | 0.05295 | 661.875 | 0.42661 | 34128.8 | 64000 | 661.875 | 16911.125 | 0 | 0 | 1350000 | 0 | 0
2021033013 | 3 | 0.53602 | 80403 | 0.72411 | 0 | 0.0417 | 521.25 | 0.47796 | 38236.8 | 64000 | 521.25 | 15881.75 | 0 | 0 | 1350000 | 0 | 0
2021033014 | 3 | 0.52864 | 79296 | 0.73264 | 0 | 0.04247 | 530.875 | 0.49242 | 39393.6 | 64000 | 530.875 | 14765.125 | 0 | 0 | 1350000 | 0 | 0
2021033015 | 3 | 0.52133 | 78199.5 | 0.77527 | 0 | 0.04838 | 604.75 | 0.45669 | 36535.2 | 64000 | 604.75 | 13594.75 | 0 | 0 | 1350000 | 0 | 0
2021033016 | 3 | 0.51754 | 77631 | 0.8231 | 0 | 0.05344 | 668 | 0.36624 | 29299.2 | 64000 | 668 | 12963 | 0 | 0 | 1350000 | 0 | 0
2021033017 | 3 | 0.51911 | 77866.5 | 0.84222 | 0 | 0.05124 | 640.5 | 0.22859 | 18287.2 | 64000 | 640.5 | 13226 | 0 | 0 | 1350000 | 0 | 0
2021033018 | 3 | 0.52622 | 78933 | 0.90298 | 0 | 0.05611 | 701.375 | 0.11165 | 8932 | 64000 | 701.375 | 8932 | 5299.625 | 5299.625 | 1350000 | 5299.625 | 0
2021033019 | 3 | 0.53231 | 79846.5 | 0.95267 | 0 | 0.05571 | 696.375 | 0.02002 | 1601.6 | 64000 | 696.375 | 1601.6 | 13548.525 | 8248.9 | 1350000 | 13548.525 | 0
2021033020 | 3 | 0.54502 | 81753 | 0.97431 | 0 | 0.05916 | 739.5 | 0 | 0 | 64000 | 739.5 | 0 | 17013.5 | 3464.975 | 1350000 | 17013.5 | 0
2021033021 | 3 | 0.55646 | 83469 | 0.97798 | 0 | 0.07937 | 992.125 | 0 | 0 | 64000 | 992.125 | 0 | 18476.875 | 1463.375 | 1350000 | 18476.875 | 0
2021033022 | 3 | 0.5393 | 80895 | 0.97376 | 0 | 0.10335 | 1291.875 | 0 | 0 | 64000 | 1291.875 | 0 | 15603.125 | -2873.75 | 1350000 | 15603.125 | 0
2021033023 | 3 | 0.50886 | 76329 | 0.96897 | 0 | 0.11927 | 1490.875 | 0 | 0 | 64000 | 1490.875 | 0 | 10838.125 | -4765 | 1350000 | 10838.125 | 0
2021033024 | 3 | 0.4786 | 71790 | 0.96327 | 0 | 0.13911 | 1738.875 | 0 | 0 | 64000 | 1738.875 | 0 | 6051.125 | -4787 | 1350000 | 6051.125 | 0
2021033101 | 4 | 0.45657 | 68485.5 | 0.93703 | 0 | 0.15859 | 1982.375 | 0 | 0 | 64000 | 1982.375 | 0 | 2503.125 | -3548 | 1350000 | 2503.125 | 0
2021033102 | 4 | 0.44372 | 66558 | 0.89672 | 0 | 0.15725 | 1965.625 | 0 | 0 | 64000 | 1965.625 | 0 | 592.375 | -1910.75 | 1350000 | 592.375 | 0
2021033103 | 4 | 0.43692 | 65538 | 0.86681 | 0 | 0.14292 | 1786.5 | 0 | 0 | 64000 | 1538 | 0 | 0 | -592.375 | 1350000 | 0 | 0
2021033104 | 4 | 0.43545 | 65317.5 | 0.83159 | 0 | 0.13546 | 1693.25 | 0 | 0 | 64000 | 1317.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021033105 | 4 | 0.4433 | 66495 | 0.8197 | 0 | 0.12159 | 1519.875 | 0 | 0 | 64000 | 1519.875 | 0 | 975.125 | 975.125 | 1350000 | 975.125 | 0
2021033106 | 4 | 0.46967 | 70450.5 | 0.82238 | 0 | 0.10908 | 1363.5 | 0 | 0 | 64000 | 1363.5 | 0 | 5087 | 4111.875 | 1350000 | 5087 | 0
2021033107 | 4 | 0.5093 | 76395 | 0.78197 | 0 | 0.13142 | 1642.75 | 0 | 0 | 64000 | 1642.75 | 0 | 10752.25 | 5665.25 | 1350000 | 10752.25 | 0
2021033108 | 4 | 0.53805 | 80707.5 | 0.75757 | 0 | 0.10541 | 1317.625 | 0.02783 | 2226.4 | 64000 | 1317.625 | 2226.4 | 13163.475 | 2411.225 | 1350000 | 13163.475 | 0
2021033109 | 4 | 0.55081 | 82621.5 | 0.7458 | 0 | 0.11632 | 1454 | 0.1961 | 15688 | 64000 | 1454 | 15688 | 1479.5 | -11683.975 | 1350000 | 1479.5 | 0
2021033110 | 4 | 0.55621 | 83431.5 | 0.7489 | 0 | 0.13437 | 1679.625 | 0.37219 | 29775.2 | 64000 | 1679.625 | 17751.875 | 0 | -1479.5 | 1350000 | 0 | 0
2021033111 | 4 | 0.56036 | 84054 | 0.67071 | 0 | 0.14393 | 1799.125 | 0.47003 | 37602.4 | 64000 | 1799.125 | 18254.875 | 0 | 0 | 1350000 | 0 | 0
2021033112 | 4 | 0.56154 | 84231 | 0.60198 | 0 | 0.09624 | 1203 | 0.55627 | 44501.6 | 64000 | 1203 | 19028 | 0 | 0 | 1350000 | 0 | 0
2021033113 | 4 | 0.56305 | 84457.5 | 0.55395 | 0 | 0.0856 | 1070 | 0.56271 | 45016.8 | 64000 | 1070 | 19387.5 | 0 | 0 | 1350000 | 0 | 0
2021033114 | 4 | 0.56235 | 84352.5 | 0.55196 | 0 | 0.0823 | 1028.75 | 0.60674 | 48539.2 | 64000 | 1028.75 | 19323.75 | 0 | 0 | 1350000 | 0 | 0
2021033115 | 4 | 0.55942 | 83913 | 0.53847 | 0 | 0.08036 | 1004.5 | 0.59514 | 47611.2 | 64000 | 1004.5 | 18908.5 | 0 | 0 | 1350000 | 0 | 0
2021033116 | 4 | 0.55513 | 83269.5 | 0.49214 | 0 | 0.08088 | 1011 | 0.58334 | 46667.2 | 64000 | 1011 | 18258.5 | 0 | 0 | 1350000 | 0 | 0
2021033117 | 4 | 0.55623 | 83434.5 | 0.4319 | 0 | 0.09205 | 1150.625 | 0.48568 | 38854.4 | 64000 | 1150.625 | 18283.875 | 0 | 0 | 1350000 | 0 | 0
2021033118 | 4 | 0.56224 | 84336 | 0.33889 | 0 | 0.11779 | 1472.375 | 0.26667 | 21333.6 | 64000 | 1472.375 | 18863.625 | 0 | 0 | 1350000 | 0 | 0
2021033119 | 4 | 0.56567 | 84850.5 | 0.41941 | 0 | 0.14612 | 1826.5 | 0.03594 | 2875.2 | 64000 | 1826.5 | 2875.2 | 16148.8 | 16148.8 | 1350000 | 16148.8 | 0
2021033120 | 4 | 0.57189 | 85783.5 | 0.53333 | 0 | 0.18668 | 2333.5 | 0 | 0 | 64000 | 2333.5 | 0 | 19450 | 3301.2 | 1350000 | 19450 | 0
2021033121 | 4 | 0.57485 | 86227.5 | 0.77678 | 0 | 0.21481 | 2685.125 | 0 | 0 | 64000 | 2685.125 | 0 | 19542.375 | 92.375 | 1350000 | 19542.375 | 0
2021033122 | 4 | 0.55781 | 83671.5 | 0.76892 | 0 | 0.22306 | 2788.25 | 0 | 0 | 64000 | 2788.25 | 0 | 16883.25 | -2659.125 | 1350000 | 16883.25 | 0
2021033123 | 4 | 0.53076 | 79614 | 0.65471 | 0 | 0.20144 | 2518 | 0 | 0 | 64000 | 2518 | 0 | 13096 | -3787.25 | 1350000 | 13096 | 0
2021033124 | 4 | 0.50283 | 75424.5 | 0.72088 | 0 | 0.20942 | 2617.75 | 0 | 0 | 64000 | 2617.75 | 0 | 8806.75 | -4289.25 | 1350000 | 8806.75 | 0
2021040101 | 5 | 0.48403 | 72604.5 | 0.70718 | 0 | 0.20543 | 2567.875 | 0 | 0 | 64000 | 2567.875 | 0 | 6036.625 | -2770.125 | 1350000 | 6036.625 | 0
2021040102 | 5 | 0.47203 | 70804.5 | 0.7751 | 0 | 0.21322 | 2665.25 | 0 | 0 | 64000 | 2665.25 | 0 | 4139.25 | -1897.375 | 1350000 | 4139.25 | 0
2021040103 | 5 | 0.46795 | 70192.5 | 0.76536 | 0 | 0.20232 | 2529 | 0 | 0 | 64000 | 2529 | 0 | 3663.5 | -475.75 | 1350000 | 3663.5 | 0
2021040104 | 5 | 0.47124 | 70686 | 0.7711 | 0 | 0.19394 | 2424.25 | 0 | 0 | 64000 | 2424.25 | 0 | 4261.75 | 598.25 | 1350000 | 4261.75 | 0
2021040105 | 5 | 0.48247 | 72370.5 | 0.76116 | 0 | 0.20668 | 2583.5 | 0 | 0 | 64000 | 2583.5 | 0 | 5787 | 1525.25 | 1350000 | 5787 | 0
2021040106 | 5 | 0.5131 | 76965 | 0.82287 | 0 | 0.18679 | 2334.875 | 0 | 0 | 64000 | 2334.875 | 0 | 10630.125 | 4843.125 | 1350000 | 10630.125 | 0
2021040107 | 5 | 0.55985 | 83977.5 | 0.82165 | 0 | 0.15124 | 1890.5 | 0 | 0 | 64000 | 1890.5 | 0 | 18087 | 7456.875 | 1350000 | 18087 | 0
2021040108 | 5 | 0.59679 | 89518.5 | 0.78659 | 0 | 0.13504 | 1688 | 0.02523 | 2018.4 | 64000 | 1688 | 2018.4 | 21812.1 | 3725.1 | 1350000 | 21812.1 | 0
2021040109 | 5 | 0.61223 | 91834.5 | 0.7875 | 0 | 0.11502 | 1437.75 | 0.25122 | 20097.6 | 64000 | 1437.75 | 20097.6 | 6299.15 | -15512.95 | 1350000 | 6299.15 | 0
2021040110 | 5 | 0.6154 | 92310 | 0.78379 | 0 | 0.16328 | 2041 | 0.48912 | 39129.6 | 64000 | 2041 | 26269 | 0 | -6299.15 | 1350000 | 0 | 0
2021040111 | 5 | 0.61473 | 92209.5 | 0.78711 | 0 | 0.1914 | 2392.5 | 0.58304 | 46643.2 | 64000 | 2392.5 | 25817 | 0 | 0 | 1350000 | 0 | 0
2021040112 | 5 | 0.61049 | 91573.5 | 0.81785 | 0 | 0.17701 | 2212.625 | 0.62247 | 49797.6 | 64000 | 2212.625 | 25360.875 | 0 | 0 | 1350000 | 0 | 0
2021040113 | 5 | 0.60242 | 90363 | 0.88081 | 0 | 0.12956 | 1619.5 | 0.6334 | 50672 | 64000 | 1619.5 | 24743.5 | 0 | 0 | 1350000 | 0 | 0
2021040114 | 5 | 0.59473 | 89209.5 | 0.92562 | 0 | 0.10348 | 1293.5 | 0.65611 | 52488.8 | 64000 | 1293.5 | 23916 | 0 | 0 | 1350000 | 0 | 0
2021040115 | 5 | 0.58712 | 88068 | 0.92603 | 0 | 0.08805 | 1100.625 | 0.65758 | 52606.4 | 64000 | 1100.625 | 22967.375 | 0 | 0 | 1350000 | 0 | 0
2021040116 | 5 | 0.58325 | 87487.5 | 0.89567 | 0 | 0.10167 | 1270.875 | 0.64786 | 51828.8 | 64000 | 1270.875 | 22216.625 | 0 | 0 | 1350000 | 0 | 0
2021040117 | 5 | 0.58624 | 87936 | 0.90882 | 0 | 0.16074 | 2009.25 | 0.57766 | 46212.8 | 64000 | 2009.25 | 21926.75 | 0 | 0 | 1350000 | 0 | 0
2021040118 | 5 | 0.59471 | 89206.5 | 0.93925 | 0 | 0.20822 | 2602.75 | 0.33849 | 27079.2 | 64000 | 2602.75 | 22603.75 | 0 | 0 | 1350000 | 0 | 0
2021040119 | 5 | 0.60377 | 90565.5 | 0.9315 | 0 | 0.2117 | 2646.25 | 0.0508 | 4064 | 64000 | 2646.25 | 4064 | 19855.25 | 19855.25 | 1350000 | 19855.25 | 0
2021040120 | 5 | 0.62017 | 93025.5 | 0.9137 | 0 | 0.23582 | 2947.75 | 0 | 0 | 64000 | 2947.75 | 0 | 26077.75 | 6222.5 | 1349388.5 | 26077.75 | 0
2021040121 | 5 | 0.6352 | 95280 | 0.8531 | 0 | 0.26637 | 3329.625 | 0 | 0 | 64000 | 3329.625 | 0 | 27950.375 | 1872.625 | 1346904.375 | 27950.375 | 0
2021040122 | 5 | 0.6235 | 93525 | 0.87248 | 0 | 0.27933 | 3491.625 | 0 | 0 | 64000 | 3491.625 | 0 | 26033.375 | -1917 | 1346337.25 | 26033.375 | 0
2021040123 | 5 | 0.5986 | 89790 | 0.93991 | 0 | 0.28217 | 3527.125 | 0 | 0 | 64000 | 3527.125 | 0 | 22262.875 | -3770.5 | 1349540.625 | 22262.875 | 0
2021040124 | 5 | 0.57237 | 85855.5 | 0.92814 | 0 | 0.26993 | 3374.125 | 0 | 0 | 64000 | 3374.125 | 0 | 18481.375 | -3781.5 | 1350000 | 18481.375 | 0
2021040201 | 6 | 0.55339 | 83008.5 | 0.92433 | 0 | 0.26267 | 3283.375 | 0 | 0 | 64000 | 3283.375 | 0 | 15725.125 | -2756.25 | 1350000 | 15725.125 | 0
2021040202 | 6 | 0.5449 | 81735 | 0.90343 | 0 | 0.2555 | 3193.75 | 0 | 0 | 64000 | 3193.75 | 0 | 14541.25 | -1183.875 | 1350000 | 14541.25 | 0
2021040203 | 6 | 0.54226 | 81339 | 0.86639 | 0 | 0.21871 | 2733.875 | 0 | 0 | 64000 | 2733.875 | 0 | 14605.125 | 63.875 | 1350000 | 14605.125 | 0
2021040204 | 6 | 0.546 | 81900 | 0.89523 | 0 | 0.22806 | 2850.75 | 0 | 0 | 64000 | 2850.75 | 0 | 15049.25 | 444.125 | 1350000 | 15049.25 | 0
2021040205 | 6 | 0.55801 | 83701.5 | 0.8737 | 0 | 0.23961 | 2995.125 | 0 | 0 | 64000 | 2995.125 | 0 | 16706.375 | 1657.125 | 1350000 | 16706.375 | 0
2021040206 | 6 | 0.58439 | 87658.5 | 0.85219 | 0 | 0.18092 | 2261.5 | 0 | 0 | 64000 | 2261.5 | 0 | 21397 | 4690.625 | 1350000 | 21397 | 0
2021040207 | 6 | 0.62247 | 93370.5 | 0.87265 | 0 | 0.11934 | 1491.75 | 0 | 0 | 64000 | 1491.75 | 0 | 27878.75 | 6481.75 | 1347587.5 | 27878.75 | 0
2021040208 | 6 | 0.64575 | 96862.5 | 0.87898 | 0 | 0.10775 | 1346.875 | 0.05594 | 4475.2 | 64000 | 1346.875 | 4475.2 | 27040.425 | -838.325 | 1346013.325 | 27040.425 | 0
2021040209 | 6 | 0.64248 | 96372 | 0.93994 | 0 | 0.11664 | 1458 | 0.33629 | 26903.2 | 64000 | 1458 | 26903.2 | 4010.8 | -23029.625 | 1350000 | 4010.8 | 0
2021040210 | 6 | 0.63003 | 94504.5 | 0.977 | 0 | 0.11862 | 1482.75 | 0.57008 | 45606.4 | 64000 | 1482.75 | 29021.75 | 0 | -4010.8 | 1350000 | 0 | 0
2021040211 | 6 | 0.61973 | 92959.5 | 0.96778 | 0 | 0.10694 | 1336.75 | 0.63869 | 51095.2 | 64000 | 1336.75 | 27622.75 | 0 | 0 | 1350000 | 0 | 0
2021040212 | 6 | 0.6066 | 90990 | 0.97515 | 0 | 0.09375 | 1171.875 | 0.66048 | 52838.4 | 64000 | 1171.875 | 25818.125 | 0 | 0 | 1350000 | 0 | 0
2021040213 | 6 | 0.59104 | 88656 | 0.98126 | 0 | 0.05583 | 697.875 | 0.67548 | 54038.4 | 64000 | 697.875 | 23958.125 | 0 | 0 | 1350000 | 0 | 0
2021040214 | 6 | 0.57606 | 86409 | 0.98333 | 0 | 0.02314 | 289.25 | 0.69008 | 55206.4 | 64000 | 289.25 | 22119.75 | 0 | 0 | 1350000 | 0 | 0
2021040215 | 6 | 0.56081 | 84121.5 | 0.98684 | 0 | 0.01815 | 226.875 | 0.69975 | 55980 | 64000 | 226.875 | 19894.625 | 0 | 0 | 1350000 | 0 | 0
2021040216 | 6 | 0.54663 | 81994.5 | 0.99051 | 0 | 0.02759 | 344.875 | 0.6763 | 54104 | 64000 | 344.875 | 17649.625 | 0 | 0 | 1350000 | 0 | 0
2021040217 | 6 | 0.54161 | 81241.5 | 0.98833 | 0 | 0.07823 | 977.875 | 0.60191 | 48152.8 | 64000 | 977.875 | 16263.625 | 0 | 0 | 1350000 | 0 | 0
2021040218 | 6 | 0.54491 | 81736.5 | 0.98286 | 0 | 0.12939 | 1617.375 | 0.3347 | 26776 | 64000 | 1617.375 | 16119.125 | 0 | 0 | 1350000 | 0 | 0
2021040219 | 6 | 0.55434 | 83151 | 0.96587 | 0 | 0.12045 | 1505.625 | 0.05045 | 4036 | 64000 | 1505.625 | 4036 | 13609.375 | 13609.375 | 1350000 | 13609.375 | 0
2021040220 | 6 | 0.57391 | 86086.5 | 0.90918 | 0 | 0.10799 | 1349.875 | 0 | 0 | 64000 | 1349.875 | 0 | 20736.625 | 7127.25 | 1350000 | 20736.625 | 0
2021040221 | 6 | 0.59499 | 89248.5 | 0.81712 | 0 | 0.107 | 1337.5 | 0 | 0 | 64000 | 1337.5 | 0 | 23911 | 3174.375 | 1350000 | 23911 | 0
2021040222 | 6 | 0.59009 | 88513.5 | 0.75111 | 0 | 0.11051 | 1381.375 | 0 | 0 | 64000 | 1381.375 | 0 | 23132.125 | -778.875 | 1350000 | 23132.125 | 0
2021040223 | 6 | 0.57483 | 86224.5 | 0.73112 | 0 | 0.1352 | 1690 | 0 | 0 | 64000 | 1690 | 0 | 20534.5 | -2597.625 | 1350000 | 20534.5 | 0
2021040224 | 6 | 0.55506 | 83259 | 0.73315 | 0 | 0.17774 | 2221.75 | 0 | 0 | 64000 | 2221.75 | 0 | 17037.25 | -3497.25 | 1350000 | 17037.25 | 0
2021040301 | 7 | 0.53982 | 80973 | 0.7296 | 0 | 0.24803 | 3100.375 | 0 | 0 | 64000 | 3100.375 | 0 | 13872.625 | -3164.625 | 1350000 | 13872.625 | 0
2021040302 | 7 | 0.53112 | 79668 | 0.71327 | 0 | 0.28605 | 3575.625 | 0 | 0 | 64000 | 3575.625 | 0 | 12092.375 | -1780.25 | 1350000 | 12092.375 | 0
2021040303 | 7 | 0.52917 | 79375.5 | 0.70409 | 0 | 0.31462 | 3932.75 | 0 | 0 | 64000 | 3932.75 | 0 | 11442.75 | -649.625 | 1350000 | 11442.75 | 0
2021040304 | 7 | 0.53142 | 79713 | 0.66189 | 0 | 0.31873 | 3984.125 | 0 | 0 | 64000 | 3984.125 | 0 | 11728.875 | 286.125 | 1350000 | 11728.875 | 0
2021040305 | 7 | 0.53934 | 80901 | 0.63889 | 0 | 0.2952 | 3690 | 0 | 0 | 64000 | 3690 | 0 | 13211 | 1482.125 | 1350000 | 13211 | 0
2021040306 | 7 | 0.55333 | 82999.5 | 0.60667 | 0 | 0.20701 | 2587.625 | 0 | 0 | 64000 | 2587.625 | 0 | 16411.875 | 3200.875 | 1350000 | 16411.875 | 0
2021040307 | 7 | 0.57477 | 86215.5 | 0.62347 | 0 | 0.12261 | 1532.625 | 0 | 0 | 64000 | 1532.625 | 0 | 20682.875 | 4271 | 1350000 | 20682.875 | 0
2021040308 | 7 | 0.59047 | 88570.5 | 0.60733 | 0 | 0.07855 | 981.875 | 0.03921 | 3136.8 | 64000 | 981.875 | 3136.8 | 20451.825 | -231.05 | 1350000 | 20451.825 | 0
2021040309 | 7 | 0.58557 | 87835.5 | 0.47829 | 0 | 0.05314 | 664.25 | 0.30155 | 24124 | 64000 | 664.25 | 23171.25 | 0 | -20451.825 | 1350000 | 0 | 0
2021040310 | 7 | 0.56876 | 85314 | 0.30203 | 0 | 0.0442 | 552.5 | 0.52502 | 42001.6 | 64000 | 552.5 | 20761.5 | 0 | 0 | 1350000 | 0 | 0
2021040311 | 7 | 0.54801 | 82201.5 | 0.21959 | 0 | 0.03306 | 413.25 | 0.59554 | 47643.2 | 64000 | 413.25 | 17788.25 | 0 | 0 | 1350000 | 0 | 0
2021040312 | 7 | 0.53012 | 79518 | 0.15909 | 0 | 0.02466 | 308.25 | 0.61091 | 48872.8 | 64000 | 308.25 | 15209.75 | 0 | 0 | 1350000 | 0 | 0
2021040313 | 7 | 0.51142 | 76713 | 0.10985 | 0 | 0.02219 | 277.375 | 0.63905 | 51124 | 64000 | 277.375 | 12435.625 | 0 | 0 | 1350000 | 0 | 0
2021040314 | 7 | 0.49384 | 74076 | 0.09157 | 0 | 0.02645 | 330.625 | 0.64759 | 51807.2 | 64000 | 330.625 | 9745.375 | 0 | 0 | 1350000 | 0 | 0
2021040315 | 7 | 0.47934 | 71901 | 0.1241 | 0 | 0.03104 | 388 | 0.66268 | 53014.4 | 64000 | 388 | 7513 | 0 | 0 | 1350000 | 0 | 0
2021040316 | 7 | 0.47023 | 70534.5 | 0.20334 | 0 | 0.02678 | 334.75 | 0.655 | 52400 | 64000 | 334.75 | 6199.75 | 0 | 0 | 1350000 | 0 | 0
2021040317 | 7 | 0.46985 | 70477.5 | 0.19575 | 0 | 0.04462 | 557.75 | 0.55194 | 44155.2 | 64000 | 557.75 | 5919.75 | 0 | 0 | 1350000 | 0 | 0
2021040318 | 7 | 0.47902 | 71853 | 0.15634 | 0 | 0.09597 | 1199.625 | 0.29734 | 23787.2 | 64000 | 1199.625 | 6653.375 | 0 | 0 | 1350000 | 0 | 0
2021040319 | 7 | 0.49072 | 73608 | 0.14284 | 0 | 0.09843 | 1230.375 | 0.04927 | 3941.6 | 64000 | 1230.375 | 3941.6 | 4436.025 | 4436.025 | 1350000 | 4436.025 | 0
2021040320 | 7 | 0.50784 | 76176 | 0.10665 | 0 | 0.10443 | 1305.375 | 0 | 0 | 64000 | 1305.375 | 0 | 10870.625 | 6434.6 | 1350000 | 10870.625 | 0
2021040321 | 7 | 0.52721 | 79081.5 | 0.22317 | 0 | 0.12746 | 1593.25 | 0 | 0 | 64000 | 1593.25 | 0 | 13488.25 | 2617.625 | 1350000 | 13488.25 | 0
2021040322 | 7 | 0.52486 | 78729 | 0.37553 | 0 | 0.16757 | 2094.625 | 0 | 0 | 64000 | 2094.625 | 0 | 12634.375 | -853.875 | 1350000 | 12634.375 | 0
2021040323 | 7 | 0.50959 | 76438.5 | 0.52036 | 0 | 0.20441 | 2555.125 | 0 | 0 | 64000 | 2555.125 | 0 | 9883.375 | -2751 | 1350000 | 9883.375 | 0
2021040324 | 7 | 0.48939 | 73408.5 | 0.55317 | 0 | 0.23649 | 2956.125 | 0 | 0 | 64000 | 2956.125 | 0 | 6452.375 | -3431 | 1350000 | 6452.375 | 0
2021040401 | 1 | 0.47213 | 70819.5 | 0.64006 | 0 | 0.25282 | 3160.25 | 0 | 0 | 64000 | 3160.25 | 0 | 3659.25 | -2793.125 | 1350000 | 3659.25 | 0
2021040402 | 1 | 0.45966 | 68949 | 0.75226 | 0 | 0.24843 | 3105.375 | 0 | 0 | 64000 | 3105.375 | 0 | 1843.625 | -1815.625 | 1350000 | 1843.625 | 0
2021040403 | 1 | 0.45519 | 68278.5 | 0.75394 | 0 | 0.21464 | 2683 | 0 | 0 | 64000 | 2683 | 0 | 1595.5 | -248.125 | 1350000 | 1595.5 | 0
2021040404 | 1 | 0.45249 | 67873.5 | 0.72804 | 0 | 0.20818 | 2602.25 | 0 | 0 | 64000 | 2602.25 | 0 | 1271.25 | -324.25 | 1350000 | 1271.25 | 0
2021040405 | 1 | 0.45588 | 68382 | 0.72094 | 0 | 0.18223 | 2277.875 | 0 | 0 | 64000 | 2277.875 | 0 | 2104.125 | 832.875 | 1350000 | 2104.125 | 0
2021040406 | 1 | 0.46509 | 69763.5 | 0.75626 | 0 | 0.12489 | 1561.125 | 0 | 0 | 64000 | 1561.125 | 0 | 4202.375 | 2098.25 | 1350000 | 4202.375 | 0
2021040407 | 1 | 0.48053 | 72079.5 | 0.75973 | 0 | 0.0657 | 821.25 | 0 | 0 | 64000 | 821.25 | 0 | 7258.25 | 3055.875 | 1350000 | 7258.25 | 0
2021040408 | 1 | 0.49359 | 74038.5 | 0.73914 | 0 | 0.03793 | 474.125 | 0.04731 | 3784.8 | 64000 | 474.125 | 3784.8 | 5779.575 | -1478.675 | 1350000 | 5779.575 | 0
2021040409 | 1 | 0.50255 | 75382.5 | 0.66022 | 0 | 0.0395 | 493.75 | 0.31244 | 24995.2 | 64000 | 493.75 | 10888.75 | 0 | -5779.575 | 1350000 | 0 | 0
2021040410 | 1 | 0.49716 | 74574 | 0.5174 | 0 | 0.04156 | 519.5 | 0.51488 | 41190.4 | 64000 | 519.5 | 10054.5 | 0 | 0 | 1350000 | 0 | 0
2021040411 | 1 | 0.48284 | 72426 | 0.44806 | 0 | 0.04043 | 505.375 | 0.56465 | 45172 | 64000 | 505.375 | 7920.625 | 0 | 0 | 1350000 | 0 | 0
2021040412 | 1 | 0.46978 | 70467 | 0.58329 | 0 | 0.04373 | 546.625 | 0.57031 | 45624.8 | 64000 | 546.625 | 5920.375 | 0 | 0 | 1350000 | 0 | 0
2021040413 | 1 | 0.46037 | 69055.5 | 0.7321 | 0 | 0.04341 | 542.625 | 0.60745 | 48596 | 64000 | 542.625 | 4512.875 | 0 | 0 | 1350000 | 0 | 0
2021040414 | 1 | 0.4505 | 67575 | 0.78744 | 0 | 0.03918 | 489.75 | 0.6234 | 49872 | 64000 | 489.75 | 3085.25 | 0 | 0 | 1350000 | 0 | 0
2021040415 | 1 | 0.44307 | 66460.5 | 0.82104 | 0 | 0.03332 | 416.5 | 0.62262 | 49809.6 | 64000 | 416.5 | 2044 | 0 | 0 | 1350000 | 0 | 0
2021040416 | 1 | 0.44101 | 66151.5 | 0.86105 | 0 | 0.03314 | 414.25 | 0.59274 | 47419.2 | 64000 | 414.25 | 1737.25 | 0 | 0 | 1350000 | 0 | 0
2021040417 | 1 | 0.44365 | 66547.5 | 0.89822 | 0 | 0.08417 | 1052.125 | 0.52696 | 42156.8 | 64000 | 1052.125 | 1495.375 | 0 | 0 | 1350000 | 0 | 0
2021040418 | 1 | 0.45166 | 67749 | 0.91368 | 0 | 0.14526 | 1815.75 | 0.29599 | 23679.2 | 64000 | 1815.75 | 1933.25 | 0 | 0 | 1350000 | 0 | 0
2021040419 | 1 | 0.46121 | 69181.5 | 0.8838 | 0 | 0.15103 | 1887.875 | 0.04425 | 3540 | 64000 | 1887.875 | 3293.625 | 0 | 0 | 1350000 | 0 | 0
2021040420 | 1 | 0.47421 | 71131.5 | 0.78857 | 0 | 0.13244 | 1655.5 | 0 | 0 | 64000 | 1655.5 | 0 | 5476 | 5476 | 1350000 | 5476 | 0
2021040421 | 1 | 0.49415 | 74122.5 | 0.74613 | 0 | 0.14754 | 1844.25 | 0 | 0 | 64000 | 1844.25 | 0 | 8278.25 | 2802.25 | 1350000 | 8278.25 | 0
2021040422 | 1 | 0.48715 | 73072.5 | 0.73368 | 0 | 0.18483 | 2310.375 | 0 | 0 | 64000 | 2310.375 | 0 | 6762.125 | -1516.125 | 1350000 | 6762.125 | 0
2021040423 | 1 | 0.46795 | 70192.5 | 0.71764 | 0 | 0.21848 | 2731 | 0 | 0 | 64000 | 2731 | 0 | 3461.5 | -3300.625 | 1350000 | 3461.5 | 0
2021040424 | 1 | 0.44657 | 66985.5 | 0.66699 | 0 | 0.23867 | 2983.375 | 0 | 0 | 64000 | 2983.375 | 0 | 2.125 | -3459.375 | 1350000 | 2.125 | 0
2021040501 | 2 | 0.43006 | 64509 | 0.60814 | 0 | 0.25376 | 3172 | 0 | 0 | 64000 | 509 | 0 | 0 | -2.125 | 1350000 | 0 | 0
2021040502 | 2 | 0.42281 | 63421.5 | 0.59738 | 0 | 0.25535 | 3191.875 | 0 | 0 | 63421.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040503 | 2 | 0.42164 | 63246 | 0.61788 | 0 | 0.25187 | 3148.375 | 0 | 0 | 63246 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040504 | 2 | 0.42556 | 63834 | 0.60387 | 0 | 0.26462 | 3307.75 | 0 | 0 | 63834 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040505 | 2 | 0.43888 | 65832 | 0.57922 | 0 | 0.26313 | 3289.125 | 0 | 0 | 64000 | 1832 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040506 | 2 | 0.46896 | 70344 | 0.60211 | 0 | 0.21885 | 2735.625 | 0 | 0 | 64000 | 2735.625 | 0 | 3608.375 | 3608.375 | 1350000 | 3608.375 | 0
2021040507 | 2 | 0.51242 | 76863 | 0.58482 | 0 | 0.14651 | 1831.375 | 0 | 0 | 64000 | 1831.375 | 0 | 11031.625 | 7423.25 | 1350000 | 11031.625 | 0
2021040508 | 2 | 0.54267 | 81400.5 | 0.54671 | 0 | 0.11144 | 1393 | 0.03958 | 3166.4 | 64000 | 1393 | 3166.4 | 12841.1 | 1809.475 | 1350000 | 12841.1 | 0
2021040509 | 2 | 0.54819 | 82228.5 | 0.4423 | 0 | 0.10153 | 1269.125 | 0.23849 | 19079.2 | 64000 | 1269.125 | 16959.375 | 0 | -12841.1 | 1350000 | 0 | 0
2021040510 | 2 | 0.54204 | 81306 | 0.40222 | 0 | 0.10128 | 1266 | 0.4604 | 36832 | 64000 | 1266 | 16040 | 0 | 0 | 1350000 | 0 | 0
2021040511 | 2 | 0.53763 | 80644.5 | 0.44884 | 0 | 0.09391 | 1173.875 | 0.49061 | 39248.8 | 64000 | 1173.875 | 15470.625 | 0 | 0 | 1350000 | 0 | 0
2021040512 | 2 | 0.53274 | 79911 | 0.41446 | 0 | 0.09357 | 1169.625 | 0.50915 | 40732 | 64000 | 1169.625 | 14741.375 | 0 | 0 | 1350000 | 0 | 0
2021040513 | 2 | 0.52894 | 79341 | 0.41583 | 0 | 0.10389 | 1298.625 | 0.49678 | 39742.4 | 64000 | 1298.625 | 14042.375 | 0 | 0 | 1350000 | 0 | 0
2021040514 | 2 | 0.52709 | 79063.5 | 0.46927 | 0 | 0.12276 | 1534.5 | 0.48595 | 38876 | 64000 | 1534.5 | 13529 | 0 | 0 | 1350000 | 0 | 0
2021040515 | 2 | 0.52273 | 78409.5 | 0.54256 | 0 | 0.13088 | 1636 | 0.52634 | 42107.2 | 64000 | 1636 | 12773.5 | 0 | 0 | 1350000 | 0 | 0
2021040516 | 2 | 0.52104 | 78156 | 0.56994 | 0 | 0.13097 | 1637.125 | 0.51038 | 40830.4 | 64000 | 1637.125 | 12518.875 | 0 | 0 | 1350000 | 0 | 0
2021040517 | 2 | 0.52388 | 78582 | 0.66976 | 0 | 0.17033 | 2129.125 | 0.51752 | 41401.6 | 64000 | 2129.125 | 12452.875 | 0 | 0 | 1350000 | 0 | 0
2021040518 | 2 | 0.53104 | 79656 | 0.6627 | 0 | 0.22191 | 2773.875 | 0.30815 | 24652 | 64000 | 2773.875 | 12882.125 | 0 | 0 | 1350000 | 0 | 0
2021040519 | 2 | 0.53655 | 80482.5 | 0.58807 | 0 | 0.23369 | 2921.125 | 0.05323 | 4258.4 | 64000 | 2921.125 | 4258.4 | 9302.975 | 9302.975 | 1350000 | 9302.975 | 0
2021040520 | 2 | 0.54572 | 81858 | 0.46874 | 0 | 0.26904 | 3363 | 0 | 0 | 64000 | 3363 | 0 | 14495 | 5192.025 | 1350000 | 14495 | 0
2021040521 | 2 | 0.55491 | 83236.5 | 0.40052 | 0 | 0.26936 | 3367 | 0 | 0 | 64000 | 3367 | 0 | 15869.5 | 1374.5 | 1350000 | 15869.5 | 0
2021040522 | 2 | 0.53678 | 80517 | 0.35563 | 0 | 0.26154 | 3269.25 | 0 | 0 | 64000 | 3269.25 | 0 | 13247.75 | -2621.75 | 1350000 | 13247.75 | 0
2021040523 | 2 | 0.50564 | 75846 | 0.26534 | 0 | 0.27593 | 3449.125 | 0 | 0 | 64000 | 3449.125 | 0 | 8396.875 | -4850.875 | 1350000 | 8396.875 | 0
2021040524 | 2 | 0.4746 | 71190 | 0.24365 | 0 | 0.29916 | 3739.5 | 0 | 0 | 64000 | 3739.5 | 0 | 3450.5 | -4946.375 | 1350000 | 3450.5 | 0
2021040601 | 3 | 0.45049 | 67573.5 | 0.235 | 0 | 0.33916 | 4239.5 | 0 | 0 | 64000 | 3573.5 | 0 | 0 | -3450.5 | 1350000 | 0 | 0
2021040602 | 3 | 0.43628 | 65442 | 0.23557 | 0 | 0.35346 | 4418.25 | 0 | 0 | 64000 | 1442 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040603 | 3 | 0.43015 | 64522.5 | 0.24957 | 0 | 0.38711 | 4838.875 | 0 | 0 | 64000 | 522.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040604 | 3 | 0.42824 | 64236 | 0.27283 | 0 | 0.41603 | 5200.375 | 0 | 0 | 64000 | 236 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040605 | 3 | 0.4378 | 65670 | 0.30264 | 0 | 0.41207 | 5150.875 | 0 | 0 | 64000 | 1670 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040606 | 3 | 0.46278 | 69417 | 0.29095 | 0 | 0.40615 | 5076.875 | 0 | 0 | 64000 | 5076.875 | 0 | 340.125 | 340.125 | 1350000 | 340.125 | 0
2021040607 | 3 | 0.50627 | 75940.5 | 0.28638 | 0 | 0.39583 | 4947.875 | 0 | 0 | 64000 | 4947.875 | 0 | 6992.625 | 6652.5 | 1350000 | 6992.625 | 0
2021040608 | 3 | 0.53369 | 80053.5 | 0.26251 | 0 | 0.46219 | 5777.375 | 0.05836 | 4668.8 | 64000 | 5777.375 | 4668.8 | 5607.325 | -1385.3 | 1350000 | 5607.325 | 0
2021040609 | 3 | 0.54059 | 81088.5 | 0.19284 | 0 | 0.54226 | 6778.25 | 0.35016 | 28012.8 | 64000 | 6778.25 | 10310.25 | 0 | -5607.325 | 1350000 | 0 | 0
2021040610 | 3 | 0.53684 | 80526 | 0.17874 | 0 | 0.57013 | 7126.625 | 0.58862 | 47089.6 | 64000 | 7126.625 | 9399.375 | 0 | 0 | 1350000 | 0 | 0
2021040611 | 3 | 0.53384 | 80076 | 0.19751 | 0 | 0.564 | 7050 | 0.65506 | 52404.8 | 64000 | 7050 | 9026 | 0 | 0 | 1350000 | 0 | 0
2021040612 | 3 | 0.53324 | 79986 | 0.2496 | 0 | 0.56415 | 7051.875 | 0.67343 | 53874.4 | 64000 | 7051.875 | 8934.125 | 0 | 0 | 1350000 | 0 | 0
2021040613 | 3 | 0.53331 | 79996.5 | 0.35794 | 0 | 0.57026 | 7128.25 | 0.6784 | 54272 | 64000 | 7128.25 | 8868.25 | 0 | 0 | 1350000 | 0 | 0
2021040614 | 3 | 0.53527 | 80290.5 | 0.47186 | 0 | 0.60798 | 7599.75 | 0.6905 | 55240 | 64000 | 7599.75 | 8690.75 | 0 | 0 | 1350000 | 0 | 0
2021040615 | 3 | 0.5366 | 80490 | 0.51229 | 0 | 0.63329 | 7916.125 | 0.70094 | 56075.2 | 64000 | 7916.125 | 8573.875 | 0 | 0 | 1350000 | 0 | 0
2021040616 | 3 | 0.53817 | 80725.5 | 0.50218 | 0 | 0.62123 | 7765.375 | 0.68862 | 55089.6 | 64000 | 7765.375 | 8960.125 | 0 | 0 | 1350000 | 0 | 0
2021040617 | 3 | 0.54478 | 81717 | 0.50564 | 0 | 0.61233 | 7654.125 | 0.62547 | 50037.6 | 64000 | 7654.125 | 10062.875 | 0 | 0 | 1350000 | 0 | 0
2021040618 | 3 | 0.55035 | 82552.5 | 0.44033 | 0 | 0.67916 | 8489.5 | 0.38568 | 30854.4 | 64000 | 8489.5 | 10063 | 0 | 0 | 1350000 | 0 | 0
2021040619 | 3 | 0.55428 | 83142 | 0.34389 | 0 | 0.72005 | 9000.625 | 0.08952 | 7161.6 | 64000 | 9000.625 | 7161.6 | 2979.775 | 2979.775 | 1350000 | 2979.775 | 0
2021040620 | 3 | 0.55764 | 83646 | 0.25396 | 0 | 0.72814 | 9101.75 | 0 | 0 | 64000 | 9101.75 | 0 | 10544.25 | 7564.475 | 1350000 | 10544.25 | 0
2021040621 | 3 | 0.56651 | 84976.5 | 0.17907 | 0 | 0.74414 | 9301.75 | 0 | 0 | 64000 | 9301.75 | 0 | 11674.75 | 1130.5 | 1350000 | 11674.75 | 0
2021040622 | 3 | 0.54818 | 82227 | 0.12408 | 0 | 0.72998 | 9124.75 | 0 | 0 | 64000 | 9124.75 | 0 | 9102.25 | -2572.5 | 1350000 | 9102.25 | 0
2021040623 | 3 | 0.51497 | 77245.5 | 0.09431 | 0 | 0.74894 | 9361.75 | 0 | 0 | 64000 | 9361.75 | 0 | 3883.75 | -5218.5 | 1350000 | 3883.75 | 0
2021040624 | 3 | 0.48105 | 72157.5 | 0.10818 | 0 | 0.74288 | 9286 | 0 | 0 | 64000 | 8157.5 | 0 | 0 | -3883.75 | 1350000 | 0 | 0
2021040701 | 4 | 0.45292 | 67938 | 0.1445 | 0 | 0.74432 | 9304 | 0 | 0 | 64000 | 3938 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040702 | 4 | 0.43616 | 65424 | 0.15716 | 0 | 0.74393 | 9299.125 | 0 | 0 | 64000 | 1424 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040703 | 4 | 0.42797 | 64195.5 | 0.20698 | 0 | 0.7434 | 9292.5 | 0 | 0 | 64000 | 195.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040704 | 4 | 0.42387 | 63580.5 | 0.27781 | 0 | 0.73556 | 9194.5 | 0 | 0 | 63580.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040705 | 4 | 0.43117 | 64675.5 | 0.29352 | 0 | 0.71759 | 8969.875 | 0 | 0 | 64000 | 675.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040706 | 4 | 0.45362 | 68043 | 0.2738 | 0 | 0.66279 | 8284.875 | 0 | 0 | 64000 | 4043 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040707 | 4 | 0.49419 | 74128.5 | 0.28141 | 0 | 0.58675 | 7334.375 | 0 | 0 | 64000 | 7334.375 | 0 | 2794.125 | 2794.125 | 1350000 | 2794.125 | 0
2021040708 | 4 | 0.52074 | 78111 | 0.31162 | 0 | 0.56188 | 7023.5 | 0.06269 | 5015.2 | 64000 | 7023.5 | 5015.2 | 2072.3 | -721.825 | 1350000 | 2072.3 | 0
2021040709 | 4 | 0.53389 | 80083.5 | 0.24477 | 0 | 0.61056 | 7632 | 0.37996 | 30396.8 | 64000 | 7632 | 8451.5 | 0 | -2072.3 | 1350000 | 0 | 0
2021040710 | 4 | 0.53918 | 80877 | 0.172 | 0 | 0.59981 | 7497.625 | 0.62488 | 49990.4 | 64000 | 7497.625 | 9379.375 | 0 | 0 | 1350000 | 0 | 0
2021040711 | 4 | 0.54307 | 81460.5 | 0.18683 | 0 | 0.60992 | 7624 | 0.69027 | 55221.6 | 64000 | 7624 | 9836.5 | 0 | 0 | 1350000 | 0 | 0
2021040712 | 4 | 0.54418 | 81627 | 0.23951 | 0 | 0.63578 | 7947.25 | 0.70605 | 56484 | 64000 | 7947.25 | 9679.75 | 0 | 0 | 1350000 | 0 | 0
2021040713 | 4 | 0.54827 | 82240.5 | 0.23047 | 0 | 0.62128 | 7766 | 0.70915 | 56732 | 64000 | 7766 | 10474.5 | 0 | 0 | 1350000 | 0 | 0
2021040714 | 4 | 0.55271 | 82906.5 | 0.22302 | 0 | 0.56116 | 7014.5 | 0.71596 | 57276.8 | 64000 | 7014.5 | 11892 | 0 | 0 | 1350000 | 0 | 0
2021040715 | 4 | 0.55651 | 83476.5 | 0.20219 | 0 | 0.48678 | 6084.75 | 0.72723 | 58178.4 | 64000 | 6084.75 | 13391.75 | 0 | 0 | 1350000 | 0 | 0
2021040716 | 4 | 0.56163 | 84244.5 | 0.1576 | 0 | 0.39441 | 4930.125 | 0.71255 | 57004 | 64000 | 4930.125 | 15314.375 | 0 | 0 | 1350000 | 0 | 0
2021040717 | 4 | 0.56695 | 85042.5 | 0.14396 | 0 | 0.42291 | 5286.375 | 0.65615 | 52492 | 64000 | 5286.375 | 15756.125 | 0 | 0 | 1350000 | 0 | 0
2021040718 | 4 | 0.57057 | 85585.5 | 0.15904 | 0 | 0.55512 | 6939 | 0.4034 | 32272 | 64000 | 6939 | 14646.5 | 0 | 0 | 1350000 | 0 | 0
2021040719 | 4 | 0.57097 | 85645.5 | 0.1128 | 0 | 0.56948 | 7118.5 | 0.06745 | 5396 | 64000 | 7118.5 | 5396 | 9131 | 9131 | 1350000 | 9131 | 0
2021040720 | 4 | 0.57155 | 85732.5 | 0.06046 | 0 | 0.5689 | 7111.25 | 0 | 0 | 64000 | 7111.25 | 0 | 14621.25 | 5490.25 | 1350000 | 14621.25 | 0
2021040721 | 4 | 0.57725 | 86587.5 | 0.07213 | 0 | 0.56175 | 7021.875 | 0 | 0 | 64000 | 7021.875 | 0 | 15565.625 | 944.375 | 1350000 | 15565.625 | 0
2021040722 | 4 | 0.55647 | 83470.5 | 0.08719 | 0 | 0.54048 | 6756 | 0 | 0 | 64000 | 6756 | 0 | 12714.5 | -2851.125 | 1350000 | 12714.5 | 0
2021040723 | 4 | 0.52123 | 78184.5 | 0.16893 | 0 | 0.51072 | 6384 | 0 | 0 | 64000 | 6384 | 0 | 7800.5 | -4914 | 1350000 | 7800.5 | 0
2021040724 | 4 | 0.48567 | 72850.5 | 0.28134 | 0 | 0.4898 | 6122.5 | 0 | 0 | 64000 | 6122.5 | 0 | 2728 | -5072.5 | 1350000 | 2728 | 0
2021040801 | 5 | 0.4559 | 68385 | 0.39669 | 0 | 0.43376 | 5422 | 0 | 0 | 64000 | 4385 | 0 | 0 | -2728 | 1350000 | 0 | 0
2021040802 | 5 | 0.43759 | 65638.5 | 0.43956 | 0 | 0.40218 | 5027.25 | 0 | 0 | 64000 | 1638.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040803 | 5 | 0.42728 | 64092 | 0.50413 | 0 | 0.35651 | 4456.375 | 0 | 0 | 64000 | 92 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040804 | 5 | 0.42287 | 63430.5 | 0.60999 | 0 | 0.29332 | 3666.5 | 0 | 0 | 63430.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040805 | 5 | 0.43052 | 64578 | 0.6707 | 0 | 0.21476 | 2684.5 | 0 | 0 | 64000 | 578 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040806 | 5 | 0.45159 | 67738.5 | 0.71603 | 0 | 0.15919 | 1989.875 | 0 | 0 | 64000 | 1989.875 | 0 | 1748.625 | 1748.625 | 1350000 | 1748.625 | 0
2021040807 | 5 | 0.48979 | 73468.5 | 0.74999 | 0 | 0.14622 | 1827.75 | 0 | 0 | 64000 | 1827.75 | 0 | 7640.75 | 5892.125 | 1350000 | 7640.75 | 0
2021040808 | 5 | 0.51657 | 77485.5 | 0.78555 | 0 | 0.19142 | 2392.75 | 0.06551 | 5240.8 | 64000 | 2392.75 | 5240.8 | 5851.95 | -1788.8 | 1350000 | 5851.95 | 0
2021040809 | 5 | 0.52788 | 79182 | 0.75917 | 0 | 0.26271 | 3283.875 | 0.31453 | 25162.4 | 64000 | 3283.875 | 11898.125 | 0 | -5851.95 | 1350000 | 0 | 0
2021040810 | 5 | 0.53139 | 79708.5 | 0.72131 | 0 | 0.28784 | 3598 | 0.52049 | 41639.2 | 64000 | 3598 | 12110.5 | 0 | 0 | 1350000 | 0 | 0
2021040811 | 5 | 0.53576 | 80364 | 0.67578 | 0 | 0.32285 | 4035.625 | 0.64607 | 51685.6 | 64000 | 4035.625 | 12328.375 | 0 | 0 | 1350000 | 0 | 0
2021040812 | 5 | 0.53772 | 80658 | 0.68552 | 0 | 0.36282 | 4535.25 | 0.67906 | 54324.8 | 64000 | 4535.25 | 12122.75 | 0 | 0 | 1350000 | 0 | 0
2021040813 | 5 | 0.54136 | 81204 | 0.70994 | 0 | 0.34692 | 4336.5 | 0.69667 | 55733.6 | 64000 | 4336.5 | 12867.5 | 0 | 0 | 1350000 | 0 | 0
2021040814 | 5 | 0.54384 | 81576 | 0.71048 | 0 | 0.26648 | 3331 | 0.67657 | 54125.6 | 64000 | 3331 | 14245 | 0 | 0 | 1350000 | 0 | 0
2021040815 | 5 | 0.54372 | 81558 | 0.71419 | 0 | 0.15563 | 1945.375 | 0.67741 | 54192.8 | 64000 | 1945.375 | 15612.625 | 0 | 0 | 1350000 | 0 | 0
2021040816 | 5 | 0.54368 | 81552 | 0.74504 | 0 | 0.09799 | 1224.875 | 0.67673 | 54138.4 | 64000 | 1224.875 | 16327.125 | 0 | 0 | 1350000 | 0 | 0
2021040817 | 5 | 0.54356 | 81534 | 0.77771 | 0 | 0.09688 | 1211 | 0.63145 | 50516 | 64000 | 1211 | 16323 | 0 | 0 | 1350000 | 0 | 0
2021040818 | 5 | 0.54827 | 82240.5 | 0.81955 | 0 | 0.16031 | 2003.875 | 0.39968 | 31974.4 | 64000 | 2003.875 | 16236.625 | 0 | 0 | 1350000 | 0 | 0
2021040819 | 5 | 0.54673 | 82009.5 | 0.86272 | 0 | 0.18266 | 2283.25 | 0.08311 | 6648.8 | 64000 | 2283.25 | 6648.8 | 9077.45 | 9077.45 | 1350000 | 9077.45 | 0
2021040820 | 5 | 0.54931 | 82396.5 | 0.90009 | 0 | 0.24152 | 3019 | 0.00197 | 157.6 | 64000 | 3019 | 157.6 | 15219.9 | 6142.45 | 1350000 | 15219.9 | 0
2021040821 | 5 | 0.55558 | 83337 | 0.93683 | 0 | 0.27613 | 3451.625 | 0 | 0 | 64000 | 3451.625 | 0 | 15885.375 | 665.475 | 1350000 | 15885.375 | 0
2021040822 | 5 | 0.5358 | 80370 | 0.94721 | 0 | 0.31592 | 3949 | 0 | 0 | 64000 | 3949 | 0 | 12421 | -3464.375 | 1350000 | 12421 | 0
2021040823 | 5 | 0.50477 | 75715.5 | 0.93833 | 0 | 0.31395 | 3924.375 | 0 | 0 | 64000 | 3924.375 | 0 | 7791.125 | -4629.875 | 1350000 | 7791.125 | 0
2021040824 | 5 | 0.47246 | 70869 | 0.9388 | 0 | 0.35872 | 4484 | 0 | 0 | 64000 | 4484 | 0 | 2385 | -5406.125 | 1350000 | 2385 | 0
2021040901 | 6 | 0.44714 | 67071 | 0.95407 | 0 | 0.44749 | 5593.625 | 0 | 0 | 64000 | 3071 | 0 | 0 | -2385 | 1350000 | 0 | 0
2021040902 | 6 | 0.4311 | 64665 | 0.95156 | 0 | 0.49557 | 6194.625 | 0 | 0 | 64000 | 665 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040903 | 6 | 0.42217 | 63325.5 | 0.93827 | 0 | 0.549 | 6862.5 | 0 | 0 | 63325.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040904 | 6 | 0.41866 | 62799 | 0.92881 | 0 | 0.57208 | 7151 | 0 | 0 | 62799 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040905 | 6 | 0.42494 | 63741 | 0.90575 | 0 | 0.58733 | 7341.625 | 0 | 0 | 63741 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040906 | 6 | 0.44729 | 67093.5 | 0.87302 | 0 | 0.4897 | 6121.25 | 0 | 0 | 64000 | 3093.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021040907 | 6 | 0.48325 | 72487.5 | 0.82318 | 0 | 0.41688 | 5211 | 0 | 0 | 64000 | 5211 | 0 | 3276.5 | 3276.5 | 1350000 | 3276.5 | 0
2021040908 | 6 | 0.51388 | 77082 | 0.78058 | 0 | 0.45041 | 5630.125 | 0.07522 | 6017.6 | 64000 | 5630.125 | 6017.6 | 1434.275 | -1842.225 | 1350000 | 1434.275 | 0
2021040909 | 6 | 0.52936 | 79404 | 0.74592 | 0 | 0.51192 | 6399 | 0.37984 | 30387.2 | 64000 | 6399 | 9005 | 0 | -1434.275 | 1350000 | 0 | 0
2021040910 | 6 | 0.53694 | 80541 | 0.71292 | 0 | 0.52104 | 6513 | 0.62749 | 50199.2 | 64000 | 6513 | 10028 | 0 | 0 | 1350000 | 0 | 0
2021040911 | 6 | 0.54126 | 81189 | 0.6859 | 0 | 0.4964 | 6205 | 0.69859 | 55887.2 | 64000 | 6205 | 10984 | 0 | 0 | 1350000 | 0 | 0
2021040912 | 6 | 0.54514 | 81771 | 0.65243 | 0 | 0.4711 | 5888.75 | 0.71785 | 57428 | 64000 | 5888.75 | 11882.25 | 0 | 0 | 1350000 | 0 | 0
2021040913 | 6 | 0.54707 | 82060.5 | 0.59757 | 0 | 0.44439 | 5554.875 | 0.73066 | 58452.8 | 64000 | 5554.875 | 12505.625 | 0 | 0 | 1350000 | 0 | 0
2021040914 | 6 | 0.54907 | 82360.5 | 0.54978 | 0 | 0.4372 | 5465 | 0.73556 | 58844.8 | 64000 | 5465 | 12895.5 | 0 | 0 | 1350000 | 0 | 0
2021040915 | 6 | 0.5471 | 82065 | 0.50485 | 0 | 0.39441 | 4930.125 | 0.73679 | 58943.2 | 64000 | 4930.125 | 13134.875 | 0 | 0 | 1350000 | 0 | 0
2021040916 | 6 | 0.54219 | 81328.5 | 0.49955 | 0 | 0.28151 | 3518.875 | 0.70895 | 56716 | 64000 | 3518.875 | 13809.625 | 0 | 0 | 1350000 | 0 | 0
2021040917 | 6 | 0.54154 | 81231 | 0.49684 | 0 | 0.34904 | 4363 | 0.61715 | 49372 | 64000 | 4363 | 12868 | 0 | 0 | 1350000 | 0 | 0
2021040918 | 6 | 0.5415 | 81225 | 0.43963 | 0 | 0.47533 | 5941.625 | 0.35013 | 28010.4 | 64000 | 5941.625 | 11283.375 | 0 | 0 | 1350000 | 0 | 0
2021040919 | 6 | 0.53822 | 80733 | 0.36783 | 0 | 0.47643 | 5955.375 | 0.06915 | 5532 | 64000 | 5955.375 | 5532 | 5245.625 | 5245.625 | 1350000 | 5245.625 | 0
2021040920 | 6 | 0.53829 | 80743.5 | 0.39614 | 0 | 0.43966 | 5495.75 | 0.00199 | 159.2 | 64000 | 5495.75 | 159.2 | 11088.55 | 5842.925 | 1350000 | 11088.55 | 0
2021040921 | 6 | 0.53851 | 80776.5 | 0.48668 | 0 | 0.38345 | 4793.125 | 0 | 0 | 64000 | 4793.125 | 0 | 11983.375 | 894.825 | 1350000 | 11983.375 | 0
2021040922 | 6 | 0.52394 | 78591 | 0.44526 | 0 | 0.36023 | 4502.875 | 0 | 0 | 64000 | 4502.875 | 0 | 10088.125 | -1895.25 | 1350000 | 10088.125 | 0
2021040923 | 6 | 0.49561 | 74341.5 | 0.45199 | 0 | 0.34669 | 4333.625 | 0 | 0 | 64000 | 4333.625 | 0 | 6007.875 | -4080.25 | 1350000 | 6007.875 | 0
2021040924 | 6 | 0.46723 | 70084.5 | 0.51956 | 0 | 0.3306 | 4132.5 | 0 | 0 | 64000 | 4132.5 | 0 | 1952 | -4055.875 | 1350000 | 1952 | 0
2021041001 | 7 | 0.4419 | 66285 | 0.52152 | 0 | 0.28025 | 3503.125 | 0 | 0 | 64000 | 2285 | 0 | 0 | -1952 | 1350000 | 0 | 0
2021041002 | 7 | 0.42499 | 63748.5 | 0.43314 | 0 | 0.20855 | 2606.875 | 0 | 0 | 63748.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041003 | 7 | 0.41493 | 62239.5 | 0.40616 | 0 | 0.19858 | 2482.25 | 0 | 0 | 62239.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041004 | 7 | 0.40954 | 61431 | 0.45702 | 0 | 0.20395 | 2549.375 | 0 | 0 | 61431 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041005 | 7 | 0.41104 | 61656 | 0.40546 | 0 | 0.19037 | 2379.625 | 0 | 0 | 61656 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041006 | 7 | 0.41866 | 62799 | 0.30888 | 0 | 0.18604 | 2325.5 | 0 | 0 | 62799 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041007 | 7 | 0.43486 | 65229 | 0.28884 | 0 | 0.20953 | 2619.125 | 0 | 0 | 64000 | 1229 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041008 | 7 | 0.44919 | 67378.5 | 0.27591 | 0 | 0.32212 | 4026.5 | 0.06526 | 5220.8 | 64000 | 3378.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041009 | 7 | 0.46931 | 70396.5 | 0.1895 | 0 | 0.43392 | 5424 | 0.29785 | 23828 | 64000 | 5424 | 972.5 | 0 | 0 | 1350000 | 0 | 0
2021041010 | 7 | 0.48233 | 72349.5 | 0.1241 | 0 | 0.51407 | 6425.875 | 0.42401 | 33920.8 | 64000 | 6425.875 | 1923.625 | 0 | 0 | 1350000 | 0 | 0
2021041011 | 7 | 0.49003 | 73504.5 | 0.17571 | 0 | 0.55239 | 6904.875 | 0.43829 | 35063.2 | 64000 | 6904.875 | 2599.625 | 0 | 0 | 1350000 | 0 | 0
2021041012 | 7 | 0.49043 | 73564.5 | 0.2768 | 0 | 0.55282 | 6910.25 | 0.46029 | 36823.2 | 64000 | 6910.25 | 2654.25 | 0 | 0 | 1350000 | 0 | 0
2021041013 | 7 | 0.49057 | 73585.5 | 0.40707 | 0 | 0.54035 | 6754.375 | 0.44831 | 35864.8 | 64000 | 6754.375 | 2831.125 | 0 | 0 | 1350000 | 0 | 0
2021041014 | 7 | 0.48807 | 73210.5 | 0.4966 | 0 | 0.50582 | 6322.75 | 0.44625 | 35700 | 64000 | 6322.75 | 2887.75 | 0 | 0 | 1350000 | 0 | 0
2021041015 | 7 | 0.488 | 73200 | 0.50943 | 0 | 0.4656 | 5820 | 0.38888 | 31110.4 | 64000 | 5820 | 3380 | 0 | 0 | 1350000 | 0 | 0
2021041016 | 7 | 0.49089 | 73633.5 | 0.50029 | 0 | 0.44692 | 5586.5 | 0.33546 | 26836.8 | 64000 | 5586.5 | 4047 | 0 | 0 | 1350000 | 0 | 0
2021041017 | 7 | 0.49653 | 74479.5 | 0.5041 | 0 | 0.43648 | 5456 | 0.26712 | 21369.6 | 64000 | 5456 | 5023.5 | 0 | 0 | 1350000 | 0 | 0
2021041018 | 7 | 0.5035 | 75525 | 0.57056 | 0 | 0.4979 | 6223.75 | 0.12893 | 10314.4 | 64000 | 6223.75 | 5301.25 | 0 | 0 | 1350000 | 0 | 0
2021041019 | 7 | 0.50644 | 75966 | 0.64949 | 0 | 0.49138 | 6142.25 | 0.01443 | 1154.4 | 64000 | 6142.25 | 1154.4 | 4669.35 | 4669.35 | 1350000 | 4669.35 | 0
2021041020 | 7 | 0.51132 | 76698 | 0.72322 | 0 | 0.46184 | 5773 | 0 | 0 | 64000 | 5773 | 0 | 6925 | 2255.65 | 1350000 | 6925 | 0
2021041021 | 7 | 0.51725 | 77587.5 | 0.74611 | 0 | 0.44146 | 5518.25 | 0 | 0 | 64000 | 5518.25 | 0 | 8069.25 | 1144.25 | 1350000 | 8069.25 | 0
2021041022 | 7 | 0.50332 | 75498 | 0.7668 | 0 | 0.42394 | 5299.25 | 0 | 0 | 64000 | 5299.25 | 0 | 6198.75 | -1870.5 | 1350000 | 6198.75 | 0
2021041023 | 7 | 0.4801 | 72015 | 0.77649 | 0 | 0.43594 | 5449.25 | 0 | 0 | 64000 | 5449.25 | 0 | 2565.75 | -3633 | 1350000 | 2565.75 | 0
2021041024 | 7 | 0.45392 | 68088 | 0.75463 | 0 | 0.46489 | 5811.125 | 0 | 0 | 64000 | 4088 | 0 | 0 | -2565.75 | 1350000 | 0 | 0
2021041101 | 1 | 0.43051 | 64576.5 | 0.74768 | 0 | 0.51016 | 6377 | 0 | 0 | 64000 | 576.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041102 | 1 | 0.41451 | 62176.5 | 0.76181 | 0 | 0.52392 | 6549 | 0 | 0 | 62176.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041103 | 1 | 0.40469 | 60703.5 | 0.69966 | 0 | 0.53436 | 6679.5 | 0 | 0 | 60703.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041104 | 1 | 0.39943 | 59914.5 | 0.60879 | 0 | 0.54596 | 6824.5 | 0 | 0 | 59914.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041105 | 1 | 0.39845 | 59767.5 | 0.53647 | 0 | 0.53182 | 6647.75 | 0 | 0 | 59767.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041106 | 1 | 0.40275 | 60412.5 | 0.51285 | 0 | 0.57378 | 7172.25 | 0 | 0 | 60412.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041107 | 1 | 0.41353 | 62029.5 | 0.49471 | 0 | 0.63235 | 7904.375 | 0 | 0 | 62029.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041108 | 1 | 0.42417 | 63625.5 | 0.42936 | 0 | 0.66211 | 8276.375 | 0.01919 | 1535.2 | 63625.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041109 | 1 | 0.4454 | 66810 | 0.36803 | 0 | 0.6765 | 8456.25 | 0.0767 | 6136 | 64000 | 2810 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041110 | 1 | 0.46339 | 69508.5 | 0.35685 | 0 | 0.68012 | 8501.5 | 0.11539 | 9231.2 | 64000 | 5508.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041111 | 1 | 0.47734 | 71601 | 0.33736 | 0 | 0.68955 | 8619.375 | 0.17577 | 14061.6 | 64000 | 7601 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041112 | 1 | 0.48353 | 72529.5 | 0.28938 | 0 | 0.66214 | 8276.75 | 0.25466 | 20372.8 | 64000 | 8276.75 | 252.75 | 0 | 0 | 1350000 | 0 | 0
2021041113 | 1 | 0.48881 | 73321.5 | 0.25826 | 0 | 0.62213 | 7776.625 | 0.33783 | 27026.4 | 64000 | 7776.625 | 1544.875 | 0 | 0 | 1350000 | 0 | 0
2021041114 | 1 | 0.49069 | 73603.5 | 0.24011 | 0 | 0.61345 | 7668.125 | 0.34634 | 27707.2 | 64000 | 7668.125 | 1935.375 | 0 | 0 | 1350000 | 0 | 0
2021041115 | 1 | 0.49106 | 73659 | 0.24876 | 0 | 0.56792 | 7099 | 0.31035 | 24828 | 64000 | 7099 | 2560 | 0 | 0 | 1350000 | 0 | 0
2021041116 | 1 | 0.49486 | 74229 | 0.21191 | 0 | 0.54985 | 6873.125 | 0.25368 | 20294.4 | 64000 | 6873.125 | 3355.875 | 0 | 0 | 1350000 | 0 | 0
2021041117 | 1 | 0.50108 | 75162 | 0.29954 | 0 | 0.45235 | 5654.375 | 0.16098 | 12878.4 | 64000 | 5654.375 | 5507.625 | 0 | 0 | 1350000 | 0 | 0
2021041118 | 1 | 0.51048 | 76572 | 0.33232 | 0 | 0.51229 | 6403.625 | 0.09228 | 7382.4 | 64000 | 6403.625 | 6168.375 | 0 | 0 | 1350000 | 0 | 0
2021041119 | 1 | 0.51484 | 77226 | 0.44068 | 0 | 0.51983 | 6497.875 | 0.02145 | 1716 | 64000 | 6497.875 | 1716 | 5012.125 | 5012.125 | 1350000 | 5012.125 | 0
2021041120 | 1 | 0.52108 | 78162 | 0.45733 | 0 | 0.48804 | 6100.5 | 0 | 0 | 64000 | 6100.5 | 0 | 8061.5 | 3049.375 | 1350000 | 8061.5 | 0
2021041121 | 1 | 0.52866 | 79299 | 0.51915 | 0 | 0.41381 | 5172.625 | 0 | 0 | 64000 | 5172.625 | 0 | 10126.375 | 2064.875 | 1350000 | 10126.375 | 0
2021041122 | 1 | 0.51331 | 76996.5 | 0.57918 | 0 | 0.41817 | 5227.125 | 0 | 0 | 64000 | 5227.125 | 0 | 7769.375 | -2357 | 1350000 | 7769.375 | 0
2021041123 | 1 | 0.48501 | 72751.5 | 0.66037 | 0 | 0.49796 | 6224.5 | 0 | 0 | 64000 | 6224.5 | 0 | 2527 | -5242.375 | 1350000 | 2527 | 0
2021041124 | 1 | 0.45739 | 68608.5 | 0.61648 | 0 | 0.4822 | 6027.5 | 0 | 0 | 64000 | 4608.5 | 0 | 0 | -2527 | 1350000 | 0 | 0
2021041201 | 2 | 0.4364 | 65460 | 0.51622 | 0 | 0.4078 | 5097.5 | 0 | 0 | 64000 | 1460 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041202 | 2 | 0.42407 | 63610.5 | 0.43182 | 0 | 0.42608 | 5326 | 0 | 0 | 63610.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041203 | 2 | 0.41753 | 62629.5 | 0.27816 | 0 | 0.3781 | 4726.25 | 0 | 0 | 62629.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041204 | 2 | 0.41615 | 62422.5 | 0.29681 | 0 | 0.33903 | 4237.875 | 0 | 0 | 62422.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041205 | 2 | 0.42618 | 63927 | 0.34301 | 0 | 0.30821 | 3852.625 | 0 | 0 | 63927 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041206 | 2 | 0.45201 | 67801.5 | 0.35931 | 0 | 0.26786 | 3348.25 | 0 | 0 | 64000 | 3348.25 | 0 | 453.25 | 453.25 | 1350000 | 453.25 | 0
2021041207 | 2 | 0.49633 | 74449.5 | 0.32917 | 0 | 0.26915 | 3364.375 | 0 | 0 | 64000 | 3364.375 | 0 | 7085.125 | 6631.875 | 1350000 | 7085.125 | 0
2021041208 | 2 | 0.52837 | 79255.5 | 0.29505 | 0 | 0.29726 | 3715.75 | 0.02097 | 1677.6 | 64000 | 3715.75 | 1677.6 | 9862.15 | 2777.025 | 1350000 | 9862.15 | 0
2021041209 | 2 | 0.54406 | 81609 | 0.2513 | 0 | 0.27447 | 3430.875 | 0.09003 | 7202.4 | 64000 | 3430.875 | 7202.4 | 6975.725 | -2886.425 | 1350000 | 6975.725 | 0
2021041210 | 2 | 0.55138 | 82707 | 0.26359 | 0 | 0.26058 | 3257.25 | 0.18111 | 14488.8 | 64000 | 3257.25 | 14488.8 | 960.95 | -6014.775 | 1350000 | 960.95 | 0
2021041211 | 2 | 0.55738 | 83607 | 0.29335 | 0 | 0.23753 | 2969.125 | 0.26126 | 20900.8 | 64000 | 2969.125 | 16637.875 | 0 | -960.95 | 1350000 | 0 | 0
2021041212 | 2 | 0.55628 | 83442 | 0.26681 | 0 | 0.18927 | 2365.875 | 0.36305 | 29044 | 64000 | 2365.875 | 17076.125 | 0 | 0 | 1350000 | 0 | 0
2021041213 | 2 | 0.55825 | 83737.5 | 0.24789 | 0 | 0.19381 | 2422.625 | 0.42047 | 33637.6 | 64000 | 2422.625 | 17314.875 | 0 | 0 | 1350000 | 0 | 0
2021041214 | 2 | 0.55573 | 83359.5 | 0.23434 | 0 | 0.22893 | 2861.625 | 0.45851 | 36680.8 | 64000 | 2861.625 | 16497.875 | 0 | 0 | 1350000 | 0 | 0
2021041215 | 2 | 0.54986 | 82479 | 0.1965 | 0 | 0.26789 | 3348.625 | 0.45726 | 36580.8 | 64000 | 3348.625 | 15130.375 | 0 | 0 | 1350000 | 0 | 0
2021041216 | 2 | 0.54301 | 81451.5 | 0.18211 | 0 | 0.31804 | 3975.5 | 0.45026 | 36020.8 | 64000 | 3975.5 | 13476 | 0 | 0 | 1350000 | 0 | 0
2021041217 | 2 | 0.54209 | 81313.5 | 0.23076 | 0 | 0.33525 | 4190.625 | 0.40782 | 32625.6 | 64000 | 4190.625 | 13122.875 | 0 | 0 | 1350000 | 0 | 0
2021041218 | 2 | 0.54623 | 81934.5 | 0.34616 | 0 | 0.33721 | 4215.125 | 0.24909 | 19927.2 | 64000 | 4215.125 | 13719.375 | 0 | 0 | 1350000 | 0 | 0
2021041219 | 2 | 0.5483 | 82245 | 0.23522 | 0 | 0.31032 | 3879 | 0.04828 | 3862.4 | 64000 | 3879 | 3862.4 | 10503.6 | 10503.6 | 1350000 | 10503.6 | 0
2021041220 | 2 | 0.55155 | 82732.5 | 0.19143 | 0 | 0.30584 | 3823 | 0 | 0 | 64000 | 3823 | 0 | 14909.5 | 4405.9 | 1350000 | 14909.5 | 0
2021041221 | 2 | 0.55697 | 83545.5 | 0.18434 | 0 | 0.28236 | 3529.5 | 0 | 0 | 64000 | 3529.5 | 0 | 16016 | 1106.5 | 1350000 | 16016 | 0
2021041222 | 2 | 0.541 | 81150 | 0.17531 | 0 | 0.30389 | 3798.625 | 0 | 0 | 64000 | 3798.625 | 0 | 13351.375 | -2664.625 | 1350000 | 13351.375 | 0
2021041223 | 2 | 0.51097 | 76645.5 | 0.15248 | 0 | 0.37182 | 4647.75 | 0 | 0 | 64000 | 4647.75 | 0 | 7997.75 | -5353.625 | 1350000 | 7997.75 | 0
2021041224 | 2 | 0.4811 | 72165 | 0.15313 | 0 | 0.40328 | 5041 | 0 | 0 | 64000 | 5041 | 0 | 3124 | -4873.75 | 1350000 | 3124 | 0
2021041301 | 3 | 0.45881 | 68821.5 | 0.18611 | 0 | 0.52297 | 6537.125 | 0 | 0 | 64000 | 4821.5 | 0 | 0 | -3124 | 1350000 | 0 | 0
2021041302 | 3 | 0.4459 | 66885 | 0.10857 | 0 | 0.59288 | 7411 | 0 | 0 | 64000 | 2885 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041303 | 3 | 0.43945 | 65917.5 | 0.12755 | 0 | 0.64194 | 8024.25 | 0 | 0 | 64000 | 1917.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041304 | 3 | 0.43852 | 65778 | 0.13359 | 0 | 0.63805 | 7975.625 | 0 | 0 | 64000 | 1778 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041305 | 3 | 0.4487 | 67305 | 0.17501 | 0 | 0.60386 | 7548.25 | 0 | 0 | 64000 | 3305 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041306 | 3 | 0.47475 | 71212.5 | 0.25083 | 0 | 0.55567 | 6945.875 | 0 | 0 | 64000 | 6945.875 | 0 | 266.625 | 266.625 | 1350000 | 266.625 | 0
2021041307 | 3 | 0.51683 | 77524.5 | 0.22103 | 0 | 0.52231 | 6528.875 | 0 | 0 | 64000 | 6528.875 | 0 | 6995.625 | 6729 | 1350000 | 6995.625 | 0
2021041308 | 3 | 0.54356 | 81534 | 0.20998 | 0 | 0.5197 | 6496.25 | 0.05073 | 4058.4 | 64000 | 6496.25 | 4058.4 | 6979.35 | -16.275 | 1350000 | 6979.35 | 0
2021041309 | 3 | 0.55129 | 82693.5 | 0.19145 | 0 | 0.51235 | 6404.375 | 0.20052 | 16041.6 | 64000 | 6404.375 | 12289.125 | 0 | -6979.35 | 1350000 | 0 | 0
2021041310 | 3 | 0.55052 | 82578 | 0.08276 | 0 | 0.44136 | 5517 | 0.38008 | 30406.4 | 64000 | 5517 | 13061 | 0 | 0 | 1350000 | 0 | 0
2021041311 | 3 | 0.54363 | 81544.5 | 0.04744 | 0 | 0.42331 | 5291.375 | 0.47933 | 38346.4 | 64000 | 5291.375 | 12253.125 | 0 | 0 | 1350000 | 0 | 0
2021041312 | 3 | 0.53919 | 80878.5 | 0.05428 | 0 | 0.36763 | 4595.375 | 0.52472 | 41977.6 | 64000 | 4595.375 | 12283.125 | 0 | 0 | 1350000 | 0 | 0
2021041313 | 3 | 0.53235 | 79852.5 | 0.07137 | 0 | 0.30874 | 3859.25 | 0.57452 | 45961.6 | 64000 | 3859.25 | 11993.25 | 0 | 0 | 1350000 | 0 | 0
2021041314 | 3 | 0.52751 | 79126.5 | 0.09834 | 0 | 0.31006 | 3875.75 | 0.60495 | 48396 | 64000 | 3875.75 | 11250.75 | 0 | 0 | 1350000 | 0 | 0
2021041315 | 3 | 0.52276 | 78414 | 0.105 | 0 | 0.29769 | 3721.125 | 0.59312 | 47449.6 | 64000 | 3721.125 | 10692.875 | 0 | 0 | 1350000 | 0 | 0
2021041316 | 3 | 0.51826 | 77739 | 0.13121 | 0 | 0.26275 | 3284.375 | 0.52553 | 42042.4 | 64000 | 3284.375 | 10454.625 | 0 | 0 | 1350000 | 0 | 0
2021041317 | 3 | 0.51948 | 77922 | 0.12677 | 0 | 0.23824 | 2978 | 0.45214 | 36171.2 | 64000 | 2978 | 10944 | 0 | 0 | 1350000 | 0 | 0
2021041318 | 3 | 0.52439 | 78658.5 | 0.14063 | 0 | 0.23409 | 2926.125 | 0.28897 | 23117.6 | 64000 | 2926.125 | 11732.375 | 0 | 0 | 1350000 | 0 | 0
2021041319 | 3 | 0.53047 | 79570.5 | 0.11042 | 0 | 0.22433 | 2804.125 | 0.06125 | 4900 | 64000 | 2804.125 | 4900 | 7866.375 | 7866.375 | 1350000 | 7866.375 | 0
2021041320 | 3 | 0.53647 | 80470.5 | 0.04956 | 0 | 0.21043 | 2630.375 | 0 | 0 | 64000 | 2630.375 | 0 | 13840.125 | 5973.75 | 1350000 | 13840.125 | 0
2021041321 | 3 | 0.54954 | 82431 | 0.03414 | 0 | 0.2242 | 2802.5 | 0 | 0 | 64000 | 2802.5 | 0 | 15628.5 | 1788.375 | 1350000 | 15628.5 | 0
2021041322 | 3 | 0.53446 | 80169 | 0.02925 | 0 | 0.22958 | 2869.75 | 0 | 0 | 64000 | 2869.75 | 0 | 13299.25 | -2329.25 | 1350000 | 13299.25 | 0
2021041323 | 3 | 0.50331 | 75496.5 | 0.0134 | 0 | 0.22591 | 2823.875 | 0 | 0 | 64000 | 2823.875 | 0 | 8672.625 | -4626.625 | 1350000 | 8672.625 | 0
2021041324 | 3 | 0.4721 | 70815 | 0.01595 | 0 | 0.2125 | 2656.25 | 0 | 0 | 64000 | 2656.25 | 0 | 4158.75 | -4513.875 | 1350000 | 4158.75 | 0
2021041401 | 4 | 0.4498 | 67470 | 0.04321 | 0 | 0.20969 | 2621.125 | 0 | 0 | 64000 | 2621.125 | 0 | 848.875 | -3309.875 | 1350000 | 848.875 | 0
2021041402 | 4 | 0.43616 | 65424 | 0.12065 | 0 | 0.223 | 2787.5 | 0 | 0 | 64000 | 1424 | 0 | 0 | -848.875 | 1350000 | 0 | 0
2021041403 | 4 | 0.43083 | 64624.5 | 0.12184 | 0 | 0.24873 | 3109.125 | 0 | 0 | 64000 | 624.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041404 | 4 | 0.43006 | 64509 | 0.11127 | 0 | 0.27423 | 3427.875 | 0 | 0 | 64000 | 509 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041405 | 4 | 0.44044 | 66066 | 0.10069 | 0 | 0.25571 | 3196.375 | 0 | 0 | 64000 | 2066 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041406 | 4 | 0.46598 | 69897 | 0.03057 | 0 | 0.22522 | 2815.25 | 0 | 0 | 64000 | 2815.25 | 0 | 3081.75 | 3081.75 | 1350000 | 3081.75 | 0
2021041407 | 4 | 0.50675 | 76012.5 | 0.00567 | 0 | 0.1811 | 2263.75 | 0 | 0 | 64000 | 2263.75 | 0 | 9748.75 | 6667 | 1350000 | 9748.75 | 0
2021041408 | 4 | 0.53301 | 79951.5 | 0.0142 | 0 | 0.16872 | 2109 | 0.07761 | 6208.8 | 64000 | 2109 | 6208.8 | 7633.7 | -2115.05 | 1350000 | 7633.7 | 0
2021041409 | 4 | 0.53994 | 80991 | 0.02081 | 0 | 0.13543 | 1692.875 | 0.37964 | 30371.2 | 64000 | 1692.875 | 15298.125 | 0 | -7633.7 | 1350000 | 0 | 0
2021041410 | 4 | 0.53695 | 80542.5 | 0.02986 | 0 | 0.11941 | 1492.625 | 0.55567 | 44453.6 | 64000 | 1492.625 | 15049.875 | 0 | 0 | 1350000 | 0 | 0
2021041411 | 4 | 0.53618 | 80427 | 0.02214 | 0 | 0.09156 | 1144.5 | 0.57812 | 46249.6 | 64000 | 1144.5 | 15282.5 | 0 | 0 | 1350000 | 0 | 0
2021041412 | 4 | 0.53661 | 80491.5 | 0.04055 | 0 | 0.07428 | 928.5 | 0.61777 | 49421.6 | 64000 | 928.5 | 15563 | 0 | 0 | 1350000 | 0 | 0
2021041413 | 4 | 0.5399 | 80985 | 0.13954 | 0 | 0.05032 | 629 | 0.657 | 52560 | 64000 | 629 | 16356 | 0 | 0 | 1350000 | 0 | 0
2021041414 | 4 | 0.54177 | 81265.5 | 0.21529 | 0 | 0.03001 | 375.125 | 0.6602 | 52816 | 64000 | 375.125 | 16890.375 | 0 | 0 | 1350000 | 0 | 0
2021041415 | 4 | 0.53832 | 80748 | 0.22624 | 0 | 0.01177 | 147.125 | 0.67895 | 54316 | 64000 | 147.125 | 16600.875 | 0 | 0 | 1350000 | 0 | 0
2021041416 | 4 | 0.53531 | 80296.5 | 0.22121 | 0 | 0.00624 | 78 | 0.66671 | 53336.8 | 64000 | 78 | 16218.5 | 0 | 0 | 1350000 | 0 | 0
2021041417 | 4 | 0.53628 | 80442 | 0.18607 | 0 | 0.02231 | 278.875 | 0.59783 | 47826.4 | 64000 | 278.875 | 16163.125 | 0 | 0 | 1350000 | 0 | 0
2021041418 | 4 | 0.53892 | 80838 | 0.17577 | 0 | 0.06524 | 815.5 | 0.36202 | 28961.6 | 64000 | 815.5 | 16022.5 | 0 | 0 | 1350000 | 0 | 0
2021041419 | 4 | 0.54162 | 81243 | 0.15867 | 0 | 0.08185 | 1023.125 | 0.06552 | 5241.6 | 64000 | 1023.125 | 5241.6 | 10978.275 | 10978.275 | 1350000 | 10978.275 | 0
2021041420 | 4 | 0.54676 | 82014 | 0.17836 | 0 | 0.08196 | 1024.5 | 0 | 0 | 64000 | 1024.5 | 0 | 16989.5 | 6011.225 | 1350000 | 16989.5 | 0
2021041421 | 4 | 0.55363 | 83044.5 | 0.26018 | 0 | 0.10952 | 1369 | 0 | 0 | 64000 | 1369 | 0 | 17675.5 | 686 | 1350000 | 17675.5 | 0
2021041422 | 4 | 0.53761 | 80641.5 | 0.38088 | 0 | 0.13111 | 1638.875 | 0 | 0 | 64000 | 1638.875 | 0 | 15002.625 | -2672.875 | 1350000 | 15002.625 | 0
2021041423 | 4 | 0.50747 | 76120.5 | 0.42111 | 0 | 0.15582 | 1947.75 | 0 | 0 | 64000 | 1947.75 | 0 | 10172.75 | -4829.875 | 1350000 | 10172.75 | 0
2021041424 | 4 | 0.47863 | 71794.5 | 0.40917 | 0 | 0.19575 | 2446.875 | 0 | 0 | 64000 | 2446.875 | 0 | 5347.625 | -4825.125 | 1350000 | 5347.625 | 0
2021041501 | 5 | 0.45571 | 68356.5 | 0.4408 | 0 | 0.22619 | 2827.375 | 0 | 0 | 64000 | 2827.375 | 0 | 1529.125 | -3818.5 | 1350000 | 1529.125 | 0
2021041502 | 5 | 0.44407 | 66610.5 | 0.43768 | 0 | 0.23966 | 2995.75 | 0 | 0 | 64000 | 2610.5 | 0 | 0 | -1529.125 | 1350000 | 0 | 0
2021041503 | 5 | 0.43694 | 65541 | 0.34183 | 0 | 0.24432 | 3054 | 0 | 0 | 64000 | 1541 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041504 | 5 | 0.43648 | 65472 | 0.36622 | 0 | 0.25347 | 3168.375 | 0 | 0 | 64000 | 1472 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041505 | 5 | 0.44611 | 66916.5 | 0.28299 | 0 | 0.22964 | 2870.5 | 0 | 0 | 64000 | 2870.5 | 0 | 46 | 46 | 1350000 | 46 | 0
2021041506 | 5 | 0.47128 | 70692 | 0.25453 | 0 | 0.16027 | 2003.375 | 0 | 0 | 64000 | 2003.375 | 0 | 4688.625 | 4642.625 | 1350000 | 4688.625 | 0
2021041507 | 5 | 0.51338 | 77007 | 0.2174 | 0 | 0.08811 | 1101.375 | 0 | 0 | 64000 | 1101.375 | 0 | 11905.625 | 7217 | 1350000 | 11905.625 | 0
2021041508 | 5 | 0.54273 | 81409.5 | 0.24416 | 0 | 0.04089 | 511.125 | 0.09346 | 7476.8 | 64000 | 511.125 | 7476.8 | 9421.575 | -2484.05 | 1350000 | 9421.575 | 0
2021041509 | 5 | 0.55649 | 83473.5 | 0.22481 | 0 | 0.02512 | 314 | 0.3657 | 29256 | 64000 | 314 | 19159.5 | 0 | -9421.575 | 1350000 | 0 | 0
2021041510 | 5 | 0.56065 | 84097.5 | 0.29342 | 0 | 0.02147 | 268.375 | 0.51937 | 41549.6 | 64000 | 268.375 | 19829.125 | 0 | 0 | 1350000 | 0 | 0
2021041511 | 5 | 0.56048 | 84072 | 0.31829 | 0 | 0.01516 | 189.5 | 0.54384 | 43507.2 | 64000 | 189.5 | 19882.5 | 0 | 0 | 1350000 | 0 | 0
2021041512 | 5 | 0.55884 | 83826 | 0.28619 | 0 | 0.01128 | 141 | 0.59635 | 47708 | 64000 | 141 | 19685 | 0 | 0 | 1350000 | 0 | 0
2021041513 | 5 | 0.55529 | 83293.5 | 0.39122 | 0 | 0.00444 | 55.5 | 0.59678 | 47742.4 | 64000 | 55.5 | 19238 | 0 | 0 | 1350000 | 0 | 0
2021041514 | 5 | 0.55154 | 82731 | 0.48488 | 0 | 0.00361 | 45.125 | 0.58662 | 46929.6 | 64000 | 45.125 | 18685.875 | 0 | 0 | 1350000 | 0 | 0
2021041515 | 5 | 0.54585 | 81877.5 | 0.56797 | 0 | 0.01722 | 215.25 | 0.54761 | 43808.8 | 64000 | 215.25 | 17662.25 | 0 | 0 | 1350000 | 0 | 0
2021041516 | 5 | 0.53878 | 80817 | 0.57465 | 0 | 0.05063 | 632.875 | 0.47861 | 38288.8 | 64000 | 632.875 | 16184.125 | 0 | 0 | 1350000 | 0 | 0
2021041517 | 5 | 0.53932 | 80898 | 0.63616 | 0 | 0.07433 | 929.125 | 0.32859 | 26287.2 | 64000 | 929.125 | 15968.875 | 0 | 0 | 1350000 | 0 | 0
2021041518 | 5 | 0.54356 | 81534 | 0.73694 | 0 | 0.12628 | 1578.5 | 0.18426 | 14740.8 | 64000 | 1578.5 | 14740.8 | 1214.7 | 1214.7 | 1350000 | 1214.7 | 0
2021041519 | 5 | 0.54518 | 81777 | 0.66198 | 0 | 0.14164 | 1770.5 | 0.03679 | 2943.2 | 64000 | 1770.5 | 2943.2 | 13063.3 | 11848.6 | 1350000 | 13063.3 | 0
2021041520 | 5 | 0.55278 | 82917 | 0.61002 | 0 | 0.13408 | 1676 | 0 | 0 | 64000 | 1676 | 0 | 17241 | 4177.7 | 1350000 | 17241 | 0
2021041521 | 5 | 0.56513 | 84769.5 | 0.57024 | 0 | 0.13106 | 1638.25 | 0 | 0 | 64000 | 1638.25 | 0 | 19131.25 | 1890.25 | 1350000 | 19131.25 | 0
2021041522 | 5 | 0.55193 | 82789.5 | 0.53121 | 0 | 0.11146 | 1393.25 | 0 | 0 | 64000 | 1393.25 | 0 | 17396.25 | -1735 | 1350000 | 17396.25 | 0
2021041523 | 5 | 0.52227 | 78340.5 | 0.6033 | 0 | 0.09515 | 1189.375 | 0 | 0 | 64000 | 1189.375 | 0 | 13151.125 | -4245.125 | 1350000 | 13151.125 | 0
2021041524 | 5 | 0.49453 | 74179.5 | 0.66715 | 0 | 0.09951 | 1243.875 | 0 | 0 | 64000 | 1243.875 | 0 | 8935.625 | -4215.5 | 1350000 | 8935.625 | 0
2021041601 | 6 | 0.47503 | 71254.5 | 0.66719 | 0 | 0.09009 | 1126.125 | 0 | 0 | 64000 | 1126.125 | 0 | 6128.375 | -2807.25 | 1350000 | 6128.375 | 0
2021041602 | 6 | 0.46452 | 69678 | 0.72187 | 0 | 0.07913 | 989.125 | 0 | 0 | 64000 | 989.125 | 0 | 4688.875 | -1439.5 | 1350000 | 4688.875 | 0
2021041603 | 6 | 0.461 | 69150 | 0.746 | 0 | 0.07785 | 973.125 | 0 | 0 | 64000 | 973.125 | 0 | 4176.875 | -512 | 1350000 | 4176.875 | 0
2021041604 | 6 | 0.46192 | 69288 | 0.74153 | 0 | 0.07352 | 919 | 0 | 0 | 64000 | 919 | 0 | 4369 | 192.125 | 1350000 | 4369 | 0
2021041605 | 6 | 0.47308 | 70962 | 0.75966 | 0 | 0.05824 | 728 | 0 | 0 | 64000 | 728 | 0 | 6234 | 1865 | 1350000 | 6234 | 0
2021041606 | 6 | 0.50165 | 75247.5 | 0.75406 | 0 | 0.04297 | 537.125 | 0 | 0 | 64000 | 537.125 | 0 | 10710.375 | 4476.375 | 1350000 | 10710.375 | 0
2021041607 | 6 | 0.54523 | 81784.5 | 0.75586 | 0 | 0.0307 | 383.75 | 0.00031 | 24.8 | 64000 | 383.75 | 24.8 | 17375.95 | 6665.575 | 1350000 | 17375.95 | 0
2021041608 | 6 | 0.57089 | 85633.5 | 0.81215 | 0 | 0.03669 | 458.625 | 0.0454 | 3632 | 64000 | 458.625 | 3632 | 17542.875 | 166.925 | 1350000 | 17542.875 | 0
2021041609 | 6 | 0.57299 | 85948.5 | 0.84309 | 0 | 0.03425 | 428.125 | 0.16452 | 13161.6 | 64000 | 428.125 | 13161.6 | 8358.775 | -9184.1 | 1350000 | 8358.775 | 0
2021041610 | 6 | 0.56931 | 85396.5 | 0.84191 | 0 | 0.03638 | 454.75 | 0.24498 | 19598.4 | 64000 | 454.75 | 19598.4 | 1343.35 | -7015.425 | 1350000 | 1343.35 | 0
2021041611 | 6 | 0.56638 | 84957 | 0.84643 | 0 | 0.03337 | 417.125 | 0.32148 | 25718.4 | 64000 | 417.125 | 20539.875 | 0 | -1343.35 | 1350000 | 0 | 0
2021041612 | 6 | 0.56303 | 84454.5 | 0.8286 | 0 | 0.03338 | 417.25 | 0.36525 | 29220 | 64000 | 417.25 | 20037.25 | 0 | 0 | 1350000 | 0 | 0
2021041613 | 6 | 0.55778 | 83667 | 0.85126 | 0 | 0.04065 | 508.125 | 0.39659 | 31727.2 | 64000 | 508.125 | 19158.875 | 0 | 0 | 1350000 | 0 | 0
2021041614 | 6 | 0.5487 | 82305 | 0.86517 | 0 | 0.05062 | 632.75 | 0.3751 | 30008 | 64000 | 632.75 | 17672.25 | 0 | 0 | 1350000 | 0 | 0
2021041615 | 6 | 0.5367 | 80505 | 0.88928 | 0 | 0.05626 | 703.25 | 0.3176 | 25408 | 64000 | 703.25 | 15801.75 | 0 | 0 | 1350000 | 0 | 0
2021041616 | 6 | 0.52872 | 79308 | 0.88744 | 0 | 0.04246 | 530.75 | 0.20829 | 16663.2 | 64000 | 530.75 | 14777.25 | 0 | 0 | 1350000 | 0 | 0
2021041617 | 6 | 0.52452 | 78678 | 0.8683 | 0 | 0.07081 | 885.125 | 0.1405 | 11240 | 64000 | 885.125 | 11240 | 2552.875 | 2552.875 | 1350000 | 2552.875 | 0
2021041618 | 6 | 0.52623 | 78934.5 | 0.88471 | 0 | 0.13843 | 1730.375 | 0.07456 | 5964.8 | 64000 | 1730.375 | 5964.8 | 7239.325 | 4686.45 | 1350000 | 7239.325 | 0
2021041619 | 6 | 0.52922 | 79383 | 0.90015 | 0 | 0.1553 | 1941.25 | 0.01277 | 1021.6 | 64000 | 1941.25 | 1021.6 | 12420.15 | 5180.825 | 1350000 | 12420.15 | 0
2021041620 | 6 | 0.53588 | 80382 | 0.86292 | 0 | 0.17888 | 2236 | 0 | 0 | 64000 | 2236 | 0 | 14146 | 1725.85 | 1350000 | 14146 | 0
2021041621 | 6 | 0.54592 | 81888 | 0.82503 | 0 | 0.21561 | 2695.125 | 0 | 0 | 64000 | 2695.125 | 0 | 15192.875 | 1046.875 | 1350000 | 15192.875 | 0
2021041622 | 6 | 0.53728 | 80592 | 0.78082 | 0 | 0.24227 | 3028.375 | 0 | 0 | 64000 | 3028.375 | 0 | 13563.625 | -1629.25 | 1350000 | 13563.625 | 0
2021041623 | 6 | 0.51364 | 77046 | 0.80494 | 0 | 0.25188 | 3148.5 | 0 | 0 | 64000 | 3148.5 | 0 | 9897.5 | -3666.125 | 1350000 | 9897.5 | 0
2021041624 | 6 | 0.48807 | 73210.5 | 0.81338 | 0 | 0.28079 | 3509.875 | 0 | 0 | 64000 | 3509.875 | 0 | 5700.625 | -4196.875 | 1350000 | 5700.625 | 0
2021041701 | 7 | 0.4673 | 70095 | 0.75796 | 0 | 0.3123 | 3903.75 | 0 | 0 | 64000 | 3903.75 | 0 | 2191.25 | -3509.375 | 1350000 | 2191.25 | 0
2021041702 | 7 | 0.45516 | 68274 | 0.72344 | 0 | 0.30199 | 3774.875 | 0 | 0 | 64000 | 3774.875 | 0 | 499.125 | -1692.125 | 1350000 | 499.125 | 0
2021041703 | 7 | 0.44996 | 67494 | 0.73629 | 0 | 0.2442 | 3052.5 | 0 | 0 | 64000 | 3052.5 | 0 | 441.5 | -57.625 | 1350000 | 441.5 | 0
2021041704 | 7 | 0.44951 | 67426.5 | 0.73308 | 0 | 0.1978 | 2472.5 | 0 | 0 | 64000 | 2472.5 | 0 | 954 | 512.5 | 1350000 | 954 | 0
2021041705 | 7 | 0.4535 | 68025 | 0.68484 | 0 | 0.16466 | 2058.25 | 0 | 0 | 64000 | 2058.25 | 0 | 1966.75 | 1012.75 | 1350000 | 1966.75 | 0
2021041706 | 7 | 0.46608 | 69912 | 0.61827 | 0 | 0.09562 | 1195.25 | 0 | 0 | 64000 | 1195.25 | 0 | 4716.75 | 2750 | 1350000 | 4716.75 | 0
2021041707 | 7 | 0.48438 | 72657 | 0.47827 | 0 | 0.06821 | 852.625 | 0.00111 | 88.8 | 64000 | 852.625 | 88.8 | 7715.575 | 2998.825 | 1350000 | 7715.575 | 0
2021041708 | 7 | 0.49752 | 74628 | 0.40305 | 0 | 0.06896 | 862 | 0.04001 | 3200.8 | 64000 | 862 | 3200.8 | 6565.2 | -1150.375 | 1350000 | 6565.2 | 0
2021041709 | 7 | 0.50506 | 75759 | 0.36439 | 0 | 0.06407 | 800.875 | 0.13714 | 10971.2 | 64000 | 800.875 | 10958.125 | 0 | -6565.2 | 1350000 | 0 | 0
2021041710 | 7 | 0.50622 | 75933 | 0.30813 | 0 | 0.06325 | 790.625 | 0.22617 | 18093.6 | 64000 | 790.625 | 11142.375 | 0 | 0 | 1350000 | 0 | 0
2021041711 | 7 | 0.50405 | 75607.5 | 0.24406 | 0 | 0.06125 | 765.625 | 0.31039 | 24831.2 | 64000 | 765.625 | 10841.875 | 0 | 0 | 1350000 | 0 | 0
2021041712 | 7 | 0.49828 | 74742 | 0.24136 | 0 | 0.05967 | 745.875 | 0.39279 | 31423.2 | 64000 | 745.875 | 9996.125 | 0 | 0 | 1350000 | 0 | 0
2021041713 | 7 | 0.49025 | 73537.5 | 0.30812 | 0 | 0.06004 | 750.5 | 0.45597 | 36477.6 | 64000 | 750.5 | 8787 | 0 | 0 | 1350000 | 0 | 0
2021041714 | 7 | 0.48349 | 72523.5 | 0.38119 | 0 | 0.05834 | 729.25 | 0.47608 | 38086.4 | 64000 | 729.25 | 7794.25 | 0 | 0 | 1350000 | 0 | 0
2021041715 | 7 | 0.47639 | 71458.5 | 0.32858 | 0 | 0.0513 | 641.25 | 0.47362 | 37889.6 | 64000 | 641.25 | 6817.25 | 0 | 0 | 1350000 | 0 | 0
2021041716 | 7 | 0.47543 | 71314.5 | 0.3161 | 0 | 0.03426 | 428.25 | 0.41047 | 32837.6 | 64000 | 428.25 | 6886.25 | 0 | 0 | 1350000 | 0 | 0
2021041717 | 7 | 0.47847 | 71770.5 | 0.29591 | 0 | 0.07704 | 963 | 0.2811 | 22488 | 64000 | 963 | 6807.5 | 0 | 0 | 1350000 | 0 | 0
2021041718 | 7 | 0.48559 | 72838.5 | 0.28181 | 0 | 0.13349 | 1668.625 | 0.17836 | 14268.8 | 64000 | 1668.625 | 7169.875 | 0 | 0 | 1350000 | 0 | 0
2021041719 | 7 | 0.49139 | 73708.5 | 0.23074 | 0 | 0.14022 | 1752.75 | 0.03667 | 2933.6 | 64000 | 1752.75 | 2933.6 | 5022.15 | 5022.15 | 1350000 | 5022.15 | 0
2021041720 | 7 | 0.49875 | 74812.5 | 0.16979 | 0 | 0.15458 | 1932.25 | 0 | 0 | 64000 | 1932.25 | 0 | 8880.25 | 3858.1 | 1350000 | 8880.25 | 0
2021041721 | 7 | 0.51045 | 76567.5 | 0.15092 | 0 | 0.16168 | 2021 | 0 | 0 | 64000 | 2021 | 0 | 10546.5 | 1666.25 | 1350000 | 10546.5 | 0
2021041722 | 7 | 0.5049 | 75735 | 0.15036 | 0 | 0.18803 | 2350.375 | 0 | 0 | 64000 | 2350.375 | 0 | 9384.625 | -1161.875 | 1350000 | 9384.625 | 0
2021041723 | 7 | 0.4875 | 73125 | 0.17276 | 0 | 0.20168 | 2521 | 0 | 0 | 64000 | 2521 | 0 | 6604 | -2780.625 | 1350000 | 6604 | 0
2021041724 | 7 | 0.4656 | 69840 | 0.17975 | 0 | 0.2083 | 2603.75 | 0 | 0 | 64000 | 2603.75 | 0 | 3236.25 | -3367.75 | 1350000 | 3236.25 | 0
2021041801 | 1 | 0.4479 | 67185 | 0.16127 | 0 | 0.22552 | 2819 | 0 | 0 | 64000 | 2819 | 0 | 366 | -2870.25 | 1350000 | 366 | 0
2021041802 | 1 | 0.4372 | 65580 | 0.1689 | 0 | 0.22733 | 2841.625 | 0 | 0 | 64000 | 1580 | 0 | 0 | -366 | 1350000 | 0 | 0
2021041803 | 1 | 0.43176 | 64764 | 0.20557 | 0 | 0.20477 | 2559.625 | 0 | 0 | 64000 | 764 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041804 | 1 | 0.43019 | 64528.5 | 0.24591 | 0 | 0.17561 | 2195.125 | 0 | 0 | 64000 | 528.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041805 | 1 | 0.43377 | 65065.5 | 0.23985 | 0 | 0.12425 | 1553.125 | 0 | 0 | 64000 | 1065.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041806 | 1 | 0.4433 | 66495 | 0.29483 | 0 | 0.07537 | 942.125 | 0 | 0 | 64000 | 942.125 | 0 | 1552.875 | 1552.875 | 1350000 | 1552.875 | 0
2021041807 | 1 | 0.45561 | 68341.5 | 0.28908 | 0 | 0.07282 | 910.25 | 0.00125 | 100 | 64000 | 910.25 | 100 | 3331.25 | 1778.375 | 1350000 | 3331.25 | 0
2021041808 | 1 | 0.46598 | 69897 | 0.24908 | 0 | 0.08026 | 1003.25 | 0.07146 | 5716.8 | 64000 | 1003.25 | 4893.75 | 0 | -3331.25 | 1350000 | 0 | 0
2021041809 | 1 | 0.47072 | 70608 | 0.18262 | 0 | 0.07647 | 955.875 | 0.29555 | 23644 | 64000 | 955.875 | 5652.125 | 0 | 0 | 1350000 | 0 | 0
2021041810 | 1 | 0.46792 | 70188 | 0.11359 | 0 | 0.08469 | 1058.625 | 0.47668 | 38134.4 | 64000 | 1058.625 | 5129.375 | 0 | 0 | 1350000 | 0 | 0
2021041811 | 1 | 0.46316 | 69474 | 0.09663 | 0 | 0.07815 | 976.875 | 0.52994 | 42395.2 | 64000 | 976.875 | 4497.125 | 0 | 0 | 1350000 | 0 | 0
2021041812 | 1 | 0.46131 | 69196.5 | 0.09123 | 0 | 0.06895 | 861.875 | 0.57129 | 45703.2 | 64000 | 861.875 | 4334.625 | 0 | 0 | 1350000 | 0 | 0
2021041813 | 1 | 0.46028 | 69042 | 0.08924 | 0 | 0.06092 | 761.5 | 0.61103 | 48882.4 | 64000 | 761.5 | 4280.5 | 0 | 0 | 1350000 | 0 | 0
2021041814 | 1 | 0.45878 | 68817 | 0.11137 | 0 | 0.05815 | 726.875 | 0.62372 | 49897.6 | 64000 | 726.875 | 4090.125 | 0 | 0 | 1350000 | 0 | 0
2021041815 | 1 | 0.45761 | 68641.5 | 0.10871 | 0 | 0.06516 | 814.5 | 0.64064 | 51251.2 | 64000 | 814.5 | 3827 | 0 | 0 | 1350000 | 0 | 0
2021041816 | 1 | 0.46074 | 69111 | 0.12466 | 0 | 0.06734 | 841.75 | 0.62356 | 49884.8 | 64000 | 841.75 | 4269.25 | 0 | 0 | 1350000 | 0 | 0
2021041817 | 1 | 0.46739 | 70108.5 | 0.1828 | 0 | 0.08732 | 1091.5 | 0.53792 | 43033.6 | 64000 | 1091.5 | 5017 | 0 | 0 | 1350000 | 0 | 0
2021041818 | 1 | 0.47796 | 71694 | 0.12334 | 0 | 0.11344 | 1418 | 0.3216 | 25728 | 64000 | 1418 | 6276 | 0 | 0 | 1350000 | 0 | 0
2021041819 | 1 | 0.48546 | 72819 | 0.09734 | 0 | 0.11139 | 1392.375 | 0.07209 | 5767.2 | 64000 | 1392.375 | 5767.2 | 1659.425 | 1659.425 | 1350000 | 1659.425 | 0
2021041820 | 1 | 0.49495 | 74242.5 | 0.07889 | 0 | 0.10715 | 1339.375 | 0 | 0 | 64000 | 1339.375 | 0 | 8903.125 | 7243.7 | 1350000 | 8903.125 | 0
2021041821 | 1 | 0.51179 | 76768.5 | 0.04321 | 0 | 0.12748 | 1593.5 | 0 | 0 | 64000 | 1593.5 | 0 | 11175 | 2271.875 | 1350000 | 11175 | 0
2021041822 | 1 | 0.50285 | 75427.5 | 0.02954 | 0 | 0.14498 | 1812.25 | 0 | 0 | 64000 | 1812.25 | 0 | 9615.25 | -1559.75 | 1350000 | 9615.25 | 0
2021041823 | 1 | 0.47951 | 71926.5 | 0.01741 | 0 | 0.18261 | 2282.625 | 0 | 0 | 64000 | 2282.625 | 0 | 5643.875 | -3971.375 | 1350000 | 5643.875 | 0
2021041824 | 1 | 0.45548 | 68322 | 0.04785 | 0 | 0.18334 | 2291.75 | 0 | 0 | 64000 | 2291.75 | 0 | 2030.25 | -3613.625 | 1350000 | 2030.25 | 0
2021041901 | 2 | 0.43907 | 65860.5 | 0.05387 | 0 | 0.17743 | 2217.875 | 0 | 0 | 64000 | 1860.5 | 0 | 0 | -2030.25 | 1350000 | 0 | 0
2021041902 | 2 | 0.42998 | 64497 | 0.02003 | 0 | 0.18902 | 2362.75 | 0 | 0 | 64000 | 497 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041903 | 2 | 0.42681 | 64021.5 | 0.04406 | 0 | 0.26245 | 3280.625 | 0 | 0 | 64000 | 21.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041904 | 2 | 0.42998 | 64497 | 0.13658 | 0 | 0.31828 | 3978.5 | 0 | 0 | 64000 | 497 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041905 | 2 | 0.44264 | 66396 | 0.1506 | 0 | 0.31823 | 3977.875 | 0 | 0 | 64000 | 2396 | 0 | 0 | 0 | 1350000 | 0 | 0
2021041906 | 2 | 0.47239 | 70858.5 | 0.06253 | 0 | 0.33565 | 4195.625 | 0 | 0 | 64000 | 4195.625 | 0 | 2662.875 | 2662.875 | 1350000 | 2662.875 | 0
2021041907 | 2 | 0.51574 | 77361 | 0.06121 | 0 | 0.36455 | 4556.875 | 0.00162 | 129.6 | 64000 | 4556.875 | 129.6 | 8674.525 | 6011.65 | 1350000 | 8674.525 | 0
2021041908 | 2 | 0.54411 | 81616.5 | 0.03637 | 0 | 0.38025 | 4753.125 | 0.09771 | 7816.8 | 64000 | 4753.125 | 7816.8 | 5046.575 | -3627.95 | 1350000 | 5046.575 | 0
2021041909 | 2 | 0.55251 | 82876.5 | 0.01093 | 0 | 0.43926 | 5490.75 | 0.33755 | 27004 | 64000 | 5490.75 | 13385.75 | 0 | -5046.575 | 1350000 | 0 | 0
2021041910 | 2 | 0.54939 | 82408.5 | 0.00242 | 0 | 0.46172 | 5771.5 | 0.47707 | 38165.6 | 64000 | 5771.5 | 12637 | 0 | 0 | 1350000 | 0 | 0
2021041911 | 2 | 0.54798 | 82197 | 0.0144 | 0 | 0.48411 | 6051.375 | 0.5414 | 43312 | 64000 | 6051.375 | 12145.625 | 0 | 0 | 1350000 | 0 | 0
2021041912 | 2 | 0.54948 | 82422 | 0.03445 | 0 | 0.50774 | 6346.75 | 0.59931 | 47944.8 | 64000 | 6346.75 | 12075.25 | 0 | 0 | 1350000 | 0 | 0
2021041913 | 2 | 0.5503 | 82545 | 0.09707 | 0 | 0.5101 | 6376.25 | 0.62587 | 50069.6 | 64000 | 6376.25 | 12168.75 | 0 | 0 | 1350000 | 0 | 0
2021041914 | 2 | 0.54625 | 81937.5 | 0.13208 | 0 | 0.51474 | 6434.25 | 0.64344 | 51475.2 | 64000 | 6434.25 | 11503.25 | 0 | 0 | 1350000 | 0 | 0
2021041915 | 2 | 0.53973 | 80959.5 | 0.14977 | 0 | 0.50842 | 6355.25 | 0.63885 | 51108 | 64000 | 6355.25 | 10604.25 | 0 | 0 | 1350000 | 0 | 0
2021041916 | 2 | 0.53115 | 79672.5 | 0.17701 | 0 | 0.46948 | 5868.5 | 0.58565 | 46852 | 64000 | 5868.5 | 9804 | 0 | 0 | 1350000 | 0 | 0
2021041917 | 2 | 0.52861 | 79291.5 | 0.21185 | 0 | 0.43276 | 5409.5 | 0.49776 | 39820.8 | 64000 | 5409.5 | 9882 | 0 | 0 | 1350000 | 0 | 0
2021041918 | 2 | 0.52977 | 79465.5 | 0.21583 | 0 | 0.46538 | 5817.25 | 0.28331 | 22664.8 | 64000 | 5817.25 | 9648.25 | 0 | 0 | 1350000 | 0 | 0
2021041919 | 2 | 0.53163 | 79744.5 | 0.20034 | 0 | 0.50502 | 6312.75 | 0.06953 | 5562.4 | 64000 | 6312.75 | 5562.4 | 3869.35 | 3869.35 | 1350000 | 3869.35 | 0
2021041920 | 2 | 0.53779 | 80668.5 | 0.13258 | 0 | 0.50031 | 6253.875 | 0 | 0 | 64000 | 6253.875 | 0 | 10414.625 | 6545.275 | 1350000 | 10414.625 | 0
2021041921 | 2 | 0.55167 | 82750.5 | 0.17962 | 0 | 0.47945 | 5993.125 | 0 | 0 | 64000 | 5993.125 | 0 | 12757.375 | 2342.75 | 1350000 | 12757.375 | 0
2021041922 | 2 | 0.53764 | 80646 | 0.31172 | 0 | 0.47539 | 5942.375 | 0 | 0 | 64000 | 5942.375 | 0 | 10703.625 | -2053.75 | 1350000 | 10703.625 | 0
2021041923 | 2 | 0.50837 | 76255.5 | 0.43721 | 0 | 0.50367 | 6295.875 | 0 | 0 | 64000 | 6295.875 | 0 | 5959.625 | -4744 | 1350000 | 5959.625 | 0
2021041924 | 2 | 0.4795 | 71925 | 0.57012 | 0 | 0.53394 | 6674.25 | 0 | 0 | 64000 | 6674.25 | 0 | 1250.75 | -4708.875 | 1350000 | 1250.75 | 0
2021042001 | 3 | 0.45864 | 68796 | 0.69219 | 0 | 0.54288 | 6786 | 0 | 0 | 64000 | 4796 | 0 | 0 | -1250.75 | 1350000 | 0 | 0
2021042002 | 3 | 0.44717 | 67075.5 | 0.70586 | 0 | 0.55664 | 6958 | 0 | 0 | 64000 | 3075.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042003 | 3 | 0.4444 | 66660 | 0.6927 | 0 | 0.46977 | 5872.125 | 0 | 0 | 64000 | 2660 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042004 | 3 | 0.44646 | 66969 | 0.73692 | 0 | 0.34645 | 4330.625 | 0 | 0 | 64000 | 2969 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042005 | 3 | 0.45939 | 68908.5 | 0.76461 | 0 | 0.22019 | 2752.375 | 0 | 0 | 64000 | 2752.375 | 0 | 2156.125 | 2156.125 | 1350000 | 2156.125 | 0
2021042006 | 3 | 0.48763 | 73144.5 | 0.7408 | 0 | 0.18784 | 2348 | 0 | 0 | 64000 | 2348 | 0 | 6796.5 | 4640.375 | 1350000 | 6796.5 | 0
2021042007 | 3 | 0.53131 | 79696.5 | 0.61749 | 0 | 0.22679 | 2834.875 | 0.00095 | 76 | 64000 | 2834.875 | 76 | 12785.625 | 5989.125 | 1350000 | 12785.625 | 0
2021042008 | 3 | 0.55726 | 83589 | 0.48032 | 0 | 0.36784 | 4598 | 0.08669 | 6935.2 | 64000 | 4598 | 6935.2 | 8055.8 | -4729.825 | 1350000 | 8055.8 | 0
2021042009 | 3 | 0.55831 | 83746.5 | 0.37603 | 0 | 0.4145 | 5181.25 | 0.31682 | 25345.6 | 64000 | 5181.25 | 14565.25 | 0 | -8055.8 | 1350000 | 0 | 0
2021042010 | 3 | 0.5518 | 82770 | 0.41345 | 0 | 0.36999 | 4624.875 | 0.48159 | 38527.2 | 64000 | 4624.875 | 14145.125 | 0 | 0 | 1350000 | 0 | 0
2021042011 | 3 | 0.54685 | 82027.5 | 0.51096 | 0 | 0.28368 | 3546 | 0.5735 | 45880 | 64000 | 3546 | 14481.5 | 0 | 0 | 1350000 | 0 | 0
2021042012 | 3 | 0.54417 | 81625.5 | 0.63567 | 0 | 0.1952 | 2440 | 0.61384 | 49107.2 | 64000 | 2440 | 15185.5 | 0 | 0 | 1350000 | 0 | 0
2021042013 | 3 | 0.54113 | 81169.5 | 0.71488 | 0 | 0.12626 | 1578.25 | 0.63323 | 50658.4 | 64000 | 1578.25 | 15591.25 | 0 | 0 | 1350000 | 0 | 0
2021042014 | 3 | 0.53685 | 80527.5 | 0.66217 | 0 | 0.10335 | 1291.875 | 0.64515 | 51612 | 64000 | 1291.875 | 15235.625 | 0 | 0 | 1350000 | 0 | 0
2021042015 | 3 | 0.53403 | 80104.5 | 0.54306 | 0 | 0.1246 | 1557.5 | 0.64506 | 51604.8 | 64000 | 1557.5 | 14547 | 0 | 0 | 1350000 | 0 | 0
2021042016 | 3 | 0.53341 | 80011.5 | 0.43433 | 0 | 0.19946 | 2493.25 | 0.61319 | 49055.2 | 64000 | 2493.25 | 13518.25 | 0 | 0 | 1350000 | 0 | 0
2021042017 | 3 | 0.53758 | 80637 | 0.36651 | 0 | 0.24436 | 3054.5 | 0.51951 | 41560.8 | 64000 | 3054.5 | 13582.5 | 0 | 0 | 1350000 | 0 | 0
2021042018 | 3 | 0.54209 | 81313.5 | 0.33015 | 0 | 0.30307 | 3788.375 | 0.30004 | 24003.2 | 64000 | 3788.375 | 13525.125 | 0 | 0 | 1350000 | 0 | 0
2021042019 | 3 | 0.5465 | 81975 | 0.30968 | 0 | 0.33969 | 4246.125 | 0.06307 | 5045.6 | 64000 | 4246.125 | 5045.6 | 8683.275 | 8683.275 | 1350000 | 8683.275 | 0
2021042020 | 3 | 0.55073 | 82609.5 | 0.31253 | 0 | 0.38927 | 4865.875 | 0 | 0 | 64000 | 4865.875 | 0 | 13743.625 | 5060.35 | 1350000 | 13743.625 | 0
2021042021 | 3 | 0.56241 | 84361.5 | 0.32973 | 0 | 0.41383 | 5172.875 | 0 | 0 | 64000 | 5172.875 | 0 | 15188.625 | 1445 | 1350000 | 15188.625 | 0
2021042022 | 3 | 0.54702 | 82053 | 0.28257 | 0 | 0.45395 | 5674.375 | 0 | 0 | 64000 | 5674.375 | 0 | 12378.625 | -2810 | 1350000 | 12378.625 | 0
2021042023 | 3 | 0.51744 | 77616 | 0.2415 | 0 | 0.46385 | 5798.125 | 0 | 0 | 64000 | 5798.125 | 0 | 7817.875 | -4560.75 | 1350000 | 7817.875 | 0
2021042024 | 3 | 0.48796 | 73194 | 0.1877 | 0 | 0.46249 | 5781.125 | 0 | 0 | 64000 | 5781.125 | 0 | 3412.875 | -4405 | 1350000 | 3412.875 | 0
2021042101 | 4 | 0.46597 | 69895.5 | 0.29278 | 0 | 0.47969 | 5996.125 | 0 | 0 | 64000 | 5895.5 | 0 | 0 | -3412.875 | 1350000 | 0 | 0
2021042102 | 4 | 0.45359 | 68038.5 | 0.33617 | 0 | 0.47159 | 5894.875 | 0 | 0 | 64000 | 4038.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042103 | 4 | 0.44714 | 67071 | 0.34658 | 0 | 0.4496 | 5620 | 0 | 0 | 64000 | 3071 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042104 | 4 | 0.44774 | 67161 | 0.36503 | 0 | 0.42596 | 5324.5 | 0 | 0 | 64000 | 3161 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042105 | 4 | 0.45632 | 68448 | 0.32879 | 0 | 0.44506 | 5563.25 | 0 | 0 | 64000 | 4448 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042106 | 4 | 0.48246 | 72369 | 0.28677 | 0 | 0.44763 | 5595.375 | 0 | 0 | 64000 | 5595.375 | 0 | 2773.625 | 2773.625 | 1350000 | 2773.625 | 0
2021042107 | 4 | 0.52277 | 78415.5 | 0.40412 | 0 | 0.43337 | 5417.125 | 0.00204 | 163.2 | 64000 | 5417.125 | 163.2 | 8835.175 | 6061.55 | 1350000 | 8835.175 | 0
2021042108 | 4 | 0.55174 | 82761 | 0.6163 | 0 | 0.45999 | 5749.875 | 0.09741 | 7792.8 | 64000 | 5749.875 | 7792.8 | 5218.325 | -3616.85 | 1350000 | 5218.325 | 0
2021042109 | 4 | 0.56389 | 84583.5 | 0.50985 | 0 | 0.51028 | 6378.5 | 0.34708 | 27766.4 | 64000 | 6378.5 | 14205 | 0 | -5218.325 | 1350000 | 0 | 0
2021042110 | 4 | 0.56582 | 84873 | 0.68506 | 0 | 0.52507 | 6563.375 | 0.52735 | 42188 | 64000 | 6563.375 | 14309.625 | 0 | 0 | 1350000 | 0 | 0
2021042111 | 4 | 0.56629 | 84943.5 | 0.83158 | 0 | 0.51068 | 6383.5 | 0.61674 | 49339.2 | 64000 | 6383.5 | 14560 | 0 | 0 | 1350000 | 0 | 0
2021042112 | 4 | 0.56566 | 84849 | 0.87613 | 0 | 0.50383 | 6297.875 | 0.6633 | 53064 | 64000 | 6297.875 | 14551.125 | 0 | 0 | 1350000 | 0 | 0
2021042113 | 4 | 0.56639 | 84958.5 | 0.90613 | 0 | 0.55189 | 6898.625 | 0.68401 | 54720.8 | 64000 | 6898.625 | 14059.875 | 0 | 0 | 1350000 | 0 | 0
2021042114 | 4 | 0.5653 | 84795 | 0.94352 | 0 | 0.61011 | 7626.375 | 0.6931 | 55448 | 64000 | 7626.375 | 13168.625 | 0 | 0 | 1350000 | 0 | 0
2021042115 | 4 | 0.56188 | 84282 | 0.94844 | 0 | 0.6387 | 7983.75 | 0.68512 | 54809.6 | 64000 | 7983.75 | 12298.25 | 0 | 0 | 1350000 | 0 | 0
2021042116 | 4 | 0.55125 | 82687.5 | 0.94722 | 0 | 0.66144 | 8268 | 0.64796 | 51836.8 | 64000 | 8268 | 10419.5 | 0 | 0 | 1350000 | 0 | 0
2021042117 | 4 | 0.5507 | 82605 | 0.96132 | 0 | 0.67884 | 8485.5 | 0.56055 | 44844 | 64000 | 8485.5 | 10119.5 | 0 | 0 | 1350000 | 0 | 0
2021042118 | 4 | 0.55772 | 83658 | 0.95449 | 0 | 0.69234 | 8654.25 | 0.36781 | 29424.8 | 64000 | 8654.25 | 11003.75 | 0 | 0 | 1350000 | 0 | 0
2021042119 | 4 | 0.56482 | 84723 | 0.93901 | 0 | 0.72183 | 9022.875 | 0.08984 | 7187.2 | 64000 | 9022.875 | 7187.2 | 4512.925 | 4512.925 | 1350000 | 4512.925 | 0
2021042120 | 4 | 0.57349 | 86023.5 | 0.95918 | 0 | 0.72732 | 9091.5 | 0.00101 | 80.8 | 64000 | 9091.5 | 80.8 | 12851.2 | 8338.275 | 1350000 | 12851.2 | 0
2021042121 | 4 | 0.58968 | 88452 | 0.96234 | 0 | 0.72138 | 9017.25 | 0 | 0 | 64000 | 9017.25 | 0 | 15434.75 | 2583.55 | 1350000 | 15434.75 | 0
2021042122 | 4 | 0.58124 | 87186 | 0.94975 | 0 | 0.71987 | 8998.375 | 0 | 0 | 64000 | 8998.375 | 0 | 14187.625 | -1247.125 | 1350000 | 14187.625 | 0
2021042123 | 4 | 0.5564 | 83460 | 0.92284 | 0 | 0.70998 | 8874.75 | 0 | 0 | 64000 | 8874.75 | 0 | 10585.25 | -3602.375 | 1350000 | 10585.25 | 0
2021042124 | 4 | 0.53028 | 79542 | 0.84296 | 0 | 0.67548 | 8443.5 | 0 | 0 | 64000 | 8443.5 | 0 | 7098.5 | -3486.75 | 1350000 | 7098.5 | 0
2021042201 | 5 | 0.5122 | 76830 | 0.80708 | 0 | 0.64611 | 8076.375 | 0 | 0 | 64000 | 8076.375 | 0 | 4753.625 | -2344.875 | 1350000 | 4753.625 | 0
2021042202 | 5 | 0.5036 | 75540 | 0.8351 | 0 | 0.65268 | 8158.5 | 0 | 0 | 64000 | 8158.5 | 0 | 3381.5 | -1372.125 | 1350000 | 3381.5 | 0
2021042203 | 5 | 0.50154 | 75231 | 0.84156 | 0 | 0.65996 | 8249.5 | 0 | 0 | 64000 | 8249.5 | 0 | 2981.5 | -400 | 1350000 | 2981.5 | 0
2021042204 | 5 | 0.50578 | 75867 | 0.91023 | 0 | 0.66688 | 8336 | 0 | 0 | 64000 | 8336 | 0 | 3531 | 549.5 | 1350000 | 3531 | 0
2021042205 | 5 | 0.51847 | 77770.5 | 0.93892 | 0 | 0.61701 | 7712.625 | 0 | 0 | 64000 | 7712.625 | 0 | 6057.875 | 2526.875 | 1350000 | 6057.875 | 0
2021042206 | 5 | 0.55144 | 82716 | 0.93874 | 0 | 0.53547 | 6693.375 | 0 | 0 | 64000 | 6693.375 | 0 | 12022.625 | 5964.75 | 1350000 | 12022.625 | 0
2021042207 | 5 | 0.59536 | 89304 | 0.93499 | 0 | 0.41081 | 5135.125 | 0.00327 | 261.6 | 64000 | 5135.125 | 261.6 | 19907.275 | 7884.65 | 1350000 | 19907.275 | 0
2021042208 | 5 | 0.61929 | 92893.5 | 0.9409 | 0 | 0.41195 | 5149.375 | 0.13551 | 10840.8 | 64000 | 5149.375 | 10840.8 | 12903.325 | -7003.95 | 1350000 | 12903.325 | 0
2021042209 | 5 | 0.616 | 92400 | 0.95024 | 0 | 0.42691 | 5336.375 | 0.40016 | 32012.8 | 64000 | 5336.375 | 23063.625 | 0 | -12903.325 | 1350000 | 0 | 0
2021042210 | 5 | 0.60577 | 90865.5 | 0.95886 | 0 | 0.42664 | 5333 | 0.55913 | 44730.4 | 64000 | 5333 | 21532.5 | 0 | 0 | 1350000 | 0 | 0
2021042211 | 5 | 0.59685 | 89527.5 | 0.96456 | 0 | 0.38243 | 4780.375 | 0.6084 | 48672 | 64000 | 4780.375 | 20747.125 | 0 | 0 | 1350000 | 0 | 0
2021042212 | 5 | 0.58858 | 88287 | 0.97302 | 0 | 0.33501 | 4187.625 | 0.62248 | 49798.4 | 64000 | 4187.625 | 20099.375 | 0 | 0 | 1350000 | 0 | 0
2021042213 | 5 | 0.58254 | 87381 | 0.97617 | 0 | 0.29336 | 3667 | 0.67606 | 54084.8 | 64000 | 3667 | 19714 | 0 | 0 | 1350000 | 0 | 0
2021042214 | 5 | 0.576 | 86400 | 0.97912 | 0 | 0.28026 | 3503.25 | 0.68695 | 54956 | 64000 | 3503.25 | 18896.75 | 0 | 0 | 1350000 | 0 | 0
2021042215 | 5 | 0.56718 | 85077 | 0.98221 | 0 | 0.28019 | 3502.375 | 0.68163 | 54530.4 | 64000 | 3502.375 | 17574.625 | 0 | 0 | 1350000 | 0 | 0
2021042216 | 5 | 0.55927 | 83890.5 | 0.9853 | 0 | 0.28206 | 3525.75 | 0.64786 | 51828.8 | 64000 | 3525.75 | 16364.75 | 0 | 0 | 1350000 | 0 | 0
2021042217 | 5 | 0.55805 | 83707.5 | 0.98564 | 0 | 0.31633 | 3954.125 | 0.60009 | 48007.2 | 64000 | 3954.125 | 15753.375 | 0 | 0 | 1350000 | 0 | 0
2021042218 | 5 | 0.56124 | 84186 | 0.97279 | 0 | 0.38428 | 4803.5 | 0.37247 | 29797.6 | 64000 | 4803.5 | 15382.5 | 0 | 0 | 1350000 | 0 | 0
2021042219 | 5 | 0.56536 | 84804 | 0.96181 | 0 | 0.41622 | 5202.75 | 0.07698 | 6158.4 | 64000 | 5202.75 | 6158.4 | 9442.85 | 9442.85 | 1350000 | 9442.85 | 0
2021042220 | 5 | 0.57561 | 86341.5 | 0.93033 | 0 | 0.4194 | 5242.5 | 0.00055 | 44 | 64000 | 5242.5 | 44 | 17055 | 7612.15 | 1350000 | 17055 | 0
2021042221 | 5 | 0.59177 | 88765.5 | 0.84665 | 0 | 0.42107 | 5263.375 | 0 | 0 | 64000 | 5263.375 | 0 | 19502.125 | 2447.125 | 1350000 | 19502.125 | 0
2021042222 | 5 | 0.58437 | 87655.5 | 0.88629 | 0 | 0.4113 | 5141.25 | 0 | 0 | 64000 | 5141.25 | 0 | 18514.25 | -987.875 | 1350000 | 18514.25 | 0
2021042223 | 5 | 0.55872 | 83808 | 0.88437 | 0 | 0.44416 | 5552 | 0 | 0 | 64000 | 5552 | 0 | 14256 | -4258.25 | 1350000 | 14256 | 0
2021042224 | 5 | 0.53241 | 79861.5 | 0.91254 | 0 | 0.47592 | 5949 | 0 | 0 | 64000 | 5949 | 0 | 9912.5 | -4343.5 | 1350000 | 9912.5 | 0
2021042301 | 6 | 0.51451 | 77176.5 | 0.89843 | 0 | 0.49016 | 6127 | 0 | 0 | 64000 | 6127 | 0 | 7049.5 | -2863 | 1350000 | 7049.5 | 0
2021042302 | 6 | 0.50542 | 75813 | 0.87629 | 0 | 0.44873 | 5609.125 | 0 | 0 | 64000 | 5609.125 | 0 | 6203.875 | -845.625 | 1350000 | 6203.875 | 0
2021042303 | 6 | 0.50236 | 75354 | 0.90025 | 0 | 0.4029 | 5036.25 | 0 | 0 | 64000 | 5036.25 | 0 | 6317.75 | 113.875 | 1350000 | 6317.75 | 0
2021042304 | 6 | 0.50415 | 75622.5 | 0.88005 | 0 | 0.31781 | 3972.625 | 0 | 0 | 64000 | 3972.625 | 0 | 7649.875 | 1332.125 | 1350000 | 7649.875 | 0
2021042305 | 6 | 0.51852 | 77778 | 0.83188 | 0 | 0.23547 | 2943.375 | 0 | 0 | 64000 | 2943.375 | 0 | 10834.625 | 3184.75 | 1350000 | 10834.625 | 0
2021042306 | 6 | 0.54714 | 82071 | 0.81202 | 0 | 0.16216 | 2027 | 0 | 0 | 64000 | 2027 | 0 | 16044 | 5209.375 | 1350000 | 16044 | 0
2021042307 | 6 | 0.58798 | 88197 | 0.82879 | 0 | 0.11509 | 1438.625 | 0.00435 | 348 | 64000 | 1438.625 | 348 | 22410.375 | 6366.375 | 1350000 | 22410.375 | 0
2021042308 | 6 | 0.60759 | 91138.5 | 0.77055 | 0 | 0.10901 | 1362.625 | 0.14708 | 11766.4 | 64000 | 1362.625 | 11766.4 | 14009.475 | -8400.9 | 1350000 | 14009.475 | 0
2021042309 | 6 | 0.59917 | 89875.5 | 0.67057 | 0 | 0.101 | 1262.5 | 0.42749 | 34199.2 | 64000 | 1262.5 | 24613 | 0 | -14009.475 | 1350000 | 0 | 0
2021042310 | 6 | 0.58114 | 87171 | 0.74929 | 0 | 0.09699 | 1212.375 | 0.56671 | 45336.8 | 64000 | 1212.375 | 21958.625 | 0 | 0 | 1350000 | 0 | 0
2021042311 | 6 | 0.56627 | 84940.5 | 0.80812 | 0 | 0.10456 | 1307 | 0.63248 | 50598.4 | 64000 | 1307 | 19633.5 | 0 | 0 | 1350000 | 0 | 0
2021042312 | 6 | 0.55304 | 82956 | 0.80018 | 0 | 0.10921 | 1365.125 | 0.68184 | 54547.2 | 64000 | 1365.125 | 17590.875 | 0 | 0 | 1350000 | 0 | 0
2021042313 | 6 | 0.54241 | 81361.5 | 0.74662 | 0 | 0.10785 | 1348.125 | 0.7092 | 56736 | 64000 | 1348.125 | 16013.375 | 0 | 0 | 1350000 | 0 | 0
2021042314 | 6 | 0.53307 | 79960.5 | 0.76783 | 0 | 0.11318 | 1414.75 | 0.73419 | 58735.2 | 64000 | 1414.75 | 14545.75 | 0 | 0 | 1350000 | 0 | 0
2021042315 | 6 | 0.52381 | 78571.5 | 0.76209 | 0 | 0.10234 | 1279.25 | 0.74206 | 59364.8 | 64000 | 1279.25 | 13292.25 | 0 | 0 | 1350000 | 0 | 0
2021042316 | 6 | 0.51574 | 77361 | 0.81366 | 0 | 0.10288 | 1286 | 0.72559 | 58047.2 | 64000 | 1286 | 12075 | 0 | 0 | 1350000 | 0 | 0
2021042317 | 6 | 0.51518 | 77277 | 0.79529 | 0 | 0.10945 | 1368.125 | 0.65292 | 52233.6 | 64000 | 1368.125 | 11908.875 | 0 | 0 | 1350000 | 0 | 0
2021042318 | 6 | 0.51771 | 77656.5 | 0.76247 | 0 | 0.10942 | 1367.75 | 0.45544 | 36435.2 | 64000 | 1367.75 | 12288.75 | 0 | 0 | 1350000 | 0 | 0
2021042319 | 6 | 0.51698 | 77547 | 0.71222 | 0 | 0.12128 | 1516 | 0.1149 | 9192 | 64000 | 1516 | 9192 | 2839 | 2839 | 1350000 | 2839 | 0
2021042320 | 6 | 0.52194 | 78291 | 0.57759 | 0 | 0.12373 | 1546.625 | 0.00066 | 52.8 | 64000 | 1546.625 | 52.8 | 12691.575 | 9852.575 | 1350000 | 12691.575 | 0
2021042321 | 6 | 0.53393 | 80089.5 | 0.54614 | 0 | 0.11826 | 1478.25 | 0 | 0 | 64000 | 1478.25 | 0 | 14611.25 | 1919.675 | 1350000 | 14611.25 | 0
2021042322 | 6 | 0.52842 | 79263 | 0.61906 | 0 | 0.10164 | 1270.5 | 0 | 0 | 64000 | 1270.5 | 0 | 13992.5 | -618.75 | 1350000 | 13992.5 | 0
2021042323 | 6 | 0.50776 | 76164 | 0.63122 | 0 | 0.0877 | 1096.25 | 0 | 0 | 64000 | 1096.25 | 0 | 11067.75 | -2924.75 | 1350000 | 11067.75 | 0
2021042324 | 6 | 0.48315 | 72472.5 | 0.64753 | 0 | 0.08539 | 1067.375 | 0 | 0 | 64000 | 1067.375 | 0 | 7405.125 | -3662.625 | 1350000 | 7405.125 | 0
2021042401 | 7 | 0.46311 | 69466.5 | 0.67844 | 0 | 0.09275 | 1159.375 | 0 | 0 | 64000 | 1159.375 | 0 | 4307.125 | -3098 | 1350000 | 4307.125 | 0
2021042402 | 7 | 0.45303 | 67954.5 | 0.65914 | 0 | 0.1041 | 1301.25 | 0 | 0 | 64000 | 1301.25 | 0 | 2653.25 | -1653.875 | 1350000 | 2653.25 | 0
2021042403 | 7 | 0.44742 | 67113 | 0.60351 | 0 | 0.10397 | 1299.625 | 0 | 0 | 64000 | 1299.625 | 0 | 1813.375 | -839.875 | 1350000 | 1813.375 | 0
2021042404 | 7 | 0.44798 | 67197 | 0.56902 | 0 | 0.09843 | 1230.375 | 0 | 0 | 64000 | 1230.375 | 0 | 1966.625 | 153.25 | 1350000 | 1966.625 | 0
2021042405 | 7 | 0.4529 | 67935 | 0.47653 | 0 | 0.09954 | 1244.25 | 0 | 0 | 64000 | 1244.25 | 0 | 2690.75 | 724.125 | 1350000 | 2690.75 | 0
2021042406 | 7 | 0.46601 | 69901.5 | 0.39373 | 0 | 0.0967 | 1208.75 | 0 | 0 | 64000 | 1208.75 | 0 | 4692.75 | 2002 | 1350000 | 4692.75 | 0
2021042407 | 7 | 0.48273 | 72409.5 | 0.3445 | 0 | 0.09922 | 1240.25 | 0.0053 | 424 | 64000 | 1240.25 | 424 | 6745.25 | 2052.5 | 1350000 | 6745.25 | 0
2021042408 | 7 | 0.49577 | 74365.5 | 0.27227 | 0 | 0.11542 | 1442.75 | 0.09084 | 7267.2 | 64000 | 1442.75 | 7267.2 | 1655.55 | -5089.7 | 1350000 | 1655.55 | 0
2021042409 | 7 | 0.5018 | 75270 | 0.1469 | 0 | 0.13282 | 1660.25 | 0.21348 | 17078.4 | 64000 | 1660.25 | 9609.75 | 0 | -1655.55 | 1350000 | 0 | 0
2021042410 | 7 | 0.50216 | 75324 | 0.06951 | 0 | 0.15132 | 1891.5 | 0.25885 | 20708 | 64000 | 1891.5 | 9432.5 | 0 | 0 | 1350000 | 0 | 0
2021042411 | 7 | 0.49805 | 74707.5 | 0.03425 | 0 | 0.1498 | 1872.5 | 0.24163 | 19330.4 | 64000 | 1872.5 | 8835 | 0 | 0 | 1350000 | 0 | 0
2021042412 | 7 | 0.49261 | 73891.5 | 0.02494 | 0 | 0.12967 | 1620.875 | 0.24409 | 19527.2 | 64000 | 1620.875 | 8270.625 | 0 | 0 | 1350000 | 0 | 0
2021042413 | 7 | 0.48795 | 73192.5 | 0.08077 | 0 | 0.11716 | 1464.5 | 0.21471 | 17176.8 | 64000 | 1464.5 | 7728 | 0 | 0 | 1350000 | 0 | 0
2021042414 | 7 | 0.48492 | 72738 | 0.13512 | 0 | 0.08358 | 1044.75 | 0.21353 | 17082.4 | 64000 | 1044.75 | 7693.25 | 0 | 0 | 1350000 | 0 | 0
2021042415 | 7 | 0.48177 | 72265.5 | 0.20594 | 0 | 0.03458 | 432.25 | 0.17988 | 14390.4 | 64000 | 432.25 | 7833.25 | 0 | 0 | 1350000 | 0 | 0
2021042416 | 7 | 0.48483 | 72724.5 | 0.29918 | 0 | 0.01297 | 162.125 | 0.15671 | 12536.8 | 64000 | 162.125 | 8562.375 | 0 | 0 | 1350000 | 0 | 0
2021042417 | 7 | 0.49058 | 73587 | 0.26086 | 0 | 0.01783 | 222.875 | 0.14538 | 11630.4 | 64000 | 222.875 | 9364.125 | 0 | 0 | 1350000 | 0 | 0
2021042418 | 7 | 0.49656 | 74484 | 0.23808 | 0 | 0.0665 | 831.25 | 0.07022 | 5617.6 | 64000 | 831.25 | 5617.6 | 4035.15 | 4035.15 | 1350000 | 4035.15 | 0
2021042419 | 7 | 0.5005 | 75075 | 0.24064 | 0 | 0.08818 | 1102.25 | 0.01816 | 1452.8 | 64000 | 1102.25 | 1452.8 | 8519.95 | 4484.8 | 1350000 | 8519.95 | 0
2021042420 | 7 | 0.50656 | 75984 | 0.28644 | 0 | 0.09341 | 1167.625 | 0 | 0 | 64000 | 1167.625 | 0 | 10816.375 | 2296.425 | 1350000 | 10816.375 | 0
2021042421 | 7 | 0.51405 | 77107.5 | 0.30804 | 0 | 0.11789 | 1473.625 | 0 | 0 | 64000 | 1473.625 | 0 | 11633.875 | 817.5 | 1350000 | 11633.875 | 0
2021042422 | 7 | 0.50386 | 75579 | 0.41158 | 0 | 0.10929 | 1366.125 | 0 | 0 | 64000 | 1366.125 | 0 | 10212.875 | -1421 | 1350000 | 10212.875 | 0
2021042423 | 7 | 0.48407 | 72610.5 | 0.364 | 0 | 0.10305 | 1288.125 | 0 | 0 | 64000 | 1288.125 | 0 | 7322.375 | -2890.5 | 1350000 | 7322.375 | 0
2021042424 | 7 | 0.46118 | 69177 | 0.31279 | 0 | 0.1319 | 1648.75 | 0 | 0 | 64000 | 1648.75 | 0 | 3528.25 | -3794.125 | 1350000 | 3528.25 | 0
2021042501 | 1 | 0.44222 | 66333 | 0.26341 | 0 | 0.14529 | 1816.125 | 0 | 0 | 64000 | 1816.125 | 0 | 516.875 | -3011.375 | 1350000 | 516.875 | 0
2021042502 | 1 | 0.42861 | 64291.5 | 0.19246 | 0 | 0.15855 | 1981.875 | 0 | 0 | 64000 | 291.5 | 0 | 0 | -516.875 | 1350000 | 0 | 0
2021042503 | 1 | 0.42131 | 63196.5 | 0.055 | 0 | 0.1992 | 2490 | 0 | 0 | 63196.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042504 | 1 | 0.41758 | 62637 | 0.01504 | 0 | 0.20717 | 2589.625 | 0 | 0 | 62637 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042505 | 1 | 0.41921 | 62881.5 | 0.01682 | 0 | 0.20193 | 2524.125 | 0 | 0 | 62881.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042506 | 1 | 0.42563 | 63844.5 | 0.0342 | 0 | 0.21488 | 2686 | 0 | 0 | 63844.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042507 | 1 | 0.43619 | 65428.5 | 0.11991 | 0 | 0.29753 | 3719.125 | 0.00418 | 334.4 | 64000 | 1428.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042508 | 1 | 0.44874 | 67311 | 0.21219 | 0 | 0.38903 | 4862.875 | 0.08906 | 7124.8 | 64000 | 3311 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042509 | 1 | 0.46526 | 69789 | 0.30624 | 0 | 0.44111 | 5513.875 | 0.24906 | 19924.8 | 64000 | 5513.875 | 275.125 | 0 | 0 | 1350000 | 0 | 0
2021042510 | 1 | 0.47636 | 71454 | 0.29393 | 0 | 0.4654 | 5817.5 | 0.36481 | 29184.8 | 64000 | 5817.5 | 1636.5 | 0 | 0 | 1350000 | 0 | 0
2021042511 | 1 | 0.48094 | 72141 | 0.3588 | 0 | 0.46546 | 5818.25 | 0.48453 | 38762.4 | 64000 | 5818.25 | 2322.75 | 0 | 0 | 1350000 | 0 | 0
2021042512 | 1 | 0.48253 | 72379.5 | 0.43779 | 0 | 0.46923 | 5865.375 | 0.54657 | 43725.6 | 64000 | 5865.375 | 2514.125 | 0 | 0 | 1350000 | 0 | 0
2021042513 | 1 | 0.47909 | 71863.5 | 0.51488 | 0 | 0.41082 | 5135.25 | 0.53882 | 43105.6 | 64000 | 5135.25 | 2728.25 | 0 | 0 | 1350000 | 0 | 0
2021042514 | 1 | 0.47201 | 70801.5 | 0.56474 | 0 | 0.26851 | 3356.375 | 0.48257 | 38605.6 | 64000 | 3356.375 | 3445.125 | 0 | 0 | 1350000 | 0 | 0
2021042515 | 1 | 0.46755 | 70132.5 | 0.63578 | 0 | 0.15219 | 1902.375 | 0.51066 | 40852.8 | 64000 | 1902.375 | 4230.125 | 0 | 0 | 1350000 | 0 | 0
2021042516 | 1 | 0.46498 | 69747 | 0.77644 | 0 | 0.11949 | 1493.625 | 0.55673 | 44538.4 | 64000 | 1493.625 | 4253.375 | 0 | 0 | 1350000 | 0 | 0
2021042517 | 1 | 0.46908 | 70362 | 0.8622 | 0 | 0.14881 | 1860.125 | 0.47073 | 37658.4 | 64000 | 1860.125 | 4501.875 | 0 | 0 | 1350000 | 0 | 0
2021042518 | 1 | 0.47713 | 71569.5 | 0.88709 | 0 | 0.23631 | 2953.875 | 0.2625 | 21000 | 64000 | 2953.875 | 4615.625 | 0 | 0 | 1350000 | 0 | 0
2021042519 | 1 | 0.48515 | 72772.5 | 0.92112 | 0 | 0.27482 | 3435.25 | 0.07376 | 5900.8 | 64000 | 3435.25 | 5337.25 | 0 | 0 | 1350000 | 0 | 0
2021042520 | 1 | 0.49706 | 74559 | 0.94004 | 0 | 0.28278 | 3534.75 | 0.00063 | 50.4 | 64000 | 3534.75 | 50.4 | 6973.85 | 6973.85 | 1350000 | 6973.85 | 0
2021042521 | 1 | 0.51549 | 77323.5 | 0.95474 | 0 | 0.3217 | 4021.25 | 0 | 0 | 64000 | 4021.25 | 0 | 9302.25 | 2328.4 | 1350000 | 9302.25 | 0
2021042522 | 1 | 0.51059 | 76588.5 | 0.95687 | 0 | 0.33292 | 4161.5 | 0 | 0 | 64000 | 4161.5 | 0 | 8427 | -875.25 | 1350000 | 8427 | 0
2021042523 | 1 | 0.48748 | 73122 | 0.93234 | 0 | 0.35468 | 4433.5 | 0 | 0 | 64000 | 4433.5 | 0 | 4688.5 | -3738.5 | 1350000 | 4688.5 | 0
2021042524 | 1 | 0.46472 | 69708 | 0.91466 | 0 | 0.40984 | 5123 | 0 | 0 | 64000 | 5123 | 0 | 585 | -4103.5 | 1350000 | 585 | 0
2021042601 | 2 | 0.44823 | 67234.5 | 0.90305 | 0 | 0.40211 | 5026.375 | 0 | 0 | 64000 | 3234.5 | 0 | 0 | -585 | 1350000 | 0 | 0
2021042602 | 2 | 0.44067 | 66100.5 | 0.88637 | 0 | 0.35227 | 4403.375 | 0 | 0 | 64000 | 2100.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042603 | 2 | 0.43926 | 65889 | 0.86418 | 0 | 0.32778 | 4097.25 | 0 | 0 | 64000 | 1889 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042604 | 2 | 0.44342 | 66513 | 0.84491 | 0 | 0.33579 | 4197.375 | 0 | 0 | 64000 | 2513 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042605 | 2 | 0.45849 | 68773.5 | 0.84524 | 0 | 0.36537 | 4567.125 | 0 | 0 | 64000 | 4567.125 | 0 | 206.375 | 206.375 | 1350000 | 206.375 | 0
2021042606 | 2 | 0.49116 | 73674 | 0.81654 | 0 | 0.33433 | 4179.125 | 0 | 0 | 64000 | 4179.125 | 0 | 5494.875 | 5288.5 | 1350000 | 5494.875 | 0
2021042607 | 2 | 0.53637 | 80455.5 | 0.83979 | 0 | 0.36132 | 4516.5 | 0.00451 | 360.8 | 64000 | 4516.5 | 360.8 | 11578.2 | 6083.325 | 1350000 | 11578.2 | 0
2021042608 | 2 | 0.56186 | 84279 | 0.79059 | 0 | 0.44773 | 5596.625 | 0.16049 | 12839.2 | 64000 | 5596.625 | 12839.2 | 1843.175 | -9735.025 | 1350000 | 1843.175 | 0
2021042609 | 2 | 0.56309 | 84463.5 | 0.69523 | 0 | 0.5408 | 6760 | 0.46504 | 37203.2 | 64000 | 6760 | 13703.5 | 0 | -1843.175 | 1350000 | 0 | 0
2021042610 | 2 | 0.55227 | 82840.5 | 0.6489 | 0 | 0.58005 | 7250.625 | 0.60803 | 48642.4 | 64000 | 7250.625 | 11589.875 | 0 | 0 | 1350000 | 0 | 0
2021042611 | 2 | 0.54333 | 81499.5 | 0.57514 | 0 | 0.62227 | 7778.375 | 0.66629 | 53303.2 | 64000 | 7778.375 | 9721.125 | 0 | 0 | 1350000 | 0 | 0
2021042612 | 2 | 0.53625 | 80437.5 | 0.57305 | 0 | 0.64071 | 8008.875 | 0.6929 | 55432 | 64000 | 8008.875 | 8428.625 | 0 | 0 | 1350000 | 0 | 0
2021042613 | 2 | 0.53156 | 79734 | 0.58051 | 0 | 0.64792 | 8099 | 0.70686 | 56548.8 | 64000 | 8099 | 7635 | 0 | 0 | 1350000 | 0 | 0
2021042614 | 2 | 0.52612 | 78918 | 0.60248 | 0 | 0.59675 | 7459.375 | 0.7101 | 56808 | 64000 | 7459.375 | 7458.625 | 0 | 0 | 1350000 | 0 | 0
2021042615 | 2 | 0.52108 | 78162 | 0.5791 | 0 | 0.4936 | 6170 | 0.72084 | 57667.2 | 64000 | 6170 | 7992 | 0 | 0 | 1350000 | 0 | 0
2021042616 | 2 | 0.518 | 77700 | 0.52168 | 0 | 0.39913 | 4989.125 | 0.67975 | 54380 | 64000 | 4989.125 | 8710.875 | 0 | 0 | 1350000 | 0 | 0
2021042617 | 2 | 0.52073 | 78109.5 | 0.45245 | 0 | 0.38533 | 4816.625 | 0.61814 | 49451.2 | 64000 | 4816.625 | 9292.875 | 0 | 0 | 1350000 | 0 | 0
2021042618 | 2 | 0.52697 | 79045.5 | 0.36669 | 0 | 0.45058 | 5632.25 | 0.42489 | 33991.2 | 64000 | 5632.25 | 9413.25 | 0 | 0 | 1350000 | 0 | 0
2021042619 | 2 | 0.53254 | 79881 | 0.27753 | 0 | 0.45223 | 5652.875 | 0.10716 | 8572.8 | 64000 | 5652.875 | 8572.8 | 1655.325 | 1655.325 | 1350000 | 1655.325 | 0
2021042620 | 2 | 0.53806 | 80709 | 0.16714 | 0 | 0.43574 | 5446.75 | 0.00077 | 61.6 | 64000 | 5446.75 | 61.6 | 11200.65 | 9545.325 | 1350000 | 11200.65 | 0
2021042621 | 2 | 0.5497 | 82455 | 0.13016 | 0 | 0.45001 | 5625.125 | 0 | 0 | 64000 | 5625.125 | 0 | 12829.875 | 1629.225 | 1350000 | 12829.875 | 0
2021042622 | 2 | 0.53889 | 80833.5 | 0.076 | 0 | 0.42735 | 5341.875 | 0 | 0 | 64000 | 5341.875 | 0 | 11491.625 | -1338.25 | 1350000 | 11491.625 | 0
2021042623 | 2 | 0.50756 | 76134 | 0.11097 | 0 | 0.37367 | 4670.875 | 0 | 0 | 64000 | 4670.875 | 0 | 7463.125 | -4028.5 | 1350000 | 7463.125 | 0
2021042624 | 2 | 0.47573 | 71359.5 | 0.19013 | 0 | 0.32496 | 4062 | 0 | 0 | 64000 | 4062 | 0 | 3297.5 | -4165.625 | 1350000 | 3297.5 | 0
2021042701 | 3 | 0.45167 | 67750.5 | 0.26261 | 0 | 0.25381 | 3172.625 | 0 | 0 | 64000 | 3172.625 | 0 | 577.875 | -2719.625 | 1350000 | 577.875 | 0
2021042702 | 3 | 0.43974 | 65961 | 0.24073 | 0 | 0.17546 | 2193.25 | 0 | 0 | 64000 | 1961 | 0 | 0 | -577.875 | 1350000 | 0 | 0
2021042703 | 3 | 0.43312 | 64968 | 0.35563 | 0 | 0.14656 | 1832 | 0 | 0 | 64000 | 968 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042704 | 3 | 0.43263 | 64894.5 | 0.29471 | 0 | 0.1236 | 1545 | 0 | 0 | 64000 | 894.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042705 | 3 | 0.44215 | 66322.5 | 0.28146 | 0 | 0.09422 | 1177.75 | 0 | 0 | 64000 | 1177.75 | 0 | 1144.75 | 1144.75 | 1350000 | 1144.75 | 0
2021042706 | 3 | 0.46892 | 70338 | 0.38727 | 0 | 0.07559 | 944.875 | 0 | 0 | 64000 | 944.875 | 0 | 5393.125 | 4248.375 | 1350000 | 5393.125 | 0
2021042707 | 3 | 0.507 | 76050 | 0.60584 | 0 | 0.0693 | 866.25 | 0.00763 | 610.4 | 64000 | 866.25 | 610.4 | 10573.35 | 5180.225 | 1350000 | 10573.35 | 0
2021042708 | 3 | 0.53138 | 79707 | 0.67236 | 0 | 0.09812 | 1226.5 | 0.15052 | 12041.6 | 64000 | 1226.5 | 12041.6 | 2438.9 | -8134.45 | 1350000 | 2438.9 | 0
2021042709 | 3 | 0.53668 | 80502 | 0.66171 | 0 | 0.14398 | 1799.75 | 0.37754 | 30203.2 | 64000 | 1799.75 | 14702.25 | 0 | -2438.9 | 1350000 | 0 | 0
2021042710 | 3 | 0.53584 | 80376 | 0.70366 | 0 | 0.1714 | 2142.5 | 0.4777 | 38216 | 64000 | 2142.5 | 14233.5 | 0 | 0 | 1350000 | 0 | 0
2021042711 | 3 | 0.53644 | 80466 | 0.69808 | 0 | 0.17935 | 2241.875 | 0.54309 | 43447.2 | 64000 | 2241.875 | 14224.125 | 0 | 0 | 1350000 | 0 | 0
2021042712 | 3 | 0.53966 | 80949 | 0.66072 | 0 | 0.17517 | 2189.625 | 0.56819 | 45455.2 | 64000 | 2189.625 | 14759.375 | 0 | 0 | 1350000 | 0 | 0
2021042713 | 3 | 0.54515 | 81772.5 | 0.56735 | 0 | 0.16201 | 2025.125 | 0.6022 | 48176 | 64000 | 2025.125 | 15747.375 | 0 | 0 | 1350000 | 0 | 0
2021042714 | 3 | 0.5522 | 82830 | 0.45019 | 0 | 0.14746 | 1843.25 | 0.60033 | 48026.4 | 64000 | 1843.25 | 16986.75 | 0 | 0 | 1350000 | 0 | 0
2021042715 | 3 | 0.55888 | 83832 | 0.41888 | 0 | 0.11877 | 1484.625 | 0.59023 | 47218.4 | 64000 | 1484.625 | 18347.375 | 0 | 0 | 1350000 | 0 | 0
2021042716 | 3 | 0.56894 | 85341 | 0.44049 | 0 | 0.10414 | 1301.75 | 0.53342 | 42673.6 | 64000 | 1301.75 | 20039.25 | 0 | 0 | 1350000 | 0 | 0
2021042717 | 3 | 0.58096 | 87144 | 0.44231 | 0 | 0.10906 | 1363.25 | 0.44943 | 35954.4 | 64000 | 1363.25 | 21780.75 | 0 | 0 | 1350000 | 0 | 0
2021042718 | 3 | 0.5918 | 88770 | 0.39956 | 0 | 0.17842 | 2230.25 | 0.25964 | 20771.2 | 64000 | 2230.25 | 20771.2 | 1768.55 | 1768.55 | 1350000 | 1768.55 | 0
2021042719 | 3 | 0.59632 | 89448 | 0.35764 | 0 | 0.2301 | 2876.25 | 0.05325 | 4260 | 64000 | 2876.25 | 4260 | 18311.75 | 16543.2 | 1350000 | 18311.75 | 0
2021042720 | 3 | 0.59253 | 88879.5 | 0.36452 | 0 | 0.29709 | 3713.625 | 0 | 0 | 64000 | 3713.625 | 0 | 21165.875 | 2854.125 | 1350000 | 21165.875 | 0
2021042721 | 3 | 0.5955 | 89325 | 0.48203 | 0 | 0.36369 | 4546.125 | 0 | 0 | 64000 | 4546.125 | 0 | 20778.875 | -387 | 1350000 | 20778.875 | 0
2021042722 | 3 | 0.57843 | 86764.5 | 0.57761 | 0 | 0.45019 | 5627.375 | 0 | 0 | 64000 | 5627.375 | 0 | 17137.125 | -3641.75 | 1350000 | 17137.125 | 0
2021042723 | 3 | 0.53951 | 80926.5 | 0.68877 | 0 | 0.47301 | 5912.625 | 0 | 0 | 64000 | 5912.625 | 0 | 11013.875 | -6123.25 | 1350000 | 11013.875 | 0
2021042724 | 3 | 0.50047 | 75070.5 | 0.76853 | 0 | 0.4816 | 6020 | 0 | 0 | 64000 | 6020 | 0 | 5050.5 | -5963.375 | 1350000 | 5050.5 | 0
2021042801 | 4 | 0.46926 | 70389 | 0.77256 | 0 | 0.45476 | 5684.5 | 0 | 0 | 64000 | 5684.5 | 0 | 704.5 | -4346 | 1350000 | 704.5 | 0
2021042802 | 4 | 0.44799 | 67198.5 | 0.7833 | 0 | 0.35072 | 4384 | 0 | 0 | 64000 | 3198.5 | 0 | 0 | -704.5 | 1350000 | 0 | 0
2021042803 | 4 | 0.43465 | 65197.5 | 0.8695 | 0 | 0.26252 | 3281.5 | 0 | 0 | 64000 | 1197.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042804 | 4 | 0.42786 | 64179 | 0.88117 | 0 | 0.20946 | 2618.25 | 0 | 0 | 64000 | 179 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042805 | 4 | 0.4322 | 64830 | 0.89547 | 0 | 0.17042 | 2130.25 | 0 | 0 | 64000 | 830 | 0 | 0 | 0 | 1350000 | 0 | 0
2021042806 | 4 | 0.4531 | 67965 | 0.87936 | 0 | 0.14749 | 1843.625 | 0 | 0 | 64000 | 1843.625 | 0 | 2121.375 | 2121.375 | 1350000 | 2121.375 | 0
2021042807 | 4 | 0.48742 | 73113 | 0.87402 | 0 | 0.13712 | 1714 | 0.00611 | 488.8 | 64000 | 1714 | 488.8 | 6910.2 | 4788.825 | 1350000 | 6910.2 | 0
2021042808 | 4 | 0.51493 | 77239.5 | 0.85615 | 0 | 0.16712 | 2089 | 0.12342 | 9873.6 | 64000 | 2089 | 9873.6 | 1276.9 | -5633.3 | 1350000 | 1276.9 | 0
2021042809 | 4 | 0.53386 | 80079 | 0.7578 | 0 | 0.17772 | 2221.5 | 0.33762 | 27009.6 | 64000 | 2221.5 | 13857.5 | 0 | -1276.9 | 1350000 | 0 | 0
2021042810 | 4 | 0.54641 | 81961.5 | 0.68322 | 0 | 0.18768 | 2346 | 0.44521 | 35616.8 | 64000 | 2346 | 15615.5 | 0 | 0 | 1350000 | 0 | 0
2021042811 | 4 | 0.55905 | 83857.5 | 0.70179 | 0 | 0.1895 | 2368.75 | 0.48453 | 38762.4 | 64000 | 2368.75 | 17488.75 | 0 | 0 | 1350000 | 0 | 0
2021042812 | 4 | 0.57294 | 85941 | 0.6707 | 0 | 0.1809 | 2261.25 | 0.54534 | 43627.2 | 64000 | 2261.25 | 19679.75 | 0 | 0 | 1350000 | 0 | 0
2021042813 | 4 | 0.58564 | 87846 | 0.68471 | 0 | 0.18714 | 2339.25 | 0.59837 | 47869.6 | 64000 | 2339.25 | 21506.75 | 0 | 0 | 1350000 | 0 | 0
2021042814 | 4 | 0.59966 | 89949 | 0.77555 | 0 | 0.14023 | 1752.875 | 0.60265 | 48212 | 64000 | 1752.875 | 24196.125 | 0 | 0 | 1350000 | 0 | 0
2021042815 | 4 | 0.61336 | 92004 | 0.76581 | 0 | 0.10676 | 1334.5 | 0.58298 | 46638.4 | 64000 | 1334.5 | 26669.5 | 0 | 0 | 1350000 | 0 | 0
2021042816 | 4 | 0.62071 | 93106.5 | 0.68835 | 0 | 0.10742 | 1342.75 | 0.55813 | 44650.4 | 64000 | 1342.75 | 27763.75 | 0 | 0 | 1350000 | 0 | 0
2021042817 | 4 | 0.62938 | 94407 | 0.68013 | 0 | 0.1517 | 1896.25 | 0.45088 | 36070.4 | 64000 | 1896.25 | 28510.75 | 0 | 0 | 1350000 | 0 | 0
2021042818 | 4 | 0.63418 | 95127 | 0.63589 | 0 | 0.20401 | 2550.125 | 0.28403 | 22722.4 | 64000 | 2550.125 | 22722.4 | 5854.475 | 5854.475 | 1350000 | 5854.475 | 0
2021042819 | 4 | 0.63036 | 94554 | 0.54187 | 0 | 0.20046 | 2505.75 | 0.07365 | 5892 | 64000 | 2505.75 | 5892 | 22156.25 | 16301.775 | 1350000 | 22156.25 | 0
2021042820 | 4 | 0.62497 | 93745.5 | 0.50017 | 0 | 0.18809 | 2351.125 | 0.0015 | 120 | 64000 | 2351.125 | 120 | 27274.375 | 5118.125 | 1348191.875 | 27274.375 | 0
2021042821 | 4 | 0.6291 | 94365 | 0.41291 | 0 | 0.19993 | 2499.125 | 0 | 0 | 64000 | 2499.125 | 0 | 27865.875 | 591.5 | 1345792.25 | 27865.875 | 0
2021042822 | 4 | 0.60604 | 90906 | 0.40139 | 0 | 0.21126 | 2640.75 | 0 | 0 | 64000 | 2640.75 | 0 | 24265.25 | -3600.625 | 1346993.25 | 24265.25 | 0
2021042823 | 4 | 0.56527 | 84790.5 | 0.37596 | 0 | 0.18583 | 2322.875 | 0 | 0 | 64000 | 2322.875 | 0 | 18467.625 | -5797.625 | 1350000 | 18467.625 | 0
2021042824 | 4 | 0.5238 | 78570 | 0.42607 | 0 | 0.19292 | 2411.5 | 0 | 0 | 64000 | 2411.5 | 0 | 12158.5 | -6309.125 | 1350000 | 12158.5 | 0
2021042901 | 5 | 0.49094 | 73641 | 0.54 | 0 | 0.18728 | 2341 | 0 | 0 | 64000 | 2341 | 0 | 7300 | -4858.5 | 1350000 | 7300 | 0
2021042902 | 5 | 0.4686 | 70290 | 0.50904 | 0 | 0.18898 | 2362.25 | 0 | 0 | 64000 | 2362.25 | 0 | 3927.75 | -3372.25 | 1350000 | 3927.75 | 0
2021042903 | 5 | 0.45395 | 68092.5 | 0.45765 | 0 | 0.17734 | 2216.75 | 0 | 0 | 64000 | 2216.75 | 0 | 1875.75 | -2052 | 1350000 | 1875.75 | 0
2021042904 | 5 | 0.44635 | 66952.5 | 0.43171 | 0 | 0.1867 | 2333.75 | 0 | 0 | 64000 | 2333.75 | 0 | 618.75 | -1257 | 1350000 | 618.75 | 0
2021042905 | 5 | 0.44968 | 67452 | 0.43016 | 0 | 0.15994 | 1999.25 | 0 | 0 | 64000 | 1999.25 | 0 | 1452.75 | 834 | 1350000 | 1452.75 | 0
2021042906 | 5 | 0.47048 | 70572 | 0.44132 | 0 | 0.13512 | 1689 | 0 | 0 | 64000 | 1689 | 0 | 4883 | 3430.25 | 1350000 | 4883 | 0
2021042907 | 5 | 0.50762 | 76143 | 0.453 | 0 | 0.10862 | 1357.75 | 0.00686 | 548.8 | 64000 | 1357.75 | 548.8 | 10236.45 | 5353.45 | 1350000 | 10236.45 | 0
2021042908 | 5 | 0.53924 | 80886 | 0.44128 | 0 | 0.11228 | 1403.5 | 0.16178 | 12942.4 | 64000 | 1403.5 | 12942.4 | 2540.1 | -7696.35 | 1350000 | 2540.1 | 0
2021042909 | 5 | 0.56061 | 84091.5 | 0.41111 | 0 | 0.11133 | 1391.625 | 0.4341 | 34728 | 64000 | 1391.625 | 18699.875 | 0 | -2540.1 | 1350000 | 0 | 0
2021042910 | 5 | 0.57465 | 86197.5 | 0.41928 | 0 | 0.11908 | 1488.5 | 0.5538 | 44304 | 64000 | 1488.5 | 20709 | 0 | 0 | 1350000 | 0 | 0
2021042911 | 5 | 0.58731 | 88096.5 | 0.49814 | 0 | 0.10734 | 1341.75 | 0.60153 | 48122.4 | 64000 | 1341.75 | 22754.75 | 0 | 0 | 1350000 | 0 | 0
2021042912 | 5 | 0.59801 | 89701.5 | 0.58039 | 0 | 0.11149 | 1393.625 | 0.66117 | 52893.6 | 64000 | 1393.625 | 24307.875 | 0 | 0 | 1350000 | 0 | 0
2021042913 | 5 | 0.60664 | 90996 | 0.67272 | 0 | 0.09907 | 1238.375 | 0.6866 | 54928 | 64000 | 1238.375 | 25757.625 | 0 | 0 | 1350000 | 0 | 0
2021042914 | 5 | 0.61394 | 92091 | 0.80567 | 0 | 0.11089 | 1386.125 | 0.70056 | 56044.8 | 64000 | 1386.125 | 26704.875 | 0 | 0 | 1350000 | 0 | 0
2021042915 | 5 | 0.61537 | 92305.5 | 0.90733 | 0 | 0.11334 | 1416.75 | 0.68697 | 54957.6 | 64000 | 1416.75 | 26888.75 | 0 | 0 | 1350000 | 0 | 0
2021042916 | 5 | 0.61188 | 91782 | 0.9433 | 0 | 0.11149 | 1393.625 | 0.62489 | 49991.2 | 64000 | 1393.625 | 26388.375 | 0 | 0 | 1350000 | 0 | 0
2021042917 | 5 | 0.60931 | 91396.5 | 0.9703 | 0 | 0.1313 | 1641.25 | 0.48667 | 38933.6 | 64000 | 1641.25 | 25755.25 | 0 | 0 | 1350000 | 0 | 0
2021042918 | 5 | 0.61238 | 91857 | 0.97679 | 0 | 0.16489 | 2061.125 | 0.32633 | 26106.4 | 64000 | 2061.125 | 25795.875 | 0 | 0 | 1350000 | 0 | 0
2021042919 | 5 | 0.60659 | 90988.5 | 0.93518 | 0 | 0.19417 | 2427.125 | 0.09471 | 7576.8 | 64000 | 2427.125 | 7576.8 | 16984.575 | 16984.575 | 1350000 | 16984.575 | 0
2021042920 | 5 | 0.60198 | 90297 | 0.86155 | 0 | 0.20689 | 2586.125 | 0.00114 | 91.2 | 64000 | 2586.125 | 91.2 | 23619.675 | 6635.1 | 1350000 | 23619.675 | 0
2021042921 | 5 | 0.59992 | 89988 | 0.80627 | 0 | 0.21498 | 2687.25 | 0 | 0 | 64000 | 2687.25 | 0 | 23300.75 | -318.925 | 1350000 | 23300.75 | 0
2021042922 | 5 | 0.58244 | 87366 | 0.78044 | 0 | 0.21255 | 2656.875 | 0 | 0 | 64000 | 2656.875 | 0 | 20709.125 | -2591.625 | 1350000 | 20709.125 | 0
2021042923 | 5 | 0.5486 | 82290 | 0.76524 | 0 | 0.2047 | 2558.75 | 0 | 0 | 64000 | 2558.75 | 0 | 15731.25 | -4977.875 | 1350000 | 15731.25 | 0
2021042924 | 5 | 0.50968 | 76452 | 0.86718 | 0 | 0.19398 | 2424.75 | 0 | 0 | 64000 | 2424.75 | 0 | 10027.25 | -5704 | 1350000 | 10027.25 | 0
2021043001 | 6 | 0.47826 | 71739 | 0.91874 | 0 | 0.18893 | 2361.625 | 0 | 0 | 64000 | 2361.625 | 0 | 5377.375 | -4649.875 | 1350000 | 5377.375 | 0
2021043002 | 6 | 0.45847 | 68770.5 | 0.94945 | 0 | 0.19723 | 2465.375 | 0 | 0 | 64000 | 2465.375 | 0 | 2305.125 | -3072.25 | 1350000 | 2305.125 | 0
2021043003 | 6 | 0.44341 | 66511.5 | 0.97132 | 0 | 0.18766 | 2345.75 | 0 | 0 | 64000 | 2345.75 | 0 | 165.75 | -2139.375 | 1350000 | 165.75 | 0
2021043004 | 6 | 0.43615 | 65422.5 | 0.9847 | 0 | 0.18581 | 2322.625 | 0 | 0 | 64000 | 1422.5 | 0 | 0 | -165.75 | 1350000 | 0 | 0
2021043005 | 6 | 0.43952 | 65928 | 0.993 | 0 | 0.18806 | 2350.75 | 0 | 0 | 64000 | 1928 | 0 | 0 | 0 | 1350000 | 0 | 0
2021043006 | 6 | 0.45835 | 68752.5 | 0.99294 | 0 | 0.17444 | 2180.5 | 0 | 0 | 64000 | 2180.5 | 0 | 2572 | 2572 | 1350000 | 2572 | 0
2021043007 | 6 | 0.4903 | 73545 | 0.98074 | 0 | 0.16344 | 2043 | 0.00832 | 665.6 | 64000 | 2043 | 665.6 | 6836.4 | 4264.4 | 1350000 | 6836.4 | 0
2021043008 | 6 | 0.51779 | 77668.5 | 0.96275 | 0 | 0.18119 | 2264.875 | 0.18495 | 14796 | 64000 | 2264.875 | 11403.625 | 0 | -6836.4 | 1350000 | 0 | 0
2021043009 | 6 | 0.53019 | 79528.5 | 0.95222 | 0 | 0.16614 | 2076.75 | 0.48911 | 39128.8 | 64000 | 2076.75 | 13451.75 | 0 | 0 | 1350000 | 0 | 0
2021043010 | 6 | 0.53485 | 80227.5 | 0.94023 | 0 | 0.13287 | 1660.875 | 0.62331 | 49864.8 | 64000 | 1660.875 | 14566.625 | 0 | 0 | 1350000 | 0 | 0
2021043011 | 6 | 0.53925 | 80887.5 | 0.97366 | 0 | 0.08283 | 1035.375 | 0.65828 | 52662.4 | 64000 | 1035.375 | 15852.125 | 0 | 0 | 1350000 | 0 | 0
2021043012 | 6 | 0.54238 | 81357 | 0.98719 | 0 | 0.04998 | 624.75 | 0.67893 | 54314.4 | 64000 | 624.75 | 16732.25 | 0 | 0 | 1350000 | 0 | 0
2021043013 | 6 | 0.54184 | 81276 | 0.99339 | 0 | 0.04212 | 526.5 | 0.68682 | 54945.6 | 64000 | 526.5 | 16749.5 | 0 | 0 | 1350000 | 0 | 0
2021043014 | 6 | 0.54005 | 81007.5 | 0.99224 | 0 | 0.0495 | 618.75 | 0.69624 | 55699.2 | 64000 | 618.75 | 16388.75 | 0 | 0 | 1350000 | 0 | 0
2021043015 | 6 | 0.53617 | 80425.5 | 0.99467 | 0 | 0.0658 | 822.5 | 0.71113 | 56890.4 | 64000 | 822.5 | 15603 | 0 | 0 | 1350000 | 0 | 0
2021043016 | 6 | 0.53175 | 79762.5 | 0.99519 | 0 | 0.06861 | 857.625 | 0.71667 | 57333.6 | 64000 | 857.625 | 14904.875 | 0 | 0 | 1350000 | 0 | 0
2021043017 | 6 | 0.53086 | 79629 | 0.99748 | 0 | 0.10109 | 1263.625 | 0.66877 | 53501.6 | 64000 | 1263.625 | 14365.375 | 0 | 0 | 1350000 | 0 | 0
2021043018 | 6 | 0.52643 | 78964.5 | 0.98947 | 0 | 0.20437 | 2554.625 | 0.48692 | 38953.6 | 64000 | 2554.625 | 12409.875 | 0 | 0 | 1350000 | 0 | 0
2021043019 | 6 | 0.52301 | 78451.5 | 0.98629 | 0 | 0.23236 | 2904.5 | 0.13709 | 10967.2 | 64000 | 2904.5 | 10967.2 | 579.8 | 579.8 | 1350000 | 579.8 | 0
2021043020 | 6 | 0.52045 | 78067.5 | 0.9895 | 0 | 0.20915 | 2614.375 | 0.00218 | 174.4 | 64000 | 2614.375 | 174.4 | 11278.725 | 10698.925 | 1350000 | 11278.725 | 0
2021043021 | 6 | 0.52672 | 79008 | 0.98579 | 0 | 0.207 | 2587.5 | 0 | 0 | 64000 | 2587.5 | 0 | 12420.5 | 1141.775 | 1350000 | 12420.5 | 0
2021043022 | 6 | 0.52145 | 78217.5 | 0.98029 | 0 | 0.19015 | 2376.875 | 0 | 0 | 64000 | 2376.875 | 0 | 11840.625 | -579.875 | 1350000 | 11840.625 | 0
2021043023 | 6 | 0.49777 | 74665.5 | 0.97611 | 0 | 0.16124 | 2015.5 | 0 | 0 | 64000 | 2015.5 | 0 | 8650 | -3190.625 | 1350000 | 8650 | 0
2021043024 | 6 | 0.47057 | 70585.5 | 0.99236 | 0 | 0.1725 | 2156.25 | 0 | 0 | 64000 | 2156.25 | 0 | 4429.25 | -4220.75 | 1350000 | 4429.25 | 0
2021050101 | 7 | 0.44883 | 67324.5 | 0.99754 | 0 | 0.19138 | 2392.25 | 0 | 0 | 64000 | 2392.25 | 0 | 932.25 | -3497 | 1350000 | 932.25 | 0
2021050102 | 7 | 0.43451 | 65176.5 | 0.99644 | 0 | 0.22169 | 2771.125 | 0 | 0 | 64000 | 1176.5 | 0 | 0 | -932.25 | 1350000 | 0 | 0
2021050103 | 7 | 0.42693 | 64039.5 | 0.99446 | 0 | 0.23248 | 2906 | 0 | 0 | 64000 | 39.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050104 | 7 | 0.42575 | 63862.5 | 0.99515 | 0 | 0.19678 | 2459.75 | 0 | 0 | 63862.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050105 | 7 | 0.42907 | 64360.5 | 0.9907 | 0 | 0.17155 | 2144.375 | 0 | 0 | 64000 | 360.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050106 | 7 | 0.43951 | 65926.5 | 0.98686 | 0 | 0.12105 | 1513.125 | 0 | 0 | 64000 | 1513.125 | 0 | 413.375 | 413.375 | 1350000 | 413.375 | 0
2021050107 | 7 | 0.45455 | 68182.5 | 0.96313 | 0 | 0.08158 | 1019.75 | 0.01417 | 1133.6 | 64000 | 1019.75 | 1133.6 | 2029.15 | 1615.775 | 1350000 | 2029.15 | 0
2021050108 | 7 | 0.46955 | 70432.5 | 0.87844 | 0 | 0.08192 | 1024 | 0.23005 | 18404 | 64000 | 1024 | 5408.5 | 0 | -2029.15 | 1350000 | 0 | 0
2021050109 | 7 | 0.47857 | 71785.5 | 0.81429 | 0 | 0.08289 | 1036.125 | 0.54113 | 43290.4 | 64000 | 1036.125 | 6749.375 | 0 | 0 | 1350000 | 0 | 0
2021050110 | 7 | 0.47865 | 71797.5 | 0.7927 | 0 | 0.08123 | 1015.375 | 0.652 | 52160 | 64000 | 1015.375 | 6782.125 | 0 | 0 | 1350000 | 0 | 0
2021050111 | 7 | 0.47666 | 71499 | 0.64025 | 0 | 0.08204 | 1025.5 | 0.66413 | 53130.4 | 64000 | 1025.5 | 6473.5 | 0 | 0 | 1350000 | 0 | 0
2021050112 | 7 | 0.47018 | 70527 | 0.39309 | 0 | 0.08329 | 1041.125 | 0.66917 | 53533.6 | 64000 | 1041.125 | 5485.875 | 0 | 0 | 1350000 | 0 | 0
2021050113 | 7 | 0.46323 | 69484.5 | 0.28148 | 0 | 0.09065 | 1133.125 | 0.67418 | 53934.4 | 64000 | 1133.125 | 4351.375 | 0 | 0 | 1350000 | 0 | 0
2021050114 | 7 | 0.45795 | 68692.5 | 0.2203 | 0 | 0.07818 | 977.25 | 0.6814 | 54512 | 64000 | 977.25 | 3715.25 | 0 | 0 | 1350000 | 0 | 0
2021050115 | 7 | 0.45559 | 68338.5 | 0.22246 | 0 | 0.08171 | 1021.375 | 0.68652 | 54921.6 | 64000 | 1021.375 | 3317.125 | 0 | 0 | 1350000 | 0 | 0
2021050116 | 7 | 0.45688 | 68532 | 0.33826 | 0 | 0.05969 | 746.125 | 0.66032 | 52825.6 | 64000 | 746.125 | 3785.875 | 0 | 0 | 1350000 | 0 | 0
2021050117 | 7 | 0.46576 | 69864 | 0.33297 | 0 | 0.06579 | 822.375 | 0.59587 | 47669.6 | 64000 | 822.375 | 5041.625 | 0 | 0 | 1350000 | 0 | 0
2021050118 | 7 | 0.47804 | 71706 | 0.41146 | 0 | 0.13471 | 1683.875 | 0.38246 | 30596.8 | 64000 | 1683.875 | 6022.125 | 0 | 0 | 1350000 | 0 | 0
2021050119 | 7 | 0.48745 | 73117.5 | 0.5537 | 0 | 0.14599 | 1824.875 | 0.08773 | 7018.4 | 64000 | 1824.875 | 7018.4 | 274.225 | 274.225 | 1350000 | 274.225 | 0
2021050120 | 7 | 0.49155 | 73732.5 | 0.59107 | 0 | 0.16583 | 2072.875 | 0.00107 | 85.6 | 64000 | 2072.875 | 85.6 | 7574.025 | 7299.8 | 1350000 | 7574.025 | 0
2021050121 | 7 | 0.50167 | 75250.5 | 0.60899 | 0 | 0.17174 | 2146.75 | 0 | 0 | 64000 | 2146.75 | 0 | 9103.75 | 1529.725 | 1350000 | 9103.75 | 0
2021050122 | 7 | 0.49764 | 74646 | 0.73053 | 0 | 0.17384 | 2173 | 0 | 0 | 64000 | 2173 | 0 | 8473 | -630.75 | 1350000 | 8473 | 0
2021050123 | 7 | 0.47813 | 71719.5 | 0.82065 | 0 | 0.20975 | 2621.875 | 0 | 0 | 64000 | 2621.875 | 0 | 5097.625 | -3375.375 | 1350000 | 5097.625 | 0
2021050124 | 7 | 0.45216 | 67824 | 0.89124 | 0 | 0.26775 | 3346.875 | 0 | 0 | 64000 | 3346.875 | 0 | 477.125 | -4620.5 | 1350000 | 477.125 | 0
2021050201 | 1 | 0.43027 | 64540.5 | 0.92681 | 0 | 0.33098 | 4137.25 | 0 | 0 | 64000 | 540.5 | 0 | 0 | -477.125 | 1350000 | 0 | 0
2021050202 | 1 | 0.41481 | 62221.5 | 0.9299 | 0 | 0.36687 | 4585.875 | 0 | 0 | 62221.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050203 | 1 | 0.40443 | 60664.5 | 0.91759 | 0 | 0.38849 | 4856.125 | 0 | 0 | 60664.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050204 | 1 | 0.39955 | 59932.5 | 0.90277 | 0 | 0.40178 | 5022.25 | 0 | 0 | 59932.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050205 | 1 | 0.39918 | 59877 | 0.92434 | 0 | 0.36015 | 4501.875 | 0 | 0 | 59877 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050206 | 1 | 0.40414 | 60621 | 0.91666 | 0 | 0.29071 | 3633.875 | 0 | 0 | 60621 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050207 | 1 | 0.40896 | 61344 | 0.88516 | 0 | 0.26537 | 3317.125 | 0.00763 | 610.4 | 61344 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050208 | 1 | 0.41817 | 62725.5 | 0.8754 | 0 | 0.28276 | 3534.5 | 0.06129 | 4903.2 | 62725.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050209 | 1 | 0.43632 | 65448 | 0.86184 | 0 | 0.30847 | 3855.875 | 0.19732 | 15785.6 | 64000 | 1448 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050210 | 1 | 0.44947 | 67420.5 | 0.79136 | 0 | 0.33008 | 4126 | 0.29743 | 23794.4 | 64000 | 3420.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050211 | 1 | 0.46021 | 69031.5 | 0.73391 | 0 | 0.33138 | 4142.25 | 0.38259 | 30607.2 | 64000 | 4142.25 | 889.25 | 0 | 0 | 1350000 | 0 | 0
2021050212 | 1 | 0.46905 | 70357.5 | 0.70742 | 0 | 0.3262 | 4077.5 | 0.3454 | 27632 | 64000 | 4077.5 | 2280 | 0 | 0 | 1350000 | 0 | 0
2021050213 | 1 | 0.47845 | 71767.5 | 0.67942 | 0 | 0.32692 | 4086.5 | 0.37479 | 29983.2 | 64000 | 4086.5 | 3681 | 0 | 0 | 1350000 | 0 | 0
2021050214 | 1 | 0.48836 | 73254 | 0.70461 | 0 | 0.3414 | 4267.5 | 0.38306 | 30644.8 | 64000 | 4267.5 | 4986.5 | 0 | 0 | 1350000 | 0 | 0
2021050215 | 1 | 0.50148 | 75222 | 0.73731 | 0 | 0.31427 | 3928.375 | 0.37108 | 29686.4 | 64000 | 3928.375 | 7293.625 | 0 | 0 | 1350000 | 0 | 0
2021050216 | 1 | 0.51855 | 77782.5 | 0.71268 | 0 | 0.30244 | 3780.5 | 0.32581 | 26064.8 | 64000 | 3780.5 | 10002 | 0 | 0 | 1350000 | 0 | 0
2021050217 | 1 | 0.53847 | 80770.5 | 0.63572 | 0 | 0.26375 | 3296.875 | 0.29608 | 23686.4 | 64000 | 3296.875 | 13473.625 | 0 | 0 | 1350000 | 0 | 0
2021050218 | 1 | 0.55568 | 83352 | 0.50789 | 0 | 0.27319 | 3414.875 | 0.21448 | 17158.4 | 64000 | 3414.875 | 15937.125 | 0 | 0 | 1350000 | 0 | 0
2021050219 | 1 | 0.5613 | 84195 | 0.41647 | 0 | 0.27998 | 3499.75 | 0.04413 | 3530.4 | 64000 | 3499.75 | 3530.4 | 13164.85 | 13164.85 | 1350000 | 13164.85 | 0
2021050220 | 1 | 0.55983 | 83974.5 | 0.29623 | 0 | 0.27114 | 3389.25 | 0.00171 | 136.8 | 64000 | 3389.25 | 136.8 | 16448.45 | 3283.6 | 1350000 | 16448.45 | 0
2021050221 | 1 | 0.56523 | 84784.5 | 0.27046 | 0 | 0.28723 | 3590.375 | 0 | 0 | 64000 | 3590.375 | 0 | 17194.125 | 745.675 | 1350000 | 17194.125 | 0
2021050222 | 1 | 0.55251 | 82876.5 | 0.27856 | 0 | 0.2919 | 3648.75 | 0 | 0 | 64000 | 3648.75 | 0 | 15227.75 | -1966.375 | 1350000 | 15227.75 | 0
2021050223 | 1 | 0.51997 | 77995.5 | 0.26987 | 0 | 0.30515 | 3814.375 | 0 | 0 | 64000 | 3814.375 | 0 | 10181.125 | -5046.625 | 1350000 | 10181.125 | 0
2021050224 | 1 | 0.484 | 72600 | 0.34285 | 0 | 0.29103 | 3637.875 | 0 | 0 | 64000 | 3637.875 | 0 | 4962.125 | -5219 | 1350000 | 4962.125 | 0
2021050301 | 2 | 0.45575 | 68362.5 | 0.42534 | 0 | 0.2982 | 3727.5 | 0 | 0 | 64000 | 3727.5 | 0 | 635 | -4327.125 | 1350000 | 635 | 0
2021050302 | 2 | 0.43613 | 65419.5 | 0.3906 | 0 | 0.33018 | 4127.25 | 0 | 0 | 64000 | 1419.5 | 0 | 0 | -635 | 1350000 | 0 | 0
2021050303 | 2 | 0.42412 | 63618 | 0.46978 | 0 | 0.35331 | 4416.375 | 0 | 0 | 63618 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050304 | 2 | 0.42123 | 63184.5 | 0.53404 | 0 | 0.32033 | 4004.125 | 0 | 0 | 63184.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050305 | 2 | 0.42642 | 63963 | 0.45326 | 0 | 0.30362 | 3795.25 | 0 | 0 | 63963 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050306 | 2 | 0.44742 | 67113 | 0.44928 | 0 | 0.27241 | 3405.125 | 0 | 0 | 64000 | 3113 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050307 | 2 | 0.48231 | 72346.5 | 0.37894 | 0 | 0.25993 | 3249.125 | 0.0052 | 416 | 64000 | 3249.125 | 416 | 4681.375 | 4681.375 | 1350000 | 4681.375 | 0
2021050308 | 2 | 0.51493 | 77239.5 | 0.29791 | 0 | 0.20889 | 2611.125 | 0.06027 | 4821.6 | 64000 | 2611.125 | 4821.6 | 5806.775 | 1125.4 | 1350000 | 5806.775 | 0
2021050309 | 2 | 0.53691 | 80536.5 | 0.24069 | 0 | 0.1696 | 2120 | 0.15334 | 12267.2 | 64000 | 2120 | 12267.2 | 2149.3 | -3657.475 | 1350000 | 2149.3 | 0
2021050310 | 2 | 0.55063 | 82594.5 | 0.20084 | 0 | 0.15342 | 1917.75 | 0.24889 | 19911.2 | 64000 | 1917.75 | 16676.75 | 0 | -2149.3 | 1350000 | 0 | 0
2021050311 | 2 | 0.56168 | 84252 | 0.20143 | 0 | 0.12068 | 1508.5 | 0.368 | 29440 | 64000 | 1508.5 | 18743.5 | 0 | 0 | 1350000 | 0 | 0
2021050312 | 2 | 0.56846 | 85269 | 0.27488 | 0 | 0.1073 | 1341.25 | 0.45328 | 36262.4 | 64000 | 1341.25 | 19927.75 | 0 | 0 | 1350000 | 0 | 0
2021050313 | 2 | 0.57362 | 86043 | 0.38949 | 0 | 0.08821 | 1102.625 | 0.51039 | 40831.2 | 64000 | 1102.625 | 20940.375 | 0 | 0 | 1350000 | 0 | 0
2021050314 | 2 | 0.58104 | 87156 | 0.39975 | 0 | 0.07158 | 894.75 | 0.55345 | 44276 | 64000 | 894.75 | 22261.25 | 0 | 0 | 1350000 | 0 | 0
2021050315 | 2 | 0.58474 | 87711 | 0.30514 | 0 | 0.06016 | 752 | 0.58429 | 46743.2 | 64000 | 752 | 22959 | 0 | 0 | 1350000 | 0 | 0
2021050316 | 2 | 0.58277 | 87415.5 | 0.27926 | 0 | 0.04119 | 514.875 | 0.60616 | 48492.8 | 64000 | 514.875 | 22900.625 | 0 | 0 | 1350000 | 0 | 0
2021050317 | 2 | 0.58495 | 87742.5 | 0.27243 | 0 | 0.03609 | 451.125 | 0.54962 | 43969.6 | 64000 | 451.125 | 23291.375 | 0 | 0 | 1350000 | 0 | 0
2021050318 | 2 | 0.5894 | 88410 | 0.29673 | 0 | 0.05909 | 738.625 | 0.36155 | 28924 | 64000 | 738.625 | 23671.375 | 0 | 0 | 1350000 | 0 | 0
2021050319 | 2 | 0.5883 | 88245 | 0.3361 | 0 | 0.06499 | 812.375 | 0.10588 | 8470.4 | 64000 | 812.375 | 8470.4 | 14962.225 | 14962.225 | 1350000 | 14962.225 | 0
2021050320 | 2 | 0.58495 | 87742.5 | 0.39788 | 0 | 0.06587 | 823.375 | 0.00182 | 145.6 | 64000 | 823.375 | 145.6 | 22773.525 | 7811.3 | 1350000 | 22773.525 | 0
2021050321 | 2 | 0.58462 | 87693 | 0.45075 | 0 | 0.07179 | 897.375 | 0 | 0 | 64000 | 897.375 | 0 | 22795.625 | 22.1 | 1350000 | 22795.625 | 0
2021050322 | 2 | 0.56716 | 85074 | 0.46608 | 0 | 0.07538 | 942.25 | 0 | 0 | 64000 | 942.25 | 0 | 20131.75 | -2663.875 | 1350000 | 20131.75 | 0
2021050323 | 2 | 0.53417 | 80125.5 | 0.42988 | 0 | 0.07179 | 897.375 | 0 | 0 | 64000 | 897.375 | 0 | 15228.125 | -4903.625 | 1350000 | 15228.125 | 0
2021050324 | 2 | 0.49791 | 74686.5 | 0.37128 | 0 | 0.07305 | 913.125 | 0 | 0 | 64000 | 913.125 | 0 | 9773.375 | -5454.75 | 1350000 | 9773.375 | 0
2021050401 | 3 | 0.46914 | 70371 | 0.39984 | 0 | 0.06728 | 841 | 0 | 0 | 64000 | 841 | 0 | 5530 | -4243.375 | 1350000 | 5530 | 0
2021050402 | 3 | 0.44986 | 67479 | 0.45329 | 0 | 0.06415 | 801.875 | 0 | 0 | 64000 | 801.875 | 0 | 2677.125 | -2852.875 | 1350000 | 2677.125 | 0
2021050403 | 3 | 0.4378 | 65670 | 0.50422 | 0 | 0.05639 | 704.875 | 0 | 0 | 64000 | 704.875 | 0 | 965.125 | -1712 | 1350000 | 965.125 | 0
2021050404 | 3 | 0.43248 | 64872 | 0.52401 | 0 | 0.0439 | 548.75 | 0 | 0 | 64000 | 548.75 | 0 | 323.25 | -641.875 | 1350000 | 323.25 | 0
2021050405 | 3 | 0.43816 | 65724 | 0.52578 | 0 | 0.03445 | 430.625 | 0 | 0 | 64000 | 430.625 | 0 | 1293.375 | 970.125 | 1350000 | 1293.375 | 0
2021050406 | 3 | 0.45962 | 68943 | 0.45285 | 0 | 0.04465 | 558.125 | 0 | 0 | 64000 | 558.125 | 0 | 4384.875 | 3091.5 | 1350000 | 4384.875 | 0
2021050407 | 3 | 0.49392 | 74088 | 0.51704 | 0 | 0.04555 | 569.375 | 0.00699 | 559.2 | 64000 | 569.375 | 559.2 | 8959.425 | 4574.55 | 1350000 | 8959.425 | 0
2021050408 | 3 | 0.52585 | 78877.5 | 0.4593 | 0 | 0.04915 | 614.375 | 0.12316 | 9852.8 | 64000 | 614.375 | 9852.8 | 4410.325 | -4549.1 | 1350000 | 4410.325 | 0
2021050409 | 3 | 0.54882 | 82323 | 0.44113 | 0 | 0.04169 | 521.125 | 0.3666 | 29328 | 64000 | 521.125 | 17801.875 | 0 | -4410.325 | 1350000 | 0 | 0
2021050410 | 3 | 0.56624 | 84936 | 0.34005 | 0 | 0.04336 | 542 | 0.44991 | 35992.8 | 64000 | 542 | 20394 | 0 | 0 | 1350000 | 0 | 0
2021050411 | 3 | 0.58068 | 87102 | 0.2772 | 0 | 0.03603 | 450.375 | 0.54992 | 43993.6 | 64000 | 450.375 | 22651.625 | 0 | 0 | 1350000 | 0 | 0
2021050412 | 3 | 0.59077 | 88615.5 | 0.29897 | 0 | 0.02843 | 355.375 | 0.62561 | 50048.8 | 64000 | 355.375 | 24260.125 | 0 | 0 | 1350000 | 0 | 0
2021050413 | 3 | 0.60211 | 90316.5 | 0.33009 | 0 | 0.02426 | 303.25 | 0.62922 | 50337.6 | 64000 | 303.25 | 26013.25 | 0 | 0 | 1350000 | 0 | 0
2021050414 | 3 | 0.61292 | 91938 | 0.53644 | 0 | 0.02292 | 286.5 | 0.61793 | 49434.4 | 64000 | 286.5 | 27651.5 | 0 | 0 | 1350000 | 0 | 0
2021050415 | 3 | 0.61962 | 92943 | 0.60273 | 0 | 0.02479 | 309.875 | 0.59052 | 47241.6 | 64000 | 309.875 | 28633.125 | 0 | 0 | 1350000 | 0 | 0
2021050416 | 3 | 0.62288 | 93432 | 0.55297 | 0 | 0.03027 | 378.375 | 0.57896 | 46316.8 | 64000 | 378.375 | 29053.625 | 0 | 0 | 1350000 | 0 | 0
2021050417 | 3 | 0.62545 | 93817.5 | 0.33426 | 0 | 0.04373 | 546.625 | 0.49458 | 39566.4 | 64000 | 546.625 | 29270.875 | 0 | 0 | 1350000 | 0 | 0
2021050418 | 3 | 0.62428 | 93642 | 0.25021 | 0 | 0.08377 | 1047.125 | 0.34157 | 27325.6 | 64000 | 1047.125 | 27325.6 | 1269.275 | 1269.275 | 1350000 | 1269.275 | 0
2021050419 | 3 | 0.61445 | 92167.5 | 0.2638 | 0 | 0.09985 | 1248.125 | 0.08806 | 7044.8 | 64000 | 1248.125 | 7044.8 | 19874.575 | 18605.3 | 1350000 | 19874.575 | 0
2021050420 | 3 | 0.60232 | 90348 | 0.36156 | 0 | 0.10716 | 1339.5 | 0.0013 | 104 | 64000 | 1339.5 | 104 | 24904.5 | 5029.925 | 1350000 | 24904.5 | 0
2021050421 | 3 | 0.59862 | 89793 | 0.46883 | 0 | 0.1395 | 1743.75 | 0 | 0 | 64000 | 1743.75 | 0 | 24049.25 | -855.25 | 1350000 | 24049.25 | 0
2021050422 | 3 | 0.57931 | 86896.5 | 0.47558 | 0 | 0.15948 | 1993.5 | 0 | 0 | 64000 | 1993.5 | 0 | 20903 | -3146.25 | 1350000 | 20903 | 0
2021050423 | 3 | 0.54097 | 81145.5 | 0.36182 | 0 | 0.1627 | 2033.75 | 0 | 0 | 64000 | 2033.75 | 0 | 15111.75 | -5791.25 | 1350000 | 15111.75 | 0
2021050424 | 3 | 0.5024 | 75360 | 0.34401 | 0 | 0.17391 | 2173.875 | 0 | 0 | 64000 | 2173.875 | 0 | 9186.125 | -5925.625 | 1350000 | 9186.125 | 0
2021050501 | 4 | 0.47329 | 70993.5 | 0.31562 | 0 | 0.17587 | 2198.375 | 0 | 0 | 64000 | 2198.375 | 0 | 4795.125 | -4391 | 1350000 | 4795.125 | 0
2021050502 | 4 | 0.45301 | 67951.5 | 0.27535 | 0 | 0.16257 | 2032.125 | 0 | 0 | 64000 | 2032.125 | 0 | 1919.375 | -2875.75 | 1350000 | 1919.375 | 0
2021050503 | 4 | 0.44205 | 66307.5 | 0.21154 | 0 | 0.16308 | 2038.5 | 0 | 0 | 64000 | 2038.5 | 0 | 269 | -1650.375 | 1350000 | 269 | 0
2021050504 | 4 | 0.4364 | 65460 | 0.13088 | 0 | 0.12794 | 1599.25 | 0 | 0 | 64000 | 1460 | 0 | 0 | -269 | 1350000 | 0 | 0
2021050505 | 4 | 0.44083 | 66124.5 | 0.08474 | 0 | 0.12104 | 1513 | 0 | 0 | 64000 | 1513 | 0 | 611.5 | 611.5 | 1350000 | 611.5 | 0
2021050506 | 4 | 0.46048 | 69072 | 0.04979 | 0 | 0.11039 | 1379.875 | 0 | 0 | 64000 | 1379.875 | 0 | 3692.125 | 3080.625 | 1350000 | 3692.125 | 0
2021050507 | 4 | 0.49502 | 74253 | 0.10684 | 0 | 0.17465 | 2183.125 | 0.01078 | 862.4 | 64000 | 2183.125 | 862.4 | 7207.475 | 3515.35 | 1350000 | 7207.475 | 0
2021050508 | 4 | 0.52792 | 79188 | 0.14092 | 0 | 0.1859 | 2323.75 | 0.14223 | 11378.4 | 64000 | 2323.75 | 11378.4 | 1485.85 | -5721.625 | 1350000 | 1485.85 | 0
2021050509 | 4 | 0.54734 | 82101 | 0.08431 | 0 | 0.23013 | 2876.625 | 0.32996 | 26396.8 | 64000 | 2876.625 | 15224.375 | 0 | -1485.85 | 1350000 | 0 | 0
2021050510 | 4 | 0.55799 | 83698.5 | 0.24772 | 0 | 0.27229 | 3403.625 | 0.42321 | 33856.8 | 64000 | 3403.625 | 16294.875 | 0 | 0 | 1350000 | 0 | 0
2021050511 | 4 | 0.56635 | 84952.5 | 0.44856 | 0 | 0.32011 | 4001.375 | 0.46196 | 36956.8 | 64000 | 4001.375 | 16951.125 | 0 | 0 | 1350000 | 0 | 0
2021050512 | 4 | 0.57131 | 85696.5 | 0.5655 | 0 | 0.34819 | 4352.375 | 0.50206 | 40164.8 | 64000 | 4352.375 | 17344.125 | 0 | 0 | 1350000 | 0 | 0
2021050513 | 4 | 0.57824 | 86736 | 0.62328 | 0 | 0.33028 | 4128.5 | 0.4733 | 37864 | 64000 | 4128.5 | 18607.5 | 0 | 0 | 1350000 | 0 | 0
2021050514 | 4 | 0.58157 | 87235.5 | 0.75317 | 0 | 0.30096 | 3762 | 0.47239 | 37791.2 | 64000 | 3762 | 19473.5 | 0 | 0 | 1350000 | 0 | 0
2021050515 | 4 | 0.58108 | 87162 | 0.86817 | 0 | 0.28029 | 3503.625 | 0.41376 | 33100.8 | 64000 | 3503.625 | 19658.375 | 0 | 0 | 1350000 | 0 | 0
2021050516 | 4 | 0.57591 | 86386.5 | 0.88835 | 0 | 0.18393 | 2299.125 | 0.33766 | 27012.8 | 64000 | 2299.125 | 20087.375 | 0 | 0 | 1350000 | 0 | 0
2021050517 | 4 | 0.57769 | 86653.5 | 0.89501 | 0 | 0.14904 | 1863 | 0.26698 | 21358.4 | 64000 | 1863 | 20790.5 | 0 | 0 | 1350000 | 0 | 0
2021050518 | 4 | 0.57845 | 86767.5 | 0.89877 | 0 | 0.19491 | 2436.375 | 0.17848 | 14278.4 | 64000 | 2436.375 | 14278.4 | 6052.725 | 6052.725 | 1350000 | 6052.725 | 0
2021050519 | 4 | 0.5707 | 85605 | 0.84972 | 0 | 0.24731 | 3091.375 | 0.0592 | 4736 | 64000 | 3091.375 | 4736 | 13777.625 | 7724.9 | 1350000 | 13777.625 | 0
2021050520 | 4 | 0.56151 | 84226.5 | 0.90074 | 0 | 0.24926 | 3115.75 | 0.00118 | 94.4 | 64000 | 3115.75 | 94.4 | 17016.35 | 3238.725 | 1350000 | 17016.35 | 0
2021050521 | 4 | 0.56129 | 84193.5 | 0.91321 | 0 | 0.26221 | 3277.625 | 0 | 0 | 64000 | 3277.625 | 0 | 16915.875 | -100.475 | 1350000 | 16915.875 | 0
2021050522 | 4 | 0.54833 | 82249.5 | 0.91834 | 0 | 0.29018 | 3627.25 | 0 | 0 | 64000 | 3627.25 | 0 | 14622.25 | -2293.625 | 1350000 | 14622.25 | 0
2021050523 | 4 | 0.51647 | 77470.5 | 0.8636 | 0 | 0.30114 | 3764.25 | 0 | 0 | 64000 | 3764.25 | 0 | 9706.25 | -4916 | 1350000 | 9706.25 | 0
2021050524 | 4 | 0.48316 | 72474 | 0.8491 | 0 | 0.30484 | 3810.5 | 0 | 0 | 64000 | 3810.5 | 0 | 4663.5 | -5042.75 | 1350000 | 4663.5 | 0
2021050601 | 5 | 0.45802 | 68703 | 0.8695 | 0 | 0.29839 | 3729.875 | 0 | 0 | 64000 | 3729.875 | 0 | 973.125 | -3690.375 | 1350000 | 973.125 | 0
2021050602 | 5 | 0.44314 | 66471 | 0.83548 | 0 | 0.27898 | 3487.25 | 0 | 0 | 64000 | 2471 | 0 | 0 | -973.125 | 1350000 | 0 | 0
2021050603 | 5 | 0.43402 | 65103 | 0.87131 | 0 | 0.23991 | 2998.875 | 0 | 0 | 64000 | 1103 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050604 | 5 | 0.43212 | 64818 | 0.85635 | 0 | 0.202 | 2525 | 0 | 0 | 64000 | 818 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050605 | 5 | 0.44108 | 66162 | 0.79986 | 0 | 0.16484 | 2060.5 | 0 | 0 | 64000 | 2060.5 | 0 | 101.5 | 101.5 | 1350000 | 101.5 | 0
2021050606 | 5 | 0.46476 | 69714 | 0.73623 | 0 | 0.09862 | 1232.75 | 0 | 0 | 64000 | 1232.75 | 0 | 4481.25 | 4379.75 | 1350000 | 4481.25 | 0
2021050607 | 5 | 0.50157 | 75235.5 | 0.65513 | 0 | 0.09947 | 1243.375 | 0.01757 | 1405.6 | 64000 | 1243.375 | 1405.6 | 8586.525 | 4105.275 | 1350000 | 8586.525 | 0
2021050608 | 5 | 0.52759 | 79138.5 | 0.54413 | 0 | 0.12833 | 1604.125 | 0.15415 | 12332 | 64000 | 1604.125 | 12332 | 1202.375 | -7384.15 | 1350000 | 1202.375 | 0
2021050609 | 5 | 0.5359 | 80385 | 0.5095 | 0 | 0.14535 | 1816.875 | 0.30575 | 24460 | 64000 | 1816.875 | 14568.125 | 0 | -1202.375 | 1350000 | 0 | 0
2021050610 | 5 | 0.53457 | 80185.5 | 0.48348 | 0 | 0.1424 | 1780 | 0.38958 | 31166.4 | 64000 | 1780 | 14405.5 | 0 | 0 | 1350000 | 0 | 0
2021050611 | 5 | 0.53325 | 79987.5 | 0.42056 | 0 | 0.14277 | 1784.625 | 0.48568 | 38854.4 | 64000 | 1784.625 | 14202.875 | 0 | 0 | 1350000 | 0 | 0
2021050612 | 5 | 0.52916 | 79374 | 0.34343 | 0 | 0.10827 | 1353.375 | 0.5345 | 42760 | 64000 | 1353.375 | 14020.625 | 0 | 0 | 1350000 | 0 | 0
2021050613 | 5 | 0.52676 | 79014 | 0.34417 | 0 | 0.09484 | 1185.5 | 0.57043 | 45634.4 | 64000 | 1185.5 | 13828.5 | 0 | 0 | 1350000 | 0 | 0
2021050614 | 5 | 0.52618 | 78927 | 0.3841 | 0 | 0.0817 | 1021.25 | 0.59203 | 47362.4 | 64000 | 1021.25 | 13905.75 | 0 | 0 | 1350000 | 0 | 0
2021050615 | 5 | 0.52537 | 78805.5 | 0.39539 | 0 | 0.0714 | 892.5 | 0.61273 | 49018.4 | 64000 | 892.5 | 13913 | 0 | 0 | 1350000 | 0 | 0
2021050616 | 5 | 0.52488 | 78732 | 0.36233 | 0 | 0.07695 | 961.875 | 0.60395 | 48316 | 64000 | 961.875 | 13770.125 | 0 | 0 | 1350000 | 0 | 0
2021050617 | 5 | 0.5275 | 79125 | 0.29545 | 0 | 0.09136 | 1142 | 0.53209 | 42567.2 | 64000 | 1142 | 13983 | 0 | 0 | 1350000 | 0 | 0
2021050618 | 5 | 0.53067 | 79600.5 | 0.23276 | 0 | 0.1261 | 1576.25 | 0.37461 | 29968.8 | 64000 | 1576.25 | 14024.25 | 0 | 0 | 1350000 | 0 | 0
2021050619 | 5 | 0.53283 | 79924.5 | 0.20276 | 0 | 0.16329 | 2041.125 | 0.10516 | 8412.8 | 64000 | 2041.125 | 8412.8 | 5470.575 | 5470.575 | 1350000 | 5470.575 | 0
2021050620 | 5 | 0.5348 | 80220 | 0.19227 | 0 | 0.16253 | 2031.625 | 0.00144 | 115.2 | 64000 | 2031.625 | 115.2 | 14073.175 | 8602.6 | 1350000 | 14073.175 | 0
2021050621 | 5 | 0.54351 | 81526.5 | 0.1869 | 0 | 0.18933 | 2366.625 | 0 | 0 | 64000 | 2366.625 | 0 | 15159.875 | 1086.7 | 1350000 | 15159.875 | 0
2021050622 | 5 | 0.53439 | 80158.5 | 0.20543 | 0 | 0.22162 | 2770.25 | 0 | 0 | 64000 | 2770.25 | 0 | 13388.25 | -1771.625 | 1350000 | 13388.25 | 0
2021050623 | 5 | 0.50558 | 75837 | 0.18167 | 0 | 0.23796 | 2974.5 | 0 | 0 | 64000 | 2974.5 | 0 | 8862.5 | -4525.75 | 1350000 | 8862.5 | 0
2021050624 | 5 | 0.47368 | 71052 | 0.1528 | 0 | 0.25903 | 3237.875 | 0 | 0 | 64000 | 3237.875 | 0 | 3814.125 | -5048.375 | 1350000 | 3814.125 | 0
2021050701 | 6 | 0.45162 | 67743 | 0.14428 | 0 | 0.27496 | 3437 | 0 | 0 | 64000 | 3437 | 0 | 306 | -3508.125 | 1350000 | 306 | 0
2021050702 | 6 | 0.43795 | 65692.5 | 0.12897 | 0 | 0.27616 | 3452 | 0 | 0 | 64000 | 1692.5 | 0 | 0 | -306 | 1350000 | 0 | 0
2021050703 | 6 | 0.4319 | 64785 | 0.10071 | 0 | 0.24921 | 3115.125 | 0 | 0 | 64000 | 785 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050704 | 6 | 0.43155 | 64732.5 | 0.15382 | 0 | 0.23233 | 2904.125 | 0 | 0 | 64000 | 732.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050705 | 6 | 0.43842 | 65763 | 0.20313 | 0 | 0.16283 | 2035.375 | 0 | 0 | 64000 | 1763 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050706 | 6 | 0.46315 | 69472.5 | 0.21939 | 0 | 0.14438 | 1804.75 | 0 | 0 | 64000 | 1804.75 | 0 | 3667.75 | 3667.75 | 1350000 | 3667.75 | 0
2021050707 | 6 | 0.49877 | 74815.5 | 0.22992 | 0 | 0.08657 | 1082.125 | 0.01707 | 1365.6 | 64000 | 1082.125 | 1365.6 | 8367.775 | 4700.025 | 1350000 | 8367.775 | 0
2021050708 | 6 | 0.5261 | 78915 | 0.22286 | 0 | 0.08323 | 1040.375 | 0.205 | 16400 | 64000 | 1040.375 | 13874.625 | 0 | -8367.775 | 1350000 | 0 | 0
2021050709 | 6 | 0.53666 | 80499 | 0.19927 | 0 | 0.06117 | 764.625 | 0.44288 | 35430.4 | 64000 | 764.625 | 15734.375 | 0 | 0 | 1350000 | 0 | 0
2021050710 | 6 | 0.53769 | 80653.5 | 0.12437 | 0 | 0.04995 | 624.375 | 0.53337 | 42669.6 | 64000 | 624.375 | 16029.125 | 0 | 0 | 1350000 | 0 | 0
2021050711 | 6 | 0.53562 | 80343 | 0.07408 | 0 | 0.03773 | 471.625 | 0.56883 | 45506.4 | 64000 | 471.625 | 15871.375 | 0 | 0 | 1350000 | 0 | 0
2021050712 | 6 | 0.53412 | 80118 | 0.11073 | 0 | 0.03781 | 472.625 | 0.58577 | 46861.6 | 64000 | 472.625 | 15645.375 | 0 | 0 | 1350000 | 0 | 0
2021050713 | 6 | 0.53532 | 80298 | 0.15239 | 0 | 0.03899 | 487.375 | 0.62742 | 50193.6 | 64000 | 487.375 | 15810.625 | 0 | 0 | 1350000 | 0 | 0
2021050714 | 6 | 0.53327 | 79990.5 | 0.16031 | 0 | 0.02221 | 277.625 | 0.65849 | 52679.2 | 64000 | 277.625 | 15712.875 | 0 | 0 | 1350000 | 0 | 0
2021050715 | 6 | 0.52994 | 79491 | 0.22555 | 0 | 0.02087 | 260.875 | 0.68142 | 54513.6 | 64000 | 260.875 | 15230.125 | 0 | 0 | 1350000 | 0 | 0
2021050716 | 6 | 0.52613 | 78919.5 | 0.44564 | 0 | 0.02732 | 341.5 | 0.65622 | 52497.6 | 64000 | 341.5 | 14578 | 0 | 0 | 1350000 | 0 | 0
2021050717 | 6 | 0.52364 | 78546 | 0.56641 | 0 | 0.0567 | 708.75 | 0.59579 | 47663.2 | 64000 | 708.75 | 13837.25 | 0 | 0 | 1350000 | 0 | 0
2021050718 | 6 | 0.52348 | 78522 | 0.52576 | 0 | 0.09784 | 1223 | 0.40061 | 32048.8 | 64000 | 1223 | 13299 | 0 | 0 | 1350000 | 0 | 0
2021050719 | 6 | 0.52193 | 78289.5 | 0.45473 | 0 | 0.1177 | 1471.25 | 0.12313 | 9850.4 | 64000 | 1471.25 | 9850.4 | 2967.85 | 2967.85 | 1350000 | 2967.85 | 0
2021050720 | 6 | 0.52152 | 78228 | 0.39153 | 0 | 0.12477 | 1559.625 | 0.00451 | 360.8 | 64000 | 1559.625 | 360.8 | 12307.575 | 9339.725 | 1350000 | 12307.575 | 0
2021050721 | 6 | 0.52857 | 79285.5 | 0.34545 | 0 | 0.0988 | 1235 | 0 | 0 | 64000 | 1235 | 0 | 14050.5 | 1742.925 | 1350000 | 14050.5 | 0
2021050722 | 6 | 0.52321 | 78481.5 | 0.32612 | 0 | 0.09416 | 1177 | 0 | 0 | 64000 | 1177 | 0 | 13304.5 | -746 | 1350000 | 13304.5 | 0
2021050723 | 6 | 0.50192 | 75288 | 0.31719 | 0 | 0.10886 | 1360.75 | 0 | 0 | 64000 | 1360.75 | 0 | 9927.25 | -3377.25 | 1350000 | 9927.25 | 0
2021050724 | 6 | 0.47595 | 71392.5 | 0.26497 | 0 | 0.06798 | 849.75 | 0 | 0 | 64000 | 849.75 | 0 | 6542.75 | -3384.5 | 1350000 | 6542.75 | 0
2021050801 | 7 | 0.45432 | 68148 | 0.16732 | 0 | 0.0459 | 573.75 | 0 | 0 | 64000 | 573.75 | 0 | 3574.25 | -2968.5 | 1350000 | 3574.25 | 0
2021050802 | 7 | 0.44005 | 66007.5 | 0.1267 | 0 | 0.06648 | 831 | 0 | 0 | 64000 | 831 | 0 | 1176.5 | -2397.75 | 1350000 | 1176.5 | 0
2021050803 | 7 | 0.43274 | 64911 | 0.13326 | 0 | 0.06714 | 839.25 | 0 | 0 | 64000 | 839.25 | 0 | 71.75 | -1104.75 | 1350000 | 71.75 | 0
2021050804 | 7 | 0.42985 | 64477.5 | 0.20863 | 0 | 0.06728 | 841 | 0 | 0 | 64000 | 477.5 | 0 | 0 | -71.75 | 1350000 | 0 | 0
2021050805 | 7 | 0.43286 | 64929 | 0.25294 | 0 | 0.07654 | 956.75 | 0 | 0 | 64000 | 929 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050806 | 7 | 0.44468 | 66702 | 0.28228 | 0 | 0.05935 | 741.875 | 0 | 0 | 64000 | 741.875 | 0 | 1960.125 | 1960.125 | 1350000 | 1960.125 | 0
2021050807 | 7 | 0.45816 | 68724 | 0.34794 | 0 | 0.05452 | 681.5 | 0.01783 | 1426.4 | 64000 | 681.5 | 1426.4 | 2616.1 | 655.975 | 1350000 | 2616.1 | 0
2021050808 | 7 | 0.4741 | 71115 | 0.48663 | 0 | 0.05019 | 627.375 | 0.17151 | 13720.8 | 64000 | 627.375 | 6487.625 | 0 | -2616.1 | 1350000 | 0 | 0
2021050809 | 7 | 0.49059 | 73588.5 | 0.43087 | 0 | 0.08779 | 1097.375 | 0.42175 | 33740 | 64000 | 1097.375 | 8491.125 | 0 | 0 | 1350000 | 0 | 0
2021050810 | 7 | 0.49882 | 74823 | 0.51084 | 0 | 0.04767 | 595.875 | 0.51952 | 41561.6 | 64000 | 595.875 | 10227.125 | 0 | 0 | 1350000 | 0 | 0
2021050811 | 7 | 0.49725 | 74587.5 | 0.55585 | 0 | 0.02512 | 314 | 0.57961 | 46368.8 | 64000 | 314 | 10273.5 | 0 | 0 | 1350000 | 0 | 0
2021050812 | 7 | 0.49319 | 73978.5 | 0.58496 | 0 | 0.01072 | 134 | 0.61919 | 49535.2 | 64000 | 134 | 9844.5 | 0 | 0 | 1350000 | 0 | 0
2021050813 | 7 | 0.48792 | 73188 | 0.62871 | 0 | 0.00763 | 95.375 | 0.61413 | 49130.4 | 64000 | 95.375 | 9092.625 | 0 | 0 | 1350000 | 0 | 0
2021050814 | 7 | 0.48004 | 72006 | 0.63914 | 0 | 0.0054 | 67.5 | 0.64292 | 51433.6 | 64000 | 67.5 | 7938.5 | 0 | 0 | 1350000 | 0 | 0
2021050815 | 7 | 0.47145 | 70717.5 | 0.62663 | 0 | 0.00734 | 91.75 | 0.65993 | 52794.4 | 64000 | 91.75 | 6625.75 | 0 | 0 | 1350000 | 0 | 0
2021050816 | 7 | 0.46756 | 70134 | 0.67946 | 0 | 0.00391 | 48.875 | 0.64611 | 51688.8 | 64000 | 48.875 | 6085.125 | 0 | 0 | 1350000 | 0 | 0
2021050817 | 7 | 0.47005 | 70507.5 | 0.74495 | 0 | 0.01274 | 159.25 | 0.56451 | 45160.8 | 64000 | 159.25 | 6348.25 | 0 | 0 | 1350000 | 0 | 0
2021050818 | 7 | 0.47425 | 71137.5 | 0.76462 | 0 | 0.0435 | 543.75 | 0.38255 | 30604 | 64000 | 543.75 | 6593.75 | 0 | 0 | 1350000 | 0 | 0
2021050819 | 7 | 0.47971 | 71956.5 | 0.65381 | 0 | 0.04464 | 558 | 0.12112 | 9689.6 | 64000 | 558 | 7398.5 | 0 | 0 | 1350000 | 0 | 0
2021050820 | 7 | 0.48472 | 72708 | 0.588 | 0 | 0.03279 | 409.875 | 0.00741 | 592.8 | 64000 | 409.875 | 592.8 | 7705.325 | 7705.325 | 1350000 | 7705.325 | 0
2021050821 | 7 | 0.5002 | 75030 | 0.49568 | 0 | 0.03771 | 471.375 | 0 | 0 | 64000 | 471.375 | 0 | 10558.625 | 2853.3 | 1350000 | 10558.625 | 0
2021050822 | 7 | 0.50133 | 75199.5 | 0.49756 | 0 | 0.06101 | 762.625 | 0 | 0 | 64000 | 762.625 | 0 | 10436.875 | -121.75 | 1350000 | 10436.875 | 0
2021050823 | 7 | 0.48493 | 72739.5 | 0.45554 | 0 | 0.09775 | 1221.875 | 0 | 0 | 64000 | 1221.875 | 0 | 7517.625 | -2919.25 | 1350000 | 7517.625 | 0
2021050824 | 7 | 0.46379 | 69568.5 | 0.4297 | 0 | 0.1228 | 1535 | 0 | 0 | 64000 | 1535 | 0 | 4033.5 | -3484.125 | 1350000 | 4033.5 | 0
2021050901 | 1 | 0.44459 | 66688.5 | 0.43973 | 0 | 0.07753 | 969.125 | 0 | 0 | 64000 | 969.125 | 0 | 1719.375 | -2314.125 | 1350000 | 1719.375 | 0
2021050902 | 1 | 0.4325 | 64875 | 0.39217 | 0 | 0.09099 | 1137.375 | 0 | 0 | 64000 | 875 | 0 | 0 | -1719.375 | 1350000 | 0 | 0
2021050903 | 1 | 0.42542 | 63813 | 0.33033 | 0 | 0.10313 | 1289.125 | 0 | 0 | 63813 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050904 | 1 | 0.42287 | 63430.5 | 0.29256 | 0 | 0.07241 | 905.125 | 0 | 0 | 63430.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050905 | 1 | 0.42299 | 63448.5 | 0.31346 | 0 | 0.0849 | 1061.25 | 0 | 0 | 63448.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050906 | 1 | 0.42954 | 64431 | 0.27526 | 0 | 0.14822 | 1852.75 | 0 | 0 | 64000 | 431 | 0 | 0 | 0 | 1350000 | 0 | 0
2021050907 | 1 | 0.43843 | 65764.5 | 0.19889 | 0 | 0.08454 | 1056.75 | 0.01893 | 1514.4 | 64000 | 1056.75 | 707.75 | 0 | 0 | 1350000 | 0 | 0
2021050908 | 1 | 0.45082 | 67623 | 0.09223 | 0 | 0.06462 | 807.75 | 0.1703 | 13624 | 64000 | 807.75 | 2815.25 | 0 | 0 | 1350000 | 0 | 0
2021050909 | 1 | 0.46894 | 70341 | 0.0243 | 0 | 0.01871 | 233.875 | 0.3631 | 29048 | 64000 | 233.875 | 6107.125 | 0 | 0 | 1350000 | 0 | 0
2021050910 | 1 | 0.48234 | 72351 | 0.04869 | 0 | 0.0072 | 90 | 0.50864 | 40691.2 | 64000 | 90 | 8261 | 0 | 0 | 1350000 | 0 | 0
2021050911 | 1 | 0.48918 | 73377 | 0.20625 | 0 | 0.01168 | 146 | 0.56652 | 45321.6 | 64000 | 146 | 9231 | 0 | 0 | 1350000 | 0 | 0
2021050912 | 1 | 0.4889 | 73335 | 0.50743 | 0 | 0.01208 | 151 | 0.60343 | 48274.4 | 64000 | 151 | 9184 | 0 | 0 | 1350000 | 0 | 0
2021050913 | 1 | 0.48665 | 72997.5 | 0.64131 | 0 | 0.02493 | 311.625 | 0.64075 | 51260 | 64000 | 311.625 | 8685.875 | 0 | 0 | 1350000 | 0 | 0
2021050914 | 1 | 0.48324 | 72486 | 0.44557 | 0 | 0.01491 | 186.375 | 0.63977 | 51181.6 | 64000 | 186.375 | 8299.625 | 0 | 0 | 1350000 | 0 | 0
2021050915 | 1 | 0.48251 | 72376.5 | 0.56252 | 0 | 0.02205 | 275.625 | 0.64768 | 51814.4 | 64000 | 275.625 | 8100.875 | 0 | 0 | 1350000 | 0 | 0
2021050916 | 1 | 0.48218 | 72327 | 0.66246 | 0 | 0.05683 | 710.375 | 0.64148 | 51318.4 | 64000 | 710.375 | 7616.625 | 0 | 0 | 1350000 | 0 | 0
2021050917 | 1 | 0.48634 | 72951 | 0.68599 | 0 | 0.10965 | 1370.625 | 0.56879 | 45503.2 | 64000 | 1370.625 | 7580.375 | 0 | 0 | 1350000 | 0 | 0
2021050918 | 1 | 0.49534 | 74301 | 0.64892 | 0 | 0.16422 | 2052.75 | 0.37604 | 30083.2 | 64000 | 2052.75 | 8248.25 | 0 | 0 | 1350000 | 0 | 0
2021050919 | 1 | 0.50133 | 75199.5 | 0.64835 | 0 | 0.14071 | 1758.875 | 0.11233 | 8986.4 | 64000 | 1758.875 | 8986.4 | 454.225 | 454.225 | 1350000 | 454.225 | 0
2021050920 | 1 | 0.50811 | 76216.5 | 0.69969 | 0 | 0.09487 | 1185.875 | 0.00361 | 288.8 | 64000 | 1185.875 | 288.8 | 10741.825 | 10287.6 | 1350000 | 10741.825 | 0
2021050921 | 1 | 0.51977 | 77965.5 | 0.66785 | 0 | 0.07332 | 916.5 | 0 | 0 | 64000 | 916.5 | 0 | 13049 | 2307.175 | 1350000 | 13049 | 0
2021050922 | 1 | 0.51538 | 77307 | 0.67078 | 0 | 0.07436 | 929.5 | 0 | 0 | 64000 | 929.5 | 0 | 12377.5 | -671.5 | 1350000 | 12377.5 | 0
2021050923 | 1 | 0.49387 | 74080.5 | 0.56666 | 0 | 0.09234 | 1154.25 | 0 | 0 | 64000 | 1154.25 | 0 | 8926.25 | -3451.25 | 1350000 | 8926.25 | 0
2021050924 | 1 | 0.46916 | 70374 | 0.49914 | 0 | 0.10924 | 1365.5 | 0 | 0 | 64000 | 1365.5 | 0 | 5008.5 | -3917.75 | 1350000 | 5008.5 | 0
2021051001 | 2 | 0.45049 | 67573.5 | 0.62714 | 0 | 0.19 | 2375 | 0 | 0 | 64000 | 2375 | 0 | 1198.5 | -3810 | 1350000 | 1198.5 | 0
2021051002 | 2 | 0.43964 | 65946 | 0.69784 | 0 | 0.21507 | 2688.375 | 0 | 0 | 64000 | 1946 | 0 | 0 | -1198.5 | 1350000 | 0 | 0
2021051003 | 2 | 0.43305 | 64957.5 | 0.62274 | 0 | 0.2087 | 2608.75 | 0 | 0 | 64000 | 957.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051004 | 2 | 0.43324 | 64986 | 0.52958 | 0 | 0.18252 | 2281.5 | 0 | 0 | 64000 | 986 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051005 | 2 | 0.44296 | 66444 | 0.43015 | 0 | 0.1848 | 2310 | 0 | 0 | 64000 | 2310 | 0 | 134 | 134 | 1350000 | 134 | 0
2021051006 | 2 | 0.47057 | 70585.5 | 0.45807 | 0 | 0.15689 | 1961.125 | 0 | 0 | 64000 | 1961.125 | 0 | 4624.375 | 4490.375 | 1350000 | 4624.375 | 0
2021051007 | 2 | 0.50749 | 76123.5 | 0.43875 | 0 | 0.1712 | 2140 | 0.02546 | 2036.8 | 64000 | 2140 | 2036.8 | 7946.7 | 3322.325 | 1350000 | 7946.7 | 0
2021051008 | 2 | 0.53925 | 80887.5 | 0.34565 | 0 | 0.15998 | 1999.75 | 0.20556 | 16444.8 | 64000 | 1999.75 | 14887.75 | 0 | -7946.7 | 1350000 | 0 | 0
2021051009 | 2 | 0.55443 | 83164.5 | 0.28933 | 0 | 0.15893 | 1986.625 | 0.43681 | 34944.8 | 64000 | 1986.625 | 17177.875 | 0 | 0 | 1350000 | 0 | 0
2021051010 | 2 | 0.55971 | 83956.5 | 0.21155 | 0 | 0.14895 | 1861.875 | 0.54732 | 43785.6 | 64000 | 1861.875 | 18094.625 | 0 | 0 | 1350000 | 0 | 0
2021051011 | 2 | 0.55786 | 83679 | 0.17839 | 0 | 0.15083 | 1885.375 | 0.60622 | 48497.6 | 64000 | 1885.375 | 17793.625 | 0 | 0 | 1350000 | 0 | 0
2021051012 | 2 | 0.55266 | 82899 | 0.22458 | 0 | 0.10626 | 1328.25 | 0.6444 | 51552 | 64000 | 1328.25 | 17570.75 | 0 | 0 | 1350000 | 0 | 0
2021051013 | 2 | 0.54888 | 82332 | 0.31024 | 0 | 0.06473 | 809.125 | 0.67203 | 53762.4 | 64000 | 809.125 | 17522.875 | 0 | 0 | 1350000 | 0 | 0
2021051014 | 2 | 0.54364 | 81546 | 0.42064 | 0 | 0.03479 | 434.875 | 0.68353 | 54682.4 | 64000 | 434.875 | 17111.125 | 0 | 0 | 1350000 | 0 | 0
2021051015 | 2 | 0.53837 | 80755.5 | 0.37523 | 0 | 0.02357 | 294.625 | 0.6897 | 55176 | 64000 | 294.625 | 16460.875 | 0 | 0 | 1350000 | 0 | 0
2021051016 | 2 | 0.53073 | 79609.5 | 0.35592 | 0 | 0.03363 | 420.375 | 0.67779 | 54223.2 | 64000 | 420.375 | 15189.125 | 0 | 0 | 1350000 | 0 | 0
2021051017 | 2 | 0.52943 | 79414.5 | 0.42297 | 0 | 0.06839 | 854.875 | 0.6168 | 49344 | 64000 | 854.875 | 14559.625 | 0 | 0 | 1350000 | 0 | 0
2021051018 | 2 | 0.53275 | 79912.5 | 0.5353 | 0 | 0.14409 | 1801.125 | 0.42836 | 34268.8 | 64000 | 1801.125 | 14111.375 | 0 | 0 | 1350000 | 0 | 0
2021051019 | 2 | 0.53584 | 80376 | 0.5167 | 0 | 0.18127 | 2265.875 | 0.14117 | 11293.6 | 64000 | 2265.875 | 11293.6 | 2816.525 | 2816.525 | 1350000 | 2816.525 | 0
2021051020 | 2 | 0.53741 | 80611.5 | 0.43136 | 0 | 0.17481 | 2185.125 | 0.00726 | 580.8 | 64000 | 2185.125 | 580.8 | 13845.575 | 11029.05 | 1350000 | 13845.575 | 0
2021051021 | 2 | 0.54711 | 82066.5 | 0.44223 | 0 | 0.16722 | 2090.25 | 0 | 0 | 64000 | 2090.25 | 0 | 15976.25 | 2130.675 | 1350000 | 15976.25 | 0
2021051022 | 2 | 0.54019 | 81028.5 | 0.43055 | 0 | 0.17304 | 2163 | 0 | 0 | 64000 | 2163 | 0 | 14865.5 | -1110.75 | 1350000 | 14865.5 | 0
2021051023 | 2 | 0.51119 | 76678.5 | 0.36085 | 0 | 0.16415 | 2051.875 | 0 | 0 | 64000 | 2051.875 | 0 | 10626.625 | -4238.875 | 1350000 | 10626.625 | 0
2021051024 | 2 | 0.48011 | 72016.5 | 0.34807 | 0 | 0.15978 | 1997.25 | 0 | 0 | 64000 | 1997.25 | 0 | 6019.25 | -4607.375 | 1350000 | 6019.25 | 0
2021051101 | 3 | 0.45847 | 68770.5 | 0.26566 | 0 | 0.16165 | 2020.625 | 0 | 0 | 64000 | 2020.625 | 0 | 2749.875 | -3269.375 | 1350000 | 2749.875 | 0
2021051102 | 3 | 0.44479 | 66718.5 | 0.23906 | 0 | 0.13835 | 1729.375 | 0 | 0 | 64000 | 1729.375 | 0 | 989.125 | -1760.75 | 1350000 | 989.125 | 0
2021051103 | 3 | 0.43974 | 65961 | 0.21628 | 0 | 0.12134 | 1516.75 | 0 | 0 | 64000 | 1516.75 | 0 | 444.25 | -544.875 | 1350000 | 444.25 | 0
2021051104 | 3 | 0.43812 | 65718 | 0.23385 | 0 | 0.13232 | 1654 | 0 | 0 | 64000 | 1654 | 0 | 64 | -380.25 | 1350000 | 64 | 0
2021051105 | 3 | 0.44753 | 67129.5 | 0.26784 | 0 | 0.12537 | 1567.125 | 0 | 0 | 64000 | 1567.125 | 0 | 1562.375 | 1498.375 | 1350000 | 1562.375 | 0
2021051106 | 3 | 0.47411 | 71116.5 | 0.3297 | 0 | 0.11269 | 1408.625 | 0 | 0 | 64000 | 1408.625 | 0 | 5707.875 | 4145.5 | 1350000 | 5707.875 | 0
2021051107 | 3 | 0.51125 | 76687.5 | 0.35845 | 0 | 0.0894 | 1117.5 | 0.03727 | 2981.6 | 64000 | 1117.5 | 2981.6 | 8588.4 | 2880.525 | 1350000 | 8588.4 | 0
2021051108 | 3 | 0.53753 | 80629.5 | 0.26166 | 0 | 0.09548 | 1193.5 | 0.21869 | 17495.2 | 64000 | 1193.5 | 15436 | 0 | -8588.4 | 1350000 | 0 | 0
2021051109 | 3 | 0.54233 | 81349.5 | 0.21491 | 0 | 0.10264 | 1283 | 0.45056 | 36044.8 | 64000 | 1283 | 16066.5 | 0 | 0 | 1350000 | 0 | 0
2021051110 | 3 | 0.54016 | 81024 | 0.35511 | 0 | 0.14555 | 1819.375 | 0.56415 | 45132 | 64000 | 1819.375 | 15204.625 | 0 | 0 | 1350000 | 0 | 0
2021051111 | 3 | 0.53517 | 80275.5 | 0.4546 | 0 | 0.13863 | 1732.875 | 0.59827 | 47861.6 | 64000 | 1732.875 | 14542.625 | 0 | 0 | 1350000 | 0 | 0
2021051112 | 3 | 0.53282 | 79923 | 0.49961 | 0 | 0.13712 | 1714 | 0.61232 | 48985.6 | 64000 | 1714 | 14209 | 0 | 0 | 1350000 | 0 | 0
2021051113 | 3 | 0.53234 | 79851 | 0.57667 | 0 | 0.12016 | 1502 | 0.59067 | 47253.6 | 64000 | 1502 | 14349 | 0 | 0 | 1350000 | 0 | 0
2021051114 | 3 | 0.5335 | 80025 | 0.62962 | 0 | 0.12051 | 1506.375 | 0.63106 | 50484.8 | 64000 | 1506.375 | 14518.625 | 0 | 0 | 1350000 | 0 | 0
2021051115 | 3 | 0.53405 | 80107.5 | 0.67765 | 0 | 0.0789 | 986.25 | 0.65813 | 52650.4 | 64000 | 986.25 | 15121.25 | 0 | 0 | 1350000 | 0 | 0
2021051116 | 3 | 0.53032 | 79548 | 0.76185 | 0 | 0.07903 | 987.875 | 0.62557 | 50045.6 | 64000 | 987.875 | 14560.125 | 0 | 0 | 1350000 | 0 | 0
2021051117 | 3 | 0.53058 | 79587 | 0.77519 | 0 | 0.08252 | 1031.5 | 0.54349 | 43479.2 | 64000 | 1031.5 | 14555.5 | 0 | 0 | 1350000 | 0 | 0
2021051118 | 3 | 0.53399 | 80098.5 | 0.78634 | 0 | 0.09515 | 1189.375 | 0.33248 | 26598.4 | 64000 | 1189.375 | 14909.125 | 0 | 0 | 1350000 | 0 | 0
2021051119 | 3 | 0.53381 | 80071.5 | 0.82777 | 0 | 0.09022 | 1127.75 | 0.09216 | 7372.8 | 64000 | 1127.75 | 7372.8 | 7570.95 | 7570.95 | 1350000 | 7570.95 | 0
2021051120 | 3 | 0.53707 | 80560.5 | 0.80667 | 0 | 0.09415 | 1176.875 | 0.00176 | 140.8 | 64000 | 1176.875 | 140.8 | 15242.825 | 7671.875 | 1350000 | 15242.825 | 0
2021051121 | 3 | 0.5464 | 81960 | 0.75932 | 0 | 0.09313 | 1164.125 | 0 | 0 | 64000 | 1164.125 | 0 | 16795.875 | 1553.05 | 1350000 | 16795.875 | 0
2021051122 | 3 | 0.5411 | 81165 | 0.75169 | 0 | 0.08252 | 1031.5 | 0 | 0 | 64000 | 1031.5 | 0 | 16133.5 | -662.375 | 1350000 | 16133.5 | 0
2021051123 | 3 | 0.5127 | 76905 | 0.75666 | 0 | 0.08881 | 1110.125 | 0 | 0 | 64000 | 1110.125 | 0 | 11794.875 | -4338.625 | 1350000 | 11794.875 | 0
2021051124 | 3 | 0.48316 | 72474 | 0.79879 | 0 | 0.0917 | 1146.25 | 0 | 0 | 64000 | 1146.25 | 0 | 7327.75 | -4467.125 | 1350000 | 7327.75 | 0
2021051201 | 4 | 0.46114 | 69171 | 0.79209 | 0 | 0.08993 | 1124.125 | 0 | 0 | 64000 | 1124.125 | 0 | 4046.875 | -3280.875 | 1350000 | 4046.875 | 0
2021051202 | 4 | 0.4478 | 67170 | 0.81748 | 0 | 0.08527 | 1065.875 | 0 | 0 | 64000 | 1065.875 | 0 | 2104.125 | -1942.75 | 1350000 | 2104.125 | 0
2021051203 | 4 | 0.44329 | 66493.5 | 0.80559 | 0 | 0.08278 | 1034.75 | 0 | 0 | 64000 | 1034.75 | 0 | 1458.75 | -645.375 | 1350000 | 1458.75 | 0
2021051204 | 4 | 0.44225 | 66337.5 | 0.82491 | 0 | 0.07612 | 951.5 | 0 | 0 | 64000 | 951.5 | 0 | 1386 | -72.75 | 1350000 | 1386 | 0
2021051205 | 4 | 0.45243 | 67864.5 | 0.81171 | 0 | 0.0554 | 692.5 | 0 | 0 | 64000 | 692.5 | 0 | 3172 | 1786 | 1350000 | 3172 | 0
2021051206 | 4 | 0.47792 | 71688 | 0.76331 | 0 | 0.03902 | 487.75 | 0 | 0 | 64000 | 487.75 | 0 | 7200.25 | 4028.25 | 1350000 | 7200.25 | 0
2021051207 | 4 | 0.51487 | 77230.5 | 0.71761 | 0 | 0.03492 | 436.5 | 0.0179 | 1432 | 64000 | 436.5 | 1432 | 11362 | 4161.75 | 1350000 | 11362 | 0
2021051208 | 4 | 0.54082 | 81123 | 0.60543 | 0 | 0.03919 | 489.875 | 0.1285 | 10280 | 64000 | 489.875 | 10280 | 6353.125 | -5008.875 | 1350000 | 6353.125 | 0
2021051209 | 4 | 0.54698 | 82047 | 0.45893 | 0 | 0.02845 | 355.625 | 0.26112 | 20889.6 | 64000 | 355.625 | 17691.375 | 0 | -6353.125 | 1350000 | 0 | 0
2021051210 | 4 | 0.54462 | 81693 | 0.31188 | 0 | 0.01872 | 234 | 0.32018 | 25614.4 | 64000 | 234 | 17459 | 0 | 0 | 1350000 | 0 | 0
2021051211 | 4 | 0.54051 | 81076.5 | 0.2844 | 0 | 0.01227 | 153.375 | 0.42203 | 33762.4 | 64000 | 153.375 | 16923.125 | 0 | 0 | 1350000 | 0 | 0
2021051212 | 4 | 0.53791 | 80686.5 | 0.39201 | 0 | 0.00744 | 93 | 0.46749 | 37399.2 | 64000 | 93 | 16593.5 | 0 | 0 | 1350000 | 0 | 0
2021051213 | 4 | 0.53428 | 80142 | 0.45721 | 0 | 0.00528 | 66 | 0.51392 | 41113.6 | 64000 | 66 | 16076 | 0 | 0 | 1350000 | 0 | 0
2021051214 | 4 | 0.53217 | 79825.5 | 0.41302 | 0 | 0.00811 | 101.375 | 0.54516 | 43612.8 | 64000 | 101.375 | 15724.125 | 0 | 0 | 1350000 | 0 | 0
2021051215 | 4 | 0.52963 | 79444.5 | 0.43838 | 0 | 0.01013 | 126.625 | 0.56722 | 45377.6 | 64000 | 126.625 | 15317.875 | 0 | 0 | 1350000 | 0 | 0
2021051216 | 4 | 0.52659 | 78988.5 | 0.42517 | 0 | 0.0153 | 191.25 | 0.57306 | 45844.8 | 64000 | 191.25 | 14797.25 | 0 | 0 | 1350000 | 0 | 0
2021051217 | 4 | 0.52744 | 79116 | 0.4335 | 0 | 0.0279 | 348.75 | 0.51849 | 41479.2 | 64000 | 348.75 | 14767.25 | 0 | 0 | 1350000 | 0 | 0
2021051218 | 4 | 0.52989 | 79483.5 | 0.40222 | 0 | 0.06474 | 809.25 | 0.39121 | 31296.8 | 64000 | 809.25 | 14674.25 | 0 | 0 | 1350000 | 0 | 0
2021051219 | 4 | 0.53065 | 79597.5 | 0.38578 | 0 | 0.09417 | 1177.125 | 0.11869 | 9495.2 | 64000 | 1177.125 | 9495.2 | 4925.175 | 4925.175 | 1350000 | 4925.175 | 0
2021051220 | 4 | 0.53236 | 79854 | 0.35054 | 0 | 0.10378 | 1297.25 | 0.00311 | 248.8 | 64000 | 1297.25 | 248.8 | 14307.95 | 9382.775 | 1350000 | 14307.95 | 0
2021051221 | 4 | 0.54085 | 81127.5 | 0.33622 | 0 | 0.11721 | 1465.125 | 0 | 0 | 64000 | 1465.125 | 0 | 15662.375 | 1354.425 | 1350000 | 15662.375 | 0
2021051222 | 4 | 0.53749 | 80623.5 | 0.37076 | 0 | 0.10822 | 1352.75 | 0 | 0 | 64000 | 1352.75 | 0 | 15270.75 | -391.625 | 1350000 | 15270.75 | 0
2021051223 | 4 | 0.51078 | 76617 | 0.38142 | 0 | 0.09737 | 1217.125 | 0 | 0 | 64000 | 1217.125 | 0 | 11399.875 | -3870.875 | 1350000 | 11399.875 | 0
2021051224 | 4 | 0.4827 | 72405 | 0.42409 | 0 | 0.08489 | 1061.125 | 0 | 0 | 64000 | 1061.125 | 0 | 7343.875 | -4056 | 1350000 | 7343.875 | 0
2021051301 | 5 | 0.45895 | 68842.5 | 0.44537 | 0 | 0.07885 | 985.625 | 0 | 0 | 64000 | 985.625 | 0 | 3856.875 | -3487 | 1350000 | 3856.875 | 0
2021051302 | 5 | 0.44892 | 67338 | 0.44449 | 0 | 0.06824 | 853 | 0 | 0 | 64000 | 853 | 0 | 2485 | -1371.875 | 1350000 | 2485 | 0
2021051303 | 5 | 0.44423 | 66634.5 | 0.41336 | 0 | 0.06477 | 809.625 | 0 | 0 | 64000 | 809.625 | 0 | 1824.875 | -660.125 | 1350000 | 1824.875 | 0
2021051304 | 5 | 0.44503 | 66754.5 | 0.39754 | 0 | 0.04651 | 581.375 | 0 | 0 | 64000 | 581.375 | 0 | 2173.125 | 348.25 | 1350000 | 2173.125 | 0
2021051305 | 5 | 0.45726 | 68589 | 0.35406 | 0 | 0.03197 | 399.625 | 0 | 0 | 64000 | 399.625 | 0 | 4189.375 | 2016.25 | 1350000 | 4189.375 | 0
2021051306 | 5 | 0.48471 | 72706.5 | 0.30569 | 0 | 0.02584 | 323 | 0 | 0 | 64000 | 323 | 0 | 8383.5 | 4194.125 | 1350000 | 8383.5 | 0
2021051307 | 5 | 0.52171 | 78256.5 | 0.27367 | 0 | 0.025 | 312.5 | 0.03094 | 2475.2 | 64000 | 312.5 | 2475.2 | 11468.8 | 3085.3 | 1350000 | 11468.8 | 0
2021051308 | 5 | 0.5434 | 81510 | 0.19596 | 0 | 0.01932 | 241.5 | 0.24216 | 19372.8 | 64000 | 241.5 | 17268.5 | 0 | -11468.8 | 1350000 | 0 | 0
2021051309 | 5 | 0.5442 | 81630 | 0.08152 | 0 | 0.02251 | 281.375 | 0.40996 | 32796.8 | 64000 | 281.375 | 17348.625 | 0 | 0 | 1350000 | 0 | 0
2021051310 | 5 | 0.53799 | 80698.5 | 0.03367 | 0 | 0.04279 | 534.875 | 0.48634 | 38907.2 | 64000 | 534.875 | 16163.625 | 0 | 0 | 1350000 | 0 | 0
2021051311 | 5 | 0.53509 | 80263.5 | 0.09552 | 0 | 0.04218 | 527.25 | 0.47682 | 38145.6 | 64000 | 527.25 | 15736.25 | 0 | 0 | 1350000 | 0 | 0
2021051312 | 5 | 0.53218 | 79827 | 0.20397 | 0 | 0.05198 | 649.75 | 0.50385 | 40308 | 64000 | 649.75 | 15177.25 | 0 | 0 | 1350000 | 0 | 0
2021051313 | 5 | 0.53438 | 80157 | 0.20247 | 0 | 0.06076 | 759.5 | 0.53194 | 42555.2 | 64000 | 759.5 | 15397.5 | 0 | 0 | 1350000 | 0 | 0
2021051314 | 5 | 0.53403 | 80104.5 | 0.22675 | 0 | 0.07598 | 949.75 | 0.51468 | 41174.4 | 64000 | 949.75 | 15154.75 | 0 | 0 | 1350000 | 0 | 0
2021051315 | 5 | 0.53196 | 79794 | 0.18789 | 0 | 0.0715 | 893.75 | 0.5172 | 41376 | 64000 | 893.75 | 14900.25 | 0 | 0 | 1350000 | 0 | 0
2021051316 | 5 | 0.53298 | 79947 | 0.20622 | 0 | 0.03962 | 495.25 | 0.46448 | 37158.4 | 64000 | 495.25 | 15451.75 | 0 | 0 | 1350000 | 0 | 0
2021051317 | 5 | 0.53385 | 80077.5 | 0.1923 | 0 | 0.04252 | 531.5 | 0.37737 | 30189.6 | 64000 | 531.5 | 15546 | 0 | 0 | 1350000 | 0 | 0
2021051318 | 5 | 0.53769 | 80653.5 | 0.17334 | 0 | 0.08072 | 1009 | 0.2564 | 20512 | 64000 | 1009 | 15644.5 | 0 | 0 | 1350000 | 0 | 0
2021051319 | 5 | 0.53538 | 80307 | 0.13878 | 0 | 0.09136 | 1142 | 0.07 | 5600 | 64000 | 1142 | 5600 | 9565 | 9565 | 1350000 | 9565 | 0
2021051320 | 5 | 0.53569 | 80353.5 | 0.1114 | 0 | 0.10661 | 1332.625 | 0.00359 | 287.2 | 64000 | 1332.625 | 287.2 | 14733.675 | 5168.675 | 1350000 | 14733.675 | 0
2021051321 | 5 | 0.54217 | 81325.5 | 0.10142 | 0 | 0.12468 | 1558.5 | 0 | 0 | 64000 | 1558.5 | 0 | 15767 | 1033.325 | 1350000 | 15767 | 0
2021051322 | 5 | 0.53653 | 80479.5 | 0.14875 | 0 | 0.12625 | 1578.125 | 0 | 0 | 64000 | 1578.125 | 0 | 14901.375 | -865.625 | 1350000 | 14901.375 | 0
2021051323 | 5 | 0.50659 | 75988.5 | 0.18827 | 0 | 0.13993 | 1749.125 | 0 | 0 | 64000 | 1749.125 | 0 | 10239.375 | -4662 | 1350000 | 10239.375 | 0
2021051324 | 5 | 0.47439 | 71158.5 | 0.20133 | 0 | 0.15226 | 1903.25 | 0 | 0 | 64000 | 1903.25 | 0 | 5255.25 | -4984.125 | 1350000 | 5255.25 | 0
2021051401 | 6 | 0.45085 | 67627.5 | 0.24497 | 0 | 0.15006 | 1875.75 | 0 | 0 | 64000 | 1875.75 | 0 | 1751.75 | -3503.5 | 1350000 | 1751.75 | 0
2021051402 | 6 | 0.43797 | 65695.5 | 0.29592 | 0 | 0.12294 | 1536.75 | 0 | 0 | 64000 | 1536.75 | 0 | 158.75 | -1593 | 1350000 | 158.75 | 0
2021051403 | 6 | 0.43111 | 64666.5 | 0.26608 | 0 | 0.1003 | 1253.75 | 0 | 0 | 64000 | 666.5 | 0 | 0 | -158.75 | 1350000 | 0 | 0
2021051404 | 6 | 0.43174 | 64761 | 0.23126 | 0 | 0.09555 | 1194.375 | 0 | 0 | 64000 | 761 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051405 | 6 | 0.44264 | 66396 | 0.20183 | 0 | 0.04909 | 613.625 | 0 | 0 | 64000 | 613.625 | 0 | 1782.375 | 1782.375 | 1350000 | 1782.375 | 0
2021051406 | 6 | 0.46874 | 70311 | 0.19089 | 0 | 0.03696 | 462 | 0 | 0 | 64000 | 462 | 0 | 5849 | 4066.625 | 1350000 | 5849 | 0
2021051407 | 6 | 0.50404 | 75606 | 0.17043 | 0 | 0.04492 | 561.5 | 0.02653 | 2122.4 | 64000 | 561.5 | 2122.4 | 8922.1 | 3073.1 | 1350000 | 8922.1 | 0
2021051408 | 6 | 0.52694 | 79041 | 0.10165 | 0 | 0.04876 | 609.5 | 0.11554 | 9243.2 | 64000 | 609.5 | 9243.2 | 5188.3 | -3733.8 | 1350000 | 5188.3 | 0
2021051409 | 6 | 0.53459 | 80188.5 | 0.0391 | 0 | 0.0501 | 626.25 | 0.23235 | 18588 | 64000 | 626.25 | 15562.25 | 0 | -5188.3 | 1350000 | 0 | 0
2021051410 | 6 | 0.53283 | 79924.5 | 0.01396 | 0 | 0.05374 | 671.75 | 0.35227 | 28181.6 | 64000 | 671.75 | 15252.75 | 0 | 0 | 1350000 | 0 | 0
2021051411 | 6 | 0.53258 | 79887 | 0.01643 | 0 | 0.04362 | 545.25 | 0.42148 | 33718.4 | 64000 | 545.25 | 15341.75 | 0 | 0 | 1350000 | 0 | 0
2021051412 | 6 | 0.53435 | 80152.5 | 0.01913 | 0 | 0.03624 | 453 | 0.43153 | 34522.4 | 64000 | 453 | 15699.5 | 0 | 0 | 1350000 | 0 | 0
2021051413 | 6 | 0.53686 | 80529 | 0.02907 | 0 | 0.0175 | 218.75 | 0.38102 | 30481.6 | 64000 | 218.75 | 16310.25 | 0 | 0 | 1350000 | 0 | 0
2021051414 | 6 | 0.53775 | 80662.5 | 0.02501 | 0 | 0.01012 | 126.5 | 0.35589 | 28471.2 | 64000 | 126.5 | 16536 | 0 | 0 | 1350000 | 0 | 0
2021051415 | 6 | 0.53575 | 80362.5 | 0.04836 | 0 | 0.00446 | 55.75 | 0.32327 | 25861.6 | 64000 | 55.75 | 16306.75 | 0 | 0 | 1350000 | 0 | 0
2021051416 | 6 | 0.53145 | 79717.5 | 0.02397 | 0 | 0.00272 | 34 | 0.29789 | 23831.2 | 64000 | 34 | 15683.5 | 0 | 0 | 1350000 | 0 | 0
2021051417 | 6 | 0.53391 | 80086.5 | 0.02455 | 0 | 0.00347 | 43.375 | 0.21728 | 17382.4 | 64000 | 43.375 | 16043.125 | 0 | 0 | 1350000 | 0 | 0
2021051418 | 6 | 0.5348 | 80220 | 0.01077 | 0 | 0.00528 | 66 | 0.09417 | 7533.6 | 64000 | 66 | 7533.6 | 8620.4 | 8620.4 | 1350000 | 8620.4 | 0
2021051419 | 6 | 0.53036 | 79554 | 0.00025 | 0 | 0.00745 | 93.125 | 0.03774 | 3019.2 | 64000 | 93.125 | 3019.2 | 12441.675 | 3821.275 | 1350000 | 12441.675 | 0
2021051420 | 6 | 0.52527 | 78790.5 | 0.01123 | 0 | 0.00915 | 114.375 | 0.00181 | 144.8 | 64000 | 114.375 | 144.8 | 14531.325 | 2089.65 | 1350000 | 14531.325 | 0
2021051421 | 6 | 0.52636 | 78954 | 0.03988 | 0 | 0.01191 | 148.875 | 0 | 0 | 64000 | 148.875 | 0 | 14805.125 | 273.8 | 1350000 | 14805.125 | 0
2021051422 | 6 | 0.52237 | 78355.5 | 0.07795 | 0 | 0.0132 | 165 | 0 | 0 | 64000 | 165 | 0 | 14190.5 | -614.625 | 1350000 | 14190.5 | 0
2021051423 | 6 | 0.49704 | 74556 | 0.13256 | 0 | 0.01351 | 168.875 | 0 | 0 | 64000 | 168.875 | 0 | 10387.125 | -3803.375 | 1350000 | 10387.125 | 0
2021051424 | 6 | 0.4658 | 69870 | 0.16377 | 0 | 0.01744 | 218 | 0 | 0 | 64000 | 218 | 0 | 5652 | -4735.125 | 1350000 | 5652 | 0
2021051501 | 7 | 0.44192 | 66288 | 0.1968 | 0 | 0.01836 | 229.5 | 0 | 0 | 64000 | 229.5 | 0 | 2058.5 | -3593.5 | 1350000 | 2058.5 | 0
2021051502 | 7 | 0.42509 | 63763.5 | 0.21613 | 0 | 0.02059 | 257.375 | 0 | 0 | 63763.5 | 0 | 0 | 0 | -2058.5 | 1350000 | 0 | 0
2021051503 | 7 | 0.41694 | 62541 | 0.22148 | 0 | 0.01979 | 247.375 | 0 | 0 | 62541 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051504 | 7 | 0.41426 | 62139 | 0.18711 | 0 | 0.01814 | 226.75 | 0 | 0 | 62139 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051505 | 7 | 0.41758 | 62637 | 0.15593 | 0 | 0.02329 | 291.125 | 0 | 0 | 62637 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051506 | 7 | 0.42775 | 64162.5 | 0.15425 | 0 | 0.02578 | 322.25 | 0 | 0 | 64000 | 162.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051507 | 7 | 0.43912 | 65868 | 0.12912 | 0 | 0.01906 | 238.25 | 0.03315 | 2652 | 64000 | 238.25 | 1629.75 | 0 | 0 | 1350000 | 0 | 0
2021051508 | 7 | 0.45222 | 67833 | 0.04793 | 0 | 0.01755 | 219.375 | 0.20654 | 16523.2 | 64000 | 219.375 | 3613.625 | 0 | 0 | 1350000 | 0 | 0
2021051509 | 7 | 0.46474 | 69711 | 0.00177 | 0 | 0.02709 | 338.625 | 0.36412 | 29129.6 | 64000 | 338.625 | 5372.375 | 0 | 0 | 1350000 | 0 | 0
2021051510 | 7 | 0.47297 | 70945.5 | 0.00107 | 0 | 0.02978 | 372.25 | 0.53602 | 42881.6 | 64000 | 372.25 | 6573.25 | 0 | 0 | 1350000 | 0 | 0
2021051511 | 7 | 0.47753 | 71629.5 | 0.00476 | 0 | 0.04636 | 579.5 | 0.59297 | 47437.6 | 64000 | 579.5 | 7050 | 0 | 0 | 1350000 | 0 | 0
2021051512 | 7 | 0.47991 | 71986.5 | 0.01448 | 0 | 0.04667 | 583.375 | 0.59965 | 47972 | 64000 | 583.375 | 7403.125 | 0 | 0 | 1350000 | 0 | 0
2021051513 | 7 | 0.48263 | 72394.5 | 0.04672 | 0 | 0.03915 | 489.375 | 0.59148 | 47318.4 | 64000 | 489.375 | 7905.125 | 0 | 0 | 1350000 | 0 | 0
2021051514 | 7 | 0.48588 | 72882 | 0.07119 | 0 | 0.04112 | 514 | 0.62895 | 50316 | 64000 | 514 | 8368 | 0 | 0 | 1350000 | 0 | 0
2021051515 | 7 | 0.48513 | 72769.5 | 0.07328 | 0 | 0.04309 | 538.625 | 0.63994 | 51195.2 | 64000 | 538.625 | 8230.875 | 0 | 0 | 1350000 | 0 | 0
2021051516 | 7 | 0.48637 | 72955.5 | 0.04701 | 0 | 0.04947 | 618.375 | 0.6555 | 52440 | 64000 | 618.375 | 8337.125 | 0 | 0 | 1350000 | 0 | 0
2021051517 | 7 | 0.49436 | 74154 | 0.01561 | 0 | 0.0587 | 733.75 | 0.60131 | 48104.8 | 64000 | 733.75 | 9420.25 | 0 | 0 | 1350000 | 0 | 0
2021051518 | 7 | 0.50107 | 75160.5 | 0.01177 | 0 | 0.06807 | 850.875 | 0.38315 | 30652 | 64000 | 850.875 | 10309.625 | 0 | 0 | 1350000 | 0 | 0
2021051519 | 7 | 0.50405 | 75607.5 | 0.01263 | 0 | 0.07365 | 920.625 | 0.10805 | 8644 | 64000 | 920.625 | 8644 | 2042.875 | 2042.875 | 1350000 | 2042.875 | 0
2021051520 | 7 | 0.50001 | 75001.5 | 0.00063 | 0 | 0.07251 | 906.375 | 0.00384 | 307.2 | 64000 | 906.375 | 307.2 | 9787.925 | 7745.05 | 1350000 | 9787.925 | 0
2021051521 | 7 | 0.50427 | 75640.5 | 0.0029 | 0 | 0.08022 | 1002.75 | 0 | 0 | 64000 | 1002.75 | 0 | 10637.75 | 849.825 | 1350000 | 10637.75 | 0
2021051522 | 7 | 0.50066 | 75099 | 0.02667 | 0 | 0.08375 | 1046.875 | 0 | 0 | 64000 | 1046.875 | 0 | 10052.125 | -585.625 | 1350000 | 10052.125 | 0
2021051523 | 7 | 0.47743 | 71614.5 | 0.04007 | 0 | 0.08927 | 1115.875 | 0 | 0 | 64000 | 1115.875 | 0 | 6498.625 | -3553.5 | 1350000 | 6498.625 | 0
2021051524 | 7 | 0.44963 | 67444.5 | 0.06632 | 0 | 0.09777 | 1222.125 | 0 | 0 | 64000 | 1222.125 | 0 | 2222.375 | -4276.25 | 1350000 | 2222.375 | 0
2021051601 | 1 | 0.42566 | 63849 | 0.08632 | 0 | 0.1096 | 1370 | 0 | 0 | 63849 | 0 | 0 | 0 | -2222.375 | 1350000 | 0 | 0
2021051602 | 1 | 0.40938 | 61407 | 0.09168 | 0 | 0.11247 | 1405.875 | 0 | 0 | 61407 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051603 | 1 | 0.39981 | 59971.5 | 0.1091 | 0 | 0.11799 | 1474.875 | 0 | 0 | 59971.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051604 | 1 | 0.39466 | 59199 | 0.15304 | 0 | 0.11805 | 1475.625 | 0 | 0 | 59199 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051605 | 1 | 0.39447 | 59170.5 | 0.16388 | 0 | 0.12182 | 1522.75 | 0 | 0 | 59170.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051606 | 1 | 0.39858 | 59787 | 0.16801 | 0 | 0.11478 | 1434.75 | 0 | 0 | 59787 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051607 | 1 | 0.40347 | 60520.5 | 0.13454 | 0 | 0.13274 | 1659.25 | 0.04209 | 3367.2 | 60520.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051608 | 1 | 0.41524 | 62286 | 0.13342 | 0 | 0.11151 | 1393.875 | 0.23578 | 18862.4 | 62286 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051609 | 1 | 0.43382 | 65073 | 0.10678 | 0 | 0.11133 | 1391.625 | 0.3714 | 29712 | 64000 | 1073 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051610 | 1 | 0.45146 | 67719 | 0.07846 | 0 | 0.10273 | 1284.125 | 0.43405 | 34724 | 64000 | 1284.125 | 2434.875 | 0 | 0 | 1350000 | 0 | 0
2021051611 | 1 | 0.45965 | 68947.5 | 0.0889 | 0 | 0.0942 | 1177.5 | 0.42006 | 33604.8 | 64000 | 1177.5 | 3770 | 0 | 0 | 1350000 | 0 | 0
2021051612 | 1 | 0.4662 | 69930 | 0.13053 | 0 | 0.08605 | 1075.625 | 0.45825 | 36660 | 64000 | 1075.625 | 4854.375 | 0 | 0 | 1350000 | 0 | 0
2021051613 | 1 | 0.47217 | 70825.5 | 0.14402 | 0 | 0.07373 | 921.625 | 0.46185 | 36948 | 64000 | 921.625 | 5903.875 | 0 | 0 | 1350000 | 0 | 0
2021051614 | 1 | 0.47656 | 71484 | 0.16586 | 0 | 0.07458 | 932.25 | 0.50462 | 40369.6 | 64000 | 932.25 | 6551.75 | 0 | 0 | 1350000 | 0 | 0
2021051615 | 1 | 0.47911 | 71866.5 | 0.16935 | 0 | 0.07365 | 920.625 | 0.47775 | 38220 | 64000 | 920.625 | 6945.875 | 0 | 0 | 1350000 | 0 | 0
2021051616 | 1 | 0.48325 | 72487.5 | 0.12279 | 0 | 0.08145 | 1018.125 | 0.40846 | 32676.8 | 64000 | 1018.125 | 7469.375 | 0 | 0 | 1350000 | 0 | 0
2021051617 | 1 | 0.49245 | 73867.5 | 0.10205 | 0 | 0.08092 | 1011.5 | 0.31611 | 25288.8 | 64000 | 1011.5 | 8856 | 0 | 0 | 1350000 | 0 | 0
2021051618 | 1 | 0.50126 | 75189 | 0.07515 | 0 | 0.08736 | 1092 | 0.2393 | 19144 | 64000 | 1092 | 10097 | 0 | 0 | 1350000 | 0 | 0
2021051619 | 1 | 0.50424 | 75636 | 0.09508 | 0 | 0.10642 | 1330.25 | 0.0935 | 7480 | 64000 | 1330.25 | 7480 | 2825.75 | 2825.75 | 1350000 | 2825.75 | 0
2021051620 | 1 | 0.50508 | 75762 | 0.09111 | 0 | 0.10497 | 1312.125 | 0.0054 | 432 | 64000 | 1312.125 | 432 | 10017.875 | 7192.125 | 1350000 | 10017.875 | 0
2021051621 | 1 | 0.51348 | 77022 | 0.0968 | 0 | 0.09665 | 1208.125 | 0 | 0 | 64000 | 1208.125 | 0 | 11813.875 | 1796 | 1350000 | 11813.875 | 0
2021051622 | 1 | 0.50791 | 76186.5 | 0.09519 | 0 | 0.08736 | 1092 | 0 | 0 | 64000 | 1092 | 0 | 11094.5 | -719.375 | 1350000 | 11094.5 | 0
2021051623 | 1 | 0.48376 | 72564 | 0.13317 | 0 | 0.09075 | 1134.375 | 0 | 0 | 64000 | 1134.375 | 0 | 7429.625 | -3664.875 | 1350000 | 7429.625 | 0
2021051624 | 1 | 0.45469 | 68203.5 | 0.22828 | 0 | 0.09021 | 1127.625 | 0 | 0 | 64000 | 1127.625 | 0 | 3075.875 | -4353.75 | 1350000 | 3075.875 | 0
2021051701 | 2 | 0.43184 | 64776 | 0.2133 | 0 | 0.09306 | 1163.25 | 0 | 0 | 64000 | 776 | 0 | 0 | -3075.875 | 1350000 | 0 | 0
2021051702 | 2 | 0.41752 | 62628 | 0.14583 | 0 | 0.10321 | 1290.125 | 0 | 0 | 62628 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051703 | 2 | 0.41013 | 61519.5 | 0.10107 | 0 | 0.10744 | 1343 | 0 | 0 | 61519.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051704 | 2 | 0.41005 | 61507.5 | 0.06191 | 0 | 0.09002 | 1125.25 | 0 | 0 | 61507.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051705 | 2 | 0.41876 | 62814 | 0.01702 | 0 | 0.06432 | 804 | 0 | 0 | 62814 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051706 | 2 | 0.44218 | 66327 | 0.01825 | 0 | 0.05467 | 683.375 | 0 | 0 | 64000 | 683.375 | 0 | 1643.625 | 1643.625 | 1350000 | 1643.625 | 0
2021051707 | 2 | 0.47773 | 71659.5 | 0.02231 | 0 | 0.04766 | 595.75 | 0.01719 | 1375.2 | 64000 | 595.75 | 1375.2 | 5688.55 | 4044.925 | 1350000 | 5688.55 | 0
2021051708 | 2 | 0.50832 | 76248 | 0.00879 | 0 | 0.04539 | 567.375 | 0.08911 | 7128.8 | 64000 | 567.375 | 7128.8 | 4551.825 | -1136.725 | 1350000 | 4551.825 | 0
2021051709 | 2 | 0.52479 | 78718.5 | 0.00089 | 0 | 0.03903 | 487.875 | 0.18735 | 14988 | 64000 | 487.875 | 14230.625 | 0 | -4551.825 | 1350000 | 0 | 0
2021051710 | 2 | 0.53386 | 80079 | 0.00169 | 0 | 0.03182 | 397.75 | 0.24835 | 19868 | 64000 | 397.75 | 15681.25 | 0 | 0 | 1350000 | 0 | 0
2021051711 | 2 | 0.54182 | 81273 | 0.02842 | 0 | 0.0324 | 405 | 0.3552 | 28416 | 64000 | 405 | 16868 | 0 | 0 | 1350000 | 0 | 0
2021051712 | 2 | 0.54864 | 82296 | 0.05576 | 0 | 0.02828 | 353.5 | 0.46317 | 37053.6 | 64000 | 353.5 | 17942.5 | 0 | 0 | 1350000 | 0 | 0
2021051713 | 2 | 0.55632 | 83448 | 0.06776 | 0 | 0.03063 | 382.875 | 0.49204 | 39363.2 | 64000 | 382.875 | 19065.125 | 0 | 0 | 1350000 | 0 | 0
2021051714 | 2 | 0.56117 | 84175.5 | 0.07508 | 0 | 0.02849 | 356.125 | 0.50596 | 40476.8 | 64000 | 356.125 | 19819.375 | 0 | 0 | 1350000 | 0 | 0
2021051715 | 2 | 0.56402 | 84603 | 0.06666 | 0 | 0.02034 | 254.25 | 0.47708 | 38166.4 | 64000 | 254.25 | 20348.75 | 0 | 0 | 1350000 | 0 | 0
2021051716 | 2 | 0.56483 | 84724.5 | 0.04597 | 0 | 0.01862 | 232.75 | 0.44742 | 35793.6 | 64000 | 232.75 | 20491.75 | 0 | 0 | 1350000 | 0 | 0
2021051717 | 2 | 0.56989 | 85483.5 | 0.03389 | 0 | 0.02051 | 256.375 | 0.39833 | 31866.4 | 64000 | 256.375 | 21227.125 | 0 | 0 | 1350000 | 0 | 0
2021051718 | 2 | 0.5729 | 85935 | 0.0355 | 0 | 0.02626 | 328.25 | 0.28956 | 23164.8 | 64000 | 328.25 | 21606.75 | 0 | 0 | 1350000 | 0 | 0
2021051719 | 2 | 0.57162 | 85743 | 0.05895 | 0 | 0.02861 | 357.625 | 0.09741 | 7792.8 | 64000 | 357.625 | 7792.8 | 13592.575 | 13592.575 | 1350000 | 13592.575 | 0
2021051720 | 2 | 0.56468 | 84702 | 0.10681 | 0 | 0.03016 | 377 | 0.00434 | 347.2 | 64000 | 377 | 347.2 | 19977.8 | 6385.225 | 1350000 | 19977.8 | 0
2021051721 | 2 | 0.56584 | 84876 | 0.20594 | 0 | 0.03364 | 420.5 | 0 | 0 | 64000 | 420.5 | 0 | 20455.5 | 477.7 | 1350000 | 20455.5 | 0
2021051722 | 2 | 0.5549 | 83235 | 0.27313 | 0 | 0.04712 | 589 | 0 | 0 | 64000 | 589 | 0 | 18646 | -1809.5 | 1350000 | 18646 | 0
2021051723 | 2 | 0.51931 | 77896.5 | 0.33346 | 0 | 0.06594 | 824.25 | 0 | 0 | 64000 | 824.25 | 0 | 13072.25 | -5573.75 | 1350000 | 13072.25 | 0
2021051724 | 2 | 0.48223 | 72334.5 | 0.37539 | 0 | 0.08125 | 1015.625 | 0 | 0 | 64000 | 1015.625 | 0 | 7318.875 | -5753.375 | 1350000 | 7318.875 | 0
2021051801 | 3 | 0.45406 | 68109 | 0.36486 | 0 | 0.09457 | 1182.125 | 0 | 0 | 64000 | 1182.125 | 0 | 2926.875 | -4392 | 1350000 | 2926.875 | 0
2021051802 | 3 | 0.43618 | 65427 | 0.3286 | 0 | 0.10419 | 1302.375 | 0 | 0 | 64000 | 1302.375 | 0 | 124.625 | -2802.25 | 1350000 | 124.625 | 0
2021051803 | 3 | 0.42624 | 63936 | 0.29316 | 0 | 0.09499 | 1187.375 | 0 | 0 | 63936 | 0 | 0 | 0 | -124.625 | 1350000 | 0 | 0
2021051804 | 3 | 0.42237 | 63355.5 | 0.27418 | 0 | 0.07385 | 923.125 | 0 | 0 | 63355.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051805 | 3 | 0.42874 | 64311 | 0.22612 | 0 | 0.05454 | 681.75 | 0 | 0 | 64000 | 311 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051806 | 3 | 0.45019 | 67528.5 | 0.20431 | 0 | 0.04177 | 522.125 | 0 | 0 | 64000 | 522.125 | 0 | 3006.375 | 3006.375 | 1350000 | 3006.375 | 0
2021051807 | 3 | 0.48266 | 72399 | 0.17264 | 0 | 0.03816 | 477 | 0.02034 | 1627.2 | 64000 | 477 | 1627.2 | 6294.8 | 3288.425 | 1350000 | 6294.8 | 0
2021051808 | 3 | 0.51205 | 76807.5 | 0.12268 | 0 | 0.0281 | 351.25 | 0.11522 | 9217.6 | 64000 | 351.25 | 9217.6 | 3238.65 | -3056.15 | 1350000 | 3238.65 | 0
2021051809 | 3 | 0.52885 | 79327.5 | 0.05668 | 0 | 0.02187 | 273.375 | 0.26742 | 21393.6 | 64000 | 273.375 | 15054.125 | 0 | -3238.65 | 1350000 | 0 | 0
2021051810 | 3 | 0.53889 | 80833.5 | 0.02191 | 0 | 0.03665 | 458.125 | 0.35675 | 28540 | 64000 | 458.125 | 16375.375 | 0 | 0 | 1350000 | 0 | 0
2021051811 | 3 | 0.54844 | 82266 | 0.01681 | 0 | 0.02782 | 347.75 | 0.40892 | 32713.6 | 64000 | 347.75 | 17918.25 | 0 | 0 | 1350000 | 0 | 0
2021051812 | 3 | 0.56089 | 84133.5 | 0.02776 | 0 | 0.02811 | 351.375 | 0.52402 | 41921.6 | 64000 | 351.375 | 19782.125 | 0 | 0 | 1350000 | 0 | 0
2021051813 | 3 | 0.57174 | 85761 | 0.03335 | 0 | 0.03149 | 393.625 | 0.49998 | 39998.4 | 64000 | 393.625 | 21367.375 | 0 | 0 | 1350000 | 0 | 0
2021051814 | 3 | 0.5831 | 87465 | 0.03997 | 0 | 0.03573 | 446.625 | 0.46304 | 37043.2 | 64000 | 446.625 | 23018.375 | 0 | 0 | 1350000 | 0 | 0
2021051815 | 3 | 0.59241 | 88861.5 | 0.03652 | 0 | 0.03151 | 393.875 | 0.40377 | 32301.6 | 64000 | 393.875 | 24467.625 | 0 | 0 | 1350000 | 0 | 0
2021051816 | 3 | 0.602 | 90300 | 0.04294 | 0 | 0.02508 | 313.5 | 0.35414 | 28331.2 | 64000 | 313.5 | 25986.5 | 0 | 0 | 1350000 | 0 | 0
2021051817 | 3 | 0.61438 | 92157 | 0.03875 | 0 | 0.04305 | 538.125 | 0.25784 | 20627.2 | 64000 | 538.125 | 20627.2 | 6991.675 | 6991.675 | 1350000 | 6991.675 | 0
2021051818 | 3 | 0.62279 | 93418.5 | 0.03731 | 0 | 0.08912 | 1114 | 0.16323 | 13058.4 | 64000 | 1114 | 13058.4 | 15246.1 | 8254.425 | 1350000 | 15246.1 | 0
2021051819 | 3 | 0.6212 | 93180 | 0.04956 | 0 | 0.1214 | 1517.5 | 0.06682 | 5345.6 | 64000 | 1517.5 | 5345.6 | 22316.9 | 7070.8 | 1350000 | 22316.9 | 0
2021051820 | 3 | 0.6104 | 91560 | 0.06043 | 0 | 0.12651 | 1581.375 | 0.00335 | 268 | 64000 | 1581.375 | 268 | 25710.625 | 3393.725 | 1349755.625 | 25710.625 | 0
2021051821 | 3 | 0.60463 | 90694.5 | 0.10772 | 0 | 0.10743 | 1342.875 | 0 | 0 | 64000 | 1342.875 | 0 | 25351.625 | -359 | 1349870.25 | 25351.625 | 0
2021051822 | 3 | 0.5906 | 88590 | 0.18814 | 0 | 0.10003 | 1250.375 | 0 | 0 | 64000 | 1250.375 | 0 | 23339.625 | -2012 | 1350000 | 23339.625 | 0
2021051823 | 3 | 0.54999 | 82498.5 | 0.24413 | 0 | 0.1223 | 1528.75 | 0 | 0 | 64000 | 1528.75 | 0 | 16969.75 | -6369.875 | 1350000 | 16969.75 | 0
2021051824 | 3 | 0.50735 | 76102.5 | 0.21231 | 0 | 0.14793 | 1849.125 | 0 | 0 | 64000 | 1849.125 | 0 | 10253.375 | -6716.375 | 1350000 | 10253.375 | 0
2021051901 | 4 | 0.47337 | 71005.5 | 0.16333 | 0 | 0.17917 | 2239.625 | 0 | 0 | 64000 | 2239.625 | 0 | 4765.875 | -5487.5 | 1350000 | 4765.875 | 0
2021051902 | 4 | 0.45213 | 67819.5 | 0.12624 | 0 | 0.18413 | 2301.625 | 0 | 0 | 64000 | 2301.625 | 0 | 1517.875 | -3248 | 1350000 | 1517.875 | 0
2021051903 | 4 | 0.43825 | 65737.5 | 0.07092 | 0 | 0.17723 | 2215.375 | 0 | 0 | 64000 | 1737.5 | 0 | 0 | -1517.875 | 1350000 | 0 | 0
2021051904 | 4 | 0.4329 | 64935 | 0.06499 | 0 | 0.15567 | 1945.875 | 0 | 0 | 64000 | 935 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051905 | 4 | 0.43665 | 65497.5 | 0.06026 | 0 | 0.12919 | 1614.875 | 0 | 0 | 64000 | 1497.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021051906 | 4 | 0.45549 | 68323.5 | 0.04827 | 0 | 0.10754 | 1344.25 | 0 | 0 | 64000 | 1344.25 | 0 | 2979.25 | 2979.25 | 1350000 | 2979.25 | 0
2021051907 | 4 | 0.48742 | 73113 | 0.05215 | 0 | 0.08961 | 1120.125 | 0.0177 | 1416 | 64000 | 1120.125 | 1416 | 6576.875 | 3597.625 | 1350000 | 6576.875 | 0
2021051908 | 4 | 0.5206 | 78090 | 0.03094 | 0 | 0.1046 | 1307.5 | 0.0864 | 6912 | 64000 | 1307.5 | 6912 | 5870.5 | -706.375 | 1350000 | 5870.5 | 0
2021051909 | 4 | 0.54416 | 81624 | 0.0145 | 0 | 0.10587 | 1323.375 | 0.16968 | 13574.4 | 64000 | 1323.375 | 13574.4 | 2726.225 | -3144.275 | 1350000 | 2726.225 | 0
2021051910 | 4 | 0.56233 | 84349.5 | 0.0119 | 0 | 0.10647 | 1330.875 | 0.26144 | 20915.2 | 64000 | 1330.875 | 19018.625 | 0 | -2726.225 | 1350000 | 0 | 0
2021051911 | 4 | 0.58218 | 87327 | 0.01471 | 0 | 0.11201 | 1400.125 | 0.37425 | 29940 | 64000 | 1400.125 | 21926.875 | 0 | 0 | 1350000 | 0 | 0
2021051912 | 4 | 0.60185 | 90277.5 | 0.02851 | 0 | 0.13285 | 1660.625 | 0.45964 | 36771.2 | 64000 | 1660.625 | 24616.875 | 0 | 0 | 1350000 | 0 | 0
2021051913 | 4 | 0.62233 | 93349.5 | 0.02235 | 0 | 0.16182 | 2022.75 | 0.50037 | 40029.6 | 64000 | 2022.75 | 27326.75 | 0 | 0 | 1350000 | 0 | 0
2021051914 | 4 | 0.64265 | 96397.5 | 0.01717 | 0 | 0.19785 | 2473.125 | 0.492 | 39360 | 64000 | 2473.125 | 29924.375 | 0 | 0 | 1350000 | 0 | 0
2021051915 | 4 | 0.66 | 99000 | 0.01121 | 0 | 0.19266 | 2408.25 | 0.49351 | 39480.8 | 64000 | 2408.25 | 32591.75 | 0 | 0 | 1350000 | 0 | 0
2021051916 | 4 | 0.67739 | 101608.5 | 0.01581 | 0 | 0.13131 | 1641.375 | 0.47037 | 37629.6 | 64000 | 1641.375 | 35967.125 | 0 | 0 | 1350000 | 0 | 0
2021051917 | 4 | 0.69333 | 103999.5 | 0.01402 | 0 | 0.12872 | 1609 | 0.40116 | 32092.8 | 64000 | 1609 | 32092.8 | 6297.7 | 6297.7 | 1350000 | 6297.7 | 0
2021051918 | 4 | 0.7048 | 105720 | 0.00964 | 0 | 0.19061 | 2382.625 | 0.28083 | 22466.4 | 64000 | 2382.625 | 22466.4 | 16870.975 | 10573.275 | 1350000 | 16870.975 | 0
2021051919 | 4 | 0.70042 | 105063 | 0.01844 | 0 | 0.21297 | 2662.125 | 0.08961 | 7168.8 | 64000 | 2662.125 | 7168.8 | 31232.075 | 14361.1 | 1344234.175 | 31232.075 | 0
2021051920 | 4 | 0.68435 | 102652.5 | 0.0447 | 0 | 0.17599 | 2199.875 | 0.00471 | 376.8 | 64000 | 2199.875 | 376.8 | 36075.825 | 4843.75 | 1333624.6 | 36075.825 | 0
2021051921 | 4 | 0.66826 | 100239 | 0.09709 | 0 | 0.16893 | 2111.625 | 0 | 0 | 64000 | 2111.625 | 0 | 34127.375 | -1948.45 | 1324963.475 | 34127.375 | 0
2021051922 | 4 | 0.64745 | 97117.5 | 0.15948 | 0 | 0.19642 | 2455.25 | 0 | 0 | 64000 | 2455.25 | 0 | 30662.25 | -3465.125 | 1319767.475 | 30662.25 | 0
2021051923 | 4 | 0.5993 | 89895 | 0.21572 | 0 | 0.22577 | 2822.125 | 0 | 0 | 64000 | 2822.125 | 0 | 23072.875 | -7589.375 | 1322160.85 | 23072.875 | 0
2021051924 | 4 | 0.54761 | 82141.5 | 0.2251 | 0 | 0.23717 | 2964.625 | 0 | 0 | 64000 | 2964.625 | 0 | 15176.875 | -7896 | 1332450.225 | 15176.875 | 0
2021052001 | 5 | 0.5063 | 75945 | 0.17196 | 0 | 0.22066 | 2758.25 | 0 | 0 | 64000 | 2758.25 | 0 | 9186.75 | -5990.125 | 1348729.725 | 9186.75 | 0
2021052002 | 5 | 0.48017 | 72025.5 | 0.13837 | 0 | 0.21924 | 2740.5 | 0 | 0 | 64000 | 2740.5 | 0 | 5285 | -3901.75 | 1350000 | 5285 | 0
2021052003 | 5 | 0.46079 | 69118.5 | 0.10041 | 0 | 0.20629 | 2578.625 | 0 | 0 | 64000 | 2578.625 | 0 | 2539.875 | -2745.125 | 1350000 | 2539.875 | 0
2021052004 | 5 | 0.45115 | 67672.5 | 0.06265 | 0 | 0.15282 | 1910.25 | 0 | 0 | 64000 | 1910.25 | 0 | 1762.25 | -777.625 | 1350000 | 1762.25 | 0
2021052005 | 5 | 0.45196 | 67794 | 0.03731 | 0 | 0.12502 | 1562.75 | 0 | 0 | 64000 | 1562.75 | 0 | 2231.25 | 469 | 1350000 | 2231.25 | 0
2021052006 | 5 | 0.46895 | 70342.5 | 0.02331 | 0 | 0.09386 | 1173.25 | 0 | 0 | 64000 | 1173.25 | 0 | 5169.25 | 2938 | 1350000 | 5169.25 | 0
2021052007 | 5 | 0.4996 | 74940 | 0.01991 | 0 | 0.07542 | 942.75 | 0.02319 | 1855.2 | 64000 | 942.75 | 1855.2 | 8142.05 | 2972.8 | 1350000 | 8142.05 | 0
2021052008 | 5 | 0.53397 | 80095.5 | 0.00598 | 0 | 0.07143 | 892.875 | 0.11672 | 9337.6 | 64000 | 892.875 | 9337.6 | 5865.025 | -2277.025 | 1350000 | 5865.025 | 0
2021052009 | 5 | 0.55969 | 83953.5 | 0.00856 | 0 | 0.06682 | 835.25 | 0.19738 | 15790.4 | 64000 | 835.25 | 15790.4 | 3327.85 | -2537.175 | 1350000 | 3327.85 | 0
2021052010 | 5 | 0.58361 | 87541.5 | 0.0067 | 0 | 0.04931 | 616.375 | 0.34636 | 27708.8 | 64000 | 616.375 | 22925.125 | 0 | -3327.85 | 1350000 | 0 | 0
2021052011 | 5 | 0.60995 | 91492.5 | 0.00011 | 0 | 0.03388 | 423.5 | 0.5369 | 42952 | 64000 | 423.5 | 27069 | 0 | 0 | 1350000 | 0 | 0
2021052012 | 5 | 0.63567 | 95350.5 | 0.02673 | 0 | 0.02787 | 348.375 | 0.61077 | 48861.6 | 64000 | 348.375 | 31002.125 | 0 | 0 | 1350000 | 0 | 0
2021052013 | 5 | 0.66184 | 99276 | 0.12212 | 0 | 0.02729 | 341.125 | 0.6385 | 51080 | 64000 | 341.125 | 34934.875 | 0 | 0 | 1350000 | 0 | 0
2021052014 | 5 | 0.68783 | 103174.5 | 0.18186 | 0 | 0.03532 | 441.5 | 0.67727 | 54181.6 | 64000 | 441.5 | 38733 | 0 | 0 | 1350000 | 0 | 0
2021052015 | 5 | 0.70647 | 105970.5 | 0.17854 | 0 | 0.04192 | 524 | 0.67889 | 54311.2 | 64000 | 524 | 41446.5 | 0 | 0 | 1350000 | 0 | 0
2021052016 | 5 | 0.72177 | 108265.5 | 0.15099 | 0 | 0.04344 | 543 | 0.65055 | 52044 | 64000 | 543 | 43722.5 | 0 | 0 | 1350000 | 0 | 0
2021052017 | 5 | 0.73493 | 110239.5 | 0.16379 | 0 | 0.06853 | 856.625 | 0.60209 | 48167.2 | 64000 | 856.625 | 45382.875 | 0 | 0 | 1350000 | 0 | 0
2021052018 | 5 | 0.73877 | 110815.5 | 0.19187 | 0 | 0.10965 | 1370.625 | 0.43053 | 34442.4 | 64000 | 1370.625 | 34442.4 | 11002.475 | 11002.475 | 1350000 | 11002.475 | 0
2021052019 | 5 | 0.72605 | 108907.5 | 0.23749 | 0 | 0.13797 | 1724.625 | 0.15716 | 12572.8 | 64000 | 1724.625 | 12572.8 | 30610.075 | 19607.6 | 1344856.175 | 30610.075 | 0
2021052020 | 5 | 0.69892 | 104838 | 0.29811 | 0 | 0.12042 | 1505.25 | 0.01125 | 900 | 64000 | 1505.25 | 900 | 38432.75 | 7822.675 | 1331889.675 | 38432.75 | 0
2021052021 | 5 | 0.67473 | 101209.5 | 0.42768 | 0 | 0.128 | 1600 | 0 | 0 | 64000 | 1600 | 0 | 35609.5 | -2823.25 | 1321746.425 | 35609.5 | 0
2021052022 | 5 | 0.65179 | 97768.5 | 0.5146 | 0 | 0.1263 | 1578.75 | 0 | 0 | 64000 | 1578.75 | 0 | 32189.75 | -3419.75 | 1315022.925 | 32189.75 | 0
2021052023 | 5 | 0.60437 | 90655.5 | 0.57578 | 0 | 0.13363 | 1670.375 | 0 | 0 | 64000 | 1670.375 | 0 | 24985.125 | -7204.625 | 1315504.05 | 24985.125 | 0
2021052024 | 5 | 0.55312 | 82968 | 0.6328 | 0 | 0.1301 | 1626.25 | 0 | 0 | 64000 | 1626.25 | 0 | 17341.75 | -7643.375 | 1323628.55 | 17341.75 | 0
2021052101 | 6 | 0.51013 | 76519.5 | 0.55761 | 0 | 0.13138 | 1642.25 | 0 | 0 | 64000 | 1642.25 | 0 | 10877.25 | -6464.5 | 1338217.55 | 10877.25 | 0
2021052102 | 6 | 0.48129 | 72193.5 | 0.55315 | 0 | 0.12356 | 1544.5 | 0 | 0 | 64000 | 1544.5 | 0 | 6649 | -4228.25 | 1350000 | 6649 | 0
2021052103 | 6 | 0.46131 | 69196.5 | 0.51145 | 0 | 0.12607 | 1575.875 | 0 | 0 | 64000 | 1575.875 | 0 | 3620.625 | -3028.375 | 1350000 | 3620.625 | 0
2021052104 | 6 | 0.45124 | 67686 | 0.49262 | 0 | 0.12152 | 1519 | 0 | 0 | 64000 | 1519 | 0 | 2167 | -1453.625 | 1350000 | 2167 | 0
2021052105 | 6 | 0.45101 | 67651.5 | 0.44099 | 0 | 0.08879 | 1109.875 | 0 | 0 | 64000 | 1109.875 | 0 | 2541.625 | 374.625 | 1350000 | 2541.625 | 0
2021052106 | 6 | 0.46747 | 70120.5 | 0.3979 | 0 | 0.08441 | 1055.125 | 0 | 0 | 64000 | 1055.125 | 0 | 5065.375 | 2523.75 | 1350000 | 5065.375 | 0
2021052107 | 6 | 0.49619 | 74428.5 | 0.35768 | 0 | 0.09127 | 1140.875 | 0.02019 | 1615.2 | 64000 | 1140.875 | 1615.2 | 7672.425 | 2607.05 | 1350000 | 7672.425 | 0
2021052108 | 6 | 0.52982 | 79473 | 0.29766 | 0 | 0.08973 | 1121.625 | 0.15624 | 12499.2 | 64000 | 1121.625 | 12499.2 | 1852.175 | -5820.25 | 1350000 | 1852.175 | 0
2021052109 | 6 | 0.55811 | 83716.5 | 0.1944 | 0 | 0.08227 | 1028.375 | 0.38758 | 31006.4 | 64000 | 1028.375 | 18688.125 | 0 | -1852.175 | 1350000 | 0 | 0
2021052110 | 6 | 0.58076 | 87114 | 0.09308 | 0 | 0.08766 | 1095.75 | 0.48417 | 38733.6 | 64000 | 1095.75 | 22018.25 | 0 | 0 | 1350000 | 0 | 0
2021052111 | 6 | 0.60472 | 90708 | 0.07993 | 0 | 0.07003 | 875.375 | 0.59284 | 47427.2 | 64000 | 875.375 | 25832.625 | 0 | 0 | 1350000 | 0 | 0
2021052112 | 6 | 0.62832 | 94248 | 0.07299 | 0 | 0.05872 | 734 | 0.65624 | 52499.2 | 64000 | 734 | 29514 | 0 | 0 | 1350000 | 0 | 0
2021052113 | 6 | 0.65129 | 97693.5 | 0.0548 | 0 | 0.04021 | 502.625 | 0.68308 | 54646.4 | 64000 | 502.625 | 33190.875 | 0 | 0 | 1350000 | 0 | 0
2021052114 | 6 | 0.67698 | 101547 | 0.03802 | 0 | 0.03324 | 415.5 | 0.70555 | 56444 | 64000 | 415.5 | 37131.5 | 0 | 0 | 1350000 | 0 | 0
2021052115 | 6 | 0.69856 | 104784 | 0.02569 | 0 | 0.0334 | 417.5 | 0.71022 | 56817.6 | 64000 | 417.5 | 40366.5 | 0 | 0 | 1350000 | 0 | 0
2021052116 | 6 | 0.71816 | 107724 | 0.01668 | 0 | 0.03651 | 456.375 | 0.66773 | 53418.4 | 64000 | 456.375 | 43267.625 | 0 | 0 | 1350000 | 0 | 0
2021052117 | 6 | 0.73329 | 109993.5 | 0.02841 | 0 | 0.06128 | 766 | 0.58556 | 46844.8 | 64000 | 766 | 45227.5 | 0 | 0 | 1350000 | 0 | 0
2021052118 | 6 | 0.73789 | 110683.5 | 0.03329 | 0 | 0.10532 | 1316.5 | 0.44641 | 35712.8 | 64000 | 1316.5 | 35712.8 | 9654.2 | 9654.2 | 1350000 | 9654.2 | 0
2021052119 | 6 | 0.72409 | 108613.5 | 0.05631 | 0 | 0.15606 | 1950.75 | 0.16343 | 13074.4 | 64000 | 1950.75 | 13074.4 | 29588.35 | 19934.15 | 1345877.9 | 29588.35 | 0
2021052120 | 6 | 0.69607 | 104410.5 | 0.13739 | 0 | 0.18007 | 2250.875 | 0.00838 | 670.4 | 64000 | 2250.875 | 670.4 | 37489.225 | 7900.875 | 1333854.925 | 37489.225 | 0
2021052121 | 6 | 0.67087 | 100630.5 | 0.26356 | 0 | 0.1682 | 2102.5 | 0 | 0 | 64000 | 2102.5 | 0 | 34528 | -2961.225 | 1324793.175 | 34528 | 0
2021052122 | 6 | 0.64781 | 97171.5 | 0.36031 | 0 | 0.14853 | 1856.625 | 0 | 0 | 64000 | 1856.625 | 0 | 31314.875 | -3213.125 | 1318944.55 | 31314.875 | 0
2021052123 | 6 | 0.60481 | 90721.5 | 0.385 | 0 | 0.13166 | 1645.75 | 0 | 0 | 64000 | 1645.75 | 0 | 25075.75 | -6239.125 | 1319335.05 | 25075.75 | 0
2021052124 | 6 | 0.55731 | 83596.5 | 0.37073 | 0 | 0.12595 | 1574.375 | 0 | 0 | 64000 | 1574.375 | 0 | 18022.125 | -7053.625 | 1326779.175 | 18022.125 | 0
2021052201 | 7 | 0.51544 | 77316 | 0.35068 | 0 | 0.12912 | 1614 | 0 | 0 | 64000 | 1614 | 0 | 11702 | -6320.125 | 1340543.425 | 11702 | 0
2021052202 | 7 | 0.48517 | 72775.5 | 0.29368 | 0 | 0.16765 | 2095.625 | 0 | 0 | 64000 | 2095.625 | 0 | 6679.875 | -5022.125 | 1350000 | 6679.875 | 0
2021052203 | 7 | 0.46509 | 69763.5 | 0.29572 | 0 | 0.2321 | 2901.25 | 0 | 0 | 64000 | 2901.25 | 0 | 2862.25 | -3817.625 | 1350000 | 2862.25 | 0
2021052204 | 7 | 0.45029 | 67543.5 | 0.22633 | 0 | 0.25084 | 3135.5 | 0 | 0 | 64000 | 3135.5 | 0 | 408 | -2454.25 | 1350000 | 408 | 0
2021052205 | 7 | 0.44305 | 66457.5 | 0.17284 | 0 | 0.22132 | 2766.5 | 0 | 0 | 64000 | 2457.5 | 0 | 0 | -408 | 1350000 | 0 | 0
2021052206 | 7 | 0.44847 | 67270.5 | 0.22585 | 0 | 0.19945 | 2493.125 | 0 | 0 | 64000 | 2493.125 | 0 | 777.375 | 777.375 | 1350000 | 777.375 | 0
2021052207 | 7 | 0.45374 | 68061 | 0.36773 | 0 | 0.22532 | 2816.5 | 0.04207 | 3365.6 | 64000 | 2816.5 | 1244.5 | 0 | -777.375 | 1350000 | 0 | 0
2021052208 | 7 | 0.47417 | 71125.5 | 0.41204 | 0 | 0.28218 | 3527.25 | 0.26032 | 20825.6 | 64000 | 3527.25 | 3598.25 | 0 | 0 | 1350000 | 0 | 0
2021052209 | 7 | 0.50554 | 75831 | 0.36253 | 0 | 0.33769 | 4221.125 | 0.48215 | 38572 | 64000 | 4221.125 | 7609.875 | 0 | 0 | 1350000 | 0 | 0
2021052210 | 7 | 0.53837 | 80755.5 | 0.2778 | 0 | 0.39404 | 4925.5 | 0.59082 | 47265.6 | 64000 | 4925.5 | 11830 | 0 | 0 | 1350000 | 0 | 0
2021052211 | 7 | 0.5713 | 85695 | 0.25225 | 0 | 0.38576 | 4822 | 0.66093 | 52874.4 | 64000 | 4822 | 16873 | 0 | 0 | 1350000 | 0 | 0
2021052212 | 7 | 0.60617 | 90925.5 | 0.27351 | 0 | 0.35873 | 4484.125 | 0.6811 | 54488 | 64000 | 4484.125 | 22441.375 | 0 | 0 | 1350000 | 0 | 0
2021052213 | 7 | 0.63806 | 95709 | 0.32274 | 0 | 0.31574 | 3946.75 | 0.68877 | 55101.6 | 64000 | 3946.75 | 27762.25 | 0 | 0 | 1350000 | 0 | 0
2021052214 | 7 | 0.66537 | 99805.5 | 0.41619 | 0 | 0.33589 | 4198.625 | 0.67455 | 53964 | 64000 | 4198.625 | 31606.875 | 0 | 0 | 1350000 | 0 | 0
2021052215 | 7 | 0.68631 | 102946.5 | 0.48267 | 0 | 0.298 | 3725 | 0.69262 | 55409.6 | 64000 | 3725 | 35221.5 | 0 | 0 | 1350000 | 0 | 0
2021052216 | 7 | 0.70238 | 105357 | 0.52308 | 0 | 0.28335 | 3541.875 | 0.66497 | 53197.6 | 64000 | 3541.875 | 37815.125 | 0 | 0 | 1350000 | 0 | 0
2021052217 | 7 | 0.71339 | 107008.5 | 0.55343 | 0 | 0.31381 | 3922.625 | 0.58948 | 47158.4 | 64000 | 3922.625 | 39085.875 | 0 | 0 | 1350000 | 0 | 0
2021052218 | 7 | 0.7171 | 107565 | 0.60328 | 0 | 0.31339 | 3917.375 | 0.42229 | 33783.2 | 64000 | 3917.375 | 33783.2 | 5864.425 | 5864.425 | 1350000 | 5864.425 | 0
2021052219 | 7 | 0.70921 | 106381.5 | 0.56931 | 0 | 0.35233 | 4404.125 | 0.15553 | 12442.4 | 64000 | 4404.125 | 12442.4 | 25534.975 | 19670.55 | 1349931.275 | 25534.975 | 0
2021052220 | 7 | 0.69218 | 103827 | 0.54838 | 0 | 0.36166 | 4520.75 | 0.00906 | 724.8 | 64000 | 4520.75 | 724.8 | 34581.45 | 9046.475 | 1340816.075 | 34581.45 | 0
2021052221 | 7 | 0.67478 | 101217 | 0.56218 | 0 | 0.36473 | 4559.125 | 0 | 0 | 64000 | 4559.125 | 0 | 32657.875 | -1923.575 | 1333624.45 | 32657.875 | 0
2021052222 | 7 | 0.65576 | 98364 | 0.60263 | 0 | 0.46661 | 5832.625 | 0 | 0 | 64000 | 5832.625 | 0 | 28531.375 | -4126.5 | 1330559.325 | 28531.375 | 0
2021052223 | 7 | 0.6206 | 93090 | 0.58978 | 0 | 0.51056 | 6382 | 0 | 0 | 64000 | 6382 | 0 | 22708 | -5823.375 | 1333317.575 | 22708 | 0
2021052224 | 7 | 0.57688 | 86532 | 0.59113 | 0 | 0.56977 | 7122.125 | 0 | 0 | 64000 | 7122.125 | 0 | 15409.875 | -7298.125 | 1343373.95 | 15409.875 | 0
2021052301 | 1 | 0.53598 | 80397 | 0.67828 | 0 | 0.57798 | 7224.75 | 0 | 0 | 64000 | 7224.75 | 0 | 9172.25 | -6237.625 | 1350000 | 9172.25 | 0
2021052302 | 1 | 0.50559 | 75838.5 | 0.68324 | 0 | 0.53152 | 6644 | 0 | 0 | 64000 | 6644 | 0 | 5194.5 | -3977.75 | 1350000 | 5194.5 | 0
2021052303 | 1 | 0.48268 | 72402 | 0.70187 | 0 | 0.51852 | 6481.5 | 0 | 0 | 64000 | 6481.5 | 0 | 1920.5 | -3274 | 1350000 | 1920.5 | 0
2021052304 | 1 | 0.46794 | 70191 | 0.82141 | 0 | 0.55489 | 6936.125 | 0 | 0 | 64000 | 6191 | 0 | 0 | -1920.5 | 1350000 | 0 | 0
2021052305 | 1 | 0.45896 | 68844 | 0.83398 | 0 | 0.50527 | 6315.875 | 0 | 0 | 64000 | 4844 | 0 | 0 | 0 | 1350000 | 0 | 0
2021052306 | 1 | 0.45668 | 68502 | 0.78082 | 0 | 0.42715 | 5339.375 | 0.00188 | 150.4 | 64000 | 4502 | 0 | 0 | 0 | 1350000 | 0 | 0
2021052307 | 1 | 0.45706 | 68559 | 0.74032 | 0 | 0.42949 | 5368.625 | 0.02925 | 2340 | 64000 | 4559 | 0 | 0 | 0 | 1350000 | 0 | 0
2021052308 | 1 | 0.4771 | 71565 | 0.62029 | 0 | 0.48688 | 6086 | 0.17106 | 13684.8 | 64000 | 6086 | 1479 | 0 | 0 | 1350000 | 0 | 0
2021052309 | 1 | 0.51491 | 77236.5 | 0.50444 | 0 | 0.5282 | 6602.5 | 0.34622 | 27697.6 | 64000 | 6602.5 | 6634 | 0 | 0 | 1350000 | 0 | 0
2021052310 | 1 | 0.55863 | 83794.5 | 0.49032 | 0 | 0.52572 | 6571.5 | 0.45686 | 36548.8 | 64000 | 6571.5 | 13223 | 0 | 0 | 1350000 | 0 | 0
2021052311 | 1 | 0.60165 | 90247.5 | 0.59705 | 0 | 0.48722 | 6090.25 | 0.59446 | 47556.8 | 64000 | 6090.25 | 20157.25 | 0 | 0 | 1350000 | 0 | 0
2021052312 | 1 | 0.64207 | 96310.5 | 0.73864 | 0 | 0.49944 | 6243 | 0.67592 | 54073.6 | 64000 | 6243 | 26067.5 | 0 | 0 | 1350000 | 0 | 0
2021052313 | 1 | 0.67684 | 101526 | 0.75455 | 0 | 0.43014 | 5376.75 | 0.68277 | 54621.6 | 64000 | 5376.75 | 32149.25 | 0 | 0 | 1350000 | 0 | 0
2021052314 | 1 | 0.70507 | 105760.5 | 0.75293 | 0 | 0.40745 | 5093.125 | 0.71212 | 56969.6 | 64000 | 5093.125 | 36667.375 | 0 | 0 | 1350000 | 0 | 0
2021052315 | 1 | 0.72759 | 109138.5 | 0.7905 | 0 | 0.45822 | 5727.75 | 0.70714 | 56571.2 | 64000 | 5727.75 | 39410.75 | 0 | 0 | 1350000 | 0 | 0
2021052316 | 1 | 0.74536 | 111804 | 0.77569 | 0 | 0.44628 | 5578.5 | 0.67236 | 53788.8 | 64000 | 5578.5 | 42225.5 | 0 | 0 | 1350000 | 0 | 0
2021052317 | 1 | 0.76347 | 114520.5 | 0.76033 | 0 | 0.41886 | 5235.75 | 0.5874 | 46992 | 64000 | 5235.75 | 45284.75 | 0 | 0 | 1350000 | 0 | 0
2021052318 | 1 | 0.77441 | 116161.5 | 0.73587 | 0 | 0.41035 | 5129.375 | 0.41591 | 33272.8 | 64000 | 5129.375 | 33272.8 | 13759.325 | 13759.325 | 1350000 | 13759.325 | 0
2021052319 | 1 | 0.7696 | 115440 | 0.72688 | 0 | 0.45692 | 5711.5 | 0.1462 | 11696 | 64000 | 5711.5 | 11696 | 34032.5 | 20273.175 | 1341433.75 | 34032.5 | 0
2021052320 | 1 | 0.75096 | 112644 | 0.71897 | 0 | 0.46695 | 5836.875 | 0.00871 | 696.8 | 64000 | 5836.875 | 696.8 | 42110.325 | 8077.825 | 1324789.675 | 42110.325 | 0
2021052321 | 1 | 0.73037 | 109555.5 | 0.64536 | 0 | 0.46602 | 5825.25 | 0 | 0 | 64000 | 5825.25 | 0 | 39730.25 | -2380.075 | 1310525.675 | 39730.25 | 0
2021052322 | 1 | 0.70647 | 105970.5 | 0.53932 | 0 | 0.45649 | 5706.125 | 0 | 0 | 64000 | 5706.125 | 0 | 36264.375 | -3465.875 | 1299727.55 | 36264.375 | 0
2021052323 | 1 | 0.65731 | 98596.5 | 0.48666 | 0 | 0.43172 | 5396.5 | 0 | 0 | 64000 | 5396.5 | 0 | 29200 | -7064.375 | 1295993.8 | 29200 | 0
2021052324 | 1 | 0.6037 | 90555 | 0.434 | 0 | 0.41318 | 5164.75 | 0 | 0 | 64000 | 5164.75 | 0 | 21390.25 | -7809.75 | 1300069.8 | 21390.25 | 0
2021052401 | 2 | 0.55874 | 83811 | 0.33752 | 0 | 0.39919 | 4989.875 | 0 | 0 | 64000 | 4989.875 | 0 | 14821.125 | -6569.125 | 1310714.925 | 14821.125 | 0
2021052402 | 2 | 0.52508 | 78762 | 0.21035 | 0 | 0.30942 | 3867.75 | 0 | 0 | 64000 | 3867.75 | 0 | 10894.25 | -3926.875 | 1325286.925 | 10894.25 | 0
2021052403 | 2 | 0.50257 | 75385.5 | 0.11516 | 0 | 0.28846 | 3605.75 | 0 | 0 | 64000 | 3605.75 | 0 | 7779.75 | -3114.5 | 1342973.425 | 7779.75 | 0
2021052404 | 2 | 0.4891 | 73365 | 0.09621 | 0 | 0.30054 | 3756.75 | 0 | 0 | 64000 | 3756.75 | 0 | 5608.25 | -2171.5 | 1350000 | 5608.25 | 0
2021052405 | 2 | 0.48869 | 73303.5 | 0.07814 | 0 | 0.28447 | 3555.875 | 0 | 0 | 64000 | 3555.875 | 0 | 5747.625 | 139.375 | 1350000 | 5747.625 | 0
2021052406 | 2 | 0.50644 | 75966 | 0.08448 | 0 | 0.30537 | 3817.125 | 0 | 0 | 64000 | 3817.125 | 0 | 8148.875 | 2401.25 | 1350000 | 8148.875 | 0
2021052407 | 2 | 0.53488 | 80232 | 0.16272 | 0 | 0.41436 | 5179.5 | 0.02679 | 2143.2 | 64000 | 5179.5 | 2143.2 | 8909.3 | 760.425 | 1350000 | 8909.3 | 0
2021052408 | 2 | 0.56674 | 85011 | 0.21394 | 0 | 0.44455 | 5556.875 | 0.19528 | 15622.4 | 64000 | 5556.875 | 15454.125 | 0 | -8909.3 | 1350000 | 0 | 0
2021052409 | 2 | 0.58984 | 88476 | 0.20283 | 0 | 0.40411 | 5051.375 | 0.37689 | 30151.2 | 64000 | 5051.375 | 19424.625 | 0 | 0 | 1350000 | 0 | 0
2021052410 | 2 | 0.60755 | 91132.5 | 0.22573 | 0 | 0.34998 | 4374.75 | 0.46964 | 37571.2 | 64000 | 4374.75 | 22757.75 | 0 | 0 | 1350000 | 0 | 0
2021052411 | 2 | 0.62542 | 93813 | 0.22924 | 0 | 0.2886 | 3607.5 | 0.60477 | 48381.6 | 64000 | 3607.5 | 26205.5 | 0 | 0 | 1350000 | 0 | 0
2021052412 | 2 | 0.64518 | 96777 | 0.26956 | 0 | 0.24031 | 3003.875 | 0.65017 | 52013.6 | 64000 | 3003.875 | 29773.125 | 0 | 0 | 1350000 | 0 | 0
2021052413 | 2 | 0.66326 | 99489 | 0.30143 | 0 | 0.19339 | 2417.375 | 0.65161 | 52128.8 | 64000 | 2417.375 | 33071.625 | 0 | 0 | 1350000 | 0 | 0
2021052414 | 2 | 0.67777 | 101665.5 | 0.31838 | 0 | 0.17465 | 2183.125 | 0.64565 | 51652 | 64000 | 2183.125 | 35482.375 | 0 | 0 | 1350000 | 0 | 0
2021052415 | 2 | 0.68434 | 102651 | 0.2745 | 0 | 0.18343 | 2292.875 | 0.64859 | 51887.2 | 64000 | 2292.875 | 36358.125 | 0 | 0 | 1350000 | 0 | 0
2021052416 | 2 | 0.68816 | 103224 | 0.32173 | 0 | 0.20463 | 2557.875 | 0.6428 | 51424 | 64000 | 2557.875 | 36666.125 | 0 | 0 | 1350000 | 0 | 0
2021052417 | 2 | 0.69175 | 103762.5 | 0.30175 | 0 | 0.21283 | 2660.375 | 0.5721 | 45768 | 64000 | 2660.375 | 37102.125 | 0 | 0 | 1350000 | 0 | 0
2021052418 | 2 | 0.69432 | 104148 | 0.27845 | 0 | 0.27239 | 3404.875 | 0.41808 | 33446.4 | 64000 | 3404.875 | 33446.4 | 3296.725 | 3296.725 | 1350000 | 3296.725 | 0
2021052419 | 2 | 0.68905 | 103357.5 | 0.24827 | 0 | 0.27157 | 3394.625 | 0.13775 | 11020 | 64000 | 3394.625 | 11020 | 24942.875 | 21646.15 | 1350000 | 24942.875 | 0
2021052420 | 2 | 0.67341 | 101011.5 | 0.28587 | 0 | 0.26925 | 3365.625 | 0.00947 | 757.6 | 64000 | 3365.625 | 757.6 | 32888.275 | 7945.4 | 1342577.975 | 32888.275 | 0
2021052421 | 2 | 0.66043 | 99064.5 | 0.31336 | 0 | 0.26239 | 3279.875 | 0 | 0 | 64000 | 3279.875 | 0 | 31784.625 | -1103.65 | 1336259.6 | 31784.625 | 0
2021052422 | 2 | 0.64101 | 96151.5 | 0.34569 | 0 | 0.3063 | 3828.75 | 0 | 0 | 64000 | 3828.75 | 0 | 28322.75 | -3461.875 | 1333403.1 | 28322.75 | 0
2021052423 | 2 | 0.59869 | 89803.5 | 0.34537 | 0 | 0.33247 | 4155.875 | 0 | 0 | 64000 | 4155.875 | 0 | 21647.625 | -6675.125 | 1337221.725 | 21647.625 | 0
2021052424 | 2 | 0.55186 | 82779 | 0.34763 | 0 | 0.35924 | 4490.5 | 0 | 0 | 64000 | 4490.5 | 0 | 14288.5 | -7359.125 | 1348399.475 | 14288.5 | 0
2021052501 | 3 | 0.51356 | 77034 | 0.35473 | 0 | 0.34099 | 4262.375 | 0 | 0 | 64000 | 4262.375 | 0 | 8771.625 | -5516.875 | 1350000 | 8771.625 | 0
2021052502 | 3 | 0.48824 | 73236 | 0.34547 | 0 | 0.3708 | 4635 | 0 | 0 | 64000 | 4635 | 0 | 4601 | -4170.625 | 1350000 | 4601 | 0
2021052503 | 3 | 0.47285 | 70927.5 | 0.34195 | 0 | 0.33956 | 4244.5 | 0 | 0 | 64000 | 4244.5 | 0 | 2683 | -1918 | 1350000 | 2683 | 0
2021052504 | 3 | 0.46369 | 69553.5 | 0.29329 | 0 | 0.30673 | 3834.125 | 0 | 0 | 64000 | 3834.125 | 0 | 1719.375 | -963.625 | 1350000 | 1719.375 | 0
2021052505 | 3 | 0.46488 | 69732 | 0.23893 | 0 | 0.28328 | 3541 | 0 | 0 | 64000 | 3541 | 0 | 2191 | 471.625 | 1350000 | 2191 | 0
2021052506 | 3 | 0.484 | 72600 | 0.22163 | 0 | 0.23701 | 2962.625 | 0 | 0 | 64000 | 2962.625 | 0 | 5637.375 | 3446.375 | 1350000 | 5637.375 | 0
2021052507 | 3 | 0.51698 | 77547 | 0.23155 | 0 | 0.21452 | 2681.5 | 0.05571 | 4456.8 | 64000 | 2681.5 | 4456.8 | 6408.7 | 771.325 | 1350000 | 6408.7 | 0
2021052508 | 3 | 0.55089 | 82633.5 | 0.22019 | 0 | 0.23462 | 2932.75 | 0.23853 | 19082.4 | 64000 | 2932.75 | 15700.75 | 0 | -6408.7 | 1350000 | 0 | 0
2021052509 | 3 | 0.58076 | 87114 | 0.17926 | 0 | 0.26262 | 3282.75 | 0.39469 | 31575.2 | 64000 | 3282.75 | 19831.25 | 0 | 0 | 1350000 | 0 | 0
2021052510 | 3 | 0.606 | 90900 | 0.13339 | 0 | 0.31273 | 3909.125 | 0.49669 | 39735.2 | 64000 | 3909.125 | 22990.875 | 0 | 0 | 1350000 | 0 | 0
2021052511 | 3 | 0.6307 | 94605 | 0.15332 | 0 | 0.34998 | 4374.75 | 0.57921 | 46336.8 | 64000 | 4374.75 | 26230.25 | 0 | 0 | 1350000 | 0 | 0
2021052512 | 3 | 0.65533 | 98299.5 | 0.16427 | 0 | 0.37853 | 4731.625 | 0.63769 | 51015.2 | 64000 | 4731.625 | 29567.875 | 0 | 0 | 1350000 | 0 | 0
2021052513 | 3 | 0.67598 | 101397 | 0.20062 | 0 | 0.38523 | 4815.375 | 0.65542 | 52433.6 | 64000 | 4815.375 | 32581.625 | 0 | 0 | 1350000 | 0 | 0
2021052514 | 3 | 0.69655 | 104482.5 | 0.22973 | 0 | 0.36395 | 4549.375 | 0.65566 | 52452.8 | 64000 | 4549.375 | 35933.125 | 0 | 0 | 1350000 | 0 | 0
2021052515 | 3 | 0.7126 | 106890 | 0.20384 | 0 | 0.37804 | 4725.5 | 0.67003 | 53602.4 | 64000 | 4725.5 | 38164.5 | 0 | 0 | 1350000 | 0 | 0
2021052516 | 3 | 0.72949 | 109423.5 | 0.20752 | 0 | 0.35098 | 4387.25 | 0.65539 | 52431.2 | 64000 | 4387.25 | 41036.25 | 0 | 0 | 1350000 | 0 | 0
2021052517 | 3 | 0.7406 | 111090 | 0.24023 | 0 | 0.32934 | 4116.75 | 0.54633 | 43706.4 | 64000 | 4116.75 | 42973.25 | 0 | 0 | 1350000 | 0 | 0
2021052518 | 3 | 0.75084 | 112626 | 0.28059 | 0 | 0.31923 | 3990.375 | 0.39742 | 31793.6 | 64000 | 3990.375 | 31793.6 | 12842.025 | 12842.025 | 1350000 | 12842.025 | 0
2021052519 | 3 | 0.74456 | 111684 | 0.33567 | 0 | 0.30312 | 3789 | 0.14358 | 11486.4 | 64000 | 3789 | 11486.4 | 32408.6 | 19566.575 | 1343057.65 | 32408.6 | 0
2021052520 | 3 | 0.72519 | 108778.5 | 0.38213 | 0 | 0.31829 | 3978.625 | 0.00952 | 761.6 | 64000 | 3978.625 | 761.6 | 40038.275 | 7629.675 | 1328485.625 | 40038.275 | 0
2021052521 | 3 | 0.70554 | 105831 | 0.44139 | 0 | 0.3542 | 4427.5 | 0 | 0 | 64000 | 4427.5 | 0 | 37403.5 | -2634.775 | 1316548.375 | 37403.5 | 0
2021052522 | 3 | 0.68564 | 102846 | 0.46748 | 0 | 0.33926 | 4240.75 | 0 | 0 | 64000 | 4240.75 | 0 | 34605.25 | -2798.25 | 1307409.375 | 34605.25 | 0
2021052523 | 3 | 0.63885 | 95827.5 | 0.49616 | 0 | 0.32455 | 4056.875 | 0 | 0 | 64000 | 4056.875 | 0 | 27770.625 | -6834.625 | 1305105 | 27770.625 | 0
2021052524 | 3 | 0.58627 | 87940.5 | 0.5481 | 0 | 0.29162 | 3645.25 | 0 | 0 | 64000 | 3645.25 | 0 | 20295.25 | -7475.375 | 1310276 | 20295.25 | 0
2021052601 | 4 | 0.54575 | 81862.5 | 0.58402 | 0 | 0.26921 | 3365.125 | 0 | 0 | 64000 | 3365.125 | 0 | 14497.375 | -5797.875 | 1321244.875 | 14497.375 | 0
2021052602 | 4 | 0.51606 | 77409 | 0.608 | 0 | 0.23486 | 2935.75 | 0 | 0 | 64000 | 2935.75 | 0 | 10473.25 | -4024.125 | 1336237.875 | 10473.25 | 0
2021052603 | 4 | 0.49831 | 74746.5 | 0.61391 | 0 | 0.21956 | 2744.5 | 0 | 0 | 64000 | 2744.5 | 0 | 8002 | -2471.25 | 1350000 | 8002 | 0
2021052604 | 4 | 0.48725 | 73087.5 | 0.59848 | 0 | 0.22808 | 2851 | 0 | 0 | 64000 | 2851 | 0 | 6236.5 | -1765.5 | 1350000 | 6236.5 | 0
2021052605 | 4 | 0.48847 | 73270.5 | 0.62891 | 0 | 0.29029 | 3628.625 | 0 | 0 | 64000 | 3628.625 | 0 | 5641.875 | -594.625 | 1350000 | 5641.875 | 0
2021052606 | 4 | 0.50726 | 76089 | 0.6707 | 0 | 0.32495 | 4061.875 | 0 | 0 | 64000 | 4061.875 | 0 | 8027.125 | 2385.25 | 1350000 | 8027.125 | 0
2021052607 | 4 | 0.53952 | 80928 | 0.6535 | 0 | 0.30425 | 3803.125 | 0.05912 | 4729.6 | 64000 | 3803.125 | 4729.6 | 8395.275 | 368.15 | 1350000 | 8395.275 | 0
2021052608 | 4 | 0.57871 | 86806.5 | 0.61486 | 0 | 0.33784 | 4223 | 0.25839 | 20671.2 | 64000 | 4223 | 18583.5 | 0 | -8395.275 | 1350000 | 0 | 0
2021052609 | 4 | 0.61164 | 91746 | 0.48675 | 0 | 0.38889 | 4861.125 | 0.48154 | 38523.2 | 64000 | 4861.125 | 22884.875 | 0 | 0 | 1350000 | 0 | 0
2021052610 | 4 | 0.63987 | 95980.5 | 0.37726 | 0 | 0.42335 | 5291.875 | 0.58376 | 46700.8 | 64000 | 5291.875 | 26688.625 | 0 | 0 | 1350000 | 0 | 0
2021052611 | 4 | 0.67198 | 100797 | 0.42998 | 0 | 0.39434 | 4929.25 | 0.61031 | 48824.8 | 64000 | 4929.25 | 31867.75 | 0 | 0 | 1350000 | 0 | 0
2021052612 | 4 | 0.70527 | 105790.5 | 0.53861 | 0 | 0.34713 | 4339.125 | 0.6131 | 49048 | 64000 | 4339.125 | 37451.375 | 0 | 0 | 1350000 | 0 | 0
2021052613 | 4 | 0.73631 | 110446.5 | 0.6628 | 0 | 0.29375 | 3671.875 | 0.61287 | 49029.6 | 64000 | 3671.875 | 42774.625 | 0 | 0 | 1350000 | 0 | 0
2021052614 | 4 | 0.76169 | 114253.5 | 0.74072 | 0 | 0.22895 | 2861.875 | 0.5771 | 46168 | 64000 | 2861.875 | 46168 | 1223.625 | 1223.625 | 1350000 | 1223.625 | 0
2021052615 | 4 | 0.78117 | 117175.5 | 0.67253 | 0 | 0.18836 | 2354.5 | 0.53656 | 42924.8 | 64000 | 2354.5 | 42924.8 | 7896.2 | 6672.575 | 1350000 | 7896.2 | 0
2021052616 | 4 | 0.79648 | 119472 | 0.65814 | 0 | 0.17717 | 2214.625 | 0.48465 | 38772 | 64000 | 2214.625 | 38772 | 14485.375 | 6589.175 | 1350000 | 14485.375 | 0
2021052617 | 4 | 0.80411 | 120616.5 | 0.75174 | 0 | 0.21533 | 2691.625 | 0.36901 | 29520.8 | 64000 | 2691.625 | 29520.8 | 24404.075 | 9918.7 | 1350000 | 24404.075 | 0
2021052618 | 4 | 0.79625 | 119437.5 | 0.73416 | 0 | 0.27265 | 3408.125 | 0.23408 | 18726.4 | 64000 | 3408.125 | 18726.4 | 33302.975 | 8898.9 | 1342163.275 | 33302.975 | 0
2021052619 | 4 | 0.77238 | 115857 | 0.78381 | 0 | 0.3196 | 3995 | 0.07953 | 6362.4 | 64000 | 3995 | 6362.4 | 41499.6 | 8196.625 | 1326129.925 | 41499.6 | 0
2021052620 | 4 | 0.74057 | 111085.5 | 0.84539 | 0 | 0.34299 | 4287.375 | 0.00597 | 477.6 | 64000 | 4287.375 | 477.6 | 42320.525 | 820.925 | 1309275.65 | 42320.525 | 0
2021052621 | 4 | 0.71078 | 106617 | 0.69894 | 0 | 0.33949 | 4243.625 | 0 | 0 | 64000 | 4243.625 | 0 | 38373.375 | -3947.15 | 1296368.525 | 38373.375 | 0
2021052622 | 4 | 0.68135 | 102202.5 | 0.64816 | 0 | 0.36797 | 4599.625 | 0 | 0 | 64000 | 4599.625 | 0 | 33602.875 | -4770.5 | 1288231.9 | 33602.875 | 0
2021052623 | 4 | 0.63393 | 95089.5 | 0.54867 | 0 | 0.39058 | 4882.25 | 0 | 0 | 64000 | 4882.25 | 0 | 26207.25 | -7395.625 | 1287490.9 | 26207.25 | 0
2021052624 | 4 | 0.58402 | 87603 | 0.6385 | 0 | 0.4143 | 5178.75 | 0 | 0 | 64000 | 5178.75 | 0 | 18424.25 | -7783 | 1294532.9 | 18424.25 | 0
2021052701 | 5 | 0.54039 | 81058.5 | 0.58805 | 0 | 0.42696 | 5337 | 0 | 0 | 64000 | 5337 | 0 | 11721.5 | -6702.75 | 1308277.65 | 11721.5 | 0
2021052702 | 5 | 0.51097 | 76645.5 | 0.59285 | 0 | 0.39456 | 4932 | 0 | 0 | 64000 | 4932 | 0 | 7713.5 | -4008 | 1326030.4 | 7713.5 | 0
2021052703 | 5 | 0.49132 | 73698 | 0.5021 | 0 | 0.36454 | 4556.75 | 0 | 0 | 64000 | 4556.75 | 0 | 5141.25 | -2572.25 | 1346355.4 | 5141.25 | 0
2021052704 | 5 | 0.47994 | 71991 | 0.4804 | 0 | 0.34764 | 4345.5 | 0 | 0 | 64000 | 4345.5 | 0 | 3645.5 | -1495.75 | 1350000 | 3645.5 | 0
2021052705 | 5 | 0.47844 | 71766 | 0.49762 | 0 | 0.2931 | 3663.75 | 0 | 0 | 64000 | 3663.75 | 0 | 4102.25 | 456.75 | 1350000 | 4102.25 | 0
2021052706 | 5 | 0.49319 | 73978.5 | 0.44172 | 0 | 0.19868 | 2483.5 | 0 | 0 | 64000 | 2483.5 | 0 | 7495 | 3392.75 | 1350000 | 7495 | 0
2021052707 | 5 | 0.52123 | 78184.5 | 0.39485 | 0 | 0.15342 | 1917.75 | 0.04135 | 3308 | 64000 | 1917.75 | 3308 | 8958.75 | 1463.75 | 1350000 | 8958.75 | 0
2021052708 | 5 | 0.55881 | 83821.5 | 0.36976 | 0 | 0.15581 | 1947.625 | 0.10738 | 8590.4 | 64000 | 1947.625 | 8590.4 | 9283.475 | 324.725 | 1350000 | 9283.475 | 0
2021052709 | 5 | 0.58912 | 88368 | 0.33336 | 0 | 0.14305 | 1788.125 | 0.16184 | 12947.2 | 64000 | 1788.125 | 12947.2 | 9632.675 | 349.2 | 1350000 | 9632.675 | 0
2021052710 | 5 | 0.61093 | 91639.5 | 0.37388 | 0 | 0.10505 | 1313.125 | 0.19572 | 15657.6 | 64000 | 1313.125 | 15657.6 | 10668.775 | 1036.1 | 1350000 | 10668.775 | 0
2021052711 | 5 | 0.63196 | 94794 | 0.4422 | 0 | 0.08677 | 1084.625 | 0.20826 | 16660.8 | 64000 | 1084.625 | 16660.8 | 13048.575 | 2379.8 | 1350000 | 13048.575 | 0
2021052712 | 5 | 0.65124 | 97686 | 0.4987 | 0 | 0.06226 | 778.25 | 0.20167 | 16133.6 | 64000 | 778.25 | 16133.6 | 16774.15 | 3725.575 | 1350000 | 16774.15 | 0
2021052713 | 5 | 0.66977 | 100465.5 | 0.3918 | 0 | 0.04941 | 617.625 | 0.25615 | 20492 | 64000 | 617.625 | 20492 | 15355.875 | -1418.275 | 1350000 | 15355.875 | 0
2021052714 | 5 | 0.68617 | 102925.5 | 0.32319 | 0 | 0.02998 | 374.75 | 0.295 | 23600 | 64000 | 374.75 | 23600 | 14950.75 | -405.125 | 1350000 | 14950.75 | 0
2021052715 | 5 | 0.69923 | 104884.5 | 0.41176 | 0 | 0.02914 | 364.25 | 0.24765 | 19812 | 64000 | 364.25 | 19812 | 20708.25 | 5757.5 | 1350000 | 20708.25 | 0
2021052716 | 5 | 0.71157 | 106735.5 | 0.35903 | 0 | 0.03671 | 458.875 | 0.19007 | 15205.6 | 64000 | 458.875 | 15205.6 | 27071.025 | 6362.775 | 1348395.225 | 27071.025 | 0
2021052717 | 5 | 0.72164 | 108246 | 0.29904 | 0 | 0.06001 | 750.125 | 0.14254 | 11403.2 | 64000 | 750.125 | 11403.2 | 32092.675 | 5021.65 | 1341768.8 | 32092.675 | 0
2021052718 | 5 | 0.72205 | 108307.5 | 0.30147 | 0 | 0.13196 | 1649.5 | 0.11106 | 8884.8 | 64000 | 1649.5 | 8884.8 | 33773.2 | 1680.525 | 1333461.85 | 33773.2 | 0
2021052719 | 5 | 0.70632 | 105948 | 0.30078 | 0 | 0.17852 | 2231.5 | 0.05522 | 4417.6 | 64000 | 2231.5 | 4417.6 | 35298.9 | 1525.7 | 1323629.2 | 35298.9 | 0
2021052720 | 5 | 0.68153 | 102229.5 | 0.32462 | 0 | 0.18468 | 2308.5 | 0.00556 | 444.8 | 64000 | 2308.5 | 444.8 | 35476.2 | 177.3 | 1313619.25 | 35476.2 | 0
2021052721 | 5 | 0.6601 | 99015 | 0.37905 | 0 | 0.18185 | 2273.125 | 0 | 0 | 64000 | 2273.125 | 0 | 32741.875 | -2734.325 | 1306343.625 | 32741.875 | 0
2021052722 | 5 | 0.63797 | 95695.5 | 0.38703 | 0 | 0.20926 | 2615.75 | 0 | 0 | 64000 | 2615.75 | 0 | 29079.75 | -3662.125 | 1302730.125 | 29079.75 | 0
2021052723 | 5 | 0.59296 | 88944 | 0.35569 | 0 | 0.21262 | 2657.75 | 0 | 0 | 64000 | 2657.75 | 0 | 22286.25 | -6793.5 | 1305910.125 | 22286.25 | 0
2021052724 | 5 | 0.54721 | 82081.5 | 0.27826 | 0 | 0.25232 | 3154 | 0 | 0 | 64000 | 3154 | 0 | 14927.5 | -7358.75 | 1316448.875 | 14927.5 | 0
2021052801 | 6 | 0.50735 | 76102.5 | 0.18883 | 0 | 0.25636 | 3204.5 | 0 | 0 | 64000 | 3204.5 | 0 | 8898 | -6029.5 | 1333017.125 | 8898 | 0
2021052802 | 6 | 0.47945 | 71917.5 | 0.18063 | 0 | 0.20654 | 2581.75 | 0 | 0 | 64000 | 2581.75 | 0 | 5335.75 | -3562.25 | 1350000 | 5335.75 | 0
2021052803 | 6 | 0.46285 | 69427.5 | 0.25401 | 0 | 0.16263 | 2032.875 | 0 | 0 | 64000 | 2032.875 | 0 | 3394.625 | -1941.125 | 1350000 | 3394.625 | 0
2021052804 | 6 | 0.45318 | 67977 | 0.34707 | 0 | 0.16017 | 2002.125 | 0 | 0 | 64000 | 2002.125 | 0 | 1974.875 | -1419.75 | 1350000 | 1974.875 | 0
2021052805 | 6 | 0.45456 | 68184 | 0.38421 | 0 | 0.13259 | 1657.375 | 0 | 0 | 64000 | 1657.375 | 0 | 2526.625 | 551.75 | 1350000 | 2526.625 | 0
2021052806 | 6 | 0.47086 | 70629 | 0.44411 | 0 | 0.12909 | 1613.625 | 0 | 0 | 64000 | 1613.625 | 0 | 5015.375 | 2488.75 | 1350000 | 5015.375 | 0
2021052807 | 6 | 0.49711 | 74566.5 | 0.54807 | 0 | 0.11814 | 1476.75 | 0.04294 | 3435.2 | 64000 | 1476.75 | 3435.2 | 5654.55 | 639.175 | 1350000 | 5654.55 | 0
2021052808 | 6 | 0.52635 | 78952.5 | 0.60997 | 0 | 0.14543 | 1817.875 | 0.1866 | 14928 | 64000 | 1817.875 | 13134.625 | 0 | -5654.55 | 1350000 | 0 | 0
2021052809 | 6 | 0.55065 | 82597.5 | 0.60116 | 0 | 0.18145 | 2268.125 | 0.38313 | 30650.4 | 64000 | 2268.125 | 16329.375 | 0 | 0 | 1350000 | 0 | 0
2021052810 | 6 | 0.5688 | 85320 | 0.59542 | 0 | 0.20364 | 2545.5 | 0.55609 | 44487.2 | 64000 | 2545.5 | 18774.5 | 0 | 0 | 1350000 | 0 | 0
2021052811 | 6 | 0.58579 | 87868.5 | 0.59616 | 0 | 0.21721 | 2715.125 | 0.64416 | 51532.8 | 64000 | 2715.125 | 21153.375 | 0 | 0 | 1350000 | 0 | 0
2021052812 | 6 | 0.59734 | 89601 | 0.60539 | 0 | 0.20713 | 2589.125 | 0.70387 | 56309.6 | 64000 | 2589.125 | 23011.875 | 0 | 0 | 1350000 | 0 | 0
2021052813 | 6 | 0.60593 | 90889.5 | 0.58077 | 0 | 0.19291 | 2411.375 | 0.72731 | 58184.8 | 64000 | 2411.375 | 24478.125 | 0 | 0 | 1350000 | 0 | 0
2021052814 | 6 | 0.60939 | 91408.5 | 0.57245 | 0 | 0.18215 | 2276.875 | 0.7429 | 59432 | 64000 | 2276.875 | 25131.625 | 0 | 0 | 1350000 | 0 | 0
2021052815 | 6 | 0.60704 | 91056 | 0.55797 | 0 | 0.17723 | 2215.375 | 0.72919 | 58335.2 | 64000 | 2215.375 | 24840.625 | 0 | 0 | 1350000 | 0 | 0
2021052816 | 6 | 0.60131 | 90196.5 | 0.62859 | 0 | 0.14653 | 1831.625 | 0.7022 | 56176 | 64000 | 1831.625 | 24364.875 | 0 | 0 | 1350000 | 0 | 0
2021052817 | 6 | 0.59758 | 89637 | 0.61838 | 0 | 0.16903 | 2112.875 | 0.63556 | 50844.8 | 64000 | 2112.875 | 23524.125 | 0 | 0 | 1350000 | 0 | 0
2021052818 | 6 | 0.59313 | 88969.5 | 0.68323 | 0 | 0.24806 | 3100.75 | 0.48703 | 38962.4 | 64000 | 3100.75 | 21868.75 | 0 | 0 | 1350000 | 0 | 0
2021052819 | 6 | 0.58166 | 87249 | 0.66278 | 0 | 0.27619 | 3452.375 | 0.20832 | 16665.6 | 64000 | 3452.375 | 16665.6 | 3131.025 | 3131.025 | 1350000 | 3131.025 | 0
2021052820 | 6 | 0.57056 | 85584 | 0.62387 | 0 | 0.27199 | 3399.875 | 0.01551 | 1240.8 | 64000 | 3399.875 | 1240.8 | 16943.325 | 13812.3 | 1350000 | 16943.325 | 0
2021052821 | 6 | 0.561 | 84150 | 0.62715 | 0 | 0.26814 | 3351.75 | 0 | 0 | 64000 | 3351.75 | 0 | 16798.25 | -145.075 | 1350000 | 16798.25 | 0
2021052822 | 6 | 0.54706 | 82059 | 0.62826 | 0 | 0.25893 | 3236.625 | 0 | 0 | 64000 | 3236.625 | 0 | 14822.375 | -1975.875 | 1350000 | 14822.375 | 0
2021052823 | 6 | 0.51747 | 77620.5 | 0.70013 | 0 | 0.25217 | 3152.125 | 0 | 0 | 64000 | 3152.125 | 0 | 10468.375 | -4354 | 1350000 | 10468.375 | 0
2021052824 | 6 | 0.48498 | 72747 | 0.79205 | 0 | 0.25596 | 3199.5 | 0 | 0 | 64000 | 3199.5 | 0 | 5547.5 | -4920.875 | 1350000 | 5547.5 | 0
2021052901 | 7 | 0.45668 | 68502 | 0.77504 | 0 | 0.22527 | 2815.875 | 0 | 0 | 64000 | 2815.875 | 0 | 1686.125 | -3861.375 | 1350000 | 1686.125 | 0
2021052902 | 7 | 0.43701 | 65551.5 | 0.663 | 0 | 0.19057 | 2382.125 | 0 | 0 | 64000 | 1551.5 | 0 | 0 | -1686.125 | 1350000 | 0 | 0
2021052903 | 7 | 0.42458 | 63687 | 0.69029 | 0 | 0.16606 | 2075.75 | 0 | 0 | 63687 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021052904 | 7 | 0.41738 | 62607 | 0.73494 | 0 | 0.12332 | 1541.5 | 0 | 0 | 62607 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021052905 | 7 | 0.41515 | 62272.5 | 0.73318 | 0 | 0.06694 | 836.75 | 0 | 0 | 62272.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021052906 | 7 | 0.41967 | 62950.5 | 0.66454 | 0 | 0.05141 | 642.625 | 0.00017 | 13.6 | 62950.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021052907 | 7 | 0.42678 | 64017 | 0.57881 | 0 | 0.04312 | 539 | 0.08105 | 6484 | 64000 | 17 | 0 | 0 | 0 | 1350000 | 0 | 0
2021052908 | 7 | 0.44287 | 66430.5 | 0.54237 | 0 | 0.04541 | 567.625 | 0.32383 | 25906.4 | 64000 | 567.625 | 1862.875 | 0 | 0 | 1350000 | 0 | 0
2021052909 | 7 | 0.46752 | 70128 | 0.51618 | 0 | 0.05116 | 639.5 | 0.52779 | 42223.2 | 64000 | 639.5 | 5488.5 | 0 | 0 | 1350000 | 0 | 0
2021052910 | 7 | 0.48667 | 73000.5 | 0.50137 | 0 | 0.04212 | 526.5 | 0.60694 | 48555.2 | 64000 | 526.5 | 8474 | 0 | 0 | 1350000 | 0 | 0
2021052911 | 7 | 0.49973 | 74959.5 | 0.44467 | 0 | 0.04074 | 509.25 | 0.64537 | 51629.6 | 64000 | 509.25 | 10450.25 | 0 | 0 | 1350000 | 0 | 0
2021052912 | 7 | 0.50378 | 75567 | 0.42323 | 0 | 0.04326 | 540.75 | 0.66628 | 53302.4 | 64000 | 540.75 | 11026.25 | 0 | 0 | 1350000 | 0 | 0
2021052913 | 7 | 0.5033 | 75495 | 0.43843 | 0 | 0.04235 | 529.375 | 0.68397 | 54717.6 | 64000 | 529.375 | 10965.625 | 0 | 0 | 1350000 | 0 | 0
2021052914 | 7 | 0.49743 | 74614.5 | 0.39755 | 0 | 0.03869 | 483.625 | 0.69958 | 55966.4 | 64000 | 483.625 | 10130.875 | 0 | 0 | 1350000 | 0 | 0
2021052915 | 7 | 0.49119 | 73678.5 | 0.36357 | 0 | 0.02436 | 304.5 | 0.69462 | 55569.6 | 64000 | 304.5 | 9374 | 0 | 0 | 1350000 | 0 | 0
2021052916 | 7 | 0.4877 | 73155 | 0.34501 | 0 | 0.01106 | 138.25 | 0.65389 | 52311.2 | 64000 | 138.25 | 9016.75 | 0 | 0 | 1350000 | 0 | 0
2021052917 | 7 | 0.48891 | 73336.5 | 0.35175 | 0 | 0.02033 | 254.125 | 0.5965 | 47720 | 64000 | 254.125 | 9082.375 | 0 | 0 | 1350000 | 0 | 0
2021052918 | 7 | 0.49212 | 73818 | 0.38453 | 0 | 0.02816 | 352 | 0.43476 | 34780.8 | 64000 | 352 | 9466 | 0 | 0 | 1350000 | 0 | 0
2021052919 | 7 | 0.49174 | 73761 | 0.37907 | 0 | 0.02563 | 320.375 | 0.15739 | 12591.2 | 64000 | 320.375 | 9440.625 | 0 | 0 | 1350000 | 0 | 0
2021052920 | 7 | 0.49067 | 73600.5 | 0.42187 | 0 | 0.01468 | 183.5 | 0.01106 | 884.8 | 64000 | 183.5 | 884.8 | 8532.2 | 8532.2 | 1350000 | 8532.2 | 0
2021052921 | 7 | 0.49365 | 74047.5 | 0.43341 | 0 | 0.01074 | 134.25 | 0 | 0 | 64000 | 134.25 | 0 | 9913.25 | 1381.05 | 1350000 | 9913.25 | 0
2021052922 | 7 | 0.49249 | 73873.5 | 0.37821 | 0 | 0.00999 | 124.875 | 0 | 0 | 64000 | 124.875 | 0 | 9748.625 | -164.625 | 1350000 | 9748.625 | 0
2021052923 | 7 | 0.47513 | 71269.5 | 0.36536 | 0 | 0.01043 | 130.375 | 0 | 0 | 64000 | 130.375 | 0 | 7139.125 | -2609.5 | 1350000 | 7139.125 | 0
2021052924 | 7 | 0.45218 | 67827 | 0.35662 | 0 | 0.01439 | 179.875 | 0 | 0 | 64000 | 179.875 | 0 | 3647.125 | -3492 | 1350000 | 3647.125 | 0
2021053001 | 1 | 0.43312 | 64968 | 0.36931 | 0 | 0.01826 | 228.25 | 0 | 0 | 64000 | 228.25 | 0 | 739.75 | -2907.375 | 1350000 | 739.75 | 0
2021053002 | 1 | 0.41749 | 62623.5 | 0.33527 | 0 | 0.02095 | 261.875 | 0 | 0 | 62623.5 | 0 | 0 | 0 | -739.75 | 1350000 | 0 | 0
2021053003 | 1 | 0.40988 | 61482 | 0.28535 | 0 | 0.01893 | 236.625 | 0 | 0 | 61482 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053004 | 1 | 0.40526 | 60789 | 0.25719 | 0 | 0.02107 | 263.375 | 0 | 0 | 60789 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053005 | 1 | 0.40421 | 60631.5 | 0.27003 | 0 | 0.01936 | 242 | 0 | 0 | 60631.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053006 | 1 | 0.40994 | 61491 | 0.23555 | 0 | 0.01793 | 224.125 | 0.00189 | 151.2 | 61491 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053007 | 1 | 0.41377 | 62065.5 | 0.14754 | 0 | 0.0158 | 197.5 | 0.06275 | 5020 | 62065.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053008 | 1 | 0.42827 | 64240.5 | 0.11623 | 0 | 0.01568 | 196 | 0.20238 | 16190.4 | 64000 | 196 | 44.5 | 0 | 0 | 1350000 | 0 | 0
2021053009 | 1 | 0.44872 | 67308 | 0.1421 | 0 | 0.01279 | 159.875 | 0.30632 | 24505.6 | 64000 | 159.875 | 3148.125 | 0 | 0 | 1350000 | 0 | 0
2021053010 | 1 | 0.46575 | 69862.5 | 0.1609 | 0 | 0.01113 | 139.125 | 0.35207 | 28165.6 | 64000 | 139.125 | 5723.375 | 0 | 0 | 1350000 | 0 | 0
2021053011 | 1 | 0.47543 | 71314.5 | 0.1388 | 0 | 0.01393 | 174.125 | 0.39822 | 31857.6 | 64000 | 174.125 | 7140.375 | 0 | 0 | 1350000 | 0 | 0
2021053012 | 1 | 0.48107 | 72160.5 | 0.12287 | 0 | 0.01677 | 209.625 | 0.43928 | 35142.4 | 64000 | 209.625 | 7950.875 | 0 | 0 | 1350000 | 0 | 0
2021053013 | 1 | 0.482 | 72300 | 0.09063 | 0 | 0.01934 | 241.75 | 0.43377 | 34701.6 | 64000 | 241.75 | 8058.25 | 0 | 0 | 1350000 | 0 | 0
2021053014 | 1 | 0.47952 | 71928 | 0.08923 | 0 | 0.02196 | 274.5 | 0.43046 | 34436.8 | 64000 | 274.5 | 7653.5 | 0 | 0 | 1350000 | 0 | 0
2021053015 | 1 | 0.4752 | 71280 | 0.06697 | 0 | 0.02181 | 272.625 | 0.38234 | 30587.2 | 64000 | 272.625 | 7007.375 | 0 | 0 | 1350000 | 0 | 0
2021053016 | 1 | 0.47234 | 70851 | 0.05993 | 0 | 0.0118 | 147.5 | 0.29612 | 23689.6 | 64000 | 147.5 | 6703.5 | 0 | 0 | 1350000 | 0 | 0
2021053017 | 1 | 0.47579 | 71368.5 | 0.09456 | 0 | 0.02068 | 258.5 | 0.19823 | 15858.4 | 64000 | 258.5 | 7110 | 0 | 0 | 1350000 | 0 | 0
2021053018 | 1 | 0.4808 | 72120 | 0.13825 | 0 | 0.03619 | 452.375 | 0.11348 | 9078.4 | 64000 | 452.375 | 7667.625 | 0 | 0 | 1350000 | 0 | 0
2021053019 | 1 | 0.48144 | 72216 | 0.15089 | 0 | 0.03792 | 474 | 0.03791 | 3032.8 | 64000 | 474 | 3032.8 | 4709.2 | 4709.2 | 1350000 | 4709.2 | 0
2021053020 | 1 | 0.48172 | 72258 | 0.14509 | 0 | 0.03423 | 427.875 | 0.00326 | 260.8 | 64000 | 427.875 | 260.8 | 7569.325 | 2860.125 | 1350000 | 7569.325 | 0
2021053021 | 1 | 0.48407 | 72610.5 | 0.09779 | 0 | 0.03207 | 400.875 | 0 | 0 | 64000 | 400.875 | 0 | 8209.625 | 640.3 | 1350000 | 8209.625 | 0
2021053022 | 1 | 0.48562 | 72843 | 0.06057 | 0 | 0.04152 | 519 | 0 | 0 | 64000 | 519 | 0 | 8324 | 114.375 | 1350000 | 8324 | 0
2021053023 | 1 | 0.46798 | 70197 | 0.12278 | 0 | 0.03886 | 485.75 | 0 | 0 | 64000 | 485.75 | 0 | 5711.25 | -2612.75 | 1350000 | 5711.25 | 0
2021053024 | 1 | 0.44746 | 67119 | 0.20237 | 0 | 0.04007 | 500.875 | 0 | 0 | 64000 | 500.875 | 0 | 2618.125 | -3093.125 | 1350000 | 2618.125 | 0
2021053101 | 2 | 0.42717 | 64075.5 | 0.25131 | 0 | 0.04705 | 588.125 | 0 | 0 | 64000 | 75.5 | 0 | 0 | -2618.125 | 1350000 | 0 | 0
2021053102 | 2 | 0.41217 | 61825.5 | 0.2651 | 0 | 0.04706 | 588.25 | 0 | 0 | 61825.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053103 | 2 | 0.40414 | 60621 | 0.34635 | 0 | 0.04563 | 570.375 | 0 | 0 | 60621 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053104 | 2 | 0.40053 | 60079.5 | 0.44557 | 0 | 0.03533 | 441.625 | 0 | 0 | 60079.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053105 | 2 | 0.40376 | 60564 | 0.50216 | 0 | 0.03423 | 427.875 | 0 | 0 | 60564 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053106 | 2 | 0.41037 | 61555.5 | 0.5951 | 0 | 0.02922 | 365.25 | 0.00135 | 108 | 61555.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053107 | 2 | 0.41577 | 62365.5 | 0.61583 | 0 | 0.01918 | 239.75 | 0.05514 | 4411.2 | 62365.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053108 | 2 | 0.4245 | 63675 | 0.56729 | 0 | 0.02027 | 253.375 | 0.14092 | 11273.6 | 63675 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021053109 | 2 | 0.43806 | 65709 | 0.4289 | 0 | 0.01953 | 244.125 | 0.17802 | 14241.6 | 64000 | 244.125 | 1464.875 | 0 | 0 | 1350000 | 0 | 0
2021053110 | 2 | 0.45193 | 67789.5 | 0.40499 | 0 | 0.01628 | 203.5 | 0.24341 | 19472.8 | 64000 | 203.5 | 3586 | 0 | 0 | 1350000 | 0 | 0
2021053111 | 2 | 0.46163 | 69244.5 | 0.36964 | 0 | 0.01277 | 159.625 | 0.31243 | 24994.4 | 64000 | 159.625 | 5084.875 | 0 | 0 | 1350000 | 0 | 0
2021053112 | 2 | 0.46688 | 70032 | 0.36184 | 0 | 0.0133 | 166.25 | 0.36771 | 29416.8 | 64000 | 166.25 | 5865.75 | 0 | 0 | 1350000 | 0 | 0
2021053113 | 2 | 0.46872 | 70308 | 0.3196 | 0 | 0.01915 | 239.375 | 0.38725 | 30980 | 64000 | 239.375 | 6068.625 | 0 | 0 | 1350000 | 0 | 0
2021053114 | 2 | 0.46856 | 70284 | 0.28461 | 0 | 0.01776 | 222 | 0.38144 | 30515.2 | 64000 | 222 | 6062 | 0 | 0 | 1350000 | 0 | 0
2021053115 | 2 | 0.46949 | 70423.5 | 0.25614 | 0 | 0.01855 | 231.875 | 0.32717 | 26173.6 | 64000 | 231.875 | 6191.625 | 0 | 0 | 1350000 | 0 | 0
2021053116 | 2 | 0.47522 | 71283 | 0.23077 | 0 | 0.02136 | 267 | 0.28412 | 22729.6 | 64000 | 267 | 7016 | 0 | 0 | 1350000 | 0 | 0
2021053117 | 2 | 0.48726 | 73089 | 0.22307 | 0 | 0.02305 | 288.125 | 0.18712 | 14969.6 | 64000 | 288.125 | 8800.875 | 0 | 0 | 1350000 | 0 | 0
2021053118 | 2 | 0.50162 | 75243 | 0.15229 | 0 | 0.02242 | 280.25 | 0.11352 | 9081.6 | 64000 | 280.25 | 9081.6 | 1881.15 | 1881.15 | 1350000 | 1881.15 | 0
2021053119 | 2 | 0.50908 | 76362 | 0.09011 | 0 | 0.02735 | 341.875 | 0.04731 | 3784.8 | 64000 | 341.875 | 3784.8 | 8235.325 | 6354.175 | 1350000 | 8235.325 | 0
2021053120 | 2 | 0.51041 | 76561.5 | 0.04324 | 0 | 0.03423 | 427.875 | 0.00436 | 348.8 | 64000 | 427.875 | 348.8 | 11784.825 | 3549.5 | 1350000 | 11784.825 | 0
2021053121 | 2 | 0.51196 | 76794 | 0.03648 | 0 | 0.0308 | 385 | 0 | 0 | 64000 | 385 | 0 | 12409 | 624.175 | 1350000 | 12409 | 0
2021053122 | 2 | 0.51118 | 76677 | 0.06114 | 0 | 0.02884 | 360.5 | 0 | 0 | 64000 | 360.5 | 0 | 12316.5 | -92.5 | 1350000 | 12316.5 | 0
2021053123 | 2 | 0.48549 | 72823.5 | 0.07386 | 0 | 0.03418 | 427.25 | 0 | 0 | 64000 | 427.25 | 0 | 8396.25 | -3920.25 | 1350000 | 8396.25 | 0
2021053124 | 2 | 0.45365 | 68047.5 | 0.10056 | 0 | 0.03339 | 417.375 | 0 | 0 | 64000 | 417.375 | 0 | 3630.125 | -4766.125 | 1350000 | 3630.125 | 0
2021060101 | 3 | 0.42836 | 64254 | 0.06109 | 0 | 0.0248 | 310 | 0 | 0 | 64000 | 254 | 0 | 0 | -3630.125 | 1350000 | 0 | 0
2021060102 | 3 | 0.41291 | 61936.5 | 0.06429 | 0 | 0.01779 | 222.375 | 0 | 0 | 61936.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021060103 | 3 | 0.40481 | 60721.5 | 0.05332 | 0 | 0.01245 | 155.625 | 0 | 0 | 60721.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021060104 | 3 | 0.40204 | 60306 | 0.03424 | 0 | 0.01324 | 165.5 | 0 | 0 | 60306 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021060105 | 3 | 0.40924 | 61386 | 0.02775 | 0 | 0.01523 | 190.375 | 0 | 0 | 61386 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021060106 | 3 | 0.43167 | 64750.5 | 0.03241 | 0 | 0.0122 | 152.5 | 0.00143 | 114.4 | 64000 | 152.5 | 114.4 | 483.6 | 483.6 | 1350000 | 483.6 | 0
2021060107 | 3 | 0.46431 | 69646.5 | 0.0296 | 0 | 0.01226 | 153.25 | 0.06673 | 5338.4 | 64000 | 153.25 | 5338.4 | 154.85 | -328.75 | 1350000 | 154.85 | 0
2021060108 | 3 | 0.498 | 74700 | 0.00817 | 0 | 0.01204 | 150.5 | 0.29 | 23200 | 64000 | 150.5 | 10549.5 | 0 | -154.85 | 1350000 | 0 | 0
2021060109 | 3 | 0.51854 | 77781 | 0.00157 | 0 | 0.01463 | 182.875 | 0.51729 | 41383.2 | 64000 | 182.875 | 13598.125 | 0 | 0 | 1350000 | 0 | 0
2021060110 | 3 | 0.53313 | 79969.5 | 0.00394 | 0 | 0.01929 | 241.125 | 0.59272 | 47417.6 | 64000 | 241.125 | 15728.375 | 0 | 0 | 1350000 | 0 | 0
2021060111 | 3 | 0.54861 | 82291.5 | 0.00513 | 0 | 0.02299 | 287.375 | 0.62644 | 50115.2 | 64000 | 287.375 | 18004.125 | 0 | 0 | 1350000 | 0 | 0
2021060112 | 3 | 0.56164 | 84246 | 0.00095 | 0 | 0.03053 | 381.625 | 0.63976 | 51180.8 | 64000 | 381.625 | 19864.375 | 0 | 0 | 1350000 | 0 | 0
2021060113 | 3 | 0.5744 | 86160 | 0.01669 | 0 | 0.03585 | 448.125 | 0.63411 | 50728.8 | 64000 | 448.125 | 21711.875 | 0 | 0 | 1350000 | 0 | 0
2021060114 | 3 | 0.58851 | 88276.5 | 0.02254 | 0 | 0.03998 | 499.75 | 0.65101 | 52080.8 | 64000 | 499.75 | 23776.75 | 0 | 0 | 1350000 | 0 | 0
2021060115 | 3 | 0.59684 | 89526 | 0.01947 | 0 | 0.04184 | 523 | 0.6777 | 54216 | 64000 | 523 | 25003 | 0 | 0 | 1350000 | 0 | 0
2021060116 | 3 | 0.60281 | 90421.5 | 0.01919 | 0 | 0.04026 | 503.25 | 0.62355 | 49884 | 64000 | 503.25 | 25918.25 | 0 | 0 | 1350000 | 0 | 0
2021060117 | 3 | 0.61189 | 91783.5 | 0.02808 | 0 | 0.03932 | 491.5 | 0.5362 | 42896 | 64000 | 491.5 | 27292 | 0 | 0 | 1350000 | 0 | 0
2021060118 | 3 | 0.61658 | 92487 | 0.02744 | 0 | 0.05384 | 673 | 0.3793 | 30344 | 64000 | 673 | 27814 | 0 | 0 | 1350000 | 0 | 0
2021060119 | 3 | 0.6112 | 91680 | 0.01541 | 0 | 0.07484 | 935.5 | 0.15125 | 12100 | 64000 | 935.5 | 12100 | 14644.5 | 14644.5 | 1350000 | 14644.5 | 0
2021060120 | 3 | 0.60223 | 90334.5 | 0.01187 | 0 | 0.07606 | 950.75 | 0.01337 | 1069.6 | 64000 | 950.75 | 1069.6 | 24314.15 | 9669.65 | 1350000 | 24314.15 | 0
2021060121 | 3 | 0.59674 | 89511 | 0.04037 | 0 | 0.08254 | 1031.75 | 0 | 0 | 64000 | 1031.75 | 0 | 24479.25 | 165.1 | 1350000 | 24479.25 | 0
2021060122 | 3 | 0.58561 | 87841.5 | 0.06827 | 0 | 0.09244 | 1155.5 | 0 | 0 | 64000 | 1155.5 | 0 | 22686 | -1793.25 | 1350000 | 22686 | 0
2021060123 | 3 | 0.5516 | 82740 | 0.08085 | 0 | 0.10528 | 1316 | 0 | 0 | 64000 | 1316 | 0 | 17424 | -5262 | 1350000 | 17424 | 0
2021060124 | 3 | 0.51043 | 76564.5 | 0.10224 | 0 | 0.11041 | 1380.125 | 0 | 0 | 64000 | 1380.125 | 0 | 11184.375 | -6239.625 | 1350000 | 11184.375 | 0
2021060201 | 4 | 0.47857 | 71785.5 | 0.13219 | 0 | 0.12483 | 1560.375 | 0 | 0 | 64000 | 1560.375 | 0 | 6225.125 | -4959.25 | 1350000 | 6225.125 | 0
2021060202 | 4 | 0.45557 | 68335.5 | 0.13144 | 0 | 0.15262 | 1907.75 | 0 | 0 | 64000 | 1907.75 | 0 | 2427.75 | -3797.375 | 1350000 | 2427.75 | 0
2021060203 | 4 | 0.44148 | 66222 | 0.13468 | 0 | 0.16627 | 2078.375 | 0 | 0 | 64000 | 2078.375 | 0 | 143.625 | -2284.125 | 1350000 | 143.625 | 0
2021060204 | 4 | 0.4347 | 65205 | 0.12984 | 0 | 0.1817 | 2271.25 | 0 | 0 | 64000 | 1205 | 0 | 0 | -143.625 | 1350000 | 0 | 0
2021060205 | 4 | 0.43855 | 65782.5 | 0.10411 | 0 | 0.1976 | 2470 | 0 | 0 | 64000 | 1782.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021060206 | 4 | 0.45746 | 68619 | 0.12937 | 0 | 0.20601 | 2575.125 | 0.00099 | 79.2 | 64000 | 2575.125 | 79.2 | 1964.675 | 1964.675 | 1350000 | 1964.675 | 0
2021060207 | 4 | 0.48672 | 73008 | 0.08835 | 0 | 0.25437 | 3179.625 | 0.06908 | 5526.4 | 64000 | 3179.625 | 5526.4 | 301.975 | -1662.7 | 1350000 | 301.975 | 0
2021060208 | 4 | 0.51854 | 77781 | 0.06263 | 0 | 0.2939 | 3673.75 | 0.20588 | 16470.4 | 64000 | 3673.75 | 10107.25 | 0 | -301.975 | 1350000 | 0 | 0
2021060209 | 4 | 0.54226 | 81339 | 0.06408 | 0 | 0.30137 | 3767.125 | 0.32282 | 25825.6 | 64000 | 3767.125 | 13571.875 | 0 | 0 | 1350000 | 0 | 0
2021060210 | 4 | 0.55863 | 83794.5 | 0.08135 | 0 | 0.29027 | 3628.375 | 0.38883 | 31106.4 | 64000 | 3628.375 | 16166.125 | 0 | 0 | 1350000 | 0 | 0
2021060211 | 4 | 0.57355 | 86032.5 | 0.09864 | 0 | 0.25363 | 3170.375 | 0.43333 | 34666.4 | 64000 | 3170.375 | 18862.125 | 0 | 0 | 1350000 | 0 | 0
2021060212 | 4 | 0.58734 | 88101 | 0.131 | 0 | 0.21215 | 2651.875 | 0.40534 | 32427.2 | 64000 | 2651.875 | 21449.125 | 0 | 0 | 1350000 | 0 | 0
2021060213 | 4 | 0.60289 | 90433.5 | 0.17673 | 0 | 0.16854 | 2106.75 | 0.29527 | 23621.6 | 64000 | 2106.75 | 23621.6 | 705.15 | 705.15 | 1350000 | 705.15 | 0
2021060214 | 4 | 0.61801 | 92701.5 | 0.2029 | 0 | 0.11095 | 1386.875 | 0.32817 | 26253.6 | 64000 | 1386.875 | 26253.6 | 1061.025 | 355.875 | 1350000 | 1061.025 | 0
2021060215 | 4 | 0.62644 | 93966 | 0.25038 | 0 | 0.07699 | 962.375 | 0.261 | 20880 | 64000 | 962.375 | 20880 | 8123.625 | 7062.6 | 1350000 | 8123.625 | 0
2021060216 | 4 | 0.63135 | 94702.5 | 0.20467 | 0 | 0.06792 | 849 | 0.21628 | 17302.4 | 64000 | 849 | 17302.4 | 12551.1 | 4427.475 | 1350000 | 12551.1 | 0
2021060217 | 4 | 0.6336 | 95040 | 0.21998 | 0 | 0.06654 | 831.75 | 0.17667 | 14133.6 | 64000 | 831.75 | 14133.6 | 16074.65 | 3523.55 | 1350000 | 16074.65 | 0
2021060218 | 4 | 0.63553 | 95329.5 | 0.22129 | 0 | 0.11168 | 1396 | 0.13637 | 10909.6 | 64000 | 1396 | 10909.6 | 19023.9 | 2949.25 | 1350000 | 19023.9 | 0
2021060219 | 4 | 0.62643 | 93964.5 | 0.17251 | 0 | 0.18466 | 2308.25 | 0.05728 | 4582.4 | 64000 | 2308.25 | 4582.4 | 23073.85 | 4049.95 | 1350000 | 23073.85 | 0
2021060220 | 4 | 0.61288 | 91932 | 0.26857 | 0 | 0.20259 | 2532.375 | 0.00671 | 536.8 | 64000 | 2532.375 | 536.8 | 24862.825 | 1788.975 | 1350000 | 24862.825 | 0
2021060221 | 4 | 0.60561 | 90841.5 | 0.45505 | 0 | 0.21224 | 2653 | 0 | 0 | 64000 | 2653 | 0 | 24188.5 | -674.325 | 1350000 | 24188.5 | 0
2021060222 | 4 | 0.59364 | 89046 | 0.54987 | 0 | 0.2203 | 2753.75 | 0 | 0 | 64000 | 2753.75 | 0 | 22292.25 | -1896.25 | 1350000 | 22292.25 | 0
2021060223 | 4 | 0.55994 | 83991 | 0.60456 | 0 | 0.21923 | 2740.375 | 0 | 0 | 64000 | 2740.375 | 0 | 17250.625 | -5041.625 | 1350000 | 17250.625 | 0
2021060224 | 4 | 0.52027 | 78040.5 | 0.61082 | 0 | 0.21801 | 2725.125 | 0 | 0 | 64000 | 2725.125 | 0 | 11315.375 | -5935.25 | 1350000 | 11315.375 | 0
2021060301 | 5 | 0.48765 | 73147.5 | 0.61739 | 0 | 0.20073 | 2509.125 | 0 | 0 | 64000 | 2509.125 | 0 | 6638.375 | -4677 | 1350000 | 6638.375 | 0
2021060302 | 5 | 0.4656 | 69840 | 0.61202 | 0 | 0.16486 | 2060.75 | 0 | 0 | 64000 | 2060.75 | 0 | 3779.25 | -2859.125 | 1350000 | 3779.25 | 0
2021060303 | 5 | 0.45206 | 67809 | 0.62881 | 0 | 0.13834 | 1729.25 | 0 | 0 | 64000 | 1729.25 | 0 | 2079.75 | -1699.5 | 1350000 | 2079.75 | 0
2021060304 | 5 | 0.44698 | 67047 | 0.61368 | 0 | 0.11595 | 1449.375 | 0 | 0 | 64000 | 1449.375 | 0 | 1597.625 | -482.125 | 1350000 | 1597.625 | 0
2021060305 | 5 | 0.45285 | 67927.5 | 0.59751 | 0 | 0.09119 | 1139.875 | 0 | 0 | 64000 | 1139.875 | 0 | 2787.625 | 1190 | 1350000 | 2787.625 | 0
2021060306 | 5 | 0.47256 | 70884 | 0.55223 | 0 | 0.06608 | 826 | 0.00129 | 103.2 | 64000 | 826 | 103.2 | 5954.8 | 3167.175 | 1350000 | 5954.8 | 0
2021060307 | 5 | 0.50561 | 75841.5 | 0.57178 | 0 | 0.06323 | 790.375 | 0.061 | 4880 | 64000 | 790.375 | 4880 | 6171.125 | 216.325 | 1350000 | 6171.125 | 0
2021060308 | 5 | 0.54005 | 81007.5 | 0.52146 | 0 | 0.05966 | 745.75 | 0.23604 | 18883.2 | 64000 | 745.75 | 16261.75 | 0 | -6171.125 | 1350000 | 0 | 0
2021060309 | 5 | 0.56736 | 85104 | 0.47757 | 0 | 0.04906 | 613.25 | 0.38098 | 30478.4 | 64000 | 613.25 | 20490.75 | 0 | 0 | 1350000 | 0 | 0
2021060310 | 5 | 0.58643 | 87964.5 | 0.44672 | 0 | 0.04058 | 507.25 | 0.48963 | 39170.4 | 64000 | 507.25 | 23457.25 | 0 | 0 | 1350000 | 0 | 0
2021060311 | 5 | 0.60429 | 90643.5 | 0.40267 | 0 | 0.04122 | 515.25 | 0.58414 | 46731.2 | 64000 | 515.25 | 26128.25 | 0 | 0 | 1350000 | 0 | 0
2021060312 | 5 | 0.6196 | 92940 | 0.37867 | 0 | 0.03931 | 491.375 | 0.61518 | 49214.4 | 64000 | 491.375 | 28448.625 | 0 | 0 | 1350000 | 0 | 0
2021060313 | 5 | 0.63528 | 95292 | 0.37552 | 0 | 0.03406 | 425.75 | 0.64182 | 51345.6 | 64000 | 425.75 | 30866.25 | 0 | 0 | 1350000 | 0 | 0
2021060314 | 5 | 0.65174 | 97761 | 0.35542 | 0 | 0.02034 | 254.25 | 0.64722 | 51777.6 | 64000 | 254.25 | 33506.75 | 0 | 0 | 1350000 | 0 | 0
2021060315 | 5 | 0.66182 | 99273 | 0.4015 | 0 | 0.01877 | 234.625 | 0.59682 | 47745.6 | 64000 | 234.625 | 35038.375 | 0 | 0 | 1350000 | 0 | 0
2021060316 | 5 | 0.67092 | 100638 | 0.37162 | 0 | 0.0064 | 80 | 0.56744 | 45395.2 | 64000 | 80 | 36558 | 0 | 0 | 1350000 | 0 | 0
2021060317 | 5 | 0.67639 | 101458.5 | 0.32798 | 0 | 0.00424 | 53 | 0.46095 | 36876 | 64000 | 53 | 36876 | 529.5 | 529.5 | 1350000 | 529.5 | 0
2021060318 | 5 | 0.67922 | 101883 | 0.29376 | 0 | 0.00976 | 122 | 0.29429 | 23543.2 | 64000 | 122 | 23543.2 | 14217.8 | 13688.3 | 1350000 | 14217.8 | 0
2021060319 | 5 | 0.67193 | 100789.5 | 0.27198 | 0 | 0.01748 | 218.5 | 0.11911 | 9528.8 | 64000 | 218.5 | 9528.8 | 27042.2 | 12824.4 | 1348424.05 | 27042.2 | 0
2021060320 | 5 | 0.65587 | 98380.5 | 0.34464 | 0 | 0.02585 | 323.125 | 0.01071 | 856.8 | 64000 | 323.125 | 856.8 | 33200.575 | 6158.375 | 1340689.725 | 33200.575 | 0
2021060321 | 5 | 0.64243 | 96364.5 | 0.33373 | 0 | 0.03563 | 445.375 | 0 | 0 | 64000 | 445.375 | 0 | 31919.125 | -1281.45 | 1334236.85 | 31919.125 | 0
2021060322 | 5 | 0.62655 | 93982.5 | 0.34933 | 0 | 0.04333 | 541.625 | 0 | 0 | 64000 | 541.625 | 0 | 29440.875 | -2478.25 | 1330262.225 | 29440.875 | 0
2021060323 | 5 | 0.59369 | 89053.5 | 0.36385 | 0 | 0.03775 | 471.875 | 0 | 0 | 64000 | 471.875 | 0 | 24581.625 | -4859.25 | 1331146.85 | 24581.625 | 0
2021060324 | 5 | 0.55502 | 83253 | 0.41225 | 0 | 0.04137 | 517.125 | 0 | 0 | 64000 | 517.125 | 0 | 18735.875 | -5845.75 | 1337877.225 | 18735.875 | 0
2021060401 | 6 | 0.52 | 78000 | 0.461 | 0 | 0.0506 | 632.5 | 0 | 0 | 64000 | 632.5 | 0 | 13367.5 | -5368.375 | 1349975.975 | 13367.5 | 0
2021060402 | 6 | 0.49628 | 74442 | 0.48966 | 0 | 0.08306 | 1038.25 | 0 | 0 | 64000 | 1038.25 | 0 | 9403.75 | -3963.75 | 1350000 | 9403.75 | 0
2021060403 | 6 | 0.47979 | 71968.5 | 0.49916 | 0 | 0.09063 | 1132.875 | 0 | 0 | 64000 | 1132.875 | 0 | 6835.625 | -2568.125 | 1350000 | 6835.625 | 0
2021060404 | 6 | 0.47098 | 70647 | 0.43148 | 0 | 0.08043 | 1005.375 | 0 | 0 | 64000 | 1005.375 | 0 | 5641.625 | -1194 | 1350000 | 5641.625 | 0
2021060405 | 6 | 0.47462 | 71193 | 0.39799 | 0 | 0.08266 | 1033.25 | 0 | 0 | 64000 | 1033.25 | 0 | 6159.75 | 518.125 | 1350000 | 6159.75 | 0
2021060406 | 6 | 0.4929 | 73935 | 0.37316 | 0 | 0.10664 | 1333 | 0.00058 | 46.4 | 64000 | 1333 | 46.4 | 8555.6 | 2395.85 | 1350000 | 8555.6 | 0
2021060407 | 6 | 0.52239 | 78358.5 | 0.25578 | 0 | 0.10592 | 1324 | 0.06571 | 5256.8 | 64000 | 1324 | 5256.8 | 7777.7 | -777.9 | 1350000 | 7777.7 | 0
2021060408 | 6 | 0.55781 | 83671.5 | 0.17703 | 0 | 0.11857 | 1482.125 | 0.29892 | 23913.6 | 64000 | 1482.125 | 18189.375 | 0 | -7777.7 | 1350000 | 0 | 0
2021060409 | 6 | 0.58608 | 87912 | 0.19731 | 0 | 0.11906 | 1488.25 | 0.49726 | 39780.8 | 64000 | 1488.25 | 22423.75 | 0 | 0 | 1350000 | 0 | 0
2021060410 | 6 | 0.60857 | 91285.5 | 0.19824 | 0 | 0.13469 | 1683.625 | 0.5626 | 45008 | 64000 | 1683.625 | 25601.875 | 0 | 0 | 1350000 | 0 | 0
2021060411 | 6 | 0.63318 | 94977 | 0.16311 | 0 | 0.15975 | 1996.875 | 0.59763 | 47810.4 | 64000 | 1996.875 | 28980.125 | 0 | 0 | 1350000 | 0 | 0
2021060412 | 6 | 0.65497 | 98245.5 | 0.17525 | 0 | 0.17853 | 2231.625 | 0.62825 | 50260 | 64000 | 2231.625 | 32013.875 | 0 | 0 | 1350000 | 0 | 0
2021060413 | 6 | 0.67384 | 101076 | 0.21396 | 0 | 0.17393 | 2174.125 | 0.66778 | 53422.4 | 64000 | 2174.125 | 34901.875 | 0 | 0 | 1350000 | 0 | 0
2021060414 | 6 | 0.69338 | 104007 | 0.27313 | 0 | 0.16199 | 2024.875 | 0.66471 | 53176.8 | 64000 | 2024.875 | 37982.125 | 0 | 0 | 1350000 | 0 | 0
2021060415 | 6 | 0.71389 | 107083.5 | 0.32043 | 0 | 0.17196 | 2149.5 | 0.66078 | 52862.4 | 64000 | 2149.5 | 40934 | 0 | 0 | 1350000 | 0 | 0
2021060416 | 6 | 0.7334 | 110010 | 0.34283 | 0 | 0.18506 | 2313.25 | 0.66195 | 52956 | 64000 | 2313.25 | 43696.75 | 0 | 0 | 1350000 | 0 | 0
2021060417 | 6 | 0.74327 | 111490.5 | 0.35135 | 0 | 0.1934 | 2417.5 | 0.51103 | 40882.4 | 64000 | 2417.5 | 40882.4 | 4190.6 | 4190.6 | 1350000 | 4190.6 | 0
2021060418 | 6 | 0.74632 | 111948 | 0.32708 | 0 | 0.2448 | 3060 | 0.35424 | 28339.2 | 64000 | 3060 | 28339.2 | 16548.8 | 12358.2 | 1350000 | 16548.8 | 0
2021060419 | 6 | 0.7398 | 110970 | 0.31584 | 0 | 0.30426 | 3803.25 | 0.15638 | 12510.4 | 64000 | 3803.25 | 12510.4 | 30656.35 | 14107.55 | 1344809.9 | 30656.35 | 0
2021060420 | 6 | 0.72079 | 108118.5 | 0.25867 | 0 | 0.31592 | 3949 | 0.01798 | 1438.4 | 64000 | 3949 | 1438.4 | 38731.1 | 8074.75 | 1331545.05 | 38731.1 | 0
2021060421 | 6 | 0.6914 | 103710 | 0.23303 | 0 | 0.30596 | 3824.5 | 0 | 0 | 64000 | 3824.5 | 0 | 35885.5 | -2845.6 | 1321125.8 | 35885.5 | 0
2021060422 | 6 | 0.66883 | 100324.5 | 0.32995 | 0 | 0.28123 | 3515.375 | 0 | 0 | 64000 | 3515.375 | 0 | 32809.125 | -3076.375 | 1313782.925 | 32809.125 | 0
2021060423 | 6 | 0.63028 | 94542 | 0.46903 | 0 | 0.25509 | 3188.625 | 0 | 0 | 64000 | 3188.625 | 0 | 27353.375 | -5455.75 | 1311895.8 | 27353.375 | 0
2021060424 | 6 | 0.58232 | 87348 | 0.60501 | 0 | 0.22925 | 2865.625 | 0 | 0 | 64000 | 2865.625 | 0 | 20482.375 | -6871 | 1316879.675 | 20482.375 | 0
2021060501 | 7 | 0.53817 | 80725.5 | 0.73637 | 0 | 0.19224 | 2403 | 0 | 0 | 64000 | 2403 | 0 | 14322.5 | -6159.875 | 1328023.425 | 14322.5 | 0
2021060502 | 7 | 0.50606 | 75909 | 0.79428 | 0 | 0.22608 | 2826 | 0 | 0 | 64000 | 2826 | 0 | 9083 | -5239.5 | 1344406.675 | 9083 | 0
2021060503 | 7 | 0.4818 | 72270 | 0.83854 | 0 | 0.26097 | 3262.125 | 0 | 0 | 64000 | 3262.125 | 0 | 5007.875 | -4075.125 | 1350000 | 5007.875 | 0
2021060504 | 7 | 0.46823 | 70234.5 | 0.86264 | 0 | 0.32112 | 4014 | 0 | 0 | 64000 | 4014 | 0 | 2220.5 | -2787.375 | 1350000 | 2220.5 | 0
2021060505 | 7 | 0.4608 | 69120 | 0.87796 | 0 | 0.2876 | 3595 | 0 | 0 | 64000 | 3595 | 0 | 1525 | -695.5 | 1350000 | 1525 | 0
2021060506 | 7 | 0.46093 | 69139.5 | 0.84771 | 0 | 0.25637 | 3204.625 | 0.00281 | 224.8 | 64000 | 3204.625 | 224.8 | 1710.075 | 185.075 | 1350000 | 1710.075 | 0
2021060507 | 7 | 0.46737 | 70105.5 | 0.8296 | 0 | 0.22046 | 2755.75 | 0.05527 | 4421.6 | 64000 | 2755.75 | 3349.75 | 0 | -1710.075 | 1350000 | 0 | 0
2021060508 | 7 | 0.49512 | 74268 | 0.74927 | 0 | 0.23051 | 2881.375 | 0.23083 | 18466.4 | 64000 | 2881.375 | 7386.625 | 0 | 0 | 1350000 | 0 | 0
2021060509 | 7 | 0.53693 | 80539.5 | 0.66153 | 0 | 0.26179 | 3272.375 | 0.41028 | 32822.4 | 64000 | 3272.375 | 13267.125 | 0 | 0 | 1350000 | 0 | 0
2021060510 | 7 | 0.58241 | 87361.5 | 0.60275 | 0 | 0.33049 | 4131.125 | 0.41498 | 33198.4 | 64000 | 4131.125 | 19230.375 | 0 | 0 | 1350000 | 0 | 0
2021060511 | 7 | 0.62637 | 93955.5 | 0.56402 | 0 | 0.38113 | 4764.125 | 0.53167 | 42533.6 | 64000 | 4764.125 | 25191.375 | 0 | 0 | 1350000 | 0 | 0
2021060512 | 7 | 0.66938 | 100407 | 0.48979 | 0 | 0.37751 | 4718.875 | 0.58448 | 46758.4 | 64000 | 4718.875 | 31688.125 | 0 | 0 | 1350000 | 0 | 0
2021060513 | 7 | 0.70394 | 105591 | 0.45481 | 0 | 0.42868 | 5358.5 | 0.60131 | 48104.8 | 64000 | 5358.5 | 36232.5 | 0 | 0 | 1350000 | 0 | 0
2021060514 | 7 | 0.73264 | 109896 | 0.44607 | 0 | 0.42081 | 5260.125 | 0.61012 | 48809.6 | 64000 | 5260.125 | 40635.875 | 0 | 0 | 1350000 | 0 | 0
2021060515 | 7 | 0.75705 | 113557.5 | 0.45937 | 0 | 0.41451 | 5181.375 | 0.61731 | 49384.8 | 64000 | 5181.375 | 44376.125 | 0 | 0 | 1350000 | 0 | 0
2021060516 | 7 | 0.77926 | 116889 | 0.45931 | 0 | 0.4333 | 5416.25 | 0.58592 | 46873.6 | 64000 | 5416.25 | 46873.6 | 599.15 | 599.15 | 1350000 | 599.15 | 0
2021060517 | 7 | 0.79933 | 119899.5 | 0.38154 | 0 | 0.39433 | 4929.125 | 0.51343 | 41074.4 | 64000 | 4929.125 | 41074.4 | 9895.975 | 9296.825 | 1350000 | 9895.975 | 0
2021060518 | 7 | 0.81069 | 121603.5 | 0.33218 | 0 | 0.38173 | 4771.625 | 0.36814 | 29451.2 | 64000 | 4771.625 | 29451.2 | 23380.675 | 13484.7 | 1350000 | 23380.675 | 0
2021060519 | 7 | 0.80773 | 121159.5 | 0.30717 | 0 | 0.32232 | 4029 | 0.14375 | 11500 | 64000 | 4029 | 11500 | 41630.5 | 18249.825 | 1333835.75 | 41630.5 | 0
2021060520 | 7 | 0.78564 | 117846 | 0.26801 | 0 | 0.26657 | 3332.125 | 0.01661 | 1328.8 | 64000 | 3332.125 | 1328.8 | 49185.075 | 7554.575 | 1310116.925 | 49185.075 | 0
2021060521 | 7 | 0.75185 | 112777.5 | 0.37348 | 0 | 0.24401 | 3050.125 | 0 | 0 | 64000 | 3050.125 | 0 | 45727.375 | -3457.7 | 1289855.8 | 45727.375 | 0
2021060522 | 7 | 0.72179 | 108268.5 | 0.46061 | 0 | 0.20208 | 2526 | 0 | 0 | 64000 | 2526 | 0 | 41742.5 | -3984.875 | 1273579.55 | 41742.5 | 0
2021060523 | 7 | 0.67705 | 101557.5 | 0.50347 | 0 | 0.19533 | 2441.625 | 0 | 0 | 64000 | 2441.625 | 0 | 35115.875 | -6626.625 | 1263929.925 | 35115.875 | 0
2021060524 | 7 | 0.62406 | 93609 | 0.52435 | 0 | 0.24581 | 3072.625 | 0 | 0 | 64000 | 3072.625 | 0 | 26536.375 | -8579.5 | 1262859.8 | 26536.375 | 0
2021060601 | 1 | 0.57668 | 86502 | 0.541 | 0 | 0.2504 | 3130 | 0 | 0 | 64000 | 3130 | 0 | 19372 | -7164.375 | 1268954.05 | 19372 | 0
2021060602 | 1 | 0.53791 | 80686.5 | 0.50127 | 0 | 0.20666 | 2583.25 | 0 | 0 | 64000 | 2583.25 | 0 | 14103.25 | -5268.75 | 1280317.05 | 14103.25 | 0
2021060603 | 1 | 0.51086 | 76629 | 0.43573 | 0 | 0.16309 | 2038.625 | 0 | 0 | 64000 | 2038.625 | 0 | 10590.375 | -3512.875 | 1295192.925 | 10590.375 | 0
2021060604 | 1 | 0.49118 | 73677 | 0.36293 | 0 | 0.12676 | 1584.5 | 0 | 0 | 64000 | 1584.5 | 0 | 8092.5 | -2497.875 | 1312566.675 | 8092.5 | 0
2021060605 | 1 | 0.47815 | 71722.5 | 0.32242 | 0 | 0.10692 | 1336.5 | 0 | 0 | 64000 | 1336.5 | 0 | 6386 | -1706.5 | 1331646.925 | 6386 | 0
2021060606 | 1 | 0.47256 | 70884 | 0.27023 | 0 | 0.06776 | 847 | 0.00147 | 117.6 | 64000 | 847 | 117.6 | 5919.4 | -466.6 | 1350000 | 5919.4 | 0
2021060607 | 1 | 0.47146 | 70719 | 0.21914 | 0 | 0.03807 | 475.875 | 0.06472 | 5177.6 | 64000 | 475.875 | 5177.6 | 1065.525 | -4853.875 | 1350000 | 1065.525 | 0
2021060608 | 1 | 0.49743 | 74614.5 | 0.13951 | 0 | 0.03857 | 482.125 | 0.24161 | 19328.8 | 64000 | 482.125 | 10132.375 | 0 | -1065.525 | 1350000 | 0 | 0
2021060609 | 1 | 0.54461 | 81691.5 | 0.05706 | 0 | 0.04791 | 598.875 | 0.34514 | 27611.2 | 64000 | 598.875 | 17092.625 | 0 | 0 | 1350000 | 0 | 0
2021060610 | 1 | 0.59949 | 89923.5 | 0.03244 | 0 | 0.04779 | 597.375 | 0.41853 | 33482.4 | 64000 | 597.375 | 25326.125 | 0 | 0 | 1350000 | 0 | 0
2021060611 | 1 | 0.65608 | 98412 | 0.094 | 0 | 0.05811 | 726.375 | 0.54394 | 43515.2 | 64000 | 726.375 | 33685.625 | 0 | 0 | 1350000 | 0 | 0
2021060612 | 1 | 0.7053 | 105795 | 0.18629 | 0 | 0.03915 | 489.375 | 0.58577 | 46861.6 | 64000 | 489.375 | 41305.625 | 0 | 0 | 1350000 | 0 | 0
2021060613 | 1 | 0.74358 | 111537 | 0.16921 | 0 | 0.03299 | 412.375 | 0.65483 | 52386.4 | 64000 | 412.375 | 47124.625 | 0 | 0 | 1350000 | 0 | 0
2021060614 | 1 | 0.77385 | 116077.5 | 0.14444 | 0 | 0.0385 | 481.25 | 0.66699 | 53359.2 | 64000 | 481.25 | 51596.25 | 0 | 0 | 1350000 | 0 | 0
2021060615 | 1 | 0.79704 | 119556 | 0.15051 | 0 | 0.04322 | 540.25 | 0.68608 | 54886.4 | 64000 | 540.25 | 54886.4 | 129.35 | 129.35 | 1350000 | 129.35 | 0
2021060616 | 1 | 0.81414 | 122121 | 0.13986 | 0 | 0.01985 | 248.125 | 0.66386 | 53108.8 | 64000 | 248.125 | 53108.8 | 4764.075 | 4634.725 | 1350000 | 4764.075 | 0
2021060617 | 1 | 0.83096 | 124644 | 0.11815 | 0 | 0.02234 | 279.25 | 0.57725 | 46180 | 64000 | 279.25 | 46180 | 14184.75 | 9420.675 | 1350000 | 14184.75 | 0
2021060618 | 1 | 0.84378 | 126567 | 0.10119 | 0 | 0.06296 | 787 | 0.41884 | 33507.2 | 64000 | 787 | 33507.2 | 28272.8 | 14088.05 | 1347193.45 | 28272.8 | 0
2021060619 | 1 | 0.84127 | 126190.5 | 0.09719 | 0 | 0.06792 | 849 | 0.16679 | 13343.2 | 64000 | 849 | 13343.2 | 47998.3 | 19725.5 | 1324661.4 | 47998.3 | 0
2021060620 | 1 | 0.82297 | 123445.5 | 0.08957 | 0 | 0.07221 | 902.625 | 0.0174 | 1392 | 64000 | 902.625 | 1392 | 57150.875 | 9152.575 | 1292976.775 | 57150.875 | 0
2021060621 | 1 | 0.79365 | 119047.5 | 0.11862 | 0 | 0.07383 | 922.875 | 0 | 0 | 64000 | 922.875 | 0 | 54124.625 | -3026.25 | 1264318.4 | 54124.625 | 0
2021060622 | 1 | 0.76839 | 115258.5 | 0.15679 | 0 | 0.09249 | 1156.125 | 0 | 0 | 64000 | 1156.125 | 0 | 50102.375 | -4022.25 | 1239682.275 | 50102.375 | 0
2021060623 | 1 | 0.72165 | 108247.5 | 0.18166 | 0 | 0.10131 | 1266.375 | 0 | 0 | 64000 | 1266.375 | 0 | 42981.125 | -7121.25 | 1222167.4 | 42981.125 | 0
2021060624 | 1 | 0.66716 | 100074 | 0.15867 | 0 | 0.07699 | 962.375 | 0 | 0 | 64000 | 962.375 | 0 | 35111.625 | -7869.5 | 1212522.025 | 35111.625 | 0
2021060701 | 2 | 0.6191 | 92865 | 0.14409 | 0 | 0.05877 | 734.625 | 0 | 0 | 64000 | 734.625 | 0 | 28130.375 | -6981.25 | 1209857.9 | 28130.375 | 0
2021060702 | 2 | 0.58289 | 87433.5 | 0.16802 | 0 | 0.04926 | 615.75 | 0 | 0 | 64000 | 615.75 | 0 | 22817.75 | -5312.625 | 1212506.4 | 22817.75 | 0
2021060703 | 2 | 0.5586 | 83790 | 0.17535 | 0 | 0.04853 | 606.625 | 0 | 0 | 64000 | 606.625 | 0 | 19183.375 | -3634.375 | 1218789.275 | 19183.375 | 0
2021060704 | 2 | 0.54562 | 81843 | 0.17601 | 0 | 0.05186 | 648.25 | 0 | 0 | 64000 | 648.25 | 0 | 17194.75 | -1988.625 | 1227060.775 | 17194.75 | 0
2021060705 | 2 | 0.54379 | 81568.5 | 0.1426 | 0 | 0.05489 | 686.125 | 0 | 0 | 64000 | 686.125 | 0 | 16882.375 | -312.375 | 1235644.65 | 16882.375 | 0
2021060706 | 2 | 0.55899 | 83848.5 | 0.09315 | 0 | 0.05029 | 628.625 | 0.00211 | 168.8 | 64000 | 628.625 | 168.8 | 19051.075 | 2168.7 | 1242059.825 | 19051.075 | 0
2021060707 | 2 | 0.59261 | 88891.5 | 0.07406 | 0 | 0.04809 | 601.125 | 0.08359 | 6687.2 | 64000 | 601.125 | 6687.2 | 17603.175 | -1447.9 | 1249922.9 | 17603.175 | 0
2021060708 | 2 | 0.6404 | 96060 | 0.05221 | 0 | 0.06739 | 842.375 | 0.31294 | 25035.2 | 64000 | 842.375 | 25035.2 | 6182.425 | -11420.75 | 1269206.725 | 6182.425 | 0
2021060709 | 2 | 0.68316 | 102474 | 0.02639 | 0 | 0.08005 | 1000.625 | 0.47196 | 37756.8 | 64000 | 1000.625 | 37473.375 | 0 | -6182.425 | 1294672.975 | 0 | 0
2021060710 | 2 | 0.72473 | 108709.5 | 0.01038 | 0 | 0.07384 | 923 | 0.54334 | 43467.2 | 64000 | 923 | 43467.2 | 319.3 | 319.3 | 1319819.925 | 319.3 | 0
2021060711 | 2 | 0.76374 | 114561 | 0.00662 | 0 | 0.05806 | 725.75 | 0.58024 | 46419.2 | 64000 | 725.75 | 46419.2 | 3416.05 | 3096.75 | 1341870.125 | 3416.05 | 0
2021060712 | 2 | 0.80018 | 120027 | 0.02557 | 0 | 0.02886 | 360.75 | 0.61675 | 49340 | 64000 | 360.75 | 49340 | 6326.25 | 2910.2 | 1350000 | 6326.25 | 0
2021060713 | 2 | 0.83513 | 125269.5 | 0.05586 | 0 | 0.01631 | 203.875 | 0.64302 | 51441.6 | 64000 | 203.875 | 51441.6 | 9624.025 | 3297.775 | 1350000 | 9624.025 | 0
2021060714 | 2 | 0.85845 | 128767.5 | 0.09765 | 0 | 0.02092 | 261.5 | 0.66118 | 52894.4 | 64000 | 261.5 | 52894.4 | 11611.6 | 1987.575 | 1350000 | 11611.6 | 0
2021060715 | 2 | 0.87257 | 130885.5 | 0.11079 | 0 | 0.01277 | 159.625 | 0.67281 | 53824.8 | 64000 | 159.625 | 53824.8 | 12901.075 | 1289.475 | 1350000 | 12901.075 | 0
2021060716 | 2 | 0.88038 | 132057 | 0.09198 | 0 | 0.00517 | 64.625 | 0.62629 | 50103.2 | 64000 | 64.625 | 50103.2 | 17889.175 | 4988.1 | 1350000 | 17889.175 | 0
2021060717 | 2 | 0.88557 | 132835.5 | 0.07173 | 0 | 0.01072 | 134 | 0.54963 | 43970.4 | 64000 | 134 | 43970.4 | 24731.1 | 6841.925 | 1350000 | 24731.1 | 0
2021060718 | 2 | 0.88373 | 132559.5 | 0.05215 | 0 | 0.01879 | 234.875 | 0.39088 | 31270.4 | 64000 | 234.875 | 31270.4 | 37054.225 | 12323.125 | 1338412.025 | 37054.225 | 0
2021060719 | 2 | 0.86863 | 130294.5 | 0.05716 | 0 | 0.0203 | 253.75 | 0.16036 | 12828.8 | 64000 | 253.75 | 12828.8 | 53211.95 | 16157.725 | 1310666.325 | 53211.95 | 0
2021060720 | 2 | 0.84332 | 126498 | 0.06509 | 0 | 0.02237 | 279.625 | 0.01562 | 1249.6 | 64000 | 279.625 | 1249.6 | 60968.775 | 7756.825 | 1275163.8 | 60968.775 | 0
2021060721 | 2 | 0.81439 | 122158.5 | 0.10634 | 0 | 0.02515 | 314.375 | 0 | 0 | 64000 | 314.375 | 0 | 57844.125 | -3124.65 | 1242785.925 | 57844.125 | 0
2021060722 | 2 | 0.78868 | 118302 | 0.15201 | 0 | 0.0208 | 260 | 0 | 0 | 64000 | 260 | 0 | 54042 | -3802.125 | 1214210.175 | 54042 | 0
2021060723 | 2 | 0.73607 | 110410.5 | 0.19743 | 0 | 0.01688 | 211 | 0 | 0 | 64000 | 211 | 0 | 46199.5 | -7842.5 | 1193476.925 | 46199.5 | 0
2021060724 | 2 | 0.67894 | 101841 | 0.24379 | 0 | 0.02181 | 272.625 | 0 | 0 | 64000 | 272.625 | 0 | 37568.375 | -8631.125 | 1181374.8 | 37568.375 | 0
2021060801 | 3 | 0.63091 | 94636.5 | 0.28064 | 0 | 0.02332 | 291.5 | 0 | 0 | 64000 | 291.5 | 0 | 30345 | -7223.375 | 1176496.05 | 30345 | 0
2021060802 | 3 | 0.59649 | 89473.5 | 0.38075 | 0 | 0.02923 | 365.375 | 0 | 0 | 64000 | 365.375 | 0 | 25108.125 | -5236.875 | 1176854.175 | 25108.125 | 0
2021060803 | 3 | 0.57132 | 85698 | 0.4153 | 0 | 0.02799 | 349.875 | 0 | 0 | 64000 | 349.875 | 0 | 21348.125 | -3760 | 1180972.3 | 21348.125 | 0
2021060804 | 3 | 0.5564 | 83460 | 0.41278 | 0 | 0.02545 | 318.125 | 0 | 0 | 64000 | 318.125 | 0 | 19141.875 | -2206.25 | 1187296.675 | 19141.875 | 0
2021060805 | 3 | 0.55472 | 83208 | 0.39405 | 0 | 0.02265 | 283.125 | 0 | 0 | 64000 | 283.125 | 0 | 18924.875 | -217 | 1193838.05 | 18924.875 | 0
2021060806 | 3 | 0.57023 | 85534.5 | 0.34659 | 0 | 0.02503 | 312.875 | 0.00148 | 118.4 | 64000 | 312.875 | 118.4 | 21103.225 | 2178.35 | 1198201.075 | 21103.225 | 0
2021060807 | 3 | 0.6018 | 90270 | 0.26014 | 0 | 0.02966 | 370.75 | 0.04557 | 3645.6 | 64000 | 370.75 | 3645.6 | 22253.65 | 1150.425 | 1201413.675 | 22253.65 | 0
2021060808 | 3 | 0.64863 | 97294.5 | 0.18351 | 0 | 0.02395 | 299.375 | 0.16451 | 13160.8 | 64000 | 299.375 | 13160.8 | 19834.325 | -2419.325 | 1207045.6 | 19834.325 | 0
2021060809 | 3 | 0.69094 | 103641 | 0.16462 | 0 | 0.0249 | 311.25 | 0.27367 | 21893.6 | 64000 | 311.25 | 21893.6 | 17436.15 | -2398.175 | 1215075.7 | 17436.15 | 0
2021060810 | 3 | 0.73066 | 109599 | 0.11915 | 0 | 0.03258 | 407.25 | 0.38877 | 31101.6 | 64000 | 407.25 | 31101.6 | 14090.15 | -3346 | 1226451.8 | 14090.15 | 0
2021060811 | 3 | 0.77263 | 115894.5 | 0.11278 | 0 | 0.03159 | 394.875 | 0.48093 | 38474.4 | 64000 | 394.875 | 38474.4 | 13025.225 | -1064.925 | 1238892.825 | 13025.225 | 0
2021060812 | 3 | 0.81477 | 122215.5 | 0.06149 | 0 | 0.02327 | 290.875 | 0.53677 | 42941.6 | 64000 | 290.875 | 42941.6 | 14983.025 | 1957.8 | 1249376.05 | 14983.025 | 0
2021060813 | 3 | 0.84918 | 127377 | 0.04899 | 0 | 0.01517 | 189.625 | 0.59121 | 47296.8 | 64000 | 189.625 | 47296.8 | 15890.575 | 907.55 | 1258951.725 | 15890.575 | 0
2021060814 | 3 | 0.87374 | 131061 | 0.09525 | 0 | 0.00946 | 118.25 | 0.57995 | 46396 | 64000 | 118.25 | 46396 | 20546.75 | 4656.175 | 1263871.225 | 20546.75 | 0
2021060815 | 3 | 0.88185 | 132277.5 | 0.12529 | 0 | 0.00562 | 70.25 | 0.52631 | 42104.8 | 64000 | 70.25 | 42104.8 | 26102.45 | 5555.7 | 1263235.025 | 26102.45 | 0
2021060816 | 3 | 0.8825 | 132375 | 0.07006 | 0 | 0.00552 | 69 | 0.47967 | 38373.6 | 64000 | 69 | 38373.6 | 29932.4 | 3829.95 | 1258768.875 | 29932.4 | 0
2021060817 | 3 | 0.87906 | 131859 | 0.06721 | 0 | 0.01111 | 138.875 | 0.44533 | 35626.4 | 64000 | 138.875 | 35626.4 | 32093.725 | 2161.325 | 1252141.4 | 32093.725 | 0
2021060818 | 3 | 0.87159 | 130738.5 | 0.09771 | 0 | 0.0223 | 278.75 | 0.36776 | 29420.8 | 64000 | 278.75 | 29420.8 | 37038.95 | 4945.225 | 1240568.7 | 37038.95 | 0
2021060819 | 3 | 0.85204 | 127806 | 0.07427 | 0 | 0.03985 | 498.125 | 0.16218 | 12974.4 | 64000 | 498.125 | 12974.4 | 50333.475 | 13294.525 | 1215701.475 | 50333.475 | 0
2021060820 | 3 | 0.8256 | 123840 | 0.08045 | 0 | 0.04018 | 502.25 | 0.01764 | 1411.2 | 64000 | 502.25 | 1411.2 | 57926.55 | 7593.075 | 1183241.175 | 57926.55 | 0
2021060821 | 3 | 0.79645 | 119467.5 | 0.03458 | 0 | 0.04675 | 584.375 | 0 | 0 | 64000 | 584.375 | 0 | 54883.125 | -3043.425 | 1153824.3 | 54883.125 | 0
2021060822 | 3 | 0.76874 | 115311 | 0.04486 | 0 | 0.06005 | 750.625 | 0 | 0 | 64000 | 750.625 | 0 | 50560.375 | -4322.75 | 1128730.175 | 50560.375 | 0
2021060823 | 3 | 0.71799 | 107698.5 | 0.11621 | 0 | 0.06457 | 807.125 | 0 | 0 | 64000 | 807.125 | 0 | 42891.375 | -7669 | 1111305.05 | 42891.375 | 0
2021060824 | 3 | 0.66297 | 99445.5 | 0.11506 | 0 | 0.06362 | 795.25 | 0 | 0 | 64000 | 795.25 | 0 | 34650.25 | -8241.125 | 1102121.05 | 34650.25 | 0
2021060901 | 4 | 0.61423 | 92134.5 | 0.222 | 0 | 0.06779 | 847.375 | 0 | 0 | 64000 | 847.375 | 0 | 27287.125 | -7363.125 | 1100300.175 | 27287.125 | 0
2021060902 | 4 | 0.57978 | 86967 | 0.31461 | 0 | 0.05861 | 732.625 | 0 | 0 | 64000 | 732.625 | 0 | 22234.375 | -5052.75 | 1103532.05 | 22234.375 | 0
2021060903 | 4 | 0.55506 | 83259 | 0.33535 | 0 | 0.05747 | 718.375 | 0 | 0 | 64000 | 718.375 | 0 | 18540.625 | -3693.75 | 1110457.675 | 18540.625 | 0
2021060904 | 4 | 0.54149 | 81223.5 | 0.44169 | 0 | 0.04995 | 624.375 | 0 | 0 | 64000 | 624.375 | 0 | 16599.125 | -1941.5 | 1119324.8 | 16599.125 | 0
2021060905 | 4 | 0.54016 | 81024 | 0.46222 | 0 | 0.04223 | 527.875 | 0 | 0 | 64000 | 527.875 | 0 | 16496.125 | -103 | 1128294.925 | 16496.125 | 0
2021060906 | 4 | 0.5559 | 83385 | 0.44333 | 0 | 0.04071 | 508.875 | 0.00148 | 118.4 | 64000 | 508.875 | 118.4 | 18757.725 | 2261.6 | 1135003.45 | 18757.725 | 0
2021060907 | 4 | 0.58591 | 87886.5 | 0.40032 | 0 | 0.05165 | 645.625 | 0.06418 | 5134.4 | 64000 | 645.625 | 5134.4 | 18106.475 | -651.25 | 1142363.225 | 18106.475 | 0
2021060908 | 4 | 0.62957 | 94435.5 | 0.35272 | 0 | 0.06328 | 791 | 0.23784 | 19027.2 | 64000 | 791 | 19027.2 | 10617.3 | -7489.175 | 1157212.175 | 10617.3 | 0
2021060909 | 4 | 0.67022 | 100533 | 0.14505 | 0 | 0.07119 | 889.875 | 0.42406 | 33924.8 | 64000 | 889.875 | 33924.8 | 1718.325 | -8898.975 | 1180960.1 | 1718.325 | 0
2021060910 | 4 | 0.70757 | 106135.5 | 0.07116 | 0 | 0.0749 | 936.25 | 0.46685 | 37348 | 64000 | 936.25 | 37348 | 3851.25 | 2132.925 | 1202575.1 | 3851.25 | 0
2021060911 | 4 | 0.74745 | 112117.5 | 0.04695 | 0 | 0.08309 | 1038.625 | 0.54301 | 43440.8 | 64000 | 1038.625 | 43440.8 | 3638.075 | -213.175 | 1224403.275 | 3638.075 | 0
2021060912 | 4 | 0.78533 | 117799.5 | 0.0371 | 0 | 0.06809 | 851.125 | 0.59991 | 47992.8 | 64000 | 851.125 | 47992.8 | 4955.575 | 1317.5 | 1244913.95 | 4955.575 | 0
2021060913 | 4 | 0.81484 | 122226 | 0.03451 | 0 | 0.05108 | 638.5 | 0.62471 | 49976.8 | 64000 | 638.5 | 49976.8 | 7610.7 | 2655.125 | 1262769.5 | 7610.7 | 0
2021060914 | 4 | 0.83833 | 125749.5 | 0.08884 | 0 | 0.03987 | 498.375 | 0.65594 | 52475.2 | 64000 | 498.375 | 52475.2 | 8775.925 | 1165.225 | 1279459.825 | 8775.925 | 0
2021060915 | 4 | 0.85382 | 128073 | 0.12519 | 0 | 0.03198 | 399.75 | 0.60443 | 48354.4 | 64000 | 399.75 | 48354.4 | 15318.85 | 6542.925 | 1289607.225 | 15318.85 | 0
2021060916 | 4 | 0.85955 | 128932.5 | 0.13199 | 0 | 0.03858 | 482.25 | 0.56389 | 45111.2 | 64000 | 482.25 | 45111.2 | 19339.05 | 4020.2 | 1295734.425 | 19339.05 | 0
2021060917 | 4 | 0.86142 | 129213 | 0.08217 | 0 | 0.0528 | 660 | 0.43255 | 34604 | 64000 | 660 | 34604 | 29949 | 10609.95 | 1291251.675 | 29949 | 0
2021060918 | 4 | 0.8562 | 128430 | 0.10965 | 0 | 0.08783 | 1097.875 | 0.27646 | 22116.8 | 64000 | 1097.875 | 22116.8 | 41215.325 | 11266.325 | 1275502.6 | 41215.325 | 0
2021060919 | 4 | 0.83556 | 125334 | 0.19184 | 0 | 0.1391 | 1738.75 | 0.11057 | 8845.6 | 64000 | 1738.75 | 8845.6 | 50749.65 | 9534.325 | 1250219.2 | 50749.65 | 0
2021060920 | 4 | 0.80729 | 121093.5 | 0.17271 | 0 | 0.13902 | 1737.75 | 0.0136 | 1088 | 64000 | 1737.75 | 1088 | 54267.75 | 3518.1 | 1221417.7 | 54267.75 | 0
2021060921 | 4 | 0.78092 | 117138 | 0.09904 | 0 | 0.14699 | 1837.375 | 0 | 0 | 64000 | 1837.375 | 0 | 51300.625 | -2967.125 | 1195583.325 | 51300.625 | 0
2021060922 | 4 | 0.75376 | 113064 | 0.10502 | 0 | 0.16286 | 2035.75 | 0 | 0 | 64000 | 2035.75 | 0 | 47028.25 | -4272.375 | 1174021.325 | 47028.25 | 0
2021060923 | 4 | 0.70563 | 105844.5 | 0.15542 | 0 | 0.17337 | 2167.125 | 0 | 0 | 64000 | 2167.125 | 0 | 39677.375 | -7350.875 | 1159810.2 | 39677.375 | 0
2021060924 | 4 | 0.64985 | 97477.5 | 0.16546 | 0 | 0.20392 | 2549 | 0 | 0 | 64000 | 2549 | 0 | 30928.5 | -8748.875 | 1154347.95 | 30928.5 | 0
2021061001 | 5 | 0.60328 | 90492 | 0.19297 | 0 | 0.2349 | 2936.25 | 0 | 0 | 64000 | 2936.25 | 0 | 23555.75 | -7372.75 | 1156258.45 | 23555.75 | 0
2021061002 | 5 | 0.56801 | 85201.5 | 0.19305 | 0 | 0.24719 | 3089.875 | 0 | 0 | 64000 | 3089.875 | 0 | 18111.625 | -5444.125 | 1163613.075 | 18111.625 | 0
2021061003 | 5 | 0.54463 | 81694.5 | 0.17412 | 0 | 0.28493 | 3561.625 | 0 | 0 | 64000 | 3561.625 | 0 | 14132.875 | -3978.75 | 1174946.45 | 14132.875 | 0
2021061004 | 5 | 0.53013 | 79519.5 | 0.17611 | 0 | 0.29084 | 3635.5 | 0 | 0 | 64000 | 3635.5 | 0 | 11884 | -2248.875 | 1188528.7 | 11884 | 0
2021061005 | 5 | 0.52876 | 79314 | 0.17549 | 0 | 0.3161 | 3951.25 | 0 | 0 | 64000 | 3951.25 | 0 | 11362.75 | -521.25 | 1202632.2 | 11362.75 | 0
2021061006 | 5 | 0.5445 | 81675 | 0.17824 | 0 | 0.32186 | 4023.25 | 0.00033 | 26.4 | 64000 | 4023.25 | 26.4 | 13625.35 | 2262.6 | 1214473.1 | 13625.35 | 0
2021061007 | 5 | 0.57363 | 86044.5 | 0.15015 | 0 | 0.35672 | 4459 | 0.05802 | 4641.6 | 64000 | 4459 | 4641.6 | 12943.9 | -681.45 | 1226995.45 | 12943.9 | 0
2021061008 | 5 | 0.6173 | 92595 | 0.14271 | 0 | 0.36473 | 4559.125 | 0.22184 | 17747.2 | 64000 | 4559.125 | 17747.2 | 6288.675 | -6655.225 | 1246173.025 | 6288.675 | 0
2021061009 | 5 | 0.6604 | 99060 | 0.12186 | 0 | 0.37788 | 4723.5 | 0.40435 | 32348 | 64000 | 4723.5 | 30336.5 | 0 | -6288.675 | 1271639.275 | 0 | 0
2021061010 | 5 | 0.69961 | 104941.5 | 0.10513 | 0 | 0.38018 | 4752.25 | 0.46755 | 37404 | 64000 | 4752.25 | 36189.25 | 0 | 0 | 1297105.525 | 0 | 0
2021061011 | 5 | 0.73644 | 110466 | 0.09817 | 0 | 0.34782 | 4347.75 | 0.53916 | 43132.8 | 64000 | 4347.75 | 42118.25 | 0 | 0 | 1322571.775 | 0 | 0
2021061012 | 5 | 0.77064 | 115596 | 0.08677 | 0 | 0.26357 | 3294.625 | 0.57794 | 46235.2 | 64000 | 3294.625 | 46235.2 | 2066.175 | 2066.175 | 1345971.85 | 2066.175 | 0
2021061013 | 5 | 0.80051 | 120076.5 | 0.08346 | 0 | 0.18894 | 2361.75 | 0.59298 | 47438.4 | 64000 | 2361.75 | 47438.4 | 6276.35 | 4210.175 | 1350000 | 6276.35 | 0
2021061014 | 5 | 0.82305 | 123457.5 | 0.09527 | 0 | 0.16237 | 2029.625 | 0.6263 | 50104 | 64000 | 2029.625 | 50104 | 7323.875 | 1047.525 | 1350000 | 7323.875 | 0
2021061015 | 5 | 0.83746 | 125619 | 0.123 | 0 | 0.15953 | 1994.125 | 0.65737 | 52589.6 | 64000 | 1994.125 | 52589.6 | 7035.275 | -288.6 | 1350000 | 7035.275 | 0
2021061016 | 5 | 0.84394 | 126591 | 0.12017 | 0 | 0.13174 | 1646.75 | 0.59484 | 47587.2 | 64000 | 1646.75 | 47587.2 | 13357.05 | 6321.775 | 1350000 | 13357.05 | 0
2021061017 | 5 | 0.84259 | 126388.5 | 0.13517 | 0 | 0.12137 | 1517.125 | 0.49364 | 39491.2 | 64000 | 1517.125 | 39491.2 | 21380.175 | 8023.125 | 1350000 | 21380.175 | 0
2021061018 | 5 | 0.83205 | 124807.5 | 0.25249 | 0 | 0.18335 | 2291.875 | 0.31976 | 25580.8 | 64000 | 2291.875 | 25580.8 | 32934.825 | 11554.65 | 1342531.425 | 32934.825 | 0
2021061019 | 5 | 0.80958 | 121437 | 0.32312 | 0 | 0.26321 | 3290.125 | 0.16864 | 13491.2 | 64000 | 3290.125 | 13491.2 | 40655.675 | 7720.85 | 1327342 | 40655.675 | 0
2021061020 | 5 | 0.77968 | 116952 | 0.4333 | 0 | 0.2884 | 3605 | 0.02253 | 1802.4 | 64000 | 3605 | 1802.4 | 47544.6 | 6888.925 | 1305263.65 | 47544.6 | 0
2021061021 | 5 | 0.75111 | 112666.5 | 0.54168 | 0 | 0.28645 | 3580.625 | 0 | 0 | 64000 | 3580.625 | 0 | 45085.875 | -2458.725 | 1285644.025 | 45085.875 | 0
2021061022 | 5 | 0.72378 | 108567 | 0.5609 | 0 | 0.28489 | 3561.125 | 0 | 0 | 64000 | 3561.125 | 0 | 41005.875 | -4080 | 1270104.4 | 41005.875 | 0
2021061023 | 5 | 0.67817 | 101725.5 | 0.61006 | 0 | 0.30525 | 3815.625 | 0 | 0 | 64000 | 3815.625 | 0 | 33909.875 | -7096 | 1261660.775 | 33909.875 | 0
2021061024 | 5 | 0.62422 | 93633 | 0.67708 | 0 | 0.30413 | 3801.625 | 0 | 0 | 64000 | 3801.625 | 0 | 25831.375 | -8078.5 | 1261295.65 | 25831.375 | 0
2021061101 | 6 | 0.57877 | 86815.5 | 0.75494 | 0 | 0.28309 | 3538.625 | 0 | 0 | 64000 | 3538.625 | 0 | 19276.875 | -6554.5 | 1267485.025 | 19276.875 | 0
2021061102 | 6 | 0.54568 | 81852 | 0.71703 | 0 | 0.23455 | 2931.875 | 0 | 0 | 64000 | 2931.875 | 0 | 14920.125 | -4356.75 | 1278031.15 | 14920.125 | 0
2021061103 | 6 | 0.52371 | 78556.5 | 0.6272 | 0 | 0.20353 | 2544.125 | 0 | 0 | 64000 | 2544.125 | 0 | 12012.375 | -2907.75 | 1291485.025 | 12012.375 | 0
2021061104 | 6 | 0.51026 | 76539 | 0.55642 | 0 | 0.19294 | 2411.75 | 0 | 0 | 64000 | 2411.75 | 0 | 10127.25 | -1885.125 | 1306824.025 | 10127.25 | 0
2021061105 | 6 | 0.51053 | 76579.5 | 0.42105 | 0 | 0.14114 | 1764.25 | 0 | 0 | 64000 | 1764.25 | 0 | 10815.25 | 688 | 1321475.025 | 10815.25 | 0
2021061106 | 6 | 0.52598 | 78897 | 0.43394 | 0 | 0.08988 | 1123.5 | 0.0029 | 232 | 64000 | 1123.5 | 232 | 13541.5 | 2726.25 | 1333399.775 | 13541.5 | 0
2021061107 | 6 | 0.55227 | 82840.5 | 0.51106 | 0 | 0.07552 | 944 | 0.08238 | 6590.4 | 64000 | 944 | 6590.4 | 11306.1 | -2235.4 | 1347559.925 | 11306.1 | 0
2021061108 | 6 | 0.58888 | 88332 | 0.51179 | 0 | 0.07645 | 955.625 | 0.31353 | 25082.4 | 64000 | 955.625 | 23376.375 | 0 | -11306.1 | 1350000 | 0 | 0
2021061109 | 6 | 0.62226 | 93339 | 0.44956 | 0 | 0.06953 | 869.125 | 0.50949 | 40759.2 | 64000 | 869.125 | 28469.875 | 0 | 0 | 1350000 | 0 | 0
2021061110 | 6 | 0.65203 | 97804.5 | 0.3797 | 0 | 0.06101 | 762.625 | 0.60147 | 48117.6 | 64000 | 762.625 | 33041.875 | 0 | 0 | 1350000 | 0 | 0
2021061111 | 6 | 0.67832 | 101748 | 0.31387 | 0 | 0.03911 | 488.875 | 0.6243 | 49944 | 64000 | 488.875 | 37259.125 | 0 | 0 | 1350000 | 0 | 0
2021061112 | 6 | 0.70107 | 105160.5 | 0.30906 | 0 | 0.02425 | 303.125 | 0.6197 | 49576 | 64000 | 303.125 | 40857.375 | 0 | 0 | 1350000 | 0 | 0
2021061113 | 6 | 0.7187 | 107805 | 0.26251 | 0 | 0.01187 | 148.375 | 0.66395 | 53116 | 64000 | 148.375 | 43656.625 | 0 | 0 | 1350000 | 0 | 0
2021061114 | 6 | 0.7328 | 109920 | 0.28308 | 0 | 0.01258 | 157.25 | 0.6861 | 54888 | 64000 | 157.25 | 45762.75 | 0 | 0 | 1350000 | 0 | 0
2021061115 | 6 | 0.73738 | 110607 | 0.25853 | 0 | 0.0258 | 322.5 | 0.66203 | 52962.4 | 64000 | 322.5 | 46284.5 | 0 | 0 | 1350000 | 0 | 0
2021061116 | 6 | 0.73656 | 110484 | 0.16389 | 0 | 0.02846 | 355.75 | 0.61931 | 49544.8 | 64000 | 355.75 | 46128.25 | 0 | 0 | 1350000 | 0 | 0
2021061117 | 6 | 0.73136 | 109704 | 0.16326 | 0 | 0.02843 | 355.375 | 0.47535 | 38028 | 64000 | 355.375 | 38028 | 7320.625 | 7320.625 | 1350000 | 7320.625 | 0
2021061118 | 6 | 0.7284 | 109260 | 0.14474 | 0 | 0.07468 | 933.5 | 0.31292 | 25033.6 | 64000 | 933.5 | 25033.6 | 19292.9 | 11972.275 | 1350000 | 19292.9 | 0
2021061119 | 6 | 0.71446 | 107169 | 0.14902 | 0 | 0.12761 | 1595.125 | 0.14301 | 11440.8 | 64000 | 1595.125 | 11440.8 | 30133.075 | 10840.175 | 1345333.175 | 30133.075 | 0
2021061120 | 6 | 0.69671 | 104506.5 | 0.21199 | 0 | 0.16279 | 2034.875 | 0.01832 | 1465.6 | 64000 | 2034.875 | 1465.6 | 37006.025 | 6872.95 | 1333793.4 | 37006.025 | 0
2021061121 | 6 | 0.67893 | 101839.5 | 0.22235 | 0 | 0.16698 | 2087.25 | 0 | 0 | 64000 | 2087.25 | 0 | 35752.25 | -1253.775 | 1323507.4 | 35752.25 | 0
2021061122 | 6 | 0.66026 | 99039 | 0.15159 | 0 | 0.16355 | 2044.375 | 0 | 0 | 64000 | 2044.375 | 0 | 32994.625 | -2757.625 | 1315979.025 | 32994.625 | 0
2021061123 | 6 | 0.62971 | 94456.5 | 0.13602 | 0 | 0.15026 | 1878.25 | 0 | 0 | 64000 | 1878.25 | 0 | 28578.25 | -4416.375 | 1312867.025 | 28578.25 | 0
2021061124 | 6 | 0.58552 | 87828 | 0.16451 | 0 | 0.14762 | 1845.25 | 0 | 0 | 64000 | 1845.25 | 0 | 21982.75 | -6595.5 | 1316350.525 | 21982.75 | 0
2021061201 | 7 | 0.54454 | 81681 | 0.07905 | 0 | 0.16189 | 2023.625 | 0 | 0 | 64000 | 2023.625 | 0 | 15657.375 | -6325.375 | 1326159.4 | 15657.375 | 0
2021061202 | 7 | 0.51495 | 77242.5 | 0.03145 | 0 | 0.16359 | 2044.875 | 0 | 0 | 64000 | 2044.875 | 0 | 11197.625 | -4459.75 | 1340428.025 | 11197.625 | 0
2021061203 | 7 | 0.49371 | 74056.5 | 0.0099 | 0 | 0.14952 | 1869 | 0 | 0 | 64000 | 1869 | 0 | 8187.5 | -3010.125 | 1350000 | 8187.5 | 0
2021061204 | 7 | 0.47895 | 71842.5 | 0.00624 | 0 | 0.11379 | 1422.375 | 0 | 0 | 64000 | 1422.375 | 0 | 6420.125 | -1767.375 | 1350000 | 6420.125 | 0
2021061205 | 7 | 0.47145 | 70717.5 | 0.00374 | 0 | 0.07166 | 895.75 | 0 | 0 | 64000 | 895.75 | 0 | 5821.75 | -598.375 | 1350000 | 5821.75 | 0
2021061206 | 7 | 0.47361 | 71041.5 | 0.00256 | 0 | 0.0398 | 497.5 | 0.00497 | 397.6 | 64000 | 497.5 | 397.6 | 6146.4 | 324.65 | 1350000 | 6146.4 | 0
2021061207 | 7 | 0.48085 | 72127.5 | 0.0077 | 0 | 0.0232 | 290 | 0.09669 | 7735.2 | 64000 | 290 | 7735.2 | 102.3 | -6044.1 | 1350000 | 102.3 | 0
2021061208 | 7 | 0.50322 | 75483 | 0.00511 | 0 | 0.0192 | 240 | 0.31152 | 24921.6 | 64000 | 240 | 11243 | 0 | -102.3 | 1350000 | 0 | 0
2021061209 | 7 | 0.53797 | 80695.5 | 0.00267 | 0 | 0.01987 | 248.375 | 0.46874 | 37499.2 | 64000 | 248.375 | 16447.125 | 0 | 0 | 1350000 | 0 | 0
2021061210 | 7 | 0.57471 | 86206.5 | 0.00536 | 0 | 0.01881 | 235.125 | 0.53379 | 42703.2 | 64000 | 235.125 | 21971.375 | 0 | 0 | 1350000 | 0 | 0
2021061211 | 7 | 0.60617 | 90925.5 | 0.00685 | 0 | 0.01625 | 203.125 | 0.57997 | 46397.6 | 64000 | 203.125 | 26722.375 | 0 | 0 | 1350000 | 0 | 0
2021061212 | 7 | 0.63629 | 95443.5 | 0.01848 | 0 | 0.01185 | 148.125 | 0.61339 | 49071.2 | 64000 | 148.125 | 31295.375 | 0 | 0 | 1350000 | 0 | 0
2021061213 | 7 | 0.65955 | 98932.5 | 0.00321 | 0 | 0.0065 | 81.25 | 0.61315 | 49052 | 64000 | 81.25 | 34851.25 | 0 | 0 | 1350000 | 0 | 0
2021061214 | 7 | 0.67675 | 101512.5 | 0.00624 | 0 | 0.00893 | 111.625 | 0.65059 | 52047.2 | 64000 | 111.625 | 37400.875 | 0 | 0 | 1350000 | 0 | 0
2021061215 | 7 | 0.68468 | 102702 | 0.00468 | 0 | 0.01175 | 146.875 | 0.6331 | 50648 | 64000 | 146.875 | 38555.125 | 0 | 0 | 1350000 | 0 | 0
2021061216 | 7 | 0.68867 | 103300.5 | 0.00072 | 0 | 0.01036 | 129.5 | 0.6255 | 50040 | 64000 | 129.5 | 39171 | 0 | 0 | 1350000 | 0 | 0
2021061217 | 7 | 0.69194 | 103791 | 0.00273 | 0 | 0.01932 | 241.5 | 0.58814 | 47051.2 | 64000 | 241.5 | 39549.5 | 0 | 0 | 1350000 | 0 | 0
2021061218 | 7 | 0.6993 | 104895 | 0.00293 | 0 | 0.04913 | 614.125 | 0.4451 | 35608 | 64000 | 614.125 | 35608 | 4672.875 | 4672.875 | 1350000 | 4672.875 | 0
2021061219 | 7 | 0.69892 | 104838 | 0.00338 | 0 | 0.06945 | 868.125 | 0.18788 | 15030.4 | 64000 | 868.125 | 15030.4 | 24939.475 | 20266.6 | 1350000 | 24939.475 | 0
2021061220 | 7 | 0.68593 | 102889.5 | 0.00585 | 0 | 0.07291 | 911.375 | 0.02292 | 1833.6 | 64000 | 911.375 | 1833.6 | 36144.525 | 11205.05 | 1339321.725 | 36144.525 | 0
2021061221 | 7 | 0.66765 | 100147.5 | 0.0217 | 0 | 0.07701 | 962.625 | 0 | 0 | 64000 | 962.625 | 0 | 35184.875 | -959.65 | 1329603.1 | 35184.875 | 0
2021061222 | 7 | 0.65053 | 97579.5 | 0.03177 | 0 | 0.08258 | 1032.25 | 0 | 0 | 64000 | 1032.25 | 0 | 32547.25 | -2637.625 | 1322522.1 | 32547.25 | 0
2021061223 | 7 | 0.61702 | 92553 | 0.05706 | 0 | 0.09309 | 1163.625 | 0 | 0 | 64000 | 1163.625 | 0 | 27389.375 | -5157.875 | 1320598.975 | 27389.375 | 0
2021061224 | 7 | 0.57517 | 86275.5 | 0.07355 | 0 | 0.10392 | 1299 | 0 | 0 | 64000 | 1299 | 0 | 20976.5 | -6412.875 | 1325088.725 | 20976.5 | 0
2021061301 | 1 | 0.53605 | 80407.5 | 0.09397 | 0 | 0.11197 | 1399.625 | 0 | 0 | 64000 | 1399.625 | 0 | 15007.875 | -5968.625 | 1335547.1 | 15007.875 | 0
2021061302 | 1 | 0.50563 | 75844.5 | 0.11604 | 0 | 0.11444 | 1430.5 | 0 | 0 | 64000 | 1430.5 | 0 | 10414 | -4593.875 | 1350000 | 10414 | 0
2021061303 | 1 | 0.48341 | 72511.5 | 0.11888 | 0 | 0.11677 | 1459.625 | 0 | 0 | 64000 | 1459.625 | 0 | 7051.875 | -3362.125 | 1350000 | 7051.875 | 0
2021061304 | 1 | 0.46847 | 70270.5 | 0.11778 | 0 | 0.09877 | 1234.625 | 0 | 0 | 64000 | 1234.625 | 0 | 5035.875 | -2016 | 1350000 | 5035.875 | 0
2021061305 | 1 | 0.45919 | 68878.5 | 0.08463 | 0 | 0.07522 | 940.25 | 0 | 0 | 64000 | 940.25 | 0 | 3938.25 | -1097.625 | 1350000 | 3938.25 | 0
2021061306 | 1 | 0.45521 | 68281.5 | 0.08362 | 0 | 0.06882 | 860.25 | 0.00352 | 281.6 | 64000 | 860.25 | 281.6 | 3139.65 | -798.6 | 1350000 | 3139.65 | 0
2021061307 | 1 | 0.45479 | 68218.5 | 0.07599 | 0 | 0.08557 | 1069.625 | 0.07303 | 5842.4 | 64000 | 1069.625 | 3148.875 | 0 | -3139.65 | 1350000 | 0 | 0
2021061308 | 1 | 0.47297 | 70945.5 | 0.04317 | 0 | 0.1032 | 1290 | 0.25323 | 20258.4 | 64000 | 1290 | 5655.5 | 0 | 0 | 1350000 | 0 | 0
2021061309 | 1 | 0.50669 | 76003.5 | 0.03958 | 0 | 0.11246 | 1405.75 | 0.41374 | 33099.2 | 64000 | 1405.75 | 10597.75 | 0 | 0 | 1350000 | 0 | 0
2021061310 | 1 | 0.54937 | 82405.5 | 0.09581 | 0 | 0.11289 | 1411.125 | 0.47611 | 38088.8 | 64000 | 1411.125 | 16994.375 | 0 | 0 | 1350000 | 0 | 0
2021061311 | 1 | 0.59045 | 88567.5 | 0.07945 | 0 | 0.10843 | 1355.375 | 0.54097 | 43277.6 | 64000 | 1355.375 | 23212.125 | 0 | 0 | 1350000 | 0 | 0
2021061312 | 1 | 0.62865 | 94297.5 | 0.00049 | 0 | 0.10024 | 1253 | 0.62932 | 50345.6 | 64000 | 1253 | 29044.5 | 0 | 0 | 1350000 | 0 | 0
2021061313 | 1 | 0.66103 | 99154.5 | 0.00294 | 0 | 0.08206 | 1025.75 | 0.63675 | 50940 | 64000 | 1025.75 | 34128.75 | 0 | 0 | 1350000 | 0 | 0
2021061314 | 1 | 0.68358 | 102537 | 0.01105 | 0 | 0.06699 | 837.375 | 0.67415 | 53932 | 64000 | 837.375 | 37699.625 | 0 | 0 | 1350000 | 0 | 0
2021061315 | 1 | 0.69646 | 104469 | 0.01783 | 0 | 0.05703 | 712.875 | 0.66624 | 53299.2 | 64000 | 712.875 | 39756.125 | 0 | 0 | 1350000 | 0 | 0
2021061316 | 1 | 0.70573 | 105859.5 | 0.05165 | 0 | 0.06177 | 772.125 | 0.62396 | 49916.8 | 64000 | 772.125 | 41087.375 | 0 | 0 | 1350000 | 0 | 0
2021061317 | 1 | 0.71588 | 107382 | 0.09994 | 0 | 0.07265 | 908.125 | 0.5184 | 41472 | 64000 | 908.125 | 41472 | 1001.875 | 1001.875 | 1350000 | 1001.875 | 0
2021061318 | 1 | 0.72313 | 108469.5 | 0.15282 | 0 | 0.08097 | 1012.125 | 0.34273 | 27418.4 | 64000 | 1012.125 | 27418.4 | 16038.975 | 15037.1 | 1350000 | 16038.975 | 0
2021061319 | 1 | 0.71608 | 107412 | 0.1806 | 0 | 0.11376 | 1422 | 0.13378 | 10702.4 | 64000 | 1422 | 10702.4 | 31287.6 | 15248.625 | 1344178.65 | 31287.6 | 0
2021061320 | 1 | 0.7008 | 105120 | 0.27867 | 0 | 0.13064 | 1633 | 0.0181 | 1448 | 64000 | 1633 | 1448 | 38039 | 6751.4 | 1331605.9 | 38039 | 0
2021061321 | 1 | 0.6806 | 102090 | 0.43798 | 0 | 0.1227 | 1533.75 | 0 | 0 | 64000 | 1533.75 | 0 | 36556.25 | -1482.75 | 1320515.9 | 36556.25 | 0
2021061322 | 1 | 0.65764 | 98646 | 0.48423 | 0 | 0.13081 | 1635.125 | 0 | 0 | 64000 | 1635.125 | 0 | 33010.875 | -3545.375 | 1312971.275 | 33010.875 | 0
2021061323 | 1 | 0.61964 | 92946 | 0.31629 | 0 | 0.14191 | 1773.875 | 0 | 0 | 64000 | 1773.875 | 0 | 27172.125 | -5838.75 | 1311265.4 | 27172.125 | 0
2021061324 | 1 | 0.57084 | 85626 | 0.35201 | 0 | 0.15543 | 1942.875 | 0 | 0 | 64000 | 1942.875 | 0 | 19683.125 | -7489 | 1317048.525 | 19683.125 | 0
2021061401 | 2 | 0.53074 | 79611 | 0.45862 | 0 | 0.16961 | 2120.125 | 0 | 0 | 64000 | 2120.125 | 0 | 13490.875 | -6192.25 | 1329023.9 | 13490.875 | 0
2021061402 | 2 | 0.50148 | 75222 | 0.5528 | 0 | 0.16786 | 2098.25 | 0 | 0 | 64000 | 2098.25 | 0 | 9123.75 | -4367.125 | 1345366.4 | 9123.75 | 0
2021061403 | 2 | 0.48319 | 72478.5 | 0.4593 | 0 | 0.16392 | 2049 | 0 | 0 | 64000 | 2049 | 0 | 6429.5 | -2694.25 | 1350000 | 6429.5 | 0
2021061404 | 2 | 0.47342 | 71013 | 0.35902 | 0 | 0.13045 | 1630.625 | 0 | 0 | 64000 | 1630.625 | 0 | 5382.375 | -1047.125 | 1350000 | 5382.375 | 0
2021061405 | 2 | 0.47655 | 71482.5 | 0.26344 | 0 | 0.09941 | 1242.625 | 0 | 0 | 64000 | 1242.625 | 0 | 6239.875 | 857.5 | 1350000 | 6239.875 | 0
2021061406 | 2 | 0.49436 | 74154 | 0.24668 | 0 | 0.07224 | 903 | 0.00324 | 259.2 | 64000 | 903 | 259.2 | 8991.8 | 2751.925 | 1350000 | 8991.8 | 0
2021061407 | 2 | 0.52224 | 78336 | 0.23735 | 0 | 0.05544 | 693 | 0.06598 | 5278.4 | 64000 | 693 | 5278.4 | 8364.6 | -627.2 | 1350000 | 8364.6 | 0
2021061408 | 2 | 0.56175 | 84262.5 | 0.19333 | 0 | 0.06789 | 848.625 | 0.18155 | 14524 | 64000 | 848.625 | 14524 | 4889.875 | -3474.725 | 1350000 | 4889.875 | 0
2021061409 | 2 | 0.5992 | 89880 | 0.11525 | 0 | 0.06463 | 807.875 | 0.33541 | 26832.8 | 64000 | 807.875 | 25072.125 | 0 | -4889.875 | 1350000 | 0 | 0
2021061410 | 2 | 0.63009 | 94513.5 | 0.10253 | 0 | 0.04775 | 596.875 | 0.49205 | 39364 | 64000 | 596.875 | 29916.625 | 0 | 0 | 1350000 | 0 | 0
2021061411 | 2 | 0.66338 | 99507 | 0.11524 | 0 | 0.03201 | 400.125 | 0.56799 | 45439.2 | 64000 | 400.125 | 35106.875 | 0 | 0 | 1350000 | 0 | 0
2021061412 | 2 | 0.69195 | 103792.5 | 0.09818 | 0 | 0.02358 | 294.75 | 0.58804 | 47043.2 | 64000 | 294.75 | 39497.75 | 0 | 0 | 1350000 | 0 | 0
2021061413 | 2 | 0.72239 | 108358.5 | 0.12115 | 0 | 0.02156 | 269.5 | 0.61218 | 48974.4 | 64000 | 269.5 | 44089 | 0 | 0 | 1350000 | 0 | 0
2021061414 | 2 | 0.74983 | 112474.5 | 0.19068 | 0 | 0.01717 | 214.625 | 0.6045 | 48360 | 64000 | 214.625 | 48259.875 | 0 | 0 | 1350000 | 0 | 0
2021061415 | 2 | 0.77083 | 115624.5 | 0.28671 | 0 | 0.00837 | 104.625 | 0.59339 | 47471.2 | 64000 | 104.625 | 47471.2 | 4048.675 | 4048.675 | 1350000 | 4048.675 | 0
2021061416 | 2 | 0.78586 | 117879 | 0.15156 | 0 | 0.00916 | 114.5 | 0.555 | 44400 | 64000 | 114.5 | 44400 | 9364.5 | 5315.825 | 1350000 | 9364.5 | 0
2021061417 | 2 | 0.80075 | 120112.5 | 0.45823 | 0 | 0.02725 | 340.625 | 0.43335 | 34668 | 64000 | 340.625 | 34668 | 21103.875 | 11739.375 | 1350000 | 21103.875 | 0
2021061418 | 2 | 0.80589 | 120883.5 | 0.3136 | 0 | 0.06484 | 810.5 | 0.29495 | 23596 | 64000 | 810.5 | 23596 | 32477 | 11373.125 | 1342989.25 | 32477 | 0
2021061419 | 2 | 0.79264 | 118896 | 0.22865 | 0 | 0.06717 | 839.625 | 0.12667 | 10133.6 | 64000 | 839.625 | 10133.6 | 43922.775 | 11445.775 | 1324532.725 | 43922.775 | 0
2021061420 | 2 | 0.76283 | 114424.5 | 0.13937 | 0 | 0.04935 | 616.875 | 0.01985 | 1588 | 64000 | 616.875 | 1588 | 48219.625 | 4296.85 | 1301779.35 | 48219.625 | 0
2021061421 | 2 | 0.7292 | 109380 | 0.1255 | 0 | 0.03614 | 451.75 | 0 | 0 | 64000 | 451.75 | 0 | 44928.25 | -3291.375 | 1282317.35 | 44928.25 | 0
2021061422 | 2 | 0.69674 | 104511 | 0.13586 | 0 | 0.02457 | 307.125 | 0 | 0 | 64000 | 307.125 | 0 | 40203.875 | -4724.375 | 1267579.725 | 40203.875 | 0
2021061423 | 2 | 0.64572 | 96858 | 0.16625 | 0 | 0.01592 | 199 | 0 | 0 | 64000 | 199 | 0 | 32659 | -7544.875 | 1260386.975 | 32659 | 0
2021061424 | 2 | 0.59014 | 88521 | 0.27591 | 0 | 0.01958 | 244.75 | 0 | 0 | 64000 | 244.75 | 0 | 24276.25 | -8382.75 | 1261576.975 | 24276.25 | 0
2021061501 | 3 | 0.54434 | 81651 | 0.35002 | 0 | 0.03211 | 401.375 | 0 | 0 | 64000 | 401.375 | 0 | 17249.625 | -7026.625 | 1269793.6 | 17249.625 | 0
2021061502 | 3 | 0.51346 | 77019 | 0.36965 | 0 | 0.04045 | 505.625 | 0 | 0 | 64000 | 505.625 | 0 | 12513.375 | -4736.25 | 1282746.475 | 12513.375 | 0
2021061503 | 3 | 0.49226 | 73839 | 0.39314 | 0 | 0.05204 | 650.5 | 0 | 0 | 64000 | 650.5 | 0 | 9188.5 | -3324.875 | 1299024.225 | 9188.5 | 0
2021061504 | 3 | 0.48029 | 72043.5 | 0.38775 | 0 | 0.05439 | 679.875 | 0 | 0 | 64000 | 679.875 | 0 | 7363.625 | -1824.875 | 1317126.85 | 7363.625 | 0
2021061505 | 3 | 0.47969 | 71953.5 | 0.40322 | 0 | 0.05497 | 687.125 | 0 | 0 | 64000 | 687.125 | 0 | 7266.375 | -97.25 | 1335326.725 | 7266.375 | 0
2021061506 | 3 | 0.49463 | 74194.5 | 0.41963 | 0 | 0.04855 | 606.875 | 0.00297 | 237.6 | 64000 | 606.875 | 237.6 | 9350.025 | 2083.65 | 1350000 | 9350.025 | 0
2021061507 | 3 | 0.51968 | 77952 | 0.39587 | 0 | 0.03936 | 492 | 0.06923 | 5538.4 | 64000 | 492 | 5538.4 | 7921.6 | -1428.425 | 1350000 | 7921.6 | 0
2021061508 | 3 | 0.55691 | 83536.5 | 0.40472 | 0 | 0.04237 | 529.625 | 0.20911 | 16728.8 | 64000 | 529.625 | 16728.8 | 2278.075 | -5643.525 | 1350000 | 2278.075 | 0
2021061509 | 3 | 0.59047 | 88570.5 | 0.34033 | 0 | 0.03513 | 439.125 | 0.35194 | 28155.2 | 64000 | 439.125 | 24131.375 | 0 | -2278.075 | 1350000 | 0 | 0
2021061510 | 3 | 0.61769 | 92653.5 | 0.3711 | 0 | 0.02832 | 354 | 0.40475 | 32380 | 64000 | 354 | 28299.5 | 0 | 0 | 1350000 | 0 | 0
2021061511 | 3 | 0.64289 | 96433.5 | 0.44159 | 0 | 0.01655 | 206.875 | 0.42453 | 33962.4 | 64000 | 206.875 | 32226.625 | 0 | 0 | 1350000 | 0 | 0
2021061512 | 3 | 0.66427 | 99640.5 | 0.48512 | 0 | 0.01076 | 134.5 | 0.42065 | 33652 | 64000 | 134.5 | 33652 | 1854 | 1854 | 1350000 | 1854 | 0
2021061513 | 3 | 0.68304 | 102456 | 0.52815 | 0 | 0.01164 | 145.5 | 0.42612 | 34089.6 | 64000 | 145.5 | 34089.6 | 4220.9 | 2366.9 | 1350000 | 4220.9 | 0
2021061514 | 3 | 0.70026 | 105039 | 0.5051 | 0 | 0.01129 | 141.125 | 0.37796 | 30236.8 | 64000 | 141.125 | 30236.8 | 10661.075 | 6440.175 | 1350000 | 10661.075 | 0
2021061515 | 3 | 0.71126 | 106689 | 0.49758 | 0 | 0.01059 | 132.375 | 0.35182 | 28145.6 | 64000 | 132.375 | 28145.6 | 14411.025 | 3749.95 | 1350000 | 14411.025 | 0
2021061516 | 3 | 0.71972 | 107958 | 0.5007 | 0 | 0.00854 | 106.75 | 0.28706 | 22964.8 | 64000 | 106.75 | 22964.8 | 20886.45 | 6475.425 | 1350000 | 20886.45 | 0
2021061517 | 3 | 0.72789 | 109183.5 | 0.50893 | 0 | 0.01563 | 195.375 | 0.22094 | 17675.2 | 64000 | 195.375 | 17675.2 | 27312.925 | 6426.475 | 1348153.325 | 27312.925 | 0
2021061518 | 3 | 0.731 | 109650 | 0.48727 | 0 | 0.0393 | 491.25 | 0.15621 | 12496.8 | 64000 | 491.25 | 12496.8 | 32661.95 | 5349.025 | 1340957.625 | 32661.95 | 0
2021061519 | 3 | 0.72015 | 108022.5 | 0.45733 | 0 | 0.04752 | 594 | 0.07183 | 5746.4 | 64000 | 594 | 5746.4 | 37682.1 | 5020.15 | 1328741.775 | 37682.1 | 0
2021061520 | 3 | 0.696 | 104400 | 0.54742 | 0 | 0.04955 | 619.375 | 0.01064 | 851.2 | 64000 | 619.375 | 851.2 | 38929.425 | 1247.325 | 1315278.6 | 38929.425 | 0
2021061521 | 3 | 0.66465 | 99697.5 | 0.58927 | 0 | 0.06013 | 751.625 | 0 | 0 | 64000 | 751.625 | 0 | 34945.875 | -3983.55 | 1305798.975 | 34945.875 | 0
2021061522 | 3 | 0.64112 | 96168 | 0.59567 | 0 | 0.07673 | 959.125 | 0 | 0 | 64000 | 959.125 | 0 | 31208.875 | -3737 | 1300056.35 | 31208.875 | 0
2021061523 | 3 | 0.59878 | 89817 | 0.5341 | 0 | 0.0873 | 1091.25 | 0 | 0 | 64000 | 1091.25 | 0 | 24725.75 | -6483.125 | 1300796.85 | 24725.75 | 0
2021061524 | 3 | 0.55035 | 82552.5 | 0.54424 | 0 | 0.10964 | 1370.5 | 0 | 0 | 64000 | 1370.5 | 0 | 17182 | -7543.75 | 1309081.1 | 17182 | 0
2021061601 | 4 | 0.5088 | 76320 | 0.47931 | 0 | 0.1264 | 1580 | 0 | 0 | 64000 | 1580 | 0 | 10740 | -6442 | 1323807.35 | 10740 | 0
2021061602 | 4 | 0.48098 | 72147 | 0.3951 | 0 | 0.15267 | 1908.375 | 0 | 0 | 64000 | 1908.375 | 0 | 6238.625 | -4501.375 | 1343034.975 | 6238.625 | 0
2021061603 | 4 | 0.46399 | 69598.5 | 0.38393 | 0 | 0.16242 | 2030.25 | 0 | 0 | 64000 | 2030.25 | 0 | 3568.25 | -2670.375 | 1350000 | 3568.25 | 0
2021061604 | 4 | 0.4543 | 68145 | 0.38329 | 0 | 0.14775 | 1846.875 | 0 | 0 | 64000 | 1846.875 | 0 | 2298.125 | -1270.125 | 1350000 | 2298.125 | 0
2021061605 | 4 | 0.45653 | 68479.5 | 0.38237 | 0 | 0.09667 | 1208.375 | 0 | 0 | 64000 | 1208.375 | 0 | 3271.125 | 973 | 1350000 | 3271.125 | 0
2021061606 | 4 | 0.47005 | 70507.5 | 0.425 | 0 | 0.08033 | 1004.125 | 0.00258 | 206.4 | 64000 | 1004.125 | 206.4 | 5296.975 | 2025.85 | 1350000 | 5296.975 | 0
2021061607 | 4 | 0.49585 | 74377.5 | 0.42534 | 0 | 0.07209 | 901.125 | 0.04616 | 3692.8 | 64000 | 901.125 | 3692.8 | 5783.575 | 486.6 | 1350000 | 5783.575 | 0
2021061608 | 4 | 0.52887 | 79330.5 | 0.30865 | 0 | 0.07933 | 991.625 | 0.1841 | 14728 | 64000 | 991.625 | 14338.875 | 0 | -5783.575 | 1350000 | 0 | 0
2021061609 | 4 | 0.55634 | 83451 | 0.15952 | 0 | 0.09902 | 1237.75 | 0.32052 | 25641.6 | 64000 | 1237.75 | 18213.25 | 0 | 0 | 1350000 | 0 | 0
2021061610 | 4 | 0.57561 | 86341.5 | 0.15217 | 0 | 0.10846 | 1355.75 | 0.47582 | 38065.6 | 64000 | 1355.75 | 20985.75 | 0 | 0 | 1350000 | 0 | 0
2021061611 | 4 | 0.5961 | 89415 | 0.35805 | 0 | 0.11438 | 1429.75 | 0.53127 | 42501.6 | 64000 | 1429.75 | 23985.25 | 0 | 0 | 1350000 | 0 | 0
2021061612 | 4 | 0.61265 | 91897.5 | 0.46376 | 0 | 0.11497 | 1437.125 | 0.57068 | 45654.4 | 64000 | 1437.125 | 26460.375 | 0 | 0 | 1350000 | 0 | 0
2021061613 | 4 | 0.62955 | 94432.5 | 0.51224 | 0 | 0.11642 | 1455.25 | 0.59764 | 47811.2 | 64000 | 1455.25 | 28977.25 | 0 | 0 | 1350000 | 0 | 0
2021061614 | 4 | 0.64558 | 96837 | 0.58312 | 0 | 0.12532 | 1566.5 | 0.58442 | 46753.6 | 64000 | 1566.5 | 31270.5 | 0 | 0 | 1350000 | 0 | 0
2021061615 | 4 | 0.66054 | 99081 | 0.56907 | 0 | 0.12241 | 1530.125 | 0.56088 | 44870.4 | 64000 | 1530.125 | 33550.875 | 0 | 0 | 1350000 | 0 | 0
2021061616 | 4 | 0.67589 | 101383.5 | 0.51993 | 0 | 0.11521 | 1440.125 | 0.53147 | 42517.6 | 64000 | 1440.125 | 35943.375 | 0 | 0 | 1350000 | 0 | 0
2021061617 | 4 | 0.69072 | 103608 | 0.53638 | 0 | 0.11958 | 1494.75 | 0.4576 | 36608 | 64000 | 1494.75 | 36608 | 1505.25 | 1505.25 | 1350000 | 1505.25 | 0
2021061618 | 4 | 0.70074 | 105111 | 0.46345 | 0 | 0.13533 | 1691.625 | 0.33928 | 27142.4 | 64000 | 1691.625 | 27142.4 | 12276.975 | 10771.725 | 1350000 | 12276.975 | 0
2021061619 | 4 | 0.69633 | 104449.5 | 0.46307 | 0 | 0.14833 | 1854.125 | 0.14424 | 11539.2 | 64000 | 1854.125 | 11539.2 | 27056.175 | 14779.2 | 1348410.075 | 27056.175 | 0
2021061620 | 4 | 0.67452 | 101178 | 0.42309 | 0 | 0.15075 | 1884.375 | 0.02114 | 1691.2 | 64000 | 1884.375 | 1691.2 | 33602.425 | 6546.25 | 1340273.9 | 33602.425 | 0
2021061621 | 4 | 0.64424 | 96636 | 0.39311 | 0 | 0.14578 | 1822.25 | 0 | 0 | 64000 | 1822.25 | 0 | 30813.75 | -2788.675 | 1334926.4 | 30813.75 | 0
2021061622 | 4 | 0.61881 | 92821.5 | 0.41588 | 0 | 0.13864 | 1733 | 0 | 0 | 64000 | 1733 | 0 | 27088.5 | -3725.25 | 1333304.15 | 27088.5 | 0
2021061623 | 4 | 0.57908 | 86862 | 0.48524 | 0 | 0.15229 | 1903.625 | 0 | 0 | 64000 | 1903.625 | 0 | 20958.375 | -6130.125 | 1337812.025 | 20958.375 | 0
2021061624 | 4 | 0.53131 | 79696.5 | 0.40469 | 0 | 0.164 | 2050 | 0 | 0 | 64000 | 2050 | 0 | 13646.5 | -7311.875 | 1349631.775 | 13646.5 | 0
2021061701 | 5 | 0.49189 | 73783.5 | 0.37383 | 0 | 0.18469 | 2308.625 | 0 | 0 | 64000 | 2308.625 | 0 | 7474.875 | -6171.625 | 1350000 | 7474.875 | 0
2021061702 | 5 | 0.46657 | 69985.5 | 0.32229 | 0 | 0.20268 | 2533.5 | 0 | 0 | 64000 | 2533.5 | 0 | 3452 | -4022.875 | 1350000 | 3452 | 0
2021061703 | 5 | 0.44939 | 67408.5 | 0.25386 | 0 | 0.1785 | 2231.25 | 0 | 0 | 64000 | 2231.25 | 0 | 1177.25 | -2274.75 | 1350000 | 1177.25 | 0
2021061704 | 5 | 0.44098 | 66147 | 0.18314 | 0 | 0.13122 | 1640.25 | 0 | 0 | 64000 | 1640.25 | 0 | 506.75 | -670.5 | 1350000 | 506.75 | 0
2021061705 | 5 | 0.4446 | 66690 | 0.19291 | 0 | 0.10725 | 1340.625 | 0 | 0 | 64000 | 1340.625 | 0 | 1349.375 | 842.625 | 1350000 | 1349.375 | 0
2021061706 | 5 | 0.45914 | 68871 | 0.19143 | 0 | 0.10255 | 1281.875 | 0.00214 | 171.2 | 64000 | 1281.875 | 171.2 | 3417.925 | 2068.55 | 1350000 | 3417.925 | 0
2021061707 | 5 | 0.48352 | 72528 | 0.1747 | 0 | 0.11479 | 1434.875 | 0.05254 | 4203.2 | 64000 | 1434.875 | 4203.2 | 2889.925 | -528 | 1350000 | 2889.925 | 0
2021061708 | 5 | 0.51697 | 77545.5 | 0.14721 | 0 | 0.11779 | 1472.375 | 0.25825 | 20660 | 64000 | 1472.375 | 12073.125 | 0 | -2889.925 | 1350000 | 0 | 0
2021061709 | 5 | 0.54375 | 81562.5 | 0.10092 | 0 | 0.10806 | 1350.75 | 0.38886 | 31108.8 | 64000 | 1350.75 | 16211.75 | 0 | 0 | 1350000 | 0 | 0
2021061710 | 5 | 0.56442 | 84663 | 0.09618 | 0 | 0.09817 | 1227.125 | 0.43207 | 34565.6 | 64000 | 1227.125 | 19435.875 | 0 | 0 | 1350000 | 0 | 0
2021061711 | 5 | 0.58642 | 87963 | 0.14523 | 0 | 0.08258 | 1032.25 | 0.51061 | 40848.8 | 64000 | 1032.25 | 22930.75 | 0 | 0 | 1350000 | 0 | 0
2021061712 | 5 | 0.60434 | 90651 | 0.16427 | 0 | 0.07128 | 891 | 0.54358 | 43486.4 | 64000 | 891 | 25760 | 0 | 0 | 1350000 | 0 | 0
2021061713 | 5 | 0.62306 | 93459 | 0.163 | 0 | 0.08111 | 1013.875 | 0.63895 | 51116 | 64000 | 1013.875 | 28445.125 | 0 | 0 | 1350000 | 0 | 0
2021061714 | 5 | 0.64528 | 96792 | 0.18904 | 0 | 0.09955 | 1244.375 | 0.66589 | 53271.2 | 64000 | 1244.375 | 31547.625 | 0 | 0 | 1350000 | 0 | 0
2021061715 | 5 | 0.66777 | 100165.5 | 0.2184 | 0 | 0.08884 | 1110.5 | 0.69982 | 55985.6 | 64000 | 1110.5 | 35055 | 0 | 0 | 1350000 | 0 | 0
2021061716 | 5 | 0.69086 | 103629 | 0.18327 | 0 | 0.06924 | 865.5 | 0.67714 | 54171.2 | 64000 | 865.5 | 38763.5 | 0 | 0 | 1350000 | 0 | 0
2021061717 | 5 | 0.71671 | 107506.5 | 0.14111 | 0 | 0.07251 | 906.375 | 0.61722 | 49377.6 | 64000 | 906.375 | 42600.125 | 0 | 0 | 1350000 | 0 | 0
2021061718 | 5 | 0.73302 | 109953 | 0.14463 | 0 | 0.08665 | 1083.125 | 0.49379 | 39503.2 | 64000 | 1083.125 | 39503.2 | 5366.675 | 5366.675 | 1350000 | 5366.675 | 0
2021061719 | 5 | 0.734 | 110100 | 0.15447 | 0 | 0.10131 | 1266.375 | 0.24521 | 19616.8 | 64000 | 1266.375 | 19616.8 | 25216.825 | 19850.15 | 1350000 | 25216.825 | 0
2021061720 | 5 | 0.71679 | 107518.5 | 0.10853 | 0 | 0.08954 | 1119.25 | 0.03109 | 2487.2 | 64000 | 1119.25 | 2487.2 | 39912.05 | 14695.225 | 1335554.2 | 39912.05 | 0
2021061721 | 5 | 0.68585 | 102877.5 | 0.07901 | 0 | 0.08635 | 1079.375 | 0 | 0 | 64000 | 1079.375 | 0 | 37798.125 | -2113.925 | 1323222.325 | 37798.125 | 0
2021061722 | 5 | 0.66358 | 99537 | 0.04754 | 0 | 0.0802 | 1002.5 | 0 | 0 | 64000 | 1002.5 | 0 | 34534.5 | -3263.625 | 1314154.075 | 34534.5 | 0
2021061723 | 5 | 0.62117 | 93175.5 | 0.02648 | 0 | 0.07294 | 911.75 | 0 | 0 | 64000 | 911.75 | 0 | 28263.75 | -6270.75 | 1311356.575 | 28263.75 | 0
2021061724 | 5 | 0.57344 | 86016 | 0.09568 | 0 | 0.06752 | 844 | 0 | 0 | 64000 | 844 | 0 | 21172 | -7091.75 | 1315650.825 | 21172 | 0
2021061801 | 6 | 0.53231 | 79846.5 | 0.2383 | 0 | 0.0752 | 940 | 0 | 0 | 64000 | 940 | 0 | 14906.5 | -6265.5 | 1326210.575 | 14906.5 | 0
2021061802 | 6 | 0.50196 | 75294 | 0.40753 | 0 | 0.07636 | 954.5 | 0 | 0 | 64000 | 954.5 | 0 | 10339.5 | -4567 | 1341337.325 | 10339.5 | 0
2021061803 | 6 | 0.48272 | 72408 | 0.48075 | 0 | 0.09402 | 1175.25 | 0 | 0 | 64000 | 1175.25 | 0 | 7232.75 | -3106.75 | 1350000 | 7232.75 | 0
2021061804 | 6 | 0.47162 | 70743 | 0.54814 | 0 | 0.11832 | 1479 | 0 | 0 | 64000 | 1479 | 0 | 5264 | -1968.75 | 1350000 | 5264 | 0
2021061805 | 6 | 0.47336 | 71004 | 0.60756 | 0 | 0.11371 | 1421.375 | 0 | 0 | 64000 | 1421.375 | 0 | 5582.625 | 318.625 | 1350000 | 5582.625 | 0
2021061806 | 6 | 0.48642 | 72963 | 0.62863 | 0 | 0.11359 | 1419.875 | 0.00315 | 252 | 64000 | 1419.875 | 252 | 7291.125 | 1708.5 | 1350000 | 7291.125 | 0
2021061807 | 6 | 0.50728 | 76092 | 0.58956 | 0 | 0.11795 | 1474.375 | 0.06896 | 5516.8 | 64000 | 1474.375 | 5516.8 | 5100.825 | -2190.3 | 1350000 | 5100.825 | 0
2021061808 | 6 | 0.53815 | 80722.5 | 0.53777 | 0 | 0.08251 | 1031.375 | 0.25354 | 20283.2 | 64000 | 1031.375 | 15691.125 | 0 | -5100.825 | 1350000 | 0 | 0
2021061809 | 6 | 0.56798 | 85197 | 0.42832 | 0 | 0.06879 | 859.875 | 0.41107 | 32885.6 | 64000 | 859.875 | 20337.125 | 0 | 0 | 1350000 | 0 | 0
2021061810 | 6 | 0.59608 | 89412 | 0.34278 | 0 | 0.05822 | 727.75 | 0.49323 | 39458.4 | 64000 | 727.75 | 24684.25 | 0 | 0 | 1350000 | 0 | 0
2021061811 | 6 | 0.62439 | 93658.5 | 0.32996 | 0 | 0.06055 | 756.875 | 0.56767 | 45413.6 | 64000 | 756.875 | 28901.625 | 0 | 0 | 1350000 | 0 | 0
2021061812 | 6 | 0.65091 | 97636.5 | 0.36611 | 0 | 0.05858 | 732.25 | 0.60244 | 48195.2 | 64000 | 732.25 | 32904.25 | 0 | 0 | 1350000 | 0 | 0
2021061813 | 6 | 0.67552 | 101328 | 0.51424 | 0 | 0.06615 | 826.875 | 0.64586 | 51668.8 | 64000 | 826.875 | 36501.125 | 0 | 0 | 1350000 | 0 | 0
2021061814 | 6 | 0.7004 | 105060 | 0.58785 | 0 | 0.07195 | 899.375 | 0.67141 | 53712.8 | 64000 | 899.375 | 40160.625 | 0 | 0 | 1350000 | 0 | 0
2021061815 | 6 | 0.72604 | 108906 | 0.48103 | 0 | 0.06096 | 762 | 0.67641 | 54112.8 | 64000 | 762 | 44144 | 0 | 0 | 1350000 | 0 | 0
2021061816 | 6 | 0.75213 | 112819.5 | 0.43557 | 0 | 0.05054 | 631.75 | 0.6514 | 52112 | 64000 | 631.75 | 48187.75 | 0 | 0 | 1350000 | 0 | 0
2021061817 | 6 | 0.77197 | 115795.5 | 0.53956 | 0 | 0.05428 | 678.5 | 0.60002 | 48001.6 | 64000 | 678.5 | 48001.6 | 3115.4 | 3115.4 | 1350000 | 3115.4 | 0
2021061818 | 6 | 0.78193 | 117289.5 | 0.58649 | 0 | 0.07456 | 932 | 0.45826 | 36660.8 | 64000 | 932 | 36660.8 | 15696.7 | 12581.3 | 1350000 | 15696.7 | 0
2021061819 | 6 | 0.77302 | 115953 | 0.53481 | 0 | 0.10701 | 1337.625 | 0.22878 | 18302.4 | 64000 | 1337.625 | 18302.4 | 32312.975 | 16616.275 | 1343153.275 | 32312.975 | 0
2021061820 | 6 | 0.74902 | 112353 | 0.50387 | 0 | 0.13573 | 1696.625 | 0.03117 | 2493.6 | 64000 | 1696.625 | 2493.6 | 44162.775 | 11849.8 | 1324456.75 | 44162.775 | 0
2021061821 | 6 | 0.72501 | 108751.5 | 0.5809 | 0 | 0.14026 | 1753.25 | 0 | 0 | 64000 | 1753.25 | 0 | 42998.25 | -1164.525 | 1306924.75 | 42998.25 | 0
2021061822 | 6 | 0.7002 | 105030 | 0.70267 | 0 | 0.12958 | 1619.75 | 0 | 0 | 64000 | 1619.75 | 0 | 39410.25 | -3588 | 1292980.75 | 39410.25 | 0
2021061823 | 6 | 0.6621 | 99315 | 0.75469 | 0 | 0.12683 | 1585.375 | 0 | 0 | 64000 | 1585.375 | 0 | 33729.625 | -5680.625 | 1284717.375 | 33729.625 | 0
2021061824 | 6 | 0.61512 | 92268 | 0.83248 | 0 | 0.14845 | 1855.625 | 0 | 0 | 64000 | 1855.625 | 0 | 26412.375 | -7317.25 | 1283771.25 | 26412.375 | 0
2021061901 | 7 | 0.57323 | 85984.5 | 0.86737 | 0 | 0.14174 | 1771.75 | 0 | 0 | 64000 | 1771.75 | 0 | 20212.75 | -6199.625 | 1289024.75 | 20212.75 | 0
2021061902 | 7 | 0.54037 | 81055.5 | 0.84446 | 0 | 0.13869 | 1733.625 | 0 | 0 | 64000 | 1733.625 | 0 | 15321.875 | -4890.875 | 1299169.125 | 15321.875 | 0
2021061903 | 7 | 0.51759 | 77638.5 | 0.79447 | 0 | 0.14828 | 1853.5 | 0 | 0 | 64000 | 1853.5 | 0 | 11785 | -3536.875 | 1312850.375 | 11785 | 0
2021061904 | 7 | 0.50202 | 75303 | 0.74518 | 0 | 0.10668 | 1333.5 | 0 | 0 | 64000 | 1333.5 | 0 | 9969.5 | -1815.5 | 1328347.125 | 9969.5 | 0
2021061905 | 7 | 0.49584 | 74376 | 0.6859 | 0 | 0.06696 | 837 | 0 | 0 | 64000 | 837 | 0 | 9539 | -430.5 | 1344274.375 | 9539 | 0
2021061906 | 7 | 0.49654 | 74481 | 0.66469 | 0 | 0.08132 | 1016.5 | 0.00327 | 261.6 | 64000 | 1016.5 | 261.6 | 9202.9 | -336.1 | 1350000 | 9202.9 | 0
2021061907 | 7 | 0.50343 | 75514.5 | 0.7698 | 0 | 0.06617 | 827.125 | 0.0915 | 7320 | 64000 | 827.125 | 7320 | 3367.375 | -5835.525 | 1350000 | 3367.375 | 0
2021061908 | 7 | 0.52393 | 78589.5 | 0.73416 | 0 | 0.10774 | 1346.75 | 0.30404 | 24323.2 | 64000 | 1346.75 | 13242.75 | 0 | -3367.375 | 1350000 | 0 | 0
2021061909 | 7 | 0.55908 | 83862 | 0.63166 | 0 | 0.17931 | 2241.375 | 0.48503 | 38802.4 | 64000 | 2241.375 | 17620.625 | 0 | 0 | 1350000 | 0 | 0
2021061910 | 7 | 0.59413 | 89119.5 | 0.58323 | 0 | 0.18736 | 2342 | 0.53203 | 42562.4 | 64000 | 2342 | 22777.5 | 0 | 0 | 1350000 | 0 | 0
2021061911 | 7 | 0.62864 | 94296 | 0.47733 | 0 | 0.21109 | 2638.625 | 0.57577 | 46061.6 | 64000 | 2638.625 | 27657.375 | 0 | 0 | 1350000 | 0 | 0
2021061912 | 7 | 0.66313 | 99469.5 | 0.38209 | 0 | 0.20985 | 2623.125 | 0.60027 | 48021.6 | 64000 | 2623.125 | 32846.375 | 0 | 0 | 1350000 | 0 | 0
2021061913 | 7 | 0.69431 | 104146.5 | 0.42747 | 0 | 0.23011 | 2876.375 | 0.63836 | 51068.8 | 64000 | 2876.375 | 37270.125 | 0 | 0 | 1350000 | 0 | 0
2021061914 | 7 | 0.71639 | 107458.5 | 0.43039 | 0 | 0.25277 | 3159.625 | 0.66218 | 52974.4 | 64000 | 3159.625 | 40298.875 | 0 | 0 | 1350000 | 0 | 0
2021061915 | 7 | 0.73559 | 110338.5 | 0.28954 | 0 | 0.26084 | 3260.5 | 0.66811 | 53448.8 | 64000 | 3260.5 | 43078 | 0 | 0 | 1350000 | 0 | 0
2021061916 | 7 | 0.751 | 112650 | 0.22832 | 0 | 0.25378 | 3172.25 | 0.65026 | 52020.8 | 64000 | 3172.25 | 45477.75 | 0 | 0 | 1350000 | 0 | 0
2021061917 | 7 | 0.75428 | 113142 | 0.30416 | 0 | 0.21542 | 2692.75 | 0.59325 | 47460 | 64000 | 2692.75 | 46449.25 | 0 | 0 | 1350000 | 0 | 0
2021061918 | 7 | 0.75369 | 113053.5 | 0.35064 | 0 | 0.22657 | 2832.125 | 0.46725 | 37380 | 64000 | 2832.125 | 37380 | 8841.375 | 8841.375 | 1350000 | 8841.375 | 0
2021061919 | 7 | 0.74411 | 111616.5 | 0.43081 | 0 | 0.29982 | 3747.75 | 0.21027 | 16821.6 | 64000 | 3747.75 | 16821.6 | 27047.15 | 18205.775 | 1348419.1 | 27047.15 | 0
2021061920 | 7 | 0.72203 | 108304.5 | 0.32197 | 0 | 0.35655 | 4456.875 | 0.03099 | 2479.2 | 64000 | 4456.875 | 2479.2 | 37368.425 | 10321.275 | 1336516.925 | 37368.425 | 0
2021061921 | 7 | 0.6986 | 104790 | 0.2357 | 0 | 0.3773 | 4716.25 | 0 | 0 | 64000 | 4716.25 | 0 | 36073.75 | -1294.675 | 1325909.425 | 36073.75 | 0
2021061922 | 7 | 0.67705 | 101557.5 | 0.26546 | 0 | 0.45511 | 5688.875 | 0 | 0 | 64000 | 5688.875 | 0 | 31868.625 | -4205.125 | 1319507.05 | 31868.625 | 0
2021061923 | 7 | 0.64114 | 96171 | 0.27052 | 0 | 0.48828 | 6103.5 | 0 | 0 | 64000 | 6103.5 | 0 | 26067.5 | -5801.125 | 1318905.8 | 26067.5 | 0
2021061924 | 7 | 0.59702 | 89553 | 0.23047 | 0 | 0.52136 | 6517 | 0 | 0 | 64000 | 6517 | 0 | 19036 | -7031.5 | 1325336.05 | 19036 | 0
2021062001 | 1 | 0.55612 | 83418 | 0.29673 | 0 | 0.53367 | 6670.875 | 0 | 0 | 64000 | 6670.875 | 0 | 12747.125 | -6288.875 | 1338055.175 | 12747.125 | 0
2021062002 | 1 | 0.52427 | 78640.5 | 0.3173 | 0 | 0.51846 | 6480.75 | 0 | 0 | 64000 | 6480.75 | 0 | 8159.75 | -4587.375 | 1350000 | 8159.75 | 0
2021062003 | 1 | 0.50199 | 75298.5 | 0.32521 | 0 | 0.45655 | 5706.875 | 0 | 0 | 64000 | 5706.875 | 0 | 5591.625 | -2568.125 | 1350000 | 5591.625 | 0
2021062004 | 1 | 0.48596 | 72894 | 0.34373 | 0 | 0.37834 | 4729.25 | 0 | 0 | 64000 | 4729.25 | 0 | 4164.75 | -1426.875 | 1350000 | 4164.75 | 0
2021062005 | 1 | 0.47676 | 71514 | 0.3799 | 0 | 0.31713 | 3964.125 | 0 | 0 | 64000 | 3964.125 | 0 | 3549.875 | -614.875 | 1350000 | 3549.875 | 0
2021062006 | 1 | 0.47214 | 70821 | 0.40586 | 0 | 0.30001 | 3750.125 | 0.00383 | 306.4 | 64000 | 3750.125 | 306.4 | 2764.475 | -785.4 | 1350000 | 2764.475 | 0
2021062007 | 1 | 0.47286 | 70929 | 0.43885 | 0 | 0.274 | 3425 | 0.08818 | 7054.4 | 64000 | 3425 | 3504 | 0 | -2764.475 | 1350000 | 0 | 0
2021062008 | 1 | 0.49582 | 74373 | 0.44122 | 0 | 0.21629 | 2703.625 | 0.24603 | 19682.4 | 64000 | 2703.625 | 7669.375 | 0 | 0 | 1350000 | 0 | 0
2021062009 | 1 | 0.53687 | 80530.5 | 0.34741 | 0 | 0.23374 | 2921.75 | 0.40134 | 32107.2 | 64000 | 2921.75 | 13608.75 | 0 | 0 | 1350000 | 0 | 0
2021062010 | 1 | 0.58675 | 88012.5 | 0.23656 | 0 | 0.22294 | 2786.75 | 0.46808 | 37446.4 | 64000 | 2786.75 | 21225.75 | 0 | 0 | 1350000 | 0 | 0
2021062011 | 1 | 0.63389 | 95083.5 | 0.21533 | 0 | 0.23967 | 2995.875 | 0.54401 | 43520.8 | 64000 | 2995.875 | 28087.625 | 0 | 0 | 1350000 | 0 | 0
2021062012 | 1 | 0.6785 | 101775 | 0.30234 | 0 | 0.22729 | 2841.125 | 0.61921 | 49536.8 | 64000 | 2841.125 | 34933.875 | 0 | 0 | 1350000 | 0 | 0
2021062013 | 1 | 0.717 | 107550 | 0.32894 | 0 | 0.1822 | 2277.5 | 0.66407 | 53125.6 | 64000 | 2277.5 | 41272.5 | 0 | 0 | 1350000 | 0 | 0
2021062014 | 1 | 0.74548 | 111822 | 0.25097 | 0 | 0.1591 | 1988.75 | 0.69452 | 55561.6 | 64000 | 1988.75 | 45833.25 | 0 | 0 | 1350000 | 0 | 0
2021062015 | 1 | 0.76961 | 115441.5 | 0.18911 | 0 | 0.1273 | 1591.25 | 0.68856 | 55084.8 | 64000 | 1591.25 | 49850.25 | 0 | 0 | 1350000 | 0 | 0
2021062016 | 1 | 0.79047 | 118570.5 | 0.1389 | 0 | 0.10005 | 1250.625 | 0.6522 | 52176 | 64000 | 1250.625 | 52176 | 1143.875 | 1143.875 | 1350000 | 1143.875 | 0
2021062017 | 1 | 0.80832 | 121248 | 0.10533 | 0 | 0.10049 | 1256.125 | 0.6074 | 48592 | 64000 | 1256.125 | 48592 | 7399.875 | 6256 | 1350000 | 7399.875 | 0
2021062018 | 1 | 0.81655 | 122482.5 | 0.12527 | 0 | 0.13553 | 1694.125 | 0.5014 | 40112 | 64000 | 1694.125 | 40112 | 16676.375 | 9276.5 | 1350000 | 16676.375 | 0
2021062019 | 1 | 0.81017 | 121525.5 | 0.1357 | 0 | 0.17494 | 2186.75 | 0.25448 | 20358.4 | 64000 | 2186.75 | 20358.4 | 34980.35 | 18303.975 | 1340485.9 | 34980.35 | 0
2021062020 | 1 | 0.79229 | 118843.5 | 0.15866 | 0 | 0.19192 | 2399 | 0.03572 | 2857.6 | 64000 | 2399 | 2857.6 | 49586.9 | 14606.55 | 1316365.25 | 49586.9 | 0
2021062021 | 1 | 0.77058 | 115587 | 0.23873 | 0 | 0.20855 | 2606.875 | 0 | 0 | 64000 | 2606.875 | 0 | 48980.125 | -606.775 | 1292851.375 | 48980.125 | 0
2021062022 | 1 | 0.7527 | 112905 | 0.34395 | 0 | 0.25171 | 3146.375 | 0 | 0 | 64000 | 3146.375 | 0 | 45758.625 | -3221.5 | 1272559 | 45758.625 | 0
2021062023 | 1 | 0.71273 | 106909.5 | 0.40979 | 0 | 0.26085 | 3260.625 | 0 | 0 | 64000 | 3260.625 | 0 | 39648.875 | -6109.75 | 1258376.375 | 39648.875 | 0
2021062024 | 1 | 0.66432 | 99648 | 0.46313 | 0 | 0.25538 | 3192.25 | 0 | 0 | 64000 | 3192.25 | 0 | 32455.75 | -7193.125 | 1251386.875 | 32455.75 | 0
2021062101 | 2 | 0.61874 | 92811 | 0.54841 | 0 | 0.24008 | 3001 | 0 | 0 | 64000 | 3001 | 0 | 25810 | -6645.75 | 1251043.125 | 25810 | 0
2021062102 | 2 | 0.58346 | 87519 | 0.53646 | 0 | 0.21211 | 2651.375 | 0 | 0 | 64000 | 2651.375 | 0 | 20867.625 | -4942.375 | 1255641.75 | 20867.625 | 0
2021062103 | 2 | 0.56046 | 84069 | 0.57352 | 0 | 0.20564 | 2570.5 | 0 | 0 | 64000 | 2570.5 | 0 | 17498.5 | -3369.125 | 1263609.5 | 17498.5 | 0
2021062104 | 2 | 0.54623 | 81934.5 | 0.52745 | 0 | 0.18971 | 2371.375 | 0 | 0 | 64000 | 2371.375 | 0 | 15563.125 | -1935.375 | 1273512.625 | 15563.125 | 0
2021062105 | 2 | 0.54699 | 82048.5 | 0.55676 | 0 | 0.16591 | 2073.875 | 0 | 0 | 64000 | 2073.875 | 0 | 15974.625 | 411.5 | 1283004.25 | 15974.625 | 0
2021062106 | 2 | 0.56587 | 84880.5 | 0.65453 | 0 | 0.13524 | 1690.5 | 0.00406 | 324.8 | 64000 | 1690.5 | 324.8 | 18865.2 | 2890.575 | 1289605.3 | 18865.2 | 0
2021062107 | 2 | 0.59414 | 89121 | 0.71435 | 0 | 0.12313 | 1539.125 | 0.10752 | 8601.6 | 64000 | 1539.125 | 8601.6 | 14980.275 | -3884.925 | 1300091.275 | 14980.275 | 0
2021062108 | 2 | 0.63222 | 94833 | 0.68818 | 0 | 0.15622 | 1952.75 | 0.31799 | 25439.2 | 64000 | 1952.75 | 25439.2 | 3441.05 | -11539.225 | 1322116.475 | 3441.05 | 0
2021062109 | 2 | 0.67101 | 100651.5 | 0.64864 | 0 | 0.18764 | 2345.5 | 0.38344 | 30675.2 | 64000 | 2345.5 | 30675.2 | 3630.8 | 189.75 | 1343951.925 | 3630.8 | 0
2021062110 | 2 | 0.71021 | 106531.5 | 0.54131 | 0 | 0.21527 | 2690.875 | 0.4769 | 38152 | 64000 | 2690.875 | 38152 | 1688.625 | -1942.175 | 1350000 | 1688.625 | 0
2021062111 | 2 | 0.74969 | 112453.5 | 0.47412 | 0 | 0.23451 | 2931.375 | 0.56392 | 45113.6 | 64000 | 2931.375 | 45113.6 | 408.525 | -1280.1 | 1350000 | 408.525 | 0
2021062112 | 2 | 0.78838 | 118257 | 0.53484 | 0 | 0.2059 | 2573.75 | 0.60579 | 48463.2 | 64000 | 2573.75 | 48463.2 | 3220.05 | 2811.525 | 1350000 | 3220.05 | 0
2021062113 | 2 | 0.81934 | 122901 | 0.57735 | 0 | 0.17659 | 2207.375 | 0.61008 | 48806.4 | 64000 | 2207.375 | 48806.4 | 7887.225 | 4667.175 | 1350000 | 7887.225 | 0
2021062114 | 2 | 0.84042 | 126063 | 0.60979 | 0 | 0.1332 | 1665 | 0.59518 | 47614.4 | 64000 | 1665 | 47614.4 | 12783.6 | 4896.375 | 1350000 | 12783.6 | 0
2021062115 | 2 | 0.85314 | 127971 | 0.6517 | 0 | 0.12086 | 1510.75 | 0.59416 | 47532.8 | 64000 | 1510.75 | 47532.8 | 14927.45 | 2143.85 | 1350000 | 14927.45 | 0
2021062116 | 2 | 0.8591 | 128865 | 0.77907 | 0 | 0.12674 | 1584.25 | 0.57996 | 46396.8 | 64000 | 1584.25 | 46396.8 | 16883.95 | 1956.5 | 1350000 | 16883.95 | 0
2021062117 | 2 | 0.85602 | 128403 | 0.82717 | 0 | 0.10826 | 1353.25 | 0.51953 | 41562.4 | 64000 | 1353.25 | 41562.4 | 21487.35 | 4603.4 | 1350000 | 21487.35 | 0
2021062118 | 2 | 0.84378 | 126567 | 0.85972 | 0 | 0.09204 | 1150.5 | 0.43241 | 34592.8 | 64000 | 1150.5 | 34592.8 | 26823.7 | 5336.35 | 1348642.55 | 26823.7 | 0
2021062119 | 2 | 0.81539 | 122308.5 | 0.6329 | 0 | 0.09715 | 1214.375 | 0.23356 | 18684.8 | 64000 | 1214.375 | 18684.8 | 38409.325 | 11585.625 | 1335699.475 | 38409.325 | 0
2021062120 | 2 | 0.77709 | 116563.5 | 0.61445 | 0 | 0.09999 | 1249.875 | 0.03767 | 3013.6 | 64000 | 1249.875 | 3013.6 | 48300.025 | 9890.7 | 1312865.7 | 48300.025 | 0
2021062121 | 2 | 0.7425 | 111375 | 0.65868 | 0 | 0.09531 | 1191.375 | 0 | 0 | 64000 | 1191.375 | 0 | 46183.625 | -2116.4 | 1292148.325 | 46183.625 | 0
2021062122 | 2 | 0.7135 | 107025 | 0.55555 | 0 | 0.10559 | 1319.875 | 0 | 0 | 64000 | 1319.875 | 0 | 41705.125 | -4478.5 | 1275909.45 | 41705.125 | 0
2021062123 | 2 | 0.66867 | 100300.5 | 0.48229 | 0 | 0.10428 | 1303.5 | 0 | 0 | 64000 | 1303.5 | 0 | 34997 | -6708.125 | 1266378.7 | 34997 | 0
2021062124 | 2 | 0.61631 | 92446.5 | 0.34792 | 0 | 0.09987 | 1248.375 | 0 | 0 | 64000 | 1248.375 | 0 | 27198.125 | -7798.875 | 1264646.825 | 27198.125 | 0
2021062201 | 3 | 0.57323 | 85984.5 | 0.28567 | 0 | 0.09506 | 1188.25 | 0 | 0 | 64000 | 1188.25 | 0 | 20796.25 | -6401.875 | 1269316.825 | 20796.25 | 0
2021062202 | 3 | 0.5425 | 81375 | 0.38426 | 0 | 0.07976 | 997 | 0 | 0 | 64000 | 997 | 0 | 16378 | -4418.25 | 1278405.075 | 16378 | 0
2021062203 | 3 | 0.52143 | 78214.5 | 0.41031 | 0 | 0.07691 | 961.375 | 0 | 0 | 64000 | 961.375 | 0 | 13253.125 | -3124.875 | 1290618.2 | 13253.125 | 0
2021062204 | 3 | 0.50849 | 76273.5 | 0.36461 | 0 | 0.08814 | 1101.75 | 0 | 0 | 64000 | 1101.75 | 0 | 11171.75 | -2081.375 | 1304912.7 | 11171.75 | 0
2021062205 | 3 | 0.50749 | 76123.5 | 0.29343 | 0 | 0.08087 | 1010.875 | 0 | 0 | 64000 | 1010.875 | 0 | 11112.625 | -59.125 | 1319266.325 | 11112.625 | 0
2021062206 | 3 | 0.52127 | 78190.5 | 0.22199 | 0 | 0.08046 | 1005.75 | 0.00357 | 285.6 | 64000 | 1005.75 | 285.6 | 12899.15 | 1786.525 | 1331833.425 | 12899.15 | 0
2021062207 | 3 | 0.54781 | 82171.5 | 0.28182 | 0 | 0.05932 | 741.5 | 0.09186 | 7348.8 | 64000 | 741.5 | 7348.8 | 10081.2 | -2817.95 | 1347218.475 | 10081.2 | 0
2021062208 | 3 | 0.58147 | 87220.5 | 0.30032 | 0 | 0.04661 | 582.625 | 0.29398 | 23518.4 | 64000 | 582.625 | 22637.875 | 0 | -10081.2 | 1350000 | 0 | 0
2021062209 | 3 | 0.60814 | 91221 | 0.29838 | 0 | 0.06468 | 808.5 | 0.46824 | 37459.2 | 64000 | 808.5 | 26412.5 | 0 | 0 | 1350000 | 0 | 0
2021062210 | 3 | 0.62634 | 93951 | 0.31103 | 0 | 0.07086 | 885.75 | 0.53058 | 42446.4 | 64000 | 885.75 | 29065.25 | 0 | 0 | 1350000 | 0 | 0
2021062211 | 3 | 0.6378 | 95670 | 0.31052 | 0 | 0.08454 | 1056.75 | 0.53847 | 43077.6 | 64000 | 1056.75 | 30613.25 | 0 | 0 | 1350000 | 0 | 0
2021062212 | 3 | 0.64219 | 96328.5 | 0.33369 | 0 | 0.09114 | 1139.25 | 0.5579 | 44632 | 64000 | 1139.25 | 31189.25 | 0 | 0 | 1350000 | 0 | 0
2021062213 | 3 | 0.64085 | 96127.5 | 0.51071 | 0 | 0.07167 | 895.875 | 0.57555 | 46044 | 64000 | 895.875 | 31231.625 | 0 | 0 | 1350000 | 0 | 0
2021062214 | 3 | 0.63884 | 95826 | 0.60361 | 0 | 0.06535 | 816.875 | 0.60353 | 48282.4 | 64000 | 816.875 | 31009.125 | 0 | 0 | 1350000 | 0 | 0
2021062215 | 3 | 0.63298 | 94947 | 0.65384 | 0 | 0.06508 | 813.5 | 0.62123 | 49698.4 | 64000 | 813.5 | 30133.5 | 0 | 0 | 1350000 | 0 | 0
2021062216 | 3 | 0.62677 | 94015.5 | 0.76476 | 0 | 0.06429 | 803.625 | 0.59982 | 47985.6 | 64000 | 803.625 | 29211.875 | 0 | 0 | 1350000 | 0 | 0
2021062217 | 3 | 0.62555 | 93832.5 | 0.80983 | 0 | 0.06216 | 777 | 0.53686 | 42948.8 | 64000 | 777 | 29055.5 | 0 | 0 | 1350000 | 0 | 0
2021062218 | 3 | 0.62471 | 93706.5 | 0.78211 | 0 | 0.07221 | 902.625 | 0.41878 | 33502.4 | 64000 | 902.625 | 28803.875 | 0 | 0 | 1350000 | 0 | 0
2021062219 | 3 | 0.61759 | 92638.5 | 0.70209 | 0 | 0.09875 | 1234.375 | 0.22293 | 17834.4 | 64000 | 1234.375 | 17834.4 | 9569.725 | 9569.725 | 1350000 | 9569.725 | 0
2021062220 | 3 | 0.60491 | 90736.5 | 0.64319 | 0 | 0.10654 | 1331.75 | 0.03889 | 3111.2 | 64000 | 1331.75 | 3111.2 | 22293.55 | 12723.825 | 1350000 | 22293.55 | 0
2021062221 | 3 | 0.59008 | 88512 | 0.56772 | 0 | 0.11733 | 1466.625 | 0 | 0 | 64000 | 1466.625 | 0 | 23045.375 | 751.825 | 1350000 | 23045.375 | 0
2021062222 | 3 | 0.57963 | 86944.5 | 0.54784 | 0 | 0.13702 | 1712.75 | 0 | 0 | 64000 | 1712.75 | 0 | 21231.75 | -1813.625 | 1350000 | 21231.75 | 0
2021062223 | 3 | 0.54859 | 82288.5 | 0.45729 | 0 | 0.12434 | 1554.25 | 0 | 0 | 64000 | 1554.25 | 0 | 16734.25 | -4497.5 | 1350000 | 16734.25 | 0
2021062224 | 3 | 0.50997 | 76495.5 | 0.41552 | 0 | 0.12796 | 1599.5 | 0 | 0 | 64000 | 1599.5 | 0 | 10896 | -5838.25 | 1350000 | 10896 | 0
2021062301 | 4 | 0.4791 | 71865 | 0.38338 | 0 | 0.15037 | 1879.625 | 0 | 0 | 64000 | 1879.625 | 0 | 5985.375 | -4910.625 | 1350000 | 5985.375 | 0
2021062302 | 4 | 0.45592 | 68388 | 0.3344 | 0 | 0.15882 | 1985.25 | 0 | 0 | 64000 | 1985.25 | 0 | 2402.75 | -3582.625 | 1350000 | 2402.75 | 0
2021062303 | 4 | 0.44309 | 66463.5 | 0.37366 | 0 | 0.15975 | 1996.875 | 0 | 0 | 64000 | 1996.875 | 0 | 466.625 | -1936.125 | 1350000 | 466.625 | 0
2021062304 | 4 | 0.43675 | 65512.5 | 0.44548 | 0 | 0.1655 | 2068.75 | 0 | 0 | 64000 | 1512.5 | 0 | 0 | -466.625 | 1350000 | 0 | 0
2021062305 | 4 | 0.44018 | 66027 | 0.40553 | 0 | 0.21322 | 2665.25 | 0 | 0 | 64000 | 2027 | 0 | 0 | 0 | 1350000 | 0 | 0
2021062306 | 4 | 0.45572 | 68358 | 0.39337 | 0 | 0.22427 | 2803.375 | 0.00504 | 403.2 | 64000 | 2803.375 | 403.2 | 1151.425 | 1151.425 | 1350000 | 1151.425 | 0
2021062307 | 4 | 0.48188 | 72282 | 0.36267 | 0 | 0.23172 | 2896.5 | 0.06349 | 5079.2 | 64000 | 2896.5 | 5079.2 | 306.3 | -845.125 | 1350000 | 306.3 | 0
2021062308 | 4 | 0.51299 | 76948.5 | 0.27171 | 0 | 0.26739 | 3342.375 | 0.212 | 16960 | 64000 | 3342.375 | 9606.125 | 0 | -306.3 | 1350000 | 0 | 0
2021062309 | 4 | 0.53393 | 80089.5 | 0.10824 | 0 | 0.26793 | 3349.125 | 0.34262 | 27409.6 | 64000 | 3349.125 | 12740.375 | 0 | 0 | 1350000 | 0 | 0
2021062310 | 4 | 0.54937 | 82405.5 | 0.09332 | 0 | 0.25104 | 3138 | 0.38211 | 30568.8 | 64000 | 3138 | 15267.5 | 0 | 0 | 1350000 | 0 | 0
2021062311 | 4 | 0.56266 | 84399 | 0.13051 | 0 | 0.21459 | 2682.375 | 0.37461 | 29968.8 | 64000 | 2682.375 | 17716.625 | 0 | 0 | 1350000 | 0 | 0
2021062312 | 4 | 0.57312 | 85968 | 0.14584 | 0 | 0.20236 | 2529.5 | 0.4688 | 37504 | 64000 | 2529.5 | 19438.5 | 0 | 0 | 1350000 | 0 | 0
2021062313 | 4 | 0.58445 | 87667.5 | 0.1326 | 0 | 0.17669 | 2208.625 | 0.48498 | 38798.4 | 64000 | 2208.625 | 21458.875 | 0 | 0 | 1350000 | 0 | 0
2021062314 | 4 | 0.59664 | 89496 | 0.08645 | 0 | 0.1833 | 2291.25 | 0.50907 | 40725.6 | 64000 | 2291.25 | 23204.75 | 0 | 0 | 1350000 | 0 | 0
2021062315 | 4 | 0.61105 | 91657.5 | 0.04207 | 0 | 0.1989 | 2486.25 | 0.44708 | 35766.4 | 64000 | 2486.25 | 25171.25 | 0 | 0 | 1350000 | 0 | 0
2021062316 | 4 | 0.62425 | 93637.5 | 0.02172 | 0 | 0.20724 | 2590.5 | 0.39441 | 31552.8 | 64000 | 2590.5 | 27047 | 0 | 0 | 1350000 | 0 | 0
2021062317 | 4 | 0.64005 | 96007.5 | 0.00758 | 0 | 0.21816 | 2727 | 0.30646 | 24516.8 | 64000 | 2727 | 24516.8 | 4763.7 | 4763.7 | 1350000 | 4763.7 | 0
2021062318 | 4 | 0.65355 | 98032.5 | 0.00012 | 0 | 0.2541 | 3176.25 | 0.19435 | 15548 | 64000 | 3176.25 | 15548 | 15308.25 | 10544.55 | 1350000 | 15308.25 | 0
2021062319 | 4 | 0.65453 | 98179.5 | 0.00283 | 0 | 0.28713 | 3589.125 | 0.10025 | 8020 | 64000 | 3589.125 | 8020 | 22570.375 | 7262.125 | 1350000 | 22570.375 | 0
2021062320 | 4 | 0.64172 | 96258 | 0.01795 | 0 | 0.29237 | 3654.625 | 0.01785 | 1428 | 64000 | 3654.625 | 1428 | 27175.375 | 4605 | 1348290.875 | 27175.375 | 0
2021062321 | 4 | 0.62021 | 93031.5 | 0.05871 | 0 | 0.26676 | 3334.5 | 0 | 0 | 64000 | 3334.5 | 0 | 25697 | -1478.375 | 1348060.125 | 25697 | 0
2021062322 | 4 | 0.60613 | 90919.5 | 0.16693 | 0 | 0.2659 | 3323.75 | 0 | 0 | 64000 | 3323.75 | 0 | 23595.75 | -2101.25 | 1349930.625 | 23595.75 | 0
2021062323 | 4 | 0.57108 | 85662 | 0.30418 | 0 | 0.28159 | 3519.875 | 0 | 0 | 64000 | 3519.875 | 0 | 18142.125 | -5453.625 | 1350000 | 18142.125 | 0
2021062324 | 4 | 0.52913 | 79369.5 | 0.39623 | 0 | 0.25217 | 3152.125 | 0 | 0 | 64000 | 3152.125 | 0 | 12217.375 | -5924.75 | 1350000 | 12217.375 | 0
2021062401 | 5 | 0.49218 | 73827 | 0.45797 | 0 | 0.23723 | 2965.375 | 0 | 0 | 64000 | 2965.375 | 0 | 6861.625 | -5355.75 | 1350000 | 6861.625 | 0
2021062402 | 5 | 0.46746 | 70119 | 0.4996 | 0 | 0.24437 | 3054.625 | 0 | 0 | 64000 | 3054.625 | 0 | 3064.375 | -3797.25 | 1350000 | 3064.375 | 0
2021062403 | 5 | 0.45238 | 67857 | 0.49618 | 0 | 0.26568 | 3321 | 0 | 0 | 64000 | 3321 | 0 | 536 | -2528.375 | 1350000 | 536 | 0
2021062404 | 5 | 0.44357 | 66535.5 | 0.50459 | 0 | 0.26241 | 3280.125 | 0 | 0 | 64000 | 2535.5 | 0 | 0 | -536 | 1350000 | 0 | 0
2021062405 | 5 | 0.44552 | 66828 | 0.49388 | 0 | 0.23296 | 2912 | 0 | 0 | 64000 | 2828 | 0 | 0 | 0 | 1350000 | 0 | 0
2021062406 | 5 | 0.46083 | 69124.5 | 0.51226 | 0 | 0.17621 | 2202.625 | 0.00222 | 177.6 | 64000 | 2202.625 | 177.6 | 2744.275 | 2744.275 | 1350000 | 2744.275 | 0
2021062407 | 5 | 0.48681 | 73021.5 | 0.4954 | 0 | 0.16051 | 2006.375 | 0.07839 | 6271.2 | 64000 | 2006.375 | 6271.2 | 743.925 | -2000.35 | 1350000 | 743.925 | 0
2021062408 | 5 | 0.51977 | 77965.5 | 0.45312 | 0 | 0.17047 | 2130.875 | 0.2937 | 23496 | 64000 | 2130.875 | 11834.625 | 0 | -743.925 | 1350000 | 0 | 0
2021062409 | 5 | 0.54656 | 81984 | 0.41489 | 0 | 0.16155 | 2019.375 | 0.45033 | 36026.4 | 64000 | 2019.375 | 15964.625 | 0 | 0 | 1350000 | 0 | 0
2021062410 | 5 | 0.56953 | 85429.5 | 0.51424 | 0 | 0.13733 | 1716.625 | 0.49903 | 39922.4 | 64000 | 1716.625 | 19712.875 | 0 | 0 | 1350000 | 0 | 0
2021062411 | 5 | 0.59305 | 88957.5 | 0.60963 | 0 | 0.10519 | 1314.875 | 0.54756 | 43804.8 | 64000 | 1314.875 | 23642.625 | 0 | 0 | 1350000 | 0 | 0
2021062412 | 5 | 0.61398 | 92097 | 0.62624 | 0 | 0.08053 | 1006.625 | 0.5889 | 47112 | 64000 | 1006.625 | 27090.375 | 0 | 0 | 1350000 | 0 | 0
2021062413 | 5 | 0.63619 | 95428.5 | 0.60166 | 0 | 0.10706 | 1338.25 | 0.61858 | 49486.4 | 64000 | 1338.25 | 30090.25 | 0 | 0 | 1350000 | 0 | 0
2021062414 | 5 | 0.65343 | 98014.5 | 0.5658 | 0 | 0.08468 | 1058.5 | 0.62968 | 50374.4 | 64000 | 1058.5 | 32956 | 0 | 0 | 1350000 | 0 | 0
2021062415 | 5 | 0.66407 | 99610.5 | 0.55399 | 0 | 0.08753 | 1094.125 | 0.61984 | 49587.2 | 64000 | 1094.125 | 34516.375 | 0 | 0 | 1350000 | 0 | 0
2021062416 | 5 | 0.68572 | 102858 | 0.53357 | 0 | 0.10373 | 1296.625 | 0.60719 | 48575.2 | 64000 | 1296.625 | 37561.375 | 0 | 0 | 1350000 | 0 | 0
2021062417 | 5 | 0.70304 | 105456 | 0.55573 | 0 | 0.10589 | 1323.625 | 0.56932 | 45545.6 | 64000 | 1323.625 | 40132.375 | 0 | 0 | 1350000 | 0 | 0
2021062418 | 5 | 0.71173 | 106759.5 | 0.5408 | 0 | 0.11205 | 1400.625 | 0.46591 | 37272.8 | 64000 | 1400.625 | 37272.8 | 4086.075 | 4086.075 | 1350000 | 4086.075 | 0
2021062419 | 5 | 0.7053 | 105795 | 0.47411 | 0 | 0.16115 | 2014.375 | 0.25134 | 20107.2 | 64000 | 2014.375 | 20107.2 | 19673.425 | 15587.35 | 1350000 | 19673.425 | 0
2021062420 | 5 | 0.688 | 103200 | 0.38667 | 0 | 0.23564 | 2945.5 | 0.04445 | 3556 | 64000 | 2945.5 | 3556 | 32698.5 | 13025.075 | 1342767.75 | 32698.5 | 0
2021062421 | 5 | 0.66271 | 99406.5 | 0.40607 | 0 | 0.21761 | 2720.125 | 0.00033 | 26.4 | 64000 | 2720.125 | 26.4 | 32659.975 | -38.525 | 1335574.025 | 32659.975 | 0
2021062422 | 5 | 0.6487 | 97305 | 0.51356 | 0 | 0.22479 | 2809.875 | 0 | 0 | 64000 | 2809.875 | 0 | 30495.125 | -2164.85 | 1330545.15 | 30495.125 | 0
2021062423 | 5 | 0.6112 | 91680 | 0.59466 | 0 | 0.21691 | 2711.375 | 0 | 0 | 64000 | 2711.375 | 0 | 24968.625 | -5526.5 | 1331042.775 | 24968.625 | 0
2021062424 | 5 | 0.56613 | 84919.5 | 0.72085 | 0 | 0.24633 | 3079.125 | 0 | 0 | 64000 | 3079.125 | 0 | 17840.375 | -7128.25 | 1338668.65 | 17840.375 | 0
2021062501 | 6 | 0.52699 | 79048.5 | 0.77389 | 0 | 0.17843 | 2230.375 | 0 | 0 | 64000 | 2230.375 | 0 | 12818.125 | -5022.25 | 1350000 | 12818.125 | 0
2021062502 | 6 | 0.49889 | 74833.5 | 0.79708 | 0 | 0.17736 | 2217 | 0 | 0 | 64000 | 2217 | 0 | 8616.5 | -4201.625 | 1350000 | 8616.5 | 0
2021062503 | 6 | 0.48144 | 72216 | 0.68101 | 0 | 0.11944 | 1493 | 0 | 0 | 64000 | 1493 | 0 | 6723 | -1893.5 | 1350000 | 6723 | 0
2021062504 | 6 | 0.47223 | 70834.5 | 0.61086 | 0 | 0.10923 | 1365.375 | 0 | 0 | 64000 | 1365.375 | 0 | 5469.125 | -1253.875 | 1350000 | 5469.125 | 0
2021062505 | 6 | 0.47367 | 71050.5 | 0.61458 | 0 | 0.08527 | 1065.875 | 0 | 0 | 64000 | 1065.875 | 0 | 5984.625 | 515.5 | 1350000 | 5984.625 | 0
2021062506 | 6 | 0.48685 | 73027.5 | 0.64197 | 0 | 0.0648 | 810 | 0.0069 | 552 | 64000 | 810 | 552 | 7665.5 | 1680.875 | 1350000 | 7665.5 | 0
2021062507 | 6 | 0.51221 | 76831.5 | 0.60809 | 0 | 0.07382 | 922.75 | 0.06961 | 5568.8 | 64000 | 922.75 | 5568.8 | 6339.95 | -1325.55 | 1350000 | 6339.95 | 0
2021062508 | 6 | 0.54702 | 82053 | 0.50257 | 0 | 0.10563 | 1320.375 | 0.15618 | 12494.4 | 64000 | 1320.375 | 12494.4 | 4238.225 | -2101.725 | 1350000 | 4238.225 | 0
2021062509 | 6 | 0.57899 | 86848.5 | 0.31267 | 0 | 0.09335 | 1166.875 | 0.27204 | 21763.2 | 64000 | 1166.875 | 21681.625 | 0 | -4238.225 | 1350000 | 0 | 0
2021062510 | 6 | 0.603 | 90450 | 0.24908 | 0 | 0.07437 | 929.625 | 0.35427 | 28341.6 | 64000 | 929.625 | 25520.375 | 0 | 0 | 1350000 | 0 | 0
2021062511 | 6 | 0.62632 | 93948 | 0.25157 | 0 | 0.06598 | 824.75 | 0.47532 | 38025.6 | 64000 | 824.75 | 29123.25 | 0 | 0 | 1350000 | 0 | 0
2021062512 | 6 | 0.64831 | 97246.5 | 0.20944 | 0 | 0.06829 | 853.625 | 0.58057 | 46445.6 | 64000 | 853.625 | 32392.875 | 0 | 0 | 1350000 | 0 | 0
2021062513 | 6 | 0.66982 | 100473 | 0.24796 | 0 | 0.07167 | 895.875 | 0.59597 | 47677.6 | 64000 | 895.875 | 35577.125 | 0 | 0 | 1350000 | 0 | 0
2021062514 | 6 | 0.69072 | 103608 | 0.24653 | 0 | 0.06955 | 869.375 | 0.61709 | 49367.2 | 64000 | 869.375 | 38738.625 | 0 | 0 | 1350000 | 0 | 0
2021062515 | 6 | 0.70996 | 106494 | 0.29612 | 0 | 0.06738 | 842.25 | 0.62652 | 50121.6 | 64000 | 842.25 | 41651.75 | 0 | 0 | 1350000 | 0 | 0
2021062516 | 6 | 0.72399 | 108598.5 | 0.36869 | 0 | 0.07695 | 961.875 | 0.59467 | 47573.6 | 64000 | 961.875 | 43636.625 | 0 | 0 | 1350000 | 0 | 0
2021062517 | 6 | 0.73687 | 110530.5 | 0.37871 | 0 | 0.06124 | 765.5 | 0.53838 | 43070.4 | 64000 | 765.5 | 43070.4 | 2694.6 | 2694.6 | 1350000 | 2694.6 | 0
2021062518 | 6 | 0.73993 | 110989.5 | 0.40916 | 0 | 0.07713 | 964.125 | 0.43941 | 35152.8 | 64000 | 964.125 | 35152.8 | 10872.575 | 8177.975 | 1350000 | 10872.575 | 0
2021062519 | 6 | 0.72917 | 109375.5 | 0.4112 | 0 | 0.08327 | 1040.875 | 0.23452 | 18761.6 | 64000 | 1040.875 | 18761.6 | 25573.025 | 14700.45 | 1349893.225 | 25573.025 | 0
2021062520 | 6 | 0.70898 | 106347 | 0.47461 | 0 | 0.08273 | 1034.125 | 0.03637 | 2909.6 | 64000 | 1034.125 | 2909.6 | 38403.275 | 12830.25 | 1336956.2 | 38403.275 | 0
2021062521 | 6 | 0.68774 | 103161 | 0.56199 | 0 | 0.07955 | 994.375 | 0 | 0 | 64000 | 994.375 | 0 | 38166.625 | -236.65 | 1324255.825 | 38166.625 | 0
2021062522 | 6 | 0.6744 | 101160 | 0.71628 | 0 | 0.08479 | 1059.875 | 0 | 0 | 64000 | 1059.875 | 0 | 36100.125 | -2066.5 | 1313621.95 | 36100.125 | 0
2021062523 | 6 | 0.64331 | 96496.5 | 0.80296 | 0 | 0.09825 | 1228.125 | 0 | 0 | 64000 | 1228.125 | 0 | 31268.375 | -4831.75 | 1307819.825 | 31268.375 | 0
2021062524 | 6 | 0.6019 | 90285 | 0.82709 | 0 | 0.11216 | 1402 | 0 | 0 | 64000 | 1402 | 0 | 24883 | -6385.375 | 1308403.075 | 24883 | 0
2021062601 | 7 | 0.56521 | 84781.5 | 0.77006 | 0 | 0.09431 | 1178.875 | 0 | 0 | 64000 | 1178.875 | 0 | 19602.625 | -5280.375 | 1314266.7 | 19602.625 | 0
2021062602 | 7 | 0.53531 | 80296.5 | 0.76589 | 0 | 0.09243 | 1155.375 | 0 | 0 | 64000 | 1155.375 | 0 | 15141.125 | -4461.5 | 1324591.825 | 15141.125 | 0
2021062603 | 7 | 0.51674 | 77511 | 0.7872 | 0 | 0.11128 | 1391 | 0 | 0 | 64000 | 1391 | 0 | 12120 | -3021.125 | 1337938.075 | 12120 | 0
2021062604 | 7 | 0.50356 | 75534 | 0.74055 | 0 | 0.11617 | 1452.125 | 0 | 0 | 64000 | 1452.125 | 0 | 10081.875 | -2038.125 | 1350000 | 10081.875 | 0
2021062605 | 7 | 0.49765 | 74647.5 | 0.75243 | 0 | 0.13146 | 1643.25 | 0 | 0 | 64000 | 1643.25 | 0 | 9004.25 | -1077.625 | 1350000 | 9004.25 | 0
2021062606 | 7 | 0.50121 | 75181.5 | 0.71202 | 0 | 0.143 | 1787.5 | 0.00048 | 38.4 | 64000 | 1787.5 | 38.4 | 9355.6 | 351.35 | 1350000 | 9355.6 | 0
2021062607 | 7 | 0.50908 | 76362 | 0.72691 | 0 | 0.15127 | 1890.875 | 0.01953 | 1562.4 | 64000 | 1890.875 | 1562.4 | 8908.725 | -446.875 | 1350000 | 8908.725 | 0
2021062608 | 7 | 0.53345 | 80017.5 | 0.67904 | 0 | 0.16343 | 2042.875 | 0.04386 | 3508.8 | 64000 | 2042.875 | 3508.8 | 10465.825 | 1557.1 | 1350000 | 10465.825 | 0
2021062609 | 7 | 0.57302 | 85953 | 0.53717 | 0 | 0.17826 | 2228.25 | 0.08695 | 6956 | 64000 | 2228.25 | 6956 | 12768.75 | 2302.925 | 1350000 | 12768.75 | 0
2021062610 | 7 | 0.6151 | 92265 | 0.41266 | 0 | 0.16835 | 2104.375 | 0.12306 | 9844.8 | 64000 | 2104.375 | 9844.8 | 16315.825 | 3547.075 | 1350000 | 16315.825 | 0
2021062611 | 7 | 0.65723 | 98584.5 | 0.37213 | 0 | 0.15041 | 1880.125 | 0.18363 | 14690.4 | 64000 | 1880.125 | 14690.4 | 18013.975 | 1698.15 | 1350000 | 18013.975 | 0
2021062612 | 7 | 0.69125 | 103687.5 | 0.29864 | 0 | 0.0987 | 1233.75 | 0.21849 | 17479.2 | 64000 | 1233.75 | 17479.2 | 20974.55 | 2960.575 | 1350000 | 20974.55 | 0
2021062613 | 7 | 0.71987 | 107980.5 | 0.3024 | 0 | 0.07268 | 908.5 | 0.24952 | 19961.6 | 64000 | 908.5 | 19961.6 | 23110.4 | 2135.85 | 1350000 | 23110.4 | 0
2021062614 | 7 | 0.73838 | 110757 | 0.33483 | 0 | 0.05346 | 668.25 | 0.24721 | 19776.8 | 64000 | 668.25 | 19776.8 | 26311.95 | 3201.55 | 1349154.3 | 26311.95 | 0
2021062615 | 7 | 0.75529 | 113293.5 | 0.37315 | 0 | 0.05598 | 699.75 | 0.23177 | 18541.6 | 64000 | 699.75 | 18541.6 | 30052.15 | 3740.2 | 1344568.4 | 30052.15 | 0
2021062616 | 7 | 0.77051 | 115576.5 | 0.42559 | 0 | 0.06246 | 780.75 | 0.20096 | 16076.8 | 64000 | 780.75 | 16076.8 | 34718.95 | 4666.8 | 1335315.7 | 34718.95 | 0
2021062617 | 7 | 0.78313 | 117469.5 | 0.44122 | 0 | 0.08197 | 1024.625 | 0.19284 | 15427.2 | 64000 | 1024.625 | 15427.2 | 37017.675 | 2298.725 | 1323764.275 | 37017.675 | 0
2021062618 | 7 | 0.79059 | 118588.5 | 0.4706 | 0 | 0.09143 | 1142.875 | 0.16281 | 13024.8 | 64000 | 1142.875 | 13024.8 | 40420.825 | 3403.15 | 1308809.7 | 40420.825 | 0
2021062619 | 7 | 0.78562 | 117843 | 0.48274 | 0 | 0.09818 | 1227.25 | 0.10343 | 8274.4 | 64000 | 1227.25 | 8274.4 | 44341.35 | 3920.525 | 1289934.6 | 44341.35 | 0
2021062620 | 7 | 0.76459 | 114688.5 | 0.4597 | 0 | 0.12469 | 1558.625 | 0.02655 | 2124 | 64000 | 1558.625 | 2124 | 47005.875 | 2664.525 | 1268394.975 | 47005.875 | 0
2021062621 | 7 | 0.73745 | 110617.5 | 0.4738 | 0 | 0.11278 | 1409.75 | 0 | 0 | 64000 | 1409.75 | 0 | 45207.75 | -1798.125 | 1248653.475 | 45207.75 | 0
2021062622 | 7 | 0.71869 | 107803.5 | 0.56256 | 0 | 0.108 | 1350 | 0 | 0 | 64000 | 1350 | 0 | 42453.5 | -2754.25 | 1231666.225 | 42453.5 | 0
2021062623 | 7 | 0.68386 | 102579 | 0.62514 | 0 | 0.11301 | 1412.625 | 0 | 0 | 64000 | 1412.625 | 0 | 37166.375 | -5287.125 | 1219966.1 | 37166.375 | 0
2021062624 | 7 | 0.63865 | 95797.5 | 0.64725 | 0 | 0.14077 | 1759.625 | 0 | 0 | 64000 | 1759.625 | 0 | 30037.875 | -7128.5 | 1215394.475 | 30037.875 | 0
2021062701 | 1 | 0.59682 | 89523 | 0.66196 | 0 | 0.13806 | 1725.75 | 0 | 0 | 64000 | 1725.75 | 0 | 23797.25 | -6240.625 | 1217063.475 | 23797.25 | 0
2021062702 | 1 | 0.56211 | 84316.5 | 0.64808 | 0 | 0.11837 | 1479.625 | 0 | 0 | 64000 | 1479.625 | 0 | 18836.875 | -4960.375 | 1223692.85 | 18836.875 | 0
2021062703 | 1 | 0.53707 | 80560.5 | 0.66496 | 0 | 0.10108 | 1263.5 | 0 | 0 | 64000 | 1263.5 | 0 | 15297 | -3539.875 | 1233862.1 | 15297 | 0
2021062704 | 1 | 0.52106 | 78159 | 0.66287 | 0 | 0.11974 | 1496.75 | 0 | 0 | 64000 | 1496.75 | 0 | 12662.25 | -2634.75 | 1246666.1 | 12662.25 | 0
2021062705 | 1 | 0.51156 | 76734 | 0.67433 | 0 | 0.10158 | 1269.75 | 0 | 0 | 64000 | 1269.75 | 0 | 11464.25 | -1198 | 1260668.1 | 11464.25 | 0
2021062706 | 1 | 0.50899 | 76348.5 | 0.67028 | 0 | 0.06777 | 847.125 | 0.00577 | 461.6 | 64000 | 847.125 | 461.6 | 11039.775 | -424.475 | 1275094.575 | 11039.775 | 0
2021062707 | 1 | 0.50827 | 76240.5 | 0.60502 | 0 | 0.07035 | 879.375 | 0.07813 | 6250.4 | 64000 | 879.375 | 6250.4 | 5110.725 | -5929.05 | 1295450.1 | 5110.725 | 0
2021062708 | 1 | 0.53321 | 79981.5 | 0.51478 | 0 | 0.08703 | 1087.875 | 0.25676 | 20540.8 | 64000 | 1087.875 | 14893.625 | 0 | -5110.725 | 1320916.35 | 0 | 0
2021062709 | 1 | 0.57829 | 86743.5 | 0.38772 | 0 | 0.10557 | 1319.625 | 0.42458 | 33966.4 | 64000 | 1319.625 | 21423.875 | 0 | 0 | 1346382.6 | 0 | 0
2021062710 | 1 | 0.63121 | 94681.5 | 0.31265 | 0 | 0.1204 | 1505 | 0.51458 | 41166.4 | 64000 | 1505 | 29176.5 | 0 | 0 | 1350000 | 0 | 0
2021062711 | 1 | 0.68145 | 102217.5 | 0.29321 | 0 | 0.12391 | 1548.875 | 0.54861 | 43888.8 | 64000 | 1548.875 | 36668.625 | 0 | 0 | 1350000 | 0 | 0
2021062712 | 1 | 0.72665 | 108997.5 | 0.32844 | 0 | 0.12661 | 1582.625 | 0.61468 | 49174.4 | 64000 | 1582.625 | 43414.875 | 0 | 0 | 1350000 | 0 | 0
2021062713 | 1 | 0.76323 | 114484.5 | 0.36708 | 0 | 0.07936 | 992 | 0.6166 | 49328 | 64000 | 992 | 49328 | 164.5 | 164.5 | 1350000 | 164.5 | 0
2021062714 | 1 | 0.79226 | 118839 | 0.36483 | 0 | 0.05966 | 745.75 | 0.6664 | 53312 | 64000 | 745.75 | 53312 | 781.25 | 616.75 | 1350000 | 781.25 | 0
2021062715 | 1 | 0.81504 | 122256 | 0.38889 | 0 | 0.04086 | 510.75 | 0.68137 | 54509.6 | 64000 | 510.75 | 54509.6 | 3235.65 | 2454.4 | 1350000 | 3235.65 | 0
2021062716 | 1 | 0.83499 | 125248.5 | 0.36506 | 0 | 0.03571 | 446.375 | 0.64471 | 51576.8 | 64000 | 446.375 | 51576.8 | 9225.325 | 5989.675 | 1350000 | 9225.325 | 0
2021062717 | 1 | 0.85288 | 127932 | 0.37354 | 0 | 0.03645 | 455.625 | 0.59524 | 47619.2 | 64000 | 455.625 | 47619.2 | 15857.175 | 6631.85 | 1350000 | 15857.175 | 0
2021062718 | 1 | 0.86274 | 129411 | 0.31091 | 0 | 0.09344 | 1168 | 0.48115 | 38492 | 64000 | 1168 | 38492 | 25751 | 9893.825 | 1349715.25 | 25751 | 0
2021062719 | 1 | 0.86147 | 129220.5 | 0.31908 | 0 | 0.15595 | 1949.375 | 0.24756 | 19804.8 | 64000 | 1949.375 | 19804.8 | 43466.325 | 17715.325 | 1331715.175 | 43466.325 | 0
2021062720 | 1 | 0.84145 | 126217.5 | 0.27407 | 0 | 0.17044 | 2130.5 | 0.03768 | 3014.4 | 64000 | 2130.5 | 3014.4 | 57072.6 | 13606.275 | 1300108.825 | 57072.6 | 0
2021062721 | 1 | 0.80863 | 121294.5 | 0.32259 | 0 | 0.1722 | 2152.5 | 0 | 0 | 64000 | 2152.5 | 0 | 55142 | -1930.6 | 1270433.075 | 55142 | 0
2021062722 | 1 | 0.7828 | 117420 | 0.44743 | 0 | 0.17467 | 2183.375 | 0 | 0 | 64000 | 2183.375 | 0 | 51236.625 | -3905.375 | 1244662.7 | 51236.625 | 0
2021062723 | 1 | 0.73778 | 110667 | 0.53343 | 0 | 0.18477 | 2309.625 | 0 | 0 | 64000 | 2309.625 | 0 | 44357.375 | -6879.25 | 1225771.575 | 44357.375 | 0
2021062724 | 1 | 0.68404 | 102606 | 0.56961 | 0 | 0.18358 | 2294.75 | 0 | 0 | 64000 | 2294.75 | 0 | 36311.25 | -8046.125 | 1214926.575 | 36311.25 | 0
2021062801 | 2 | 0.63478 | 95217 | 0.5524 | 0 | 0.16661 | 2082.625 | 0 | 0 | 64000 | 2082.625 | 0 | 29134.375 | -7176.875 | 1211258.45 | 29134.375 | 0
2021062802 | 2 | 0.59817 | 89725.5 | 0.52322 | 0 | 0.14986 | 1873.25 | 0 | 0 | 64000 | 1873.25 | 0 | 23852.25 | -5282.125 | 1212872.45 | 23852.25 | 0
2021062803 | 2 | 0.57395 | 86092.5 | 0.54116 | 0 | 0.12556 | 1569.5 | 0 | 0 | 64000 | 1569.5 | 0 | 20523 | -3329.25 | 1217815.7 | 20523 | 0
2021062804 | 2 | 0.55906 | 83859 | 0.54976 | 0 | 0.1035 | 1293.75 | 0 | 0 | 64000 | 1293.75 | 0 | 18565.25 | -1957.75 | 1224716.7 | 18565.25 | 0
2021062805 | 2 | 0.5571 | 83565 | 0.54048 | 0 | 0.09905 | 1238.125 | 0 | 0 | 64000 | 1238.125 | 0 | 18326.875 | -238.375 | 1231856.075 | 18326.875 | 0
2021062806 | 2 | 0.57127 | 85690.5 | 0.52869 | 0 | 0.11634 | 1454.25 | 0.00603 | 482.4 | 64000 | 1454.25 | 482.4 | 19753.85 | 1426.975 | 1237568.475 | 19753.85 | 0
2021062807 | 2 | 0.59982 | 89973 | 0.4733 | 0 | 0.1665 | 2081.25 | 0.10905 | 8724 | 64000 | 2081.25 | 8724 | 15167.75 | -4586.1 | 1247866.975 | 15167.75 | 0
2021062808 | 2 | 0.65085 | 97627.5 | 0.31032 | 0 | 0.22007 | 2750.875 | 0.32865 | 26292 | 64000 | 2750.875 | 26292 | 4584.625 | -10583.125 | 1268748.6 | 4584.625 | 0
2021062809 | 2 | 0.70361 | 105541.5 | 0.18343 | 0 | 0.20774 | 2596.75 | 0.50607 | 40485.6 | 64000 | 2596.75 | 38944.75 | 0 | -4584.625 | 1294214.85 | 0 | 0
2021062810 | 2 | 0.75704 | 113556 | 0.10149 | 0 | 0.17034 | 2129.25 | 0.60889 | 48711.2 | 64000 | 2129.25 | 47426.75 | 0 | 0 | 1319681.1 | 0 | 0
2021062811 | 2 | 0.80884 | 121326 | 0.07256 | 0 | 0.15418 | 1927.25 | 0.65592 | 52473.6 | 64000 | 1927.25 | 52473.6 | 2925.15 | 2925.15 | 1342222.2 | 2925.15 | 0
2021062812 | 2 | 0.85665 | 128497.5 | 0.03891 | 0 | 0.14416 | 1802 | 0.67902 | 54321.6 | 64000 | 1802 | 54321.6 | 8373.9 | 5448.75 | 1350000 | 8373.9 | 0
2021062813 | 2 | 0.89521 | 134281.5 | 0.03186 | 0 | 0.13975 | 1746.875 | 0.70517 | 56413.6 | 64000 | 1746.875 | 56413.6 | 12121.025 | 3747.125 | 1350000 | 12121.025 | 0
2021062814 | 2 | 0.92243 | 138364.5 | 0.04035 | 0 | 0.1388 | 1735 | 0.71403 | 57122.4 | 64000 | 1735 | 57122.4 | 15507.1 | 3386.075 | 1350000 | 15507.1 | 0
2021062815 | 2 | 0.9383 | 140745 | 0.08821 | 0 | 0.14619 | 1827.375 | 0.70485 | 56388 | 64000 | 1827.375 | 56388 | 18529.625 | 3022.525 | 1350000 | 18529.625 | 0
2021062816 | 2 | 0.94478 | 141717 | 0.12731 | 0 | 0.11823 | 1477.875 | 0.67753 | 54202.4 | 64000 | 1477.875 | 54202.4 | 22036.725 | 3507.1 | 1350000 | 22036.725 | 0
2021062817 | 2 | 0.94666 | 141999 | 0.14087 | 0 | 0.11175 | 1396.875 | 0.6163 | 49304 | 64000 | 1396.875 | 49304 | 27298.125 | 5261.4 | 1348168.125 | 27298.125 | 0
2021062818 | 2 | 0.94738 | 142107 | 0.16487 | 0 | 0.16688 | 2086 | 0.48439 | 38751.2 | 64000 | 2086 | 38751.2 | 37269.8 | 9971.675 | 1336364.575 | 37269.8 | 0
2021062819 | 2 | 0.9441 | 141615 | 0.15388 | 0 | 0.24386 | 3048.25 | 0.24053 | 19242.4 | 64000 | 3048.25 | 19242.4 | 55324.35 | 18054.55 | 1306506.475 | 55324.35 | 0
2021062820 | 2 | 0.92492 | 138738 | 0.18827 | 0 | 0.27659 | 3457.375 | 0.04019 | 3215.2 | 64000 | 3457.375 | 3215.2 | 68065.425 | 12741.075 | 1263907.3 | 68065.425 | 0
2021062821 | 2 | 0.88767 | 133150.5 | 0.19266 | 0 | 0.28759 | 3594.875 | 0 | 0 | 64000 | 3594.875 | 0 | 65555.625 | -2509.8 | 1223817.925 | 65555.625 | 0
2021062822 | 2 | 0.85528 | 128292 | 0.27531 | 0 | 0.31067 | 3883.375 | 0 | 0 | 64000 | 3883.375 | 0 | 60408.625 | -5147 | 1188875.55 | 60408.625 | 0
2021062823 | 2 | 0.79914 | 119871 | 0.26113 | 0 | 0.36937 | 4617.125 | 0 | 0 | 64000 | 4617.125 | 0 | 51253.875 | -9154.75 | 1163087.925 | 51253.875 | 0
2021062824 | 2 | 0.73676 | 110514 | 0.30076 | 0 | 0.42243 | 5280.375 | 0 | 0 | 64000 | 5280.375 | 0 | 41233.625 | -10020.25 | 1147320.55 | 41233.625 | 0
2021062901 | 3 | 0.68306 | 102459 | 0.35459 | 0 | 0.4342 | 5427.5 | 0 | 0 | 64000 | 5427.5 | 0 | 33031.5 | -8202.125 | 1139755.3 | 33031.5 | 0
2021062902 | 3 | 0.64248 | 96372 | 0.35173 | 0 | 0.38233 | 4779.125 | 0 | 0 | 64000 | 4779.125 | 0 | 27592.875 | -5438.625 | 1137628.675 | 27592.875 | 0
2021062903 | 3 | 0.61342 | 92013 | 0.34082 | 0 | 0.32868 | 4108.5 | 0 | 0 | 64000 | 4108.5 | 0 | 23904.5 | -3688.375 | 1139190.425 | 23904.5 | 0
2021062904 | 3 | 0.59291 | 88936.5 | 0.37812 | 0 | 0.27008 | 3376 | 0 | 0 | 64000 | 3376 | 0 | 21560.5 | -2344 | 1143096.175 | 21560.5 | 0
2021062905 | 3 | 0.58688 | 88032 | 0.30878 | 0 | 0.19983 | 2497.875 | 0 | 0 | 64000 | 2497.875 | 0 | 21534.125 | -26.375 | 1147028.3 | 21534.125 | 0
2021062906 | 3 | 0.59915 | 89872.5 | 0.25612 | 0 | 0.15347 | 1918.375 | 0.00658 | 526.4 | 64000 | 1918.375 | 526.4 | 23427.725 | 1893.6 | 1149066.825 | 23427.725 | 0
2021062907 | 3 | 0.62627 | 93940.5 | 0.20243 | 0 | 0.18983 | 2372.875 | 0.11386 | 9108.8 | 64000 | 2372.875 | 9108.8 | 18458.825 | -4968.9 | 1156074.25 | 18458.825 | 0
2021062908 | 3 | 0.67764 | 101646 | 0.12113 | 0 | 0.23376 | 2922 | 0.33973 | 27178.4 | 64000 | 2922 | 27178.4 | 7545.6 | -10913.225 | 1173994.9 | 7545.6 | 0
2021062909 | 3 | 0.73484 | 110226 | 0.03661 | 0 | 0.24331 | 3041.375 | 0.5272 | 42176 | 64000 | 3041.375 | 42176 | 1008.625 | -6536.975 | 1198452.525 | 1008.625 | 0
2021062910 | 3 | 0.78809 | 118213.5 | 0.00934 | 0 | 0.23007 | 2875.875 | 0.60215 | 48172 | 64000 | 2875.875 | 48172 | 3165.625 | 2157 | 1220753.15 | 3165.625 | 0
2021062911 | 3 | 0.84028 | 126042 | 0.00741 | 0 | 0.19747 | 2468.375 | 0.63754 | 51003.2 | 64000 | 2468.375 | 51003.2 | 8570.425 | 5404.8 | 1237648.975 | 8570.425 | 0
2021062912 | 3 | 0.88438 | 132657 | 0.0097 | 0 | 0.15988 | 1998.5 | 0.66528 | 53222.4 | 64000 | 1998.5 | 53222.4 | 13436.1 | 4865.675 | 1249679.125 | 13436.1 | 0
2021062913 | 3 | 0.92227 | 138340.5 | 0.02435 | 0 | 0.12433 | 1554.125 | 0.69535 | 55628 | 64000 | 1554.125 | 55628 | 17158.375 | 3722.275 | 1257987 | 17158.375 | 0
2021062914 | 3 | 0.95416 | 143124 | 0.04385 | 0 | 0.09977 | 1247.125 | 0.70409 | 56327.2 | 64000 | 1247.125 | 56327.2 | 21549.675 | 4391.3 | 1261903.575 | 21549.675 | 0
2021062915 | 3 | 0.97388 | 146082 | 0.06597 | 0 | 0.08841 | 1105.125 | 0.71137 | 56909.6 | 64000 | 1105.125 | 56909.6 | 24067.275 | 2517.6 | 1263302.55 | 24067.275 | 0
2021062916 | 3 | 0.98264 | 147396 | 0.099 | 0 | 0.0799 | 998.75 | 0.65546 | 52436.8 | 64000 | 998.75 | 52436.8 | 29960.45 | 5893.175 | 1258808.35 | 29960.45 | 0
2021062917 | 3 | 0.98712 | 148068 | 0.14915 | 0 | 0.09077 | 1134.625 | 0.53277 | 42621.6 | 64000 | 1134.625 | 42621.6 | 40311.775 | 10351.325 | 1243962.825 | 40311.775 | 0
2021062918 | 3 | 0.98446 | 147669 | 0.17326 | 0 | 0.15435 | 1929.375 | 0.40088 | 32070.4 | 64000 | 1929.375 | 32070.4 | 49669.225 | 9357.45 | 1219759.85 | 49669.225 | 0
2021062919 | 3 | 0.97408 | 146112 | 0.18247 | 0 | 0.20231 | 2528.875 | 0.20293 | 16234.4 | 64000 | 2528.875 | 16234.4 | 63348.725 | 13679.5 | 1181877.375 | 63348.725 | 0
2021062920 | 3 | 0.94646 | 141969 | 0.16347 | 0 | 0.22682 | 2835.25 | 0.0345 | 2760 | 64000 | 2835.25 | 2760 | 72373.75 | 9025.025 | 1134969.875 | 72373.75 | 0
2021062921 | 3 | 0.90682 | 136023 | 0.21199 | 0 | 0.23476 | 2934.5 | 0 | 0 | 64000 | 2934.5 | 0 | 69088.5 | -3285.25 | 1091347.625 | 69088.5 | 0
2021062922 | 3 | 0.8712 | 130680 | 0.17591 | 0 | 0.24154 | 3019.25 | 0 | 0 | 64000 | 3019.25 | 0 | 63660.75 | -5427.75 | 1053153.125 | 63660.75 | 0
2021062923 | 3 | 0.81389 | 122083.5 | 0.13725 | 0 | 0.23528 | 2941 | 0 | 0 | 64000 | 2941 | 0 | 55142.5 | -8518.25 | 1023476.875 | 55142.5 | 0
2021062924 | 3 | 0.75182 | 112773 | 0.19115 | 0 | 0.23794 | 2974.25 | 0 | 0 | 64000 | 2974.25 | 0 | 45798.75 | -9343.75 | 1003144.375 | 45798.75 | 0
2021063001 | 4 | 0.69718 | 104577 | 0.14521 | 0 | 0.22866 | 2858.25 | 0 | 0 | 64000 | 2858.25 | 0 | 37718.75 | -8080 | 990891.875 | 37718.75 | 0
2021063002 | 4 | 0.65635 | 98452.5 | 0.10907 | 0 | 0.20196 | 2524.5 | 0 | 0 | 64000 | 2524.5 | 0 | 31928 | -5790.75 | 984430.125 | 31928 | 0
2021063003 | 4 | 0.62572 | 93858 | 0.09162 | 0 | 0.19221 | 2402.625 | 0 | 0 | 64000 | 2402.625 | 0 | 27455.375 | -4472.625 | 982441 | 27455.375 | 0
2021063004 | 4 | 0.60631 | 90946.5 | 0.24632 | 0 | 0.16614 | 2076.75 | 0 | 0 | 64000 | 2076.75 | 0 | 24869.75 | -2585.625 | 983037.5 | 24869.75 | 0
2021063005 | 4 | 0.60037 | 90055.5 | 0.38272 | 0 | 0.13407 | 1675.875 | 0 | 0 | 64000 | 1675.875 | 0 | 24379.625 | -490.125 | 984124.125 | 24379.625 | 0
2021063006 | 4 | 0.61005 | 91507.5 | 0.46666 | 0 | 0.09297 | 1162.125 | 0.00538 | 430.4 | 64000 | 1162.125 | 430.4 | 25914.975 | 1535.35 | 983675.4 | 25914.975 | 0
2021063007 | 4 | 0.63769 | 95653.5 | 0.51949 | 0 | 0.08764 | 1095.5 | 0.11919 | 9535.2 | 64000 | 1095.5 | 9535.2 | 21022.8 | -4892.175 | 988118.85 | 21022.8 | 0
2021063008 | 4 | 0.68659 | 102988.5 | 0.50262 | 0 | 0.08838 | 1104.75 | 0.38149 | 30519.2 | 64000 | 1104.75 | 30519.2 | 7364.55 | -13658.25 | 1006220.55 | 7364.55 | 0
2021063009 | 4 | 0.73571 | 110356.5 | 0.47017 | 0 | 0.07277 | 909.625 | 0.54045 | 43236 | 64000 | 909.625 | 43236 | 2210.875 | -5153.675 | 1029475.925 | 2210.875 | 0
2021063010 | 4 | 0.78181 | 117271.5 | 0.35216 | 0 | 0.05756 | 719.5 | 0.56216 | 44972.8 | 64000 | 719.5 | 44972.8 | 7579.2 | 5368.325 | 1047362.975 | 7579.2 | 0
2021063011 | 4 | 0.82638 | 123957 | 0.23594 | 0 | 0.03891 | 486.375 | 0.63532 | 50825.6 | 64000 | 486.375 | 50825.6 | 8645.025 | 1065.825 | 1064184.2 | 8645.025 | 0
2021063012 | 4 | 0.86764 | 130146 | 0.23873 | 0 | 0.02594 | 324.25 | 0.64091 | 51272.8 | 64000 | 324.25 | 51272.8 | 14548.95 | 5903.925 | 1075101.5 | 14548.95 | 0
2021063013 | 4 | 0.90326 | 135489 | 0.29484 | 0 | 0.02318 | 289.75 | 0.64477 | 51581.6 | 64000 | 289.75 | 51581.6 | 19617.65 | 5068.7 | 1080950.1 | 19617.65 | 0
2021063014 | 4 | 0.92494 | 138741 | 0.25687 | 0 | 0.03798 | 474.75 | 0.66685 | 53348 | 64000 | 474.75 | 53348 | 20918.25 | 1300.6 | 1085498.1 | 20918.25 | 0
2021063015 | 4 | 0.93027 | 139540.5 | 0.28256 | 0 | 0.05751 | 718.875 | 0.68955 | 55164 | 64000 | 718.875 | 55164 | 19657.625 | -1260.625 | 1091306.725 | 19657.625 | 0
2021063016 | 4 | 0.93022 | 139533 | 0.54656 | 0 | 0.06599 | 824.875 | 0.67278 | 53822.4 | 64000 | 824.875 | 53822.4 | 20885.725 | 1228.1 | 1095887.25 | 20885.725 | 0
2021063017 | 4 | 0.93393 | 140089.5 | 0.60396 | 0 | 0.08679 | 1084.875 | 0.62431 | 49944.8 | 64000 | 1084.875 | 49944.8 | 25059.825 | 4174.1 | 1096293.675 | 25059.825 | 0
2021063018 | 4 | 0.9323 | 139845 | 0.64992 | 0 | 0.17102 | 2137.75 | 0.49818 | 39854.4 | 64000 | 2137.75 | 39854.4 | 33852.85 | 8793.025 | 1087907.075 | 33852.85 | 0
2021063019 | 4 | 0.92265 | 138397.5 | 0.60148 | 0 | 0.20981 | 2622.625 | 0.30117 | 24093.6 | 64000 | 2622.625 | 24093.6 | 47681.275 | 13828.425 | 1065692.05 | 47681.275 | 0
2021063020 | 4 | 0.89315 | 133972.5 | 0.52132 | 0 | 0.29742 | 3717.75 | 0.05471 | 4376.8 | 64000 | 3717.75 | 4376.8 | 61877.95 | 14196.675 | 1029280.35 | 61877.95 | 0
2021063021 | 4 | 0.85437 | 128155.5 | 0.54829 | 0 | 0.32675 | 4084.375 | 0 | 0 | 64000 | 4084.375 | 0 | 60071.125 | -1806.825 | 994675.475 | 60071.125 | 0
2021063022 | 4 | 0.81578 | 122367 | 0.47084 | 0 | 0.36595 | 4574.375 | 0 | 0 | 64000 | 4574.375 | 0 | 53792.625 | -6278.5 | 966349.1 | 53792.625 | 0
2021063023 | 4 | 0.76117 | 114175.5 | 0.46172 | 0 | 0.38058 | 4757.25 | 0 | 0 | 64000 | 4757.25 | 0 | 45418.25 | -8374.375 | 946397.1 | 45418.25 | 0
2021063024 | 4 | 0.70261 | 105391.5 | 0.37032 | 0 | 0.37096 | 4637 | 0 | 0 | 64000 | 4637 | 0 | 36754.5 | -8663.75 | 935108.85 | 36754.5 | 0
2021070101 | 5 | 0.65416 | 98124 | 0.31249 | 0 | 0.34664 | 4333 | 0 | 0 | 64000 | 4333 | 0 | 29791 | -6963.5 | 930784.1 | 29791 | 0
2021070102 | 5 | 0.61749 | 92623.5 | 0.3153 | 0 | 0.32259 | 4032.375 | 0 | 0 | 64000 | 4032.375 | 0 | 24591.125 | -5199.875 | 931659.225 | 24591.125 | 0
2021070103 | 5 | 0.59035 | 88552.5 | 0.28887 | 0 | 0.31651 | 3956.375 | 0 | 0 | 64000 | 3956.375 | 0 | 20596.125 | -3995 | 936529.35 | 20596.125 | 0
2021070104 | 5 | 0.5743 | 86145 | 0.22306 | 0 | 0.27528 | 3441 | 0 | 0 | 64000 | 3441 | 0 | 18704 | -1892.125 | 943291.6 | 18704 | 0
2021070105 | 5 | 0.57012 | 85518 | 0.15873 | 0 | 0.23221 | 2902.625 | 0 | 0 | 64000 | 2902.625 | 0 | 18615.375 | -88.625 | 950142.475 | 18615.375 | 0
2021070106 | 5 | 0.58259 | 87388.5 | 0.13212 | 0 | 0.19463 | 2432.875 | 0.00859 | 687.2 | 64000 | 2432.875 | 687.2 | 20268.425 | 1653.05 | 955340.3 | 20268.425 | 0
2021070107 | 5 | 0.60788 | 91182 | 0.10959 | 0 | 0.20554 | 2569.25 | 0.11695 | 9356 | 64000 | 2569.25 | 9356 | 15256.75 | -5011.675 | 965549.8 | 15256.75 | 0
2021070108 | 5 | 0.64578 | 96867 | 0.08397 | 0 | 0.22477 | 2809.625 | 0.337 | 26960 | 64000 | 2809.625 | 26960 | 3097.375 | -12159.375 | 987918.675 | 3097.375 | 0
2021070109 | 5 | 0.68076 | 102114 | 0.06026 | 0 | 0.20882 | 2610.25 | 0.45419 | 36335.2 | 64000 | 2610.25 | 35503.75 | 0 | -3097.375 | 1013384.925 | 0 | 0
2021070110 | 5 | 0.71626 | 107439 | 0.12793 | 0 | 0.17118 | 2139.75 | 0.52621 | 42096.8 | 64000 | 2139.75 | 41299.25 | 0 | 0 | 1038851.175 | 0 | 0
2021070111 | 5 | 0.74592 | 111888 | 0.10922 | 0 | 0.15965 | 1995.625 | 0.49173 | 39338.4 | 64000 | 1995.625 | 39338.4 | 6553.975 | 6553.975 | 1057763.45 | 6553.975 | 0
2021070112 | 5 | 0.77255 | 115882.5 | 0.10125 | 0 | 0.14087 | 1760.875 | 0.55341 | 44272.8 | 64000 | 1760.875 | 44272.8 | 5848.825 | -705.15 | 1077380.875 | 5848.825 | 0
2021070113 | 5 | 0.78856 | 118284 | 0.14277 | 0 | 0.12861 | 1607.625 | 0.58989 | 47191.2 | 64000 | 1607.625 | 47191.2 | 5485.175 | -363.65 | 1097361.95 | 5485.175 | 0
2021070114 | 5 | 0.79547 | 119320.5 | 0.18692 | 0 | 0.11869 | 1483.625 | 0.59224 | 47379.2 | 64000 | 1483.625 | 47379.2 | 6457.675 | 972.5 | 1116370.525 | 6457.675 | 0
2021070115 | 5 | 0.79527 | 119290.5 | 0.23918 | 0 | 0.12514 | 1564.25 | 0.60102 | 48081.6 | 64000 | 1564.25 | 48081.6 | 5644.65 | -813.025 | 1136192.125 | 5644.65 | 0
2021070116 | 5 | 0.78767 | 118150.5 | 0.25627 | 0 | 0.08257 | 1032.125 | 0.59168 | 47334.4 | 64000 | 1032.125 | 47334.4 | 5783.975 | 139.325 | 1155874.4 | 5783.975 | 0
2021070117 | 5 | 0.78162 | 117243 | 0.17257 | 0 | 0.06688 | 836 | 0.57332 | 45865.6 | 64000 | 836 | 45865.6 | 6541.4 | 757.425 | 1174799.25 | 6541.4 | 0
2021070118 | 5 | 0.77433 | 116149.5 | 0.16115 | 0 | 0.10659 | 1332.375 | 0.49175 | 39340 | 64000 | 1332.375 | 39340 | 11477.125 | 4935.725 | 1188788.375 | 11477.125 | 0
2021070119 | 5 | 0.75704 | 113556 | 0.22524 | 0 | 0.10782 | 1347.75 | 0.26221 | 20976.8 | 64000 | 1347.75 | 20976.8 | 27231.45 | 15754.325 | 1187023.175 | 27231.45 | 0
2021070120 | 5 | 0.7322 | 109830 | 0.16898 | 0 | 0.07781 | 972.625 | 0.03894 | 3115.2 | 64000 | 972.625 | 3115.2 | 41742.175 | 14510.725 | 1170747.25 | 41742.175 | 0
2021070121 | 5 | 0.70906 | 106359 | 0.09723 | 0 | 0.06026 | 753.25 | 0 | 0 | 64000 | 753.25 | 0 | 41605.75 | -136.425 | 1154607.75 | 41605.75 | 0
2021070122 | 5 | 0.68316 | 102474 | 0.13318 | 0 | 0.0601 | 751.25 | 0 | 0 | 64000 | 751.25 | 0 | 37722.75 | -3883 | 1142351.25 | 37722.75 | 0
2021070123 | 5 | 0.6448 | 96720 | 0.1989 | 0 | 0.06783 | 847.875 | 0 | 0 | 64000 | 847.875 | 0 | 31872.125 | -5850.625 | 1135945.375 | 31872.125 | 0
2021070124 | 5 | 0.59997 | 89995.5 | 0.20472 | 0 | 0.08705 | 1088.125 | 0 | 0 | 64000 | 1088.125 | 0 | 24907.375 | -6964.75 | 1136504.25 | 24907.375 | 0
2021070201 | 6 | 0.55971 | 83956.5 | 0.24444 | 0 | 0.10552 | 1319 | 0 | 0 | 64000 | 1319 | 0 | 18637.5 | -6269.875 | 1143333 | 18637.5 | 0
2021070202 | 6 | 0.53045 | 79567.5 | 0.18395 | 0 | 0.14278 | 1784.75 | 0 | 0 | 64000 | 1784.75 | 0 | 13782.75 | -4854.75 | 1155016.5 | 13782.75 | 0
2021070203 | 6 | 0.5119 | 76785 | 0.13178 | 0 | 0.17897 | 2237.125 | 0 | 0 | 64000 | 2237.125 | 0 | 10547.875 | -3234.875 | 1169934.875 | 10547.875 | 0
2021070204 | 6 | 0.50009 | 75013.5 | 0.13856 | 0 | 0.17926 | 2240.75 | 0 | 0 | 64000 | 2240.75 | 0 | 8772.75 | -1775.125 | 1186628.375 | 8772.75 | 0
2021070205 | 6 | 0.49959 | 74938.5 | 0.19249 | 0 | 0.18272 | 2284 | 0 | 0 | 64000 | 2284 | 0 | 8654.5 | -118.25 | 1203440.125 | 8654.5 | 0
2021070206 | 6 | 0.512 | 76800 | 0.21295 | 0 | 0.15652 | 1956.5 | 0.00788 | 630.4 | 64000 | 1956.5 | 630.4 | 10213.1 | 1558.6 | 1218693.275 | 10213.1 | 0
2021070207 | 6 | 0.53348 | 80022 | 0.25687 | 0 | 0.16025 | 2003.125 | 0.09588 | 7670.4 | 64000 | 2003.125 | 7670.4 | 6348.475 | -3864.625 | 1237811.05 | 6348.475 | 0
2021070208 | 6 | 0.5629 | 84435 | 0.20819 | 0 | 0.16173 | 2021.625 | 0.20797 | 16637.6 | 64000 | 2021.625 | 16637.6 | 1775.775 | -4572.7 | 1261501.525 | 1775.775 | 0
2021070209 | 6 | 0.5917 | 88755 | 0.18309 | 0 | 0.15585 | 1948.125 | 0.28225 | 22580 | 64000 | 1948.125 | 22580 | 226.875 | -1548.9 | 1286740.9 | 226.875 | 0
2021070210 | 6 | 0.61149 | 91723.5 | 0.2344 | 0 | 0.14949 | 1868.625 | 0.334 | 26720 | 64000 | 1868.625 | 25854.875 | 0 | -226.875 | 1312207.15 | 0 | 0
2021070211 | 6 | 0.62991 | 94486.5 | 0.30261 | 0 | 0.1372 | 1715 | 0.36095 | 28876 | 64000 | 1715 | 28771.5 | 0 | 0 | 1337673.4 | 0 | 0
2021070212 | 6 | 0.64407 | 96610.5 | 0.35191 | 0 | 0.1427 | 1783.75 | 0.36189 | 28951.2 | 64000 | 1783.75 | 28951.2 | 1875.55 | 1875.55 | 1350000 | 1875.55 | 0
2021070213 | 6 | 0.65738 | 98607 | 0.33408 | 0 | 0.14583 | 1822.875 | 0.3679 | 29432 | 64000 | 1822.875 | 29432 | 3352.125 | 1476.575 | 1350000 | 3352.125 | 0
2021070214 | 6 | 0.67168 | 100752 | 0.34527 | 0 | 0.14541 | 1817.625 | 0.34943 | 27954.4 | 64000 | 1817.625 | 27954.4 | 6979.975 | 3627.85 | 1350000 | 6979.975 | 0
2021070215 | 6 | 0.68152 | 102228 | 0.38374 | 0 | 0.12622 | 1577.75 | 0.28269 | 22615.2 | 64000 | 1577.75 | 22615.2 | 14035.05 | 7055.075 | 1350000 | 14035.05 | 0
2021070216 | 6 | 0.687 | 103050 | 0.40607 | 0 | 0.10728 | 1341 | 0.19115 | 15292 | 64000 | 1341 | 15292 | 22417 | 8381.95 | 1350000 | 22417 | 0
2021070217 | 6 | 0.69371 | 104056.5 | 0.53375 | 0 | 0.11852 | 1481.5 | 0.13385 | 10708 | 64000 | 1481.5 | 10708 | 27867 | 5450 | 1347599.25 | 27867 | 0
2021070218 | 6 | 0.69409 | 104113.5 | 0.53468 | 0 | 0.13256 | 1657 | 0.106 | 8480 | 64000 | 1657 | 8480 | 29976.5 | 2109.5 | 1343089 | 29976.5 | 0
2021070219 | 6 | 0.68185 | 102277.5 | 0.49666 | 0 | 0.1911 | 2388.75 | 0.05805 | 4644 | 64000 | 2388.75 | 4644 | 31244.75 | 1268.25 | 1337310.5 | 31244.75 | 0
2021070220 | 6 | 0.65667 | 98500.5 | 0.54548 | 0 | 0.23799 | 2974.875 | 0.00705 | 564 | 64000 | 2974.875 | 564 | 30961.625 | -283.125 | 1331815.125 | 30961.625 | 0
2021070221 | 6 | 0.62679 | 94018.5 | 0.53818 | 0 | 0.2443 | 3053.75 | 0 | 0 | 64000 | 3053.75 | 0 | 26964.75 | -3996.875 | 1330316.625 | 26964.75 | 0
2021070222 | 6 | 0.60773 | 91159.5 | 0.53926 | 0 | 0.24233 | 3029.125 | 0 | 0 | 64000 | 3029.125 | 0 | 24130.375 | -2834.375 | 1331652.5 | 24130.375 | 0
2021070223 | 6 | 0.5756 | 86340 | 0.54087 | 0 | 0.22764 | 2845.5 | 0 | 0 | 64000 | 2845.5 | 0 | 19494.5 | -4635.875 | 1337624.25 | 19494.5 | 0
2021070224 | 6 | 0.53425 | 80137.5 | 0.50286 | 0 | 0.22392 | 2799 | 0 | 0 | 64000 | 2799 | 0 | 13338.5 | -6156 | 1349752 | 13338.5 | 0
2021070301 | 7 | 0.49657 | 74485.5 | 0.45765 | 0 | 0.23354 | 2919.25 | 0 | 0 | 64000 | 2919.25 | 0 | 7566.25 | -5772.25 | 1350000 | 7566.25 | 0
2021070302 | 7 | 0.4682 | 70230 | 0.30674 | 0 | 0.24342 | 3042.75 | 0 | 0 | 64000 | 3042.75 | 0 | 3187.25 | -4379 | 1350000 | 3187.25 | 0
2021070303 | 7 | 0.44943 | 67414.5 | 0.26877 | 0 | 0.25395 | 3174.375 | 0 | 0 | 64000 | 3174.375 | 0 | 240.125 | -2947.125 | 1350000 | 240.125 | 0
2021070304 | 7 | 0.43707 | 65560.5 | 0.23476 | 0 | 0.28909 | 3613.625 | 0 | 0 | 64000 | 1560.5 | 0 | 0 | -240.125 | 1350000 | 0 | 0
2021070305 | 7 | 0.43098 | 64647 | 0.19598 | 0 | 0.29594 | 3699.25 | 0 | 0 | 64000 | 647 | 0 | 0 | 0 | 1350000 | 0 | 0
2021070306 | 7 | 0.4323 | 64845 | 0.17679 | 0 | 0.30906 | 3863.25 | 0.00444 | 355.2 | 64000 | 845 | 0 | 0 | 0 | 1350000 | 0 | 0
2021070307 | 7 | 0.43208 | 64812 | 0.26086 | 0 | 0.34547 | 4318.375 | 0.03569 | 2855.2 | 64000 | 812 | 0 | 0 | 0 | 1350000 | 0 | 0
2021070308 | 7 | 0.44909 | 67363.5 | 0.34458 | 0 | 0.32634 | 4079.25 | 0.11325 | 9060 | 64000 | 3363.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021070309 | 7 | 0.47587 | 71380.5 | 0.32357 | 0 | 0.32401 | 4050.125 | 0.19659 | 15727.2 | 64000 | 4050.125 | 3330.375 | 0 | 0 | 1350000 | 0 | 0
2021070310 | 7 | 0.50324 | 75486 | 0.27507 | 0 | 0.32641 | 4080.125 | 0.3077 | 24616 | 64000 | 4080.125 | 7405.875 | 0 | 0 | 1350000 | 0 | 0
2021070311 | 7 | 0.52729 | 79093.5 | 0.33935 | 0 | 0.30037 | 3754.625 | 0.45587 | 36469.6 | 64000 | 3754.625 | 11338.875 | 0 | 0 | 1350000 | 0 | 0
2021070312 | 7 | 0.54935 | 82402.5 | 0.42155 | 0 | 0.2583 | 3228.75 | 0.44495 | 35596 | 64000 | 3228.75 | 15173.75 | 0 | 0 | 1350000 | 0 | 0
2021070313 | 7 | 0.56806 | 85209 | 0.43881 | 0 | 0.21281 | 2660.125 | 0.45796 | 36636.8 | 64000 | 2660.125 | 18548.875 | 0 | 0 | 1350000 | 0 | 0
2021070314 | 7 | 0.58288 | 87432 | 0.51354 | 0 | 0.18292 | 2286.5 | 0.55902 | 44721.6 | 64000 | 2286.5 | 21145.5 | 0 | 0 | 1350000 | 0 | 0
2021070315 | 7 | 0.60049 | 90073.5 | 0.53855 | 0 | 0.12984 | 1623 | 0.57567 | 46053.6 | 64000 | 1623 | 24450.5 | 0 | 0 | 1350000 | 0 | 0
2021070316 | 7 | 0.61612 | 92418 | 0.61349 | 0 | 0.11791 | 1473.875 | 0.60008 | 48006.4 | 64000 | 1473.875 | 26944.125 | 0 | 0 | 1350000 | 0 | 0
2021070317 | 7 | 0.63019 | 94528.5 | 0.57837 | 0 | 0.14687 | 1835.875 | 0.55457 | 44365.6 | 64000 | 1835.875 | 28692.625 | 0 | 0 | 1350000 | 0 | 0
2021070318 | 7 | 0.63994 | 95991 | 0.61889 | 0 | 0.12033 | 1504.125 | 0.48004 | 38403.2 | 64000 | 1504.125 | 30486.875 | 0 | 0 | 1350000 | 0 | 0
2021070319 | 7 | 0.63789 | 95683.5 | 0.54079 | 0 | 0.07473 | 934.125 | 0.26173 | 20938.4 | 64000 | 934.125 | 20938.4 | 9810.975 | 9810.975 | 1350000 | 9810.975 | 0
2021070320 | 7 | 0.6223 | 93345 | 0.45695 | 0 | 0.07992 | 999 | 0.04486 | 3588.8 | 64000 | 999 | 3588.8 | 24757.2 | 14946.225 | 1350000 | 24757.2 | 0
2021070321 | 7 | 0.60239 | 90358.5 | 0.39456 | 0 | 0.08621 | 1077.625 | 0 | 0 | 64000 | 1077.625 | 0 | 25280.875 | 523.675 | 1350000 | 25280.875 | 0
2021070322 | 7 | 0.58779 | 88168.5 | 0.37973 | 0 | 0.08037 | 1004.625 | 0 | 0 | 64000 | 1004.625 | 0 | 23163.875 | -2117 | 1350000 | 23163.875 | 0
2021070323 | 7 | 0.56434 | 84651 | 0.30725 | 0 | 0.07725 | 965.625 | 0 | 0 | 64000 | 965.625 | 0 | 19685.375 | -3478.5 | 1350000 | 19685.375 | 0
2021070324 | 7 | 0.5329 | 79935 | 0.221 | 0 | 0.09009 | 1126.125 | 0 | 0 | 64000 | 1126.125 | 0 | 14808.875 | -4876.5 | 1350000 | 14808.875 | 0
2021070401 | 1 | 0.4985 | 74775 | 0.21979 | 0 | 0.0948 | 1185 | 0 | 0 | 64000 | 1185 | 0 | 9590 | -5218.875 | 1350000 | 9590 | 0
2021070402 | 1 | 0.47161 | 70741.5 | 0.24205 | 0 | 0.09691 | 1211.375 | 0 | 0 | 64000 | 1211.375 | 0 | 5530.125 | -4059.875 | 1350000 | 5530.125 | 0
2021070403 | 1 | 0.45158 | 67737 | 0.25404 | 0 | 0.08931 | 1116.375 | 0 | 0 | 64000 | 1116.375 | 0 | 2620.625 | -2909.5 | 1350000 | 2620.625 | 0
2021070404 | 1 | 0.4381 | 65715 | 0.27585 | 0 | 0.0926 | 1157.5 | 0 | 0 | 64000 | 1157.5 | 0 | 557.5 | -2063.125 | 1350000 | 557.5 | 0
2021070405 | 1 | 0.43158 | 64737 | 0.28735 | 0 | 0.0852 | 1065 | 0 | 0 | 64000 | 737 | 0 | 0 | -557.5 | 1350000 | 0 | 0
2021070406 | 1 | 0.42834 | 64251 | 0.23976 | 0 | 0.08048 | 1006 | 0.00348 | 278.4 | 64000 | 251 | 0 | 0 | 0 | 1350000 | 0 | 0
2021070407 | 1 | 0.42708 | 64062 | 0.25621 | 0 | 0.0695 | 868.75 | 0.12458 | 9966.4 | 64000 | 62 | 0 | 0 | 0 | 1350000 | 0 | 0
2021070408 | 1 | 0.44239 | 66358.5 | 0.10594 | 0 | 0.08251 | 1031.375 | 0.37023 | 29618.4 | 64000 | 1031.375 | 1327.125 | 0 | 0 | 1350000 | 0 | 0
2021070409 | 1 | 0.47453 | 71179.5 | 0.05159 | 0 | 0.11513 | 1439.125 | 0.51066 | 40852.8 | 64000 | 1439.125 | 5740.375 | 0 | 0 | 1350000 | 0 | 0
2021070410 | 1 | 0.51329 | 76993.5 | 0.02475 | 0 | 0.13794 | 1724.25 | 0.55832 | 44665.6 | 64000 | 1724.25 | 11269.25 | 0 | 0 | 1350000 | 0 | 0
2021070411 | 1 | 0.55489 | 83233.5 | 0.00971 | 0 | 0.09895 | 1236.875 | 0.60055 | 48044 | 64000 | 1236.875 | 17996.625 | 0 | 0 | 1350000 | 0 | 0
2021070412 | 1 | 0.59679 | 89518.5 | 0.02283 | 0 | 0.09103 | 1137.875 | 0.60574 | 48459.2 | 64000 | 1137.875 | 24380.625 | 0 | 0 | 1350000 | 0 | 0
2021070413 | 1 | 0.6345 | 95175 | 0.05055 | 0 | 0.11091 | 1386.375 | 0.61675 | 49340 | 64000 | 1386.375 | 29788.625 | 0 | 0 | 1350000 | 0 | 0
2021070414 | 1 | 0.66547 | 99820.5 | 0.03059 | 0 | 0.10107 | 1263.375 | 0.62362 | 49889.6 | 64000 | 1263.375 | 34557.125 | 0 | 0 | 1350000 | 0 | 0
2021070415 | 1 | 0.68752 | 103128 | 0.03178 | 0 | 0.05275 | 659.375 | 0.63889 | 51111.2 | 64000 | 659.375 | 38468.625 | 0 | 0 | 1350000 | 0 | 0
2021070416 | 1 | 0.70855 | 106282.5 | 0.04711 | 0 | 0.06384 | 798 | 0.59355 | 47484 | 64000 | 798 | 41484.5 | 0 | 0 | 1350000 | 0 | 0
2021070417 | 1 | 0.72641 | 108961.5 | 0.06393 | 0 | 0.06772 | 846.5 | 0.55039 | 44031.2 | 64000 | 846.5 | 44031.2 | 83.8 | 83.8 | 1350000 | 83.8 | 0
2021070418 | 1 | 0.73636 | 110454 | 0.0474 | 0 | 0.09165 | 1145.625 | 0.4667 | 37336 | 64000 | 1145.625 | 37336 | 7972.375 | 7888.575 | 1350000 | 7972.375 | 0
2021070419 | 1 | 0.73185 | 109777.5 | 0.03015 | 0 | 0.12042 | 1505.25 | 0.2599 | 20792 | 64000 | 1505.25 | 20792 | 23480.25 | 15507.875 | 1350000 | 23480.25 | 0
2021070420 | 1 | 0.71072 | 106608 | 0.01371 | 0 | 0.12637 | 1579.625 | 0.04835 | 3868 | 64000 | 1579.625 | 3868 | 37160.375 | 13680.125 | 1338305.875 | 37160.375 | 0
2021070421 | 1 | 0.67864 | 101796 | 0.00233 | 0 | 0.11085 | 1385.625 | 0 | 0 | 64000 | 1385.625 | 0 | 36410.375 | -750 | 1327361.75 | 36410.375 | 0
2021070422 | 1 | 0.65101 | 97651.5 | 0.00221 | 0 | 0.09639 | 1204.875 | 0 | 0 | 64000 | 1204.875 | 0 | 32446.625 | -3963.75 | 1320381.375 | 32446.625 | 0
2021070423 | 1 | 0.62392 | 93588 | 0.00557 | 0 | 0.08581 | 1072.625 | 0 | 0 | 64000 | 1072.625 | 0 | 28515.375 | -3931.25 | 1317332.25 | 28515.375 | 0
2021070424 | 1 | 0.59308 | 88962 | 0.01341 | 0 | 0.06391 | 798.875 | 0 | 0 | 64000 | 798.875 | 0 | 24163.125 | -4352.25 | 1318635.375 | 24163.125 | 0
2021070501 | 2 | 0.55506 | 83259 | 0.00835 | 0 | 0.06695 | 836.875 | 0 | 0 | 64000 | 836.875 | 0 | 18422.125 | -5741 | 1325679.5 | 18422.125 | 0
2021070502 | 2 | 0.52113 | 78169.5 | 0.00945 | 0 | 0.08797 | 1099.625 | 0 | 0 | 64000 | 1099.625 | 0 | 13069.875 | -5352.25 | 1338075.875 | 13069.875 | 0
2021070503 | 2 | 0.49653 | 74479.5 | 0.02317 | 0 | 0.0868 | 1085 | 0 | 0 | 64000 | 1085 | 0 | 9394.5 | -3675.375 | 1350000 | 9394.5 | 0
2021070504 | 2 | 0.47998 | 71997 | 0.06413 | 0 | 0.073 | 912.5 | 0 | 0 | 64000 | 912.5 | 0 | 7084.5 | -2310 | 1350000 | 7084.5 | 0
2021070505 | 2 | 0.47322 | 70983 | 0.08805 | 0 | 0.0821 | 1026.25 | 0 | 0 | 64000 | 1026.25 | 0 | 5956.75 | -1127.75 | 1350000 | 5956.75 | 0
2021070506 | 2 | 0.47495 | 71242.5 | 0.09244 | 0 | 0.06193 | 774.125 | 0.00461 | 368.8 | 64000 | 774.125 | 368.8 | 6099.575 | 142.825 | 1350000 | 6099.575 | 0
2021070507 | 2 | 0.47856 | 71784 | 0.11069 | 0 | 0.06551 | 818.875 | 0.11683 | 9346.4 | 64000 | 818.875 | 6965.125 | 0 | -6099.575 | 1350000 | 0 | 0
2021070508 | 2 | 0.50122 | 75183 | 0.10718 | 0 | 0.07073 | 884.125 | 0.33558 | 26846.4 | 64000 | 884.125 | 10298.875 | 0 | 0 | 1350000 | 0 | 0
2021070509 | 2 | 0.54274 | 81411 | 0.06096 | 0 | 0.11592 | 1449 | 0.46396 | 37116.8 | 64000 | 1449 | 15962 | 0 | 0 | 1350000 | 0 | 0
2021070510 | 2 | 0.59568 | 89352 | 0.02165 | 0 | 0.12138 | 1517.25 | 0.55285 | 44228 | 64000 | 1517.25 | 23834.75 | 0 | 0 | 1350000 | 0 | 0
2021070511 | 2 | 0.65314 | 97971 | 0.02668 | 0 | 0.09208 | 1151 | 0.58545 | 46836 | 64000 | 1151 | 32820 | 0 | 0 | 1350000 | 0 | 0
2021070512 | 2 | 0.70789 | 106183.5 | 0.05401 | 0 | 0.10379 | 1297.375 | 0.60303 | 48242.4 | 64000 | 1297.375 | 40886.125 | 0 | 0 | 1350000 | 0 | 0
2021070513 | 2 | 0.7543 | 113145 | 0.09192 | 0 | 0.06733 | 841.625 | 0.61244 | 48995.2 | 64000 | 841.625 | 48303.375 | 0 | 0 | 1350000 | 0 | 0
2021070514 | 2 | 0.78874 | 118311 | 0.10088 | 0 | 0.03936 | 492 | 0.63062 | 50449.6 | 64000 | 492 | 50449.6 | 3369.4 | 3369.4 | 1350000 | 3369.4 | 0
2021070515 | 2 | 0.81606 | 122409 | 0.11534 | 0 | 0.03334 | 416.75 | 0.62139 | 49711.2 | 64000 | 416.75 | 49711.2 | 8281.05 | 4911.65 | 1350000 | 8281.05 | 0
2021070516 | 2 | 0.84278 | 126417 | 0.15132 | 0 | 0.02406 | 300.75 | 0.60373 | 48298.4 | 64000 | 300.75 | 48298.4 | 13817.85 | 5536.8 | 1350000 | 13817.85 | 0
2021070517 | 2 | 0.86511 | 129766.5 | 0.17889 | 0 | 0.0265 | 331.25 | 0.54655 | 43724 | 64000 | 331.25 | 43724 | 21711.25 | 7893.4 | 1350000 | 21711.25 | 0
2021070518 | 2 | 0.87909 | 131863.5 | 0.25126 | 0 | 0.0377 | 471.25 | 0.44309 | 35447.2 | 64000 | 471.25 | 35447.2 | 31945.05 | 10233.8 | 1343521.2 | 31945.05 | 0
2021070519 | 2 | 0.87283 | 130924.5 | 0.3071 | 0 | 0.05018 | 627.25 | 0.25553 | 20442.4 | 64000 | 627.25 | 20442.4 | 45854.85 | 13909.8 | 1323132.6 | 45854.85 | 0
2021070520 | 2 | 0.8499 | 127485 | 0.34295 | 0 | 0.08677 | 1084.625 | 0.04619 | 3695.2 | 64000 | 1084.625 | 3695.2 | 58705.175 | 12850.325 | 1289893.675 | 58705.175 | 0
2021070521 | 2 | 0.8177 | 122655 | 0.44236 | 0 | 0.08474 | 1059.25 | 0 | 0 | 64000 | 1059.25 | 0 | 57595.75 | -1109.425 | 1257764.175 | 57595.75 | 0
2021070522 | 2 | 0.78795 | 118192.5 | 0.55926 | 0 | 0.092 | 1150 | 0 | 0 | 64000 | 1150 | 0 | 53042.5 | -4553.25 | 1230187.925 | 53042.5 | 0
2021070523 | 2 | 0.73891 | 110836.5 | 0.62937 | 0 | 0.10652 | 1331.5 | 0 | 0 | 64000 | 1331.5 | 0 | 45505 | -7537.5 | 1210149.175 | 45505 | 0
2021070524 | 2 | 0.68157 | 102235.5 | 0.71555 | 0 | 0.10833 | 1354.125 | 0 | 0 | 64000 | 1354.125 | 0 | 36881.375 | -8623.625 | 1198734.05 | 36881.375 | 0
2021070601 | 3 | 0.63161 | 94741.5 | 0.78859 | 0 | 0.10929 | 1366.125 | 0 | 0 | 64000 | 1366.125 | 0 | 29375.375 | -7506 | 1194824.925 | 29375.375 | 0
2021070602 | 3 | 0.59513 | 89269.5 | 0.82017 | 0 | 0.10049 | 1256.125 | 0 | 0 | 64000 | 1256.125 | 0 | 24013.375 | -5362 | 1196277.8 | 24013.375 | 0
2021070603 | 3 | 0.56872 | 85308 | 0.80723 | 0 | 0.11372 | 1421.5 | 0 | 0 | 64000 | 1421.5 | 0 | 19886.5 | -4126.875 | 1201857.55 | 19886.5 | 0
2021070604 | 3 | 0.55179 | 82768.5 | 0.78893 | 0 | 0.10495 | 1311.875 | 0 | 0 | 64000 | 1311.875 | 0 | 17456.625 | -2429.875 | 1209867.175 | 17456.625 | 0
2021070605 | 3 | 0.54877 | 82315.5 | 0.78456 | 0 | 0.08744 | 1093 | 0 | 0 | 64000 | 1093 | 0 | 17222.5 | -234.125 | 1218110.925 | 17222.5 | 0
2021070606 | 3 | 0.56372 | 84558 | 0.77482 | 0 | 0.09513 | 1189.125 | 0.00416 | 332.8 | 64000 | 1189.125 | 332.8 | 19036.075 | 1813.575 | 1224541.1 | 19036.075 | 0
2021070607 | 3 | 0.59104 | 88656 | 0.74611 | 0 | 0.14363 | 1795.375 | 0.1284 | 10272 | 64000 | 1795.375 | 10272 | 12588.625 | -6447.45 | 1237418.725 | 12588.625 | 0
2021070608 | 3 | 0.63606 | 95409 | 0.66367 | 0 | 0.13912 | 1739 | 0.37302 | 29841.6 | 64000 | 1739 | 29670 | 0 | -12588.625 | 1262884.975 | 0 | 0
2021070609 | 3 | 0.68887 | 103330.5 | 0.53343 | 0 | 0.12815 | 1601.875 | 0.47731 | 38184.8 | 64000 | 1601.875 | 37728.625 | 0 | 0 | 1288351.225 | 0 | 0
2021070610 | 3 | 0.74357 | 111535.5 | 0.47839 | 0 | 0.15133 | 1891.625 | 0.53817 | 43053.6 | 64000 | 1891.625 | 43053.6 | 2590.275 | 2590.275 | 1311227.2 | 2590.275 | 0
2021070611 | 3 | 0.80173 | 120259.5 | 0.5433 | 0 | 0.15596 | 1949.5 | 0.55375 | 44300 | 64000 | 1949.5 | 44300 | 10010 | 7419.725 | 1326683.45 | 10010 | 0
2021070612 | 3 | 0.85732 | 128598 | 0.58369 | 0 | 0.12623 | 1577.875 | 0.57424 | 45939.2 | 64000 | 1577.875 | 45939.2 | 17080.925 | 7070.925 | 1335068.775 | 17080.925 | 0
2021070613 | 3 | 0.90296 | 135444 | 0.53152 | 0 | 0.10428 | 1303.5 | 0.60102 | 48081.6 | 64000 | 1303.5 | 48081.6 | 22058.9 | 4977.975 | 1338476.125 | 22058.9 | 0
2021070614 | 3 | 0.93871 | 140806.5 | 0.55426 | 0 | 0.07107 | 888.375 | 0.60057 | 48045.6 | 64000 | 888.375 | 48045.6 | 27872.525 | 5813.625 | 1336069.85 | 27872.525 | 0
2021070615 | 3 | 0.95996 | 143994 | 0.61297 | 0 | 0.04782 | 597.75 | 0.60575 | 48460 | 64000 | 597.75 | 48460 | 30936.25 | 3063.725 | 1330599.85 | 30936.25 | 0
2021070616 | 3 | 0.97325 | 145987.5 | 0.60979 | 0 | 0.03797 | 474.625 | 0.61296 | 49036.8 | 64000 | 474.625 | 49036.8 | 32476.075 | 1539.825 | 1323590.025 | 32476.075 | 0
2021070617 | 3 | 0.98147 | 147220.5 | 0.56884 | 0 | 0.03922 | 490.25 | 0.57805 | 46244 | 64000 | 490.25 | 46244 | 36486.25 | 4010.175 | 1312570.025 | 36486.25 | 0
2021070618 | 3 | 0.9809 | 147135 | 0.58001 | 0 | 0.05915 | 739.375 | 0.52598 | 42078.4 | 64000 | 739.375 | 42078.4 | 40317.225 | 3830.975 | 1297719.05 | 40317.225 | 0
2021070619 | 3 | 0.96227 | 144340.5 | 0.47186 | 0 | 0.10332 | 1291.5 | 0.30969 | 24775.2 | 64000 | 1291.5 | 24775.2 | 54273.8 | 13956.575 | 1268911.5 | 54273.8 | 0
2021070620 | 3 | 0.93265 | 139897.5 | 0.43076 | 0 | 0.13774 | 1721.75 | 0.05654 | 4523.2 | 64000 | 1721.75 | 4523.2 | 69652.55 | 15378.75 | 1224725.2 | 69652.55 | 0
2021070621 | 3 | 0.89316 | 133974 | 0.39814 | 0 | 0.1752 | 2190 | 0 | 0 | 64000 | 2190 | 0 | 67784 | -1868.55 | 1182407.45 | 67784 | 0
2021070622 | 3 | 0.85697 | 128545.5 | 0.36715 | 0 | 0.21765 | 2720.625 | 0 | 0 | 64000 | 2720.625 | 0 | 61824.875 | -5959.125 | 1146048.825 | 61824.875 | 0
2021070623 | 3 | 0.8005 | 120075 | 0.33515 | 0 | 0.26258 | 3282.25 | 0 | 0 | 64000 | 3282.25 | 0 | 52792.75 | -9032.125 | 1118722.325 | 52792.75 | 0
2021070624 | 3 | 0.73752 | 110628 | 0.35473 | 0 | 0.28075 | 3509.375 | 0 | 0 | 64000 | 3509.375 | 0 | 43118.625 | -9674.125 | 1101069.95 | 43118.625 | 0
2021070701 | 4 | 0.68284 | 102426 | 0.38282 | 0 | 0.27974 | 3496.75 | 0 | 0 | 64000 | 3496.75 | 0 | 34929.25 | -8189.375 | 1091606.95 | 34929.25 | 0
2021070702 | 4 | 0.63974 | 95961 | 0.35377 | 0 | 0.19433 | 2429.125 | 0 | 0 | 64000 | 2429.125 | 0 | 29531.875 | -5397.375 | 1087541.325 | 29531.875 | 0
2021070703 | 4 | 0.60903 | 91354.5 | 0.32449 | 0 | 0.15435 | 1929.375 | 0 | 0 | 64000 | 1929.375 | 0 | 25425.125 | -4106.75 | 1087582.45 | 25425.125 | 0
2021070704 | 4 | 0.58709 | 88063.5 | 0.30989 | 0 | 0.12039 | 1504.875 | 0 | 0 | 64000 | 1504.875 | 0 | 22558.625 | -2866.5 | 1090490.075 | 22558.625 | 0
2021070705 | 4 | 0.58034 | 87051 | 0.36216 | 0 | 0.09672 | 1209 | 0 | 0 | 64000 | 1209 | 0 | 21842 | -716.625 | 1094114.325 | 21842 | 0
2021070706 | 4 | 0.59034 | 88551 | 0.36076 | 0 | 0.11441 | 1430.125 | 0.009 | 720 | 64000 | 1430.125 | 720 | 22400.875 | 558.875 | 1097179.7 | 22400.875 | 0
2021070707 | 4 | 0.61556 | 92334 | 0.34828 | 0 | 0.10545 | 1318.125 | 0.12419 | 9935.2 | 64000 | 1318.125 | 9935.2 | 17080.675 | -5320.2 | 1105565.275 | 17080.675 | 0
2021070708 | 4 | 0.65742 | 98613 | 0.31329 | 0 | 0.12224 | 1528 | 0.34997 | 27997.6 | 64000 | 1528 | 27997.6 | 5087.4 | -11993.275 | 1125944.125 | 5087.4 | 0
2021070709 | 4 | 0.70983 | 106474.5 | 0.21324 | 0 | 0.13721 | 1715.125 | 0.5037 | 40296 | 64000 | 1715.125 | 40296 | 463.375 | -4624.025 | 1150947 | 463.375 | 0
2021070710 | 4 | 0.76517 | 114775.5 | 0.13319 | 0 | 0.20072 | 2509 | 0.54475 | 43580 | 64000 | 2509 | 43580 | 4686.5 | 4223.125 | 1171726.75 | 4686.5 | 0
2021070711 | 4 | 0.82395 | 123592.5 | 0.21538 | 0 | 0.23353 | 2919.125 | 0.58044 | 46435.2 | 64000 | 2919.125 | 46435.2 | 10238.175 | 5551.675 | 1186954.825 | 10238.175 | 0
2021070712 | 4 | 0.87725 | 131587.5 | 0.26729 | 0 | 0.27472 | 3434 | 0.58909 | 47127.2 | 64000 | 3434 | 47127.2 | 17026.3 | 6788.125 | 1195394.775 | 17026.3 | 0
2021070713 | 4 | 0.9175 | 137625 | 0.21097 | 0 | 0.29726 | 3715.75 | 0.58761 | 47008.8 | 64000 | 3715.75 | 47008.8 | 22900.45 | 5874.15 | 1197960.575 | 22900.45 | 0
2021070714 | 4 | 0.94697 | 142045.5 | 0.14653 | 0 | 0.32395 | 4049.375 | 0.60486 | 48388.8 | 64000 | 4049.375 | 48388.8 | 25607.325 | 2706.875 | 1197819.5 | 25607.325 | 0
2021070715 | 4 | 0.9592 | 143880 | 0.10372 | 0 | 0.36258 | 4532.25 | 0.58929 | 47143.2 | 64000 | 4532.25 | 47143.2 | 28204.55 | 2597.225 | 1195081.2 | 28204.55 | 0
2021070716 | 4 | 0.95662 | 143493 | 0.07003 | 0 | 0.39021 | 4877.625 | 0.55494 | 44395.2 | 64000 | 4877.625 | 44395.2 | 30220.175 | 2015.625 | 1190327.275 | 30220.175 | 0
2021070717 | 4 | 0.94904 | 142356 | 0.12065 | 0 | 0.42653 | 5331.625 | 0.45616 | 36492.8 | 64000 | 5331.625 | 36492.8 | 36531.575 | 6311.4 | 1179261.95 | 36531.575 | 0
2021070718 | 4 | 0.94251 | 141376.5 | 0.22283 | 0 | 0.45713 | 5714.125 | 0.34774 | 27819.2 | 64000 | 5714.125 | 27819.2 | 43843.175 | 7311.6 | 1160885.025 | 43843.175 | 0
2021070719 | 4 | 0.92208 | 138312 | 0.17378 | 0 | 0.47211 | 5901.375 | 0.1583 | 12664 | 64000 | 5901.375 | 12664 | 55746.625 | 11903.45 | 1130604.65 | 55746.625 | 0
2021070720 | 4 | 0.8864 | 132960 | 0.12218 | 0 | 0.51992 | 6499 | 0.03409 | 2727.2 | 64000 | 6499 | 2727.2 | 59733.8 | 3987.175 | 1096337.1 | 59733.8 | 0
2021070721 | 4 | 0.85283 | 127924.5 | 0.25774 | 0 | 0.556 | 6950 | 0 | 0 | 64000 | 6950 | 0 | 56974.5 | -2759.3 | 1064828.85 | 56974.5 | 0
2021070722 | 4 | 0.82156 | 123234 | 0.53211 | 0 | 0.56106 | 7013.25 | 0 | 0 | 64000 | 7013.25 | 0 | 52220.75 | -4753.75 | 1038074.35 | 52220.75 | 0
2021070723 | 4 | 0.76677 | 115015.5 | 0.47598 | 0 | 0.58774 | 7346.75 | 0 | 0 | 64000 | 7346.75 | 0 | 43668.75 | -8552 | 1019871.85 | 43668.75 | 0
2021070724 | 4 | 0.70863 | 106294.5 | 0.22551 | 0 | 0.62542 | 7817.75 | 0 | 0 | 64000 | 7817.75 | 0 | 34476.75 | -9192 | 1010861.35 | 34476.75 | 0
2021070801 | 5 | 0.65872 | 98808 | 0.24098 | 0 | 0.62654 | 7831.75 | 0 | 0 | 64000 | 7831.75 | 0 | 26976.25 | -7500.5 | 1009351.35 | 26976.25 | 0
2021070802 | 5 | 0.62116 | 93174 | 0.26979 | 0 | 0.61506 | 7688.25 | 0 | 0 | 64000 | 7688.25 | 0 | 21485.75 | -5490.5 | 1013331.85 | 21485.75 | 0
2021070803 | 5 | 0.59474 | 89211 | 0.28522 | 0 | 0.57551 | 7193.875 | 0 | 0 | 64000 | 7193.875 | 0 | 18017.125 | -3468.625 | 1020780.975 | 18017.125 | 0
2021070804 | 5 | 0.57625 | 86437.5 | 0.27272 | 0 | 0.53885 | 6735.625 | 0 | 0 | 64000 | 6735.625 | 0 | 15701.875 | -2315.25 | 1030545.35 | 15701.875 | 0
2021070805 | 5 | 0.5733 | 85995 | 0.3058 | 0 | 0.51432 | 6429 | 0 | 0 | 64000 | 6429 | 0 | 15566 | -135.875 | 1040445.6 | 15566 | 0
2021070806 | 5 | 0.58718 | 88077 | 0.37027 | 0 | 0.48003 | 6000.375 | 0.00743 | 594.4 | 64000 | 6000.375 | 594.4 | 17482.225 | 1916.225 | 1048429.625 | 17482.225 | 0
2021070807 | 5 | 0.61235 | 91852.5 | 0.3477 | 0 | 0.48744 | 6093 | 0.09966 | 7972.8 | 64000 | 6093 | 7972.8 | 13786.7 | -3695.525 | 1060109.175 | 13786.7 | 0
2021070808 | 5 | 0.64682 | 97023 | 0.32855 | 0 | 0.53024 | 6628 | 0.2409 | 19272 | 64000 | 6628 | 19272 | 7123 | -6663.7 | 1078452.425 | 7123 | 0
2021070809 | 5 | 0.67864 | 101796 | 0.24799 | 0 | 0.5399 | 6748.75 | 0.35099 | 28079.2 | 64000 | 6748.75 | 28079.2 | 2968.05 | -4154.95 | 1100950.625 | 2968.05 | 0
2021070810 | 5 | 0.70954 | 106431 | 0.16344 | 0 | 0.55345 | 6918.125 | 0.38633 | 30906.4 | 64000 | 6918.125 | 30906.4 | 4606.475 | 1638.425 | 1121810.4 | 4606.475 | 0
2021070811 | 5 | 0.74048 | 111072 | 0.16677 | 0 | 0.58147 | 7268.375 | 0.43402 | 34721.6 | 64000 | 7268.375 | 34721.6 | 5082.025 | 475.55 | 1142194.625 | 5082.025 | 0
2021070812 | 5 | 0.7675 | 115125 | 0.1443 | 0 | 0.61372 | 7671.5 | 0.47709 | 38167.2 | 64000 | 7671.5 | 38167.2 | 5286.3 | 204.275 | 1162374.575 | 5286.3 | 0
2021070813 | 5 | 0.79232 | 118848 | 0.14905 | 0 | 0.59252 | 7406.5 | 0.49804 | 39843.2 | 64000 | 7406.5 | 39843.2 | 7598.3 | 2312 | 1180242.525 | 7598.3 | 0
2021070814 | 5 | 0.81092 | 121638 | 0.15498 | 0 | 0.58518 | 7314.75 | 0.50588 | 40470.4 | 64000 | 7314.75 | 40470.4 | 9852.85 | 2254.55 | 1195855.925 | 9852.85 | 0
2021070815 | 5 | 0.81394 | 122091 | 0.19774 | 0 | 0.5419 | 6773.75 | 0.45895 | 36716 | 64000 | 6773.75 | 36716 | 14601.25 | 4748.4 | 1206720.925 | 14601.25 | 0
2021070816 | 5 | 0.80431 | 120646.5 | 0.27708 | 0 | 0.50574 | 6321.75 | 0.39248 | 31398.4 | 64000 | 6321.75 | 31398.4 | 18926.35 | 4325.1 | 1213260.825 | 18926.35 | 0
2021070817 | 5 | 0.80008 | 120012 | 0.25717 | 0 | 0.47425 | 5928.125 | 0.33078 | 26462.4 | 64000 | 5928.125 | 26462.4 | 23621.475 | 4695.125 | 1215105.6 | 23621.475 | 0
2021070818 | 5 | 0.79412 | 119118 | 0.3388 | 0 | 0.43646 | 5455.75 | 0.22457 | 17965.6 | 64000 | 5455.75 | 17965.6 | 31696.65 | 8075.175 | 1208875.2 | 31696.65 | 0
2021070819 | 5 | 0.77389 | 116083.5 | 0.40197 | 0 | 0.45972 | 5746.5 | 0.12526 | 10020.8 | 64000 | 5746.5 | 10020.8 | 36316.2 | 4619.55 | 1198025.25 | 36316.2 | 0
2021070820 | 5 | 0.74966 | 112449 | 0.52348 | 0 | 0.45594 | 5699.25 | 0.02741 | 2192.8 | 64000 | 5699.25 | 2192.8 | 40556.95 | 4240.75 | 1182934.55 | 40556.95 | 0
2021070821 | 5 | 0.72672 | 109008 | 0.55824 | 0 | 0.43216 | 5402 | 0 | 0 | 64000 | 5402 | 0 | 39606 | -950.95 | 1168794.8 | 39606 | 0
2021070822 | 5 | 0.70568 | 105852 | 0.55051 | 0 | 0.40821 | 5102.625 | 0 | 0 | 64000 | 5102.625 | 0 | 36749.375 | -2856.625 | 1157511.675 | 36749.375 | 0
2021070823 | 5 | 0.66671 | 100006.5 | 0.46041 | 0 | 0.46003 | 5750.375 | 0 | 0 | 64000 | 5750.375 | 0 | 30256.125 | -6493.25 | 1152721.8 | 30256.125 | 0
2021070824 | 5 | 0.62089 | 93133.5 | 0.44129 | 0 | 0.5206 | 6507.5 | 0 | 0 | 64000 | 6507.5 | 0 | 22626 | -7630.125 | 1155562.05 | 22626 | 0
2021070901 | 6 | 0.58118 | 87177 | 0.38635 | 0 | 0.54887 | 6860.875 | 0 | 0 | 64000 | 6860.875 | 0 | 16316.125 | -6309.875 | 1164712.175 | 16316.125 | 0
2021070902 | 6 | 0.55302 | 82953 | 0.37151 | 0 | 0.57019 | 7127.375 | 0 | 0 | 64000 | 7127.375 | 0 | 11825.625 | -4490.5 | 1178352.8 | 11825.625 | 0
2021070903 | 6 | 0.53372 | 80058 | 0.36715 | 0 | 0.50693 | 6336.625 | 0 | 0 | 64000 | 6336.625 | 0 | 9721.375 | -2104.25 | 1194097.675 | 9721.375 | 0
2021070904 | 6 | 0.52249 | 78373.5 | 0.27628 | 0 | 0.44331 | 5541.375 | 0 | 0 | 64000 | 5541.375 | 0 | 8832.125 | -889.25 | 1210731.8 | 8832.125 | 0
2021070905 | 6 | 0.52198 | 78297 | 0.23536 | 0 | 0.32796 | 4099.5 | 0 | 0 | 64000 | 4099.5 | 0 | 10197.5 | 1365.375 | 1226000.55 | 10197.5 | 0
2021070906 | 6 | 0.53713 | 80569.5 | 0.21511 | 0 | 0.2609 | 3261.25 | 0.00451 | 360.8 | 64000 | 3261.25 | 360.8 | 12947.45 | 2749.95 | 1238519.35 | 12947.45 | 0
2021070907 | 6 | 0.56087 | 84130.5 | 0.18855 | 0 | 0.23228 | 2903.5 | 0.0864 | 6912 | 64000 | 2903.5 | 6912 | 10315 | -2632.45 | 1253670.6 | 10315 | 0
2021070908 | 6 | 0.59455 | 89182.5 | 0.15267 | 0 | 0.23224 | 2903 | 0.2267 | 18136 | 64000 | 2903 | 18136 | 4143.5 | -6171.5 | 1274993.35 | 4143.5 | 0
2021070909 | 6 | 0.62637 | 93955.5 | 0.15495 | 0 | 0.26933 | 3366.625 | 0.32203 | 25762.4 | 64000 | 3366.625 | 25762.4 | 826.475 | -3317.025 | 1299633.125 | 826.475 | 0
2021070910 | 6 | 0.65604 | 98406 | 0.18612 | 0 | 0.29111 | 3638.875 | 0.4118 | 32944 | 64000 | 3638.875 | 30767.125 | 0 | -826.475 | 1325099.375 | 0 | 0
2021070911 | 6 | 0.68693 | 103039.5 | 0.19776 | 0 | 0.29777 | 3722.125 | 0.47283 | 37826.4 | 64000 | 3722.125 | 35317.375 | 0 | 0 | 1350000 | 0 | 0
2021070912 | 6 | 0.71766 | 107649 | 0.23596 | 0 | 0.27093 | 3386.625 | 0.53058 | 42446.4 | 64000 | 3386.625 | 40262.375 | 0 | 0 | 1350000 | 0 | 0
2021070913 | 6 | 0.74657 | 111985.5 | 0.18149 | 0 | 0.26998 | 3374.75 | 0.54213 | 43370.4 | 64000 | 3374.75 | 43370.4 | 1240.35 | 1240.35 | 1350000 | 1240.35 | 0
2021070914 | 6 | 0.77197 | 115795.5 | 0.25358 | 0 | 0.28127 | 3515.875 | 0.5387 | 43096 | 64000 | 3515.875 | 43096 | 5183.625 | 3943.275 | 1350000 | 5183.625 | 0
2021070915 | 6 | 0.79164 | 118746 | 0.33905 | 0 | 0.36893 | 4611.625 | 0.56803 | 45442.4 | 64000 | 4611.625 | 45442.4 | 4691.975 | -491.65 | 1350000 | 4691.975 | 0
2021070916 | 6 | 0.80562 | 120843 | 0.37317 | 0 | 0.4276 | 5345 | 0.5815 | 46520 | 64000 | 5345 | 46520 | 4978 | 286.025 | 1350000 | 4978 | 0
2021070917 | 6 | 0.80796 | 121194 | 0.4319 | 0 | 0.44124 | 5515.5 | 0.54873 | 43898.4 | 64000 | 5515.5 | 43898.4 | 7780.1 | 2802.1 | 1350000 | 7780.1 | 0
2021070918 | 6 | 0.80411 | 120616.5 | 0.53113 | 0 | 0.41232 | 5154 | 0.3933 | 31464 | 64000 | 5154 | 31464 | 19998.5 | 12218.4 | 1350000 | 19998.5 | 0
2021070919 | 6 | 0.78431 | 117646.5 | 0.52233 | 0 | 0.43716 | 5464.5 | 0.20542 | 16433.6 | 64000 | 5464.5 | 16433.6 | 31748.4 | 11749.9 | 1343717.85 | 31748.4 | 0
2021070920 | 6 | 0.75278 | 112917 | 0.33816 | 0 | 0.44522 | 5565.25 | 0.04338 | 3470.4 | 64000 | 5565.25 | 3470.4 | 39881.35 | 8132.95 | 1329302.75 | 39881.35 | 0
2021070921 | 6 | 0.71921 | 107881.5 | 0.25104 | 0 | 0.49889 | 6236.125 | 0.00016 | 12.8 | 64000 | 6236.125 | 12.8 | 37632.575 | -2248.775 | 1317136.425 | 37632.575 | 0
2021070922 | 6 | 0.69568 | 104352 | 0.29596 | 0 | 0.52003 | 6500.375 | 0 | 0 | 64000 | 6500.375 | 0 | 33851.625 | -3780.95 | 1308751.05 | 33851.625 | 0
2021070923 | 6 | 0.65588 | 98382 | 0.33803 | 0 | 0.45366 | 5670.75 | 0 | 0 | 64000 | 5670.75 | 0 | 28711.25 | -5140.375 | 1305506.05 | 28711.25 | 0
2021070924 | 6 | 0.60868 | 91302 | 0.4414 | 0 | 0.47558 | 5944.75 | 0 | 0 | 64000 | 5944.75 | 0 | 21357.25 | -7354 | 1309615.05 | 21357.25 | 0
2021071001 | 7 | 0.56602 | 84903 | 0.40002 | 0 | 0.43861 | 5482.625 | 0 | 0 | 64000 | 5482.625 | 0 | 15420.375 | -5936.875 | 1319660.925 | 15420.375 | 0
2021071002 | 7 | 0.53256 | 79884 | 0.40715 | 0 | 0.41305 | 5163.125 | 0 | 0 | 64000 | 5163.125 | 0 | 10720.875 | -4699.5 | 1334406.3 | 10720.875 | 0
2021071003 | 7 | 0.51009 | 76513.5 | 0.34542 | 0 | 0.45026 | 5628.25 | 0 | 0 | 64000 | 5628.25 | 0 | 6885.25 | -3835.625 | 1350000 | 6885.25 | 0
2021071004 | 7 | 0.49292 | 73938 | 0.32682 | 0 | 0.47124 | 5890.5 | 0 | 0 | 64000 | 5890.5 | 0 | 4047.5 | -2837.75 | 1350000 | 4047.5 | 0
2021071005 | 7 | 0.4842 | 72630 | 0.33049 | 0 | 0.34928 | 4366 | 0 | 0 | 64000 | 4366 | 0 | 4264 | 216.5 | 1350000 | 4264 | 0
2021071006 | 7 | 0.48368 | 72552 | 0.29602 | 0 | 0.29781 | 3722.625 | 0.00542 | 433.6 | 64000 | 3722.625 | 433.6 | 4395.775 | 131.775 | 1350000 | 4395.775 | 0
2021071007 | 7 | 0.48846 | 73269 | 0.20055 | 0 | 0.29037 | 3629.625 | 0.13774 | 11019.2 | 64000 | 3629.625 | 5639.375 | 0 | -4395.775 | 1350000 | 0 | 0
2021071008 | 7 | 0.5087 | 76305 | 0.10623 | 0 | 0.33269 | 4158.625 | 0.40142 | 32113.6 | 64000 | 4158.625 | 8146.375 | 0 | 0 | 1350000 | 0 | 0
2021071009 | 7 | 0.5418 | 81270 | 0.07903 | 0 | 0.38577 | 4822.125 | 0.54508 | 43606.4 | 64000 | 4822.125 | 12447.875 | 0 | 0 | 1350000 | 0 | 0
2021071010 | 7 | 0.57634 | 86451 | 0.04701 | 0 | 0.42454 | 5306.75 | 0.61296 | 49036.8 | 64000 | 5306.75 | 17144.25 | 0 | 0 | 1350000 | 0 | 0
2021071011 | 7 | 0.60712 | 91068 | 0.04674 | 0 | 0.42063 | 5257.875 | 0.64526 | 51620.8 | 64000 | 5257.875 | 21810.125 | 0 | 0 | 1350000 | 0 | 0
2021071012 | 7 | 0.63359 | 95038.5 | 0.03369 | 0 | 0.37908 | 4738.5 | 0.65859 | 52687.2 | 64000 | 4738.5 | 26300 | 0 | 0 | 1350000 | 0 | 0
2021071013 | 7 | 0.65424 | 98136 | 0.01974 | 0 | 0.42978 | 5372.25 | 0.66481 | 53184.8 | 64000 | 5372.25 | 28763.75 | 0 | 0 | 1350000 | 0 | 0
2021071014 | 7 | 0.67088 | 100632 | 0.01017 | 0 | 0.49473 | 6184.125 | 0.67372 | 53897.6 | 64000 | 6184.125 | 30447.875 | 0 | 0 | 1350000 | 0 | 0
2021071015 | 7 | 0.68365 | 102547.5 | 0.00852 | 0 | 0.47148 | 5893.5 | 0.67328 | 53862.4 | 64000 | 5893.5 | 32654 | 0 | 0 | 1350000 | 0 | 0
2021071016 | 7 | 0.69546 | 104319 | 0.00518 | 0 | 0.42055 | 5256.875 | 0.65797 | 52637.6 | 64000 | 5256.875 | 35062.125 | 0 | 0 | 1350000 | 0 | 0
2021071017 | 7 | 0.70772 | 106158 | 0.00026 | 0 | 0.40986 | 5123.25 | 0.62185 | 49748 | 64000 | 5123.25 | 37034.75 | 0 | 0 | 1350000 | 0 | 0
2021071018 | 7 | 0.71614 | 107421 | 0.00457 | 0 | 0.4502 | 5627.5 | 0.54229 | 43383.2 | 64000 | 5627.5 | 37793.5 | 0 | 0 | 1350000 | 0 | 0
2021071019 | 7 | 0.70673 | 106009.5 | 0.00589 | 0 | 0.51606 | 6450.75 | 0.33582 | 26865.6 | 64000 | 6450.75 | 26865.6 | 8693.15 | 8693.15 | 1350000 | 8693.15 | 0
2021071020 | 7 | 0.68331 | 102496.5 | 0.00441 | 0 | 0.5291 | 6613.75 | 0.0668 | 5344 | 64000 | 6613.75 | 5344 | 26538.75 | 17845.6 | 1348927.5 | 26538.75 | 0
2021071021 | 7 | 0.66408 | 99612 | 0.03625 | 0 | 0.53352 | 6669 | 0.00071 | 56.8 | 64000 | 6669 | 56.8 | 28886.2 | 2347.45 | 1345507.55 | 28886.2 | 0
2021071022 | 7 | 0.65104 | 97656 | 0.11586 | 0 | 0.54637 | 6829.625 | 0 | 0 | 64000 | 6829.625 | 0 | 26826.375 | -2059.825 | 1344147.425 | 26826.375 | 0
2021071023 | 7 | 0.62006 | 93009 | 0.20297 | 0 | 0.56331 | 7041.375 | 0 | 0 | 64000 | 7041.375 | 0 | 21967.625 | -4858.75 | 1347646.05 | 21967.625 | 0
2021071024 | 7 | 0.58325 | 87487.5 | 0.26021 | 0 | 0.55862 | 6982.75 | 0 | 0 | 64000 | 6982.75 | 0 | 16504.75 | -5462.875 | 1350000 | 16504.75 | 0
2021071101 | 1 | 0.54728 | 82092 | 0.3266 | 0 | 0.54826 | 6853.25 | 0 | 0 | 64000 | 6853.25 | 0 | 11238.75 | -5266 | 1350000 | 11238.75 | 0
2021071102 | 1 | 0.5206 | 78090 | 0.35178 | 0 | 0.5573 | 6966.25 | 0 | 0 | 64000 | 6966.25 | 0 | 7123.75 | -4115 | 1350000 | 7123.75 | 0
2021071103 | 1 | 0.49952 | 74928 | 0.36893 | 0 | 0.54274 | 6784.25 | 0 | 0 | 64000 | 6784.25 | 0 | 4143.75 | -2980 | 1350000 | 4143.75 | 0
2021071104 | 1 | 0.48701 | 73051.5 | 0.34135 | 0 | 0.51113 | 6389.125 | 0 | 0 | 64000 | 6389.125 | 0 | 2662.375 | -1481.375 | 1350000 | 2662.375 | 0
2021071105 | 1 | 0.48013 | 72019.5 | 0.2981 | 0 | 0.45802 | 5725.25 | 0 | 0 | 64000 | 5725.25 | 0 | 2294.25 | -368.125 | 1350000 | 2294.25 | 0
2021071106 | 1 | 0.47995 | 71992.5 | 0.29769 | 0 | 0.4591 | 5738.75 | 0.00529 | 423.2 | 64000 | 5738.75 | 423.2 | 1830.55 | -463.7 | 1350000 | 1830.55 | 0
2021071107 | 1 | 0.48176 | 72264 | 0.41033 | 0 | 0.52125 | 6515.625 | 0.13371 | 10696.8 | 64000 | 6515.625 | 1748.375 | 0 | -1830.55 | 1350000 | 0 | 0
2021071108 | 1 | 0.49705 | 74557.5 | 0.42649 | 0 | 0.55532 | 6941.5 | 0.38136 | 30508.8 | 64000 | 6941.5 | 3616 | 0 | 0 | 1350000 | 0 | 0
2021071109 | 1 | 0.52888 | 79332 | 0.35149 | 0 | 0.54369 | 6796.125 | 0.51032 | 40825.6 | 64000 | 6796.125 | 8535.875 | 0 | 0 | 1350000 | 0 | 0
2021071110 | 1 | 0.56624 | 84936 | 0.2812 | 0 | 0.52943 | 6617.875 | 0.54903 | 43922.4 | 64000 | 6617.875 | 14318.125 | 0 | 0 | 1350000 | 0 | 0
2021071111 | 1 | 0.60438 | 90657 | 0.29039 | 0 | 0.49497 | 6187.125 | 0.58459 | 46767.2 | 64000 | 6187.125 | 20469.875 | 0 | 0 | 1350000 | 0 | 0
2021071112 | 1 | 0.63868 | 95802 | 0.32878 | 0 | 0.42378 | 5297.25 | 0.6136 | 49088 | 64000 | 5297.25 | 26504.75 | 0 | 0 | 1350000 | 0 | 0
2021071113 | 1 | 0.66779 | 100168.5 | 0.39574 | 0 | 0.33546 | 4193.25 | 0.62427 | 49941.6 | 64000 | 4193.25 | 31975.25 | 0 | 0 | 1350000 | 0 | 0
2021071114 | 1 | 0.69179 | 103768.5 | 0.41132 | 0 | 0.29409 | 3676.125 | 0.61667 | 49333.6 | 64000 | 3676.125 | 36092.375 | 0 | 0 | 1350000 | 0 | 0
2021071115 | 1 | 0.71119 | 106678.5 | 0.34616 | 0 | 0.29455 | 3681.875 | 0.63088 | 50470.4 | 64000 | 3681.875 | 38996.625 | 0 | 0 | 1350000 | 0 | 0
2021071116 | 1 | 0.72815 | 109222.5 | 0.32004 | 0 | 0.3034 | 3792.5 | 0.61095 | 48876 | 64000 | 3792.5 | 41430 | 0 | 0 | 1350000 | 0 | 0
2021071117 | 1 | 0.74067 | 111100.5 | 0.29438 | 0 | 0.29785 | 3723.125 | 0.57738 | 46190.4 | 64000 | 3723.125 | 43377.375 | 0 | 0 | 1350000 | 0 | 0
2021071118 | 1 | 0.75091 | 112636.5 | 0.33245 | 0 | 0.34808 | 4351 | 0.47604 | 38083.2 | 64000 | 4351 | 38083.2 | 6202.3 | 6202.3 | 1350000 | 6202.3 | 0
2021071119 | 1 | 0.74931 | 112396.5 | 0.3624 | 0 | 0.39165 | 4895.625 | 0.24681 | 19744.8 | 64000 | 4895.625 | 19744.8 | 23756.075 | 17553.775 | 1350000 | 23756.075 | 0
2021071120 | 1 | 0.73448 | 110172 | 0.22421 | 0 | 0.45183 | 5647.875 | 0.04295 | 3436 | 64000 | 5647.875 | 3436 | 37088.125 | 13332.05 | 1338378.125 | 37088.125 | 0
2021071121 | 1 | 0.71705 | 107557.5 | 0.23295 | 0 | 0.44298 | 5537.25 | 0.00014 | 11.2 | 64000 | 5537.25 | 11.2 | 38009.05 | 920.925 | 1325835.325 | 38009.05 | 0
2021071122 | 1 | 0.70469 | 105703.5 | 0.2073 | 0 | 0.44048 | 5506 | 0 | 0 | 64000 | 5506 | 0 | 36197.5 | -1811.55 | 1315104.075 | 36197.5 | 0
2021071123 | 1 | 0.66943 | 100414.5 | 0.21628 | 0 | 0.39661 | 4957.625 | 0 | 0 | 64000 | 4957.625 | 0 | 31456.875 | -4740.625 | 1309113.45 | 31456.875 | 0
2021071124 | 1 | 0.6286 | 94290 | 0.22547 | 0 | 0.34894 | 4361.75 | 0 | 0 | 64000 | 4361.75 | 0 | 25928.25 | -5528.625 | 1308651.45 | 25928.25 | 0
2021071201 | 2 | 0.5917 | 88755 | 0.26054 | 0 | 0.3184 | 3980 | 0 | 0 | 64000 | 3980 | 0 | 20775 | -5153.25 | 1313342.7 | 20775 | 0
2021071202 | 2 | 0.565 | 84750 | 0.31297 | 0 | 0.31258 | 3907.25 | 0 | 0 | 64000 | 3907.25 | 0 | 16842.75 | -3932.25 | 1321966.2 | 16842.75 | 0
2021071203 | 2 | 0.54437 | 81655.5 | 0.28958 | 0 | 0.29939 | 3742.375 | 0 | 0 | 64000 | 3742.375 | 0 | 13913.125 | -2929.625 | 1333519.325 | 13913.125 | 0
2021071204 | 2 | 0.53459 | 80188.5 | 0.32596 | 0 | 0.23478 | 2934.75 | 0 | 0 | 64000 | 2934.75 | 0 | 13253.75 | -659.375 | 1345731.825 | 13253.75 | 0
2021071205 | 2 | 0.5379 | 80685 | 0.35049 | 0 | 0.18038 | 2254.75 | 0 | 0 | 64000 | 2254.75 | 0 | 14430.25 | 1176.5 | 1350000 | 14430.25 | 0
2021071206 | 2 | 0.55719 | 83578.5 | 0.29393 | 0 | 0.1373 | 1716.25 | 0.00927 | 741.6 | 64000 | 1716.25 | 741.6 | 17120.65 | 2690.4 | 1350000 | 17120.65 | 0
2021071207 | 2 | 0.59045 | 88567.5 | 0.23264 | 0 | 0.17583 | 2197.875 | 0.07709 | 6167.2 | 64000 | 2197.875 | 6167.2 | 16202.425 | -918.225 | 1350000 | 16202.425 | 0
2021071208 | 2 | 0.63152 | 94728 | 0.18326 | 0 | 0.18649 | 2331.125 | 0.15342 | 12273.6 | 64000 | 2331.125 | 12273.6 | 16123.275 | -79.15 | 1350000 | 16123.275 | 0
2021071209 | 2 | 0.67265 | 100897.5 | 0.11382 | 0 | 0.19118 | 2389.75 | 0.16219 | 12975.2 | 64000 | 2389.75 | 12975.2 | 21532.55 | 5409.275 | 1350000 | 21532.55 | 0
2021071210 | 2 | 0.71082 | 106623 | 0.07328 | 0 | 0.19592 | 2449 | 0.17664 | 14131.2 | 64000 | 2449 | 14131.2 | 26042.8 | 4510.25 | 1349423.45 | 26042.8 | 0
2021071211 | 2 | 0.75023 | 112534.5 | 0.07326 | 0 | 0.1894 | 2367.5 | 0.20875 | 16700 | 64000 | 2367.5 | 16700 | 29467 | 3424.2 | 1345422.7 | 29467 | 0
2021071212 | 2 | 0.78947 | 118420.5 | 0.08871 | 0 | 0.16098 | 2012.25 | 0.19584 | 15667.2 | 64000 | 2012.25 | 15667.2 | 36741.05 | 7274.05 | 1334147.9 | 36741.05 | 0
2021071213 | 2 | 0.82358 | 123537 | 0.1045 | 0 | 0.1433 | 1791.25 | 0.21083 | 16866.4 | 64000 | 1791.25 | 16866.4 | 40879.35 | 4138.3 | 1318734.8 | 40879.35 | 0
2021071214 | 2 | 0.85548 | 128322 | 0.1434 | 0 | 0.13793 | 1724.125 | 0.23151 | 18520.8 | 64000 | 1724.125 | 18520.8 | 44077.075 | 3197.725 | 1300123.975 | 44077.075 | 0
2021071215 | 2 | 0.87723 | 131584.5 | 0.14425 | 0 | 0.11965 | 1495.625 | 0.23473 | 18778.4 | 64000 | 1495.625 | 18778.4 | 47310.475 | 3233.4 | 1278279.75 | 47310.475 | 0
2021071216 | 2 | 0.88739 | 133108.5 | 0.12906 | 0 | 0.09829 | 1228.625 | 0.22295 | 17836 | 64000 | 1228.625 | 17836 | 50043.875 | 2733.4 | 1253702.125 | 50043.875 | 0
2021071217 | 2 | 0.88645 | 132967.5 | 0.086 | 0 | 0.06719 | 839.875 | 0.20624 | 16499.2 | 64000 | 839.875 | 16499.2 | 51628.425 | 1584.55 | 1227539.95 | 51628.425 | 0
2021071218 | 2 | 0.87983 | 131974.5 | 0.07695 | 0 | 0.08043 | 1005.375 | 0.21283 | 17026.4 | 64000 | 1005.375 | 17026.4 | 49942.725 | -1685.7 | 1203063.475 | 49942.725 | 0
2021071219 | 2 | 0.86206 | 129309 | 0.06041 | 0 | 0.08299 | 1037.375 | 0.12573 | 10058.4 | 64000 | 1037.375 | 10058.4 | 54213.225 | 4270.5 | 1174316.5 | 54213.225 | 0
2021071220 | 2 | 0.8329 | 124935 | 0.0661 | 0 | 0.07866 | 983.25 | 0.0326 | 2608 | 64000 | 983.25 | 2608 | 57343.75 | 3130.525 | 1142439 | 57343.75 | 0
2021071221 | 2 | 0.80415 | 120622.5 | 0.06931 | 0 | 0.09425 | 1178.125 | 0 | 0 | 64000 | 1178.125 | 0 | 55444.375 | -1899.375 | 1112460.875 | 55444.375 | 0
2021071222 | 2 | 0.77821 | 116731.5 | 0.07907 | 0 | 0.12124 | 1515.5 | 0 | 0 | 64000 | 1515.5 | 0 | 51216 | -4228.375 | 1086711.125 | 51216 | 0
2021071223 | 2 | 0.73219 | 109828.5 | 0.08921 | 0 | 0.13938 | 1742.25 | 0 | 0 | 64000 | 1742.25 | 0 | 44086.25 | -7129.75 | 1068091.125 | 44086.25 | 0
2021071224 | 2 | 0.67885 | 101827.5 | 0.07809 | 0 | 0.17608 | 2201 | 0 | 0 | 64000 | 2201 | 0 | 35626.5 | -8459.75 | 1057930.875 | 35626.5 | 0
2021071301 | 3 | 0.63333 | 94999.5 | 0.14563 | 0 | 0.20862 | 2607.75 | 0 | 0 | 64000 | 2607.75 | 0 | 28391.75 | -7234.75 | 1055005.375 | 28391.75 | 0
2021071302 | 3 | 0.59899 | 89848.5 | 0.23104 | 0 | 0.2455 | 3068.75 | 0 | 0 | 64000 | 3068.75 | 0 | 22779.75 | -5612 | 1057691.875 | 22779.75 | 0
2021071303 | 3 | 0.57625 | 86437.5 | 0.29872 | 0 | 0.26806 | 3350.75 | 0 | 0 | 64000 | 3350.75 | 0 | 19086.75 | -3693 | 1064071.375 | 19086.75 | 0
2021071304 | 3 | 0.56197 | 84295.5 | 0.34352 | 0 | 0.32418 | 4052.25 | 0 | 0 | 64000 | 4052.25 | 0 | 16243.25 | -2843.5 | 1073294.375 | 16243.25 | 0
2021071305 | 3 | 0.56062 | 84093 | 0.32327 | 0 | 0.33836 | 4229.5 | 0 | 0 | 64000 | 4229.5 | 0 | 15863.5 | -379.75 | 1082897.125 | 15863.5 | 0
2021071306 | 3 | 0.57691 | 86536.5 | 0.32612 | 0 | 0.42052 | 5256.5 | 0.00244 | 195.2 | 64000 | 5256.5 | 195.2 | 17084.8 | 1221.3 | 1091278.575 | 17084.8 | 0
2021071307 | 3 | 0.60534 | 90801 | 0.24239 | 0 | 0.46489 | 5811.125 | 0.08183 | 6546.4 | 64000 | 5811.125 | 6546.4 | 14443.475 | -2641.325 | 1102301.35 | 14443.475 | 0
2021071308 | 3 | 0.64421 | 96631.5 | 0.11417 | 0 | 0.45387 | 5673.375 | 0.28095 | 22476 | 64000 | 5673.375 | 22476 | 4482.125 | -9961.35 | 1123285.475 | 4482.125 | 0
2021071309 | 3 | 0.68372 | 102558 | 0.07025 | 0 | 0.50259 | 6282.375 | 0.42476 | 33980.8 | 64000 | 6282.375 | 32275.625 | 0 | -4482.125 | 1148751.725 | 0 | 0
2021071310 | 3 | 0.71799 | 107698.5 | 0.1013 | 0 | 0.52911 | 6613.875 | 0.50662 | 40529.6 | 64000 | 6613.875 | 37084.625 | 0 | 0 | 1174217.975 | 0 | 0
2021071311 | 3 | 0.75258 | 112887 | 0.11134 | 0 | 0.54686 | 6835.75 | 0.55842 | 44673.6 | 64000 | 6835.75 | 42051.25 | 0 | 0 | 1199684.225 | 0 | 0
2021071312 | 3 | 0.78192 | 117288 | 0.10535 | 0 | 0.4972 | 6215 | 0.58474 | 46779.2 | 64000 | 6215 | 46779.2 | 293.8 | 293.8 | 1224856.675 | 293.8 | 0
2021071313 | 3 | 0.80839 | 121258.5 | 0.11998 | 0 | 0.45946 | 5743.25 | 0.58031 | 46424.8 | 64000 | 5743.25 | 46424.8 | 5090.45 | 4796.65 | 1245232.475 | 5090.45 | 0
2021071314 | 3 | 0.83368 | 125052 | 0.16175 | 0 | 0.46432 | 5804 | 0.60396 | 48316.8 | 64000 | 5804 | 48316.8 | 6931.2 | 1840.75 | 1263767.525 | 6931.2 | 0
2021071315 | 3 | 0.85036 | 127554 | 0.20047 | 0 | 0.48897 | 6112.125 | 0.59218 | 47374.4 | 64000 | 6112.125 | 47374.4 | 10067.475 | 3136.275 | 1279166.3 | 10067.475 | 0
2021071316 | 3 | 0.85986 | 128979 | 0.33697 | 0 | 0.53755 | 6719.375 | 0.52007 | 41605.6 | 64000 | 6719.375 | 41605.6 | 16654.025 | 6586.55 | 1287978.525 | 16654.025 | 0
2021071317 | 3 | 0.8657 | 129855 | 0.35515 | 0 | 0.60883 | 7610.375 | 0.40051 | 32040.8 | 64000 | 7610.375 | 32040.8 | 26203.825 | 9549.8 | 1287240.95 | 26203.825 | 0
2021071318 | 3 | 0.86586 | 129879 | 0.3897 | 0 | 0.6115 | 7643.75 | 0.24191 | 19352.8 | 64000 | 7643.75 | 19352.8 | 38882.45 | 12678.625 | 1273824.75 | 38882.45 | 0
2021071319 | 3 | 0.85484 | 128226 | 0.4522 | 0 | 0.64461 | 8057.625 | 0.09006 | 7204.8 | 64000 | 8057.625 | 7204.8 | 48963.575 | 10081.125 | 1250327.425 | 48963.575 | 0
2021071320 | 3 | 0.83101 | 124651.5 | 0.452 | 0 | 0.63352 | 7919 | 0.01732 | 1385.6 | 64000 | 7919 | 1385.6 | 51346.9 | 2383.325 | 1224446.775 | 51346.9 | 0
2021071321 | 3 | 0.80403 | 120604.5 | 0.56481 | 0 | 0.59191 | 7398.875 | 0 | 0 | 64000 | 7398.875 | 0 | 49205.625 | -2141.275 | 1200707.4 | 49205.625 | 0
2021071322 | 3 | 0.77778 | 116667 | 0.46325 | 0 | 0.5737 | 7171.25 | 0 | 0 | 64000 | 7171.25 | 0 | 45495.75 | -3709.875 | 1180677.9 | 45495.75 | 0
2021071323 | 3 | 0.73017 | 109525.5 | 0.6666 | 0 | 0.5398 | 6747.5 | 0 | 0 | 64000 | 6747.5 | 0 | 38778 | -6717.75 | 1167366.15 | 38778 | 0
2021071324 | 3 | 0.67924 | 101886 | 0.62022 | 0 | 0.54066 | 6758.25 | 0 | 0 | 64000 | 6758.25 | 0 | 31127.75 | -7650.25 | 1161704.65 | 31127.75 | 0
2021071401 | 4 | 0.63211 | 94816.5 | 0.59977 | 0 | 0.59353 | 7419.125 | 0 | 0 | 64000 | 7419.125 | 0 | 23397.375 | -7730.375 | 1163773.525 | 23397.375 | 0
2021071402 | 4 | 0.5986 | 89790 | 0.57796 | 0 | 0.61221 | 7652.625 | 0 | 0 | 64000 | 7652.625 | 0 | 18137.375 | -5260 | 1171102.4 | 18137.375 | 0
2021071403 | 4 | 0.57572 | 86358 | 0.6221 | 0 | 0.61279 | 7659.875 | 0 | 0 | 64000 | 7659.875 | 0 | 14698.125 | -3439.25 | 1181870.525 | 14698.125 | 0
2021071404 | 4 | 0.56142 | 84213 | 0.66613 | 0 | 0.46553 | 5819.125 | 0 | 0 | 64000 | 5819.125 | 0 | 14393.875 | -304.25 | 1192942.9 | 14393.875 | 0
2021071405 | 4 | 0.55894 | 83841 | 0.60322 | 0 | 0.29362 | 3670.25 | 0 | 0 | 64000 | 3670.25 | 0 | 16170.75 | 1776.875 | 1202238.4 | 16170.75 | 0
2021071406 | 4 | 0.57402 | 86103 | 0.55715 | 0 | 0.26388 | 3298.5 | 0.00485 | 388 | 64000 | 3298.5 | 388 | 18416.5 | 2245.75 | 1209288.15 | 18416.5 | 0
2021071407 | 4 | 0.60139 | 90208.5 | 0.51892 | 0 | 0.32089 | 4011.125 | 0.07187 | 5749.6 | 64000 | 4011.125 | 5749.6 | 16447.775 | -1968.725 | 1218306.625 | 16447.775 | 0
2021071408 | 4 | 0.64018 | 96027 | 0.40889 | 0 | 0.27431 | 3428.875 | 0.16262 | 13009.6 | 64000 | 3428.875 | 13009.6 | 15588.525 | -859.25 | 1228184.35 | 15588.525 | 0
2021071409 | 4 | 0.6827 | 102405 | 0.34078 | 0 | 0.2022 | 2527.5 | 0.26803 | 21442.4 | 64000 | 2527.5 | 21442.4 | 14435.1 | -1153.425 | 1239215.5 | 14435.1 | 0
2021071410 | 4 | 0.7241 | 108615 | 0.29804 | 0 | 0.15469 | 1933.625 | 0.36634 | 29307.2 | 64000 | 1933.625 | 29307.2 | 13374.175 | -1060.925 | 1251307.575 | 13374.175 | 0
2021071411 | 4 | 0.76739 | 115108.5 | 0.27614 | 0 | 0.07846 | 980.75 | 0.43889 | 35111.2 | 64000 | 980.75 | 35111.2 | 15016.55 | 1642.375 | 1261757.275 | 15016.55 | 0
2021071412 | 4 | 0.80701 | 121051.5 | 0.26914 | 0 | 0.0546 | 682.5 | 0.49263 | 39410.4 | 64000 | 682.5 | 39410.4 | 16958.6 | 1942.05 | 1270264.925 | 16958.6 | 0
2021071413 | 4 | 0.84399 | 126598.5 | 0.28959 | 0 | 0.06522 | 815.25 | 0.47979 | 38383.2 | 64000 | 815.25 | 38383.2 | 23400.05 | 6441.45 | 1272331.125 | 23400.05 | 0
2021071414 | 4 | 0.87907 | 131860.5 | 0.30338 | 0 | 0.0876 | 1095 | 0.47227 | 37781.6 | 64000 | 1095 | 37781.6 | 28983.9 | 5583.85 | 1268813.475 | 28983.9 | 0
2021071415 | 4 | 0.90037 | 135055.5 | 0.29947 | 0 | 0.12156 | 1519.5 | 0.47625 | 38100 | 64000 | 1519.5 | 38100 | 31436 | 2452.1 | 1262843.725 | 31436 | 0
2021071416 | 4 | 0.91273 | 136909.5 | 0.27183 | 0 | 0.11889 | 1486.125 | 0.44948 | 35958.4 | 64000 | 1486.125 | 35958.4 | 35464.975 | 4028.975 | 1252845 | 35464.975 | 0
2021071417 | 4 | 0.9136 | 137040 | 0.20272 | 0 | 0.12001 | 1500.125 | 0.35995 | 28796 | 64000 | 1500.125 | 28796 | 42743.875 | 7278.9 | 1235567.375 | 42743.875 | 0
2021071418 | 4 | 0.90521 | 135781.5 | 0.23429 | 0 | 0.13503 | 1687.875 | 0.28814 | 23051.2 | 64000 | 1687.875 | 23051.2 | 47042.425 | 4298.55 | 1213991.2 | 47042.425 | 0
2021071419 | 4 | 0.88661 | 132991.5 | 0.07276 | 0 | 0.15062 | 1882.75 | 0.15106 | 12084.8 | 64000 | 1882.75 | 12084.8 | 55023.95 | 7981.525 | 1184433.5 | 55023.95 | 0
2021071420 | 4 | 0.8579 | 128685 | 0.03369 | 0 | 0.17211 | 2151.375 | 0.03245 | 2596 | 64000 | 2151.375 | 2596 | 59937.625 | 4913.675 | 1149962.125 | 59937.625 | 0
2021071421 | 4 | 0.82475 | 123712.5 | 0.02373 | 0 | 0.18481 | 2310.125 | 7e-05 | 5.6 | 64000 | 2310.125 | 5.6 | 57396.775 | -2540.85 | 1118031.6 | 57396.775 | 0
2021071422 | 4 | 0.7973 | 119595 | 0.01564 | 0 | 0.18047 | 2255.875 | 0 | 0 | 64000 | 2255.875 | 0 | 53339.125 | -4057.65 | 1090158.725 | 53339.125 | 0
2021071423 | 4 | 0.74645 | 111967.5 | 0.03619 | 0 | 0.17326 | 2165.75 | 0 | 0 | 64000 | 2165.75 | 0 | 45801.75 | -7537.375 | 1069823.225 | 45801.75 | 0
2021071424 | 4 | 0.69034 | 103551 | 0.05513 | 0 | 0.18355 | 2294.375 | 0 | 0 | 64000 | 2294.375 | 0 | 37256.625 | -8545.125 | 1058032.85 | 37256.625 | 0
2021071501 | 5 | 0.64106 | 96159 | 0.07669 | 0 | 0.2137 | 2671.25 | 0 | 0 | 64000 | 2671.25 | 0 | 29487.75 | -7768.875 | 1054011.35 | 29487.75 | 0
2021071502 | 5 | 0.60467 | 90700.5 | 0.12377 | 0 | 0.21436 | 2679.5 | 0 | 0 | 64000 | 2679.5 | 0 | 24021 | -5466.75 | 1055456.6 | 24021 | 0
2021071503 | 5 | 0.57786 | 86679 | 0.15301 | 0 | 0.21877 | 2734.625 | 0 | 0 | 64000 | 2734.625 | 0 | 19944.375 | -4076.625 | 1060978.475 | 19944.375 | 0
2021071504 | 5 | 0.56234 | 84351 | 0.16569 | 0 | 0.24011 | 3001.375 | 0 | 0 | 64000 | 3001.375 | 0 | 17349.625 | -2594.75 | 1069095.1 | 17349.625 | 0
2021071505 | 5 | 0.55816 | 83724 | 0.15731 | 0 | 0.21467 | 2683.375 | 0 | 0 | 64000 | 2683.375 | 0 | 17040.625 | -309 | 1077520.725 | 17040.625 | 0
2021071506 | 5 | 0.57225 | 85837.5 | 0.17796 | 0 | 0.19519 | 2439.875 | 0.00506 | 404.8 | 64000 | 2439.875 | 404.8 | 18992.825 | 1952.2 | 1083994.15 | 18992.825 | 0
2021071507 | 5 | 0.59891 | 89836.5 | 0.19941 | 0 | 0.25803 | 3225.375 | 0.06106 | 4884.8 | 64000 | 3225.375 | 4884.8 | 17726.325 | -1266.5 | 1091734.075 | 17726.325 | 0
2021071508 | 5 | 0.6392 | 95880 | 0.12399 | 0 | 0.3764 | 4705 | 0.18445 | 14756 | 64000 | 4705 | 14756 | 12419 | -5307.325 | 1104781.325 | 12419 | 0
2021071509 | 5 | 0.68292 | 102438 | 0.05425 | 0 | 0.45445 | 5680.625 | 0.31003 | 24802.4 | 64000 | 5680.625 | 24802.4 | 7954.975 | -4464.025 | 1122292.6 | 7954.975 | 0
2021071510 | 5 | 0.72681 | 109021.5 | 0.03891 | 0 | 0.49914 | 6239.25 | 0.43218 | 34574.4 | 64000 | 6239.25 | 34574.4 | 4207.85 | -3747.125 | 1143551 | 4207.85 | 0
2021071511 | 5 | 0.77484 | 116226 | 0.10276 | 0 | 0.53695 | 6711.875 | 0.48707 | 38965.6 | 64000 | 6711.875 | 38965.6 | 6548.525 | 2340.675 | 1162468.725 | 6548.525 | 0
2021071512 | 5 | 0.81968 | 122952 | 0.14401 | 0 | 0.55095 | 6886.875 | 0.6014 | 48112 | 64000 | 6886.875 | 48112 | 3953.125 | -2595.4 | 1183981.85 | 3953.125 | 0
2021071513 | 5 | 0.85825 | 128737.5 | 0.19057 | 0 | 0.53546 | 6693.25 | 0.63522 | 50817.6 | 64000 | 6693.25 | 50817.6 | 7226.65 | 3273.525 | 1202221.45 | 7226.65 | 0
2021071514 | 5 | 0.88885 | 133327.5 | 0.21934 | 0 | 0.44156 | 5519.5 | 0.61117 | 48893.6 | 64000 | 5519.5 | 48893.6 | 14914.4 | 7687.75 | 1212773.3 | 14914.4 | 0
2021071515 | 5 | 0.90702 | 136053 | 0.24877 | 0 | 0.46737 | 5842.125 | 0.55791 | 44632.8 | 64000 | 5842.125 | 44632.8 | 21578.075 | 6663.675 | 1216661.475 | 21578.075 | 0
2021071516 | 5 | 0.91986 | 137979 | 0.26071 | 0 | 0.52394 | 6549.25 | 0.53999 | 43199.2 | 64000 | 6549.25 | 43199.2 | 24230.55 | 2652.475 | 1217897.175 | 24230.55 | 0
2021071517 | 5 | 0.92789 | 139183.5 | 0.27412 | 0 | 0.49139 | 6142.375 | 0.45966 | 36772.8 | 64000 | 6142.375 | 36772.8 | 32268.325 | 8037.775 | 1211095.1 | 32268.325 | 0
2021071518 | 5 | 0.92734 | 139101 | 0.26164 | 0 | 0.38165 | 4770.625 | 0.37138 | 29710.4 | 64000 | 4770.625 | 29710.4 | 40619.975 | 8351.65 | 1195941.375 | 40619.975 | 0
2021071519 | 5 | 0.91581 | 137371.5 | 0.21999 | 0 | 0.43759 | 5469.875 | 0.21343 | 17074.4 | 64000 | 5469.875 | 17074.4 | 50827.225 | 10207.25 | 1170580.4 | 50827.225 | 0
2021071520 | 5 | 0.88678 | 133017 | 0.20911 | 0 | 0.44208 | 5526 | 0.04625 | 3700 | 64000 | 5526 | 3700 | 59791 | 8963.775 | 1136255.65 | 59791 | 0
2021071521 | 5 | 0.85187 | 127780.5 | 0.2878 | 0 | 0.52212 | 6526.5 | 0.00042 | 33.6 | 64000 | 6526.5 | 33.6 | 57220.4 | -2570.6 | 1104501.5 | 57220.4 | 0
2021071522 | 5 | 0.82223 | 123334.5 | 0.46814 | 0 | 0.50848 | 6356 | 0 | 0 | 64000 | 6356 | 0 | 52978.5 | -4241.9 | 1076989.25 | 52978.5 | 0
2021071523 | 5 | 0.77005 | 115507.5 | 0.60298 | 0 | 0.47634 | 5954.25 | 0 | 0 | 64000 | 5954.25 | 0 | 45553.25 | -7425.25 | 1056902.25 | 45553.25 | 0
2021071524 | 5 | 0.71252 | 106878 | 0.63297 | 0 | 0.26806 | 3350.75 | 0 | 0 | 64000 | 3350.75 | 0 | 39527.25 | -6026 | 1042841.25 | 39527.25 | 0
2021071601 | 6 | 0.66212 | 99318 | 0.70027 | 0 | 0.23186 | 2898.25 | 0 | 0 | 64000 | 2898.25 | 0 | 32419.75 | -7107.5 | 1035887.75 | 32419.75 | 0
2021071602 | 6 | 0.62471 | 93706.5 | 0.71289 | 0 | 0.21773 | 2721.625 | 0 | 0 | 64000 | 2721.625 | 0 | 26984.875 | -5434.875 | 1034369.125 | 26984.875 | 0
2021071603 | 6 | 0.59768 | 89652 | 0.68503 | 0 | 0.22078 | 2759.75 | 0 | 0 | 64000 | 2759.75 | 0 | 22892.25 | -4092.625 | 1036943.125 | 22892.25 | 0
2021071604 | 6 | 0.57998 | 86997 | 0.63079 | 0 | 0.19243 | 2405.375 | 0 | 0 | 64000 | 2405.375 | 0 | 20591.625 | -2300.625 | 1041817.75 | 20591.625 | 0
2021071605 | 6 | 0.57653 | 86479.5 | 0.62938 | 0 | 0.20699 | 2587.375 | 0 | 0 | 64000 | 2587.375 | 0 | 19892.125 | -699.5 | 1047391.875 | 19892.125 | 0
2021071606 | 6 | 0.58895 | 88342.5 | 0.58165 | 0 | 0.17874 | 2234.25 | 0.00984 | 787.2 | 64000 | 2234.25 | 787.2 | 21321.05 | 1428.925 | 1051537.075 | 21321.05 | 0
2021071607 | 6 | 0.61219 | 91828.5 | 0.49155 | 0 | 0.13 | 1625 | 0.1084 | 8672 | 64000 | 1625 | 8672 | 17531.5 | -3789.55 | 1059471.825 | 17531.5 | 0
2021071608 | 6 | 0.652 | 97800 | 0.34269 | 0 | 0.18414 | 2301.75 | 0.29315 | 23452 | 64000 | 2301.75 | 23452 | 8046.25 | -9485.25 | 1076891.825 | 8046.25 | 0
2021071609 | 6 | 0.69808 | 104712 | 0.19543 | 0 | 0.21658 | 2707.25 | 0.44753 | 35802.4 | 64000 | 2707.25 | 35802.4 | 2202.35 | -5843.9 | 1100155.725 | 2202.35 | 0
2021071610 | 6 | 0.74375 | 111562.5 | 0.10314 | 0 | 0.25153 | 3144.125 | 0.52902 | 42321.6 | 64000 | 3144.125 | 42321.6 | 2096.775 | -105.575 | 1123525.2 | 2096.775 | 0
2021071611 | 6 | 0.78684 | 118026 | 0.13998 | 0 | 0.26965 | 3370.625 | 0.62474 | 49979.2 | 64000 | 3370.625 | 49979.2 | 676.175 | -1420.6 | 1148315.275 | 676.175 | 0
2021071612 | 6 | 0.82707 | 124060.5 | 0.16174 | 0 | 0.34452 | 4306.5 | 0.67213 | 53770.4 | 64000 | 4306.5 | 53770.4 | 1983.6 | 1307.425 | 1171797.925 | 1983.6 | 0
2021071613 | 6 | 0.86263 | 129394.5 | 0.19853 | 0 | 0.55469 | 6933.625 | 0.6886 | 55088 | 64000 | 6933.625 | 55088 | 3372.875 | 1389.275 | 1193891.3 | 3372.875 | 0
2021071614 | 6 | 0.88931 | 133396.5 | 0.21853 | 0 | 0.60355 | 7544.375 | 0.69441 | 55552.8 | 64000 | 7544.375 | 55552.8 | 6299.325 | 2926.45 | 1213058.225 | 6299.325 | 0
2021071615 | 6 | 0.90202 | 135303 | 0.22765 | 0 | 0.53872 | 6734 | 0.6936 | 55488 | 64000 | 6734 | 55488 | 9081 | 2781.675 | 1229443.475 | 9081 | 0
2021071616 | 6 | 0.90207 | 135310.5 | 0.19908 | 0 | 0.41717 | 5214.625 | 0.6717 | 53736 | 64000 | 5214.625 | 53736 | 12359.875 | 3278.875 | 1242549.85 | 12359.875 | 0
2021071617 | 6 | 0.89827 | 134740.5 | 0.18185 | 0 | 0.29192 | 3649 | 0.63129 | 50503.2 | 64000 | 3649 | 50503.2 | 16588.3 | 4228.425 | 1251427.8 | 16588.3 | 0
2021071618 | 6 | 0.89018 | 133527 | 0.21244 | 0 | 0.26154 | 3269.25 | 0.55009 | 44007.2 | 64000 | 3269.25 | 44007.2 | 22250.55 | 5662.25 | 1254643.5 | 22250.55 | 0
2021071619 | 6 | 0.87145 | 130717.5 | 0.18822 | 0 | 0.29072 | 3634 | 0.33561 | 26848.8 | 64000 | 3634 | 26848.8 | 36234.7 | 13984.15 | 1243875.05 | 36234.7 | 0
2021071620 | 6 | 0.83892 | 125838 | 0.2204 | 0 | 0.38245 | 4780.625 | 0.07214 | 5771.2 | 64000 | 4780.625 | 5771.2 | 51286.175 | 15051.475 | 1218055.125 | 51286.175 | 0
2021071621 | 6 | 0.80842 | 121263 | 0.29026 | 0 | 0.52764 | 6595.5 | 0.00073 | 58.4 | 64000 | 6595.5 | 58.4 | 50609.1 | -677.075 | 1192912.275 | 50609.1 | 0
2021071622 | 6 | 0.78257 | 117385.5 | 0.25508 | 0 | 0.63564 | 7945.5 | 0 | 0 | 64000 | 7945.5 | 0 | 45440 | -5169.1 | 1172938.525 | 45440 | 0
2021071623 | 6 | 0.7385 | 110775 | 0.15854 | 0 | 0.63576 | 7947 | 0 | 0 | 64000 | 7947 | 0 | 38828 | -6612 | 1159576.775 | 38828 | 0
2021071624 | 6 | 0.68755 | 103132.5 | 0.13526 | 0 | 0.61864 | 7733 | 0 | 0 | 64000 | 7733 | 0 | 31399.5 | -7428.5 | 1153643.525 | 31399.5 | 0
2021071701 | 7 | 0.64184 | 96276 | 0.16037 | 0 | 0.60738 | 7592.25 | 0 | 0 | 64000 | 7592.25 | 0 | 24683.75 | -6715.75 | 1154426.025 | 24683.75 | 0
2021071702 | 7 | 0.60705 | 91057.5 | 0.16858 | 0 | 0.57432 | 7179 | 0 | 0 | 64000 | 7179 | 0 | 19878.5 | -4805.25 | 1160013.775 | 19878.5 | 0
2021071703 | 7 | 0.58211 | 87316.5 | 0.1567 | 0 | 0.48689 | 6086.125 | 0 | 0 | 64000 | 6086.125 | 0 | 17230.375 | -2648.125 | 1168249.65 | 17230.375 | 0
2021071704 | 7 | 0.56373 | 84559.5 | 0.18801 | 0 | 0.28443 | 3555.375 | 0 | 0 | 64000 | 3555.375 | 0 | 17004.125 | -226.25 | 1176711.775 | 17004.125 | 0
2021071705 | 7 | 0.55291 | 82936.5 | 0.20737 | 0 | 0.15893 | 1986.625 | 0 | 0 | 64000 | 1986.625 | 0 | 16949.875 | -54.25 | 1185228.15 | 16949.875 | 0
2021071706 | 7 | 0.55209 | 82813.5 | 0.21357 | 0 | 0.16018 | 2002.25 | 0.0091 | 728 | 64000 | 2002.25 | 728 | 16083.25 | -866.625 | 1194611.15 | 16083.25 | 0
2021071707 | 7 | 0.55715 | 83572.5 | 0.22405 | 0 | 0.23566 | 2945.75 | 0.14791 | 11832.8 | 64000 | 2945.75 | 11832.8 | 4793.95 | -11289.3 | 1215283.45 | 4793.95 | 0
2021071708 | 7 | 0.58286 | 87429 | 0.28162 | 0 | 0.23112 | 2889 | 0.41059 | 32847.2 | 64000 | 2889 | 20540 | 0 | -4793.95 | 1240749.7 | 0 | 0
2021071709 | 7 | 0.62742 | 94113 | 0.17508 | 0 | 0.18379 | 2297.375 | 0.58379 | 46703.2 | 64000 | 2297.375 | 27815.625 | 0 | 0 | 1266215.95 | 0 | 0
2021071710 | 7 | 0.67456 | 101184 | 0.16044 | 0 | 0.14752 | 1844 | 0.64799 | 51839.2 | 64000 | 1844 | 35340 | 0 | 0 | 1291682.2 | 0 | 0
2021071711 | 7 | 0.7227 | 108405 | 0.1176 | 0 | 0.11467 | 1433.375 | 0.67865 | 54292 | 64000 | 1433.375 | 42971.625 | 0 | 0 | 1317148.45 | 0 | 0
2021071712 | 7 | 0.76475 | 114712.5 | 0.15313 | 0 | 0.11422 | 1427.75 | 0.69547 | 55637.6 | 64000 | 1427.75 | 49284.75 | 0 | 0 | 1342614.7 | 0 | 0
2021071713 | 7 | 0.79756 | 119634 | 0.22283 | 0 | 0.13253 | 1656.625 | 0.70715 | 56572 | 64000 | 1656.625 | 53977.375 | 0 | 0 | 1350000 | 0 | 0
2021071714 | 7 | 0.81719 | 122578.5 | 0.27423 | 0 | 0.15248 | 1906 | 0.71523 | 57218.4 | 64000 | 1906 | 56672.5 | 0 | 0 | 1350000 | 0 | 0
2021071715 | 7 | 0.82207 | 123310.5 | 0.30807 | 0 | 0.18116 | 2264.5 | 0.70726 | 56580.8 | 64000 | 2264.5 | 56580.8 | 465.2 | 465.2 | 1350000 | 465.2 | 0
2021071716 | 7 | 0.81501 | 122251.5 | 0.3652 | 0 | 0.14839 | 1854.875 | 0.69169 | 55335.2 | 64000 | 1854.875 | 55335.2 | 1061.425 | 596.225 | 1350000 | 1061.425 | 0
2021071717 | 7 | 0.81096 | 121644 | 0.36214 | 0 | 0.09516 | 1189.5 | 0.65904 | 52723.2 | 64000 | 1189.5 | 52723.2 | 3731.3 | 2669.875 | 1350000 | 3731.3 | 0
2021071718 | 7 | 0.80613 | 120919.5 | 0.39648 | 0 | 0.13643 | 1705.375 | 0.5706 | 45648 | 64000 | 1705.375 | 45648 | 9566.125 | 5834.825 | 1350000 | 9566.125 | 0
2021071719 | 7 | 0.79068 | 118602 | 0.48096 | 0 | 0.17328 | 2166 | 0.31459 | 25167.2 | 64000 | 2166 | 25167.2 | 27268.8 | 17702.675 | 1348197.45 | 27268.8 | 0
2021071720 | 7 | 0.76311 | 114466.5 | 0.47298 | 0 | 0.15701 | 1962.625 | 0.05738 | 4590.4 | 64000 | 1962.625 | 4590.4 | 43913.475 | 16644.675 | 1329750.225 | 43913.475 | 0
2021071721 | 7 | 0.73267 | 109900.5 | 0.28726 | 0 | 0.1285 | 1606.25 | 0.00025 | 20 | 64000 | 1606.25 | 20 | 44274.25 | 360.775 | 1310942.225 | 44274.25 | 0
2021071722 | 7 | 0.7036 | 105540 | 0.33181 | 0 | 0.13215 | 1651.875 | 0 | 0 | 64000 | 1651.875 | 0 | 39888.125 | -4386.125 | 1296520.35 | 39888.125 | 0
2021071723 | 7 | 0.6644 | 99660 | 0.38354 | 0 | 0.14886 | 1860.75 | 0 | 0 | 64000 | 1860.75 | 0 | 33799.25 | -6088.875 | 1288187.35 | 33799.25 | 0
2021071724 | 7 | 0.62171 | 93256.5 | 0.49376 | 0 | 0.13579 | 1697.375 | 0 | 0 | 64000 | 1697.375 | 0 | 27559.125 | -6240.125 | 1286094.475 | 27559.125 | 0
2021071801 | 1 | 0.58263 | 87394.5 | 0.56992 | 0 | 0.11625 | 1453.125 | 0 | 0 | 64000 | 1453.125 | 0 | 21941.375 | -5617.75 | 1289619.35 | 21941.375 | 0
2021071802 | 1 | 0.54986 | 82479 | 0.56987 | 0 | 0.11118 | 1389.75 | 0 | 0 | 64000 | 1389.75 | 0 | 17089.25 | -4852.125 | 1297996.35 | 17089.25 | 0
2021071803 | 1 | 0.52813 | 79219.5 | 0.58559 | 0 | 0.11016 | 1377 | 0 | 0 | 64000 | 1377 | 0 | 13842.5 | -3246.75 | 1309620.1 | 13842.5 | 0
2021071804 | 1 | 0.5116 | 76740 | 0.56979 | 0 | 0.10885 | 1360.625 | 0 | 0 | 64000 | 1360.625 | 0 | 11379.375 | -2463.125 | 1323706.975 | 11379.375 | 0
2021071805 | 1 | 0.50428 | 75642 | 0.57294 | 0 | 0.09208 | 1151 | 0 | 0 | 64000 | 1151 | 0 | 10491 | -888.375 | 1338682.225 | 10491 | 0
2021071806 | 1 | 0.50208 | 75312 | 0.58144 | 0 | 0.08519 | 1064.875 | 0.00884 | 707.2 | 64000 | 1064.875 | 707.2 | 9539.925 | -951.075 | 1350000 | 9539.925 | 0
2021071807 | 1 | 0.50086 | 75129 | 0.58275 | 0 | 0.07623 | 952.875 | 0.14374 | 11499.2 | 64000 | 952.875 | 10176.125 | 0 | -9539.925 | 1350000 | 0 | 0
2021071808 | 1 | 0.5163 | 77445 | 0.57332 | 0 | 0.07624 | 953 | 0.41114 | 32891.2 | 64000 | 953 | 12492 | 0 | 0 | 1350000 | 0 | 0
2021071809 | 1 | 0.54883 | 82324.5 | 0.58872 | 0 | 0.08044 | 1005.5 | 0.55265 | 44212 | 64000 | 1005.5 | 17319 | 0 | 0 | 1350000 | 0 | 0
2021071810 | 1 | 0.58689 | 88033.5 | 0.59206 | 0 | 0.08406 | 1050.75 | 0.60009 | 48007.2 | 64000 | 1050.75 | 22982.75 | 0 | 0 | 1350000 | 0 | 0
2021071811 | 1 | 0.6235 | 93525 | 0.53405 | 0 | 0.07439 | 929.875 | 0.63939 | 51151.2 | 64000 | 929.875 | 28595.125 | 0 | 0 | 1350000 | 0 | 0
2021071812 | 1 | 0.65614 | 98421 | 0.57739 | 0 | 0.08922 | 1115.25 | 0.64995 | 51996 | 64000 | 1115.25 | 33305.75 | 0 | 0 | 1350000 | 0 | 0
2021071813 | 1 | 0.68662 | 102993 | 0.64753 | 0 | 0.09163 | 1145.375 | 0.65863 | 52690.4 | 64000 | 1145.375 | 37847.625 | 0 | 0 | 1350000 | 0 | 0
2021071814 | 1 | 0.70845 | 106267.5 | 0.67254 | 0 | 0.07583 | 947.875 | 0.67332 | 53865.6 | 64000 | 947.875 | 41319.625 | 0 | 0 | 1350000 | 0 | 0
2021071815 | 1 | 0.72629 | 108943.5 | 0.71003 | 0 | 0.07582 | 947.75 | 0.68 | 54400 | 64000 | 947.75 | 43995.75 | 0 | 0 | 1350000 | 0 | 0
2021071816 | 1 | 0.73862 | 110793 | 0.69931 | 0 | 0.05245 | 655.625 | 0.67899 | 54319.2 | 64000 | 655.625 | 46137.375 | 0 | 0 | 1350000 | 0 | 0
2021071817 | 1 | 0.75111 | 112666.5 | 0.67671 | 0 | 0.03711 | 463.875 | 0.64616 | 51692.8 | 64000 | 463.875 | 48202.625 | 0 | 0 | 1350000 | 0 | 0
2021071818 | 1 | 0.758 | 113700 | 0.65628 | 0 | 0.06561 | 820.125 | 0.56661 | 45328.8 | 64000 | 820.125 | 45328.8 | 3551.075 | 3551.075 | 1350000 | 3551.075 | 0
2021071819 | 1 | 0.75148 | 112722 | 0.49814 | 0 | 0.14886 | 1860.75 | 0.33387 | 26709.6 | 64000 | 1860.75 | 26709.6 | 20151.65 | 16600.575 | 1350000 | 20151.65 | 0
2021071820 | 1 | 0.72983 | 109474.5 | 0.39489 | 0 | 0.18279 | 2284.875 | 0.06289 | 5031.2 | 64000 | 2284.875 | 5031.2 | 38158.425 | 18006.775 | 1337307.825 | 38158.425 | 0
2021071821 | 1 | 0.70688 | 106032 | 0.40076 | 0 | 0.18148 | 2268.5 | 0.00022 | 17.6 | 64000 | 2268.5 | 17.6 | 39745.9 | 1587.475 | 1323028.175 | 39745.9 | 0
2021071822 | 1 | 0.68703 | 103054.5 | 0.51122 | 0 | 0.20103 | 2512.875 | 0 | 0 | 64000 | 2512.875 | 0 | 36541.625 | -3204.275 | 1311952.8 | 36541.625 | 0
2021071823 | 1 | 0.6476 | 97140 | 0.56259 | 0 | 0.19493 | 2436.625 | 0 | 0 | 64000 | 2436.625 | 0 | 30703.375 | -5838.25 | 1306715.675 | 30703.375 | 0
2021071824 | 1 | 0.60209 | 90313.5 | 0.51022 | 0 | 0.19544 | 2443 | 0 | 0 | 64000 | 2443 | 0 | 23870.5 | -6832.875 | 1308311.425 | 23870.5 | 0
2021071901 | 2 | 0.56134 | 84201 | 0.44107 | 0 | 0.20895 | 2611.875 | 0 | 0 | 64000 | 2611.875 | 0 | 17589.125 | -6281.375 | 1316188.55 | 17589.125 | 0
2021071902 | 2 | 0.53223 | 79834.5 | 0.4147 | 0 | 0.25712 | 3214 | 0 | 0 | 64000 | 3214 | 0 | 12620.5 | -4968.625 | 1329034.3 | 12620.5 | 0
2021071903 | 2 | 0.51405 | 77107.5 | 0.39742 | 0 | 0.35954 | 4494.25 | 0 | 0 | 64000 | 4494.25 | 0 | 8613.25 | -4007.25 | 1345887.3 | 8613.25 | 0
2021071904 | 2 | 0.50487 | 75730.5 | 0.38901 | 0 | 0.38433 | 4804.125 | 0 | 0 | 64000 | 4804.125 | 0 | 6926.375 | -1686.875 | 1350000 | 6926.375 | 0
2021071905 | 2 | 0.50646 | 75969 | 0.41471 | 0 | 0.28764 | 3595.5 | 0 | 0 | 64000 | 3595.5 | 0 | 8373.5 | 1447.125 | 1350000 | 8373.5 | 0
2021071906 | 2 | 0.52447 | 78670.5 | 0.43438 | 0 | 0.27282 | 3410.25 | 0.01352 | 1081.6 | 64000 | 3410.25 | 1081.6 | 10178.65 | 1805.15 | 1350000 | 10178.65 | 0
2021071907 | 2 | 0.55103 | 82654.5 | 0.41531 | 0 | 0.27404 | 3425.5 | 0.13946 | 11156.8 | 64000 | 3425.5 | 11156.8 | 4072.2 | -6106.45 | 1350000 | 4072.2 | 0
2021071908 | 2 | 0.58523 | 87784.5 | 0.40995 | 0 | 0.25211 | 3151.375 | 0.38773 | 31018.4 | 64000 | 3151.375 | 20633.125 | 0 | -4072.2 | 1350000 | 0 | 0
2021071909 | 2 | 0.62008 | 93012 | 0.32237 | 0 | 0.24385 | 3048.125 | 0.51203 | 40962.4 | 64000 | 3048.125 | 25963.875 | 0 | 0 | 1350000 | 0 | 0
2021071910 | 2 | 0.65564 | 98346 | 0.1675 | 0 | 0.24285 | 3035.625 | 0.56497 | 45197.6 | 64000 | 3035.625 | 31310.375 | 0 | 0 | 1350000 | 0 | 0
2021071911 | 2 | 0.69493 | 104239.5 | 0.12527 | 0 | 0.20991 | 2623.875 | 0.57116 | 45692.8 | 64000 | 2623.875 | 37615.625 | 0 | 0 | 1350000 | 0 | 0
2021071912 | 2 | 0.73402 | 110103 | 0.12311 | 0 | 0.19265 | 2408.125 | 0.59456 | 47564.8 | 64000 | 2408.125 | 43694.875 | 0 | 0 | 1350000 | 0 | 0
2021071913 | 2 | 0.76907 | 115360.5 | 0.10753 | 0 | 0.17905 | 2238.125 | 0.6061 | 48488 | 64000 | 2238.125 | 48488 | 634.375 | 634.375 | 1350000 | 634.375 | 0
2021071914 | 2 | 0.80086 | 120129 | 0.10608 | 0 | 0.18284 | 2285.5 | 0.61376 | 49100.8 | 64000 | 2285.5 | 49100.8 | 4742.7 | 4108.325 | 1350000 | 4742.7 | 0
2021071915 | 2 | 0.82551 | 123826.5 | 0.09114 | 0 | 0.1392 | 1740 | 0.60404 | 48323.2 | 64000 | 1740 | 48323.2 | 9763.3 | 5020.6 | 1350000 | 9763.3 | 0
2021071916 | 2 | 0.84426 | 126639 | 0.11158 | 0 | 0.08108 | 1013.5 | 0.6071 | 48568 | 64000 | 1013.5 | 48568 | 13057.5 | 3294.2 | 1350000 | 13057.5 | 0
2021071917 | 2 | 0.85835 | 128752.5 | 0.12008 | 0 | 0.07086 | 885.75 | 0.56946 | 45556.8 | 64000 | 885.75 | 45556.8 | 18309.95 | 5252.45 | 1350000 | 18309.95 | 0
2021071918 | 2 | 0.86415 | 129622.5 | 0.11789 | 0 | 0.07747 | 968.375 | 0.45423 | 36338.4 | 64000 | 968.375 | 36338.4 | 28315.725 | 10005.775 | 1347150.525 | 28315.725 | 0
2021071919 | 2 | 0.85058 | 127587 | 0.20105 | 0 | 0.10397 | 1299.625 | 0.26717 | 21373.6 | 64000 | 1299.625 | 21373.6 | 40913.775 | 12598.05 | 1331703 | 40913.775 | 0
2021071920 | 2 | 0.81977 | 122965.5 | 0.15256 | 0 | 0.1032 | 1290 | 0.0539 | 4312 | 64000 | 1290 | 4312 | 53363.5 | 12449.725 | 1303805.75 | 53363.5 | 0
2021071921 | 2 | 0.78559 | 117838.5 | 0.16084 | 0 | 0.10009 | 1251.125 | 0 | 0 | 64000 | 1251.125 | 0 | 52587.375 | -776.125 | 1276684.625 | 52587.375 | 0
2021071922 | 2 | 0.75429 | 113143.5 | 0.16727 | 0 | 0.10028 | 1253.5 | 0 | 0 | 64000 | 1253.5 | 0 | 47890 | -4697.375 | 1254260.875 | 47890 | 0
2021071923 | 2 | 0.70276 | 105414 | 0.22004 | 0 | 0.10755 | 1344.375 | 0 | 0 | 64000 | 1344.375 | 0 | 40069.625 | -7820.375 | 1239657.5 | 40069.625 | 0
2021071924 | 2 | 0.64417 | 96625.5 | 0.25148 | 0 | 0.12539 | 1567.375 | 0 | 0 | 64000 | 1567.375 | 0 | 31058.125 | -9011.5 | 1234065.625 | 31058.125 | 0
2021072001 | 3 | 0.59534 | 89301 | 0.22897 | 0 | 0.14187 | 1773.375 | 0 | 0 | 64000 | 1773.375 | 0 | 23527.625 | -7530.5 | 1236004.25 | 23527.625 | 0
2021072002 | 3 | 0.56096 | 84144 | 0.17017 | 0 | 0.14839 | 1854.875 | 0 | 0 | 64000 | 1854.875 | 0 | 18289.125 | -5238.5 | 1243181.375 | 18289.125 | 0
2021072003 | 3 | 0.53706 | 80559 | 0.16279 | 0 | 0.15882 | 1985.25 | 0 | 0 | 64000 | 1985.25 | 0 | 14573.75 | -3715.375 | 1254073.875 | 14573.75 | 0
2021072004 | 3 | 0.52192 | 78288 | 0.15963 | 0 | 0.18167 | 2270.875 | 0 | 0 | 64000 | 2270.875 | 0 | 12017.125 | -2556.625 | 1267523 | 12017.125 | 0
2021072005 | 3 | 0.5205 | 78075 | 0.15739 | 0 | 0.21512 | 2689 | 0 | 0 | 64000 | 2689 | 0 | 11386 | -631.125 | 1281603.25 | 11386 | 0
2021072006 | 3 | 0.53553 | 80329.5 | 0.14309 | 0 | 0.30666 | 3833.25 | 0.00568 | 454.4 | 64000 | 3833.25 | 454.4 | 12041.85 | 655.85 | 1295027.65 | 12041.85 | 0
2021072007 | 3 | 0.56168 | 84252 | 0.14086 | 0 | 0.36412 | 4551.5 | 0.11481 | 9184.8 | 64000 | 4551.5 | 9184.8 | 6515.7 | -5526.15 | 1313978.2 | 6515.7 | 0
2021072008 | 3 | 0.59624 | 89436 | 0.10725 | 0 | 0.35648 | 4456 | 0.31319 | 25055.2 | 64000 | 4456 | 20980 | 0 | -6515.7 | 1339444.45 | 0 | 0
2021072009 | 3 | 0.63534 | 95301 | 0.05208 | 0 | 0.2952 | 3690 | 0.48094 | 38475.2 | 64000 | 3690 | 27611 | 0 | 0 | 1350000 | 0 | 0
2021072010 | 3 | 0.67448 | 101172 | 0.00795 | 0 | 0.28384 | 3548 | 0.54831 | 43864.8 | 64000 | 3548 | 33624 | 0 | 0 | 1350000 | 0 | 0
2021072011 | 3 | 0.72237 | 108355.5 | 0.00526 | 0 | 0.2836 | 3545 | 0.57127 | 45701.6 | 64000 | 3545 | 40810.5 | 0 | 0 | 1350000 | 0 | 0
2021072012 | 3 | 0.76998 | 115497 | 0.00433 | 0 | 0.33784 | 4223 | 0.57628 | 46102.4 | 64000 | 4223 | 46102.4 | 1171.6 | 1171.6 | 1350000 | 1171.6 | 0
2021072013 | 3 | 0.81488 | 122232 | 0.00399 | 0 | 0.38399 | 4799.875 | 0.59041 | 47232.8 | 64000 | 4799.875 | 47232.8 | 6199.325 | 5027.725 | 1350000 | 6199.325 | 0
2021072014 | 3 | 0.8511 | 127665 | 0.00341 | 0 | 0.38446 | 4805.75 | 0.62016 | 49612.8 | 64000 | 4805.75 | 49612.8 | 9246.45 | 3047.125 | 1350000 | 9246.45 | 0
2021072015 | 3 | 0.87791 | 131686.5 | 0.00086 | 0 | 0.37982 | 4747.75 | 0.62397 | 49917.6 | 64000 | 4747.75 | 49917.6 | 13021.15 | 3774.7 | 1350000 | 13021.15 | 0
2021072016 | 3 | 0.89714 | 134571 | 0.0141 | 0 | 0.38684 | 4835.5 | 0.58261 | 46608.8 | 64000 | 4835.5 | 46608.8 | 19126.7 | 6105.55 | 1350000 | 19126.7 | 0
2021072017 | 3 | 0.91173 | 136759.5 | 0.03906 | 0 | 0.36114 | 4514.25 | 0.49887 | 39909.6 | 64000 | 4514.25 | 39909.6 | 28335.65 | 9208.95 | 1347130.6 | 28335.65 | 0
2021072018 | 3 | 0.91305 | 136957.5 | 0.08551 | 0 | 0.38011 | 4751.375 | 0.38949 | 31159.2 | 64000 | 4751.375 | 31159.2 | 37046.925 | 8711.275 | 1335549.925 | 37046.925 | 0
2021072019 | 3 | 0.89458 | 134187 | 0.11926 | 0 | 0.44459 | 5557.375 | 0.21728 | 17382.4 | 64000 | 5557.375 | 17382.4 | 47247.225 | 10200.3 | 1313768.95 | 47247.225 | 0
2021072020 | 3 | 0.85949 | 128923.5 | 0.15833 | 0 | 0.46212 | 5776.5 | 0.04842 | 3873.6 | 64000 | 5776.5 | 3873.6 | 55273.4 | 8026.175 | 1283961.8 | 55273.4 | 0
2021072021 | 3 | 0.82258 | 123387 | 0.30725 | 0 | 0.46971 | 5871.375 | 0 | 0 | 64000 | 5871.375 | 0 | 53515.625 | -1757.775 | 1255912.425 | 53515.625 | 0
2021072022 | 3 | 0.79 | 118500 | 0.49694 | 0 | 0.44397 | 5549.625 | 0 | 0 | 64000 | 5549.625 | 0 | 48950.375 | -4565.25 | 1232428.3 | 48950.375 | 0
2021072023 | 3 | 0.73405 | 110107.5 | 0.48897 | 0 | 0.35712 | 4464 | 0 | 0 | 64000 | 4464 | 0 | 41643.5 | -7306.875 | 1216251.05 | 41643.5 | 0
2021072024 | 3 | 0.67538 | 101307 | 0.48982 | 0 | 0.26281 | 3285.125 | 0 | 0 | 64000 | 3285.125 | 0 | 34021.875 | -7621.625 | 1207695.425 | 34021.875 | 0
2021072101 | 4 | 0.62472 | 93708 | 0.36888 | 0 | 0.16311 | 2038.875 | 0 | 0 | 64000 | 2038.875 | 0 | 27669.125 | -6352.75 | 1205492.55 | 27669.125 | 0
2021072102 | 4 | 0.58747 | 88120.5 | 0.29841 | 0 | 0.09882 | 1235.25 | 0 | 0 | 64000 | 1235.25 | 0 | 22885.25 | -4783.875 | 1208073.55 | 22885.25 | 0
2021072103 | 4 | 0.5613 | 84195 | 0.23284 | 0 | 0.08451 | 1056.375 | 0 | 0 | 64000 | 1056.375 | 0 | 19138.625 | -3746.625 | 1214401.175 | 19138.625 | 0
2021072104 | 4 | 0.54502 | 81753 | 0.1861 | 0 | 0.11055 | 1381.875 | 0 | 0 | 64000 | 1381.875 | 0 | 16371.125 | -2767.5 | 1223496.3 | 16371.125 | 0
2021072105 | 4 | 0.54126 | 81189 | 0.12564 | 0 | 0.11609 | 1451.125 | 0 | 0 | 64000 | 1451.125 | 0 | 15737.875 | -633.25 | 1233224.675 | 15737.875 | 0
2021072106 | 4 | 0.55538 | 83307 | 0.12685 | 0 | 0.11844 | 1480.5 | 0.00679 | 543.2 | 64000 | 1480.5 | 543.2 | 17283.3 | 1545.425 | 1241407.625 | 17283.3 | 0
2021072107 | 4 | 0.58166 | 87249 | 0.1695 | 0 | 0.1572 | 1965 | 0.10555 | 8444 | 64000 | 1965 | 8444 | 12840 | -4443.3 | 1254033.875 | 12840 | 0
2021072108 | 4 | 0.61491 | 92236.5 | 0.18373 | 0 | 0.18369 | 2296.125 | 0.30124 | 24099.2 | 64000 | 2296.125 | 24099.2 | 1841.175 | -10998.825 | 1277658.95 | 1841.175 | 0
2021072109 | 4 | 0.6498 | 97470 | 0.18918 | 0 | 0.19212 | 2401.5 | 0.43605 | 34884 | 64000 | 2401.5 | 31068.5 | 0 | -1841.175 | 1303125.2 | 0 | 0
2021072110 | 4 | 0.68332 | 102498 | 0.23453 | 0 | 0.16588 | 2073.5 | 0.49443 | 39554.4 | 64000 | 2073.5 | 36424.5 | 0 | 0 | 1328591.45 | 0 | 0
2021072111 | 4 | 0.71815 | 107722.5 | 0.25131 | 0 | 0.13085 | 1635.625 | 0.53718 | 42974.4 | 64000 | 1635.625 | 42086.875 | 0 | 0 | 1350000 | 0 | 0
2021072112 | 4 | 0.7517 | 112755 | 0.25682 | 0 | 0.12175 | 1521.875 | 0.59076 | 47260.8 | 64000 | 1521.875 | 47233.125 | 0 | 0 | 1350000 | 0 | 0
2021072113 | 4 | 0.78145 | 117217.5 | 0.26468 | 0 | 0.13609 | 1701.125 | 0.59302 | 47441.6 | 64000 | 1701.125 | 47441.6 | 4074.775 | 4074.775 | 1350000 | 4074.775 | 0
2021072114 | 4 | 0.8024 | 120360 | 0.40674 | 0 | 0.14787 | 1848.375 | 0.61065 | 48852 | 64000 | 1848.375 | 48852 | 5659.625 | 1584.85 | 1350000 | 5659.625 | 0
2021072115 | 4 | 0.81596 | 122394 | 0.53749 | 0 | 0.10319 | 1289.875 | 0.61667 | 49333.6 | 64000 | 1289.875 | 49333.6 | 7770.525 | 2110.9 | 1350000 | 7770.525 | 0
2021072116 | 4 | 0.81747 | 122620.5 | 0.62496 | 0 | 0.08743 | 1092.875 | 0.58852 | 47081.6 | 64000 | 1092.875 | 47081.6 | 10446.025 | 2675.5 | 1350000 | 10446.025 | 0
2021072117 | 4 | 0.81604 | 122406 | 0.68426 | 0 | 0.10221 | 1277.625 | 0.54943 | 43954.4 | 64000 | 1277.625 | 43954.4 | 13173.975 | 2727.95 | 1350000 | 13173.975 | 0
2021072118 | 4 | 0.81612 | 122418 | 0.65231 | 0 | 0.14511 | 1813.875 | 0.41492 | 33193.6 | 64000 | 1813.875 | 33193.6 | 23410.525 | 10236.55 | 1350000 | 23410.525 | 0
2021072119 | 4 | 0.80147 | 120220.5 | 0.58791 | 0 | 0.16758 | 2094.75 | 0.23389 | 18711.2 | 64000 | 2094.75 | 18711.2 | 35414.55 | 12004.025 | 1340051.7 | 35414.55 | 0
2021072120 | 4 | 0.76982 | 115473 | 0.51569 | 0 | 0.15243 | 1905.375 | 0.05181 | 4144.8 | 64000 | 1905.375 | 4144.8 | 45422.825 | 10008.275 | 1320095.125 | 45422.825 | 0
2021072121 | 4 | 0.73884 | 110826 | 0.39093 | 0 | 0.16599 | 2074.875 | 5e-05 | 4 | 64000 | 2074.875 | 4 | 44747.125 | -675.7 | 1300814.25 | 44747.125 | 0
2021072122 | 4 | 0.71078 | 106617 | 0.42752 | 0 | 0.21993 | 2749.125 | 0 | 0 | 64000 | 2749.125 | 0 | 39867.875 | -4879.25 | 1286412.625 | 39867.875 | 0
2021072123 | 4 | 0.66225 | 99337.5 | 0.4293 | 0 | 0.26867 | 3358.375 | 0 | 0 | 64000 | 3358.375 | 0 | 31979.125 | -7888.75 | 1279899.75 | 31979.125 | 0
2021072124 | 4 | 0.6088 | 91320 | 0.36277 | 0 | 0.25997 | 3249.625 | 0 | 0 | 64000 | 3249.625 | 0 | 24070.375 | -7908.75 | 1281295.625 | 24070.375 | 0
2021072201 | 5 | 0.56398 | 84597 | 0.31324 | 0 | 0.22279 | 2784.875 | 0 | 0 | 64000 | 2784.875 | 0 | 17812.125 | -6258.25 | 1288949.75 | 17812.125 | 0
2021072202 | 5 | 0.53091 | 79636.5 | 0.30942 | 0 | 0.14265 | 1783.125 | 0 | 0 | 64000 | 1783.125 | 0 | 13853.375 | -3958.75 | 1300562.625 | 13853.375 | 0
2021072203 | 5 | 0.50804 | 76206 | 0.32147 | 0 | 0.10532 | 1316.5 | 0 | 0 | 64000 | 1316.5 | 0 | 10889.5 | -2963.875 | 1315139.375 | 10889.5 | 0
2021072204 | 5 | 0.49416 | 74124 | 0.27937 | 0 | 0.10051 | 1256.375 | 0 | 0 | 64000 | 1256.375 | 0 | 8867.625 | -2021.875 | 1331738 | 8867.625 | 0
2021072205 | 5 | 0.49358 | 74037 | 0.2622 | 0 | 0.0975 | 1218.75 | 0 | 0 | 64000 | 1218.75 | 0 | 8818.25 | -49.375 | 1348386 | 8818.25 | 0
2021072206 | 5 | 0.50648 | 75972 | 0.25771 | 0 | 0.11443 | 1430.375 | 0.00424 | 339.2 | 64000 | 1430.375 | 339.2 | 10202.425 | 1384.175 | 1350000 | 10202.425 | 0
2021072207 | 5 | 0.53045 | 79567.5 | 0.26315 | 0 | 0.14571 | 1821.375 | 0.05525 | 4420 | 64000 | 1821.375 | 4420 | 9326.125 | -876.3 | 1350000 | 9326.125 | 0
2021072208 | 5 | 0.5622 | 84330 | 0.23314 | 0 | 0.11801 | 1475.125 | 0.13137 | 10509.6 | 64000 | 1475.125 | 10509.6 | 8345.275 | -980.85 | 1350000 | 8345.275 | 0
2021072209 | 5 | 0.59325 | 88987.5 | 0.13698 | 0 | 0.12374 | 1546.75 | 0.1886 | 15088 | 64000 | 1546.75 | 15088 | 8352.75 | 7.475 | 1350000 | 8352.75 | 0
2021072210 | 5 | 0.6212 | 93180 | 0.06154 | 0 | 0.07858 | 982.25 | 0.25418 | 20334.4 | 64000 | 982.25 | 20334.4 | 7863.35 | -489.4 | 1350000 | 7863.35 | 0
2021072211 | 5 | 0.65165 | 97747.5 | 0.03781 | 0 | 0.05591 | 698.875 | 0.27973 | 22378.4 | 64000 | 698.875 | 22378.4 | 10670.225 | 2806.875 | 1350000 | 10670.225 | 0
2021072212 | 5 | 0.67936 | 101904 | 0.06376 | 0 | 0.03786 | 473.25 | 0.31666 | 25332.8 | 64000 | 473.25 | 25332.8 | 12097.95 | 1427.725 | 1350000 | 12097.95 | 0
2021072213 | 5 | 0.70848 | 106272 | 0.08266 | 0 | 0.02566 | 320.75 | 0.28246 | 22596.8 | 64000 | 320.75 | 22596.8 | 19354.45 | 7256.5 | 1350000 | 19354.45 | 0
2021072214 | 5 | 0.73657 | 110485.5 | 0.09219 | 0 | 0.0197 | 246.25 | 0.29252 | 23401.6 | 64000 | 246.25 | 23401.6 | 22837.65 | 3483.2 | 1350000 | 22837.65 | 0
2021072215 | 5 | 0.75998 | 113997 | 0.14034 | 0 | 0.01493 | 186.625 | 0.27215 | 21772 | 64000 | 186.625 | 21772 | 28038.375 | 5200.725 | 1347427.875 | 28038.375 | 0
2021072216 | 5 | 0.77902 | 116853 | 0.16443 | 0 | 0.01261 | 157.625 | 0.26277 | 21021.6 | 64000 | 157.625 | 21021.6 | 31673.775 | 3635.4 | 1341220.35 | 31673.775 | 0
2021072217 | 5 | 0.79228 | 118842 | 0.21035 | 0 | 0.01083 | 135.375 | 0.1949 | 15592 | 64000 | 135.375 | 15592 | 39114.625 | 7440.85 | 1327571.975 | 39114.625 | 0
2021072218 | 5 | 0.79655 | 119482.5 | 0.19149 | 0 | 0.00753 | 94.125 | 0.12358 | 9886.4 | 64000 | 94.125 | 9886.4 | 45501.975 | 6387.35 | 1307536.25 | 45501.975 | 0
2021072219 | 5 | 0.78538 | 117807 | 0.15717 | 0 | 0.00423 | 52.875 | 0.06038 | 4830.4 | 64000 | 52.875 | 4830.4 | 48923.725 | 3421.75 | 1284078.775 | 48923.725 | 0
2021072220 | 5 | 0.75742 | 113613 | 0.12609 | 0 | 0.00371 | 46.375 | 0.01084 | 867.2 | 64000 | 46.375 | 867.2 | 48699.425 | -224.3 | 1260845.6 | 48699.425 | 0
2021072221 | 5 | 0.72538 | 108807 | 0.12503 | 0 | 0.00405 | 50.625 | 0 | 0 | 64000 | 50.625 | 0 | 44756.375 | -3943.05 | 1241555.475 | 44756.375 | 0
2021072222 | 5 | 0.70073 | 105109.5 | 0.1265 | 0 | 0.00789 | 98.625 | 0 | 0 | 64000 | 98.625 | 0 | 41010.875 | -3745.5 | 1226010.85 | 41010.875 | 0
2021072223 | 5 | 0.6562 | 98430 | 0.13345 | 0 | 0.01267 | 158.375 | 0 | 0 | 64000 | 158.375 | 0 | 34271.625 | -6739.25 | 1217205.475 | 34271.625 | 0
2021072224 | 5 | 0.6048 | 90720 | 0.12248 | 0 | 0.007 | 87.5 | 0 | 0 | 64000 | 87.5 | 0 | 26632.5 | -7639.125 | 1216039.225 | 26632.5 | 0
2021072301 | 6 | 0.56074 | 84111 | 0.09916 | 0 | 0.02074 | 259.25 | 0 | 0 | 64000 | 259.25 | 0 | 19851.75 | -6780.75 | 1221653.725 | 19851.75 | 0
2021072302 | 6 | 0.52903 | 79354.5 | 0.0879 | 0 | 0.03476 | 434.5 | 0 | 0 | 64000 | 434.5 | 0 | 14920 | -4931.75 | 1232199.975 | 14920 | 0
2021072303 | 6 | 0.50885 | 76327.5 | 0.08906 | 0 | 0.05319 | 664.875 | 0 | 0 | 64000 | 664.875 | 0 | 11662.625 | -3257.375 | 1246003.6 | 11662.625 | 0
2021072304 | 6 | 0.49783 | 74674.5 | 0.13596 | 0 | 0.03677 | 459.625 | 0 | 0 | 64000 | 459.625 | 0 | 10214.875 | -1447.75 | 1261254.975 | 10214.875 | 0
2021072305 | 6 | 0.49652 | 74478 | 0.18318 | 0 | 0.06151 | 768.875 | 0 | 0 | 64000 | 768.875 | 0 | 9709.125 | -505.75 | 1277012.1 | 9709.125 | 0
2021072306 | 6 | 0.51034 | 76551 | 0.20327 | 0 | 0.07773 | 971.625 | 0.00252 | 201.6 | 64000 | 971.625 | 201.6 | 11377.775 | 1668.65 | 1291100.575 | 11377.775 | 0
2021072307 | 6 | 0.53473 | 80209.5 | 0.20383 | 0 | 0.15367 | 1920.875 | 0.03434 | 2747.2 | 64000 | 1920.875 | 2747.2 | 11541.425 | 163.65 | 1305025.4 | 11541.425 | 0
2021072308 | 6 | 0.5651 | 84765 | 0.13312 | 0 | 0.11454 | 1431.75 | 0.09889 | 7911.2 | 64000 | 1431.75 | 7911.2 | 11422.05 | -119.375 | 1319069.6 | 11422.05 | 0
2021072309 | 6 | 0.59773 | 89659.5 | 0.0531 | 0 | 0.123 | 1537.5 | 0.16472 | 13177.6 | 64000 | 1537.5 | 13177.6 | 10944.4 | -477.65 | 1333591.45 | 10944.4 | 0
2021072310 | 6 | 0.62748 | 94122 | 0.00659 | 0 | 0.0805 | 1006.25 | 0.27002 | 21601.6 | 64000 | 1006.25 | 21601.6 | 7514.15 | -3430.25 | 1350000 | 7514.15 | 0
2021072311 | 6 | 0.66454 | 99681 | 0.01126 | 0 | 0.08679 | 1084.875 | 0.32732 | 26185.6 | 64000 | 1084.875 | 26185.6 | 8410.525 | 896.375 | 1350000 | 8410.525 | 0
2021072312 | 6 | 0.69852 | 104778 | 0.03578 | 0 | 0.06121 | 765.125 | 0.35816 | 28652.8 | 64000 | 765.125 | 28652.8 | 11360.075 | 2949.55 | 1350000 | 11360.075 | 0
2021072313 | 6 | 0.72981 | 109471.5 | 0.02643 | 0 | 0.04082 | 510.25 | 0.3265 | 26120 | 64000 | 510.25 | 26120 | 18841.25 | 7481.175 | 1350000 | 18841.25 | 0
2021072314 | 6 | 0.75753 | 113629.5 | 0.02074 | 0 | 0.02662 | 332.75 | 0.3109 | 24872 | 64000 | 332.75 | 24872 | 24424.75 | 5583.5 | 1350000 | 24424.75 | 0
2021072315 | 6 | 0.78029 | 117043.5 | 0.01738 | 0 | 0.0244 | 305 | 0.25759 | 20607.2 | 64000 | 305 | 20607.2 | 32131.3 | 7706.55 | 1343334.95 | 32131.3 | 0
2021072316 | 6 | 0.7968 | 119520 | 0.01556 | 0 | 0.02322 | 290.25 | 0.19874 | 15899.2 | 64000 | 290.25 | 15899.2 | 39330.55 | 7199.25 | 1329470.65 | 39330.55 | 0
2021072317 | 6 | 0.81081 | 121621.5 | 0.01309 | 0 | 0.0277 | 346.25 | 0.16912 | 13529.6 | 64000 | 346.25 | 13529.6 | 43745.65 | 4415.1 | 1311191.25 | 43745.65 | 0
2021072318 | 6 | 0.81391 | 122086.5 | 0.00963 | 0 | 0.03525 | 440.625 | 0.09738 | 7790.4 | 64000 | 440.625 | 7790.4 | 49855.475 | 6109.825 | 1286802.025 | 49855.475 | 0
2021072319 | 6 | 0.79943 | 119914.5 | 0.00351 | 0 | 0.04156 | 519.5 | 0.06207 | 4965.6 | 64000 | 519.5 | 4965.6 | 50429.4 | 573.925 | 1261838.875 | 50429.4 | 0
2021072320 | 6 | 0.77129 | 115693.5 | 0.00086 | 0 | 0.04381 | 547.625 | 0.0123 | 984 | 64000 | 547.625 | 984 | 50161.875 | -267.525 | 1237143.25 | 50161.875 | 0
2021072321 | 6 | 0.7366 | 110490 | 0.01154 | 0 | 0.0396 | 495 | 0 | 0 | 64000 | 495 | 0 | 45995 | -4166.875 | 1216614.5 | 45995 | 0
2021072322 | 6 | 0.70982 | 106473 | 0.0266 | 0 | 0.04496 | 562 | 0 | 0 | 64000 | 562 | 0 | 41911 | -4084 | 1200169.75 | 41911 | 0
2021072323 | 6 | 0.665 | 99750 | 0.04377 | 0 | 0.05716 | 714.5 | 0 | 0 | 64000 | 714.5 | 0 | 35035.5 | -6875.5 | 1190600.5 | 35035.5 | 0
2021072324 | 6 | 0.61474 | 92211 | 0.05901 | 0 | 0.07091 | 886.375 | 0 | 0 | 64000 | 886.375 | 0 | 27324.625 | -7710.875 | 1188742.125 | 27324.625 | 0
2021072401 | 7 | 0.57183 | 85774.5 | 0.06506 | 0 | 0.09259 | 1157.375 | 0 | 0 | 64000 | 1157.375 | 0 | 20617.125 | -6707.5 | 1193591.25 | 20617.125 | 0
2021072402 | 7 | 0.53903 | 80854.5 | 0.07825 | 0 | 0.10504 | 1313 | 0 | 0 | 64000 | 1313 | 0 | 15541.5 | -5075.625 | 1203516 | 15541.5 | 0
2021072403 | 7 | 0.51555 | 77332.5 | 0.09506 | 0 | 0.09369 | 1171.125 | 0 | 0 | 64000 | 1171.125 | 0 | 12161.375 | -3380.125 | 1216820.875 | 12161.375 | 0
2021072404 | 7 | 0.49979 | 74968.5 | 0.1039 | 0 | 0.09339 | 1167.375 | 0 | 0 | 64000 | 1167.375 | 0 | 9801.125 | -2360.25 | 1232486 | 9801.125 | 0
2021072405 | 7 | 0.49189 | 73783.5 | 0.11459 | 0 | 0.08318 | 1039.75 | 0 | 0 | 64000 | 1039.75 | 0 | 8743.75 | -1057.375 | 1249208.5 | 8743.75 | 0
2021072406 | 7 | 0.49262 | 73893 | 0.10576 | 0 | 0.07924 | 990.5 | 0.00325 | 260 | 64000 | 990.5 | 260 | 8642.5 | -101.25 | 1266032.25 | 8642.5 | 0
2021072407 | 7 | 0.49735 | 74602.5 | 0.11159 | 0 | 0.06377 | 797.125 | 0.04155 | 3324 | 64000 | 797.125 | 3324 | 6481.375 | -2161.125 | 1285017.125 | 6481.375 | 0
2021072408 | 7 | 0.51529 | 77293.5 | 0.11141 | 0 | 0.05007 | 625.875 | 0.13301 | 10640.8 | 64000 | 625.875 | 10640.8 | 2026.825 | -4454.55 | 1308456.55 | 2026.825 | 0
2021072409 | 7 | 0.55277 | 82915.5 | 0.08296 | 0 | 0.06933 | 866.625 | 0.19114 | 15291.2 | 64000 | 866.625 | 15291.2 | 2757.675 | 730.85 | 1331165.125 | 2757.675 | 0
2021072410 | 7 | 0.59771 | 89656.5 | 0.0397 | 0 | 0.04612 | 576.5 | 0.2809 | 22472 | 64000 | 576.5 | 22472 | 2608 | -149.675 | 1350000 | 2608 | 0
2021072411 | 7 | 0.6431 | 96465 | 0.02554 | 0 | 0.02464 | 308 | 0.45455 | 36364 | 64000 | 308 | 32157 | 0 | -2608 | 1350000 | 0 | 0
2021072412 | 7 | 0.68495 | 102742.5 | 0.05921 | 0 | 0.01635 | 204.375 | 0.49804 | 39843.2 | 64000 | 204.375 | 38538.125 | 0 | 0 | 1350000 | 0 | 0
2021072413 | 7 | 0.72473 | 108709.5 | 0.10055 | 0 | 0.01201 | 150.125 | 0.47246 | 37796.8 | 64000 | 150.125 | 37796.8 | 6762.575 | 6762.575 | 1350000 | 6762.575 | 0
2021072414 | 7 | 0.7542 | 113130 | 0.13604 | 0 | 0.01059 | 132.375 | 0.46185 | 36948 | 64000 | 132.375 | 36948 | 12049.625 | 5287.05 | 1350000 | 12049.625 | 0
2021072415 | 7 | 0.77809 | 116713.5 | 0.15327 | 0 | 0.01335 | 166.875 | 0.42871 | 34296.8 | 64000 | 166.875 | 34296.8 | 18249.825 | 6200.2 | 1350000 | 18249.825 | 0
2021072416 | 7 | 0.79656 | 119484 | 0.17617 | 0 | 0.01177 | 147.125 | 0.43176 | 34540.8 | 64000 | 147.125 | 34540.8 | 20796.075 | 2546.25 | 1350000 | 20796.075 | 0
2021072417 | 7 | 0.80744 | 121116 | 0.23006 | 0 | 0.00944 | 118 | 0.35038 | 28030.4 | 64000 | 118 | 28030.4 | 28967.6 | 8171.525 | 1346498.65 | 28967.6 | 0
2021072418 | 7 | 0.80717 | 121075.5 | 0.22437 | 0 | 0.00947 | 118.375 | 0.27322 | 21857.6 | 64000 | 118.375 | 21857.6 | 35099.525 | 6131.925 | 1336865.375 | 35099.525 | 0
2021072419 | 7 | 0.78925 | 118387.5 | 0.27573 | 0 | 0.01771 | 221.375 | 0.16344 | 13075.2 | 64000 | 221.375 | 13075.2 | 41090.925 | 5991.4 | 1321240.7 | 41090.925 | 0
2021072420 | 7 | 0.76495 | 114742.5 | 0.39658 | 0 | 0.02609 | 326.125 | 0.03997 | 3197.6 | 64000 | 326.125 | 3197.6 | 47218.775 | 6127.85 | 1299488.175 | 47218.775 | 0
2021072421 | 7 | 0.7408 | 111120 | 0.49731 | 0 | 0.02946 | 368.25 | 0 | 0 | 64000 | 368.25 | 0 | 46751.75 | -467.025 | 1278202.675 | 46751.75 | 0
2021072422 | 7 | 0.72118 | 108177 | 0.60851 | 0 | 0.04108 | 513.5 | 0 | 0 | 64000 | 513.5 | 0 | 43663.5 | -3088.25 | 1260005.425 | 43663.5 | 0
2021072423 | 7 | 0.6846 | 102690 | 0.67174 | 0 | 0.05077 | 634.625 | 0 | 0 | 64000 | 634.625 | 0 | 38055.375 | -5608.125 | 1247416.3 | 38055.375 | 0
2021072424 | 7 | 0.64074 | 96111 | 0.69433 | 0 | 0.06731 | 841.375 | 0 | 0 | 64000 | 841.375 | 0 | 31269.625 | -6785.75 | 1241612.925 | 31269.625 | 0
2021072501 | 1 | 0.59974 | 89961 | 0.69137 | 0 | 0.08407 | 1050.875 | 0 | 0 | 64000 | 1050.875 | 0 | 24910.125 | -6359.5 | 1242169.05 | 24910.125 | 0
2021072502 | 1 | 0.56772 | 85158 | 0.70793 | 0 | 0.07699 | 962.375 | 0 | 0 | 64000 | 962.375 | 0 | 20195.625 | -4714.5 | 1247439.675 | 20195.625 | 0
2021072503 | 1 | 0.54314 | 81471 | 0.72833 | 0 | 0.06474 | 809.25 | 0 | 0 | 64000 | 809.25 | 0 | 16661.75 | -3533.875 | 1256244.175 | 16661.75 | 0
2021072504 | 1 | 0.52656 | 78984 | 0.68333 | 0 | 0.05834 | 729.25 | 0 | 0 | 64000 | 729.25 | 0 | 14254.75 | -2407 | 1267455.675 | 14254.75 | 0
2021072505 | 1 | 0.51618 | 77427 | 0.63155 | 0 | 0.05613 | 701.625 | 0 | 0 | 64000 | 701.625 | 0 | 12725.375 | -1529.375 | 1280196.55 | 12725.375 | 0
2021072506 | 1 | 0.51388 | 77082 | 0.67973 | 0 | 0.06032 | 754 | 0.00159 | 127.2 | 64000 | 754 | 127.2 | 12200.8 | -524.575 | 1293462 | 12200.8 | 0
2021072507 | 1 | 0.51353 | 77029.5 | 0.63802 | 0 | 0.06066 | 758.25 | 0.03407 | 2725.6 | 64000 | 758.25 | 2725.6 | 9545.65 | -2655.15 | 1309382.6 | 9545.65 | 0
2021072508 | 1 | 0.52801 | 79201.5 | 0.60466 | 0 | 0.06733 | 841.625 | 0.07422 | 5937.6 | 64000 | 841.625 | 5937.6 | 8422.275 | -1123.375 | 1326426.575 | 8422.275 | 0
2021072509 | 1 | 0.56137 | 84205.5 | 0.5443 | 0 | 0.07393 | 924.125 | 0.13602 | 10881.6 | 64000 | 924.125 | 10881.6 | 8399.775 | -22.5 | 1343493.05 | 8399.775 | 0
2021072510 | 1 | 0.60647 | 90970.5 | 0.40283 | 0 | 0.10352 | 1294 | 0.2519 | 20152 | 64000 | 1294 | 20152 | 5524.5 | -2875.275 | 1350000 | 5524.5 | 0
2021072511 | 1 | 0.65294 | 97941 | 0.28627 | 0 | 0.08873 | 1109.125 | 0.37516 | 30012.8 | 64000 | 1109.125 | 30012.8 | 2819.075 | -2705.425 | 1350000 | 2819.075 | 0
2021072512 | 1 | 0.70197 | 105295.5 | 0.23484 | 0 | 0.05812 | 726.5 | 0.4327 | 34616 | 64000 | 726.5 | 34616 | 5953 | 3133.925 | 1350000 | 5953 | 0
2021072513 | 1 | 0.74682 | 112023 | 0.22208 | 0 | 0.04833 | 604.125 | 0.50326 | 40260.8 | 64000 | 604.125 | 40260.8 | 7158.075 | 1205.075 | 1350000 | 7158.075 | 0
2021072514 | 1 | 0.78296 | 117444 | 0.16868 | 0 | 0.04459 | 557.375 | 0.52841 | 42272.8 | 64000 | 557.375 | 42272.8 | 10613.825 | 3455.75 | 1350000 | 10613.825 | 0
2021072515 | 1 | 0.81398 | 122097 | 0.13836 | 0 | 0.02938 | 367.25 | 0.53806 | 43044.8 | 64000 | 367.25 | 43044.8 | 14684.95 | 4071.125 | 1350000 | 14684.95 | 0
2021072516 | 1 | 0.83812 | 125718 | 0.12541 | 0 | 0.02151 | 268.875 | 0.51122 | 40897.6 | 64000 | 268.875 | 40897.6 | 20551.525 | 5866.575 | 1350000 | 20551.525 | 0
2021072517 | 1 | 0.85859 | 128788.5 | 0.1388 | 0 | 0.01955 | 244.375 | 0.46634 | 37307.2 | 64000 | 244.375 | 37307.2 | 27236.925 | 6685.4 | 1348229.325 | 27236.925 | 0
2021072518 | 1 | 0.86791 | 130186.5 | 0.18184 | 0 | 0.0291 | 363.75 | 0.3564 | 28512 | 64000 | 363.75 | 28512 | 37310.75 | 10073.825 | 1336384.825 | 37310.75 | 0
2021072519 | 1 | 0.86309 | 129463.5 | 0.16647 | 0 | 0.06244 | 780.5 | 0.19429 | 15543.2 | 64000 | 780.5 | 15543.2 | 49139.8 | 11829.05 | 1312711.275 | 49139.8 | 0
2021072520 | 1 | 0.84128 | 126192 | 0.14157 | 0 | 0.07682 | 960.25 | 0.04071 | 3256.8 | 64000 | 960.25 | 3256.8 | 57974.95 | 8835.15 | 1280202.575 | 57974.95 | 0
2021072521 | 1 | 0.81396 | 122094 | 0.15116 | 0 | 0.08831 | 1103.875 | 0.00029 | 23.2 | 64000 | 1103.875 | 23.2 | 56966.925 | -1008.025 | 1248701.9 | 56966.925 | 0
2021072522 | 1 | 0.78646 | 117969 | 0.18113 | 0 | 0.10395 | 1299.375 | 0 | 0 | 64000 | 1299.375 | 0 | 52669.625 | -4297.3 | 1221498.525 | 52669.625 | 0
2021072523 | 1 | 0.73957 | 110935.5 | 0.18319 | 0 | 0.12886 | 1610.75 | 0 | 0 | 64000 | 1610.75 | 0 | 45324.75 | -7344.875 | 1201640.025 | 45324.75 | 0
2021072524 | 1 | 0.68586 | 102879 | 0.23111 | 0 | 0.13245 | 1655.625 | 0 | 0 | 64000 | 1655.625 | 0 | 37223.375 | -8101.375 | 1189882.9 | 37223.375 | 0
2021072601 | 2 | 0.63827 | 95740.5 | 0.20559 | 0 | 0.12883 | 1610.375 | 0 | 0 | 64000 | 1610.375 | 0 | 30130.125 | -7093.25 | 1185219.025 | 30130.125 | 0
2021072602 | 2 | 0.60307 | 90460.5 | 0.21023 | 0 | 0.13133 | 1641.625 | 0 | 0 | 64000 | 1641.625 | 0 | 24818.875 | -5311.25 | 1185866.4 | 24818.875 | 0
2021072603 | 2 | 0.57772 | 86658 | 0.11585 | 0 | 0.12804 | 1600.5 | 0 | 0 | 64000 | 1600.5 | 0 | 21057.5 | -3761.375 | 1190275.15 | 21057.5 | 0
2021072604 | 2 | 0.56087 | 84130.5 | 0.08978 | 0 | 0.11332 | 1416.5 | 0 | 0 | 64000 | 1416.5 | 0 | 18714 | -2343.5 | 1197027.4 | 18714 | 0
2021072605 | 2 | 0.55931 | 83896.5 | 0.05807 | 0 | 0.07623 | 952.875 | 0 | 0 | 64000 | 952.875 | 0 | 18943.625 | 229.625 | 1203550.025 | 18943.625 | 0
2021072606 | 2 | 0.57443 | 86164.5 | 0.07309 | 0 | 0.07941 | 992.625 | 0.00238 | 190.4 | 64000 | 992.625 | 190.4 | 20981.475 | 2037.85 | 1208034.8 | 20981.475 | 0
2021072607 | 2 | 0.60127 | 90190.5 | 0.06361 | 0 | 0.10006 | 1250.75 | 0.06162 | 4929.6 | 64000 | 1250.75 | 4929.6 | 20010.15 | -971.325 | 1213490.9 | 20010.15 | 0
2021072608 | 2 | 0.63836 | 95754 | 0.05017 | 0 | 0.14363 | 1795.375 | 0.24568 | 19654.4 | 64000 | 1795.375 | 19654.4 | 10304.225 | -9705.925 | 1228652.925 | 10304.225 | 0
2021072609 | 2 | 0.68575 | 102862.5 | 0.01467 | 0 | 0.17014 | 2126.75 | 0.3786 | 30288 | 64000 | 2126.75 | 30288 | 6447.75 | -3856.475 | 1247671.425 | 6447.75 | 0
2021072610 | 2 | 0.73729 | 110593.5 | 0.00428 | 0 | 0.17148 | 2143.5 | 0.45473 | 36378.4 | 64000 | 2143.5 | 36378.4 | 8071.6 | 1623.85 | 1265066.075 | 8071.6 | 0
2021072611 | 2 | 0.78967 | 118450.5 | 0.00091 | 0 | 0.09319 | 1164.875 | 0.52107 | 41685.6 | 64000 | 1164.875 | 41685.6 | 11600.025 | 3528.425 | 1278932.3 | 11600.025 | 0
2021072612 | 2 | 0.83568 | 125352 | 0.03568 | 0 | 0.07929 | 991.125 | 0.57775 | 46220 | 64000 | 991.125 | 46220 | 14140.875 | 2540.85 | 1290257.675 | 14140.875 | 0
2021072613 | 2 | 0.87545 | 131317.5 | 0.08265 | 0 | 0.06278 | 784.75 | 0.57962 | 46369.6 | 64000 | 784.75 | 46369.6 | 20163.15 | 6022.275 | 1295560.775 | 20163.15 | 0
2021072614 | 2 | 0.90416 | 135624 | 0.12397 | 0 | 0.04562 | 570.25 | 0.5375 | 43000 | 64000 | 570.25 | 43000 | 28053.75 | 7890.6 | 1292973.275 | 28053.75 | 0
2021072615 | 2 | 0.92069 | 138103.5 | 0.16343 | 0 | 0.03777 | 472.125 | 0.49364 | 39491.2 | 64000 | 472.125 | 39491.2 | 34140.175 | 6086.425 | 1284299.35 | 34140.175 | 0
2021072616 | 2 | 0.92859 | 139288.5 | 0.18443 | 0 | 0.02574 | 321.75 | 0.43083 | 34466.4 | 64000 | 321.75 | 34466.4 | 40500.35 | 6360.175 | 1269265.25 | 40500.35 | 0
2021072617 | 2 | 0.93876 | 140814 | 0.12438 | 0 | 0.02607 | 325.875 | 0.36311 | 29048.8 | 64000 | 325.875 | 29048.8 | 47439.325 | 6938.975 | 1247292.175 | 47439.325 | 0
2021072618 | 2 | 0.93842 | 140763 | 0.09612 | 0 | 0.0376 | 470 | 0.23975 | 19180 | 64000 | 470 | 19180 | 57113 | 9673.675 | 1215645.425 | 57113 | 0
2021072619 | 2 | 0.927 | 139050 | 0.08515 | 0 | 0.0576 | 720 | 0.11252 | 9001.6 | 64000 | 720 | 9001.6 | 65328.4 | 8215.4 | 1175783.275 | 65328.4 | 0
2021072620 | 2 | 0.89047 | 133570.5 | 0.0637 | 0 | 0.06318 | 789.75 | 0.03221 | 2576.8 | 64000 | 789.75 | 2576.8 | 66203.95 | 875.55 | 1135045.575 | 66203.95 | 0
2021072621 | 2 | 0.84667 | 127000.5 | 0.06272 | 0 | 0.08745 | 1093.125 | 0 | 0 | 64000 | 1093.125 | 0 | 61907.375 | -4296.575 | 1098604.45 | 61907.375 | 0
2021072622 | 2 | 0.80675 | 121012.5 | 0.10168 | 0 | 0.10718 | 1339.75 | 0 | 0 | 64000 | 1339.75 | 0 | 55672.75 | -6234.625 | 1068397.95 | 55672.75 | 0
2021072623 | 2 | 0.74816 | 112224 | 0.14328 | 0 | 0.13494 | 1686.75 | 0 | 0 | 64000 | 1686.75 | 0 | 46537.25 | -9135.5 | 1047326.95 | 46537.25 | 0
2021072624 | 2 | 0.68592 | 102888 | 0.17849 | 0 | 0.17064 | 2133 | 0 | 0 | 64000 | 2133 | 0 | 36755 | -9782.25 | 1036038.2 | 36755 | 0
2021072701 | 3 | 0.63205 | 94807.5 | 0.13329 | 0 | 0.18128 | 2266 | 0 | 0 | 64000 | 2266 | 0 | 28541.5 | -8213.5 | 1032962.95 | 28541.5 | 0
2021072702 | 3 | 0.59188 | 88782 | 0.14149 | 0 | 0.15104 | 1888 | 0 | 0 | 64000 | 1888 | 0 | 22894 | -5647.5 | 1035535.2 | 22894 | 0
2021072703 | 3 | 0.56343 | 84514.5 | 0.10034 | 0 | 0.08652 | 1081.5 | 0 | 0 | 64000 | 1081.5 | 0 | 19433 | -3461 | 1041568.45 | 19433 | 0
2021072704 | 3 | 0.54694 | 82041 | 0.07289 | 0 | 0.07138 | 892.25 | 0 | 0 | 64000 | 892.25 | 0 | 17148.75 | -2284.25 | 1049885.95 | 17148.75 | 0
2021072705 | 3 | 0.5423 | 81345 | 0.09195 | 0 | 0.05604 | 700.5 | 0 | 0 | 64000 | 700.5 | 0 | 16644.5 | -504.25 | 1058707.7 | 16644.5 | 0
2021072706 | 3 | 0.55571 | 83356.5 | 0.14613 | 0 | 0.08364 | 1045.5 | 0.00197 | 157.6 | 64000 | 1045.5 | 157.6 | 18153.4 | 1508.9 | 1066020.55 | 18153.4 | 0
2021072707 | 3 | 0.58205 | 87307.5 | 0.10911 | 0 | 0.08416 | 1052 | 0.09098 | 7278.4 | 64000 | 1052 | 7278.4 | 14977.1 | -3176.3 | 1076509.7 | 14977.1 | 0
2021072708 | 3 | 0.61812 | 92718 | 0.09685 | 0 | 0.08542 | 1067.75 | 0.33369 | 26695.2 | 64000 | 1067.75 | 26695.2 | 955.05 | -14022.05 | 1101020.9 | 955.05 | 0
2021072709 | 3 | 0.6626 | 99390 | 0.09357 | 0 | 0.14219 | 1777.375 | 0.40536 | 32428.8 | 64000 | 1777.375 | 32428.8 | 1183.825 | 228.775 | 1125303.325 | 1183.825 | 0
2021072710 | 3 | 0.71156 | 106734 | 0.07933 | 0 | 0.14595 | 1824.375 | 0.47257 | 37805.6 | 64000 | 1824.375 | 37805.6 | 3104.025 | 1920.2 | 1147665.55 | 3104.025 | 0
2021072711 | 3 | 0.76584 | 114876 | 0.09591 | 0 | 0.12962 | 1620.25 | 0.48915 | 39132 | 64000 | 1620.25 | 39132 | 10123.75 | 7019.725 | 1163008.05 | 10123.75 | 0
2021072712 | 3 | 0.81774 | 122661 | 0.1371 | 0 | 0.11087 | 1385.875 | 0.53269 | 42615.2 | 64000 | 1385.875 | 42615.2 | 14659.925 | 4536.175 | 1173814.375 | 14659.925 | 0
2021072713 | 3 | 0.85843 | 128764.5 | 0.14177 | 0 | 0.08984 | 1123 | 0.55764 | 44611.2 | 64000 | 1123 | 44611.2 | 19030.3 | 4370.375 | 1180250.325 | 19030.3 | 0
2021072714 | 3 | 0.89145 | 133717.5 | 0.12548 | 0 | 0.09067 | 1133.375 | 0.5715 | 45720 | 64000 | 1133.375 | 45720 | 22864.125 | 3833.825 | 1182852.45 | 22864.125 | 0
2021072715 | 3 | 0.9121 | 136815 | 0.15723 | 0 | 0.08053 | 1006.625 | 0.5706 | 45648 | 64000 | 1006.625 | 45648 | 26160.375 | 3296.25 | 1182158.325 | 26160.375 | 0
2021072716 | 3 | 0.92896 | 139344 | 0.17274 | 0 | 0.081 | 1012.5 | 0.5021 | 40168 | 64000 | 1012.5 | 40168 | 34163.5 | 8003.125 | 1173461.075 | 34163.5 | 0
2021072717 | 3 | 0.9404 | 141060 | 0.28356 | 0 | 0.07962 | 995.25 | 0.43944 | 35155.2 | 64000 | 995.25 | 35155.2 | 40909.55 | 6746.05 | 1158017.775 | 40909.55 | 0
2021072718 | 3 | 0.94391 | 141586.5 | 0.35805 | 0 | 0.08318 | 1039.75 | 0.33481 | 26784.8 | 64000 | 1039.75 | 26784.8 | 49761.95 | 8852.4 | 1133722.075 | 49761.95 | 0
2021072719 | 3 | 0.93683 | 140524.5 | 0.39939 | 0 | 0.10609 | 1326.125 | 0.20812 | 16649.6 | 64000 | 1326.125 | 16649.6 | 58548.775 | 8786.825 | 1100639.55 | 58548.775 | 0
2021072720 | 3 | 0.90413 | 135619.5 | 0.31852 | 0 | 0.12957 | 1619.625 | 0.04834 | 3867.2 | 64000 | 1619.625 | 3867.2 | 66132.675 | 7583.9 | 1059973.125 | 66132.675 | 0
2021072721 | 3 | 0.86226 | 129339 | 0.3373 | 0 | 0.17083 | 2135.375 | 0.00022 | 17.6 | 64000 | 2135.375 | 17.6 | 63186.025 | -2946.65 | 1022253.35 | 63186.025 | 0
2021072722 | 3 | 0.82387 | 123580.5 | 0.39652 | 0 | 0.20988 | 2623.5 | 0 | 0 | 64000 | 2623.5 | 0 | 56957 | -6229.025 | 990762.6 | 56957 | 0
2021072723 | 3 | 0.76343 | 114514.5 | 0.36565 | 0 | 0.24121 | 3015.125 | 0 | 0 | 64000 | 3015.125 | 0 | 47499.375 | -9457.625 | 968729.475 | 47499.375 | 0
2021072724 | 3 | 0.6999 | 104985 | 0.38373 | 0 | 0.26149 | 3268.625 | 0 | 0 | 64000 | 3268.625 | 0 | 37716.375 | -9783 | 956479.35 | 37716.375 | 0
2021072801 | 4 | 0.64591 | 96886.5 | 0.33007 | 0 | 0.28722 | 3590.25 | 0 | 0 | 64000 | 3590.25 | 0 | 29296.25 | -8420.125 | 952649.35 | 29296.25 | 0
2021072802 | 4 | 0.60659 | 90988.5 | 0.27755 | 0 | 0.30955 | 3869.375 | 0 | 0 | 64000 | 3869.375 | 0 | 23119.125 | -6177.125 | 954996.475 | 23119.125 | 0
2021072803 | 4 | 0.57967 | 86950.5 | 0.23797 | 0 | 0.29559 | 3694.875 | 0.0012 | 96 | 64000 | 3694.875 | 96 | 19159.625 | -3959.5 | 961303.1 | 19159.625 | 0
2021072804 | 4 | 0.56248 | 84372 | 0.13511 | 0 | 0.29384 | 3673 | 0 | 0 | 64000 | 3673 | 0 | 16699 | -2460.625 | 970070.35 | 16699 | 0
2021072805 | 4 | 0.55801 | 83701.5 | 0.08334 | 0 | 0.26373 | 3296.625 | 0 | 0 | 64000 | 3296.625 | 0 | 16404.875 | -294.125 | 979131.725 | 16404.875 | 0
2021072806 | 4 | 0.5711 | 85665 | 0.07038 | 0 | 0.30492 | 3811.5 | 0.00266 | 212.8 | 64000 | 3811.5 | 212.8 | 17640.7 | 1235.825 | 986957.275 | 17640.7 | 0
2021072807 | 4 | 0.594 | 89100 | 0.08085 | 0 | 0.35277 | 4409.625 | 0.09461 | 7568.8 | 64000 | 4409.625 | 7568.8 | 13121.575 | -4519.125 | 999301.95 | 13121.575 | 0
2021072808 | 4 | 0.63035 | 94552.5 | 0.07836 | 0 | 0.38243 | 4780.375 | 0.3375 | 27000 | 64000 | 4780.375 | 25772.125 | 0 | -13121.575 | 1024768.2 | 0 | 0
2021072809 | 4 | 0.673 | 100950 | 0.07264 | 0 | 0.38071 | 4758.875 | 0.51742 | 41393.6 | 64000 | 4758.875 | 32191.125 | 0 | 0 | 1050234.45 | 0 | 0
2021072810 | 4 | 0.71946 | 107919 | 0.07597 | 0 | 0.37879 | 4734.875 | 0.59557 | 47645.6 | 64000 | 4734.875 | 39184.125 | 0 | 0 | 1075700.7 | 0 | 0
2021072811 | 4 | 0.76751 | 115126.5 | 0.06185 | 0 | 0.37973 | 4746.625 | 0.62005 | 49604 | 64000 | 4746.625 | 46379.875 | 0 | 0 | 1101166.95 | 0 | 0
2021072812 | 4 | 0.81338 | 122007 | 0.09158 | 0 | 0.37919 | 4739.875 | 0.64074 | 51259.2 | 64000 | 4739.875 | 51259.2 | 2007.925 | 2007.925 | 1124625.275 | 2007.925 | 0
2021072813 | 4 | 0.85379 | 128068.5 | 0.08942 | 0 | 0.27779 | 3472.375 | 0.66351 | 53080.8 | 64000 | 3472.375 | 53080.8 | 7515.325 | 5507.4 | 1142576.2 | 7515.325 | 0
2021072814 | 4 | 0.88427 | 132640.5 | 0.09172 | 0 | 0.22313 | 2789.125 | 0.69951 | 55960.8 | 64000 | 2789.125 | 55960.8 | 9890.575 | 2375.25 | 1158151.875 | 9890.575 | 0
2021072815 | 4 | 0.9027 | 135405 | 0.08933 | 0 | 0.15511 | 1938.875 | 0.704 | 56320 | 64000 | 1938.875 | 56320 | 13146.125 | 3255.55 | 1170472 | 13146.125 | 0
2021072816 | 4 | 0.91351 | 137026.5 | 0.08288 | 0 | 0.06766 | 845.75 | 0.68449 | 54759.2 | 64000 | 845.75 | 54759.2 | 17421.55 | 4275.425 | 1178516.7 | 17421.55 | 0
2021072817 | 4 | 0.9212 | 138180 | 0.06089 | 0 | 0.03166 | 395.75 | 0.63429 | 50743.2 | 64000 | 395.75 | 50743.2 | 23041.05 | 5619.5 | 1180941.9 | 23041.05 | 0
2021072818 | 4 | 0.92259 | 138388.5 | 0.03384 | 0 | 0.05247 | 655.875 | 0.53345 | 42676 | 64000 | 655.875 | 42676 | 31056.625 | 8015.575 | 1175351.525 | 31056.625 | 0
2021072819 | 4 | 0.90881 | 136321.5 | 0.02406 | 0 | 0.13695 | 1711.875 | 0.31815 | 25452 | 64000 | 1711.875 | 25452 | 45157.625 | 14101 | 1155660.15 | 45157.625 | 0
2021072820 | 4 | 0.87725 | 131587.5 | 0.00846 | 0 | 0.20281 | 2535.125 | 0.06366 | 5092.8 | 64000 | 2535.125 | 5092.8 | 59959.575 | 14801.95 | 1121166.825 | 59959.575 | 0
2021072821 | 4 | 0.84293 | 126439.5 | 0.00868 | 0 | 0.25145 | 3143.125 | 0.00014 | 11.2 | 64000 | 3143.125 | 11.2 | 59285.175 | -674.4 | 1087347.9 | 59285.175 | 0
2021072822 | 4 | 0.81194 | 121791 | 0.00081 | 0 | 0.31309 | 3913.625 | 0 | 0 | 64000 | 3913.625 | 0 | 53877.375 | -5407.8 | 1058936.775 | 53877.375 | 0
2021072823 | 4 | 0.75702 | 113553 | 0.00511 | 0 | 0.37381 | 4672.625 | 0 | 0 | 64000 | 4672.625 | 0 | 44880.375 | -8997 | 1039522.65 | 44880.375 | 0
2021072824 | 4 | 0.6965 | 104475 | 0.02422 | 0 | 0.40134 | 5016.75 | 0 | 0 | 64000 | 5016.75 | 0 | 35458.25 | -9422.125 | 1029530.65 | 35458.25 | 0
2021072901 | 5 | 0.64548 | 96822 | 0.06376 | 0 | 0.42199 | 5274.875 | 0 | 0 | 64000 | 5274.875 | 0 | 27547.125 | -7911.125 | 1027449.775 | 27547.125 | 0
2021072902 | 5 | 0.60821 | 91231.5 | 0.09901 | 0 | 0.44522 | 5565.25 | 0 | 0 | 64000 | 5565.25 | 0 | 21666.25 | -5880.875 | 1031249.775 | 21666.25 | 0
2021072903 | 5 | 0.58356 | 87534 | 0.17286 | 0 | 0.44834 | 5604.25 | 0 | 0 | 64000 | 5604.25 | 0 | 17929.75 | -3736.5 | 1038786.275 | 17929.75 | 0
2021072904 | 5 | 0.56794 | 85191 | 0.29558 | 0 | 0.39761 | 4970.125 | 0 | 0 | 64000 | 4970.125 | 0 | 16220.875 | -1708.875 | 1048031.65 | 16220.875 | 0
2021072905 | 5 | 0.56163 | 84244.5 | 0.42432 | 0 | 0.34016 | 4252 | 0 | 0 | 64000 | 4252 | 0 | 15992.5 | -228.375 | 1057505.4 | 15992.5 | 0
2021072906 | 5 | 0.57476 | 86214 | 0.42696 | 0 | 0.32813 | 4101.625 | 0.00487 | 389.6 | 64000 | 4101.625 | 389.6 | 17722.775 | 1730.275 | 1065248.875 | 17722.775 | 0
2021072907 | 5 | 0.60179 | 90268.5 | 0.44983 | 0 | 0.35691 | 4461.375 | 0.13091 | 10472.8 | 64000 | 4461.375 | 10472.8 | 11334.325 | -6388.45 | 1079380.8 | 11334.325 | 0
2021072908 | 5 | 0.63518 | 95277 | 0.43188 | 0 | 0.34327 | 4290.875 | 0.40345 | 32276 | 64000 | 4290.875 | 26986.125 | 0 | -11334.325 | 1104847.05 | 0 | 0
2021072909 | 5 | 0.66831 | 100246.5 | 0.41958 | 0 | 0.31302 | 3912.75 | 0.54743 | 43794.4 | 64000 | 3912.75 | 32333.75 | 0 | 0 | 1130313.3 | 0 | 0
2021072910 | 5 | 0.70254 | 105381 | 0.41844 | 0 | 0.31185 | 3898.125 | 0.58619 | 46895.2 | 64000 | 3898.125 | 37482.875 | 0 | 0 | 1155779.55 | 0 | 0
2021072911 | 5 | 0.74208 | 111312 | 0.50569 | 0 | 0.31501 | 3937.625 | 0.60536 | 48428.8 | 64000 | 3937.625 | 43374.375 | 0 | 0 | 1181245.8 | 0 | 0
2021072912 | 5 | 0.78202 | 117303 | 0.50439 | 0 | 0.32882 | 4110.25 | 0.62278 | 49822.4 | 64000 | 4110.25 | 49192.75 | 0 | 0 | 1206712.05 | 0 | 0
2021072913 | 5 | 0.81833 | 122749.5 | 0.57133 | 0 | 0.33913 | 4239.125 | 0.62112 | 49689.6 | 64000 | 4239.125 | 49689.6 | 4820.775 | 4820.775 | 1227357.525 | 4820.775 | 0
2021072914 | 5 | 0.84685 | 127027.5 | 0.59314 | 0 | 0.33351 | 4168.875 | 0.65145 | 52116 | 64000 | 4168.875 | 52116 | 6742.625 | 1921.85 | 1246081.15 | 6742.625 | 0
2021072915 | 5 | 0.86502 | 129753 | 0.69516 | 0 | 0.30885 | 3860.625 | 0.65613 | 52490.4 | 64000 | 3860.625 | 52490.4 | 9401.975 | 2659.35 | 1262145.425 | 9401.975 | 0
2021072916 | 5 | 0.87206 | 130809 | 0.74091 | 0 | 0.25968 | 3246 | 0.63202 | 50561.6 | 64000 | 3246 | 50561.6 | 13001.4 | 3599.425 | 1274610.275 | 13001.4 | 0
2021072917 | 5 | 0.87162 | 130743 | 0.73947 | 0 | 0.22479 | 2809.875 | 0.60263 | 48210.4 | 64000 | 2809.875 | 48210.4 | 15722.725 | 2721.325 | 1284353.8 | 15722.725 | 0
2021072918 | 5 | 0.86857 | 130285.5 | 0.64335 | 0 | 0.24945 | 3118.125 | 0.48201 | 38560.8 | 64000 | 3118.125 | 38560.8 | 24606.575 | 8883.85 | 1285213.475 | 24606.575 | 0
2021072919 | 5 | 0.85321 | 127981.5 | 0.53509 | 0 | 0.39795 | 4974.375 | 0.27457 | 21965.6 | 64000 | 4974.375 | 21965.6 | 37041.525 | 12434.95 | 1273638.2 | 37041.525 | 0
2021072920 | 5 | 0.82766 | 124149 | 0.56453 | 0 | 0.48221 | 6027.625 | 0.06159 | 4927.2 | 64000 | 6027.625 | 4927.2 | 49194.175 | 12152.65 | 1249910.275 | 49194.175 | 0
2021072921 | 5 | 0.79894 | 119841 | 0.68318 | 0 | 0.5008 | 6260 | 0.0001 | 8 | 64000 | 6260 | 8 | 49573 | 378.825 | 1225803.525 | 49573 | 0
2021072922 | 5 | 0.77208 | 115812 | 0.75474 | 0 | 0.51854 | 6481.75 | 0 | 0 | 64000 | 6481.75 | 0 | 45330.25 | -4242.75 | 1205939.525 | 45330.25 | 0
2021072923 | 5 | 0.72527 | 108790.5 | 0.67924 | 0 | 0.53427 | 6678.375 | 0 | 0 | 64000 | 6678.375 | 0 | 38112.125 | -7218.125 | 1193293.65 | 38112.125 | 0
2021072924 | 5 | 0.67482 | 101223 | 0.55374 | 0 | 0.55882 | 6985.25 | 0 | 0 | 64000 | 6985.25 | 0 | 30237.75 | -7874.375 | 1188522.15 | 30237.75 | 0
2021073001 | 6 | 0.6294 | 94410 | 0.5282 | 0 | 0.57922 | 7240.25 | 0 | 0 | 64000 | 7240.25 | 0 | 23169.75 | -7068 | 1190818.65 | 23169.75 | 0
2021073002 | 6 | 0.59455 | 89182.5 | 0.51822 | 0 | 0.57966 | 7245.75 | 0 | 0 | 64000 | 7245.75 | 0 | 17936.75 | -5233 | 1198348.15 | 17936.75 | 0
2021073003 | 6 | 0.57046 | 85569 | 0.44574 | 0 | 0.56067 | 7008.375 | 0 | 0 | 64000 | 7008.375 | 0 | 14560.625 | -3376.125 | 1209253.775 | 14560.625 | 0
2021073004 | 6 | 0.55643 | 83464.5 | 0.47286 | 0 | 0.48351 | 6043.875 | 0 | 0 | 64000 | 6043.875 | 0 | 13420.625 | -1140 | 1221299.4 | 13420.625 | 0
2021073005 | 6 | 0.55456 | 83184 | 0.49819 | 0 | 0.37362 | 4670.25 | 0 | 0 | 64000 | 4670.25 | 0 | 14513.75 | 1093.125 | 1232251.9 | 14513.75 | 0
2021073006 | 6 | 0.56807 | 85210.5 | 0.47214 | 0 | 0.32419 | 4052.375 | 0.00524 | 419.2 | 64000 | 4052.375 | 419.2 | 16738.925 | 2225.175 | 1240979.225 | 16738.925 | 0
2021073007 | 6 | 0.58988 | 88482 | 0.51014 | 0 | 0.35711 | 4463.875 | 0.11237 | 8989.6 | 64000 | 4463.875 | 8989.6 | 11028.525 | -5710.4 | 1255416.95 | 11028.525 | 0
2021073008 | 6 | 0.62161 | 93241.5 | 0.58583 | 0 | 0.38411 | 4801.375 | 0.32878 | 26302.4 | 64000 | 4801.375 | 24440.125 | 0 | -11028.525 | 1280883.2 | 0 | 0
2021073009 | 6 | 0.66001 | 99001.5 | 0.61925 | 0 | 0.37233 | 4654.125 | 0.39123 | 31298.4 | 64000 | 4654.125 | 30347.375 | 0 | 0 | 1306349.45 | 0 | 0
2021073010 | 6 | 0.69683 | 104524.5 | 0.64423 | 0 | 0.35209 | 4401.125 | 0.45349 | 36279.2 | 64000 | 4401.125 | 36123.375 | 0 | 0 | 1331815.7 | 0 | 0
2021073011 | 6 | 0.72863 | 109294.5 | 0.66717 | 0 | 0.32865 | 4108.125 | 0.531 | 42480 | 64000 | 4108.125 | 41186.375 | 0 | 0 | 1350000 | 0 | 0
2021073012 | 6 | 0.75943 | 113914.5 | 0.70885 | 0 | 0.30443 | 3805.375 | 0.50094 | 40075.2 | 64000 | 3805.375 | 40075.2 | 6033.925 | 6033.925 | 1350000 | 6033.925 | 0
2021073013 | 6 | 0.78325 | 117487.5 | 0.75716 | 0 | 0.27661 | 3457.625 | 0.48675 | 38940 | 64000 | 3457.625 | 38940 | 11089.875 | 5055.95 | 1350000 | 11089.875 | 0
2021073014 | 6 | 0.80425 | 120637.5 | 0.78652 | 0 | 0.23386 | 2923.25 | 0.45285 | 36228 | 64000 | 2923.25 | 36228 | 17486.25 | 6396.375 | 1350000 | 17486.25 | 0
2021073015 | 6 | 0.81612 | 122418 | 0.79022 | 0 | 0.26906 | 3363.25 | 0.33904 | 27123.2 | 64000 | 3363.25 | 27123.2 | 27931.55 | 10445.3 | 1347534.7 | 27931.55 | 0
2021073016 | 6 | 0.82111 | 123166.5 | 0.7556 | 0 | 0.30464 | 3808 | 0.27336 | 21868.8 | 64000 | 3808 | 21868.8 | 33489.7 | 5558.15 | 1339511.25 | 33489.7 | 0
2021073017 | 6 | 0.82281 | 123421.5 | 0.7595 | 0 | 0.29454 | 3681.75 | 0.1559 | 12472 | 64000 | 3681.75 | 12472 | 43267.75 | 9778.05 | 1321709.75 | 43267.75 | 0
2021073018 | 6 | 0.8164 | 122460 | 0.69914 | 0 | 0.32082 | 4010.25 | 0.08448 | 6758.4 | 64000 | 4010.25 | 6758.4 | 47691.35 | 4423.6 | 1299484.65 | 47691.35 | 0
2021073019 | 6 | 0.79301 | 118951.5 | 0.60987 | 0 | 0.38043 | 4755.375 | 0.03781 | 3024.8 | 64000 | 4755.375 | 3024.8 | 47171.325 | -520.025 | 1277779.575 | 47171.325 | 0
2021073020 | 6 | 0.75498 | 113247 | 0.46896 | 0 | 0.41734 | 5216.75 | 0.01016 | 812.8 | 64000 | 5216.75 | 812.8 | 43217.45 | -3953.875 | 1260028.375 | 43217.45 | 0
2021073021 | 6 | 0.71785 | 107677.5 | 0.40351 | 0 | 0.43389 | 5423.625 | 0 | 0 | 64000 | 5423.625 | 0 | 38253.875 | -4963.575 | 1247240.75 | 38253.875 | 0
2021073022 | 6 | 0.69002 | 103503 | 0.45831 | 0 | 0.47304 | 5913 | 0 | 0 | 64000 | 5913 | 0 | 33590 | -4663.875 | 1239117 | 33590 | 0
2021073023 | 6 | 0.64565 | 96847.5 | 0.50313 | 0 | 0.48414 | 6051.75 | 0 | 0 | 64000 | 6051.75 | 0 | 26795.75 | -6794.25 | 1237787.5 | 26795.75 | 0
2021073024 | 6 | 0.59589 | 89383.5 | 0.38881 | 0 | 0.45641 | 5705.125 | 0 | 0 | 64000 | 5705.125 | 0 | 19678.375 | -7117.375 | 1243575.375 | 19678.375 | 0
2021073101 | 7 | 0.55265 | 82897.5 | 0.2495 | 0 | 0.42637 | 5329.625 | 0 | 0 | 64000 | 5329.625 | 0 | 13567.875 | -6110.5 | 1255473.75 | 13567.875 | 0
2021073102 | 7 | 0.51891 | 77836.5 | 0.14401 | 0 | 0.40227 | 5028.375 | 0 | 0 | 64000 | 5028.375 | 0 | 8808.125 | -4759.75 | 1272131.875 | 8808.125 | 0
2021073103 | 7 | 0.49529 | 74293.5 | 0.17449 | 0 | 0.29695 | 3711.875 | 0 | 0 | 64000 | 3711.875 | 0 | 6581.625 | -2226.5 | 1291016.5 | 6581.625 | 0
2021073104 | 7 | 0.47745 | 71617.5 | 0.21539 | 0 | 0.19645 | 2455.625 | 0 | 0 | 64000 | 2455.625 | 0 | 5161.875 | -1419.75 | 1311320.875 | 5161.875 | 0
2021073105 | 7 | 0.47013 | 70519.5 | 0.19165 | 0 | 0.10846 | 1355.75 | 0 | 0 | 64000 | 1355.75 | 0 | 5163.75 | 1.875 | 1331623.375 | 5163.75 | 0
2021073106 | 7 | 0.47085 | 70627.5 | 0.16737 | 0 | 0.06787 | 848.375 | 0.00121 | 96.8 | 64000 | 848.375 | 96.8 | 5682.325 | 518.575 | 1350000 | 5682.325 | 0
2021073107 | 7 | 0.47487 | 71230.5 | 0.11268 | 0 | 0.06759 | 844.875 | 0.02294 | 1835.2 | 64000 | 844.875 | 1835.2 | 4550.425 | -1131.9 | 1350000 | 4550.425 | 0
2021073108 | 7 | 0.48917 | 73375.5 | 0.02394 | 0 | 0.06207 | 775.875 | 0.06233 | 4986.4 | 64000 | 775.875 | 4986.4 | 3613.225 | -937.2 | 1350000 | 3613.225 | 0
2021073109 | 7 | 0.51408 | 77112 | 0.003 | 0 | 0.06765 | 845.625 | 0.08817 | 7053.6 | 64000 | 845.625 | 7053.6 | 5212.775 | 1599.55 | 1350000 | 5212.775 | 0
2021073110 | 7 | 0.54262 | 81393 | 0.00651 | 0 | 0.06318 | 789.75 | 0.18061 | 14448.8 | 64000 | 789.75 | 14448.8 | 2154.45 | -3058.325 | 1350000 | 2154.45 | 0
2021073111 | 7 | 0.56837 | 85255.5 | 0.01436 | 0 | 0.06487 | 810.875 | 0.22939 | 18351.2 | 64000 | 810.875 | 18351.2 | 2093.425 | -61.025 | 1350000 | 2093.425 | 0
2021073112 | 7 | 0.59199 | 88798.5 | 0.00926 | 0 | 0.0802 | 1002.5 | 0.28592 | 22873.6 | 64000 | 1002.5 | 22873.6 | 922.4 | -1171.025 | 1350000 | 922.4 | 0
2021073113 | 7 | 0.61772 | 92658 | 0.01038 | 0 | 0.08438 | 1054.75 | 0.31947 | 25557.6 | 64000 | 1054.75 | 25557.6 | 2045.65 | 1123.25 | 1350000 | 2045.65 | 0
2021073114 | 7 | 0.63782 | 95673 | 0.02374 | 0 | 0.06798 | 849.75 | 0.37496 | 29996.8 | 64000 | 849.75 | 29996.8 | 826.45 | -1219.2 | 1350000 | 826.45 | 0
2021073115 | 7 | 0.65866 | 98799 | 0.04433 | 0 | 0.06844 | 855.5 | 0.373 | 29840 | 64000 | 855.5 | 29840 | 4103.5 | 3277.05 | 1350000 | 4103.5 | 0
2021073116 | 7 | 0.67789 | 101683.5 | 0.0669 | 0 | 0.07101 | 887.625 | 0.33581 | 26864.8 | 64000 | 887.625 | 26864.8 | 9931.075 | 5827.575 | 1350000 | 9931.075 | 0
2021073117 | 7 | 0.69286 | 103929 | 0.06951 | 0 | 0.06219 | 777.375 | 0.23569 | 18855.2 | 64000 | 777.375 | 18855.2 | 20296.425 | 10365.35 | 1350000 | 20296.425 | 0
2021073118 | 7 | 0.69949 | 104923.5 | 0.08988 | 0 | 0.06907 | 863.375 | 0.16293 | 13034.4 | 64000 | 863.375 | 13034.4 | 27025.725 | 6729.3 | 1348440.525 | 27025.725 | 0
2021073119 | 7 | 0.69115 | 103672.5 | 0.06932 | 0 | 0.07943 | 992.875 | 0.08145 | 6516 | 64000 | 992.875 | 6516 | 32163.625 | 5137.9 | 1341743.15 | 32163.625 | 0
2021073120 | 7 | 0.66955 | 100432.5 | 0.03923 | 0 | 0.07677 | 959.625 | 0.01269 | 1015.2 | 64000 | 959.625 | 1015.2 | 34457.675 | 2294.05 | 1332751.725 | 34457.675 | 0
2021073121 | 7 | 0.64989 | 97483.5 | 0.03681 | 0 | 0.07543 | 942.875 | 0 | 0 | 64000 | 942.875 | 0 | 32540.625 | -1917.05 | 1325677.35 | 32540.625 | 0
2021073122 | 7 | 0.6326 | 94890 | 0.06951 | 0 | 0.08084 | 1010.5 | 0 | 0 | 64000 | 1010.5 | 0 | 29879.5 | -2661.125 | 1321264.1 | 29879.5 | 0
2021073123 | 7 | 0.60138 | 90207 | 0.0845 | 0 | 0.10294 | 1286.75 | 0 | 0 | 64000 | 1286.75 | 0 | 24920.25 | -4959.25 | 1321810.1 | 24920.25 | 0
2021073124 | 7 | 0.5642 | 84630 | 0.10103 | 0 | 0.12268 | 1533.5 | 0 | 0 | 64000 | 1533.5 | 0 | 19096.5 | -5823.75 | 1328179.85 | 19096.5 | 0
2021080101 | 1 | 0.5286 | 79290 | 0.08166 | 0 | 0.11915 | 1489.375 | 0 | 0 | 64000 | 1489.375 | 0 | 13800.625 | -5295.875 | 1339845.475 | 13800.625 | 0
2021080102 | 1 | 0.50068 | 75102 | 0.09234 | 0 | 0.1091 | 1363.75 | 0 | 0 | 64000 | 1363.75 | 0 | 9738.25 | -4062.375 | 1350000 | 9738.25 | 0
2021080103 | 1 | 0.48182 | 72273 | 0.10774 | 0 | 0.09839 | 1229.875 | 0 | 0 | 64000 | 1229.875 | 0 | 7043.125 | -2695.125 | 1350000 | 7043.125 | 0
2021080104 | 1 | 0.46876 | 70314 | 0.17741 | 0 | 0.10163 | 1270.375 | 0 | 0 | 64000 | 1270.375 | 0 | 5043.625 | -1999.5 | 1350000 | 5043.625 | 0
2021080105 | 1 | 0.46293 | 69439.5 | 0.25931 | 0 | 0.08723 | 1090.375 | 0 | 0 | 64000 | 1090.375 | 0 | 4349.125 | -694.5 | 1350000 | 4349.125 | 0
2021080106 | 1 | 0.46261 | 69391.5 | 0.26418 | 0 | 0.06302 | 787.75 | 0 | 0 | 64000 | 787.75 | 0 | 4603.75 | 254.625 | 1350000 | 4603.75 | 0
2021080107 | 1 | 0.46364 | 69546 | 0.25299 | 0 | 0.06154 | 769.25 | 0.02009 | 1607.2 | 64000 | 769.25 | 1607.2 | 3169.55 | -1434.2 | 1350000 | 3169.55 | 0
2021080108 | 1 | 0.47429 | 71143.5 | 0.19702 | 0 | 0.06286 | 785.75 | 0.08979 | 7183.2 | 64000 | 785.75 | 6357.75 | 0 | -3169.55 | 1350000 | 0 | 0
2021080109 | 1 | 0.50283 | 75424.5 | 0.10782 | 0 | 0.08506 | 1063.25 | 0.15657 | 12525.6 | 64000 | 1063.25 | 10361.25 | 0 | 0 | 1350000 | 0 | 0
2021080110 | 1 | 0.53376 | 80064 | 0.0518 | 0 | 0.09734 | 1216.75 | 0.26481 | 21184.8 | 64000 | 1216.75 | 14847.25 | 0 | 0 | 1350000 | 0 | 0
2021080111 | 1 | 0.56376 | 84564 | 0.07482 | 0 | 0.09666 | 1208.25 | 0.35467 | 28373.6 | 64000 | 1208.25 | 19355.75 | 0 | 0 | 1350000 | 0 | 0
2021080112 | 1 | 0.58946 | 88419 | 0.11404 | 0 | 0.10103 | 1262.875 | 0.41419 | 33135.2 | 64000 | 1262.875 | 23156.125 | 0 | 0 | 1350000 | 0 | 0
2021080113 | 1 | 0.60982 | 91473 | 0.18841 | 0 | 0.10284 | 1285.5 | 0.50998 | 40798.4 | 64000 | 1285.5 | 26187.5 | 0 | 0 | 1350000 | 0 | 0
2021080114 | 1 | 0.62597 | 93895.5 | 0.23939 | 0 | 0.09838 | 1229.75 | 0.55057 | 44045.6 | 64000 | 1229.75 | 28665.75 | 0 | 0 | 1350000 | 0 | 0
2021080115 | 1 | 0.63589 | 95383.5 | 0.29712 | 0 | 0.07437 | 929.625 | 0.52816 | 42252.8 | 64000 | 929.625 | 30453.875 | 0 | 0 | 1350000 | 0 | 0
2021080116 | 1 | 0.64504 | 96756 | 0.36631 | 0 | 0.04684 | 585.5 | 0.44222 | 35377.6 | 64000 | 585.5 | 32170.5 | 0 | 0 | 1350000 | 0 | 0
2021080117 | 1 | 0.65962 | 98943 | 0.54384 | 0 | 0.03474 | 434.25 | 0.36836 | 29468.8 | 64000 | 434.25 | 29468.8 | 5039.95 | 5039.95 | 1350000 | 5039.95 | 0
2021080118 | 1 | 0.67234 | 100851 | 0.6345 | 0 | 0.03339 | 417.375 | 0.23639 | 18911.2 | 64000 | 417.375 | 18911.2 | 17522.425 | 12482.475 | 1350000 | 17522.425 | 0
2021080119 | 1 | 0.67093 | 100639.5 | 0.44503 | 0 | 0.03789 | 473.625 | 0.12375 | 9900 | 64000 | 473.625 | 9900 | 26265.875 | 8743.45 | 1349200.375 | 26265.875 | 0
2021080120 | 1 | 0.65464 | 98196 | 0.35249 | 0 | 0.03566 | 445.75 | 0.02772 | 2217.6 | 64000 | 445.75 | 2217.6 | 31532.65 | 5266.775 | 1343133.975 | 31532.65 | 0
2021080121 | 1 | 0.63767 | 95650.5 | 0.30155 | 0 | 0.02952 | 369 | 0 | 0 | 64000 | 369 | 0 | 31281.5 | -251.15 | 1337318.725 | 31281.5 | 0
2021080122 | 1 | 0.62123 | 93184.5 | 0.29397 | 0 | 0.03552 | 444 | 0 | 0 | 64000 | 444 | 0 | 28740.5 | -2541 | 1334044.475 | 28740.5 | 0
2021080123 | 1 | 0.58412 | 87618 | 0.31343 | 0 | 0.03635 | 454.375 | 0 | 0 | 64000 | 454.375 | 0 | 23163.625 | -5576.875 | 1336347.1 | 23163.625 | 0
2021080124 | 1 | 0.5447 | 81705 | 0.29528 | 0 | 0.03554 | 444.25 | 0 | 0 | 64000 | 444.25 | 0 | 17260.75 | -5902.875 | 1344552.6 | 17260.75 | 0
2021080201 | 2 | 0.51024 | 76536 | 0.37269 | 0 | 0.04593 | 574.125 | 0 | 0 | 64000 | 574.125 | 0 | 11961.875 | -5298.875 | 1350000 | 11961.875 | 0
2021080202 | 2 | 0.48497 | 72745.5 | 0.38454 | 0 | 0.05169 | 646.125 | 0 | 0 | 64000 | 646.125 | 0 | 8099.375 | -3862.5 | 1350000 | 8099.375 | 0
2021080203 | 2 | 0.4688 | 70320 | 0.43072 | 0 | 0.04234 | 529.25 | 0 | 0 | 64000 | 529.25 | 0 | 5790.75 | -2308.625 | 1350000 | 5790.75 | 0
2021080204 | 2 | 0.46146 | 69219 | 0.47628 | 0 | 0.02865 | 358.125 | 0 | 0 | 64000 | 358.125 | 0 | 4860.875 | -929.875 | 1350000 | 4860.875 | 0
2021080205 | 2 | 0.46391 | 69586.5 | 0.49175 | 0 | 0.02641 | 330.125 | 0 | 0 | 64000 | 330.125 | 0 | 5256.375 | 395.5 | 1350000 | 5256.375 | 0
2021080206 | 2 | 0.48093 | 72139.5 | 0.51533 | 0 | 0.01712 | 214 | 0.00216 | 172.8 | 64000 | 214 | 172.8 | 7752.7 | 2496.325 | 1350000 | 7752.7 | 0
2021080207 | 2 | 0.50733 | 76099.5 | 0.50666 | 0 | 0.01879 | 234.875 | 0.06232 | 4985.6 | 64000 | 234.875 | 4985.6 | 6879.025 | -873.675 | 1350000 | 6879.025 | 0
2021080208 | 2 | 0.53853 | 80779.5 | 0.44689 | 0 | 0.01851 | 231.375 | 0.22329 | 17863.2 | 64000 | 231.375 | 16548.125 | 0 | -6879.025 | 1350000 | 0 | 0
2021080209 | 2 | 0.56813 | 85219.5 | 0.35705 | 0 | 0.01605 | 200.625 | 0.37541 | 30032.8 | 64000 | 200.625 | 21018.875 | 0 | 0 | 1350000 | 0 | 0
2021080210 | 2 | 0.59574 | 89361 | 0.29455 | 0 | 0.01644 | 205.5 | 0.46974 | 37579.2 | 64000 | 205.5 | 25155.5 | 0 | 0 | 1350000 | 0 | 0
2021080211 | 2 | 0.62113 | 93169.5 | 0.30724 | 0 | 0.01337 | 167.125 | 0.55573 | 44458.4 | 64000 | 167.125 | 29002.375 | 0 | 0 | 1350000 | 0 | 0
2021080212 | 2 | 0.64449 | 96673.5 | 0.33941 | 0 | 0.01237 | 154.625 | 0.58502 | 46801.6 | 64000 | 154.625 | 32518.875 | 0 | 0 | 1350000 | 0 | 0
2021080213 | 2 | 0.66709 | 100063.5 | 0.35507 | 0 | 0.01323 | 165.375 | 0.60288 | 48230.4 | 64000 | 165.375 | 35898.125 | 0 | 0 | 1350000 | 0 | 0
2021080214 | 2 | 0.68715 | 103072.5 | 0.31443 | 0 | 0.01084 | 135.5 | 0.61457 | 49165.6 | 64000 | 135.5 | 38937 | 0 | 0 | 1350000 | 0 | 0
2021080215 | 2 | 0.7054 | 105810 | 0.25169 | 0 | 0.00726 | 90.75 | 0.60319 | 48255.2 | 64000 | 90.75 | 41719.25 | 0 | 0 | 1350000 | 0 | 0
2021080216 | 2 | 0.71837 | 107755.5 | 0.20939 | 0 | 0.00403 | 50.375 | 0.63508 | 50806.4 | 64000 | 50.375 | 43705.125 | 0 | 0 | 1350000 | 0 | 0
2021080217 | 2 | 0.73075 | 109612.5 | 0.17387 | 0 | 0.00307 | 38.375 | 0.5956 | 47648 | 64000 | 38.375 | 45574.125 | 0 | 0 | 1350000 | 0 | 0
2021080218 | 2 | 0.74087 | 111130.5 | 0.11218 | 0 | 0.01051 | 131.375 | 0.49682 | 39745.6 | 64000 | 131.375 | 39745.6 | 7253.525 | 7253.525 | 1350000 | 7253.525 | 0
2021080219 | 2 | 0.73526 | 110289 | 0.07871 | 0 | 0.01584 | 198 | 0.28894 | 23115.2 | 64000 | 198 | 23115.2 | 22975.8 | 15722.275 | 1350000 | 22975.8 | 0
2021080220 | 2 | 0.71171 | 106756.5 | 0.0422 | 0 | 0.0172 | 215 | 0.06209 | 4967.2 | 64000 | 215 | 4967.2 | 37574.3 | 14598.5 | 1337891.95 | 37574.3 | 0
2021080221 | 2 | 0.68283 | 102424.5 | 0.03249 | 0 | 0.01833 | 229.125 | 0.00013 | 10.4 | 64000 | 229.125 | 10.4 | 38184.975 | 610.675 | 1325173.225 | 38184.975 | 0
2021080222 | 2 | 0.65624 | 98436 | 0.02842 | 0 | 0.02051 | 256.375 | 0 | 0 | 64000 | 256.375 | 0 | 34179.625 | -4005.35 | 1316459.85 | 34179.625 | 0
2021080223 | 2 | 0.61059 | 91588.5 | 0.0236 | 0 | 0.02165 | 270.625 | 0 | 0 | 64000 | 270.625 | 0 | 27317.875 | -6861.75 | 1314608.225 | 27317.875 | 0
2021080224 | 2 | 0.56115 | 84172.5 | 0.02587 | 0 | 0.0215 | 268.75 | 0 | 0 | 64000 | 268.75 | 0 | 19903.75 | -7414.125 | 1320170.725 | 19903.75 | 0
2021080301 | 3 | 0.5219 | 78285 | 0.02722 | 0 | 0.02704 | 338 | 0 | 0 | 64000 | 338 | 0 | 13947 | -5956.75 | 1331689.975 | 13947 | 0
2021080302 | 3 | 0.49363 | 74044.5 | 0.01425 | 0 | 0.02551 | 318.875 | 0 | 0 | 64000 | 318.875 | 0 | 9725.625 | -4221.375 | 1347430.6 | 9725.625 | 0
2021080303 | 3 | 0.4763 | 71445 | 0.00015 | 0 | 0.01907 | 238.375 | 0 | 0 | 64000 | 238.375 | 0 | 7206.625 | -2519 | 1350000 | 7206.625 | 0
2021080304 | 3 | 0.46631 | 69946.5 | 0.00133 | 0 | 0.02136 | 267 | 0 | 0 | 64000 | 267 | 0 | 5679.5 | -1527.125 | 1350000 | 5679.5 | 0
2021080305 | 3 | 0.46763 | 70144.5 | 0.00939 | 0 | 0.02283 | 285.375 | 0 | 0 | 64000 | 285.375 | 0 | 5859.125 | 179.625 | 1350000 | 5859.125 | 0
2021080306 | 3 | 0.48505 | 72757.5 | 0.01426 | 0 | 0.03295 | 411.875 | 0.00221 | 176.8 | 64000 | 411.875 | 176.8 | 8168.825 | 2309.7 | 1350000 | 8168.825 | 0
2021080307 | 3 | 0.51232 | 76848 | 0.0341 | 0 | 0.05183 | 647.875 | 0.11153 | 8922.4 | 64000 | 647.875 | 8922.4 | 3277.725 | -4891.1 | 1350000 | 3277.725 | 0
2021080308 | 3 | 0.53984 | 80976 | 0.0263 | 0 | 0.06452 | 806.5 | 0.37245 | 29796 | 64000 | 806.5 | 16169.5 | 0 | -3277.725 | 1350000 | 0 | 0
2021080309 | 3 | 0.5679 | 85185 | 0.0241 | 0 | 0.07101 | 887.625 | 0.52955 | 42364 | 64000 | 887.625 | 20297.375 | 0 | 0 | 1350000 | 0 | 0
2021080310 | 3 | 0.59374 | 89061 | 0.01556 | 0 | 0.06334 | 791.75 | 0.57654 | 46123.2 | 64000 | 791.75 | 24269.25 | 0 | 0 | 1350000 | 0 | 0
2021080311 | 3 | 0.6185 | 92775 | 0.02286 | 0 | 0.06372 | 796.5 | 0.5868 | 46944 | 64000 | 796.5 | 27978.5 | 0 | 0 | 1350000 | 0 | 0
2021080312 | 3 | 0.64098 | 96147 | 0.03364 | 0 | 0.06978 | 872.25 | 0.59831 | 47864.8 | 64000 | 872.25 | 31274.75 | 0 | 0 | 1350000 | 0 | 0
2021080313 | 3 | 0.66418 | 99627 | 0.04614 | 0 | 0.08211 | 1026.375 | 0.62329 | 49863.2 | 64000 | 1026.375 | 34600.625 | 0 | 0 | 1350000 | 0 | 0
2021080314 | 3 | 0.68576 | 102864 | 0.03941 | 0 | 0.07613 | 951.625 | 0.62961 | 50368.8 | 64000 | 951.625 | 37912.375 | 0 | 0 | 1350000 | 0 | 0
2021080315 | 3 | 0.70397 | 105595.5 | 0.01902 | 0 | 0.08326 | 1040.75 | 0.60686 | 48548.8 | 64000 | 1040.75 | 40554.75 | 0 | 0 | 1350000 | 0 | 0
2021080316 | 3 | 0.71968 | 107952 | 0.02983 | 0 | 0.07562 | 945.25 | 0.59705 | 47764 | 64000 | 945.25 | 43006.75 | 0 | 0 | 1350000 | 0 | 0
2021080317 | 3 | 0.7306 | 109590 | 0.05924 | 0 | 0.08558 | 1069.75 | 0.60069 | 48055.2 | 64000 | 1069.75 | 44520.25 | 0 | 0 | 1350000 | 0 | 0
2021080318 | 3 | 0.7357 | 110355 | 0.07092 | 0 | 0.11077 | 1384.625 | 0.54828 | 43862.4 | 64000 | 1384.625 | 43862.4 | 1107.975 | 1107.975 | 1350000 | 1107.975 | 0
2021080319 | 3 | 0.72674 | 109011 | 0.04565 | 0 | 0.13842 | 1730.25 | 0.34932 | 27945.6 | 64000 | 1730.25 | 27945.6 | 15335.15 | 14227.175 | 1350000 | 15335.15 | 0
2021080320 | 3 | 0.70617 | 105925.5 | 0.04609 | 0 | 0.16843 | 2105.375 | 0.07064 | 5651.2 | 64000 | 2105.375 | 5651.2 | 34168.925 | 18833.775 | 1341297.325 | 34168.925 | 0
2021080321 | 3 | 0.68623 | 102934.5 | 0.07524 | 0 | 0.15853 | 1981.625 | 3e-05 | 2.4 | 64000 | 1981.625 | 2.4 | 36950.475 | 2781.55 | 1329813.1 | 36950.475 | 0
2021080322 | 3 | 0.66379 | 99568.5 | 0.1536 | 0 | 0.12351 | 1543.875 | 0 | 0 | 64000 | 1543.875 | 0 | 34024.625 | -2925.85 | 1321254.725 | 34024.625 | 0
2021080323 | 3 | 0.61976 | 92964 | 0.20427 | 0 | 0.10579 | 1322.375 | 0 | 0 | 64000 | 1322.375 | 0 | 27641.625 | -6383 | 1319079.35 | 27641.625 | 0
2021080324 | 3 | 0.57182 | 85773 | 0.24306 | 0 | 0.11643 | 1455.375 | 0 | 0 | 64000 | 1455.375 | 0 | 20317.625 | -7324 | 1324227.975 | 20317.625 | 0
2021080401 | 4 | 0.53234 | 79851 | 0.25807 | 0 | 0.10745 | 1343.125 | 0 | 0 | 64000 | 1343.125 | 0 | 14507.875 | -5809.75 | 1335186.35 | 14507.875 | 0
2021080402 | 4 | 0.50344 | 75516 | 0.245 | 0 | 0.08586 | 1073.25 | 0 | 0 | 64000 | 1073.25 | 0 | 10442.75 | -4065.125 | 1350000 | 10442.75 | 0
2021080403 | 4 | 0.48502 | 72753 | 0.24339 | 0 | 0.0601 | 751.25 | 0 | 0 | 64000 | 751.25 | 0 | 8001.75 | -2441 | 1350000 | 8001.75 | 0
2021080404 | 4 | 0.47516 | 71274 | 0.22984 | 0 | 0.0375 | 468.75 | 0 | 0 | 64000 | 468.75 | 0 | 6805.25 | -1196.5 | 1350000 | 6805.25 | 0
2021080405 | 4 | 0.47619 | 71428.5 | 0.22953 | 0 | 0.02341 | 292.625 | 0 | 0 | 64000 | 292.625 | 0 | 7135.875 | 330.625 | 1350000 | 7135.875 | 0
2021080406 | 4 | 0.49277 | 73915.5 | 0.18167 | 0 | 0.02454 | 306.75 | 0.00216 | 172.8 | 64000 | 306.75 | 172.8 | 9435.95 | 2300.075 | 1350000 | 9435.95 | 0
2021080407 | 4 | 0.5197 | 77955 | 0.11407 | 0 | 0.03418 | 427.25 | 0.04293 | 3434.4 | 64000 | 427.25 | 3434.4 | 10093.35 | 657.4 | 1350000 | 10093.35 | 0
2021080408 | 4 | 0.5468 | 82020 | 0.06032 | 0 | 0.03817 | 477.125 | 0.10812 | 8649.6 | 64000 | 477.125 | 8649.6 | 8893.275 | -1200.075 | 1350000 | 8893.275 | 0
2021080409 | 4 | 0.57581 | 86371.5 | 0.04091 | 0 | 0.04027 | 503.375 | 0.15231 | 12184.8 | 64000 | 503.375 | 12184.8 | 9683.325 | 790.05 | 1350000 | 9683.325 | 0
2021080410 | 4 | 0.60117 | 90175.5 | 0.01432 | 0 | 0.03505 | 438.125 | 0.21133 | 16906.4 | 64000 | 438.125 | 16906.4 | 8830.975 | -852.35 | 1350000 | 8830.975 | 0
2021080411 | 4 | 0.62806 | 94209 | 0.02375 | 0 | 0.0303 | 378.75 | 0.25202 | 20161.6 | 64000 | 378.75 | 20161.6 | 9668.65 | 837.675 | 1350000 | 9668.65 | 0
2021080412 | 4 | 0.65319 | 97978.5 | 0.06622 | 0 | 0.03453 | 431.625 | 0.25974 | 20779.2 | 64000 | 431.625 | 20779.2 | 12767.675 | 3099.025 | 1350000 | 12767.675 | 0
2021080413 | 4 | 0.67877 | 101815.5 | 0.07413 | 0 | 0.04066 | 508.25 | 0.26011 | 20808.8 | 64000 | 508.25 | 20808.8 | 16498.45 | 3730.775 | 1350000 | 16498.45 | 0
2021080414 | 4 | 0.70213 | 105319.5 | 0.05096 | 0 | 0.03848 | 481 | 0.22684 | 18147.2 | 64000 | 481 | 18147.2 | 22691.3 | 6192.85 | 1350000 | 22691.3 | 0
2021080415 | 4 | 0.72247 | 108370.5 | 0.03975 | 0 | 0.04532 | 566.5 | 0.20572 | 16457.6 | 64000 | 566.5 | 16457.6 | 27346.4 | 4655.1 | 1348119.85 | 27346.4 | 0
2021080416 | 4 | 0.73788 | 110682 | 0.03432 | 0 | 0.05336 | 667 | 0.1763 | 14104 | 64000 | 667 | 14104 | 31911 | 4564.6 | 1341675.1 | 31911 | 0
2021080417 | 4 | 0.75158 | 112737 | 0.02935 | 0 | 0.03995 | 499.375 | 0.13508 | 10806.4 | 64000 | 499.375 | 10806.4 | 37431.225 | 5520.225 | 1329710.125 | 37431.225 | 0
2021080418 | 4 | 0.75607 | 113410.5 | 0.03727 | 0 | 0.03732 | 466.5 | 0.08474 | 6779.2 | 64000 | 466.5 | 6779.2 | 42164.8 | 4733.575 | 1313011.575 | 42164.8 | 0
2021080419 | 4 | 0.74552 | 111828 | 0.05452 | 0 | 0.06403 | 800.375 | 0.04056 | 3244.8 | 64000 | 800.375 | 3244.8 | 43782.825 | 1618.025 | 1294695 | 43782.825 | 0
2021080420 | 4 | 0.71948 | 107922 | 0.05966 | 0 | 0.08944 | 1118 | 0.00678 | 542.4 | 64000 | 1118 | 542.4 | 42261.6 | -1521.225 | 1277899.65 | 42261.6 | 0
2021080421 | 4 | 0.69707 | 104560.5 | 0.07786 | 0 | 0.1044 | 1305 | 0 | 0 | 64000 | 1305 | 0 | 39255.5 | -3006.1 | 1264110.4 | 39255.5 | 0
2021080422 | 4 | 0.67362 | 101043 | 0.11302 | 0 | 0.12295 | 1536.875 | 0 | 0 | 64000 | 1536.875 | 0 | 35506.125 | -3749.375 | 1254070.525 | 35506.125 | 0
2021080423 | 4 | 0.62907 | 94360.5 | 0.12877 | 0 | 0.15405 | 1925.625 | 0 | 0 | 64000 | 1925.625 | 0 | 28434.875 | -7071.25 | 1251101.9 | 28434.875 | 0
2021080424 | 4 | 0.58065 | 87097.5 | 0.13485 | 0 | 0.17845 | 2230.625 | 0 | 0 | 64000 | 2230.625 | 0 | 20866.875 | -7568 | 1255701.275 | 20866.875 | 0
2021080501 | 5 | 0.54064 | 81096 | 0.12563 | 0 | 0.21718 | 2714.75 | 0 | 0 | 64000 | 2714.75 | 0 | 14381.25 | -6485.625 | 1266786.275 | 14381.25 | 0
2021080502 | 5 | 0.51022 | 76533 | 0.10491 | 0 | 0.25378 | 3172.25 | 0 | 0 | 64000 | 3172.25 | 0 | 9360.75 | -5020.5 | 1282891.775 | 9360.75 | 0
2021080503 | 5 | 0.49014 | 73521 | 0.07562 | 0 | 0.27372 | 3421.5 | 0 | 0 | 64000 | 3421.5 | 0 | 6099.5 | -3261.25 | 1302258.525 | 6099.5 | 0
2021080504 | 5 | 0.48004 | 72006 | 0.03985 | 0 | 0.26802 | 3350.25 | 0 | 0 | 64000 | 3350.25 | 0 | 4655.75 | -1443.75 | 1323069.025 | 4655.75 | 0
2021080505 | 5 | 0.47952 | 71928 | 0.02312 | 0 | 0.25633 | 3204.125 | 0 | 0 | 64000 | 3204.125 | 0 | 4723.875 | 68.125 | 1343811.4 | 4723.875 | 0
2021080506 | 5 | 0.49575 | 74362.5 | 0.02679 | 0 | 0.29212 | 3651.5 | 0.00268 | 214.4 | 64000 | 3651.5 | 214.4 | 6496.6 | 1772.725 | 1350000 | 6496.6 | 0
2021080507 | 5 | 0.52307 | 78460.5 | 0.04306 | 0 | 0.35011 | 4376.375 | 0.02855 | 2284 | 64000 | 4376.375 | 2284 | 7800.125 | 1303.525 | 1350000 | 7800.125 | 0
2021080508 | 5 | 0.55166 | 82749 | 0.06396 | 0 | 0.36292 | 4536.5 | 0.06287 | 5029.6 | 64000 | 4536.5 | 5029.6 | 9182.9 | 1382.775 | 1350000 | 9182.9 | 0
2021080509 | 5 | 0.584 | 87600 | 0.05523 | 0 | 0.35562 | 4445.25 | 0.09346 | 7476.8 | 64000 | 4445.25 | 7476.8 | 11677.95 | 2495.05 | 1350000 | 11677.95 | 0
2021080510 | 5 | 0.6175 | 92625 | 0.02635 | 0 | 0.3815 | 4768.75 | 0.16399 | 13119.2 | 64000 | 4768.75 | 13119.2 | 10737.05 | -940.9 | 1350000 | 10737.05 | 0
2021080511 | 5 | 0.6545 | 98175 | 0.00931 | 0 | 0.40357 | 5044.625 | 0.20154 | 16123.2 | 64000 | 5044.625 | 16123.2 | 13007.175 | 2270.125 | 1350000 | 13007.175 | 0
2021080512 | 5 | 0.69111 | 103666.5 | 0.00881 | 0 | 0.42352 | 5294 | 0.2665 | 21320 | 64000 | 5294 | 21320 | 13052.5 | 45.325 | 1350000 | 13052.5 | 0
2021080513 | 5 | 0.72555 | 108832.5 | 0.02023 | 0 | 0.45142 | 5642.75 | 0.24214 | 19371.2 | 64000 | 5642.75 | 19371.2 | 19818.55 | 6766.05 | 1350000 | 19818.55 | 0
2021080514 | 5 | 0.76039 | 114058.5 | 0.02637 | 0 | 0.47198 | 5899.75 | 0.27086 | 21668.8 | 64000 | 5899.75 | 21668.8 | 22489.95 | 2671.4 | 1350000 | 22489.95 | 0
2021080515 | 5 | 0.78656 | 117984 | 0.02424 | 0 | 0.48084 | 6010.5 | 0.24868 | 19894.4 | 64000 | 6010.5 | 19894.4 | 28079.1 | 5589.15 | 1347387.15 | 28079.1 | 0
2021080516 | 5 | 0.80767 | 121150.5 | 0.02567 | 0 | 0.45723 | 5715.375 | 0.21604 | 17283.2 | 64000 | 5715.375 | 17283.2 | 34151.925 | 6072.825 | 1338701.475 | 34151.925 | 0
2021080517 | 5 | 0.82558 | 123837 | 0.03619 | 0 | 0.45692 | 5711.5 | 0.1594 | 12752 | 64000 | 5711.5 | 12752 | 41373.5 | 7221.575 | 1322794.225 | 41373.5 | 0
2021080518 | 5 | 0.83401 | 125101.5 | 0.02847 | 0 | 0.40085 | 5010.625 | 0.10385 | 8308 | 64000 | 5010.625 | 8308 | 47782.875 | 6409.375 | 1300477.6 | 47782.875 | 0
2021080519 | 5 | 0.82243 | 123364.5 | 0.00963 | 0 | 0.37704 | 4713 | 0.05647 | 4517.6 | 64000 | 4713 | 4517.6 | 50133.9 | 2351.025 | 1275809.95 | 50133.9 | 0
2021080520 | 5 | 0.79225 | 118837.5 | 0.00136 | 0 | 0.38692 | 4836.5 | 0.01579 | 1263.2 | 64000 | 4836.5 | 1263.2 | 48737.8 | -1396.1 | 1252538.4 | 48737.8 | 0
2021080521 | 5 | 0.75831 | 113746.5 | 0.0001 | 0 | 0.39017 | 4877.125 | 0 | 0 | 64000 | 4877.125 | 0 | 44869.375 | -3868.425 | 1233135.275 | 44869.375 | 0
2021080522 | 5 | 0.72808 | 109212 | 0.00398 | 0 | 0.41188 | 5148.5 | 0 | 0 | 64000 | 5148.5 | 0 | 40063.5 | -4805.875 | 1218538.025 | 40063.5 | 0
2021080523 | 5 | 0.67581 | 101371.5 | 0.0381 | 0 | 0.42732 | 5341.5 | 0 | 0 | 64000 | 5341.5 | 0 | 32030 | -8033.5 | 1211974.275 | 32030 | 0
2021080524 | 5 | 0.62258 | 93387 | 0.05692 | 0 | 0.44956 | 5619.5 | 0 | 0 | 64000 | 5619.5 | 0 | 23767.5 | -8262.5 | 1213673.025 | 23767.5 | 0
2021080601 | 6 | 0.57694 | 86541 | 0.11946 | 0 | 0.48472 | 6059 | 0 | 0 | 64000 | 6059 | 0 | 16482 | -7285.5 | 1222657.275 | 16482 | 0
2021080602 | 6 | 0.54432 | 81648 | 0.15906 | 0 | 0.52423 | 6552.875 | 0 | 0 | 64000 | 6552.875 | 0 | 11095.125 | -5386.875 | 1237028.4 | 11095.125 | 0
2021080603 | 6 | 0.51997 | 77995.5 | 0.16251 | 0 | 0.56186 | 7023.25 | 0 | 0 | 64000 | 7023.25 | 0 | 6972.25 | -4122.875 | 1255522.4 | 6972.25 | 0
2021080604 | 6 | 0.50737 | 76105.5 | 0.18355 | 0 | 0.6017 | 7521.25 | 0 | 0 | 64000 | 7521.25 | 0 | 4584.25 | -2388 | 1276404.4 | 4584.25 | 0
2021080605 | 6 | 0.50465 | 75697.5 | 0.18119 | 0 | 0.60143 | 7517.875 | 0 | 0 | 64000 | 7517.875 | 0 | 4179.625 | -404.625 | 1297691.025 | 4179.625 | 0
2021080606 | 6 | 0.51874 | 77811 | 0.10233 | 0 | 0.60709 | 7588.625 | 0 | 0 | 64000 | 7588.625 | 0 | 6222.375 | 2042.75 | 1316934.9 | 6222.375 | 0
2021080607 | 6 | 0.54381 | 81571.5 | 0.0405 | 0 | 0.62766 | 7845.75 | 0.03427 | 2741.6 | 64000 | 7845.75 | 2741.6 | 6984.15 | 761.775 | 1335417 | 6984.15 | 0
2021080608 | 6 | 0.57508 | 86262 | 0.03276 | 0 | 0.59777 | 7472.125 | 0.15592 | 12473.6 | 64000 | 7472.125 | 12473.6 | 2316.275 | -4667.875 | 1350000 | 2316.275 | 0
2021080609 | 6 | 0.61499 | 92248.5 | 0.03365 | 0 | 0.60015 | 7501.875 | 0.26308 | 21046.4 | 64000 | 7501.875 | 20746.625 | 0 | -2316.275 | 1350000 | 0 | 0
2021080610 | 6 | 0.65622 | 98433 | 0.01704 | 0 | 0.63115 | 7889.375 | 0.32684 | 26147.2 | 64000 | 7889.375 | 26147.2 | 396.425 | 396.425 | 1350000 | 396.425 | 0
2021080611 | 6 | 0.70392 | 105588 | 0.01509 | 0 | 0.64812 | 8101.5 | 0.4348 | 34784 | 64000 | 8101.5 | 33486.5 | 0 | -396.425 | 1350000 | 0 | 0
2021080612 | 6 | 0.74935 | 112402.5 | 0.02442 | 0 | 0.6231 | 7788.75 | 0.45685 | 36548 | 64000 | 7788.75 | 36548 | 4065.75 | 4065.75 | 1350000 | 4065.75 | 0
2021080613 | 6 | 0.79123 | 118684.5 | 0.03018 | 0 | 0.58971 | 7371.375 | 0.48417 | 38733.6 | 64000 | 7371.375 | 38733.6 | 8579.525 | 4513.775 | 1350000 | 8579.525 | 0
2021080614 | 6 | 0.82757 | 124135.5 | 0.07017 | 0 | 0.57584 | 7198 | 0.50264 | 40211.2 | 64000 | 7198 | 40211.2 | 12726.3 | 4146.775 | 1350000 | 12726.3 | 0
2021080615 | 6 | 0.85078 | 127617 | 0.09611 | 0 | 0.54919 | 6864.875 | 0.5161 | 41288 | 64000 | 6864.875 | 41288 | 15464.125 | 2737.825 | 1350000 | 15464.125 | 0
2021080616 | 6 | 0.86723 | 130084.5 | 0.10883 | 0 | 0.50958 | 6369.75 | 0.54376 | 43500.8 | 64000 | 6369.75 | 43500.8 | 16213.95 | 749.825 | 1350000 | 16213.95 | 0
2021080617 | 6 | 0.87818 | 131727 | 0.10114 | 0 | 0.49006 | 6125.75 | 0.49949 | 39959.2 | 64000 | 6125.75 | 39959.2 | 21642.05 | 5428.1 | 1350000 | 21642.05 | 0
2021080618 | 6 | 0.87602 | 131403 | 0.08356 | 0 | 0.43508 | 5438.5 | 0.43292 | 34633.6 | 64000 | 5438.5 | 34633.6 | 27330.9 | 5688.85 | 1348135.35 | 27330.9 | 0
2021080619 | 6 | 0.8526 | 127890 | 0.06907 | 0 | 0.44441 | 5555.125 | 0.22439 | 17951.2 | 64000 | 5555.125 | 17951.2 | 40383.675 | 13052.775 | 1333217.925 | 40383.675 | 0
2021080620 | 6 | 0.81369 | 122053.5 | 0.08775 | 0 | 0.4419 | 5523.75 | 0.03489 | 2791.2 | 64000 | 5523.75 | 2791.2 | 49738.55 | 9354.875 | 1308945.625 | 49738.55 | 0
2021080621 | 6 | 0.78133 | 117199.5 | 0.17946 | 0 | 0.39771 | 4971.375 | 0 | 0 | 64000 | 4971.375 | 0 | 48228.125 | -1510.425 | 1286183.75 | 48228.125 | 0
2021080622 | 6 | 0.7482 | 112230 | 0.23447 | 0 | 0.31247 | 3905.875 | 0 | 0 | 64000 | 3905.875 | 0 | 44324.125 | -3904 | 1267325.875 | 44324.125 | 0
2021080623 | 6 | 0.69677 | 104515.5 | 0.30903 | 0 | 0.29195 | 3649.375 | 0 | 0 | 64000 | 3649.375 | 0 | 36866.125 | -7458 | 1255926 | 36866.125 | 0
2021080624 | 6 | 0.64256 | 96384 | 0.32955 | 0 | 0.26571 | 3321.375 | 0 | 0 | 64000 | 3321.375 | 0 | 29062.625 | -7803.5 | 1252329.625 | 29062.625 | 0
2021080701 | 7 | 0.59589 | 89383.5 | 0.36098 | 0 | 0.24041 | 3005.125 | 0 | 0 | 64000 | 3005.125 | 0 | 22378.375 | -6684.25 | 1255417.5 | 22378.375 | 0
2021080702 | 7 | 0.55989 | 83983.5 | 0.32583 | 0 | 0.24316 | 3039.5 | 0 | 0 | 64000 | 3039.5 | 0 | 16944 | -5434.375 | 1263939.75 | 16944 | 0
2021080703 | 7 | 0.53375 | 80062.5 | 0.31718 | 0 | 0.26979 | 3372.375 | 0 | 0 | 64000 | 3372.375 | 0 | 12690.125 | -4253.875 | 1276715.875 | 12690.125 | 0
2021080704 | 7 | 0.5157 | 77355 | 0.29077 | 0 | 0.27764 | 3470.5 | 0 | 0 | 64000 | 3470.5 | 0 | 9884.5 | -2805.625 | 1292297.625 | 9884.5 | 0
2021080705 | 7 | 0.50639 | 75958.5 | 0.22876 | 0 | 0.2696 | 3370 | 0 | 0 | 64000 | 3370 | 0 | 8588.5 | -1296 | 1309175.375 | 8588.5 | 0
2021080706 | 7 | 0.5076 | 76140 | 0.20762 | 0 | 0.28852 | 3606.5 | 0.00116 | 92.8 | 64000 | 3606.5 | 92.8 | 8440.7 | -147.8 | 1326200.925 | 8440.7 | 0
2021080707 | 7 | 0.51275 | 76912.5 | 0.15499 | 0 | 0.2998 | 3747.5 | 0.06986 | 5588.8 | 64000 | 3747.5 | 5588.8 | 3576.2 | -4864.5 | 1348090.975 | 3576.2 | 0
2021080708 | 7 | 0.52997 | 79495.5 | 0.12292 | 0 | 0.32836 | 4104.5 | 0.30356 | 24284.8 | 64000 | 4104.5 | 11391 | 0 | -3576.2 | 1350000 | 0 | 0
2021080709 | 7 | 0.5671 | 85065 | 0.06946 | 0 | 0.33943 | 4242.875 | 0.4418 | 35344 | 64000 | 4242.875 | 16822.125 | 0 | 0 | 1350000 | 0 | 0
2021080710 | 7 | 0.61168 | 91752 | 0.02821 | 0 | 0.33734 | 4216.75 | 0.5269 | 42152 | 64000 | 4216.75 | 23535.25 | 0 | 0 | 1350000 | 0 | 0
2021080711 | 7 | 0.65643 | 98464.5 | 0.00474 | 0 | 0.32823 | 4102.875 | 0.57093 | 45674.4 | 64000 | 4102.875 | 30361.625 | 0 | 0 | 1350000 | 0 | 0
2021080712 | 7 | 0.69215 | 103822.5 | 0.00568 | 0 | 0.31483 | 3935.375 | 0.6069 | 48552 | 64000 | 3935.375 | 35887.125 | 0 | 0 | 1350000 | 0 | 0
2021080713 | 7 | 0.72127 | 108190.5 | 0.0517 | 0 | 0.33016 | 4127 | 0.61362 | 49089.6 | 64000 | 4127 | 40063.5 | 0 | 0 | 1350000 | 0 | 0
2021080714 | 7 | 0.74283 | 111424.5 | 0.08012 | 0 | 0.27151 | 3393.875 | 0.61793 | 49434.4 | 64000 | 3393.875 | 44030.625 | 0 | 0 | 1350000 | 0 | 0
2021080715 | 7 | 0.75784 | 113676 | 0.08794 | 0 | 0.27763 | 3470.375 | 0.64653 | 51722.4 | 64000 | 3470.375 | 46205.625 | 0 | 0 | 1350000 | 0 | 0
2021080716 | 7 | 0.76562 | 114843 | 0.0945 | 0 | 0.26514 | 3314.25 | 0.65666 | 52532.8 | 64000 | 3314.25 | 47528.75 | 0 | 0 | 1350000 | 0 | 0
2021080717 | 7 | 0.76797 | 115195.5 | 0.10681 | 0 | 0.28375 | 3546.875 | 0.61205 | 48964 | 64000 | 3546.875 | 47648.625 | 0 | 0 | 1350000 | 0 | 0
2021080718 | 7 | 0.76213 | 114319.5 | 0.07035 | 0 | 0.28365 | 3545.625 | 0.51553 | 41242.4 | 64000 | 3545.625 | 41242.4 | 5531.475 | 5531.475 | 1350000 | 5531.475 | 0
2021080719 | 7 | 0.74581 | 111871.5 | 0.07874 | 0 | 0.29033 | 3629.125 | 0.27158 | 21726.4 | 64000 | 3629.125 | 21726.4 | 22515.975 | 16984.5 | 1350000 | 22515.975 | 0
2021080720 | 7 | 0.72204 | 108306 | 0.12078 | 0 | 0.30322 | 3790.25 | 0.04668 | 3734.4 | 64000 | 3790.25 | 3734.4 | 36781.35 | 14265.375 | 1338684.9 | 36781.35 | 0
2021080721 | 7 | 0.7048 | 105720 | 0.10954 | 0 | 0.2875 | 3593.75 | 0 | 0 | 64000 | 3593.75 | 0 | 38126.25 | 1344.9 | 1326024.9 | 38126.25 | 0
2021080722 | 7 | 0.68503 | 102754.5 | 0.07347 | 0 | 0.30305 | 3788.125 | 0 | 0 | 64000 | 3788.125 | 0 | 34966.375 | -3159.875 | 1316524.775 | 34966.375 | 0
2021080723 | 7 | 0.64998 | 97497 | 0.11783 | 0 | 0.2751 | 3438.75 | 0 | 0 | 64000 | 3438.75 | 0 | 30058.25 | -4908.125 | 1311932.775 | 30058.25 | 0
2021080724 | 7 | 0.6095 | 91425 | 0.09039 | 0 | 0.22599 | 2824.875 | 0 | 0 | 64000 | 2824.875 | 0 | 24600.125 | -5458.125 | 1312798.9 | 24600.125 | 0
2021080801 | 1 | 0.56999 | 85498.5 | 0.07785 | 0 | 0.19301 | 2412.625 | 0 | 0 | 64000 | 2412.625 | 0 | 19085.875 | -5514.25 | 1319179.275 | 19085.875 | 0
2021080802 | 1 | 0.53999 | 80998.5 | 0.07438 | 0 | 0.16907 | 2113.375 | 0 | 0 | 64000 | 2113.375 | 0 | 14885.125 | -4200.75 | 1329760.4 | 14885.125 | 0
2021080803 | 1 | 0.5177 | 77655 | 0.0336 | 0 | 0.17253 | 2156.625 | 0 | 0 | 64000 | 2156.625 | 0 | 11498.375 | -3386.75 | 1343728.275 | 11498.375 | 0
2021080804 | 1 | 0.50159 | 75238.5 | 0.02862 | 0 | 0.20343 | 2542.875 | 0 | 0 | 64000 | 2542.875 | 0 | 8695.625 | -2802.75 | 1350000 | 8695.625 | 0
2021080805 | 1 | 0.49055 | 73582.5 | 0.04006 | 0 | 0.28027 | 3503.375 | 0 | 0 | 64000 | 3503.375 | 0 | 6079.125 | -2616.5 | 1350000 | 6079.125 | 0
2021080806 | 1 | 0.48838 | 73257 | 0.10333 | 0 | 0.32944 | 4118 | 0.00094 | 75.2 | 64000 | 4118 | 75.2 | 5063.8 | -1015.325 | 1350000 | 5063.8 | 0
2021080807 | 1 | 0.48838 | 73257 | 0.21622 | 0 | 0.43734 | 5466.75 | 0.06515 | 5212 | 64000 | 5466.75 | 3790.25 | 0 | -5063.8 | 1350000 | 0 | 0
2021080808 | 1 | 0.5001 | 75015 | 0.18055 | 0 | 0.51144 | 6393 | 0.23991 | 19192.8 | 64000 | 6393 | 4622 | 0 | 0 | 1350000 | 0 | 0
2021080809 | 1 | 0.5345 | 80175 | 0.15019 | 0 | 0.4992 | 6240 | 0.39372 | 31497.6 | 64000 | 6240 | 9935 | 0 | 0 | 1350000 | 0 | 0
2021080810 | 1 | 0.57747 | 86620.5 | 0.10719 | 0 | 0.45821 | 5727.625 | 0.48469 | 38775.2 | 64000 | 5727.625 | 16892.875 | 0 | 0 | 1350000 | 0 | 0
2021080811 | 1 | 0.62254 | 93381 | 0.05729 | 0 | 0.38615 | 4826.875 | 0.53193 | 42554.4 | 64000 | 4826.875 | 24554.125 | 0 | 0 | 1350000 | 0 | 0
2021080812 | 1 | 0.66783 | 100174.5 | 0.03198 | 0 | 0.32893 | 4111.625 | 0.61338 | 49070.4 | 64000 | 4111.625 | 32062.875 | 0 | 0 | 1350000 | 0 | 0
2021080813 | 1 | 0.70761 | 106141.5 | 0.04293 | 0 | 0.26965 | 3370.625 | 0.63392 | 50713.6 | 64000 | 3370.625 | 38770.875 | 0 | 0 | 1350000 | 0 | 0
2021080814 | 1 | 0.73684 | 110526 | 0.04136 | 0 | 0.19908 | 2488.5 | 0.61686 | 49348.8 | 64000 | 2488.5 | 44037.5 | 0 | 0 | 1350000 | 0 | 0
2021080815 | 1 | 0.76328 | 114492 | 0.04748 | 0 | 0.1513 | 1891.25 | 0.56737 | 45389.6 | 64000 | 1891.25 | 45389.6 | 3211.15 | 3211.15 | 1350000 | 3211.15 | 0
2021080816 | 1 | 0.78918 | 118377 | 0.08203 | 0 | 0.12028 | 1503.5 | 0.49628 | 39702.4 | 64000 | 1503.5 | 39702.4 | 13171.1 | 9959.95 | 1350000 | 13171.1 | 0
2021080817 | 1 | 0.81034 | 121551 | 0.05931 | 0 | 0.11038 | 1379.75 | 0.44272 | 35417.6 | 64000 | 1379.75 | 35417.6 | 20753.65 | 7582.55 | 1350000 | 20753.65 | 0
2021080818 | 1 | 0.82337 | 123505.5 | 0.01424 | 0 | 0.17576 | 2197 | 0.33968 | 27174.4 | 64000 | 2197 | 27174.4 | 30134.1 | 9380.45 | 1345332.15 | 30134.1 | 0
2021080819 | 1 | 0.81635 | 122452.5 | 0.00098 | 0 | 0.2329 | 2911.25 | 0.19341 | 15472.8 | 64000 | 2911.25 | 15472.8 | 40068.45 | 9934.35 | 1330729.95 | 40068.45 | 0
2021080820 | 1 | 0.78732 | 118098 | 0.02434 | 0 | 0.30907 | 3863.375 | 0.03703 | 2962.4 | 64000 | 3863.375 | 2962.4 | 47272.225 | 7203.775 | 1308923.975 | 47272.225 | 0
2021080821 | 1 | 0.76066 | 114099 | 0.07435 | 0 | 0.31513 | 3939.125 | 0 | 0 | 64000 | 3939.125 | 0 | 46159.875 | -1112.35 | 1288230.35 | 46159.875 | 0
2021080822 | 1 | 0.73039 | 109558.5 | 0.13876 | 0 | 0.3707 | 4633.75 | 0 | 0 | 64000 | 4633.75 | 0 | 40924.75 | -5235.125 | 1272771.85 | 40924.75 | 0
2021080823 | 1 | 0.68244 | 102366 | 0.18221 | 0 | 0.38011 | 4751.375 | 0 | 0 | 64000 | 4751.375 | 0 | 33614.625 | -7310.125 | 1264623.475 | 33614.625 | 0
2021080824 | 1 | 0.63259 | 94888.5 | 0.19766 | 0 | 0.4055 | 5068.75 | 0 | 0 | 64000 | 5068.75 | 0 | 25819.75 | -7794.875 | 1264269.975 | 25819.75 | 0
2021080901 | 2 | 0.59044 | 88566 | 0.22501 | 0 | 0.4341 | 5426.25 | 0 | 0 | 64000 | 5426.25 | 0 | 19139.75 | -6680 | 1270596.475 | 19139.75 | 0
2021080902 | 2 | 0.55982 | 83973 | 0.21465 | 0 | 0.38174 | 4771.75 | 0 | 0 | 64000 | 4771.75 | 0 | 15201.25 | -3938.5 | 1280861.475 | 15201.25 | 0
2021080903 | 2 | 0.53974 | 80961 | 0.21762 | 0 | 0.36499 | 4562.375 | 0 | 0 | 64000 | 4562.375 | 0 | 12398.625 | -2802.625 | 1293929.1 | 12398.625 | 0
2021080904 | 2 | 0.52732 | 79098 | 0.15456 | 0 | 0.35352 | 4419 | 0 | 0 | 64000 | 4419 | 0 | 10679 | -1719.625 | 1308716.35 | 10679 | 0
2021080905 | 2 | 0.52957 | 79435.5 | 0.10713 | 0 | 0.33067 | 4133.375 | 0 | 0 | 64000 | 4133.375 | 0 | 11302.125 | 623.125 | 1322880.475 | 11302.125 | 0
2021080906 | 2 | 0.54884 | 82326 | 0.08869 | 0 | 0.37207 | 4650.875 | 0.00135 | 108 | 64000 | 4650.875 | 108 | 13567.125 | 2265 | 1334779.6 | 13567.125 | 0
2021080907 | 2 | 0.5782 | 86730 | 0.06587 | 0 | 0.43124 | 5390.5 | 0.06811 | 5448.8 | 64000 | 5390.5 | 5448.8 | 11890.7 | -1676.425 | 1348355.15 | 11890.7 | 0
2021080908 | 2 | 0.61363 | 92044.5 | 0.06828 | 0 | 0.54422 | 6802.75 | 0.25045 | 20036 | 64000 | 6802.75 | 20036 | 1205.75 | -10684.95 | 1350000 | 1205.75 | 0
2021080909 | 2 | 0.65606 | 98409 | 0.03993 | 0 | 0.55953 | 6994.125 | 0.41368 | 33094.4 | 64000 | 6994.125 | 27414.875 | 0 | -1205.75 | 1350000 | 0 | 0
2021080910 | 2 | 0.70051 | 105076.5 | 0.01014 | 0 | 0.57142 | 7142.75 | 0.50148 | 40118.4 | 64000 | 7142.75 | 33933.75 | 0 | 0 | 1350000 | 0 | 0
2021080911 | 2 | 0.74883 | 112324.5 | 0.00503 | 0 | 0.56809 | 7101.125 | 0.56102 | 44881.6 | 64000 | 7101.125 | 41223.375 | 0 | 0 | 1350000 | 0 | 0
2021080912 | 2 | 0.79416 | 119124 | 0.00669 | 0 | 0.57703 | 7212.875 | 0.55506 | 44404.8 | 64000 | 7212.875 | 44404.8 | 3506.325 | 3506.325 | 1350000 | 3506.325 | 0
2021080913 | 2 | 0.83514 | 125271 | 0.00428 | 0 | 0.55619 | 6952.375 | 0.51987 | 41589.6 | 64000 | 6952.375 | 41589.6 | 12729.025 | 9222.7 | 1350000 | 12729.025 | 0
2021080914 | 2 | 0.86434 | 129651 | 0.01793 | 0 | 0.50682 | 6335.25 | 0.48996 | 39196.8 | 64000 | 6335.25 | 39196.8 | 20118.95 | 7389.925 | 1350000 | 20118.95 | 0
2021080915 | 2 | 0.88222 | 132333 | 0.04112 | 0 | 0.41535 | 5191.875 | 0.4378 | 35024 | 64000 | 5191.875 | 35024 | 28117.125 | 7998.175 | 1347349.125 | 28117.125 | 0
2021080916 | 2 | 0.89206 | 133809 | 0.05381 | 0 | 0.29478 | 3684.75 | 0.36229 | 28983.2 | 64000 | 3684.75 | 28983.2 | 37141.05 | 9023.925 | 1335674.325 | 37141.05 | 0
2021080917 | 2 | 0.89393 | 134089.5 | 0.0666 | 0 | 0.22051 | 2756.375 | 0.25065 | 20052 | 64000 | 2756.375 | 20052 | 47281.125 | 10140.075 | 1313859.45 | 47281.125 | 0
2021080918 | 2 | 0.89072 | 133608 | 0.08538 | 0 | 0.21506 | 2688.25 | 0.15535 | 12428 | 64000 | 2688.25 | 12428 | 54491.75 | 7210.625 | 1284833.95 | 54491.75 | 0
2021080919 | 2 | 0.86649 | 129973.5 | 0.11311 | 0 | 0.27705 | 3463.125 | 0.06984 | 5587.2 | 64000 | 3463.125 | 5587.2 | 56923.175 | 2431.425 | 1253377.025 | 56923.175 | 0
2021080920 | 2 | 0.83453 | 125179.5 | 0.16306 | 0 | 0.28911 | 3613.875 | 0.01504 | 1203.2 | 64000 | 3613.875 | 1203.2 | 56362.425 | -560.75 | 1222480.85 | 56362.425 | 0
2021080921 | 2 | 0.80962 | 121443 | 0.27191 | 0 | 0.27913 | 3489.125 | 0 | 0 | 64000 | 3489.125 | 0 | 53953.875 | -2408.55 | 1193993.225 | 53953.875 | 0
2021080922 | 2 | 0.77843 | 116764.5 | 0.32822 | 0 | 0.27748 | 3468.5 | 0 | 0 | 64000 | 3468.5 | 0 | 49296 | -4657.875 | 1170163.475 | 49296 | 0
2021080923 | 2 | 0.72796 | 109194 | 0.36103 | 0 | 0.28287 | 3535.875 | 0 | 0 | 64000 | 3535.875 | 0 | 41658.125 | -7637.875 | 1153971.6 | 41658.125 | 0
2021080924 | 2 | 0.677 | 101550 | 0.45164 | 0 | 0.29559 | 3694.875 | 0 | 0 | 64000 | 3694.875 | 0 | 33855.125 | -7803 | 1145582.725 | 33855.125 | 0
2021081001 | 3 | 0.63267 | 94900.5 | 0.50385 | 0 | 0.28701 | 3587.625 | 0 | 0 | 64000 | 3587.625 | 0 | 27312.875 | -6542.25 | 1143736.1 | 27312.875 | 0
2021081002 | 3 | 0.60107 | 90160.5 | 0.44438 | 0 | 0.27598 | 3449.75 | 0 | 0 | 64000 | 3449.75 | 0 | 22710.75 | -4602.125 | 1146491.6 | 22710.75 | 0
2021081003 | 3 | 0.57833 | 86749.5 | 0.48803 | 0 | 0.2815 | 3518.75 | 0 | 0 | 64000 | 3518.75 | 0 | 19230.75 | -3480 | 1152727.1 | 19230.75 | 0
2021081004 | 3 | 0.56547 | 84820.5 | 0.45912 | 0 | 0.26944 | 3368 | 0 | 0 | 64000 | 3368 | 0 | 17452.5 | -1778.25 | 1160740.85 | 17452.5 | 0
2021081005 | 3 | 0.56551 | 84826.5 | 0.42075 | 0 | 0.25195 | 3149.375 | 0 | 0 | 64000 | 3149.375 | 0 | 17677.125 | 224.625 | 1168529.975 | 17677.125 | 0
2021081006 | 3 | 0.58296 | 87444 | 0.39147 | 0 | 0.24568 | 3071 | 0.00025 | 20 | 64000 | 3071 | 20 | 20353 | 2675.875 | 1173643.225 | 20353 | 0
2021081007 | 3 | 0.61591 | 92386.5 | 0.40264 | 0 | 0.27631 | 3453.875 | 0.03314 | 2651.2 | 64000 | 3453.875 | 2651.2 | 22281.425 | 1928.425 | 1176828.05 | 22281.425 | 0
2021081008 | 3 | 0.64893 | 97339.5 | 0.42398 | 0 | 0.27336 | 3417 | 0.14914 | 11931.2 | 64000 | 3417 | 11931.2 | 17991.3 | -4290.125 | 1184303 | 17991.3 | 0
2021081009 | 3 | 0.68684 | 103026 | 0.40587 | 0 | 0.23489 | 2936.125 | 0.25944 | 20755.2 | 64000 | 2936.125 | 20755.2 | 15334.675 | -2656.625 | 1194434.575 | 15334.675 | 0
2021081010 | 3 | 0.72521 | 108781.5 | 0.34611 | 0 | 0.21906 | 2738.25 | 0.30092 | 24073.6 | 64000 | 2738.25 | 24073.6 | 17969.65 | 2634.975 | 1201931.175 | 17969.65 | 0
2021081011 | 3 | 0.7723 | 115845 | 0.35154 | 0 | 0.23489 | 2936.125 | 0.37588 | 30070.4 | 64000 | 2936.125 | 30070.4 | 18838.475 | 868.825 | 1208558.95 | 18838.475 | 0
2021081012 | 3 | 0.81797 | 122695.5 | 0.438 | 0 | 0.17514 | 2189.25 | 0.43353 | 34682.4 | 64000 | 2189.25 | 34682.4 | 21823.85 | 2985.375 | 1212201.35 | 21823.85 | 0
2021081013 | 3 | 0.86164 | 129246 | 0.44962 | 0 | 0.15174 | 1896.75 | 0.45311 | 36248.8 | 64000 | 1896.75 | 36248.8 | 27100.45 | 5276.6 | 1210567.15 | 27100.45 | 0
2021081014 | 3 | 0.89761 | 134641.5 | 0.51172 | 0 | 0.11146 | 1393.25 | 0.47176 | 37740.8 | 64000 | 1393.25 | 37740.8 | 31507.45 | 4407 | 1204525.95 | 31507.45 | 0
2021081015 | 3 | 0.92098 | 138147 | 0.56812 | 0 | 0.08582 | 1072.75 | 0.47807 | 38245.6 | 64000 | 1072.75 | 38245.6 | 34828.65 | 3321.2 | 1195163.55 | 34828.65 | 0
2021081016 | 3 | 0.93519 | 140278.5 | 0.65844 | 0 | 0.04783 | 597.875 | 0.41643 | 33314.4 | 64000 | 597.875 | 33314.4 | 42366.225 | 7537.575 | 1178263.575 | 42366.225 | 0
2021081017 | 3 | 0.94177 | 141265.5 | 0.52496 | 0 | 0.03831 | 478.875 | 0.35281 | 28224.8 | 64000 | 478.875 | 28224.8 | 48561.825 | 6195.6 | 1155168 | 48561.825 | 0
2021081018 | 3 | 0.93642 | 140463 | 0.35041 | 0 | 0.04729 | 591.125 | 0.24225 | 19380 | 64000 | 591.125 | 19380 | 56491.875 | 7930.05 | 1124142.375 | 56491.875 | 0
2021081019 | 3 | 0.91625 | 137437.5 | 0.39406 | 0 | 0.05056 | 632 | 0.16289 | 13031.2 | 64000 | 632 | 13031.2 | 59774.3 | 3282.425 | 1089834.325 | 59774.3 | 0
2021081020 | 3 | 0.8816 | 132240 | 0.39959 | 0 | 0.04903 | 612.875 | 0.03312 | 2649.6 | 64000 | 612.875 | 2649.6 | 64977.525 | 5203.225 | 1050323.05 | 64977.525 | 0
2021081021 | 3 | 0.84254 | 126381 | 0.50127 | 0 | 0.04006 | 500.75 | 0 | 0 | 64000 | 500.75 | 0 | 61880.25 | -3097.275 | 1013909.05 | 61880.25 | 0
2021081022 | 3 | 0.79877 | 119815.5 | 0.53463 | 0 | 0.03674 | 459.25 | 0 | 0 | 64000 | 459.25 | 0 | 55356.25 | -6524 | 984019.05 | 55356.25 | 0
2021081023 | 3 | 0.74569 | 111853.5 | 0.62274 | 0 | 0.04191 | 523.875 | 0 | 0 | 64000 | 523.875 | 0 | 47329.625 | -8026.625 | 962155.675 | 47329.625 | 0
2021081024 | 3 | 0.69102 | 103653 | 0.72326 | 0 | 0.04356 | 544.5 | 0 | 0 | 64000 | 544.5 | 0 | 39108.5 | -8221.125 | 948513.425 | 39108.5 | 0
2021081101 | 4 | 0.64687 | 97030.5 | 0.80972 | 0 | 0.06067 | 758.375 | 0 | 0 | 64000 | 758.375 | 0 | 32272.125 | -6836.375 | 941707.55 | 32272.125 | 0
2021081102 | 4 | 0.61234 | 91851 | 0.81767 | 0 | 0.07711 | 963.875 | 0 | 0 | 64000 | 963.875 | 0 | 26887.125 | -5385 | 940286.675 | 26887.125 | 0
2021081103 | 4 | 0.58988 | 88482 | 0.78036 | 0 | 0.08454 | 1056.75 | 0 | 0 | 64000 | 1056.75 | 0 | 23425.25 | -3461.875 | 942327.675 | 23425.25 | 0
2021081104 | 4 | 0.57604 | 86406 | 0.68765 | 0 | 0.09302 | 1162.75 | 0 | 0 | 64000 | 1162.75 | 0 | 21243.25 | -2182 | 946550.675 | 21243.25 | 0
2021081105 | 4 | 0.57506 | 86259 | 0.63699 | 0 | 0.09726 | 1215.75 | 0 | 0 | 64000 | 1215.75 | 0 | 21043.25 | -200 | 950973.675 | 21043.25 | 0
2021081106 | 4 | 0.59338 | 89007 | 0.60577 | 0 | 0.12811 | 1601.375 | 0.00043 | 34.4 | 64000 | 1601.375 | 34.4 | 23371.225 | 2327.975 | 953068.7 | 23371.225 | 0
2021081107 | 4 | 0.62587 | 93880.5 | 0.63722 | 0 | 0.17021 | 2127.625 | 0.06819 | 5455.2 | 64000 | 2127.625 | 5455.2 | 22297.675 | -1073.55 | 956237.275 | 22297.675 | 0
2021081108 | 4 | 0.66165 | 99247.5 | 0.61988 | 0 | 0.20161 | 2520.125 | 0.28605 | 22884 | 64000 | 2520.125 | 22884 | 9843.375 | -12454.3 | 971860.15 | 9843.375 | 0
2021081109 | 4 | 0.70499 | 105748.5 | 0.44188 | 0 | 0.22367 | 2795.875 | 0.47564 | 38051.2 | 64000 | 2795.875 | 38051.2 | 901.425 | -8941.95 | 996424.975 | 901.425 | 0
2021081110 | 4 | 0.75163 | 112744.5 | 0.30408 | 0 | 0.25137 | 3142.125 | 0.54578 | 43662.4 | 64000 | 3142.125 | 43662.4 | 1939.975 | 1038.55 | 1019951.25 | 1939.975 | 0
2021081111 | 4 | 0.80044 | 120066 | 0.37475 | 0 | 0.24484 | 3060.5 | 0.59875 | 47900 | 64000 | 3060.5 | 47900 | 5105.5 | 3165.525 | 1040312 | 5105.5 | 0
2021081112 | 4 | 0.84093 | 126139.5 | 0.33156 | 0 | 0.23248 | 2906 | 0.60918 | 48734.4 | 64000 | 2906 | 48734.4 | 10499.1 | 5393.6 | 1055279.15 | 10499.1 | 0
2021081113 | 4 | 0.87523 | 131284.5 | 0.42215 | 0 | 0.24888 | 3111 | 0.62348 | 49878.4 | 64000 | 3111 | 49878.4 | 14295.1 | 3796 | 1066450.3 | 14295.1 | 0
2021081114 | 4 | 0.90753 | 136129.5 | 0.38007 | 0 | 0.24705 | 3088.125 | 0.65395 | 52316 | 64000 | 3088.125 | 52316 | 16725.375 | 2430.275 | 1075191.175 | 16725.375 | 0
2021081115 | 4 | 0.92912 | 139368 | 0.54934 | 0 | 0.21627 | 2703.375 | 0.6384 | 51072 | 64000 | 2703.375 | 51072 | 21592.625 | 4867.25 | 1079064.8 | 21592.625 | 0
2021081116 | 4 | 0.94564 | 141846 | 0.67303 | 0 | 0.14459 | 1807.375 | 0.58403 | 46722.4 | 64000 | 1807.375 | 46722.4 | 29316.225 | 7723.6 | 1075214.825 | 29316.225 | 0
2021081117 | 4 | 0.94849 | 142273.5 | 0.47722 | 0 | 0.10817 | 1352.125 | 0.45076 | 36060.8 | 64000 | 1352.125 | 36060.8 | 40860.575 | 11544.35 | 1059820.5 | 40860.575 | 0
2021081118 | 4 | 0.93659 | 140488.5 | 0.42775 | 0 | 0.12357 | 1544.625 | 0.32218 | 25774.4 | 64000 | 1544.625 | 25774.4 | 49169.475 | 8308.9 | 1036117.275 | 49169.475 | 0
2021081119 | 4 | 0.91618 | 137427 | 0.55252 | 0 | 0.18211 | 2276.375 | 0.14492 | 11593.6 | 64000 | 2276.375 | 11593.6 | 59557.025 | 10387.55 | 1002026.5 | 59557.025 | 0
2021081120 | 4 | 0.88317 | 132475.5 | 0.50001 | 0 | 0.24467 | 3058.375 | 0.02421 | 1936.8 | 64000 | 3058.375 | 1936.8 | 63480.325 | 3923.3 | 964012.425 | 63480.325 | 0
2021081121 | 4 | 0.84803 | 127204.5 | 0.5942 | 0 | 0.308 | 3850 | 0 | 0 | 64000 | 3850 | 0 | 59354.5 | -4125.825 | 930124.175 | 59354.5 | 0
2021081122 | 4 | 0.81386 | 122079 | 0.71783 | 0 | 0.3438 | 4297.5 | 0 | 0 | 64000 | 4297.5 | 0 | 53781.5 | -5573 | 901808.925 | 53781.5 | 0
2021081123 | 4 | 0.76151 | 114226.5 | 0.69884 | 0 | 0.35176 | 4397 | 0 | 0 | 64000 | 4397 | 0 | 45829.5 | -7952 | 881445.675 | 45829.5 | 0
2021081124 | 4 | 0.70922 | 106383 | 0.58103 | 0 | 0.32695 | 4086.875 | 0 | 0 | 64000 | 4086.875 | 0 | 38296.125 | -7533.375 | 868615.8 | 38296.125 | 0
2021081201 | 5 | 0.66456 | 99684 | 0.67265 | 0 | 0.31956 | 3994.5 | 0 | 0 | 64000 | 3994.5 | 0 | 31689.5 | -6606.625 | 862392.55 | 31689.5 | 0
2021081202 | 5 | 0.63061 | 94591.5 | 0.76573 | 0 | 0.31453 | 3931.625 | 0 | 0 | 64000 | 3931.625 | 0 | 26659.875 | -5029.625 | 861198.925 | 26659.875 | 0
2021081203 | 5 | 0.60725 | 91087.5 | 0.78457 | 0 | 0.27174 | 3396.75 | 0 | 0 | 64000 | 3396.75 | 0 | 23690.75 | -2969.125 | 862974.425 | 23690.75 | 0
2021081204 | 5 | 0.59174 | 88761 | 0.76533 | 0 | 0.22904 | 2863 | 0 | 0 | 64000 | 2863 | 0 | 21898 | -1792.75 | 866542.675 | 21898 | 0
2021081205 | 5 | 0.58713 | 88069.5 | 0.76613 | 0 | 0.20319 | 2539.875 | 0 | 0 | 64000 | 2539.875 | 0 | 21529.625 | -368.375 | 870479.3 | 21529.625 | 0
2021081206 | 5 | 0.60246 | 90369 | 0.78118 | 0 | 0.20283 | 2535.375 | 0.00171 | 136.8 | 64000 | 2535.375 | 136.8 | 23696.825 | 2167.2 | 872248.725 | 23696.825 | 0
2021081207 | 5 | 0.6294 | 94410 | 0.77649 | 0 | 0.23428 | 2928.5 | 0.05632 | 4505.6 | 64000 | 2928.5 | 4505.6 | 22975.9 | -720.925 | 874739.075 | 22975.9 | 0
2021081208 | 5 | 0.66423 | 99634.5 | 0.73883 | 0 | 0.23082 | 2885.25 | 0.17526 | 14020.8 | 64000 | 2885.25 | 14020.8 | 18728.45 | -4247.45 | 881476.875 | 18728.45 | 0
2021081209 | 5 | 0.70752 | 106128 | 0.59835 | 0 | 0.23692 | 2961.5 | 0.28961 | 23168.8 | 64000 | 2961.5 | 23168.8 | 15997.7 | -2730.75 | 890945.425 | 15997.7 | 0
2021081210 | 5 | 0.75517 | 113275.5 | 0.48873 | 0 | 0.20973 | 2621.625 | 0.43191 | 34552.8 | 64000 | 2621.625 | 34552.8 | 12101.075 | -3896.625 | 904310.6 | 12101.075 | 0
2021081211 | 5 | 0.81015 | 121522.5 | 0.53158 | 0 | 0.18628 | 2328.5 | 0.50591 | 40472.8 | 64000 | 2328.5 | 40472.8 | 14721.2 | 2620.125 | 915055.65 | 14721.2 | 0
2021081212 | 5 | 0.86412 | 129618 | 0.54932 | 0 | 0.17669 | 2208.625 | 0.5799 | 46392 | 64000 | 2208.625 | 46392 | 17017.375 | 2296.175 | 923504.525 | 17017.375 | 0
2021081213 | 5 | 0.91481 | 137221.5 | 0.48085 | 0 | 0.1495 | 1868.75 | 0.6236 | 49888 | 64000 | 1868.75 | 49888 | 21464.75 | 4447.375 | 927506.025 | 21464.75 | 0
2021081214 | 5 | 0.95724 | 143586 | 0.41661 | 0 | 0.12044 | 1505.5 | 0.62605 | 50084 | 64000 | 1505.5 | 50084 | 27996.5 | 6531.75 | 924975.775 | 27996.5 | 0
2021081215 | 5 | 0.98075 | 147112.5 | 0.4063 | 0 | 0.11038 | 1379.75 | 0.62712 | 50169.6 | 64000 | 1379.75 | 50169.6 | 31563.15 | 3566.65 | 918878.875 | 31563.15 | 0
2021081216 | 5 | 0.99242 | 148863 | 0.32484 | 0 | 0.10083 | 1260.375 | 0.59588 | 47670.4 | 64000 | 1260.375 | 47670.4 | 35932.225 | 4369.075 | 908412.9 | 35932.225 | 0
2021081217 | 5 | 0.99627 | 149440.5 | 0.25702 | 0 | 0.09939 | 1242.375 | 0.53687 | 42949.6 | 64000 | 1242.375 | 42949.6 | 41248.525 | 5316.3 | 892630.625 | 41248.525 | 0
2021081218 | 5 | 0.98956 | 148434 | 0.28334 | 0 | 0.14342 | 1792.75 | 0.43038 | 34430.4 | 64000 | 1792.75 | 34430.4 | 48210.85 | 6962.325 | 869886.025 | 48210.85 | 0
2021081219 | 5 | 0.9757 | 146355 | 0.33874 | 0 | 0.17072 | 2134 | 0.23956 | 19164.8 | 64000 | 2134 | 19164.8 | 61056.2 | 12845.35 | 834296.075 | 61056.2 | 0
2021081220 | 5 | 0.9422 | 141330 | 0.38513 | 0 | 0.17798 | 2224.75 | 0.05096 | 4076.8 | 64000 | 2224.75 | 4076.8 | 71028.45 | 9972.25 | 788733.875 | 71028.45 | 0
2021081221 | 5 | 0.91061 | 136591.5 | 0.58687 | 0 | 0.16937 | 2117.125 | 0 | 0 | 64000 | 2117.125 | 0 | 70474.375 | -554.075 | 743725.75 | 70474.375 | 0
2021081222 | 5 | 0.8706 | 130590 | 0.62444 | 0 | 0.17979 | 2247.375 | 0 | 0 | 64000 | 2247.375 | 0 | 64342.625 | -6131.75 | 704849.375 | 64342.625 | 0
2021081223 | 5 | 0.8109 | 121635 | 0.69417 | 0 | 0.20177 | 2522.125 | 0 | 0 | 64000 | 2522.125 | 0 | 55112.875 | -9229.75 | 675202.75 | 55112.875 | 0
2021081224 | 5 | 0.75405 | 113107.5 | 0.67566 | 0 | 0.20583 | 2572.875 | 0 | 0 | 64000 | 2572.875 | 0 | 46534.625 | -8578.25 | 654134.375 | 46534.625 | 0
2021081301 | 6 | 0.70385 | 105577.5 | 0.60903 | 0 | 0.20935 | 2616.875 | 0 | 0 | 64000 | 2616.875 | 0 | 38960.625 | -7574 | 640640 | 38960.625 | 0
2021081302 | 6 | 0.66415 | 99622.5 | 0.6289 | 0 | 0.17737 | 2217.125 | 0 | 0 | 64000 | 2217.125 | 0 | 33405.375 | -5555.25 | 632700.875 | 33405.375 | 0
2021081303 | 6 | 0.63395 | 95092.5 | 0.63725 | 0 | 0.13753 | 1719.125 | 0 | 0 | 64000 | 1719.125 | 0 | 29373.375 | -4032 | 628793.75 | 29373.375 | 0
2021081304 | 6 | 0.61329 | 91993.5 | 0.62421 | 0 | 0.12711 | 1588.875 | 0 | 0 | 64000 | 1588.875 | 0 | 26404.625 | -2968.75 | 627855.375 | 26404.625 | 0
2021081305 | 6 | 0.60564 | 90846 | 0.48904 | 0 | 0.14266 | 1783.25 | 0 | 0 | 64000 | 1783.25 | 0 | 25062.75 | -1341.875 | 628258.875 | 25062.75 | 0
2021081306 | 6 | 0.61593 | 92389.5 | 0.42261 | 0 | 0.14911 | 1863.875 | 0.00121 | 96.8 | 64000 | 1863.875 | 96.8 | 26428.825 | 1366.075 | 627296.3 | 26428.825 | 0
2021081307 | 6 | 0.63981 | 95971.5 | 0.49118 | 0 | 0.1546 | 1932.5 | 0.09862 | 7889.6 | 64000 | 1932.5 | 7889.6 | 22149.4 | -4279.425 | 630613.15 | 22149.4 | 0
2021081308 | 6 | 0.66981 | 100471.5 | 0.48001 | 0 | 0.16853 | 2106.625 | 0.37173 | 29738.4 | 64000 | 2106.625 | 29738.4 | 4626.475 | -17522.925 | 651452.925 | 4626.475 | 0
2021081309 | 6 | 0.71397 | 107095.5 | 0.3713 | 0 | 0.16906 | 2113.25 | 0.56561 | 45248.8 | 64000 | 2113.25 | 40982.25 | 0 | -4626.475 | 676919.175 | 0 | 0
2021081310 | 6 | 0.76238 | 114357 | 0.27424 | 0 | 0.19031 | 2378.875 | 0.63636 | 50908.8 | 64000 | 2378.875 | 47978.125 | 0 | 0 | 702385.425 | 0 | 0
2021081311 | 6 | 0.81168 | 121752 | 0.19643 | 0 | 0.22854 | 2856.75 | 0.69053 | 55242.4 | 64000 | 2856.75 | 54895.25 | 0 | 0 | 727851.675 | 0 | 0
2021081312 | 6 | 0.86102 | 129153 | 0.18476 | 0 | 0.28384 | 3548 | 0.71633 | 57306.4 | 64000 | 3548 | 57306.4 | 4298.6 | 4298.6 | 749019.325 | 4298.6 | 0
2021081313 | 6 | 0.90304 | 135456 | 0.19318 | 0 | 0.33648 | 4206 | 0.72538 | 58030.4 | 64000 | 4206 | 58030.4 | 9219.6 | 4921 | 765265.975 | 9219.6 | 0
2021081314 | 6 | 0.93447 | 140170.5 | 0.23624 | 0 | 0.38736 | 4842 | 0.72395 | 57916 | 64000 | 4842 | 57916 | 13412.5 | 4192.9 | 777319.725 | 13412.5 | 0
2021081315 | 6 | 0.94843 | 142264.5 | 0.26177 | 0 | 0.41345 | 5168.125 | 0.70969 | 56775.2 | 64000 | 5168.125 | 56775.2 | 16321.175 | 2908.675 | 786464.8 | 16321.175 | 0
2021081316 | 6 | 0.95344 | 143016 | 0.26239 | 0 | 0.39003 | 4875.375 | 0.69193 | 55354.4 | 64000 | 4875.375 | 55354.4 | 18786.225 | 2465.05 | 793144.825 | 18786.225 | 0
2021081317 | 6 | 0.95079 | 142618.5 | 0.18443 | 0 | 0.32497 | 4062.125 | 0.6507 | 52056 | 64000 | 4062.125 | 52056 | 22500.375 | 3714.15 | 796110.7 | 22500.375 | 0
2021081318 | 6 | 0.93658 | 140487 | 0.15666 | 0 | 0.31394 | 3924.25 | 0.56244 | 44995.2 | 64000 | 3924.25 | 44995.2 | 27567.55 | 5067.175 | 794009.4 | 27567.55 | 0
2021081319 | 6 | 0.90347 | 135520.5 | 0.2172 | 0 | 0.37134 | 4641.75 | 0.31677 | 25341.6 | 64000 | 4641.75 | 25341.6 | 41537.15 | 13969.6 | 777938.5 | 41537.15 | 0
2021081320 | 6 | 0.8632 | 129480 | 0.18801 | 0 | 0.39501 | 4937.625 | 0.05407 | 4325.6 | 64000 | 4937.625 | 4325.6 | 56216.775 | 14679.625 | 747187.975 | 56216.775 | 0
2021081321 | 6 | 0.82902 | 124353 | 0.2912 | 0 | 0.43574 | 5446.75 | 0 | 0 | 64000 | 5446.75 | 0 | 54906.25 | -1310.525 | 717747.975 | 54906.25 | 0
2021081322 | 6 | 0.79119 | 118678.5 | 0.34152 | 0 | 0.46155 | 5769.375 | 0 | 0 | 64000 | 5769.375 | 0 | 48909.125 | -5997.125 | 694305.1 | 48909.125 | 0
2021081323 | 6 | 0.74079 | 111118.5 | 0.45404 | 0 | 0.48785 | 6098.125 | 0 | 0 | 64000 | 6098.125 | 0 | 41020.375 | -7888.75 | 678750.975 | 41020.375 | 0
2021081324 | 6 | 0.68743 | 103114.5 | 0.42535 | 0 | 0.50085 | 6260.625 | 0 | 0 | 64000 | 6260.625 | 0 | 32853.875 | -8166.5 | 671363.35 | 32853.875 | 0
2021081401 | 7 | 0.6408 | 96120 | 0.45676 | 0 | 0.50064 | 6258 | 0 | 0 | 64000 | 6258 | 0 | 25862 | -6991.875 | 670967.6 | 25862 | 0
2021081402 | 7 | 0.60564 | 90846 | 0.53784 | 0 | 0.472 | 5900 | 0 | 0 | 64000 | 5900 | 0 | 20946 | -4916 | 675487.85 | 20946 | 0
2021081403 | 7 | 0.5785 | 86775 | 0.50131 | 0 | 0.43955 | 5494.375 | 0 | 0 | 64000 | 5494.375 | 0 | 17280.625 | -3665.375 | 683673.475 | 17280.625 | 0
2021081404 | 7 | 0.56102 | 84153 | 0.52667 | 0 | 0.38351 | 4793.875 | 0 | 0 | 64000 | 4793.875 | 0 | 15359.125 | -1921.5 | 693780.6 | 15359.125 | 0
2021081405 | 7 | 0.55044 | 82566 | 0.47808 | 0 | 0.31684 | 3960.5 | 0 | 0 | 64000 | 3960.5 | 0 | 14605.5 | -753.625 | 704641.35 | 14605.5 | 0
2021081406 | 7 | 0.55131 | 82696.5 | 0.41807 | 0 | 0.29995 | 3749.375 | 0.00164 | 131.2 | 64000 | 3749.375 | 131.2 | 14815.925 | 210.425 | 715291.675 | 14815.925 | 0
2021081407 | 7 | 0.55551 | 83326.5 | 0.30091 | 0 | 0.33973 | 4246.625 | 0.07548 | 6038.4 | 64000 | 4246.625 | 6038.4 | 9041.475 | -5774.45 | 731716.45 | 9041.475 | 0
2021081408 | 7 | 0.57104 | 85656 | 0.27858 | 0 | 0.39264 | 4908 | 0.28909 | 23127.2 | 64000 | 4908 | 16748 | 0 | -9041.475 | 757182.7 | 0 | 0
2021081409 | 7 | 0.6094 | 91410 | 0.24588 | 0 | 0.41265 | 5158.125 | 0.4824 | 38592 | 64000 | 5158.125 | 22251.875 | 0 | 0 | 782648.95 | 0 | 0
2021081410 | 7 | 0.6548 | 98220 | 0.21141 | 0 | 0.4174 | 5217.5 | 0.59006 | 47204.8 | 64000 | 5217.5 | 29002.5 | 0 | 0 | 808115.2 | 0 | 0
2021081411 | 7 | 0.69938 | 104907 | 0.22106 | 0 | 0.41046 | 5130.75 | 0.63434 | 50747.2 | 64000 | 5130.75 | 35776.25 | 0 | 0 | 833581.45 | 0 | 0
2021081412 | 7 | 0.73844 | 110766 | 0.16692 | 0 | 0.39619 | 4952.375 | 0.67855 | 54284 | 64000 | 4952.375 | 41813.625 | 0 | 0 | 859047.7 | 0 | 0
2021081413 | 7 | 0.7698 | 115470 | 0.13529 | 0 | 0.39777 | 4972.125 | 0.69939 | 55951.2 | 64000 | 4972.125 | 46497.875 | 0 | 0 | 884513.95 | 0 | 0
2021081414 | 7 | 0.7919 | 118785 | 0.12216 | 0 | 0.39995 | 4999.375 | 0.7012 | 56096 | 64000 | 4999.375 | 49785.625 | 0 | 0 | 909980.2 | 0 | 0
2021081415 | 7 | 0.80774 | 121161 | 0.11511 | 0 | 0.40359 | 5044.875 | 0.67775 | 54220 | 64000 | 5044.875 | 52116.125 | 0 | 0 | 935446.45 | 0 | 0
2021081416 | 7 | 0.82323 | 123484.5 | 0.12175 | 0 | 0.38966 | 4870.75 | 0.64178 | 51342.4 | 64000 | 4870.75 | 51342.4 | 3271.35 | 3271.35 | 957641.35 | 3271.35 | 0
2021081417 | 7 | 0.83627 | 125440.5 | 0.20352 | 0 | 0.34722 | 4340.25 | 0.60595 | 48476 | 64000 | 4340.25 | 48476 | 8624.25 | 5352.9 | 974483.35 | 8624.25 | 0
2021081418 | 7 | 0.8314 | 124710 | 0.20914 | 0 | 0.34981 | 4372.625 | 0.5056 | 40448 | 64000 | 4372.625 | 40448 | 15889.375 | 7265.125 | 984060.225 | 15889.375 | 0
2021081419 | 7 | 0.81003 | 121504.5 | 0.16318 | 0 | 0.39153 | 4894.125 | 0.27273 | 21818.4 | 64000 | 4894.125 | 21818.4 | 30791.975 | 14902.6 | 978734.5 | 30791.975 | 0
2021081420 | 7 | 0.77572 | 116358 | 0.17299 | 0 | 0.40568 | 5071 | 0.04197 | 3357.6 | 64000 | 5071 | 3357.6 | 43929.4 | 13137.425 | 960271.35 | 43929.4 | 0
2021081421 | 7 | 0.74407 | 111610.5 | 0.17184 | 0 | 0.39023 | 4877.875 | 0 | 0 | 64000 | 4877.875 | 0 | 42732.625 | -1196.775 | 943004.975 | 42732.625 | 0
2021081422 | 7 | 0.71343 | 107014.5 | 0.1505 | 0 | 0.38084 | 4760.5 | 0 | 0 | 64000 | 4760.5 | 0 | 38254 | -4478.625 | 930217.225 | 38254 | 0
2021081423 | 7 | 0.66887 | 100330.5 | 0.1561 | 0 | 0.37067 | 4633.375 | 0 | 0 | 64000 | 4633.375 | 0 | 31697.125 | -6556.875 | 923986.35 | 31697.125 | 0
2021081424 | 7 | 0.62249 | 93373.5 | 0.18982 | 0 | 0.33436 | 4179.5 | 0 | 0 | 64000 | 4179.5 | 0 | 25194 | -6503.125 | 924258.6 | 25194 | 0
2021081501 | 1 | 0.57901 | 86851.5 | 0.24837 | 0 | 0.3314 | 4142.5 | 0 | 0 | 64000 | 4142.5 | 0 | 18709 | -6485 | 931015.85 | 18709 | 0
2021081502 | 1 | 0.54565 | 81847.5 | 0.25942 | 0 | 0.3369 | 4211.25 | 0 | 0 | 64000 | 4211.25 | 0 | 13636.25 | -5072.75 | 942845.85 | 13636.25 | 0
2021081503 | 1 | 0.52076 | 78114 | 0.27932 | 0 | 0.32836 | 4104.5 | 0 | 0 | 64000 | 4104.5 | 0 | 10009.5 | -3626.75 | 958302.6 | 10009.5 | 0
2021081504 | 1 | 0.50428 | 75642 | 0.2602 | 0 | 0.32846 | 4105.75 | 0 | 0 | 64000 | 4105.75 | 0 | 7536.25 | -2473.25 | 976232.6 | 7536.25 | 0
2021081505 | 1 | 0.49285 | 73927.5 | 0.26771 | 0 | 0.30353 | 3794.125 | 0 | 0 | 64000 | 3794.125 | 0 | 6133.375 | -1402.875 | 995565.475 | 6133.375 | 0
2021081506 | 1 | 0.4876 | 73140 | 0.30229 | 0 | 0.27587 | 3448.375 | 0.00107 | 85.6 | 64000 | 3448.375 | 85.6 | 5606.025 | -527.35 | 1015425.7 | 5606.025 | 0
2021081507 | 1 | 0.48616 | 72924 | 0.36391 | 0 | 0.26226 | 3278.25 | 0.091 | 7280 | 64000 | 3278.25 | 5645.75 | 0 | -5606.025 | 1040891.95 | 0 | 0
2021081508 | 1 | 0.49458 | 74187 | 0.36503 | 0 | 0.27172 | 3396.5 | 0.344 | 27520 | 64000 | 3396.5 | 6790.5 | 0 | 0 | 1066358.2 | 0 | 0
2021081509 | 1 | 0.51871 | 77806.5 | 0.30696 | 0 | 0.28979 | 3622.375 | 0.5576 | 44608 | 64000 | 3622.375 | 10184.125 | 0 | 0 | 1091824.45 | 0 | 0
2021081510 | 1 | 0.54701 | 82051.5 | 0.2833 | 0 | 0.36194 | 4524.25 | 0.62298 | 49838.4 | 64000 | 4524.25 | 13527.25 | 0 | 0 | 1117290.7 | 0 | 0
2021081511 | 1 | 0.57736 | 86604 | 0.21827 | 0 | 0.42987 | 5373.375 | 0.66867 | 53493.6 | 64000 | 5373.375 | 17230.625 | 0 | 0 | 1142756.95 | 0 | 0
2021081512 | 1 | 0.60691 | 91036.5 | 0.20403 | 0 | 0.44194 | 5524.25 | 0.69166 | 55332.8 | 64000 | 5524.25 | 21512.25 | 0 | 0 | 1168223.2 | 0 | 0
2021081513 | 1 | 0.63387 | 95080.5 | 0.16934 | 0 | 0.46704 | 5838 | 0.69924 | 55939.2 | 64000 | 5838 | 25242.5 | 0 | 0 | 1193689.45 | 0 | 0
2021081514 | 1 | 0.65742 | 98613 | 0.11358 | 0 | 0.46485 | 5810.625 | 0.68532 | 54825.6 | 64000 | 5810.625 | 28802.375 | 0 | 0 | 1219155.7 | 0 | 0
2021081515 | 1 | 0.6793 | 101895 | 0.04687 | 0 | 0.45771 | 5721.375 | 0.67952 | 54361.6 | 64000 | 5721.375 | 32173.625 | 0 | 0 | 1244621.95 | 0 | 0
2021081516 | 1 | 0.69997 | 104995.5 | 0.02621 | 0 | 0.41388 | 5173.5 | 0.65054 | 52043.2 | 64000 | 5173.5 | 35822 | 0 | 0 | 1270088.2 | 0 | 0
2021081517 | 1 | 0.7173 | 107595 | 0.02721 | 0 | 0.3415 | 4268.75 | 0.6281 | 50248 | 64000 | 4268.75 | 39326.25 | 0 | 0 | 1295554.45 | 0 | 0
2021081518 | 1 | 0.72628 | 108942 | 0.04157 | 0 | 0.32319 | 4039.875 | 0.54798 | 43838.4 | 64000 | 4039.875 | 40902.125 | 0 | 0 | 1321020.7 | 0 | 0
2021081519 | 1 | 0.72097 | 108145.5 | 0.07476 | 0 | 0.36757 | 4594.625 | 0.30122 | 24097.6 | 64000 | 4594.625 | 24097.6 | 15453.275 | 15453.275 | 1331033.675 | 15453.275 | 0
2021081520 | 1 | 0.7004 | 105060 | 0.10235 | 0 | 0.34634 | 4329.25 | 0.04889 | 3911.2 | 64000 | 4329.25 | 3911.2 | 32819.55 | 17366.275 | 1323680.375 | 32819.55 | 0
2021081521 | 1 | 0.68506 | 102759 | 0.16381 | 0 | 0.36467 | 4558.375 | 0 | 0 | 64000 | 4558.375 | 0 | 34200.625 | 1381.075 | 1314946 | 34200.625 | 0
2021081522 | 1 | 0.66447 | 99670.5 | 0.21045 | 0 | 0.36704 | 4588 | 0 | 0 | 64000 | 4588 | 0 | 31082.5 | -3118.125 | 1309329.75 | 31082.5 | 0
2021081523 | 1 | 0.62811 | 94216.5 | 0.27565 | 0 | 0.38182 | 4772.75 | 0 | 0 | 64000 | 4772.75 | 0 | 25443.75 | -5638.75 | 1309352.25 | 25443.75 | 0
2021081524 | 1 | 0.58925 | 88387.5 | 0.26931 | 0 | 0.40025 | 5003.125 | 0 | 0 | 64000 | 5003.125 | 0 | 19384.375 | -6059.375 | 1315434.125 | 19384.375 | 0
2021081601 | 2 | 0.55573 | 83359.5 | 0.30512 | 0 | 0.40374 | 5046.75 | 0 | 0 | 64000 | 5046.75 | 0 | 14312.75 | -5071.625 | 1326587.625 | 14312.75 | 0
2021081602 | 2 | 0.53119 | 79678.5 | 0.31404 | 0 | 0.42077 | 5259.625 | 0 | 0 | 64000 | 5259.625 | 0 | 10418.875 | -3893.875 | 1341635 | 10418.875 | 0
2021081603 | 2 | 0.51559 | 77338.5 | 0.28228 | 0 | 0.42943 | 5367.875 | 0 | 0 | 64000 | 5367.875 | 0 | 7970.625 | -2448.25 | 1350000 | 7970.625 | 0
2021081604 | 2 | 0.50902 | 76353 | 0.32813 | 0 | 0.43781 | 5472.625 | 0 | 0 | 64000 | 5472.625 | 0 | 6880.375 | -1090.25 | 1350000 | 6880.375 | 0
2021081605 | 2 | 0.5132 | 76980 | 0.35504 | 0 | 0.42753 | 5344.125 | 0 | 0 | 64000 | 5344.125 | 0 | 7635.875 | 755.5 | 1350000 | 7635.875 | 0
2021081606 | 2 | 0.53465 | 80197.5 | 0.33737 | 0 | 0.38152 | 4769 | 0.00075 | 60 | 64000 | 4769 | 60 | 11368.5 | 3732.625 | 1350000 | 11368.5 | 0
2021081607 | 2 | 0.56852 | 85278 | 0.36594 | 0 | 0.33257 | 4157.125 | 0.06165 | 4932 | 64000 | 4157.125 | 4932 | 12188.875 | 820.375 | 1350000 | 12188.875 | 0
2021081608 | 2 | 0.60168 | 90252 | 0.35272 | 0 | 0.32372 | 4046.5 | 0.26108 | 20886.4 | 64000 | 4046.5 | 20886.4 | 1319.1 | -10869.775 | 1350000 | 1319.1 | 0
2021081609 | 2 | 0.62985 | 94477.5 | 0.3249 | 0 | 0.35965 | 4495.625 | 0.45324 | 36259.2 | 64000 | 4495.625 | 25981.875 | 0 | -1319.1 | 1350000 | 0 | 0
2021081610 | 2 | 0.6566 | 98490 | 0.27772 | 0 | 0.3691 | 4613.75 | 0.55679 | 44543.2 | 64000 | 4613.75 | 29876.25 | 0 | 0 | 1350000 | 0 | 0
2021081611 | 2 | 0.68292 | 102438 | 0.22275 | 0 | 0.38151 | 4768.875 | 0.60466 | 48372.8 | 64000 | 4768.875 | 33669.125 | 0 | 0 | 1350000 | 0 | 0
2021081612 | 2 | 0.7074 | 106110 | 0.20807 | 0 | 0.42267 | 5283.375 | 0.61603 | 49282.4 | 64000 | 5283.375 | 36826.625 | 0 | 0 | 1350000 | 0 | 0
2021081613 | 2 | 0.73173 | 109759.5 | 0.17767 | 0 | 0.41941 | 5242.625 | 0.63939 | 51151.2 | 64000 | 5242.625 | 40516.875 | 0 | 0 | 1350000 | 0 | 0
2021081614 | 2 | 0.753 | 112950 | 0.18016 | 0 | 0.36238 | 4529.75 | 0.64607 | 51685.6 | 64000 | 4529.75 | 44420.25 | 0 | 0 | 1350000 | 0 | 0
2021081615 | 2 | 0.76709 | 115063.5 | 0.22773 | 0 | 0.31791 | 3973.875 | 0.64215 | 51372 | 64000 | 3973.875 | 47089.625 | 0 | 0 | 1350000 | 0 | 0
2021081616 | 2 | 0.77616 | 116424 | 0.24499 | 0 | 0.29344 | 3668 | 0.61648 | 49318.4 | 64000 | 3668 | 48756 | 0 | 0 | 1350000 | 0 | 0
2021081617 | 2 | 0.78335 | 117502.5 | 0.19429 | 0 | 0.30069 | 3758.625 | 0.54032 | 43225.6 | 64000 | 3758.625 | 43225.6 | 6518.275 | 6518.275 | 1350000 | 6518.275 | 0
2021081618 | 2 | 0.78624 | 117936 | 0.18622 | 0 | 0.31598 | 3949.75 | 0.41119 | 32895.2 | 64000 | 3949.75 | 32895.2 | 17091.05 | 10572.775 | 1350000 | 17091.05 | 0
2021081619 | 2 | 0.77667 | 116500.5 | 0.22262 | 0 | 0.35451 | 4431.375 | 0.23139 | 18511.2 | 64000 | 4431.375 | 18511.2 | 29557.925 | 12466.875 | 1345908.325 | 29557.925 | 0
2021081620 | 2 | 0.75739 | 113608.5 | 0.32945 | 0 | 0.32836 | 4104.5 | 0.04301 | 3440.8 | 64000 | 4104.5 | 3440.8 | 42063.2 | 12505.275 | 1329311.375 | 42063.2 | 0
2021081621 | 2 | 0.74191 | 111286.5 | 0.41543 | 0 | 0.28717 | 3589.625 | 0 | 0 | 64000 | 3589.625 | 0 | 43696.875 | 1633.675 | 1311080.75 | 43696.875 | 0
2021081622 | 2 | 0.71525 | 107287.5 | 0.46669 | 0 | 0.23028 | 2878.5 | 0 | 0 | 64000 | 2878.5 | 0 | 40409 | -3287.875 | 1296138 | 40409 | 0
2021081623 | 2 | 0.67124 | 100686 | 0.50803 | 0 | 0.21548 | 2693.5 | 0 | 0 | 64000 | 2693.5 | 0 | 33992.5 | -6416.5 | 1287611.75 | 33992.5 | 0
2021081624 | 2 | 0.62636 | 93954 | 0.50572 | 0 | 0.2273 | 2841.25 | 0 | 0 | 64000 | 2841.25 | 0 | 27112.75 | -6879.75 | 1285965.25 | 27112.75 | 0
2021081701 | 3 | 0.58776 | 88164 | 0.48558 | 0 | 0.26825 | 3353.125 | 0 | 0 | 64000 | 3353.125 | 0 | 20810.875 | -6301.875 | 1290620.625 | 20810.875 | 0
2021081702 | 3 | 0.56115 | 84172.5 | 0.46197 | 0 | 0.31684 | 3960.5 | 0 | 0 | 64000 | 3960.5 | 0 | 16212 | -4598.875 | 1299874.875 | 16212 | 0
2021081703 | 3 | 0.54337 | 81505.5 | 0.38162 | 0 | 0.33804 | 4225.5 | 0 | 0 | 64000 | 4225.5 | 0 | 13280 | -2932 | 1312061.125 | 13280 | 0
2021081704 | 3 | 0.53226 | 79839 | 0.33223 | 0 | 0.32634 | 4079.25 | 0 | 0 | 64000 | 4079.25 | 0 | 11759.75 | -1520.25 | 1325767.625 | 11759.75 | 0
2021081705 | 3 | 0.53418 | 80127 | 0.33183 | 0 | 0.31185 | 3898.125 | 0 | 0 | 64000 | 3898.125 | 0 | 12228.875 | 469.125 | 1339005 | 12228.875 | 0
2021081706 | 3 | 0.55552 | 83328 | 0.32826 | 0 | 0.31924 | 3990.5 | 0.00066 | 52.8 | 64000 | 3990.5 | 52.8 | 15284.7 | 3055.825 | 1349186.55 | 15284.7 | 0
2021081707 | 3 | 0.59166 | 88749 | 0.33613 | 0 | 0.32502 | 4062.75 | 0.02912 | 2329.6 | 64000 | 4062.75 | 2329.6 | 18356.65 | 3071.95 | 1350000 | 18356.65 | 0
2021081708 | 3 | 0.62246 | 93369 | 0.32249 | 0 | 0.31486 | 3935.75 | 0.11916 | 9532.8 | 64000 | 3935.75 | 9532.8 | 15900.45 | -2456.2 | 1350000 | 15900.45 | 0
2021081709 | 3 | 0.65283 | 97924.5 | 0.28709 | 0 | 0.29063 | 3632.875 | 0.25132 | 20105.6 | 64000 | 3632.875 | 20105.6 | 10186.025 | -5714.425 | 1350000 | 10186.025 | 0
2021081710 | 3 | 0.68281 | 102421.5 | 0.25218 | 0 | 0.25437 | 3179.625 | 0.37793 | 30234.4 | 64000 | 3179.625 | 30234.4 | 5007.475 | -5178.55 | 1350000 | 5007.475 | 0
2021081711 | 3 | 0.71648 | 107472 | 0.23594 | 0 | 0.22559 | 2819.875 | 0.44167 | 35333.6 | 64000 | 2819.875 | 35333.6 | 5318.525 | 311.05 | 1350000 | 5318.525 | 0
2021081712 | 3 | 0.74996 | 112494 | 0.17916 | 0 | 0.22944 | 2868 | 0.47162 | 37729.6 | 64000 | 2868 | 37729.6 | 7896.4 | 2577.875 | 1350000 | 7896.4 | 0
2021081713 | 3 | 0.77888 | 116832 | 0.15163 | 0 | 0.26475 | 3309.375 | 0.53472 | 42777.6 | 64000 | 3309.375 | 42777.6 | 6745.025 | -1151.375 | 1350000 | 6745.025 | 0
2021081714 | 3 | 0.80428 | 120642 | 0.16543 | 0 | 0.2687 | 3358.75 | 0.57984 | 46387.2 | 64000 | 3358.75 | 46387.2 | 6896.05 | 151.025 | 1350000 | 6896.05 | 0
2021081715 | 3 | 0.82281 | 123421.5 | 0.15655 | 0 | 0.26049 | 3256.125 | 0.60332 | 48265.6 | 64000 | 3256.125 | 48265.6 | 7899.775 | 1003.725 | 1350000 | 7899.775 | 0
2021081716 | 3 | 0.83425 | 125137.5 | 0.18169 | 0 | 0.23333 | 2916.625 | 0.59108 | 47286.4 | 64000 | 2916.625 | 47286.4 | 10934.475 | 3034.7 | 1350000 | 10934.475 | 0
2021081717 | 3 | 0.83933 | 125899.5 | 0.18983 | 0 | 0.17923 | 2240.375 | 0.54076 | 43260.8 | 64000 | 2240.375 | 43260.8 | 16398.325 | 5463.85 | 1350000 | 16398.325 | 0
2021081718 | 3 | 0.83889 | 125833.5 | 0.21432 | 0 | 0.18024 | 2253 | 0.44161 | 35328.8 | 64000 | 2253 | 35328.8 | 24251.7 | 7853.375 | 1350000 | 24251.7 | 0
2021081719 | 3 | 0.82445 | 123667.5 | 0.23774 | 0 | 0.18662 | 2332.75 | 0.23879 | 19103.2 | 64000 | 2332.75 | 19103.2 | 38231.55 | 13979.85 | 1337234.7 | 38231.55 | 0
2021081720 | 3 | 0.80158 | 120237 | 0.23408 | 0 | 0.16597 | 2074.625 | 0.03836 | 3068.8 | 64000 | 2074.625 | 3068.8 | 51093.575 | 12862.025 | 1311607.375 | 51093.575 | 0
2021081721 | 3 | 0.78651 | 117976.5 | 0.28763 | 0 | 0.16077 | 2009.625 | 0 | 0 | 64000 | 2009.625 | 0 | 51966.875 | 873.3 | 1285106.75 | 51966.875 | 0
2021081722 | 3 | 0.75749 | 113623.5 | 0.33677 | 0 | 0.15698 | 1962.25 | 0 | 0 | 64000 | 1962.25 | 0 | 47661.25 | -4305.625 | 1262911.75 | 47661.25 | 0
2021081723 | 3 | 0.71402 | 107103 | 0.34689 | 0 | 0.21618 | 2702.25 | 0 | 0 | 64000 | 2702.25 | 0 | 40400.75 | -7260.5 | 1247977.25 | 40400.75 | 0
2021081724 | 3 | 0.66408 | 99612 | 0.38321 | 0 | 0.21366 | 2670.75 | 0 | 0 | 64000 | 2670.75 | 0 | 32941.25 | -7459.5 | 1240502.25 | 32941.25 | 0
2021081801 | 4 | 0.62402 | 93603 | 0.40686 | 0 | 0.1648 | 2060 | 0 | 0 | 64000 | 2060 | 0 | 27543 | -5398.25 | 1238425.5 | 27543 | 0
2021081802 | 4 | 0.59604 | 89406 | 0.44077 | 0 | 0.13899 | 1737.375 | 0 | 0 | 64000 | 1737.375 | 0 | 23668.625 | -3874.375 | 1240223.125 | 23668.625 | 0
2021081803 | 4 | 0.57526 | 86289 | 0.39647 | 0 | 0.1118 | 1397.5 | 0 | 0 | 64000 | 1397.5 | 0 | 20891.5 | -2777.125 | 1244797.875 | 20891.5 | 0
2021081804 | 4 | 0.56234 | 84351 | 0.47246 | 0 | 0.10421 | 1302.625 | 0 | 0 | 64000 | 1302.625 | 0 | 19048.375 | -1843.125 | 1251215.75 | 19048.375 | 0
2021081805 | 4 | 0.56464 | 84696 | 0.45426 | 0 | 0.08295 | 1036.875 | 0 | 0 | 64000 | 1036.875 | 0 | 19659.125 | 610.75 | 1257022.875 | 19659.125 | 0
2021081806 | 4 | 0.58647 | 87970.5 | 0.51375 | 0 | 0.05202 | 650.25 | 0 | 0 | 64000 | 650.25 | 0 | 23320.25 | 3661.125 | 1259168.875 | 23320.25 | 0
2021081807 | 4 | 0.62427 | 93640.5 | 0.58479 | 0 | 0.03575 | 446.875 | 0.01589 | 1271.2 | 64000 | 446.875 | 1271.2 | 27922.425 | 4602.175 | 1256712.7 | 27922.425 | 0
2021081808 | 4 | 0.65556 | 98334 | 0.67192 | 0 | 0.03363 | 420.375 | 0.06248 | 4998.4 | 64000 | 420.375 | 4998.4 | 28915.225 | 992.8 | 1253263.725 | 28915.225 | 0
2021081809 | 4 | 0.68709 | 103063.5 | 0.66102 | 0 | 0.02821 | 352.625 | 0.1244 | 9952 | 64000 | 352.625 | 9952 | 28758.875 | -156.35 | 1249971.1 | 28758.875 | 0
2021081810 | 4 | 0.71975 | 107962.5 | 0.63959 | 0 | 0.02864 | 358 | 0.23096 | 18476.8 | 64000 | 358 | 18476.8 | 25127.7 | -3631.175 | 1250309.65 | 25127.7 | 0
2021081811 | 4 | 0.75576 | 113364 | 0.61945 | 0 | 0.03146 | 393.25 | 0.34835 | 27868 | 64000 | 393.25 | 27868 | 21102.75 | -4024.95 | 1254673.15 | 21102.75 | 0
2021081812 | 4 | 0.78987 | 118480.5 | 0.49159 | 0 | 0.03531 | 441.375 | 0.45049 | 36039.2 | 64000 | 441.375 | 36039.2 | 17999.925 | -3102.825 | 1262139.475 | 17999.925 | 0
2021081813 | 4 | 0.82005 | 123007.5 | 0.44367 | 0 | 0.03106 | 388.25 | 0.46682 | 37345.6 | 64000 | 388.25 | 37345.6 | 21273.65 | 3273.725 | 1266332.075 | 21273.65 | 0
2021081814 | 4 | 0.84604 | 126906 | 0.48102 | 0 | 0.02855 | 356.875 | 0.48327 | 38661.6 | 64000 | 356.875 | 38661.6 | 23887.525 | 2613.875 | 1267910.8 | 23887.525 | 0
2021081815 | 4 | 0.86688 | 130032 | 0.51782 | 0 | 0.02093 | 261.625 | 0.43817 | 35053.6 | 64000 | 261.625 | 35053.6 | 30716.775 | 6829.25 | 1262660.275 | 30716.775 | 0
2021081816 | 4 | 0.88032 | 132048 | 0.56827 | 0 | 0.01324 | 165.5 | 0.40669 | 32535.2 | 64000 | 165.5 | 32535.2 | 35347.3 | 4630.525 | 1252779.225 | 35347.3 | 0
2021081817 | 4 | 0.88801 | 133201.5 | 0.60886 | 0 | 0.01437 | 179.625 | 0.34113 | 27290.4 | 64000 | 179.625 | 27290.4 | 41731.475 | 6384.175 | 1236514 | 41731.475 | 0
2021081818 | 4 | 0.88911 | 133366.5 | 0.68114 | 0 | 0.02663 | 332.875 | 0.31748 | 25398.4 | 64000 | 332.875 | 25398.4 | 43635.225 | 1903.75 | 1218345.025 | 43635.225 | 0
2021081819 | 4 | 0.87454 | 131181 | 0.66585 | 0 | 0.05164 | 645.5 | 0.24525 | 19620 | 64000 | 645.5 | 19620 | 46915.5 | 3280.275 | 1196895.775 | 46915.5 | 0
2021081820 | 4 | 0.85052 | 127578 | 0.71093 | 0 | 0.06545 | 818.125 | 0.03931 | 3144.8 | 64000 | 818.125 | 3144.8 | 59615.075 | 12699.575 | 1162746.95 | 59615.075 | 0
2021081821 | 4 | 0.82919 | 124378.5 | 0.78905 | 0 | 0.07015 | 876.875 | 0 | 0 | 64000 | 876.875 | 0 | 59501.625 | -113.45 | 1128711.575 | 59501.625 | 0
2021081822 | 4 | 0.79856 | 119784 | 0.8036 | 0 | 0.07843 | 980.375 | 0 | 0 | 64000 | 980.375 | 0 | 54803.625 | -4698 | 1099374.2 | 54803.625 | 0
2021081823 | 4 | 0.74905 | 112357.5 | 0.7399 | 0 | 0.08164 | 1020.5 | 0 | 0 | 64000 | 1020.5 | 0 | 47337 | -7466.625 | 1077503.45 | 47337 | 0
2021081824 | 4 | 0.69879 | 104818.5 | 0.70451 | 0 | 0.08702 | 1087.75 | 0 | 0 | 64000 | 1087.75 | 0 | 39730.75 | -7606.25 | 1063238.95 | 39730.75 | 0
2021081901 | 5 | 0.65453 | 98179.5 | 0.68416 | 0 | 0.08576 | 1072 | 0 | 0 | 64000 | 1072 | 0 | 33107.5 | -6623.25 | 1055597.7 | 33107.5 | 0
2021081902 | 5 | 0.62158 | 93237 | 0.71947 | 0 | 0.07698 | 962.25 | 0 | 0 | 64000 | 962.25 | 0 | 28274.75 | -4832.75 | 1052789.2 | 28274.75 | 0
2021081903 | 5 | 0.5988 | 89820 | 0.66242 | 0 | 0.0729 | 911.25 | 0 | 0 | 64000 | 911.25 | 0 | 24908.75 | -3366 | 1053346.7 | 24908.75 | 0
2021081904 | 5 | 0.5836 | 87540 | 0.66179 | 0 | 0.05926 | 740.75 | 0 | 0 | 64000 | 740.75 | 0 | 22799.25 | -2109.5 | 1056013.7 | 22799.25 | 0
2021081905 | 5 | 0.58216 | 87324 | 0.65811 | 0 | 0.07387 | 923.375 | 0 | 0 | 64000 | 923.375 | 0 | 22400.625 | -398.625 | 1059079.325 | 22400.625 | 0
2021081906 | 5 | 0.59961 | 89941.5 | 0.66145 | 0 | 0.10099 | 1262.375 | 0 | 0 | 64000 | 1262.375 | 0 | 24679.125 | 2278.5 | 1059866.45 | 24679.125 | 0
2021081907 | 5 | 0.63177 | 94765.5 | 0.64162 | 0 | 0.1099 | 1373.75 | 0.05935 | 4748 | 64000 | 1373.75 | 4748 | 24643.75 | -35.375 | 1060688.95 | 24643.75 | 0
2021081908 | 5 | 0.66207 | 99310.5 | 0.64669 | 0 | 0.13127 | 1640.875 | 0.28022 | 22417.6 | 64000 | 1640.875 | 22417.6 | 11252.025 | -13391.725 | 1074903.175 | 11252.025 | 0
2021081909 | 5 | 0.69758 | 104637 | 0.69926 | 0 | 0.15979 | 1997.375 | 0.42827 | 34261.6 | 64000 | 1997.375 | 34261.6 | 4378.025 | -6874 | 1095991.4 | 4378.025 | 0
2021081910 | 5 | 0.73578 | 110367 | 0.63538 | 0 | 0.17185 | 2148.125 | 0.49129 | 39303.2 | 64000 | 2148.125 | 39303.2 | 4915.675 | 537.65 | 1116541.975 | 4915.675 | 0
2021081911 | 5 | 0.77693 | 116539.5 | 0.58329 | 0 | 0.16381 | 2047.625 | 0.5303 | 42424 | 64000 | 2047.625 | 42424 | 8067.875 | 3152.2 | 1133940.35 | 8067.875 | 0
2021081912 | 5 | 0.81345 | 122017.5 | 0.54371 | 0 | 0.14864 | 1858 | 0.55758 | 44606.4 | 64000 | 1858 | 44606.4 | 11553.1 | 3485.225 | 1147853.5 | 11553.1 | 0
2021081913 | 5 | 0.84351 | 126526.5 | 0.52877 | 0 | 0.14828 | 1853.5 | 0.58357 | 46685.6 | 64000 | 1853.5 | 46685.6 | 13987.4 | 2434.3 | 1159332.35 | 13987.4 | 0
2021081914 | 5 | 0.86727 | 130090.5 | 0.48195 | 0 | 0.17184 | 2148 | 0.61065 | 48852 | 64000 | 2148 | 48852 | 15090.5 | 1103.1 | 1169708.1 | 15090.5 | 0
2021081915 | 5 | 0.88557 | 132835.5 | 0.43417 | 0 | 0.1668 | 2085 | 0.64925 | 51940 | 64000 | 2085 | 51940 | 14810.5 | -280 | 1180363.85 | 14810.5 | 0
2021081916 | 5 | 0.89861 | 134791.5 | 0.37049 | 0 | 0.13049 | 1631.125 | 0.64839 | 51871.2 | 64000 | 1631.125 | 51871.2 | 17289.175 | 2478.675 | 1188540.925 | 17289.175 | 0
2021081917 | 5 | 0.908 | 136200 | 0.29101 | 0 | 0.11118 | 1389.75 | 0.61689 | 49351.2 | 64000 | 1389.75 | 49351.2 | 21459.05 | 4169.875 | 1192548.125 | 21459.05 | 0
2021081918 | 5 | 0.90701 | 136051.5 | 0.27781 | 0 | 0.12788 | 1598.5 | 0.54071 | 43256.8 | 64000 | 1598.5 | 43256.8 | 27196.2 | 5737.15 | 1190818.175 | 27196.2 | 0
2021081919 | 5 | 0.88992 | 133488 | 0.21123 | 0 | 0.16378 | 2047.25 | 0.3026 | 24208 | 64000 | 2047.25 | 24208 | 43232.75 | 16036.55 | 1173051.675 | 43232.75 | 0
2021081920 | 5 | 0.85723 | 128584.5 | 0.20928 | 0 | 0.17894 | 2236.75 | 0.04632 | 3705.6 | 64000 | 2236.75 | 3705.6 | 58642.15 | 15409.4 | 1139875.775 | 58642.15 | 0
2021081921 | 5 | 0.83165 | 124747.5 | 0.23 | 0 | 0.21588 | 2698.5 | 0.00072 | 57.6 | 64000 | 2698.5 | 57.6 | 57991.4 | -650.75 | 1107350.625 | 57991.4 | 0
2021081922 | 5 | 0.79363 | 119044.5 | 0.18723 | 0 | 0.16957 | 2119.625 | 0 | 0 | 64000 | 2119.625 | 0 | 52924.875 | -5066.525 | 1079892 | 52924.875 | 0
2021081923 | 5 | 0.74003 | 111004.5 | 0.13932 | 0 | 0.15107 | 1888.375 | 0 | 0 | 64000 | 1888.375 | 0 | 45116.125 | -7808.75 | 1060242.125 | 45116.125 | 0
2021081924 | 5 | 0.68575 | 102862.5 | 0.11672 | 0 | 0.14794 | 1849.25 | 0 | 0 | 64000 | 1849.25 | 0 | 37013.25 | -8102.875 | 1048695.125 | 37013.25 | 0
2021082001 | 6 | 0.63876 | 95814 | 0.13665 | 0 | 0.14023 | 1752.875 | 0 | 0 | 64000 | 1752.875 | 0 | 30061.125 | -6952.125 | 1044100.25 | 30061.125 | 0
2021082002 | 6 | 0.60501 | 90751.5 | 0.14245 | 0 | 0.13278 | 1659.75 | 0 | 0 | 64000 | 1659.75 | 0 | 25091.75 | -4969.375 | 1044474.75 | 25091.75 | 0
2021082003 | 6 | 0.5807 | 87105 | 0.14081 | 0 | 0.10395 | 1299.375 | 0 | 0 | 64000 | 1299.375 | 0 | 21805.625 | -3286.125 | 1048135.375 | 21805.625 | 0
2021082004 | 6 | 0.56758 | 85137 | 0.15359 | 0 | 0.07511 | 938.875 | 0 | 0 | 64000 | 938.875 | 0 | 20198.125 | -1607.5 | 1053403.5 | 20198.125 | 0
2021082005 | 6 | 0.56442 | 84663 | 0.16806 | 0 | 0.05274 | 659.25 | 0 | 0 | 64000 | 659.25 | 0 | 20003.75 | -194.375 | 1058866 | 20003.75 | 0
2021082006 | 6 | 0.57867 | 86800.5 | 0.15137 | 0 | 0.05269 | 658.625 | 0.00199 | 159.2 | 64000 | 658.625 | 159.2 | 21982.675 | 1978.925 | 1062349.575 | 21982.675 | 0
2021082007 | 6 | 0.61134 | 91701 | 0.11422 | 0 | 0.05055 | 631.875 | 0.06579 | 5263.2 | 64000 | 631.875 | 5263.2 | 21805.925 | -176.75 | 1066009.9 | 21805.925 | 0
2021082008 | 6 | 0.63831 | 95746.5 | 0.09619 | 0 | 0.04305 | 538.125 | 0.24931 | 19944.8 | 64000 | 538.125 | 19944.8 | 11263.575 | -10542.35 | 1080212.575 | 11263.575 | 0
2021082009 | 6 | 0.67018 | 100527 | 0.0553 | 0 | 0.05203 | 650.375 | 0.37476 | 29980.8 | 64000 | 650.375 | 29980.8 | 5895.825 | -5367.75 | 1099783 | 5895.825 | 0
2021082010 | 6 | 0.70215 | 105322.5 | 0.04856 | 0 | 0.05222 | 652.75 | 0.40218 | 32174.4 | 64000 | 652.75 | 32174.4 | 8495.35 | 2599.525 | 1116753.9 | 8495.35 | 0
2021082011 | 6 | 0.73437 | 110155.5 | 0.02696 | 0 | 0.04815 | 601.875 | 0.43904 | 35123.2 | 64000 | 601.875 | 35123.2 | 10430.425 | 1935.075 | 1131789.725 | 10430.425 | 0
2021082012 | 6 | 0.7646 | 114690 | 0.01161 | 0 | 0.04259 | 532.375 | 0.45549 | 36439.2 | 64000 | 532.375 | 36439.2 | 13718.425 | 3288 | 1143537.55 | 13718.425 | 0
2021082013 | 6 | 0.79333 | 118999.5 | 0.02643 | 0 | 0.03368 | 421 | 0.48253 | 38602.4 | 64000 | 421 | 38602.4 | 15976.1 | 2257.675 | 1153027.7 | 15976.1 | 0
2021082014 | 6 | 0.82185 | 123277.5 | 0.03294 | 0 | 0.02474 | 309.25 | 0.56096 | 44876.8 | 64000 | 309.25 | 44876.8 | 14091.45 | -1884.65 | 1164402.5 | 14091.45 | 0
2021082015 | 6 | 0.84027 | 126040.5 | 0.02698 | 0 | 0.01015 | 126.875 | 0.6376 | 51008 | 64000 | 126.875 | 51008 | 10905.625 | -3185.825 | 1178963.125 | 10905.625 | 0
2021082016 | 6 | 0.85322 | 127983 | 0.01495 | 0 | 0.00324 | 40.5 | 0.64542 | 51633.6 | 64000 | 40.5 | 51633.6 | 12308.9 | 1403.275 | 1192120.475 | 12308.9 | 0
2021082017 | 6 | 0.86518 | 129777 | 0.04483 | 0 | 0.00045 | 5.625 | 0.61077 | 48861.6 | 64000 | 5.625 | 48861.6 | 16909.775 | 4600.875 | 1200676.95 | 16909.775 | 0
2021082018 | 6 | 0.86774 | 130161 | 0.03367 | 0 | 0.00724 | 90.5 | 0.53439 | 42751.2 | 64000 | 90.5 | 42751.2 | 23319.3 | 6409.525 | 1202823.9 | 23319.3 | 0
2021082019 | 6 | 0.84751 | 127126.5 | 0.0361 | 0 | 0.0214 | 267.5 | 0.30894 | 24715.2 | 64000 | 267.5 | 24715.2 | 38143.8 | 14824.5 | 1190146.35 | 38143.8 | 0
2021082020 | 6 | 0.81348 | 122022 | 0.03418 | 0 | 0.03667 | 458.375 | 0.04621 | 3696.8 | 64000 | 458.375 | 3696.8 | 53866.825 | 15723.025 | 1161745.775 | 53866.825 | 0
2021082021 | 6 | 0.78489 | 117733.5 | 0.01502 | 0 | 0.05374 | 671.75 | 0 | 0 | 64000 | 671.75 | 0 | 53061.75 | -805.075 | 1134150.275 | 53061.75 | 0
2021082022 | 6 | 0.74924 | 112386 | 0.02196 | 0 | 0.0661 | 826.25 | 0 | 0 | 64000 | 826.25 | 0 | 47559.75 | -5502 | 1112056.775 | 47559.75 | 0
2021082023 | 6 | 0.70232 | 105348 | 0.02654 | 0 | 0.06779 | 847.375 | 0 | 0 | 64000 | 847.375 | 0 | 40500.625 | -7059.125 | 1097022.4 | 40500.625 | 0
2021082024 | 6 | 0.651 | 97650 | 0.00435 | 0 | 0.05973 | 746.625 | 0 | 0 | 64000 | 746.625 | 0 | 32903.375 | -7597.25 | 1089585.275 | 32903.375 | 0
2021082101 | 7 | 0.60613 | 90919.5 | 0.00035 | 0 | 0.05137 | 642.125 | 0 | 0 | 64000 | 642.125 | 0 | 26277.375 | -6626 | 1088774.15 | 26277.375 | 0
2021082102 | 7 | 0.57137 | 85705.5 | 0.00707 | 0 | 0.0368 | 460 | 0 | 0 | 64000 | 460 | 0 | 21245.5 | -5031.875 | 1092994.9 | 21245.5 | 0
2021082103 | 7 | 0.5475 | 82125 | 0.00742 | 0 | 0.03086 | 385.75 | 0 | 0 | 64000 | 385.75 | 0 | 17739.25 | -3506.25 | 1100721.9 | 17739.25 | 0
2021082104 | 7 | 0.52965 | 79447.5 | 0.00537 | 0 | 0.02912 | 364 | 0 | 0 | 64000 | 364 | 0 | 15083.5 | -2655.75 | 1111104.65 | 15083.5 | 0
2021082105 | 7 | 0.52074 | 78111 | 0.00701 | 0 | 0.02595 | 324.375 | 0 | 0 | 64000 | 324.375 | 0 | 13786.625 | -1296.875 | 1122784.275 | 13786.625 | 0
2021082106 | 7 | 0.52152 | 78228 | 1e-05 | 0 | 0.01828 | 228.5 | 0.0007 | 56 | 64000 | 228.5 | 56 | 13943.5 | 156.875 | 1134307.025 | 13943.5 | 0
2021082107 | 7 | 0.53031 | 79546.5 | 0.00293 | 0 | 0.01807 | 225.875 | 0.07025 | 5620 | 64000 | 225.875 | 5620 | 9700.625 | -4242.875 | 1150072.65 | 9700.625 | 0
2021082108 | 7 | 0.5474 | 82110 | 0.00626 | 0 | 0.01664 | 208 | 0.28143 | 22514.4 | 64000 | 208 | 17902 | 0 | -9700.625 | 1175538.9 | 0 | 0
2021082109 | 7 | 0.58723 | 88084.5 | 0.00673 | 0 | 0.01986 | 248.25 | 0.42752 | 34201.6 | 64000 | 248.25 | 23836.25 | 0 | 0 | 1201005.15 | 0 | 0
2021082110 | 7 | 0.63589 | 95383.5 | 0.00691 | 0 | 0.02201 | 275.125 | 0.49739 | 39791.2 | 64000 | 275.125 | 31108.375 | 0 | 0 | 1226471.4 | 0 | 0
2021082111 | 7 | 0.6878 | 103170 | 0.00704 | 0 | 0.02344 | 293 | 0.54487 | 43589.6 | 64000 | 293 | 38877 | 0 | 0 | 1251937.65 | 0 | 0
2021082112 | 7 | 0.7325 | 109875 | 0.00673 | 0 | 0.02172 | 271.5 | 0.56875 | 45500 | 64000 | 271.5 | 45500 | 103.5 | 103.5 | 1277300.4 | 103.5 | 0
2021082113 | 7 | 0.76733 | 115099.5 | 0.00722 | 0 | 0.02439 | 304.875 | 0.58453 | 46762.4 | 64000 | 304.875 | 46762.4 | 4032.225 | 3928.725 | 1298734.425 | 4032.225 | 0
2021082114 | 7 | 0.79139 | 118708.5 | 0.00647 | 0 | 0.0227 | 283.75 | 0.60576 | 48460.8 | 64000 | 283.75 | 48460.8 | 5963.95 | 1931.725 | 1318236.725 | 5963.95 | 0
2021082115 | 7 | 0.80738 | 121107 | 0.00049 | 0 | 0.02522 | 315.25 | 0.65712 | 52569.6 | 64000 | 315.25 | 52569.6 | 4222.15 | -1741.8 | 1339480.825 | 4222.15 | 0
2021082116 | 7 | 0.81631 | 122446.5 | 0.01302 | 0 | 0.01845 | 230.625 | 0.65812 | 52649.6 | 64000 | 230.625 | 52649.6 | 5566.275 | 1344.125 | 1350000 | 5566.275 | 0
2021082117 | 7 | 0.82322 | 123483 | 0.02985 | 0 | 0.00828 | 103.5 | 0.62418 | 49934.4 | 64000 | 103.5 | 49934.4 | 9445.1 | 3878.825 | 1350000 | 9445.1 | 0
2021082118 | 7 | 0.82407 | 123610.5 | 0.03063 | 0 | 0.02049 | 256.125 | 0.55573 | 44458.4 | 64000 | 256.125 | 44458.4 | 14895.975 | 5450.875 | 1350000 | 14895.975 | 0
2021082119 | 7 | 0.81204 | 121806 | 0.04366 | 0 | 0.03461 | 432.625 | 0.30449 | 24359.2 | 64000 | 432.625 | 24359.2 | 33014.175 | 18118.2 | 1342452.075 | 33014.175 | 0
2021082120 | 7 | 0.78518 | 117777 | 0.03228 | 0 | 0.04378 | 547.25 | 0.04248 | 3398.4 | 64000 | 547.25 | 3398.4 | 49831.35 | 16817.175 | 1318086.975 | 49831.35 | 0
2021082121 | 7 | 0.76136 | 114204 | 0.02709 | 0 | 0.05129 | 641.125 | 0 | 0 | 64000 | 641.125 | 0 | 49562.875 | -268.475 | 1293990.35 | 49562.875 | 0
2021082122 | 7 | 0.73077 | 109615.5 | 0.01703 | 0 | 0.06115 | 764.375 | 0 | 0 | 64000 | 764.375 | 0 | 44851.125 | -4711.75 | 1274605.475 | 44851.125 | 0
2021082123 | 7 | 0.68903 | 103354.5 | 0.04162 | 0 | 0.07541 | 942.625 | 0 | 0 | 64000 | 942.625 | 0 | 38411.875 | -6439.25 | 1261659.85 | 38411.875 | 0
2021082124 | 7 | 0.64445 | 96667.5 | 0.04138 | 0 | 0.09383 | 1172.875 | 0 | 0 | 64000 | 1172.875 | 0 | 31494.625 | -6917.25 | 1255631.475 | 31494.625 | 0
2021082201 | 1 | 0.60311 | 90466.5 | 0.03383 | 0 | 0.12282 | 1535.25 | 0 | 0 | 64000 | 1535.25 | 0 | 24931.25 | -6563.375 | 1256166.475 | 24931.25 | 0
2021082202 | 1 | 0.57294 | 85941 | 0.02534 | 0 | 0.15217 | 1902.125 | 0 | 0 | 64000 | 1902.125 | 0 | 20038.875 | -4892.375 | 1261593.85 | 20038.875 | 0
2021082203 | 1 | 0.54726 | 82089 | 0.0333 | 0 | 0.15789 | 1973.625 | 0 | 0 | 64000 | 1973.625 | 0 | 16115.375 | -3923.5 | 1270944.725 | 16115.375 | 0
2021082204 | 1 | 0.53008 | 79512 | 0.06029 | 0 | 0.17222 | 2152.75 | 0 | 0 | 64000 | 2152.75 | 0 | 13359.25 | -2756.125 | 1283051.725 | 13359.25 | 0
2021082205 | 1 | 0.51841 | 77761.5 | 0.06641 | 0 | 0.18218 | 2277.25 | 0 | 0 | 64000 | 2277.25 | 0 | 11484.25 | -1875 | 1297033.725 | 11484.25 | 0
2021082206 | 1 | 0.51572 | 77358 | 0.06728 | 0 | 0.16982 | 2122.75 | 0.00056 | 44.8 | 64000 | 2122.75 | 44.8 | 11190.45 | -293.8 | 1311309.525 | 11190.45 | 0
2021082207 | 1 | 0.51681 | 77521.5 | 0.11795 | 0 | 0.16054 | 2006.75 | 0.06636 | 5308.8 | 64000 | 2006.75 | 5308.8 | 6205.95 | -4984.5 | 1330569.825 | 6205.95 | 0
2021082208 | 1 | 0.5244 | 78660 | 0.12673 | 0 | 0.15226 | 1903.25 | 0.2399 | 19192 | 64000 | 1903.25 | 12756.75 | 0 | -6205.95 | 1350000 | 0 | 0
2021082209 | 1 | 0.55822 | 83733 | 0.12489 | 0 | 0.14387 | 1798.375 | 0.32111 | 25688.8 | 64000 | 1798.375 | 17934.625 | 0 | 0 | 1350000 | 0 | 0
2021082210 | 1 | 0.60466 | 90699 | 0.10002 | 0 | 0.13904 | 1738 | 0.32171 | 25736.8 | 64000 | 1738 | 24961 | 0 | 0 | 1350000 | 0 | 0
2021082211 | 1 | 0.65117 | 97675.5 | 0.06491 | 0 | 0.13879 | 1734.875 | 0.34899 | 27919.2 | 64000 | 1734.875 | 27919.2 | 4021.425 | 4021.425 | 1350000 | 4021.425 | 0
2021082212 | 1 | 0.69805 | 104707.5 | 0.06773 | 0 | 0.15114 | 1889.25 | 0.36609 | 29287.2 | 64000 | 1889.25 | 29287.2 | 9531.05 | 5509.625 | 1350000 | 9531.05 | 0
2021082213 | 1 | 0.73325 | 109987.5 | 0.03794 | 0 | 0.15513 | 1939.125 | 0.37252 | 29801.6 | 64000 | 1939.125 | 29801.6 | 14246.775 | 4715.725 | 1350000 | 14246.775 | 0
2021082214 | 1 | 0.75895 | 113842.5 | 0.02592 | 0 | 0.14802 | 1850.25 | 0.37225 | 29780 | 64000 | 1850.25 | 29780 | 18212.25 | 3965.475 | 1350000 | 18212.25 | 0
2021082215 | 1 | 0.77554 | 116331 | 0.0274 | 0 | 0.11401 | 1425.125 | 0.32414 | 25931.2 | 64000 | 1425.125 | 25931.2 | 24974.675 | 6762.425 | 1350000 | 24974.675 | 0
2021082216 | 1 | 0.78803 | 118204.5 | 0.04628 | 0 | 0.08841 | 1105.125 | 0.2732 | 21856 | 64000 | 1105.125 | 21856 | 31243.375 | 6268.7 | 1344222.875 | 31243.375 | 0
2021082217 | 1 | 0.79668 | 119502 | 0.0936 | 0 | 0.0868 | 1085 | 0.2142 | 17136 | 64000 | 1085 | 17136 | 37281 | 6037.625 | 1332408.125 | 37281 | 0
2021082218 | 1 | 0.80243 | 120364.5 | 0.13543 | 0 | 0.16083 | 2010.375 | 0.17716 | 14172.8 | 64000 | 2010.375 | 14172.8 | 40181.325 | 2900.325 | 1317693.05 | 40181.325 | 0
2021082219 | 1 | 0.79085 | 118627.5 | 0.25467 | 0 | 0.24403 | 3050.375 | 0.08617 | 6893.6 | 64000 | 3050.375 | 6893.6 | 44683.525 | 4502.2 | 1298475.775 | 44683.525 | 0
2021082220 | 1 | 0.77196 | 115794 | 0.35563 | 0 | 0.27656 | 3457 | 0.01478 | 1182.4 | 64000 | 3457 | 1182.4 | 47154.6 | 2471.075 | 1276787.425 | 47154.6 | 0
2021082221 | 1 | 0.75358 | 113037 | 0.43264 | 0 | 0.27816 | 3477 | 0 | 0 | 64000 | 3477 | 0 | 45560 | -1594.6 | 1256693.675 | 45560 | 0
2021082222 | 1 | 0.72298 | 108447 | 0.50661 | 0 | 0.28821 | 3602.625 | 0 | 0 | 64000 | 3602.625 | 0 | 40844.375 | -4715.625 | 1241315.55 | 40844.375 | 0
2021082223 | 1 | 0.67828 | 101742 | 0.55994 | 0 | 0.29788 | 3723.5 | 0 | 0 | 64000 | 3723.5 | 0 | 34018.5 | -6825.875 | 1232763.3 | 34018.5 | 0
2021082224 | 1 | 0.63272 | 94908 | 0.58555 | 0 | 0.3008 | 3760 | 0 | 0 | 64000 | 3760 | 0 | 27148 | -6870.5 | 1231081.55 | 27148 | 0
2021082301 | 2 | 0.59343 | 89014.5 | 0.56169 | 0 | 0.29066 | 3633.25 | 0 | 0 | 64000 | 3633.25 | 0 | 21381.25 | -5766.75 | 1235166.55 | 21381.25 | 0
2021082302 | 2 | 0.56441 | 84661.5 | 0.55873 | 0 | 0.3109 | 3886.25 | 0 | 0 | 64000 | 3886.25 | 0 | 16775.25 | -4606 | 1243857.55 | 16775.25 | 0
2021082303 | 2 | 0.54603 | 81904.5 | 0.57236 | 0 | 0.33692 | 4211.5 | 0 | 0 | 64000 | 4211.5 | 0 | 13693 | -3082.25 | 1255630.8 | 13693 | 0
2021082304 | 2 | 0.536 | 80400 | 0.59907 | 0 | 0.32903 | 4112.875 | 0 | 0 | 64000 | 4112.875 | 0 | 12287.125 | -1405.875 | 1268809.925 | 12287.125 | 0
2021082305 | 2 | 0.53914 | 80871 | 0.60687 | 0 | 0.33666 | 4208.25 | 0 | 0 | 64000 | 4208.25 | 0 | 12662.75 | 375.625 | 1281613.425 | 12662.75 | 0
2021082306 | 2 | 0.56054 | 84081 | 0.62333 | 0 | 0.33848 | 4231 | 0.00047 | 37.6 | 64000 | 4231 | 37.6 | 15812.4 | 3149.65 | 1291267.275 | 15812.4 | 0
2021082307 | 2 | 0.60051 | 90076.5 | 0.59072 | 0 | 0.32186 | 4023.25 | 0.05953 | 4762.4 | 64000 | 4023.25 | 4762.4 | 17290.85 | 1478.45 | 1299442.675 | 17290.85 | 0
2021082308 | 2 | 0.63229 | 94843.5 | 0.58673 | 0 | 0.31514 | 3939.25 | 0.26218 | 20974.4 | 64000 | 3939.25 | 20974.4 | 5929.85 | -11361 | 1318979.075 | 5929.85 | 0
2021082309 | 2 | 0.67041 | 100561.5 | 0.61778 | 0 | 0.31834 | 3979.25 | 0.34929 | 27943.2 | 64000 | 3979.25 | 27943.2 | 4639.05 | -1290.8 | 1339806.275 | 4639.05 | 0
2021082310 | 2 | 0.71249 | 106873.5 | 0.59311 | 0 | 0.31061 | 3882.625 | 0.36737 | 29389.6 | 64000 | 3882.625 | 29389.6 | 9601.275 | 4962.225 | 1350000 | 9601.275 | 0
2021082311 | 2 | 0.76201 | 114301.5 | 0.55338 | 0 | 0.30757 | 3844.625 | 0.4236 | 33888 | 64000 | 3844.625 | 33888 | 12568.875 | 2967.6 | 1350000 | 12568.875 | 0
2021082312 | 2 | 0.80765 | 121147.5 | 0.51906 | 0 | 0.30141 | 3767.625 | 0.47192 | 37753.6 | 64000 | 3767.625 | 37753.6 | 15626.275 | 3057.4 | 1350000 | 15626.275 | 0
2021082313 | 2 | 0.84878 | 127317 | 0.5037 | 0 | 0.27771 | 3471.375 | 0.54743 | 43794.4 | 64000 | 3471.375 | 43794.4 | 16051.225 | 424.95 | 1350000 | 16051.225 | 0
2021082314 | 2 | 0.88577 | 132865.5 | 0.45647 | 0 | 0.25084 | 3135.5 | 0.59375 | 47500 | 64000 | 3135.5 | 47500 | 18230 | 2178.775 | 1350000 | 18230 | 0
2021082315 | 2 | 0.91098 | 136647 | 0.44514 | 0 | 0.17299 | 2162.375 | 0.57846 | 46276.8 | 64000 | 2162.375 | 46276.8 | 24207.825 | 5977.825 | 1350000 | 24207.825 | 0
2021082316 | 2 | 0.92938 | 139407 | 0.46016 | 0 | 0.1372 | 1715 | 0.50256 | 40204.8 | 64000 | 1715 | 40204.8 | 33487.2 | 9279.375 | 1341979.05 | 33487.2 | 0
2021082317 | 2 | 0.94296 | 141444 | 0.44359 | 0 | 0.13105 | 1638.125 | 0.40153 | 32122.4 | 64000 | 1638.125 | 32122.4 | 43683.475 | 10196.275 | 1323761.825 | 43683.475 | 0
2021082318 | 2 | 0.94527 | 141790.5 | 0.42762 | 0 | 0.12991 | 1623.875 | 0.25831 | 20664.8 | 64000 | 1623.875 | 20664.8 | 55501.825 | 11818.35 | 1293726.25 | 55501.825 | 0
2021082319 | 2 | 0.92974 | 139461 | 0.36966 | 0 | 0.13825 | 1728.125 | 0.12048 | 9638.4 | 64000 | 1728.125 | 9638.4 | 64094.475 | 8592.65 | 1255098.025 | 64094.475 | 0
2021082320 | 2 | 0.89802 | 134703 | 0.3727 | 0 | 0.14036 | 1754.5 | 0.01947 | 1557.6 | 64000 | 1754.5 | 1557.6 | 67390.9 | 3296.425 | 1213173.375 | 67390.9 | 0
2021082321 | 2 | 0.86908 | 130362 | 0.37487 | 0 | 0.12486 | 1560.75 | 0 | 0 | 64000 | 1560.75 | 0 | 64801.25 | -2589.65 | 1173838.375 | 64801.25 | 0
2021082322 | 2 | 0.82502 | 123753 | 0.36413 | 0 | 0.11447 | 1430.875 | 0 | 0 | 64000 | 1430.875 | 0 | 58322.125 | -6479.125 | 1140982.5 | 58322.125 | 0
2021082323 | 2 | 0.76371 | 114556.5 | 0.4056 | 0 | 0.1133 | 1416.25 | 0 | 0 | 64000 | 1416.25 | 0 | 49140.25 | -9181.875 | 1117308.5 | 49140.25 | 0
2021082324 | 2 | 0.70327 | 105490.5 | 0.4055 | 0 | 0.11586 | 1448.25 | 0 | 0 | 64000 | 1448.25 | 0 | 40042.25 | -9098 | 1102732.5 | 40042.25 | 0
2021082401 | 3 | 0.65505 | 98257.5 | 0.43629 | 0 | 0.13606 | 1700.75 | 0 | 0 | 64000 | 1700.75 | 0 | 32556.75 | -7485.5 | 1095642 | 32556.75 | 0
2021082402 | 3 | 0.618 | 92700 | 0.48032 | 0 | 0.15286 | 1910.75 | 0 | 0 | 64000 | 1910.75 | 0 | 26789.25 | -5767.5 | 1094319 | 26789.25 | 0
2021082403 | 3 | 0.59183 | 88774.5 | 0.45139 | 0 | 0.21554 | 2694.25 | 0 | 0 | 64000 | 2694.25 | 0 | 22080.25 | -4709 | 1097705 | 22080.25 | 0
2021082404 | 3 | 0.57591 | 86386.5 | 0.44563 | 0 | 0.26038 | 3254.75 | 0 | 0 | 64000 | 3254.75 | 0 | 19131.75 | -2948.5 | 1104039.5 | 19131.75 | 0
2021082405 | 3 | 0.57238 | 85857 | 0.43691 | 0 | 0.30834 | 3854.25 | 0 | 0 | 64000 | 3854.25 | 0 | 18002.75 | -1129 | 1111503 | 18002.75 | 0
2021082406 | 3 | 0.59021 | 88531.5 | 0.3794 | 0 | 0.24492 | 3061.5 | 0 | 0 | 64000 | 3061.5 | 0 | 21470 | 3467.25 | 1115499.25 | 21470 | 0
2021082407 | 3 | 0.6261 | 93915 | 0.31026 | 0 | 0.17117 | 2139.625 | 0.0355 | 2840 | 64000 | 2139.625 | 2840 | 24935.375 | 3465.375 | 1116030.125 | 24935.375 | 0
2021082408 | 3 | 0.65858 | 98787 | 0.23567 | 0 | 0.17406 | 2175.75 | 0.17163 | 13730.4 | 64000 | 2175.75 | 13730.4 | 18880.85 | -6054.525 | 1122615.525 | 18880.85 | 0
2021082409 | 3 | 0.70315 | 105472.5 | 0.18422 | 0 | 0.19766 | 2470.75 | 0.26631 | 21304.8 | 64000 | 2470.75 | 21304.8 | 17696.95 | -1183.9 | 1130384.825 | 17696.95 | 0
2021082410 | 3 | 0.75385 | 113077.5 | 0.1407 | 0 | 0.1628 | 2035 | 0.34952 | 27961.6 | 64000 | 2035 | 27961.6 | 19080.9 | 1383.95 | 1136770.175 | 19080.9 | 0
2021082411 | 3 | 0.80763 | 121144.5 | 0.09099 | 0 | 0.15897 | 1987.125 | 0.40176 | 32140.8 | 64000 | 1987.125 | 32140.8 | 23016.575 | 3935.675 | 1139219.85 | 23016.575 | 0
2021082412 | 3 | 0.86001 | 129001.5 | 0.03815 | 0 | 0.1419 | 1773.75 | 0.40656 | 32524.8 | 64000 | 1773.75 | 32524.8 | 30702.95 | 7686.375 | 1133983.15 | 30702.95 | 0
2021082413 | 3 | 0.9075 | 136125 | 0.02627 | 0 | 0.11921 | 1490.125 | 0.39677 | 31741.6 | 64000 | 1490.125 | 31741.6 | 38893.275 | 8190.325 | 1120556.125 | 38893.275 | 0
2021082414 | 3 | 0.94801 | 142201.5 | 0.01491 | 0 | 0.09725 | 1215.625 | 0.3573 | 28584 | 64000 | 1215.625 | 28584 | 48401.875 | 9508.6 | 1097620.5 | 48401.875 | 0
2021082415 | 3 | 0.97159 | 145738.5 | 0.01735 | 0 | 0.09362 | 1170.25 | 0.25316 | 20252.8 | 64000 | 1170.25 | 20252.8 | 60315.45 | 11913.575 | 1062771.3 | 60315.45 | 0
2021082416 | 3 | 0.98806 | 148209 | 0.04558 | 0 | 0.07497 | 937.125 | 0.20362 | 16289.6 | 64000 | 937.125 | 16289.6 | 66982.275 | 6666.825 | 1021255.275 | 66982.275 | 0
2021082417 | 3 | 1 | 150000 | 0.03847 | 0 | 0.071 | 887.5 | 0.15373 | 12298.4 | 64000 | 887.5 | 12298.4 | 72814.1 | 5831.825 | 973907.425 | 72814.1 | 0
2021082418 | 3 | 0.99984 | 149976 | 0.03964 | 0 | 0.12092 | 1511.5 | 0.10616 | 8492.8 | 64000 | 1511.5 | 8492.8 | 75971.7 | 3157.6 | 923401.975 | 75971.7 | 0
2021082419 | 3 | 0.98348 | 147522 | 0.04734 | 0 | 0.15135 | 1891.875 | 0.04344 | 3475.2 | 64000 | 1891.875 | 3475.2 | 78154.925 | 2183.225 | 870713.3 | 78154.925 | 0
2021082420 | 3 | 0.9428 | 141420 | 0.0467 | 0 | 0.18593 | 2324.125 | 0.00626 | 500.8 | 64000 | 2324.125 | 500.8 | 74595.075 | -3559.85 | 821584.475 | 74595.075 | 0
2021082421 | 3 | 0.90913 | 136369.5 | 0.04745 | 0 | 0.19307 | 2413.375 | 0 | 0 | 64000 | 2413.375 | 0 | 69956.125 | -4638.95 | 777094.6 | 69956.125 | 0
2021082422 | 3 | 0.85577 | 128365.5 | 0.0254 | 0 | 0.16864 | 2108 | 0 | 0 | 64000 | 2108 | 0 | 62257.5 | -7698.625 | 740303.35 | 62257.5 | 0
2021082423 | 3 | 0.78982 | 118473 | 0.01147 | 0 | 0.15583 | 1947.875 | 0 | 0 | 64000 | 1947.875 | 0 | 52525.125 | -9732.375 | 713244.475 | 52525.125 | 0
2021082424 | 3 | 0.72647 | 108970.5 | 0.00636 | 0 | 0.15258 | 1907.25 | 0 | 0 | 64000 | 1907.25 | 0 | 43063.25 | -9461.875 | 695647.475 | 43063.25 | 0
2021082501 | 4 | 0.67291 | 100936.5 | 0.01184 | 0 | 0.16735 | 2091.875 | 0 | 0 | 64000 | 2091.875 | 0 | 34844.625 | -8218.625 | 686269.1 | 34844.625 | 0
2021082502 | 4 | 0.6325 | 94875 | 0.0028 | 0 | 0.16428 | 2053.5 | 0 | 0 | 64000 | 2053.5 | 0 | 28821.5 | -6023.125 | 682913.85 | 28821.5 | 0
2021082503 | 4 | 0.60373 | 90559.5 | 0.00978 | 0 | 0.15168 | 1896 | 0 | 0 | 64000 | 1896 | 0 | 24663.5 | -4158 | 683716.6 | 24663.5 | 0
2021082504 | 4 | 0.58504 | 87756 | 0.02074 | 0 | 0.15379 | 1922.375 | 0 | 0 | 64000 | 1922.375 | 0 | 21833.625 | -2829.875 | 687349.225 | 21833.625 | 0
2021082505 | 4 | 0.58236 | 87354 | 0.03168 | 0 | 0.18911 | 2363.875 | 0 | 0 | 64000 | 2363.875 | 0 | 20990.125 | -843.5 | 691825.35 | 20990.125 | 0
2021082506 | 4 | 0.59784 | 89676 | 0.00717 | 0 | 0.24242 | 3030.25 | 0 | 0 | 64000 | 3030.25 | 0 | 22645.75 | 1655.625 | 694645.85 | 22645.75 | 0
2021082507 | 4 | 0.6305 | 94575 | 0.00414 | 0 | 0.33688 | 4211 | 0.01906 | 1524.8 | 64000 | 4211 | 1524.8 | 24839.2 | 2193.45 | 695272.9 | 24839.2 | 0
2021082508 | 4 | 0.66239 | 99358.5 | 0.01758 | 0 | 0.43469 | 5433.625 | 0.08819 | 7055.2 | 64000 | 5433.625 | 7055.2 | 22869.675 | -1969.525 | 697869.475 | 22869.675 | 0
2021082509 | 4 | 0.70173 | 105259.5 | 0.02605 | 0 | 0.53908 | 6738.5 | 0.24379 | 19503.2 | 64000 | 6738.5 | 19503.2 | 15017.8 | -7851.875 | 708317.925 | 15017.8 | 0
2021082510 | 4 | 0.75399 | 113098.5 | 0.0174 | 0 | 0.65702 | 8212.75 | 0.3806 | 30448 | 64000 | 8212.75 | 30448 | 10437.75 | -4580.05 | 723346.425 | 10437.75 | 0
2021082511 | 4 | 0.81066 | 121599 | 0.00444 | 0 | 0.7021 | 8776.25 | 0.47387 | 37909.6 | 64000 | 8776.25 | 37909.6 | 10913.15 | 475.4 | 737899.525 | 10913.15 | 0
2021082512 | 4 | 0.86327 | 129490.5 | 0.00682 | 0 | 0.69669 | 8708.625 | 0.5109 | 40872 | 64000 | 8708.625 | 40872 | 15909.875 | 4996.725 | 747455.9 | 15909.875 | 0
2021082513 | 4 | 0.90229 | 135343.5 | 0.0078 | 0 | 0.69896 | 8737 | 0.54751 | 43800.8 | 64000 | 8737 | 43800.8 | 18805.7 | 2895.825 | 754116.45 | 18805.7 | 0
2021082514 | 4 | 0.93442 | 140163 | 0.00045 | 0 | 0.73025 | 9128.125 | 0.57011 | 45608.8 | 64000 | 9128.125 | 45608.8 | 21426.075 | 2620.375 | 758156.625 | 21426.075 | 0
2021082515 | 4 | 0.95186 | 142779 | 0.00023 | 0 | 0.74431 | 9303.875 | 0.54358 | 43486.4 | 64000 | 9303.875 | 43486.4 | 25988.725 | 4562.65 | 757634.15 | 25988.725 | 0
2021082516 | 4 | 0.96252 | 144378 | 0.00163 | 0 | 0.72178 | 9022.25 | 0.48941 | 39152.8 | 64000 | 9022.25 | 39152.8 | 32202.95 | 6214.225 | 750897.45 | 32202.95 | 0
2021082517 | 4 | 0.96719 | 145078.5 | 0.00241 | 0 | 0.67976 | 8497 | 0.40141 | 32112.8 | 64000 | 8497 | 32112.8 | 40468.7 | 8265.75 | 735895 | 40468.7 | 0
2021082518 | 4 | 0.9621 | 144315 | 0.00383 | 0 | 0.67269 | 8408.625 | 0.31363 | 25090.4 | 64000 | 8408.625 | 25090.4 | 46815.975 | 6347.275 | 714545.275 | 46815.975 | 0
2021082519 | 4 | 0.94557 | 141835.5 | 0.01197 | 0 | 0.64042 | 8005.25 | 0.12523 | 10018.4 | 64000 | 8005.25 | 10018.4 | 59811.85 | 12995.875 | 680199.675 | 59811.85 | 0
2021082520 | 4 | 0.9107 | 136605 | 0.1099 | 0 | 0.59187 | 7398.375 | 0.01225 | 980 | 64000 | 7398.375 | 980 | 64226.625 | 4414.775 | 641439.3 | 64226.625 | 0
2021082521 | 4 | 0.88069 | 132103.5 | 0.13438 | 0 | 0.5752 | 7190 | 0 | 0 | 64000 | 7190 | 0 | 60913.5 | -3313.125 | 605992.05 | 60913.5 | 0
2021082522 | 4 | 0.83345 | 125017.5 | 0.06298 | 0 | 0.56228 | 7028.5 | 0 | 0 | 64000 | 7028.5 | 0 | 53989 | -6924.5 | 577469.3 | 53989 | 0
2021082523 | 4 | 0.77203 | 115804.5 | 0.10247 | 0 | 0.51409 | 6426.125 | 0 | 0 | 64000 | 6426.125 | 0 | 45378.375 | -8610.625 | 557557.175 | 45378.375 | 0
2021082524 | 4 | 0.7134 | 107010 | 0.16999 | 0 | 0.45533 | 5691.625 | 0 | 0 | 64000 | 5691.625 | 0 | 37318.375 | -8060 | 545705.05 | 37318.375 | 0
2021082601 | 5 | 0.66168 | 99252 | 0.1543 | 0 | 0.41118 | 5139.75 | 0 | 0 | 64000 | 5139.75 | 0 | 30112.25 | -7206.125 | 541059.05 | 30112.25 | 0
2021082602 | 5 | 0.62635 | 93952.5 | 0.18674 | 0 | 0.3801 | 4751.25 | 0 | 0 | 64000 | 4751.25 | 0 | 25201.25 | -4911 | 541324.05 | 25201.25 | 0
2021082603 | 5 | 0.59981 | 89971.5 | 0.26808 | 0 | 0.34738 | 4342.25 | 0 | 0 | 64000 | 4342.25 | 0 | 21629.25 | -3572 | 545161.05 | 21629.25 | 0
2021082604 | 5 | 0.58411 | 87616.5 | 0.29758 | 0 | 0.27241 | 3405.125 | 0 | 0 | 64000 | 3405.125 | 0 | 20211.375 | -1417.875 | 550415.925 | 20211.375 | 0
2021082605 | 5 | 0.58139 | 87208.5 | 0.24722 | 0 | 0.26956 | 3369.5 | 0 | 0 | 64000 | 3369.5 | 0 | 19839 | -372.375 | 556043.175 | 19839 | 0
2021082606 | 5 | 0.59803 | 89704.5 | 0.19355 | 0 | 0.28602 | 3575.25 | 0 | 0 | 64000 | 3575.25 | 0 | 22129.25 | 2290.25 | 559380.175 | 22129.25 | 0
2021082607 | 5 | 0.63504 | 95256 | 0.11694 | 0 | 0.25811 | 3226.375 | 0.05642 | 4513.6 | 64000 | 3226.375 | 4513.6 | 23516.025 | 1386.775 | 561330.4 | 23516.025 | 0
2021082608 | 5 | 0.66708 | 100062 | 0.06786 | 0 | 0.21196 | 2649.5 | 0.30753 | 24602.4 | 64000 | 2649.5 | 24602.4 | 8810.1 | -14705.925 | 577986.55 | 8810.1 | 0
2021082609 | 5 | 0.70679 | 106018.5 | 0.04021 | 0 | 0.17247 | 2155.875 | 0.46965 | 37572 | 64000 | 2155.875 | 37572 | 2290.625 | -6519.475 | 601162.175 | 2290.625 | 0
2021082610 | 5 | 0.75521 | 113281.5 | 0.00076 | 0 | 0.17827 | 2228.375 | 0.53157 | 42525.6 | 64000 | 2228.375 | 42525.6 | 4527.525 | 2236.9 | 622100.9 | 4527.525 | 0
2021082611 | 5 | 0.80951 | 121426.5 | 0.00643 | 0 | 0.17182 | 2147.75 | 0.5248 | 41984 | 64000 | 2147.75 | 41984 | 13294.75 | 8767.225 | 634272.4 | 13294.75 | 0
2021082612 | 5 | 0.86531 | 129796.5 | 0.00622 | 0 | 0.17236 | 2154.5 | 0.53474 | 42779.2 | 64000 | 2154.5 | 42779.2 | 20862.8 | 7568.05 | 638875.85 | 20862.8 | 0
2021082613 | 5 | 0.91602 | 137403 | 0.00586 | 0 | 0.18289 | 2286.125 | 0.54365 | 43492 | 64000 | 2286.125 | 43492 | 27624.875 | 6762.075 | 636717.225 | 27624.875 | 0
2021082614 | 5 | 0.95608 | 143412 | 0.00695 | 0 | 0.18267 | 2283.375 | 0.52775 | 42220 | 64000 | 2283.375 | 42220 | 34908.625 | 7283.75 | 627274.85 | 34908.625 | 0
2021082615 | 5 | 0.97544 | 146316 | 0.00613 | 0 | 0.17559 | 2194.875 | 0.52838 | 42270.4 | 64000 | 2194.875 | 42270.4 | 37850.725 | 2942.1 | 614890.375 | 37850.725 | 0
2021082616 | 5 | 0.98012 | 147018 | 0.02382 | 0 | 0.16466 | 2058.25 | 0.53293 | 42634.4 | 64000 | 2058.25 | 42634.4 | 38325.35 | 474.625 | 602031.275 | 38325.35 | 0
2021082617 | 5 | 0.97341 | 146011.5 | 0.13445 | 0 | 0.14463 | 1807.875 | 0.49302 | 39441.6 | 64000 | 1807.875 | 39441.6 | 40762.025 | 2436.675 | 586735.5 | 40762.025 | 0
2021082618 | 5 | 0.96696 | 145044 | 0.08751 | 0 | 0.13833 | 1729.125 | 0.38186 | 30548.8 | 64000 | 1729.125 | 30548.8 | 48766.075 | 8004.05 | 563435.675 | 48766.075 | 0
2021082619 | 5 | 0.94933 | 142399.5 | 0.05105 | 0 | 0.16393 | 2049.125 | 0.15336 | 12268.8 | 64000 | 2049.125 | 12268.8 | 64081.575 | 15315.5 | 524820.35 | 64081.575 | 0
2021082620 | 5 | 0.91535 | 137302.5 | 0.08236 | 0 | 0.1569 | 1961.25 | 0.01874 | 1499.2 | 64000 | 1961.25 | 1499.2 | 69842.05 | 5760.475 | 480444.55 | 69842.05 | 0
2021082621 | 5 | 0.88906 | 133359 | 0.03394 | 0 | 0.1334 | 1667.5 | 0 | 0 | 64000 | 1667.5 | 0 | 67691.5 | -2150.55 | 438219.3 | 67691.5 | 0
2021082622 | 5 | 0.84472 | 126708 | 0.00276 | 0 | 0.13647 | 1705.875 | 0 | 0 | 64000 | 1705.875 | 0 | 61002.125 | -6689.375 | 402683.425 | 61002.125 | 0
2021082623 | 5 | 0.78605 | 117907.5 | 0.00161 | 0 | 0.15109 | 1888.625 | 0 | 0 | 64000 | 1888.625 | 0 | 52018.875 | -8983.25 | 376130.8 | 52018.875 | 0
2021082624 | 5 | 0.72653 | 108979.5 | 0.00875 | 0 | 0.18877 | 2359.625 | 0 | 0 | 64000 | 2359.625 | 0 | 42619.875 | -9399 | 358977.175 | 42619.875 | 0
2021082701 | 6 | 0.6765 | 101475 | 0.10485 | 0 | 0.23326 | 2915.75 | 0 | 0 | 64000 | 2915.75 | 0 | 34559.25 | -8060.625 | 349884.175 | 34559.25 | 0
2021082702 | 6 | 0.63995 | 95992.5 | 0.10372 | 0 | 0.26785 | 3348.125 | 0 | 0 | 64000 | 3348.125 | 0 | 28644.375 | -5914.875 | 346706.05 | 28644.375 | 0
2021082703 | 6 | 0.6125 | 91875 | 0.04357 | 0 | 0.32549 | 4068.625 | 0 | 0 | 64000 | 4068.625 | 0 | 23806.375 | -4838 | 348365.925 | 23806.375 | 0
2021082704 | 6 | 0.59577 | 89365.5 | 0.01062 | 0 | 0.38425 | 4803.125 | 0 | 0 | 64000 | 4803.125 | 0 | 20562.375 | -3244 | 353269.8 | 20562.375 | 0
2021082705 | 6 | 0.59119 | 88678.5 | 0.00446 | 0 | 0.42497 | 5312.125 | 0 | 0 | 64000 | 5312.125 | 0 | 19366.375 | -1196 | 359369.675 | 19366.375 | 0
2021082706 | 6 | 0.60688 | 91032 | 0.01193 | 0 | 0.48423 | 6052.875 | 0 | 0 | 64000 | 6052.875 | 0 | 20979.125 | 1612.75 | 363856.8 | 20979.125 | 0
2021082707 | 6 | 0.63996 | 95994 | 0.0263 | 0 | 0.55301 | 6912.625 | 0.03247 | 2597.6 | 64000 | 6912.625 | 2597.6 | 22483.775 | 1504.65 | 366839.275 | 22483.775 | 0
2021082708 | 6 | 0.67148 | 100722 | 0.02831 | 0 | 0.59134 | 7391.75 | 0.13382 | 10705.6 | 64000 | 7391.75 | 10705.6 | 18624.65 | -3859.125 | 373680.875 | 18624.65 | 0
2021082709 | 6 | 0.71392 | 107088 | 0.00928 | 0 | 0.62184 | 7773 | 0.20346 | 16276.8 | 64000 | 7773 | 16276.8 | 19038.2 | 413.55 | 380108.925 | 19038.2 | 0
2021082710 | 6 | 0.76431 | 114646.5 | 0.00391 | 0 | 0.60773 | 7596.625 | 0.23203 | 18562.4 | 64000 | 7596.625 | 18562.4 | 24487.475 | 5449.275 | 381087.7 | 24487.475 | 0
2021082711 | 6 | 0.8195 | 122925 | 0.00557 | 0 | 0.53133 | 6641.625 | 0.24725 | 19780 | 64000 | 6641.625 | 19780 | 32503.375 | 8015.9 | 374050.575 | 32503.375 | 0
2021082712 | 6 | 0.87429 | 131143.5 | 0.00584 | 0 | 0.46173 | 5771.625 | 0.31308 | 25046.4 | 64000 | 5771.625 | 25046.4 | 36325.475 | 3822.1 | 363191.35 | 36325.475 | 0
2021082713 | 6 | 0.92238 | 138357 | 0.00316 | 0 | 0.37308 | 4663.5 | 0.38619 | 30895.2 | 64000 | 4663.5 | 30895.2 | 38798.3 | 2472.825 | 349859.3 | 38798.3 | 0
2021082714 | 6 | 0.95839 | 143758.5 | 0.0045 | 0 | 0.30568 | 3821 | 0.41852 | 33481.6 | 64000 | 3821 | 33481.6 | 42455.9 | 3657.6 | 332869.65 | 42455.9 | 0
2021082715 | 6 | 0.97694 | 146541 | 0.02753 | 0 | 0.21825 | 2728.125 | 0.41413 | 33130.4 | 64000 | 2728.125 | 33130.4 | 46682.475 | 4226.575 | 311653.425 | 46682.475 | 0
2021082716 | 6 | 0.97481 | 146221.5 | 0.03825 | 0 | 0.14816 | 1852 | 0.38725 | 30980 | 64000 | 1852 | 30980 | 49389.5 | 2707.025 | 287730.175 | 49389.5 | 0
2021082717 | 6 | 0.96887 | 145330.5 | 0.05573 | 0 | 0.12266 | 1533.25 | 0.33894 | 27115.2 | 64000 | 1533.25 | 27115.2 | 52682.05 | 3292.55 | 260514.375 | 52682.05 | 0
2021082718 | 6 | 0.95576 | 143364 | 0.07673 | 0 | 0.17167 | 2145.875 | 0.24887 | 19909.6 | 64000 | 2145.875 | 19909.6 | 57308.525 | 4626.475 | 228672.1 | 57308.525 | 0
2021082719 | 6 | 0.92843 | 139264.5 | 0.06578 | 0 | 0.18363 | 2295.375 | 0.14893 | 11914.4 | 64000 | 2295.375 | 11914.4 | 61054.725 | 3746.2 | 193083.625 | 61054.725 | 0
2021082720 | 6 | 0.89102 | 133653 | 0.11509 | 0 | 0.15002 | 1875.25 | 0.02928 | 2342.4 | 64000 | 1875.25 | 2342.4 | 65435.35 | 4380.625 | 153114.525 | 65435.35 | 0
2021082721 | 6 | 0.86149 | 129223.5 | 0.12029 | 0 | 0.11212 | 1401.5 | 0 | 0 | 64000 | 1401.5 | 0 | 63822 | -1613.35 | 114758.775 | 63822 | 0
2021082722 | 6 | 0.82112 | 123168 | 0.07277 | 0 | 0.10853 | 1356.625 | 0 | 0 | 64000 | 1356.625 | 0 | 57811.375 | -6010.625 | 82413.65 | 57811.375 | 0
2021082723 | 6 | 0.77161 | 115741.5 | 0.04604 | 0 | 0.10259 | 1282.375 | 0 | 0 | 64000 | 1282.375 | 0 | 50459.125 | -7352.25 | 57420.775 | 50459.125 | 0
2021082724 | 6 | 0.71883 | 107824.5 | 0.0245 | 0 | 0.10943 | 1367.875 | 0 | 0 | 64000 | 1367.875 | 0 | 42456.625 | -8002.5 | 40430.4 | 42456.625 | 0
2021082801 | 7 | 0.67326 | 100989 | 0.01385 | 0 | 0.10457 | 1307.125 | 0 | 0 | 64000 | 1307.125 | 0 | 35681.875 | -6774.75 | 30214.775 | 35681.875 | 0
2021082802 | 7 | 0.63534 | 95301 | 0.0213 | 0 | 0.11459 | 1432.375 | 0 | 0 | 64000 | 1432.375 | 0 | 29868.625 | -5813.25 | 25812.4 | 29868.625 | 0
2021082803 | 7 | 0.60828 | 91242 | 0.02844 | 0 | 0.10927 | 1365.875 | 0 | 0 | 64000 | 1365.875 | 0 | 25876.125 | -3992.5 | 25402.525 | 25876.125 | 0
2021082804 | 7 | 0.58825 | 88237.5 | 0.04712 | 0 | 0.12808 | 1601 | 0 | 0 | 64000 | 1601 | 0 | 22636.5 | -3239.625 | 28232.275 | 22636.5 | 0
2021082805 | 7 | 0.57765 | 86647.5 | 0.09077 | 0 | 0.13709 | 1713.625 | 0 | 0 | 64000 | 1713.625 | 0 | 20933.875 | -1702.625 | 32764.65 | 20933.875 | 0
2021082806 | 7 | 0.57646 | 86469 | 0.15244 | 0 | 0.18654 | 2331.75 | 0 | 0 | 64000 | 2331.75 | 0 | 20137.25 | -796.625 | 38093.65 | 20137.25 | 0
2021082807 | 7 | 0.58462 | 87693 | 0.15803 | 0 | 0.29634 | 3704.25 | 0.04448 | 3558.4 | 64000 | 3704.25 | 3558.4 | 16430.35 | -3706.9 | 47129.55 | 16430.35 | 0
2021082808 | 7 | 0.59904 | 89856 | 0.15232 | 0 | 0.41153 | 5144.125 | 0.23405 | 18724 | 64000 | 5144.125 | 18724 | 1987.875 | -14442.475 | 70607.925 | 1987.875 | 0
2021082809 | 7 | 0.63633 | 95449.5 | 0.13182 | 0 | 0.39623 | 4952.875 | 0.37237 | 29789.6 | 64000 | 4952.875 | 26496.625 | 0 | -1987.875 | 96074.175 | 0 | 0
2021082810 | 7 | 0.68456 | 102684 | 0.11575 | 0 | 0.39305 | 4913.125 | 0.44489 | 35591.2 | 64000 | 4913.125 | 33770.875 | 0 | 0 | 121540.425 | 0 | 0
2021082811 | 7 | 0.73354 | 110031 | 0.13313 | 0 | 0.41665 | 5208.125 | 0.50339 | 40271.2 | 64000 | 5208.125 | 40271.2 | 551.675 | 551.675 | 146455 | 551.675 | 0
2021082812 | 7 | 0.77942 | 116913 | 0.11866 | 0 | 0.35223 | 4402.875 | 0.55393 | 44314.4 | 64000 | 4402.875 | 44314.4 | 4195.725 | 3644.05 | 167725.525 | 4195.725 | 0
2021082813 | 7 | 0.8148 | 122220 | 0.09719 | 0 | 0.24233 | 3029.125 | 0.6 | 48000 | 64000 | 3029.125 | 48000 | 7190.875 | 2995.15 | 186000.9 | 7190.875 | 0
2021082814 | 7 | 0.83884 | 125826 | 0.07833 | 0 | 0.21009 | 2626.125 | 0.61484 | 49187.2 | 64000 | 2626.125 | 49187.2 | 10012.675 | 2821.8 | 201454.475 | 10012.675 | 0
2021082815 | 7 | 0.85455 | 128182.5 | 0.13296 | 0 | 0.18161 | 2270.125 | 0.61308 | 49046.4 | 64000 | 2270.125 | 49046.4 | 12865.975 | 2853.3 | 214054.75 | 12865.975 | 0
2021082816 | 7 | 0.86391 | 129586.5 | 0.14679 | 0 | 0.16699 | 2087.375 | 0.58911 | 47128.8 | 64000 | 2087.375 | 47128.8 | 16370.325 | 3504.35 | 223150.675 | 16370.325 | 0
2021082817 | 7 | 0.86818 | 130227 | 0.12154 | 0 | 0.1757 | 2196.25 | 0.55251 | 44200.8 | 64000 | 2196.25 | 44200.8 | 19829.95 | 3459.625 | 228786.975 | 19829.95 | 0
2021082818 | 7 | 0.86397 | 129595.5 | 0.17897 | 0 | 0.20712 | 2589 | 0.47259 | 37807.2 | 64000 | 2589 | 37807.2 | 25199.3 | 5369.35 | 229053.925 | 25199.3 | 0
2021082819 | 7 | 0.84486 | 126729 | 0.21584 | 0 | 0.2321 | 2901.25 | 0.24141 | 19312.8 | 64000 | 2901.25 | 19312.8 | 40514.95 | 15315.65 | 214005.225 | 40514.95 | 0
2021082820 | 7 | 0.81691 | 122536.5 | 0.25854 | 0 | 0.26911 | 3363.875 | 0.03137 | 2509.6 | 64000 | 3363.875 | 2509.6 | 52663.025 | 12148.075 | 186808.45 | 52663.025 | 0
2021082821 | 7 | 0.79412 | 119118 | 0.25482 | 0 | 0.29954 | 3744.25 | 0 | 0 | 64000 | 3744.25 | 0 | 51373.75 | -1289.275 | 160900.95 | 51373.75 | 0
2021082822 | 7 | 0.76106 | 114159 | 0.31567 | 0 | 0.31989 | 3998.625 | 0 | 0 | 64000 | 3998.625 | 0 | 46160.375 | -5213.375 | 140206.825 | 46160.375 | 0
2021082823 | 7 | 0.71722 | 107583 | 0.33142 | 0 | 0.32239 | 4029.875 | 0 | 0 | 64000 | 4029.875 | 0 | 39553.125 | -6607.25 | 126119.95 | 39553.125 | 0
2021082824 | 7 | 0.67108 | 100662 | 0.35056 | 0 | 0.33671 | 4208.875 | 0 | 0 | 64000 | 4208.875 | 0 | 32453.125 | -7100 | 119133.075 | 32453.125 | 0
2021082901 | 1 | 0.62986 | 94479 | 0.33975 | 0 | 0.32632 | 4079 | 0 | 0 | 64000 | 4079 | 0 | 26400 | -6053.125 | 118199.325 | 26400 | 0
2021082902 | 1 | 0.59541 | 89311.5 | 0.29798 | 0 | 0.2683 | 3353.75 | 0 | 0 | 64000 | 3353.75 | 0 | 21957.75 | -4442.25 | 121707.825 | 21957.75 | 0
2021082903 | 1 | 0.57107 | 85660.5 | 0.26836 | 0 | 0.24622 | 3077.75 | 0 | 0 | 64000 | 3077.75 | 0 | 18582.75 | -3375 | 128591.325 | 18582.75 | 0
2021082904 | 1 | 0.55237 | 82855.5 | 0.22277 | 0 | 0.24528 | 3066 | 0 | 0 | 64000 | 3066 | 0 | 15789.5 | -2793.25 | 138268.075 | 15789.5 | 0
2021082905 | 1 | 0.54204 | 81306 | 0.20909 | 0 | 0.23053 | 2881.625 | 0 | 0 | 64000 | 2881.625 | 0 | 14424.375 | -1365.125 | 149309.95 | 14424.375 | 0
2021082906 | 1 | 0.53883 | 80824.5 | 0.17315 | 0 | 0.22303 | 2787.875 | 0 | 0 | 64000 | 2787.875 | 0 | 14036.625 | -387.75 | 160739.575 | 14036.625 | 0
2021082907 | 1 | 0.54247 | 81370.5 | 0.1599 | 0 | 0.21657 | 2707.125 | 0.03448 | 2758.4 | 64000 | 2707.125 | 2758.4 | 11904.975 | -2131.65 | 174300.85 | 11904.975 | 0
2021082908 | 1 | 0.55064 | 82596 | 0.1602 | 0 | 0.21871 | 2733.875 | 0.17487 | 13989.6 | 64000 | 2733.875 | 13989.6 | 1872.525 | -10032.45 | 197894.575 | 1872.525 | 0
2021082909 | 1 | 0.58424 | 87636 | 0.13093 | 0 | 0.265 | 3312.5 | 0.3426 | 27408 | 64000 | 3312.5 | 20323.5 | 0 | -1872.525 | 223360.825 | 0 | 0
2021082910 | 1 | 0.62794 | 94191 | 0.0967 | 0 | 0.28822 | 3602.75 | 0.43053 | 34442.4 | 64000 | 3602.75 | 26588.25 | 0 | 0 | 248827.075 | 0 | 0
2021082911 | 1 | 0.66821 | 100231.5 | 0.06096 | 0 | 0.30982 | 3872.75 | 0.46631 | 37304.8 | 64000 | 3872.75 | 32358.75 | 0 | 0 | 274293.325 | 0 | 0
2021082912 | 1 | 0.71039 | 106558.5 | 0.05883 | 0 | 0.32875 | 4109.375 | 0.47993 | 38394.4 | 64000 | 4109.375 | 38394.4 | 54.725 | 54.725 | 299704.85 | 54.725 | 0
2021082913 | 1 | 0.75192 | 112788 | 0.05873 | 0 | 0.34042 | 4255.25 | 0.4727 | 37816 | 64000 | 4255.25 | 37816 | 6716.75 | 6662.025 | 318454.35 | 6716.75 | 0
2021082914 | 1 | 0.7796 | 116940 | 0.09651 | 0 | 0.38393 | 4799.125 | 0.49062 | 39249.6 | 64000 | 4799.125 | 39249.6 | 8891.275 | 2174.525 | 335029.325 | 8891.275 | 0
2021082915 | 1 | 0.79568 | 119352 | 0.13882 | 0 | 0.39004 | 4875.5 | 0.52387 | 41909.6 | 64000 | 4875.5 | 41909.6 | 8566.9 | -324.375 | 351928.675 | 8566.9 | 0
2021082916 | 1 | 0.80733 | 121099.5 | 0.15082 | 0 | 0.3294 | 4117.5 | 0.48566 | 38852.8 | 64000 | 4117.5 | 38852.8 | 14129.2 | 5562.3 | 363265.725 | 14129.2 | 0
2021082917 | 1 | 0.8155 | 122325 | 0.16359 | 0 | 0.23352 | 2919 | 0.34472 | 27577.6 | 64000 | 2919 | 27577.6 | 27828.4 | 13699.2 | 360903.575 | 27828.4 | 0
2021082918 | 1 | 0.81598 | 122397 | 0.15477 | 0 | 0.1689 | 2111.25 | 0.22966 | 18372.8 | 64000 | 2111.25 | 18372.8 | 37912.95 | 10084.55 | 348456.875 | 37912.95 | 0
2021082919 | 1 | 0.81118 | 121677 | 0.24837 | 0 | 0.22718 | 2839.75 | 0.04683 | 3746.4 | 64000 | 2839.75 | 3746.4 | 51090.85 | 13177.9 | 322832.275 | 51090.85 | 0
2021082920 | 1 | 0.79667 | 119500.5 | 0.31771 | 0 | 0.21156 | 2644.5 | 0.00689 | 551.2 | 64000 | 2644.5 | 551.2 | 52304.8 | 1213.95 | 295993.725 | 52304.8 | 0
2021082921 | 1 | 0.78185 | 117277.5 | 0.27948 | 0 | 0.18398 | 2299.75 | 0 | 0 | 64000 | 2299.75 | 0 | 50977.75 | -1327.05 | 270482.225 | 50977.75 | 0
2021082922 | 1 | 0.74915 | 112372.5 | 0.35634 | 0 | 0.17142 | 2142.75 | 0 | 0 | 64000 | 2142.75 | 0 | 46229.75 | -4748 | 249718.725 | 46229.75 | 0
2021082923 | 1 | 0.70072 | 105108 | 0.44497 | 0 | 0.17121 | 2140.125 | 0 | 0 | 64000 | 2140.125 | 0 | 38967.875 | -7261.875 | 236217.1 | 38967.875 | 0
2021082924 | 1 | 0.65369 | 98053.5 | 0.45135 | 0 | 0.15959 | 1994.875 | 0 | 0 | 64000 | 1994.875 | 0 | 32058.625 | -6909.25 | 229624.725 | 32058.625 | 0
2021083001 | 2 | 0.61151 | 91726.5 | 0.46047 | 0 | 0.14777 | 1847.125 | 0 | 0 | 64000 | 1847.125 | 0 | 25879.375 | -6179.25 | 229211.6 | 25879.375 | 0
2021083002 | 2 | 0.58201 | 87301.5 | 0.53295 | 0 | 0.151 | 1887.5 | 0 | 0 | 64000 | 1887.5 | 0 | 21414 | -4465.375 | 233263.85 | 21414 | 0
2021083003 | 2 | 0.56289 | 84433.5 | 0.58011 | 0 | 0.16353 | 2044.125 | 0 | 0 | 64000 | 2044.125 | 0 | 18389.375 | -3024.625 | 240340.725 | 18389.375 | 0
2021083004 | 2 | 0.55207 | 82810.5 | 0.60069 | 0 | 0.15947 | 1993.375 | 0 | 0 | 64000 | 1993.375 | 0 | 16817.125 | -1572.25 | 248989.85 | 16817.125 | 0
2021083005 | 2 | 0.554 | 83100 | 0.54917 | 0 | 0.18293 | 2286.625 | 0 | 0 | 64000 | 2286.625 | 0 | 16813.375 | -3.75 | 257642.725 | 16813.375 | 0
2021083006 | 2 | 0.57652 | 86478 | 0.50246 | 0 | 0.2103 | 2628.75 | 0 | 0 | 64000 | 2628.75 | 0 | 19849.25 | 3035.875 | 263259.725 | 19849.25 | 0
2021083007 | 2 | 0.61762 | 92643 | 0.42984 | 0 | 0.26387 | 3298.375 | 0.02691 | 2152.8 | 64000 | 3298.375 | 2152.8 | 23191.825 | 3342.575 | 265534.15 | 23191.825 | 0
2021083008 | 2 | 0.64859 | 97288.5 | 0.41501 | 0 | 0.29344 | 3668 | 0.07954 | 6363.2 | 64000 | 3668 | 6363.2 | 23257.3 | 65.475 | 267743.1 | 23257.3 | 0
2021083009 | 2 | 0.68075 | 102112.5 | 0.41622 | 0 | 0.30526 | 3815.75 | 0.15239 | 12191.2 | 64000 | 3815.75 | 12191.2 | 22105.55 | -1151.75 | 271103.8 | 22105.55 | 0
2021083010 | 2 | 0.71772 | 107658 | 0.283 | 0 | 0.27175 | 3396.875 | 0.36641 | 29312.8 | 64000 | 3396.875 | 29312.8 | 10948.325 | -11157.225 | 285621.725 | 10948.325 | 0
2021083011 | 2 | 0.7591 | 113865 | 0.29427 | 0 | 0.27145 | 3393.125 | 0.46471 | 37176.8 | 64000 | 3393.125 | 37176.8 | 9295.075 | -1653.25 | 301792.9 | 9295.075 | 0
2021083012 | 2 | 0.8013 | 120195 | 0.21101 | 0 | 0.30239 | 3779.875 | 0.54094 | 43275.2 | 64000 | 3779.875 | 43275.2 | 9139.925 | -155.15 | 318119.225 | 9139.925 | 0
2021083013 | 2 | 0.83905 | 125857.5 | 0.1853 | 0 | 0.27036 | 3379.5 | 0.59162 | 47329.6 | 64000 | 3379.5 | 47329.6 | 11148.4 | 2008.475 | 332437.075 | 11148.4 | 0
2021083014 | 2 | 0.87452 | 131178 | 0.18758 | 0 | 0.23266 | 2908.25 | 0.59819 | 47855.2 | 64000 | 2908.25 | 47855.2 | 16414.55 | 5266.15 | 341488.775 | 16414.55 | 0
2021083015 | 2 | 0.89824 | 134736 | 0.18739 | 0 | 0.18261 | 2282.625 | 0.59602 | 47681.6 | 64000 | 2282.625 | 47681.6 | 20771.775 | 4357.225 | 346183.25 | 20771.775 | 0
2021083016 | 2 | 0.91211 | 136816.5 | 0.20474 | 0 | 0.16726 | 2090.75 | 0.56123 | 44898.4 | 64000 | 2090.75 | 44898.4 | 25827.35 | 5055.575 | 345822.15 | 25827.35 | 0
2021083017 | 2 | 0.91595 | 137392.5 | 0.23375 | 0 | 0.22905 | 2863.125 | 0.51879 | 41503.2 | 64000 | 2863.125 | 41503.2 | 29026.175 | 3198.825 | 342262.225 | 29026.175 | 0
2021083018 | 2 | 0.90931 | 136396.5 | 0.20733 | 0 | 0.29477 | 3684.625 | 0.42137 | 33709.6 | 64000 | 3684.625 | 33709.6 | 35002.275 | 5976.1 | 332726.2 | 35002.275 | 0
2021083019 | 2 | 0.88294 | 132441 | 0.22353 | 0 | 0.35545 | 4443.125 | 0.1877 | 15016 | 64000 | 4443.125 | 15016 | 48981.875 | 13979.6 | 309210.575 | 48981.875 | 0
2021083020 | 2 | 0.84859 | 127288.5 | 0.28657 | 0 | 0.34615 | 4326.875 | 0.01891 | 1512.8 | 64000 | 4326.875 | 1512.8 | 57448.825 | 8466.95 | 277228 | 57448.825 | 0
2021083021 | 2 | 0.82099 | 123148.5 | 0.34502 | 0 | 0.41224 | 5153 | 0 | 0 | 64000 | 5153 | 0 | 53995.5 | -3453.325 | 248698.75 | 53995.5 | 0
2021083022 | 2 | 0.77729 | 116593.5 | 0.28436 | 0 | 0.37746 | 4718.25 | 0 | 0 | 64000 | 4718.25 | 0 | 47875.25 | -6120.25 | 226289.75 | 47875.25 | 0
2021083023 | 2 | 0.71917 | 107875.5 | 0.2617 | 0 | 0.34216 | 4277 | 0 | 0 | 64000 | 4277 | 0 | 39598.5 | -8276.75 | 212157.5 | 39598.5 | 0
2021083024 | 2 | 0.66368 | 99552 | 0.31997 | 0 | 0.36282 | 4535.25 | 0 | 0 | 64000 | 4535.25 | 0 | 31016.75 | -8581.75 | 206607 | 31016.75 | 0
2021083101 | 3 | 0.61771 | 92656.5 | 0.29757 | 0 | 0.34561 | 4320.125 | 0 | 0 | 64000 | 4320.125 | 0 | 24336.375 | -6680.375 | 207736.875 | 24336.375 | 0
2021083102 | 3 | 0.58529 | 87793.5 | 0.19212 | 0 | 0.35985 | 4498.125 | 0 | 0 | 64000 | 4498.125 | 0 | 19295.375 | -5041 | 213907.75 | 19295.375 | 0
2021083103 | 3 | 0.56514 | 84771 | 0.17901 | 0 | 0.37027 | 4628.375 | 0 | 0 | 64000 | 4628.375 | 0 | 16142.625 | -3152.75 | 223231.375 | 16142.625 | 0
2021083104 | 3 | 0.54941 | 82411.5 | 0.16656 | 0 | 0.29794 | 3724.25 | 0 | 0 | 64000 | 3724.25 | 0 | 14687.25 | -1455.375 | 234010.375 | 14687.25 | 0
2021083105 | 3 | 0.54812 | 82218 | 0.12004 | 0 | 0.23873 | 2984.125 | 0 | 0 | 64000 | 2984.125 | 0 | 15233.875 | 546.625 | 244242.75 | 15233.875 | 0
2021083106 | 3 | 0.56872 | 85308 | 0.08646 | 0 | 0.20281 | 2535.125 | 0 | 0 | 64000 | 2535.125 | 0 | 18772.875 | 3539 | 250936.125 | 18772.875 | 0
2021083107 | 3 | 0.60847 | 91270.5 | 0.05966 | 0 | 0.21728 | 2716 | 0.02349 | 1879.2 | 64000 | 2716 | 1879.2 | 22675.3 | 3902.425 | 253727.075 | 22675.3 | 0
2021083108 | 3 | 0.6363 | 95445 | 0.01895 | 0 | 0.23448 | 2931 | 0.10161 | 8128.8 | 64000 | 2931 | 8128.8 | 20385.2 | -2290.1 | 258808.125 | 20385.2 | 0
2021083109 | 3 | 0.66329 | 99493.5 | 0.00515 | 0 | 0.21443 | 2680.375 | 0.12953 | 10362.4 | 64000 | 2680.375 | 10362.4 | 22450.725 | 2065.525 | 261823.65 | 22450.725 | 0
2021083110 | 3 | 0.69157 | 103735.5 | 0.0079 | 0 | 0.20768 | 2596 | 0.14791 | 11832.8 | 64000 | 2596 | 11832.8 | 25306.7 | 2855.975 | 261983.2 | 25306.7 | 0
2021083111 | 3 | 0.72694 | 109041 | 0.00729 | 0 | 0.16692 | 2086.5 | 0.25336 | 20268.8 | 64000 | 2086.5 | 20268.8 | 22685.7 | -2621 | 264763.75 | 22685.7 | 0
2021083112 | 3 | 0.75969 | 113953.5 | 6e-05 | 0 | 0.10581 | 1322.625 | 0.28621 | 22896.8 | 64000 | 1322.625 | 22896.8 | 25734.075 | 3048.375 | 264495.925 | 25734.075 | 0
2021083113 | 3 | 0.78932 | 118398 | 0.01067 | 0 | 0.07523 | 940.375 | 0.26569 | 21255.2 | 64000 | 940.375 | 21255.2 | 32202.425 | 6468.35 | 257759.75 | 32202.425 | 0
2021083114 | 3 | 0.81088 | 121632 | 0.01677 | 0 | 0.07651 | 956.375 | 0.30132 | 24105.6 | 64000 | 956.375 | 24105.6 | 32570.025 | 367.6 | 250655.975 | 32570.025 | 0
2021083115 | 3 | 0.82014 | 123021 | 0.02247 | 0 | 0.07672 | 959 | 0.26744 | 21395.2 | 64000 | 959 | 21395.2 | 36666.8 | 4096.775 | 239455.425 | 36666.8 | 0
2021083116 | 3 | 0.82212 | 123318 | 0.02512 | 0 | 0.07766 | 970.75 | 0.23673 | 18938.4 | 64000 | 970.75 | 18938.4 | 39408.85 | 2742.05 | 225512.825 | 39408.85 | 0
2021083117 | 3 | 0.82134 | 123201 | 0.01497 | 0 | 0.09267 | 1158.375 | 0.15604 | 12483.2 | 64000 | 1158.375 | 12483.2 | 45559.425 | 6150.575 | 205419.65 | 45559.425 | 0
2021083118 | 3 | 0.81309 | 121963.5 | 0.02228 | 0 | 0.09083 | 1135.375 | 0.10761 | 8608.8 | 64000 | 1135.375 | 8608.8 | 48219.325 | 2659.9 | 182666.575 | 48219.325 | 0
2021083119 | 3 | 0.79342 | 119013 | 0.03514 | 0 | 0.09555 | 1194.375 | 0.0556 | 4448 | 64000 | 1194.375 | 4448 | 49370.625 | 1151.3 | 158762.2 | 49370.625 | 0
2021083120 | 3 | 0.77554 | 116331 | 0.09394 | 0 | 0.11412 | 1426.5 | 0.00892 | 713.6 | 64000 | 1426.5 | 713.6 | 50190.9 | 820.275 | 134037.55 | 50190.9 | 0
2021083121 | 3 | 0.76311 | 114466.5 | 0.12426 | 0 | 0.13961 | 1745.125 | 0 | 0 | 64000 | 1745.125 | 0 | 48721.375 | -1469.525 | 110782.425 | 48721.375 | 0
2021083122 | 3 | 0.72953 | 109429.5 | 0.13659 | 0 | 0.18051 | 2256.375 | 0 | 0 | 64000 | 2256.375 | 0 | 43173.125 | -5548.25 | 93075.55 | 43173.125 | 0
2021083123 | 3 | 0.68324 | 102486 | 0.13924 | 0 | 0.24149 | 3018.625 | 0 | 0 | 64000 | 3018.625 | 0 | 35467.375 | -7705.75 | 83074.425 | 35467.375 | 0
2021083124 | 3 | 0.63608 | 95412 | 0.13833 | 0 | 0.357 | 4462.5 | 0 | 0 | 64000 | 4462.5 | 0 | 26949.5 | -8517.875 | 81591.175 | 26949.5 | 0
2021090101 | 4 | 0.59647 | 89470.5 | 0.12273 | 0 | 0.45703 | 5712.875 | 0 | 0 | 64000 | 5712.875 | 0 | 19757.625 | -7191.875 | 87299.8 | 19757.625 | 0
2021090102 | 4 | 0.56891 | 85336.5 | 0.06922 | 0 | 0.54561 | 6820.125 | 0 | 0 | 64000 | 6820.125 | 0 | 14516.375 | -5241.25 | 98249.675 | 14516.375 | 0
2021090103 | 4 | 0.55078 | 82617 | 0.06943 | 0 | 0.56563 | 7070.375 | 0 | 0 | 64000 | 7070.375 | 0 | 11546.625 | -2969.75 | 112169.3 | 11546.625 | 0
2021090104 | 4 | 0.53953 | 80929.5 | 0.09452 | 0 | 0.61673 | 7709.125 | 0 | 0 | 64000 | 7709.125 | 0 | 9220.375 | -2326.25 | 128415.175 | 9220.375 | 0
2021090105 | 4 | 0.5405 | 81075 | 0.12733 | 0 | 0.62865 | 7858.125 | 0 | 0 | 64000 | 7858.125 | 0 | 9216.875 | -3.5 | 144664.55 | 9216.875 | 0
2021090106 | 4 | 0.55874 | 83811 | 0.15445 | 0 | 0.61595 | 7699.375 | 0 | 0 | 64000 | 7699.375 | 0 | 12111.625 | 2894.75 | 158019.175 | 12111.625 | 0
2021090107 | 4 | 0.59667 | 89500.5 | 0.21677 | 0 | 0.61426 | 7678.25 | 0.03705 | 2964 | 64000 | 7678.25 | 2964 | 14858.25 | 2746.625 | 168627.175 | 14858.25 | 0
2021090108 | 4 | 0.62523 | 93784.5 | 0.28968 | 0 | 0.63999 | 7999.875 | 0.21226 | 16980.8 | 64000 | 7999.875 | 16980.8 | 4803.825 | -10054.425 | 189289.6 | 4803.825 | 0
2021090109 | 4 | 0.6472 | 97080 | 0.34603 | 0 | 0.65132 | 8141.5 | 0.3965 | 31720 | 64000 | 8141.5 | 24938.5 | 0 | -4803.825 | 214755.85 | 0 | 0
2021090110 | 4 | 0.66755 | 100132.5 | 0.36147 | 0 | 0.67664 | 8458 | 0.5157 | 41256 | 64000 | 8458 | 27674.5 | 0 | 0 | 240222.1 | 0 | 0
2021090111 | 4 | 0.6887 | 103305 | 0.43168 | 0 | 0.69604 | 8700.5 | 0.57775 | 46220 | 64000 | 8700.5 | 30604.5 | 0 | 0 | 265688.35 | 0 | 0
2021090112 | 4 | 0.70731 | 106096.5 | 0.51991 | 0 | 0.69553 | 8694.125 | 0.63117 | 50493.6 | 64000 | 8694.125 | 33402.375 | 0 | 0 | 291154.6 | 0 | 0
2021090113 | 4 | 0.72325 | 108487.5 | 0.68017 | 0 | 0.68525 | 8565.625 | 0.64273 | 51418.4 | 64000 | 8565.625 | 35921.875 | 0 | 0 | 316620.85 | 0 | 0
2021090114 | 4 | 0.7345 | 110175 | 0.73899 | 0 | 0.6697 | 8371.25 | 0.6304 | 50432 | 64000 | 8371.25 | 37803.75 | 0 | 0 | 342087.1 | 0 | 0
2021090115 | 4 | 0.73876 | 110814 | 0.80949 | 0 | 0.63535 | 7941.875 | 0.61005 | 48804 | 64000 | 7941.875 | 38872.125 | 0 | 0 | 367553.35 | 0 | 0
2021090116 | 4 | 0.74201 | 111301.5 | 0.82764 | 0 | 0.63547 | 7943.375 | 0.54807 | 43845.6 | 64000 | 7943.375 | 39358.125 | 0 | 0 | 393019.6 | 0 | 0
2021090117 | 4 | 0.75091 | 112636.5 | 0.82337 | 0 | 0.61519 | 7689.875 | 0.46842 | 37473.6 | 64000 | 7689.875 | 37473.6 | 3473.025 | 3473.025 | 415012.825 | 3473.025 | 0
2021090118 | 4 | 0.75121 | 112681.5 | 0.79082 | 0 | 0.65112 | 8139 | 0.37028 | 29622.4 | 64000 | 8139 | 29622.4 | 10920.1 | 7447.075 | 429558.975 | 10920.1 | 0
2021090119 | 4 | 0.73369 | 110053.5 | 0.79009 | 0 | 0.70192 | 8774 | 0.16339 | 13071.2 | 64000 | 8774 | 13071.2 | 24208.3 | 13288.2 | 430816.925 | 24208.3 | 0
2021090120 | 4 | 0.70995 | 106492.5 | 0.78054 | 0 | 0.71819 | 8977.375 | 0.02248 | 1798.4 | 64000 | 8977.375 | 1798.4 | 31716.725 | 7508.425 | 424566.45 | 31716.725 | 0
2021090121 | 4 | 0.68828 | 103242 | 0.7725 | 0 | 0.72526 | 9065.75 | 0 | 0 | 64000 | 9065.75 | 0 | 30176.25 | -1540.475 | 419856.45 | 30176.25 | 0
2021090122 | 4 | 0.65517 | 98275.5 | 0.82557 | 0 | 0.73934 | 9241.75 | 0 | 0 | 64000 | 9241.75 | 0 | 25033.75 | -5142.5 | 420288.95 | 25033.75 | 0
2021090123 | 4 | 0.60978 | 91467 | 0.81868 | 0 | 0.74391 | 9298.875 | 0 | 0 | 64000 | 9298.875 | 0 | 18168.125 | -6865.625 | 427587.075 | 18168.125 | 0
2021090124 | 4 | 0.56185 | 84277.5 | 0.78249 | 0 | 0.75144 | 9393 | 0 | 0 | 64000 | 9393 | 0 | 10884.5 | -7283.625 | 442168.825 | 10884.5 | 0
2021090201 | 5 | 0.52505 | 78757.5 | 0.77792 | 0 | 0.77119 | 9639.875 | 0 | 0 | 64000 | 9639.875 | 0 | 5117.625 | -5766.875 | 462517.45 | 5117.625 | 0
2021090202 | 5 | 0.49771 | 74656.5 | 0.76169 | 0 | 0.76312 | 9539 | 0 | 0 | 64000 | 9539 | 0 | 1117.5 | -4000.125 | 486866.2 | 1117.5 | 0
2021090203 | 5 | 0.4801 | 72015 | 0.71933 | 0 | 0.74142 | 9267.75 | 0 | 0 | 64000 | 8015 | 0 | 0 | -1117.5 | 512332.45 | 0 | 0
2021090204 | 5 | 0.47025 | 70537.5 | 0.68264 | 0 | 0.71249 | 8906.125 | 0 | 0 | 64000 | 6537.5 | 0 | 0 | 0 | 537798.7 | 0 | 0
2021090205 | 5 | 0.47047 | 70570.5 | 0.65336 | 0 | 0.68224 | 8528 | 0 | 0 | 64000 | 6570.5 | 0 | 0 | 0 | 563264.95 | 0 | 0
2021090206 | 5 | 0.48838 | 73257 | 0.65794 | 0 | 0.66315 | 8289.375 | 0 | 0 | 64000 | 8289.375 | 0 | 967.625 | 967.625 | 587763.575 | 967.625 | 0
2021090207 | 5 | 0.52206 | 78309 | 0.64864 | 0 | 0.683 | 8537.5 | 0.05189 | 4151.2 | 64000 | 8537.5 | 4151.2 | 1620.3 | 652.675 | 611609.525 | 1620.3 | 0
2021090208 | 5 | 0.54639 | 81958.5 | 0.57389 | 0 | 0.68757 | 8594.625 | 0.31875 | 25500 | 64000 | 8594.625 | 9363.875 | 0 | -1620.3 | 637075.775 | 0 | 0
2021090209 | 5 | 0.56479 | 84718.5 | 0.45151 | 0 | 0.67272 | 8409 | 0.54442 | 43553.6 | 64000 | 8409 | 12309.5 | 0 | 0 | 662542.025 | 0 | 0
2021090210 | 5 | 0.58388 | 87582 | 0.37707 | 0 | 0.66304 | 8288 | 0.60986 | 48788.8 | 64000 | 8288 | 15294 | 0 | 0 | 688008.275 | 0 | 0
2021090211 | 5 | 0.60158 | 90237 | 0.44029 | 0 | 0.66798 | 8349.75 | 0.65429 | 52343.2 | 64000 | 8349.75 | 17887.25 | 0 | 0 | 713474.525 | 0 | 0
2021090212 | 5 | 0.61772 | 92658 | 0.53186 | 0 | 0.65479 | 8184.875 | 0.65666 | 52532.8 | 64000 | 8184.875 | 20473.125 | 0 | 0 | 738940.775 | 0 | 0
2021090213 | 5 | 0.63681 | 95521.5 | 0.52332 | 0 | 0.64044 | 8005.5 | 0.62374 | 49899.2 | 64000 | 8005.5 | 23516 | 0 | 0 | 764407.025 | 0 | 0
2021090214 | 5 | 0.65654 | 98481 | 0.57427 | 0 | 0.61442 | 7680.25 | 0.65911 | 52728.8 | 64000 | 7680.25 | 26800.75 | 0 | 0 | 789873.275 | 0 | 0
2021090215 | 5 | 0.67343 | 101014.5 | 0.58615 | 0 | 0.59368 | 7421 | 0.65754 | 52603.2 | 64000 | 7421 | 29593.5 | 0 | 0 | 815339.525 | 0 | 0
2021090216 | 5 | 0.68887 | 103330.5 | 0.56374 | 0 | 0.5912 | 7390 | 0.61374 | 49099.2 | 64000 | 7390 | 31940.5 | 0 | 0 | 840805.775 | 0 | 0
2021090217 | 5 | 0.70273 | 105409.5 | 0.5887 | 0 | 0.60353 | 7544.125 | 0.62118 | 49694.4 | 64000 | 7544.125 | 33865.375 | 0 | 0 | 866272.025 | 0 | 0
2021090218 | 5 | 0.7074 | 106110 | 0.59106 | 0 | 0.59396 | 7424.5 | 0.54033 | 43226.4 | 64000 | 7424.5 | 34685.5 | 0 | 0 | 891738.275 | 0 | 0
2021090219 | 5 | 0.69234 | 103851 | 0.51659 | 0 | 0.59896 | 7487 | 0.26838 | 21470.4 | 64000 | 7487 | 21470.4 | 10893.6 | 10893.6 | 906310.925 | 10893.6 | 0
2021090220 | 5 | 0.66511 | 99766.5 | 0.49406 | 0 | 0.5632 | 7040 | 0.02423 | 1938.4 | 64000 | 7040 | 1938.4 | 26788.1 | 15894.5 | 904989.075 | 26788.1 | 0
2021090221 | 5 | 0.65102 | 97653 | 0.58349 | 0 | 0.53299 | 6662.375 | 0 | 0 | 64000 | 6662.375 | 0 | 26990.625 | 202.525 | 903464.7 | 26990.625 | 0
2021090222 | 5 | 0.61855 | 92782.5 | 0.59814 | 0 | 0.52615 | 6576.875 | 0 | 0 | 64000 | 6576.875 | 0 | 22205.625 | -4785 | 906725.325 | 22205.625 | 0
2021090223 | 5 | 0.57528 | 86292 | 0.51626 | 0 | 0.50832 | 6354 | 0 | 0 | 64000 | 6354 | 0 | 15938 | -6267.625 | 916253.575 | 15938 | 0
2021090224 | 5 | 0.53269 | 79903.5 | 0.45883 | 0 | 0.49566 | 6195.75 | 0 | 0 | 64000 | 6195.75 | 0 | 9707.75 | -6230.25 | 932012.075 | 9707.75 | 0
2021090301 | 6 | 0.49819 | 74728.5 | 0.39323 | 0 | 0.49611 | 6201.375 | 0 | 0 | 64000 | 6201.375 | 0 | 4527.125 | -5180.625 | 952951.2 | 4527.125 | 0
2021090302 | 6 | 0.47319 | 70978.5 | 0.32346 | 0 | 0.49536 | 6192 | 0 | 0 | 64000 | 6192 | 0 | 786.5 | -3740.625 | 977630.95 | 786.5 | 0
2021090303 | 6 | 0.45859 | 68788.5 | 0.29484 | 0 | 0.45287 | 5660.875 | 0 | 0 | 64000 | 4788.5 | 0 | 0 | -786.5 | 1003097.2 | 0 | 0
2021090304 | 6 | 0.4507 | 67605 | 0.28778 | 0 | 0.41027 | 5128.375 | 0 | 0 | 64000 | 3605 | 0 | 0 | 0 | 1028563.45 | 0 | 0
2021090305 | 6 | 0.45206 | 67809 | 0.26517 | 0 | 0.37825 | 4728.125 | 0 | 0 | 64000 | 3809 | 0 | 0 | 0 | 1054029.7 | 0 | 0
2021090306 | 6 | 0.46939 | 70408.5 | 0.27547 | 0 | 0.3824 | 4780 | 0 | 0 | 64000 | 4780 | 0 | 1628.5 | 1628.5 | 1077867.45 | 1628.5 | 0
2021090307 | 6 | 0.4999 | 74985 | 0.27322 | 0 | 0.40656 | 5082 | 0.04498 | 3598.4 | 64000 | 5082 | 3598.4 | 2304.6 | 676.1 | 1101029.1 | 2304.6 | 0
2021090308 | 6 | 0.52255 | 78382.5 | 0.20351 | 0 | 0.42043 | 5255.375 | 0.25998 | 20798.4 | 64000 | 5255.375 | 9127.125 | 0 | -2304.6 | 1126495.35 | 0 | 0
2021090309 | 6 | 0.54188 | 81282 | 0.12264 | 0 | 0.44471 | 5558.875 | 0.48211 | 38568.8 | 64000 | 5558.875 | 11723.125 | 0 | 0 | 1151961.6 | 0 | 0
2021090310 | 6 | 0.55903 | 83854.5 | 0.13398 | 0 | 0.48938 | 6117.25 | 0.55624 | 44499.2 | 64000 | 6117.25 | 13737.25 | 0 | 0 | 1177427.85 | 0 | 0
2021090311 | 6 | 0.57733 | 86599.5 | 0.14495 | 0 | 0.52869 | 6608.625 | 0.59291 | 47432.8 | 64000 | 6608.625 | 15990.875 | 0 | 0 | 1202894.1 | 0 | 0
2021090312 | 6 | 0.59424 | 89136 | 0.12889 | 0 | 0.59506 | 7438.25 | 0.60838 | 48670.4 | 64000 | 7438.25 | 17697.75 | 0 | 0 | 1228360.35 | 0 | 0
2021090313 | 6 | 0.61059 | 91588.5 | 0.09908 | 0 | 0.6325 | 7906.25 | 0.59943 | 47954.4 | 64000 | 7906.25 | 19682.25 | 0 | 0 | 1253826.6 | 0 | 0
2021090314 | 6 | 0.62535 | 93802.5 | 0.08049 | 0 | 0.64649 | 8081.125 | 0.5652 | 45216 | 64000 | 8081.125 | 21721.375 | 0 | 0 | 1279292.85 | 0 | 0
2021090315 | 6 | 0.63673 | 95509.5 | 0.09836 | 0 | 0.6654 | 8317.5 | 0.56778 | 45422.4 | 64000 | 8317.5 | 23192 | 0 | 0 | 1304759.1 | 0 | 0
2021090316 | 6 | 0.64583 | 96874.5 | 0.08365 | 0 | 0.65584 | 8198 | 0.57626 | 46100.8 | 64000 | 8198 | 24676.5 | 0 | 0 | 1330225.35 | 0 | 0
2021090317 | 6 | 0.65559 | 98338.5 | 0.097 | 0 | 0.61715 | 7714.375 | 0.56191 | 44952.8 | 64000 | 7714.375 | 26624.125 | 0 | 0 | 1350000 | 0 | 0
2021090318 | 6 | 0.65655 | 98482.5 | 0.09355 | 0 | 0.60313 | 7539.125 | 0.5054 | 40432 | 64000 | 7539.125 | 26943.375 | 0 | 0 | 1350000 | 0 | 0
2021090319 | 6 | 0.64137 | 96205.5 | 0.08939 | 0 | 0.53395 | 6674.375 | 0.21396 | 17116.8 | 64000 | 6674.375 | 17116.8 | 8414.325 | 8414.325 | 1350000 | 8414.325 | 0
2021090320 | 6 | 0.62118 | 93177 | 0.09934 | 0 | 0.41663 | 5207.875 | 0.01119 | 895.2 | 64000 | 5207.875 | 895.2 | 23073.925 | 14659.6 | 1350000 | 23073.925 | 0
2021090321 | 6 | 0.61147 | 91720.5 | 0.10562 | 0 | 0.36962 | 4620.25 | 0 | 0 | 64000 | 4620.25 | 0 | 23100.25 | 26.325 | 1350000 | 23100.25 | 0
2021090322 | 6 | 0.58565 | 87847.5 | 0.10672 | 0 | 0.37685 | 4710.625 | 0 | 0 | 64000 | 4710.625 | 0 | 19136.875 | -3963.375 | 1350000 | 19136.875 | 0
2021090323 | 6 | 0.55249 | 82873.5 | 0.10116 | 0 | 0.46266 | 5783.25 | 0 | 0 | 64000 | 5783.25 | 0 | 13090.25 | -6046.625 | 1350000 | 13090.25 | 0
2021090324 | 6 | 0.51599 | 77398.5 | 0.07682 | 0 | 0.59459 | 7432.375 | 0 | 0 | 64000 | 7432.375 | 0 | 5966.125 | -7124.125 | 1350000 | 5966.125 | 0
2021090401 | 7 | 0.48356 | 72534 | 0.03331 | 0 | 0.58712 | 7339 | 0 | 0 | 64000 | 7339 | 0 | 1195 | -4771.125 | 1350000 | 1195 | 0
2021090402 | 7 | 0.46044 | 69066 | 0.02318 | 0 | 0.5481 | 6851.25 | 0 | 0 | 64000 | 5066 | 0 | 0 | -1195 | 1350000 | 0 | 0
2021090403 | 7 | 0.44532 | 66798 | 0.04723 | 0 | 0.50653 | 6331.625 | 0 | 0 | 64000 | 2798 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090404 | 7 | 0.43644 | 65466 | 0.10071 | 0 | 0.46479 | 5809.875 | 0 | 0 | 64000 | 1466 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090405 | 7 | 0.43301 | 64951.5 | 0.11814 | 0 | 0.46408 | 5801 | 0 | 0 | 64000 | 951.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090406 | 7 | 0.43711 | 65566.5 | 0.11874 | 0 | 0.45553 | 5694.125 | 0 | 0 | 64000 | 1566.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090407 | 7 | 0.44651 | 66976.5 | 0.11399 | 0 | 0.44285 | 5535.625 | 0.02153 | 1722.4 | 64000 | 2976.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090408 | 7 | 0.45691 | 68536.5 | 0.0983 | 0 | 0.4826 | 6032.5 | 0.08913 | 7130.4 | 64000 | 4536.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090409 | 7 | 0.47801 | 71701.5 | 0.06195 | 0 | 0.51199 | 6399.875 | 0.19069 | 15255.2 | 64000 | 6399.875 | 1301.625 | 0 | 0 | 1350000 | 0 | 0
2021090410 | 7 | 0.50043 | 75064.5 | 0.01655 | 0 | 0.51349 | 6418.625 | 0.28522 | 22817.6 | 64000 | 6418.625 | 4645.875 | 0 | 0 | 1350000 | 0 | 0
2021090411 | 7 | 0.5223 | 78345 | 0.00843 | 0 | 0.50378 | 6297.25 | 0.36735 | 29388 | 64000 | 6297.25 | 8047.75 | 0 | 0 | 1350000 | 0 | 0
2021090412 | 7 | 0.54308 | 81462 | 0.01235 | 0 | 0.46744 | 5843 | 0.42059 | 33647.2 | 64000 | 5843 | 11619 | 0 | 0 | 1350000 | 0 | 0
2021090413 | 7 | 0.56632 | 84948 | 0.00128 | 0 | 0.41616 | 5202 | 0.48172 | 38537.6 | 64000 | 5202 | 15746 | 0 | 0 | 1350000 | 0 | 0
2021090414 | 7 | 0.5873 | 88095 | 0.00569 | 0 | 0.33827 | 4228.375 | 0.51575 | 41260 | 64000 | 4228.375 | 19866.625 | 0 | 0 | 1350000 | 0 | 0
2021090415 | 7 | 0.6065 | 90975 | 0.00166 | 0 | 0.2832 | 3540 | 0.4644 | 37152 | 64000 | 3540 | 23435 | 0 | 0 | 1350000 | 0 | 0
2021090416 | 7 | 0.62398 | 93597 | 0.01328 | 0 | 0.26647 | 3330.875 | 0.39048 | 31238.4 | 64000 | 3330.875 | 26266.125 | 0 | 0 | 1350000 | 0 | 0
2021090417 | 7 | 0.63658 | 95487 | 0.03299 | 0 | 0.22265 | 2783.125 | 0.28329 | 22663.2 | 64000 | 2783.125 | 22663.2 | 6040.675 | 6040.675 | 1350000 | 6040.675 | 0
2021090418 | 7 | 0.64231 | 96346.5 | 0.05132 | 0 | 0.15832 | 1979 | 0.16712 | 13369.6 | 64000 | 1979 | 13369.6 | 16997.9 | 10957.225 | 1350000 | 16997.9 | 0
2021090419 | 7 | 0.63363 | 95044.5 | 0.07097 | 0 | 0.16248 | 2031 | 0.05888 | 4710.4 | 64000 | 2031 | 4710.4 | 24303.1 | 7305.2 | 1350000 | 24303.1 | 0
2021090420 | 7 | 0.61673 | 92509.5 | 0.13116 | 0 | 0.16845 | 2105.625 | 0.0054 | 432 | 64000 | 2105.625 | 432 | 25971.875 | 1668.775 | 1349494.375 | 25971.875 | 0
2021090421 | 7 | 0.6081 | 91215 | 0.15459 | 0 | 0.21323 | 2665.375 | 0 | 0 | 64000 | 2665.375 | 0 | 24549.625 | -1422.25 | 1350000 | 24549.625 | 0
2021090422 | 7 | 0.58418 | 87627 | 0.22513 | 0 | 0.21309 | 2663.625 | 0 | 0 | 64000 | 2663.625 | 0 | 20963.375 | -3586.25 | 1350000 | 20963.375 | 0
2021090423 | 7 | 0.55478 | 83217 | 0.31191 | 0 | 0.17925 | 2240.625 | 0 | 0 | 64000 | 2240.625 | 0 | 16976.375 | -3987 | 1350000 | 16976.375 | 0
2021090424 | 7 | 0.52162 | 78243 | 0.35507 | 0 | 0.20068 | 2508.5 | 0 | 0 | 64000 | 2508.5 | 0 | 11734.5 | -5241.875 | 1350000 | 11734.5 | 0
2021090501 | 1 | 0.49193 | 73789.5 | 0.40984 | 0 | 0.23095 | 2886.875 | 0 | 0 | 64000 | 2886.875 | 0 | 6902.625 | -4831.875 | 1350000 | 6902.625 | 0
2021090502 | 1 | 0.46941 | 70411.5 | 0.48323 | 0 | 0.24151 | 3018.875 | 0 | 0 | 64000 | 3018.875 | 0 | 3392.625 | -3510 | 1350000 | 3392.625 | 0
2021090503 | 1 | 0.4548 | 68220 | 0.49448 | 0 | 0.23021 | 2877.625 | 0 | 0 | 64000 | 2877.625 | 0 | 1342.375 | -2050.25 | 1350000 | 1342.375 | 0
2021090504 | 1 | 0.44497 | 66745.5 | 0.52467 | 0 | 0.20494 | 2561.75 | 0 | 0 | 64000 | 2561.75 | 0 | 183.75 | -1158.625 | 1350000 | 183.75 | 0
2021090505 | 1 | 0.44193 | 66289.5 | 0.52415 | 0 | 0.22291 | 2786.375 | 0 | 0 | 64000 | 2289.5 | 0 | 0 | -183.75 | 1350000 | 0 | 0
2021090506 | 1 | 0.44276 | 66414 | 0.47105 | 0 | 0.1918 | 2397.5 | 0 | 0 | 64000 | 2397.5 | 0 | 16.5 | 16.5 | 1350000 | 16.5 | 0
2021090507 | 1 | 0.45015 | 67522.5 | 0.44729 | 0 | 0.17313 | 2164.125 | 0.01934 | 1547.2 | 64000 | 2164.125 | 1358.375 | 0 | -16.5 | 1350000 | 0 | 0
2021090508 | 1 | 0.4586 | 68790 | 0.51179 | 0 | 0.20535 | 2566.875 | 0.17697 | 14157.6 | 64000 | 2566.875 | 2223.125 | 0 | 0 | 1350000 | 0 | 0
2021090509 | 1 | 0.48153 | 72229.5 | 0.55897 | 0 | 0.24996 | 3124.5 | 0.36984 | 29587.2 | 64000 | 3124.5 | 5105 | 0 | 0 | 1350000 | 0 | 0
2021090510 | 1 | 0.50847 | 76270.5 | 0.54777 | 0 | 0.31429 | 3928.625 | 0.47708 | 38166.4 | 64000 | 3928.625 | 8341.875 | 0 | 0 | 1350000 | 0 | 0
2021090511 | 1 | 0.53551 | 80326.5 | 0.47604 | 0 | 0.35851 | 4481.375 | 0.54111 | 43288.8 | 64000 | 4481.375 | 11845.125 | 0 | 0 | 1350000 | 0 | 0
2021090512 | 1 | 0.55839 | 83758.5 | 0.41886 | 0 | 0.40267 | 5033.375 | 0.57831 | 46264.8 | 64000 | 5033.375 | 14725.125 | 0 | 0 | 1350000 | 0 | 0
2021090513 | 1 | 0.57818 | 86727 | 0.3808 | 0 | 0.35039 | 4379.875 | 0.59997 | 47997.6 | 64000 | 4379.875 | 18347.125 | 0 | 0 | 1350000 | 0 | 0
2021090514 | 1 | 0.59663 | 89494.5 | 0.37572 | 0 | 0.32059 | 4007.375 | 0.59952 | 47961.6 | 64000 | 4007.375 | 21487.125 | 0 | 0 | 1350000 | 0 | 0
2021090515 | 1 | 0.61069 | 91603.5 | 0.32214 | 0 | 0.29608 | 3701 | 0.57979 | 46383.2 | 64000 | 3701 | 23902.5 | 0 | 0 | 1350000 | 0 | 0
2021090516 | 1 | 0.61966 | 92949 | 0.30197 | 0 | 0.31697 | 3962.125 | 0.50522 | 40417.6 | 64000 | 3962.125 | 24986.875 | 0 | 0 | 1350000 | 0 | 0
2021090517 | 1 | 0.62995 | 94492.5 | 0.2455 | 0 | 0.33816 | 4227 | 0.38271 | 30616.8 | 64000 | 4227 | 26265.5 | 0 | 0 | 1350000 | 0 | 0
2021090518 | 1 | 0.63719 | 95578.5 | 0.22314 | 0 | 0.39966 | 4995.75 | 0.20977 | 16781.6 | 64000 | 4995.75 | 16781.6 | 9801.15 | 9801.15 | 1350000 | 9801.15 | 0
2021090519 | 1 | 0.63244 | 94866 | 0.21318 | 0 | 0.43106 | 5388.25 | 0.08229 | 6583.2 | 64000 | 5388.25 | 6583.2 | 18894.55 | 9093.4 | 1350000 | 18894.55 | 0
2021090520 | 1 | 0.62285 | 93427.5 | 0.26172 | 0 | 0.46737 | 5842.125 | 0.00951 | 760.8 | 64000 | 5842.125 | 760.8 | 22824.575 | 3930.025 | 1350000 | 22824.575 | 0
2021090521 | 1 | 0.6115 | 91725 | 0.26906 | 0 | 0.52611 | 6576.375 | 0 | 0 | 64000 | 6576.375 | 0 | 21148.625 | -1675.95 | 1350000 | 21148.625 | 0
2021090522 | 1 | 0.58927 | 88390.5 | 0.25435 | 0 | 0.55567 | 6945.875 | 0 | 0 | 64000 | 6945.875 | 0 | 17444.625 | -3704 | 1350000 | 17444.625 | 0
2021090523 | 1 | 0.56 | 84000 | 0.28189 | 0 | 0.61969 | 7746.125 | 0 | 0 | 64000 | 7746.125 | 0 | 12253.875 | -5190.75 | 1350000 | 12253.875 | 0
2021090524 | 1 | 0.52848 | 79272 | 0.30074 | 0 | 0.63566 | 7945.75 | 0 | 0 | 64000 | 7945.75 | 0 | 7326.25 | -4927.625 | 1350000 | 7326.25 | 0
2021090601 | 2 | 0.49942 | 74913 | 0.30905 | 0 | 0.60886 | 7610.75 | 0 | 0 | 64000 | 7610.75 | 0 | 3302.25 | -4024 | 1350000 | 3302.25 | 0
2021090602 | 2 | 0.47635 | 71452.5 | 0.32325 | 0 | 0.56372 | 7046.5 | 0 | 0 | 64000 | 7046.5 | 0 | 406 | -2896.25 | 1350000 | 406 | 0
2021090603 | 2 | 0.46264 | 69396 | 0.36507 | 0 | 0.48727 | 6090.875 | 0 | 0 | 64000 | 5396 | 0 | 0 | -406 | 1350000 | 0 | 0
2021090604 | 2 | 0.45273 | 67909.5 | 0.46945 | 0 | 0.46073 | 5759.125 | 0 | 0 | 64000 | 3909.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090605 | 2 | 0.45067 | 67600.5 | 0.58624 | 0 | 0.44587 | 5573.375 | 0 | 0 | 64000 | 3600.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090606 | 2 | 0.45627 | 68440.5 | 0.56462 | 0 | 0.47197 | 5899.625 | 0 | 0 | 64000 | 4440.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090607 | 2 | 0.46365 | 69547.5 | 0.5352 | 0 | 0.51662 | 6457.75 | 0.03903 | 3122.4 | 64000 | 5547.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090608 | 2 | 0.47004 | 70506 | 0.5373 | 0 | 0.54689 | 6836.125 | 0.25204 | 20163.2 | 64000 | 6506 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090609 | 2 | 0.49426 | 74139 | 0.45092 | 0 | 0.55263 | 6907.875 | 0.47909 | 38327.2 | 64000 | 6907.875 | 3231.125 | 0 | 0 | 1350000 | 0 | 0
2021090610 | 2 | 0.52907 | 79360.5 | 0.47841 | 0 | 0.55008 | 6876 | 0.55421 | 44336.8 | 64000 | 6876 | 8484.5 | 0 | 0 | 1350000 | 0 | 0
2021090611 | 2 | 0.56385 | 84577.5 | 0.58121 | 0 | 0.54384 | 6798 | 0.60298 | 48238.4 | 64000 | 6798 | 13779.5 | 0 | 0 | 1350000 | 0 | 0
2021090612 | 2 | 0.59617 | 89425.5 | 0.63766 | 0 | 0.50783 | 6347.875 | 0.63701 | 50960.8 | 64000 | 6347.875 | 19077.625 | 0 | 0 | 1350000 | 0 | 0
2021090613 | 2 | 0.62408 | 93612 | 0.77035 | 0 | 0.45569 | 5696.125 | 0.64937 | 51949.6 | 64000 | 5696.125 | 23915.875 | 0 | 0 | 1350000 | 0 | 0
2021090614 | 2 | 0.64772 | 97158 | 0.79957 | 0 | 0.51926 | 6490.75 | 0.65007 | 52005.6 | 64000 | 6490.75 | 26667.25 | 0 | 0 | 1350000 | 0 | 0
2021090615 | 2 | 0.67019 | 100528.5 | 0.79746 | 0 | 0.61283 | 7660.375 | 0.63984 | 51187.2 | 64000 | 7660.375 | 28868.125 | 0 | 0 | 1350000 | 0 | 0
2021090616 | 2 | 0.69017 | 103525.5 | 0.74452 | 0 | 0.63527 | 7940.875 | 0.62227 | 49781.6 | 64000 | 7940.875 | 31584.625 | 0 | 0 | 1350000 | 0 | 0
2021090617 | 2 | 0.70817 | 106225.5 | 0.69286 | 0 | 0.6169 | 7711.25 | 0.57933 | 46346.4 | 64000 | 7711.25 | 34514.25 | 0 | 0 | 1350000 | 0 | 0
2021090618 | 2 | 0.71704 | 107556 | 0.5771 | 0 | 0.59721 | 7465.125 | 0.46716 | 37372.8 | 64000 | 7465.125 | 36090.875 | 0 | 0 | 1350000 | 0 | 0
2021090619 | 2 | 0.70413 | 105619.5 | 0.45285 | 0 | 0.6324 | 7905 | 0.1986 | 15888 | 64000 | 7905 | 15888 | 17826.5 | 17826.5 | 1350000 | 17826.5 | 0
2021090620 | 2 | 0.67867 | 101800.5 | 0.37991 | 0 | 0.61605 | 7700.625 | 0.01552 | 1241.6 | 64000 | 7700.625 | 1241.6 | 28858.275 | 11031.775 | 1346607.975 | 28858.275 | 0
2021090621 | 2 | 0.6611 | 99165 | 0.36831 | 0 | 0.60746 | 7593.25 | 0 | 0 | 64000 | 7593.25 | 0 | 27571.75 | -1286.525 | 1344502.475 | 27571.75 | 0
2021090622 | 2 | 0.6242 | 93630 | 0.37576 | 0 | 0.59807 | 7475.875 | 0 | 0 | 64000 | 7475.875 | 0 | 22154.125 | -5417.625 | 1347814.6 | 22154.125 | 0
2021090623 | 2 | 0.57888 | 86832 | 0.31748 | 0 | 0.56229 | 7028.625 | 0 | 0 | 64000 | 7028.625 | 0 | 15803.375 | -6350.75 | 1350000 | 15803.375 | 0
2021090624 | 2 | 0.53492 | 80238 | 0.25125 | 0 | 0.53262 | 6657.75 | 0 | 0 | 64000 | 6657.75 | 0 | 9580.25 | -6223.125 | 1350000 | 9580.25 | 0
2021090701 | 3 | 0.49902 | 74853 | 0.19711 | 0 | 0.53667 | 6708.375 | 0 | 0 | 64000 | 6708.375 | 0 | 4144.625 | -5435.625 | 1350000 | 4144.625 | 0
2021090702 | 3 | 0.474 | 71100 | 0.20472 | 0 | 0.55608 | 6951 | 0 | 0 | 64000 | 6951 | 0 | 149 | -3995.625 | 1350000 | 149 | 0
2021090703 | 3 | 0.46047 | 69070.5 | 0.23482 | 0 | 0.57865 | 7233.125 | 0 | 0 | 64000 | 5070.5 | 0 | 0 | -149 | 1350000 | 0 | 0
2021090704 | 3 | 0.45161 | 67741.5 | 0.2324 | 0 | 0.55973 | 6996.625 | 0 | 0 | 64000 | 3741.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090705 | 3 | 0.45527 | 68290.5 | 0.19395 | 0 | 0.53252 | 6656.5 | 0 | 0 | 64000 | 4290.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021090706 | 3 | 0.47799 | 71698.5 | 0.16639 | 0 | 0.52278 | 6534.75 | 0 | 0 | 64000 | 6534.75 | 0 | 1163.75 | 1163.75 | 1350000 | 1163.75 | 0
2021090707 | 3 | 0.5173 | 77595 | 0.16524 | 0 | 0.54095 | 6761.875 | 0.03858 | 3086.4 | 64000 | 6761.875 | 3086.4 | 3746.725 | 2582.975 | 1350000 | 3746.725 | 0
2021090708 | 3 | 0.54646 | 81969 | 0.19189 | 0 | 0.54819 | 6852.375 | 0.27529 | 22023.2 | 64000 | 6852.375 | 11116.625 | 0 | -3746.725 | 1350000 | 0 | 0
2021090709 | 3 | 0.57409 | 86113.5 | 0.16459 | 0 | 0.54647 | 6830.875 | 0.5176 | 41408 | 64000 | 6830.875 | 15282.625 | 0 | 0 | 1350000 | 0 | 0
2021090710 | 3 | 0.60225 | 90337.5 | 0.07369 | 0 | 0.53884 | 6735.5 | 0.60196 | 48156.8 | 64000 | 6735.5 | 19602 | 0 | 0 | 1350000 | 0 | 0
2021090711 | 3 | 0.63295 | 94942.5 | 0.0947 | 0 | 0.53802 | 6725.25 | 0.63039 | 50431.2 | 64000 | 6725.25 | 24217.25 | 0 | 0 | 1350000 | 0 | 0
2021090712 | 3 | 0.66804 | 100206 | 0.16734 | 0 | 0.5145 | 6431.25 | 0.65301 | 52240.8 | 64000 | 6431.25 | 29774.75 | 0 | 0 | 1350000 | 0 | 0
2021090713 | 3 | 0.70472 | 105708 | 0.21819 | 0 | 0.51286 | 6410.75 | 0.65459 | 52367.2 | 64000 | 6410.75 | 35297.25 | 0 | 0 | 1350000 | 0 | 0
2021090714 | 3 | 0.7431 | 111465 | 0.26492 | 0 | 0.51253 | 6406.625 | 0.65817 | 52653.6 | 64000 | 6406.625 | 41058.375 | 0 | 0 | 1350000 | 0 | 0
2021090715 | 3 | 0.7701 | 115515 | 0.28372 | 0 | 0.50015 | 6251.875 | 0.65122 | 52097.6 | 64000 | 6251.875 | 45263.125 | 0 | 0 | 1350000 | 0 | 0
2021090716 | 3 | 0.78362 | 117543 | 0.26965 | 0 | 0.46943 | 5867.875 | 0.63929 | 51143.2 | 64000 | 5867.875 | 47675.125 | 0 | 0 | 1350000 | 0 | 0
2021090717 | 3 | 0.79293 | 118939.5 | 0.23694 | 0 | 0.46047 | 5755.875 | 0.60866 | 48692.8 | 64000 | 5755.875 | 48692.8 | 490.825 | 490.825 | 1350000 | 490.825 | 0
2021090718 | 3 | 0.79588 | 119382 | 0.21584 | 0 | 0.48865 | 6108.125 | 0.50295 | 40236 | 64000 | 6108.125 | 40236 | 9037.875 | 8547.05 | 1350000 | 9037.875 | 0
2021090719 | 3 | 0.77956 | 116934 | 0.22742 | 0 | 0.54848 | 6856 | 0.21309 | 17047.2 | 64000 | 6856 | 17047.2 | 29030.8 | 19992.925 | 1346435.45 | 29030.8 | 0
2021090720 | 3 | 0.74974 | 112461 | 0.30589 | 0 | 0.55189 | 6898.625 | 0.01502 | 1201.6 | 64000 | 6898.625 | 1201.6 | 40360.775 | 11329.975 | 1331540.925 | 40360.775 | 0
2021090721 | 3 | 0.7312 | 109680 | 0.43895 | 0 | 0.51897 | 6487.125 | 0 | 0 | 64000 | 6487.125 | 0 | 39192.875 | -1167.9 | 1317814.3 | 39192.875 | 0
2021090722 | 3 | 0.68922 | 103383 | 0.5385 | 0 | 0.47183 | 5897.875 | 0 | 0 | 64000 | 5897.875 | 0 | 33485.125 | -5707.75 | 1309795.425 | 33485.125 | 0
2021090723 | 3 | 0.6379 | 95685 | 0.59168 | 0 | 0.39688 | 4961 | 0 | 0 | 64000 | 4961 | 0 | 26724 | -6761.125 | 1308537.675 | 26724 | 0
2021090724 | 3 | 0.58844 | 88266 | 0.6542 | 0 | 0.33092 | 4136.5 | 0 | 0 | 64000 | 4136.5 | 0 | 20129.5 | -6594.5 | 1313874.425 | 20129.5 | 0
2021090801 | 4 | 0.54698 | 82047 | 0.72155 | 0 | 0.32924 | 4115.5 | 0 | 0 | 64000 | 4115.5 | 0 | 13931.5 | -6198 | 1325409.175 | 13931.5 | 0
2021090802 | 4 | 0.51969 | 77953.5 | 0.74965 | 0 | 0.36072 | 4509 | 0 | 0 | 64000 | 4509 | 0 | 9444.5 | -4487 | 1341430.925 | 9444.5 | 0
2021090803 | 4 | 0.50172 | 75258 | 0.71666 | 0 | 0.42625 | 5328.125 | 0 | 0 | 64000 | 5328.125 | 0 | 5929.875 | -3514.625 | 1350000 | 5929.875 | 0
2021090804 | 4 | 0.49225 | 73837.5 | 0.69894 | 0 | 0.48066 | 6008.25 | 0 | 0 | 64000 | 6008.25 | 0 | 3829.25 | -2100.625 | 1350000 | 3829.25 | 0
2021090805 | 4 | 0.4929 | 73935 | 0.75554 | 0 | 0.49188 | 6148.5 | 0 | 0 | 64000 | 6148.5 | 0 | 3786.5 | -42.75 | 1350000 | 3786.5 | 0
2021090806 | 4 | 0.5115 | 76725 | 0.75903 | 0 | 0.43445 | 5430.625 | 0 | 0 | 64000 | 5430.625 | 0 | 7294.375 | 3507.875 | 1350000 | 7294.375 | 0
2021090807 | 4 | 0.55306 | 82959 | 0.70318 | 0 | 0.36214 | 4526.75 | 0.02596 | 2076.8 | 64000 | 4526.75 | 2076.8 | 12355.45 | 5061.075 | 1350000 | 12355.45 | 0
2021090808 | 4 | 0.58246 | 87369 | 0.69792 | 0 | 0.3175 | 3968.75 | 0.18314 | 14651.2 | 64000 | 3968.75 | 14651.2 | 4749.05 | -7606.4 | 1350000 | 4749.05 | 0
2021090809 | 4 | 0.60675 | 91012.5 | 0.61678 | 0 | 0.24446 | 3055.75 | 0.32554 | 26043.2 | 64000 | 3055.75 | 23956.75 | 0 | -4749.05 | 1350000 | 0 | 0
2021090810 | 4 | 0.6342 | 95130 | 0.55052 | 0 | 0.21747 | 2718.375 | 0.37182 | 29745.6 | 64000 | 2718.375 | 28411.625 | 0 | 0 | 1350000 | 0 | 0
2021090811 | 4 | 0.66653 | 99979.5 | 0.53541 | 0 | 0.18478 | 2309.75 | 0.39345 | 31476 | 64000 | 2309.75 | 31476 | 2193.75 | 2193.75 | 1350000 | 2193.75 | 0
2021090812 | 4 | 0.70014 | 105021 | 0.51972 | 0 | 0.16588 | 2073.5 | 0.40211 | 32168.8 | 64000 | 2073.5 | 32168.8 | 6778.7 | 4584.95 | 1350000 | 6778.7 | 0
2021090813 | 4 | 0.7327 | 109905 | 0.43613 | 0 | 0.17618 | 2202.25 | 0.40169 | 32135.2 | 64000 | 2202.25 | 32135.2 | 11567.55 | 4788.85 | 1350000 | 11567.55 | 0
2021090814 | 4 | 0.75927 | 113890.5 | 0.51165 | 0 | 0.20053 | 2506.625 | 0.38079 | 30463.2 | 64000 | 2506.625 | 30463.2 | 16920.675 | 5353.125 | 1350000 | 16920.675 | 0
2021090815 | 4 | 0.77465 | 116197.5 | 0.54543 | 0 | 0.22105 | 2763.125 | 0.33751 | 27000.8 | 64000 | 2763.125 | 27000.8 | 22433.575 | 5512.9 | 1350000 | 22433.575 | 0
2021090816 | 4 | 0.7882 | 118230 | 0.52836 | 0 | 0.25199 | 3149.875 | 0.2931 | 23448 | 64000 | 3149.875 | 23448 | 27632.125 | 5198.55 | 1347834.125 | 27632.125 | 0
2021090817 | 4 | 0.79885 | 119827.5 | 0.36787 | 0 | 0.29767 | 3720.875 | 0.23553 | 18842.4 | 64000 | 3720.875 | 18842.4 | 33264.225 | 5632.1 | 1340036.15 | 33264.225 | 0
2021090818 | 4 | 0.79875 | 119812.5 | 0.33838 | 0 | 0.3116 | 3895 | 0.11434 | 9147.2 | 64000 | 3895 | 9147.2 | 42770.3 | 9506.075 | 1322732.1 | 42770.3 | 0
2021090819 | 4 | 0.7778 | 116670 | 0.36449 | 0 | 0.30649 | 3831.125 | 0.04618 | 3694.4 | 64000 | 3831.125 | 3694.4 | 45144.475 | 2374.175 | 1303053.875 | 45144.475 | 0
2021090820 | 4 | 0.75194 | 112791 | 0.43924 | 0 | 0.29944 | 3743 | 0.00213 | 170.4 | 64000 | 3743 | 170.4 | 44877.6 | -266.875 | 1283642.525 | 44877.6 | 0
2021090821 | 4 | 0.7328 | 109920 | 0.30544 | 0 | 0.30589 | 3823.625 | 0 | 0 | 64000 | 3823.625 | 0 | 42096.375 | -2781.225 | 1267012.4 | 42096.375 | 0
2021090822 | 4 | 0.69238 | 103857 | 0.27996 | 0 | 0.33973 | 4246.625 | 0 | 0 | 64000 | 4246.625 | 0 | 35610.375 | -6486 | 1256868.275 | 35610.375 | 0
2021090823 | 4 | 0.64142 | 96213 | 0.32732 | 0 | 0.37815 | 4726.875 | 0 | 0 | 64000 | 4726.875 | 0 | 27486.125 | -8124.25 | 1254848.4 | 27486.125 | 0
2021090824 | 4 | 0.59482 | 89223 | 0.19445 | 0 | 0.40182 | 5022.75 | 0 | 0 | 64000 | 5022.75 | 0 | 20200.25 | -7285.875 | 1260114.4 | 20200.25 | 0
2021090901 | 5 | 0.55468 | 83202 | 0.08394 | 0 | 0.3774 | 4717.5 | 0 | 0 | 64000 | 4717.5 | 0 | 14484.5 | -5715.75 | 1271096.15 | 14484.5 | 0
2021090902 | 5 | 0.52541 | 78811.5 | 0.05664 | 0 | 0.39842 | 4980.25 | 0 | 0 | 64000 | 4980.25 | 0 | 9831.25 | -4653.25 | 1286731.15 | 9831.25 | 0
2021090903 | 5 | 0.50552 | 75828 | 0.04807 | 0 | 0.36781 | 4597.625 | 0 | 0 | 64000 | 4597.625 | 0 | 7230.375 | -2600.875 | 1304967.025 | 7230.375 | 0
2021090904 | 5 | 0.49448 | 74172 | 0.03534 | 0 | 0.29994 | 3749.25 | 0 | 0 | 64000 | 3749.25 | 0 | 6422.75 | -807.625 | 1324010.525 | 6422.75 | 0
2021090905 | 5 | 0.4944 | 74160 | 0.04879 | 0 | 0.2286 | 2857.5 | 0 | 0 | 64000 | 2857.5 | 0 | 7302.5 | 879.75 | 1342174.275 | 7302.5 | 0
2021090906 | 5 | 0.5143 | 77145 | 0.06746 | 0 | 0.17539 | 2192.375 | 0 | 0 | 64000 | 2192.375 | 0 | 10952.625 | 3650.125 | 1350000 | 10952.625 | 0
2021090907 | 5 | 0.55432 | 83148 | 0.07151 | 0 | 0.14029 | 1753.625 | 0.00303 | 242.4 | 64000 | 1753.625 | 242.4 | 17151.975 | 6199.35 | 1350000 | 17151.975 | 0
2021090908 | 5 | 0.58116 | 87174 | 0.05371 | 0 | 0.08224 | 1028 | 0.02384 | 1907.2 | 64000 | 1028 | 1907.2 | 20238.8 | 3086.825 | 1350000 | 20238.8 | 0
2021090909 | 5 | 0.5987 | 89805 | 0.04022 | 0 | 0.06627 | 828.375 | 0.05966 | 4772.8 | 64000 | 828.375 | 4772.8 | 20203.825 | -34.975 | 1350000 | 20203.825 | 0
2021090910 | 5 | 0.6158 | 92370 | 0.04192 | 0 | 0.06758 | 844.75 | 0.10297 | 8237.6 | 64000 | 844.75 | 8237.6 | 19287.65 | -916.175 | 1350000 | 19287.65 | 0
2021090911 | 5 | 0.63293 | 94939.5 | 0.02854 | 0 | 0.08918 | 1114.75 | 0.15196 | 12156.8 | 64000 | 1114.75 | 12156.8 | 17667.95 | -1619.7 | 1350000 | 17667.95 | 0
2021090912 | 5 | 0.64371 | 96556.5 | 0.04601 | 0 | 0.07701 | 962.625 | 0.24473 | 19578.4 | 64000 | 962.625 | 19578.4 | 12015.475 | -5652.475 | 1350000 | 12015.475 | 0
2021090913 | 5 | 0.65512 | 98268 | 0.10437 | 0 | 0.06541 | 817.625 | 0.32809 | 26247.2 | 64000 | 817.625 | 26247.2 | 7203.175 | -4812.3 | 1350000 | 7203.175 | 0
2021090914 | 5 | 0.66415 | 99622.5 | 0.19454 | 0 | 0.05717 | 714.625 | 0.37447 | 29957.6 | 64000 | 714.625 | 29957.6 | 4950.275 | -2252.9 | 1350000 | 4950.275 | 0
2021090915 | 5 | 0.66726 | 100089 | 0.24462 | 0 | 0.04246 | 530.75 | 0.39763 | 31810.4 | 64000 | 530.75 | 31810.4 | 3747.85 | -1202.425 | 1350000 | 3747.85 | 0
2021090916 | 5 | 0.67024 | 100536 | 0.37513 | 0 | 0.03042 | 380.25 | 0.3793 | 30344 | 64000 | 380.25 | 30344 | 5811.75 | 2063.9 | 1350000 | 5811.75 | 0
2021090917 | 5 | 0.67638 | 101457 | 0.22877 | 0 | 0.02427 | 303.375 | 0.33126 | 26500.8 | 64000 | 303.375 | 26500.8 | 10652.825 | 4841.075 | 1350000 | 10652.825 | 0
2021090918 | 5 | 0.67746 | 101619 | 0.31883 | 0 | 0.03995 | 499.375 | 0.25579 | 20463.2 | 64000 | 499.375 | 20463.2 | 16656.425 | 6003.6 | 1350000 | 16656.425 | 0
2021090919 | 5 | 0.66898 | 100347 | 0.37218 | 0 | 0.05036 | 629.5 | 0.12582 | 10065.6 | 64000 | 629.5 | 10065.6 | 25651.9 | 8995.475 | 1349814.35 | 25651.9 | 0
2021090920 | 5 | 0.65565 | 98347.5 | 0.43675 | 0 | 0.05214 | 651.75 | 0.01272 | 1017.6 | 64000 | 651.75 | 1017.6 | 32678.15 | 7026.25 | 1342602.45 | 32678.15 | 0
2021090921 | 5 | 0.64541 | 96811.5 | 0.49233 | 0 | 0.05618 | 702.25 | 0 | 0 | 64000 | 702.25 | 0 | 32109.25 | -568.9 | 1335959.45 | 32109.25 | 0
2021090922 | 5 | 0.61419 | 92128.5 | 0.51993 | 0 | 0.09182 | 1147.75 | 0 | 0 | 64000 | 1147.75 | 0 | 26980.75 | -5128.5 | 1334444.95 | 26980.75 | 0
2021090923 | 5 | 0.57316 | 85974 | 0.42955 | 0 | 0.11924 | 1490.5 | 0 | 0 | 64000 | 1490.5 | 0 | 20483.5 | -6497.25 | 1339427.7 | 20483.5 | 0
2021090924 | 5 | 0.53089 | 79633.5 | 0.42916 | 0 | 0.13813 | 1726.625 | 0 | 0 | 64000 | 1726.625 | 0 | 13906.875 | -6576.625 | 1350000 | 13906.875 | 0
2021091001 | 6 | 0.49803 | 74704.5 | 0.49814 | 0 | 0.18916 | 2364.5 | 0 | 0 | 64000 | 2364.5 | 0 | 8340 | -5566.875 | 1350000 | 8340 | 0
2021091002 | 6 | 0.47527 | 71290.5 | 0.53071 | 0 | 0.23074 | 2884.25 | 0 | 0 | 64000 | 2884.25 | 0 | 4406.25 | -3933.75 | 1350000 | 4406.25 | 0
2021091003 | 6 | 0.45861 | 68791.5 | 0.47048 | 0 | 0.22063 | 2757.875 | 0 | 0 | 64000 | 2757.875 | 0 | 2033.625 | -2372.625 | 1350000 | 2033.625 | 0
2021091004 | 6 | 0.45175 | 67762.5 | 0.49259 | 0 | 0.18221 | 2277.625 | 0 | 0 | 64000 | 2277.625 | 0 | 1484.875 | -548.75 | 1350000 | 1484.875 | 0
2021091005 | 6 | 0.45349 | 68023.5 | 0.53066 | 0 | 0.16255 | 2031.875 | 0 | 0 | 64000 | 2031.875 | 0 | 1991.625 | 506.75 | 1350000 | 1991.625 | 0
2021091006 | 6 | 0.47296 | 70944 | 0.61555 | 0 | 0.14666 | 1833.25 | 0 | 0 | 64000 | 1833.25 | 0 | 5110.75 | 3119.125 | 1350000 | 5110.75 | 0
2021091007 | 6 | 0.51015 | 76522.5 | 0.61417 | 0 | 0.21255 | 2656.875 | 0.02571 | 2056.8 | 64000 | 2656.875 | 2056.8 | 7808.825 | 2698.075 | 1350000 | 7808.825 | 0
2021091008 | 6 | 0.53442 | 80163 | 0.54078 | 0 | 0.28559 | 3569.875 | 0.119 | 9520 | 64000 | 3569.875 | 9520 | 3073.125 | -4735.7 | 1350000 | 3073.125 | 0
2021091009 | 6 | 0.55162 | 82743 | 0.52501 | 0 | 0.33931 | 4241.375 | 0.24046 | 19236.8 | 64000 | 4241.375 | 14501.625 | 0 | -3073.125 | 1350000 | 0 | 0
2021091010 | 6 | 0.56585 | 84877.5 | 0.61125 | 0 | 0.40099 | 5012.375 | 0.34705 | 27764 | 64000 | 5012.375 | 15865.125 | 0 | 0 | 1350000 | 0 | 0
2021091011 | 6 | 0.58137 | 87205.5 | 0.65142 | 0 | 0.4191 | 5238.75 | 0.45342 | 36273.6 | 64000 | 5238.75 | 17966.75 | 0 | 0 | 1350000 | 0 | 0
2021091012 | 6 | 0.59416 | 89124 | 0.6623 | 0 | 0.38292 | 4786.5 | 0.56374 | 45099.2 | 64000 | 4786.5 | 20337.5 | 0 | 0 | 1350000 | 0 | 0
2021091013 | 6 | 0.60797 | 91195.5 | 0.69094 | 0 | 0.3563 | 4453.75 | 0.59652 | 47721.6 | 64000 | 4453.75 | 22741.75 | 0 | 0 | 1350000 | 0 | 0
2021091014 | 6 | 0.62278 | 93417 | 0.65588 | 0 | 0.34818 | 4352.25 | 0.62238 | 49790.4 | 64000 | 4352.25 | 25064.75 | 0 | 0 | 1350000 | 0 | 0
2021091015 | 6 | 0.63668 | 95502 | 0.65031 | 0 | 0.3806 | 4757.5 | 0.61428 | 49142.4 | 64000 | 4757.5 | 26744.5 | 0 | 0 | 1350000 | 0 | 0
2021091016 | 6 | 0.6485 | 97275 | 0.53981 | 0 | 0.42882 | 5360.25 | 0.59679 | 47743.2 | 64000 | 5360.25 | 27914.75 | 0 | 0 | 1350000 | 0 | 0
2021091017 | 6 | 0.66011 | 99016.5 | 0.39931 | 0 | 0.38393 | 4799.125 | 0.538 | 43040 | 64000 | 4799.125 | 30217.375 | 0 | 0 | 1350000 | 0 | 0
2021091018 | 6 | 0.66277 | 99415.5 | 0.32589 | 0 | 0.37681 | 4710.125 | 0.44901 | 35920.8 | 64000 | 4710.125 | 30705.375 | 0 | 0 | 1350000 | 0 | 0
2021091019 | 6 | 0.64828 | 97242 | 0.24376 | 0 | 0.42383 | 5297.875 | 0.19328 | 15462.4 | 64000 | 5297.875 | 15462.4 | 12481.725 | 12481.725 | 1350000 | 12481.725 | 0
2021091020 | 6 | 0.62543 | 93814.5 | 0.19918 | 0 | 0.45938 | 5742.25 | 0.01257 | 1005.6 | 64000 | 5742.25 | 1005.6 | 23066.65 | 10584.925 | 1350000 | 23066.65 | 0
2021091021 | 6 | 0.60958 | 91437 | 0.16851 | 0 | 0.51061 | 6382.625 | 0 | 0 | 64000 | 6382.625 | 0 | 21054.375 | -2012.275 | 1350000 | 21054.375 | 0
2021091022 | 6 | 0.58014 | 87021 | 0.13473 | 0 | 0.54553 | 6819.125 | 0 | 0 | 64000 | 6819.125 | 0 | 16201.875 | -4852.5 | 1350000 | 16201.875 | 0
2021091023 | 6 | 0.54545 | 81817.5 | 0.13764 | 0 | 0.58256 | 7282 | 0 | 0 | 64000 | 7282 | 0 | 10535.5 | -5666.375 | 1350000 | 10535.5 | 0
2021091024 | 6 | 0.50936 | 76404 | 0.16896 | 0 | 0.58579 | 7322.375 | 0 | 0 | 64000 | 7322.375 | 0 | 5081.625 | -5453.875 | 1350000 | 5081.625 | 0
2021091101 | 7 | 0.47823 | 71734.5 | 0.19791 | 0 | 0.59662 | 7457.75 | 0 | 0 | 64000 | 7457.75 | 0 | 276.75 | -4804.875 | 1350000 | 276.75 | 0
2021091102 | 7 | 0.45553 | 68329.5 | 0.20138 | 0 | 0.56329 | 7041.125 | 0 | 0 | 64000 | 4329.5 | 0 | 0 | -276.75 | 1350000 | 0 | 0
2021091103 | 7 | 0.44253 | 66379.5 | 0.17696 | 0 | 0.51705 | 6463.125 | 0 | 0 | 64000 | 2379.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021091104 | 7 | 0.43217 | 64825.5 | 0.15249 | 0 | 0.45578 | 5697.25 | 0 | 0 | 64000 | 825.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021091105 | 7 | 0.42997 | 64495.5 | 0.14495 | 0 | 0.37518 | 4689.75 | 0 | 0 | 64000 | 495.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021091106 | 7 | 0.43624 | 65436 | 0.17199 | 0 | 0.28313 | 3539.125 | 0 | 0 | 64000 | 1436 | 0 | 0 | 0 | 1350000 | 0 | 0
2021091107 | 7 | 0.44801 | 67201.5 | 0.23397 | 0 | 0.32337 | 4042.125 | 0.03144 | 2515.2 | 64000 | 3201.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021091108 | 7 | 0.46032 | 69048 | 0.29584 | 0 | 0.39281 | 4910.125 | 0.19792 | 15833.6 | 64000 | 4910.125 | 137.875 | 0 | 0 | 1350000 | 0 | 0
2021091109 | 7 | 0.48165 | 72247.5 | 0.27858 | 0 | 0.43278 | 5409.75 | 0.2901 | 23208 | 64000 | 5409.75 | 2837.75 | 0 | 0 | 1350000 | 0 | 0
2021091110 | 7 | 0.50411 | 75616.5 | 0.17539 | 0 | 0.461 | 5762.5 | 0.37039 | 29631.2 | 64000 | 5762.5 | 5854 | 0 | 0 | 1350000 | 0 | 0
2021091111 | 7 | 0.52505 | 78757.5 | 0.10266 | 0 | 0.47341 | 5917.625 | 0.40842 | 32673.6 | 64000 | 5917.625 | 8839.875 | 0 | 0 | 1350000 | 0 | 0
2021091112 | 7 | 0.54735 | 82102.5 | 0.11877 | 0 | 0.48657 | 6082.125 | 0.4575 | 36600 | 64000 | 6082.125 | 12020.375 | 0 | 0 | 1350000 | 0 | 0
2021091113 | 7 | 0.56978 | 85467 | 0.15233 | 0 | 0.49044 | 6130.5 | 0.48422 | 38737.6 | 64000 | 6130.5 | 15336.5 | 0 | 0 | 1350000 | 0 | 0
2021091114 | 7 | 0.59194 | 88791 | 0.1709 | 0 | 0.45848 | 5731 | 0.52149 | 41719.2 | 64000 | 5731 | 19060 | 0 | 0 | 1350000 | 0 | 0
2021091115 | 7 | 0.61288 | 91932 | 0.18449 | 0 | 0.37957 | 4744.625 | 0.55293 | 44234.4 | 64000 | 4744.625 | 23187.375 | 0 | 0 | 1350000 | 0 | 0
2021091116 | 7 | 0.63301 | 94951.5 | 0.25603 | 0 | 0.3071 | 3838.75 | 0.56483 | 45186.4 | 64000 | 3838.75 | 27112.75 | 0 | 0 | 1350000 | 0 | 0
2021091117 | 7 | 0.64978 | 97467 | 0.35299 | 0 | 0.24532 | 3066.5 | 0.53921 | 43136.8 | 64000 | 3066.5 | 30400.5 | 0 | 0 | 1350000 | 0 | 0
2021091118 | 7 | 0.6608 | 99120 | 0.37074 | 0 | 0.27541 | 3442.625 | 0.45685 | 36548 | 64000 | 3442.625 | 31677.375 | 0 | 0 | 1350000 | 0 | 0
2021091119 | 7 | 0.65256 | 97884 | 0.36981 | 0 | 0.29486 | 3685.75 | 0.18733 | 14986.4 | 64000 | 3685.75 | 14986.4 | 15211.85 | 15211.85 | 1350000 | 15211.85 | 0
2021091120 | 7 | 0.63616 | 95424 | 0.46243 | 0 | 0.28827 | 3603.375 | 0.01124 | 899.2 | 64000 | 3603.375 | 899.2 | 26921.425 | 11709.575 | 1348544.825 | 26921.425 | 0
2021091121 | 7 | 0.6263 | 93945 | 0.63736 | 0 | 0.28442 | 3555.25 | 0 | 0 | 64000 | 3555.25 | 0 | 26389.75 | -531.675 | 1347621.325 | 26389.75 | 0
2021091122 | 7 | 0.60063 | 90094.5 | 0.74618 | 0 | 0.31071 | 3883.875 | 0 | 0 | 64000 | 3883.875 | 0 | 22210.625 | -4179.125 | 1350000 | 22210.625 | 0
2021091123 | 7 | 0.56918 | 85377 | 0.82181 | 0 | 0.31238 | 3904.75 | 0 | 0 | 64000 | 3904.75 | 0 | 17472.25 | -4738.375 | 1350000 | 17472.25 | 0
2021091124 | 7 | 0.53526 | 80289 | 0.86833 | 0 | 0.27518 | 3439.75 | 0 | 0 | 64000 | 3439.75 | 0 | 12849.25 | -4623 | 1350000 | 12849.25 | 0
2021091201 | 1 | 0.50371 | 75556.5 | 0.91809 | 0 | 0.25648 | 3206 | 0 | 0 | 64000 | 3206 | 0 | 8350.5 | -4498.75 | 1350000 | 8350.5 | 0
2021091202 | 1 | 0.48054 | 72081 | 0.93455 | 0 | 0.2635 | 3293.75 | 0 | 0 | 64000 | 3293.75 | 0 | 4787.25 | -3563.25 | 1350000 | 4787.25 | 0
2021091203 | 1 | 0.46404 | 69606 | 0.91543 | 0 | 0.24905 | 3113.125 | 0 | 0 | 64000 | 3113.125 | 0 | 2492.875 | -2294.375 | 1350000 | 2492.875 | 0
2021091204 | 1 | 0.45294 | 67941 | 0.92116 | 0 | 0.2346 | 2932.5 | 0 | 0 | 64000 | 2932.5 | 0 | 1008.5 | -1484.375 | 1350000 | 1008.5 | 0
2021091205 | 1 | 0.4477 | 67155 | 0.93402 | 0 | 0.26495 | 3311.875 | 0 | 0 | 64000 | 3155 | 0 | 0 | -1008.5 | 1350000 | 0 | 0
2021091206 | 1 | 0.44888 | 67332 | 0.9379 | 0 | 0.31985 | 3998.125 | 0 | 0 | 64000 | 3332 | 0 | 0 | 0 | 1350000 | 0 | 0
2021091207 | 1 | 0.45573 | 68359.5 | 0.92331 | 0 | 0.40919 | 5114.875 | 0.01984 | 1587.2 | 64000 | 4359.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021091208 | 1 | 0.46339 | 69508.5 | 0.93452 | 0 | 0.44911 | 5613.875 | 0.1485 | 11880 | 64000 | 5508.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021091209 | 1 | 0.48863 | 73294.5 | 0.92322 | 0 | 0.48967 | 6120.875 | 0.35623 | 28498.4 | 64000 | 6120.875 | 3173.625 | 0 | 0 | 1350000 | 0 | 0
2021091210 | 1 | 0.52174 | 78261 | 0.87043 | 0 | 0.53139 | 6642.375 | 0.42203 | 33762.4 | 64000 | 6642.375 | 7618.625 | 0 | 0 | 1350000 | 0 | 0
2021091211 | 1 | 0.55881 | 83821.5 | 0.78311 | 0 | 0.52163 | 6520.375 | 0.42573 | 34058.4 | 64000 | 6520.375 | 13301.125 | 0 | 0 | 1350000 | 0 | 0
2021091212 | 1 | 0.59959 | 89938.5 | 0.74342 | 0 | 0.50398 | 6299.75 | 0.38896 | 31116.8 | 64000 | 6299.75 | 19638.75 | 0 | 0 | 1350000 | 0 | 0
2021091213 | 1 | 0.64065 | 96097.5 | 0.71761 | 0 | 0.44472 | 5559 | 0.40416 | 32332.8 | 64000 | 5559 | 26538.5 | 0 | 0 | 1350000 | 0 | 0
2021091214 | 1 | 0.67604 | 101406 | 0.67085 | 0 | 0.37052 | 4631.5 | 0.43111 | 34488.8 | 64000 | 4631.5 | 32774.5 | 0 | 0 | 1350000 | 0 | 0
2021091215 | 1 | 0.71029 | 106543.5 | 0.62458 | 0 | 0.32726 | 4090.75 | 0.49377 | 39501.6 | 64000 | 4090.75 | 38452.75 | 0 | 0 | 1350000 | 0 | 0
2021091216 | 1 | 0.73734 | 110601 | 0.56667 | 0 | 0.24267 | 3033.375 | 0.51696 | 41356.8 | 64000 | 3033.375 | 41356.8 | 2210.825 | 2210.825 | 1350000 | 2210.825 | 0
2021091217 | 1 | 0.75967 | 113950.5 | 0.58721 | 0 | 0.21503 | 2687.875 | 0.46612 | 37289.6 | 64000 | 2687.875 | 37289.6 | 9973.025 | 7762.2 | 1350000 | 9973.025 | 0
2021091218 | 1 | 0.76932 | 115398 | 0.57302 | 0 | 0.22057 | 2757.125 | 0.35499 | 28399.2 | 64000 | 2757.125 | 28399.2 | 20241.675 | 10268.65 | 1350000 | 20241.675 | 0
2021091219 | 1 | 0.7582 | 113730 | 0.54373 | 0 | 0.22106 | 2763.25 | 0.14055 | 11244 | 64000 | 2763.25 | 11244 | 35722.75 | 15481.075 | 1339743.5 | 35722.75 | 0
2021091220 | 1 | 0.74024 | 111036 | 0.63531 | 0 | 0.17091 | 2136.375 | 0.00838 | 670.4 | 64000 | 2136.375 | 670.4 | 44229.225 | 8506.475 | 1320980.525 | 44229.225 | 0
2021091221 | 1 | 0.72636 | 108954 | 0.76514 | 0 | 0.15387 | 1923.375 | 0 | 0 | 64000 | 1923.375 | 0 | 43030.625 | -1198.6 | 1303416.15 | 43030.625 | 0
2021091222 | 1 | 0.68818 | 103227 | 0.84336 | 0 | 0.15145 | 1893.125 | 0 | 0 | 64000 | 1893.125 | 0 | 37333.875 | -5696.75 | 1291548.525 | 37333.875 | 0
2021091223 | 1 | 0.64181 | 96271.5 | 0.87005 | 0 | 0.14616 | 1827 | 0 | 0 | 64000 | 1827 | 0 | 30444.5 | -6889.375 | 1286570.275 | 30444.5 | 0
2021091224 | 1 | 0.59765 | 89647.5 | 0.89424 | 0 | 0.14752 | 1844 | 0 | 0 | 64000 | 1844 | 0 | 23803.5 | -6641 | 1288233.025 | 23803.5 | 0
2021091301 | 2 | 0.56033 | 84049.5 | 0.913 | 0 | 0.13623 | 1702.875 | 0 | 0 | 64000 | 1702.875 | 0 | 18346.625 | -5456.875 | 1295352.65 | 18346.625 | 0
2021091302 | 2 | 0.5342 | 80130 | 0.90447 | 0 | 0.10859 | 1357.375 | 0 | 0 | 64000 | 1357.375 | 0 | 14772.625 | -3574 | 1306046.275 | 14772.625 | 0
2021091303 | 2 | 0.51771 | 77656.5 | 0.89429 | 0 | 0.08279 | 1034.875 | 0 | 0 | 64000 | 1034.875 | 0 | 12621.625 | -2151 | 1318890.9 | 12621.625 | 0
2021091304 | 2 | 0.50927 | 76390.5 | 0.87015 | 0 | 0.09019 | 1127.375 | 0 | 0 | 64000 | 1127.375 | 0 | 11263.125 | -1358.5 | 1333094.025 | 11263.125 | 0
2021091305 | 2 | 0.51253 | 76879.5 | 0.78119 | 0 | 0.10023 | 1252.875 | 0 | 0 | 64000 | 1252.875 | 0 | 11626.625 | 363.5 | 1346933.65 | 11626.625 | 0
2021091306 | 2 | 0.53577 | 80365.5 | 0.77414 | 0 | 0.12346 | 1543.25 | 0 | 0 | 64000 | 1543.25 | 0 | 14822.25 | 3195.625 | 1350000 | 14822.25 | 0
2021091307 | 2 | 0.57893 | 86839.5 | 0.72867 | 0 | 0.15583 | 1947.875 | 0.01832 | 1465.6 | 64000 | 1947.875 | 1465.6 | 19426.025 | 4603.775 | 1350000 | 19426.025 | 0
2021091308 | 2 | 0.60865 | 91297.5 | 0.59547 | 0 | 0.19421 | 2427.625 | 0.186 | 14880 | 64000 | 2427.625 | 14880 | 9989.875 | -9436.15 | 1350000 | 9989.875 | 0
2021091309 | 2 | 0.63495 | 95242.5 | 0.5632 | 0 | 0.1936 | 2420 | 0.37805 | 30244 | 64000 | 2420 | 28822.5 | 0 | -9989.875 | 1350000 | 0 | 0
2021091310 | 2 | 0.6647 | 99705 | 0.5116 | 0 | 0.15914 | 1989.25 | 0.47491 | 37992.8 | 64000 | 1989.25 | 33715.75 | 0 | 0 | 1350000 | 0 | 0
2021091311 | 2 | 0.70115 | 105172.5 | 0.52842 | 0 | 0.13507 | 1688.375 | 0.50643 | 40514.4 | 64000 | 1688.375 | 39484.125 | 0 | 0 | 1350000 | 0 | 0
2021091312 | 2 | 0.73912 | 110868 | 0.45439 | 0 | 0.1232 | 1540 | 0.53712 | 42969.6 | 64000 | 1540 | 42969.6 | 2358.4 | 2358.4 | 1350000 | 2358.4 | 0
2021091313 | 2 | 0.77859 | 116788.5 | 0.39323 | 0 | 0.09393 | 1174.125 | 0.54657 | 43725.6 | 64000 | 1174.125 | 43725.6 | 7888.775 | 5530.375 | 1350000 | 7888.775 | 0
2021091314 | 2 | 0.81798 | 122697 | 0.27941 | 0 | 0.08979 | 1122.375 | 0.53928 | 43142.4 | 64000 | 1122.375 | 43142.4 | 14432.225 | 6543.45 | 1350000 | 14432.225 | 0
2021091315 | 2 | 0.84667 | 127000.5 | 0.20125 | 0 | 0.09867 | 1233.375 | 0.52789 | 42231.2 | 64000 | 1233.375 | 42231.2 | 19535.925 | 5103.7 | 1350000 | 19535.925 | 0
2021091316 | 2 | 0.86825 | 130237.5 | 0.21257 | 0 | 0.09978 | 1247.25 | 0.50426 | 40340.8 | 64000 | 1247.25 | 40340.8 | 24649.45 | 5113.525 | 1350000 | 24649.45 | 0
2021091317 | 2 | 0.88216 | 132324 | 0.26633 | 0 | 0.10044 | 1255.5 | 0.47087 | 37669.6 | 64000 | 1255.5 | 37669.6 | 29398.9 | 4749.45 | 1346067.35 | 29398.9 | 0
2021091318 | 2 | 0.87806 | 131709 | 0.23283 | 0 | 0.09304 | 1163 | 0.38056 | 30444.8 | 64000 | 1163 | 30444.8 | 36101.2 | 6702.3 | 1335432.4 | 36101.2 | 0
2021091319 | 2 | 0.8535 | 128025 | 0.26648 | 0 | 0.09663 | 1207.875 | 0.15671 | 12536.8 | 64000 | 1207.875 | 12536.8 | 50280.325 | 14179.125 | 1310618.325 | 50280.325 | 0
2021091320 | 2 | 0.82491 | 123736.5 | 0.25673 | 0 | 0.10785 | 1348.125 | 0.00931 | 744.8 | 64000 | 1348.125 | 744.8 | 57643.575 | 7363.25 | 1278441 | 57643.575 | 0
2021091321 | 2 | 0.79848 | 119772 | 0.22125 | 0 | 0.14018 | 1752.25 | 0 | 0 | 64000 | 1752.25 | 0 | 54019.75 | -3623.825 | 1249887.5 | 54019.75 | 0
2021091322 | 2 | 0.74835 | 112252.5 | 0.28367 | 0 | 0.17718 | 2214.75 | 0 | 0 | 64000 | 2214.75 | 0 | 46037.75 | -7982 | 1229316 | 46037.75 | 0
2021091323 | 2 | 0.68822 | 103233 | 0.44944 | 0 | 0.19626 | 2453.25 | 0 | 0 | 64000 | 2453.25 | 0 | 36779.75 | -9258 | 1218002.5 | 36779.75 | 0
2021091324 | 2 | 0.63378 | 95067 | 0.49472 | 0 | 0.19393 | 2424.125 | 0 | 0 | 64000 | 2424.125 | 0 | 28642.875 | -8136.875 | 1214825.875 | 28642.875 | 0
2021091401 | 3 | 0.59067 | 88600.5 | 0.52949 | 0 | 0.20517 | 2564.625 | 0 | 0 | 64000 | 2564.625 | 0 | 22035.875 | -6607 | 1218256.25 | 22035.875 | 0
2021091402 | 3 | 0.55783 | 83674.5 | 0.46635 | 0 | 0.24694 | 3086.75 | 0 | 0 | 64000 | 3086.75 | 0 | 16587.75 | -5448.125 | 1227134.75 | 16587.75 | 0
2021091403 | 3 | 0.53646 | 80469 | 0.37794 | 0 | 0.29217 | 3652.125 | 0 | 0 | 64000 | 3652.125 | 0 | 12816.875 | -3770.875 | 1239784.125 | 12816.875 | 0
2021091404 | 3 | 0.52548 | 78822 | 0.31212 | 0 | 0.29925 | 3740.625 | 0 | 0 | 64000 | 3740.625 | 0 | 11081.375 | -1735.5 | 1254169 | 11081.375 | 0
2021091405 | 3 | 0.52636 | 78954 | 0.30331 | 0 | 0.36946 | 4618.25 | 0 | 0 | 64000 | 4618.25 | 0 | 10335.75 | -745.625 | 1269299.5 | 10335.75 | 0
2021091406 | 3 | 0.54737 | 82105.5 | 0.3263 | 0 | 0.42459 | 5307.375 | 0 | 0 | 64000 | 5307.375 | 0 | 12798.125 | 2462.375 | 1281967.625 | 12798.125 | 0
2021091407 | 3 | 0.59006 | 88509 | 0.30229 | 0 | 0.48953 | 6119.125 | 0.02036 | 1628.8 | 64000 | 6119.125 | 1628.8 | 16761.075 | 3962.95 | 1290672.8 | 16761.075 | 0
2021091408 | 3 | 0.61974 | 92961 | 0.25307 | 0 | 0.52555 | 6569.375 | 0.19166 | 15332.8 | 64000 | 6569.375 | 15332.8 | 7058.825 | -9702.25 | 1309080.225 | 7058.825 | 0
2021091409 | 3 | 0.64526 | 96789 | 0.18052 | 0 | 0.55877 | 6984.625 | 0.30895 | 24716 | 64000 | 6984.625 | 24716 | 1088.375 | -5970.45 | 1333458.1 | 1088.375 | 0
2021091410 | 3 | 0.67962 | 101943 | 0.13854 | 0 | 0.56536 | 7067 | 0.29805 | 23844 | 64000 | 7067 | 23844 | 7032 | 5943.625 | 1350000 | 7032 | 0
2021091411 | 3 | 0.72277 | 108415.5 | 0.11629 | 0 | 0.53567 | 6695.875 | 0.2778 | 22224 | 64000 | 6695.875 | 22224 | 15495.625 | 8463.625 | 1350000 | 15495.625 | 0
2021091412 | 3 | 0.76706 | 115059 | 0.15616 | 0 | 0.52009 | 6501.125 | 0.2573 | 20584 | 64000 | 6501.125 | 20584 | 23973.875 | 8478.25 | 1350000 | 23973.875 | 0
2021091413 | 3 | 0.80967 | 121450.5 | 0.2054 | 0 | 0.50524 | 6315.5 | 0.26265 | 21012 | 64000 | 6315.5 | 21012 | 30123 | 6149.125 | 1345343.25 | 30123 | 0
2021091414 | 3 | 0.84642 | 126963 | 0.242 | 0 | 0.49996 | 6249.5 | 0.27849 | 22279.2 | 64000 | 6249.5 | 22279.2 | 34434.3 | 4311.3 | 1336375.2 | 34434.3 | 0
2021091415 | 3 | 0.86928 | 130392 | 0.2595 | 0 | 0.42963 | 5370.375 | 0.31379 | 25103.2 | 64000 | 5370.375 | 25103.2 | 35918.425 | 1484.125 | 1325923.025 | 35918.425 | 0
2021091416 | 3 | 0.88289 | 132433.5 | 0.28591 | 0 | 0.32175 | 4021.875 | 0.32591 | 26072.8 | 64000 | 4021.875 | 26072.8 | 38338.825 | 2420.4 | 1313050.45 | 38338.825 | 0
2021091417 | 3 | 0.89048 | 133572 | 0.24171 | 0 | 0.27881 | 3485.125 | 0.30083 | 24066.4 | 64000 | 3485.125 | 24066.4 | 42020.475 | 3681.65 | 1296496.225 | 42020.475 | 0
2021091418 | 3 | 0.88566 | 132849 | 0.20963 | 0 | 0.30711 | 3838.875 | 0.24526 | 19620.8 | 64000 | 3838.875 | 19620.8 | 45389.325 | 3368.85 | 1276573.15 | 45389.325 | 0
2021091419 | 3 | 0.85867 | 128800.5 | 0.27449 | 0 | 0.38368 | 4796 | 0.09368 | 7494.4 | 64000 | 4796 | 7494.4 | 52510.1 | 7120.775 | 1249529.3 | 52510.1 | 0
2021091420 | 3 | 0.82768 | 124152 | 0.43184 | 0 | 0.41117 | 5139.625 | 0.00596 | 476.8 | 64000 | 5139.625 | 476.8 | 54535.575 | 2025.475 | 1220459.975 | 54535.575 | 0
2021091421 | 3 | 0.80212 | 120318 | 0.54589 | 0 | 0.42069 | 5258.625 | 0 | 0 | 64000 | 5258.625 | 0 | 51059.375 | -3476.2 | 1194866.85 | 51059.375 | 0
2021091422 | 3 | 0.75276 | 112914 | 0.60232 | 0 | 0.40578 | 5072.25 | 0 | 0 | 64000 | 5072.25 | 0 | 43841.75 | -7217.625 | 1176491.35 | 43841.75 | 0
2021091423 | 3 | 0.6969 | 104535 | 0.62271 | 0 | 0.38697 | 4837.125 | 0 | 0 | 64000 | 4837.125 | 0 | 35697.875 | -8143.875 | 1166259.725 | 35697.875 | 0
2021091424 | 3 | 0.64242 | 96363 | 0.64932 | 0 | 0.37587 | 4698.375 | 0 | 0 | 64000 | 4698.375 | 0 | 27664.625 | -8033.25 | 1164061.35 | 27664.625 | 0
2021091501 | 4 | 0.59871 | 89806.5 | 0.63682 | 0 | 0.28837 | 3604.625 | 0 | 0 | 64000 | 3604.625 | 0 | 22201.875 | -5462.75 | 1167325.725 | 22201.875 | 0
2021091502 | 4 | 0.56582 | 84873 | 0.66445 | 0 | 0.2254 | 2817.5 | 0 | 0 | 64000 | 2817.5 | 0 | 18055.5 | -4146.375 | 1174736.475 | 18055.5 | 0
2021091503 | 4 | 0.54402 | 81603 | 0.65933 | 0 | 0.1669 | 2086.25 | 0 | 0 | 64000 | 2086.25 | 0 | 15516.75 | -2538.75 | 1184685.975 | 15516.75 | 0
2021091504 | 4 | 0.53013 | 79519.5 | 0.64786 | 0 | 0.14635 | 1829.375 | 0 | 0 | 64000 | 1829.375 | 0 | 13690.125 | -1826.625 | 1196462.1 | 13690.125 | 0
2021091505 | 4 | 0.52982 | 79473 | 0.60642 | 0 | 0.12175 | 1521.875 | 0 | 0 | 64000 | 1521.875 | 0 | 13951.125 | 261 | 1207977.225 | 13951.125 | 0
2021091506 | 4 | 0.54903 | 82354.5 | 0.58927 | 0 | 0.09087 | 1135.875 | 0 | 0 | 64000 | 1135.875 | 0 | 17218.625 | 3267.5 | 1216224.85 | 17218.625 | 0
2021091507 | 4 | 0.5901 | 88515 | 0.53536 | 0 | 0.10248 | 1281 | 0.01806 | 1444.8 | 64000 | 1281 | 1444.8 | 21789.2 | 4570.575 | 1219901.9 | 21789.2 | 0
2021091508 | 4 | 0.61784 | 92676 | 0.56683 | 0 | 0.0933 | 1166.25 | 0.1235 | 9880 | 64000 | 1166.25 | 9880 | 17629.75 | -4159.45 | 1227738.4 | 17629.75 | 0
2021091509 | 4 | 0.64191 | 96286.5 | 0.5041 | 0 | 0.10125 | 1265.625 | 0.22567 | 18053.6 | 64000 | 1265.625 | 18053.6 | 12967.275 | -4662.475 | 1240237.375 | 12967.275 | 0
2021091510 | 4 | 0.66765 | 100147.5 | 0.42075 | 0 | 0.08977 | 1122.125 | 0.32004 | 25603.2 | 64000 | 1122.125 | 25603.2 | 9422.175 | -3545.1 | 1256281.45 | 9422.175 | 0
2021091511 | 4 | 0.6979 | 104685 | 0.36237 | 0 | 0.06715 | 839.375 | 0.34354 | 27483.2 | 64000 | 839.375 | 27483.2 | 12362.425 | 2940.25 | 1269385.275 | 12362.425 | 0
2021091512 | 4 | 0.72818 | 109227 | 0.35001 | 0 | 0.04995 | 624.375 | 0.44336 | 35468.8 | 64000 | 624.375 | 35468.8 | 9133.825 | -3228.6 | 1285717.7 | 9133.825 | 0
2021091513 | 4 | 0.75897 | 113845.5 | 0.37547 | 0 | 0.0354 | 442.5 | 0.49816 | 39852.8 | 64000 | 442.5 | 39852.8 | 9550.2 | 416.375 | 1301633.75 | 9550.2 | 0
2021091514 | 4 | 0.7863 | 117945 | 0.4744 | 0 | 0.02397 | 299.625 | 0.52819 | 42255.2 | 64000 | 299.625 | 42255.2 | 11390.175 | 1839.975 | 1315709.825 | 11390.175 | 0
2021091515 | 4 | 0.80167 | 120250.5 | 0.47735 | 0 | 0.02219 | 277.375 | 0.55566 | 44452.8 | 64000 | 277.375 | 44452.8 | 11520.325 | 130.15 | 1329655.75 | 11520.325 | 0
2021091516 | 4 | 0.80983 | 121474.5 | 0.50966 | 0 | 0.01791 | 223.875 | 0.57955 | 46364 | 64000 | 223.875 | 46364 | 10886.625 | -633.7 | 1344235.375 | 10886.625 | 0
2021091517 | 4 | 0.81374 | 122061 | 0.42915 | 0 | 0.02086 | 260.75 | 0.53014 | 42411.2 | 64000 | 260.75 | 42411.2 | 15389.05 | 4502.425 | 1350000 | 15389.05 | 0
2021091518 | 4 | 0.80802 | 121203 | 0.36785 | 0 | 0.04753 | 594.125 | 0.3931 | 31448 | 64000 | 594.125 | 31448 | 25160.875 | 9771.825 | 1350000 | 25160.875 | 0
2021091519 | 4 | 0.78659 | 117988.5 | 0.27034 | 0 | 0.07108 | 888.5 | 0.12726 | 10180.8 | 64000 | 888.5 | 10180.8 | 42919.2 | 17758.325 | 1332547.05 | 42919.2 | 0
2021091520 | 4 | 0.764 | 114600 | 0.15617 | 0 | 0.07801 | 975.125 | 0.00596 | 476.8 | 64000 | 975.125 | 476.8 | 49148.075 | 6228.875 | 1308865.225 | 49148.075 | 0
2021091521 | 4 | 0.74101 | 111151.5 | 0.07764 | 0 | 0.08122 | 1015.25 | 0 | 0 | 64000 | 1015.25 | 0 | 46136.25 | -3011.825 | 1288195.225 | 46136.25 | 0
2021091522 | 4 | 0.70131 | 105196.5 | 0.04324 | 0 | 0.08149 | 1018.625 | 0 | 0 | 64000 | 1018.625 | 0 | 40177.875 | -5958.375 | 1273483.6 | 40177.875 | 0
2021091523 | 4 | 0.64901 | 97351.5 | 0.05155 | 0 | 0.07808 | 976 | 0 | 0 | 64000 | 976 | 0 | 32375.5 | -7802.375 | 1266574.35 | 32375.5 | 0
2021091524 | 4 | 0.59798 | 89697 | 0.0367 | 0 | 0.08027 | 1003.375 | 0 | 0 | 64000 | 1003.375 | 0 | 24693.625 | -7681.875 | 1267346.975 | 24693.625 | 0
2021091601 | 5 | 0.55875 | 83812.5 | 0.01773 | 0 | 0.08795 | 1099.375 | 0 | 0 | 64000 | 1099.375 | 0 | 18713.125 | -5980.5 | 1274100.1 | 18713.125 | 0
2021091602 | 5 | 0.53058 | 79587 | 0.04026 | 0 | 0.09297 | 1162.125 | 0 | 0 | 64000 | 1162.125 | 0 | 14424.875 | -4288.25 | 1285141.475 | 14424.875 | 0
2021091603 | 5 | 0.51196 | 76794 | 0.03096 | 0 | 0.08359 | 1044.875 | 0 | 0 | 64000 | 1044.875 | 0 | 11749.125 | -2675.75 | 1298858.6 | 11749.125 | 0
2021091604 | 5 | 0.50135 | 75202.5 | 0.03646 | 0 | 0.0775 | 968.75 | 0 | 0 | 64000 | 968.75 | 0 | 10233.75 | -1515.375 | 1314091.1 | 10233.75 | 0
2021091605 | 5 | 0.50306 | 75459 | 0.02857 | 0 | 0.08824 | 1103 | 0 | 0 | 64000 | 1103 | 0 | 10356 | 122.25 | 1329201.35 | 10356 | 0
2021091606 | 5 | 0.52262 | 78393 | 0.04261 | 0 | 0.09772 | 1221.5 | 0 | 0 | 64000 | 1221.5 | 0 | 13171.5 | 2815.5 | 1341496.1 | 13171.5 | 0
2021091607 | 5 | 0.55986 | 83979 | 0.04876 | 0 | 0.12307 | 1538.375 | 0.0066 | 528 | 64000 | 1538.375 | 528 | 17912.625 | 4741.125 | 1349049.725 | 17912.625 | 0
2021091608 | 5 | 0.58612 | 87918 | 0.05354 | 0 | 0.11916 | 1489.5 | 0.05771 | 4616.8 | 64000 | 1489.5 | 4616.8 | 17811.7 | -100.925 | 1350000 | 17811.7 | 0
2021091609 | 5 | 0.60621 | 90931.5 | 0.08184 | 0 | 0.13737 | 1717.125 | 0.14285 | 11428 | 64000 | 1717.125 | 11428 | 13786.375 | -4025.325 | 1350000 | 13786.375 | 0
2021091610 | 5 | 0.62818 | 94227 | 0.08044 | 0 | 0.11931 | 1491.375 | 0.24102 | 19281.6 | 64000 | 1491.375 | 19281.6 | 9454.025 | -4332.35 | 1350000 | 9454.025 | 0
2021091611 | 5 | 0.65468 | 98202 | 0.06955 | 0 | 0.1196 | 1495 | 0.35008 | 28006.4 | 64000 | 1495 | 28006.4 | 4700.6 | -4753.425 | 1350000 | 4700.6 | 0
2021091612 | 5 | 0.683 | 102450 | 0.05672 | 0 | 0.10357 | 1294.625 | 0.45892 | 36713.6 | 64000 | 1294.625 | 36713.6 | 441.775 | -4258.825 | 1350000 | 441.775 | 0
2021091613 | 5 | 0.71148 | 106722 | 0.04406 | 0 | 0.08248 | 1031 | 0.48904 | 39123.2 | 64000 | 1031 | 39123.2 | 2567.8 | 2126.025 | 1350000 | 2567.8 | 0
2021091614 | 5 | 0.73373 | 110059.5 | 0.04038 | 0 | 0.06053 | 756.625 | 0.48711 | 38968.8 | 64000 | 756.625 | 38968.8 | 6334.075 | 3766.275 | 1350000 | 6334.075 | 0
2021091615 | 5 | 0.74765 | 112147.5 | 0.04617 | 0 | 0.04584 | 573 | 0.49897 | 39917.6 | 64000 | 573 | 39917.6 | 7656.9 | 1322.825 | 1350000 | 7656.9 | 0
2021091616 | 5 | 0.75875 | 113812.5 | 0.04234 | 0 | 0.03969 | 496.125 | 0.49662 | 39729.6 | 64000 | 496.125 | 39729.6 | 9586.775 | 1929.875 | 1350000 | 9586.775 | 0
2021091617 | 5 | 0.76384 | 114576 | 0.04506 | 0 | 0.03995 | 499.375 | 0.48209 | 38567.2 | 64000 | 499.375 | 38567.2 | 11509.425 | 1922.65 | 1350000 | 11509.425 | 0
2021091618 | 5 | 0.76006 | 114009 | 0.08061 | 0 | 0.05643 | 705.375 | 0.40344 | 32275.2 | 64000 | 705.375 | 32275.2 | 17028.425 | 5519 | 1350000 | 17028.425 | 0
2021091619 | 5 | 0.74585 | 111877.5 | 0.14665 | 0 | 0.06577 | 822.125 | 0.15874 | 12699.2 | 64000 | 822.125 | 12699.2 | 34356.175 | 17327.75 | 1341110.075 | 34356.175 | 0
2021091620 | 5 | 0.73216 | 109824 | 0.22415 | 0 | 0.07374 | 921.75 | 0.00645 | 516 | 64000 | 921.75 | 516 | 44386.25 | 10030.075 | 1322190.075 | 44386.25 | 0
2021091621 | 5 | 0.71591 | 107386.5 | 0.3031 | 0 | 0.09392 | 1174 | 0 | 0 | 64000 | 1174 | 0 | 42212.5 | -2173.75 | 1305443.825 | 42212.5 | 0
2021091622 | 5 | 0.68011 | 102016.5 | 0.35699 | 0 | 0.13088 | 1636 | 0 | 0 | 64000 | 1636 | 0 | 36380.5 | -5832 | 1294529.575 | 36380.5 | 0
2021091623 | 5 | 0.6354 | 95310 | 0.31387 | 0 | 0.17687 | 2210.875 | 0 | 0 | 64000 | 2210.875 | 0 | 29099.125 | -7281.375 | 1290896.7 | 29099.125 | 0
2021091624 | 5 | 0.59145 | 88717.5 | 0.31907 | 0 | 0.21165 | 2645.625 | 0 | 0 | 64000 | 2645.625 | 0 | 22071.875 | -7027.25 | 1294291.075 | 22071.875 | 0
2021091701 | 6 | 0.55548 | 83322 | 0.31624 | 0 | 0.26223 | 3277.875 | 0 | 0 | 64000 | 3277.875 | 0 | 16044.125 | -6027.75 | 1303713.2 | 16044.125 | 0
2021091702 | 6 | 0.53092 | 79638 | 0.35167 | 0 | 0.28434 | 3554.25 | 0 | 0 | 64000 | 3554.25 | 0 | 12083.75 | -3960.375 | 1317095.7 | 12083.75 | 0
2021091703 | 6 | 0.51408 | 77112 | 0.33026 | 0 | 0.29698 | 3712.25 | 0 | 0 | 64000 | 3712.25 | 0 | 9399.75 | -2684 | 1333162.2 | 9399.75 | 0
2021091704 | 6 | 0.50628 | 75942 | 0.29793 | 0 | 0.26989 | 3373.625 | 0 | 0 | 64000 | 3373.625 | 0 | 8568.375 | -831.375 | 1350000 | 8568.375 | 0
2021091705 | 6 | 0.509 | 76350 | 0.23236 | 0 | 0.22984 | 2873 | 0 | 0 | 64000 | 2873 | 0 | 9477 | 908.625 | 1350000 | 9477 | 0
2021091706 | 6 | 0.5304 | 79560 | 0.1619 | 0 | 0.20736 | 2592 | 0 | 0 | 64000 | 2592 | 0 | 12968 | 3491 | 1350000 | 12968 | 0
2021091707 | 6 | 0.57356 | 86034 | 0.13797 | 0 | 0.20953 | 2619.125 | 0.02349 | 1879.2 | 64000 | 2619.125 | 1879.2 | 17535.675 | 4567.675 | 1350000 | 17535.675 | 0
2021091708 | 6 | 0.60477 | 90715.5 | 0.17123 | 0 | 0.20473 | 2559.125 | 0.20835 | 16668 | 64000 | 2559.125 | 16668 | 7488.375 | -10047.3 | 1350000 | 7488.375 | 0
2021091709 | 6 | 0.6274 | 94110 | 0.16074 | 0 | 0.19695 | 2461.875 | 0.40867 | 32693.6 | 64000 | 2461.875 | 27648.125 | 0 | -7488.375 | 1350000 | 0 | 0
2021091710 | 6 | 0.65156 | 97734 | 0.14593 | 0 | 0.19344 | 2418 | 0.48187 | 38549.6 | 64000 | 2418 | 31316 | 0 | 0 | 1350000 | 0 | 0
2021091711 | 6 | 0.67914 | 101871 | 0.17026 | 0 | 0.18887 | 2360.875 | 0.51132 | 40905.6 | 64000 | 2360.875 | 35510.125 | 0 | 0 | 1350000 | 0 | 0
2021091712 | 6 | 0.70651 | 105976.5 | 0.13243 | 0 | 0.18536 | 2317 | 0.52644 | 42115.2 | 64000 | 2317 | 39659.5 | 0 | 0 | 1350000 | 0 | 0
2021091713 | 6 | 0.73257 | 109885.5 | 0.08677 | 0 | 0.20819 | 2602.375 | 0.50406 | 40324.8 | 64000 | 2602.375 | 40324.8 | 2958.325 | 2958.325 | 1350000 | 2958.325 | 0
2021091714 | 6 | 0.75812 | 113718 | 0.04549 | 0 | 0.22812 | 2851.5 | 0.49275 | 39420 | 64000 | 2851.5 | 39420 | 7446.5 | 4488.175 | 1350000 | 7446.5 | 0
2021091715 | 6 | 0.77642 | 116463 | 0.03282 | 0 | 0.21723 | 2715.375 | 0.51077 | 40861.6 | 64000 | 2715.375 | 40861.6 | 8886.025 | 1439.525 | 1350000 | 8886.025 | 0
2021091716 | 6 | 0.78896 | 118344 | 0.0326 | 0 | 0.21147 | 2643.375 | 0.50417 | 40333.6 | 64000 | 2643.375 | 40333.6 | 11367.025 | 2481 | 1350000 | 11367.025 | 0
2021091717 | 6 | 0.79805 | 119707.5 | 0.04244 | 0 | 0.21583 | 2697.875 | 0.49184 | 39347.2 | 64000 | 2697.875 | 39347.2 | 13662.425 | 2295.4 | 1350000 | 13662.425 | 0
2021091718 | 6 | 0.79466 | 119199 | 0.06447 | 0 | 0.22518 | 2814.75 | 0.43008 | 34406.4 | 64000 | 2814.75 | 34406.4 | 17977.85 | 4315.425 | 1350000 | 17977.85 | 0
2021091719 | 6 | 0.77177 | 115765.5 | 0.09455 | 0 | 0.25046 | 3130.75 | 0.15861 | 12688.8 | 64000 | 3130.75 | 12688.8 | 35945.95 | 17968.1 | 1339520.3 | 35945.95 | 0
2021091720 | 6 | 0.74663 | 111994.5 | 0.15515 | 0 | 0.24837 | 3104.625 | 0.00552 | 441.6 | 64000 | 3104.625 | 441.6 | 44448.275 | 8502.325 | 1320538.275 | 44448.275 | 0
2021091721 | 6 | 0.72473 | 108709.5 | 0.23872 | 0 | 0.23312 | 2914 | 0 | 0 | 64000 | 2914 | 0 | 41795.5 | -2652.775 | 1304209.025 | 41795.5 | 0
2021091722 | 6 | 0.68743 | 103114.5 | 0.27768 | 0 | 0.23731 | 2966.375 | 0 | 0 | 64000 | 2966.375 | 0 | 36148.125 | -5647.375 | 1293527.15 | 36148.125 | 0
2021091723 | 6 | 0.64627 | 96940.5 | 0.2482 | 0 | 0.24341 | 3042.625 | 0 | 0 | 64000 | 3042.625 | 0 | 29897.875 | -6250.25 | 1289095.525 | 29897.875 | 0
2021091724 | 6 | 0.60017 | 90025.5 | 0.23454 | 0 | 0.24548 | 3068.5 | 0 | 0 | 64000 | 3068.5 | 0 | 22957 | -6940.875 | 1291604.775 | 22957 | 0
2021091801 | 7 | 0.56128 | 84192 | 0.19302 | 0 | 0.24448 | 3056 | 0 | 0 | 64000 | 3056 | 0 | 17136 | -5821 | 1299935.025 | 17136 | 0
2021091802 | 7 | 0.5307 | 79605 | 0.15921 | 0 | 0.24845 | 3105.625 | 0 | 0 | 64000 | 3105.625 | 0 | 12499.375 | -4636.625 | 1312901.9 | 12499.375 | 0
2021091803 | 7 | 0.50956 | 76434 | 0.13576 | 0 | 0.28077 | 3509.625 | 0 | 0 | 64000 | 3509.625 | 0 | 8924.375 | -3575 | 1329443.775 | 8924.375 | 0
2021091804 | 7 | 0.49611 | 74416.5 | 0.15752 | 0 | 0.28269 | 3533.625 | 0 | 0 | 64000 | 3533.625 | 0 | 6882.875 | -2041.5 | 1348027.15 | 6882.875 | 0
2021091805 | 7 | 0.48924 | 73386 | 0.21431 | 0 | 0.27711 | 3463.875 | 0 | 0 | 64000 | 3463.875 | 0 | 5922.125 | -960.75 | 1350000 | 5922.125 | 0
2021091806 | 7 | 0.49356 | 74034 | 0.24286 | 0 | 0.3016 | 3770 | 0 | 0 | 64000 | 3770 | 0 | 6264 | 341.875 | 1350000 | 6264 | 0
2021091807 | 7 | 0.50431 | 75646.5 | 0.28705 | 0 | 0.35992 | 4499 | 0.01523 | 1218.4 | 64000 | 4499 | 1218.4 | 5929.1 | -334.9 | 1350000 | 5929.1 | 0
2021091808 | 7 | 0.51909 | 77863.5 | 0.26985 | 0 | 0.41107 | 5138.375 | 0.14829 | 11863.2 | 64000 | 5138.375 | 8725.125 | 0 | -5929.1 | 1350000 | 0 | 0
2021091809 | 7 | 0.55016 | 82524 | 0.18998 | 0 | 0.47511 | 5938.875 | 0.28729 | 22983.2 | 64000 | 5938.875 | 12585.125 | 0 | 0 | 1350000 | 0 | 0
2021091810 | 7 | 0.58778 | 88167 | 0.11176 | 0 | 0.46784 | 5848 | 0.29676 | 23740.8 | 64000 | 5848 | 18319 | 0 | 0 | 1350000 | 0 | 0
2021091811 | 7 | 0.62596 | 93894 | 0.07861 | 0 | 0.44271 | 5533.875 | 0.28828 | 23062.4 | 64000 | 5533.875 | 23062.4 | 1297.725 | 1297.725 | 1350000 | 1297.725 | 0
2021091812 | 7 | 0.66687 | 100030.5 | 0.05463 | 0 | 0.40914 | 5114.25 | 0.32818 | 26254.4 | 64000 | 5114.25 | 26254.4 | 4661.85 | 3364.125 | 1350000 | 4661.85 | 0
2021091813 | 7 | 0.70278 | 105417 | 0.01667 | 0 | 0.39169 | 4896.125 | 0.29196 | 23356.8 | 64000 | 4896.125 | 23356.8 | 13164.075 | 8502.225 | 1350000 | 13164.075 | 0
2021091814 | 7 | 0.73297 | 109945.5 | 0.04068 | 0 | 0.37464 | 4683 | 0.3159 | 25272 | 64000 | 4683 | 25272 | 15990.5 | 2826.425 | 1350000 | 15990.5 | 0
2021091815 | 7 | 0.75731 | 113596.5 | 0.08305 | 0 | 0.37466 | 4683.25 | 0.26161 | 20928.8 | 64000 | 4683.25 | 20928.8 | 23984.45 | 7993.95 | 1350000 | 23984.45 | 0
2021091816 | 7 | 0.77704 | 116556 | 0.10709 | 0 | 0.39538 | 4942.25 | 0.2619 | 20952 | 64000 | 4942.25 | 20952 | 26661.75 | 2677.3 | 1348804.5 | 26661.75 | 0
2021091817 | 7 | 0.78733 | 118099.5 | 0.14176 | 0 | 0.35985 | 4498.125 | 0.15392 | 12313.6 | 64000 | 4498.125 | 12313.6 | 37287.775 | 10626.025 | 1336982.975 | 37287.775 | 0
2021091818 | 7 | 0.7849 | 117735 | 0.17285 | 0 | 0.27526 | 3440.75 | 0.08197 | 6557.6 | 64000 | 3440.75 | 6557.6 | 43736.65 | 6448.875 | 1318712.575 | 43736.65 | 0
2021091819 | 7 | 0.76054 | 114081 | 0.21322 | 0 | 0.29321 | 3665.125 | 0.02253 | 1802.4 | 64000 | 3665.125 | 1802.4 | 44613.475 | 876.825 | 1299565.35 | 44613.475 | 0
2021091820 | 7 | 0.72929 | 109393.5 | 0.29716 | 0 | 0.29481 | 3685.125 | 0.00043 | 34.4 | 64000 | 3685.125 | 34.4 | 41673.975 | -2939.5 | 1283357.625 | 41673.975 | 0
2021091821 | 7 | 0.70455 | 105682.5 | 0.35758 | 0 | 0.26529 | 3316.125 | 0 | 0 | 64000 | 3316.125 | 0 | 38366.375 | -3307.6 | 1270457.5 | 38366.375 | 0
2021091822 | 7 | 0.66669 | 100003.5 | 0.37815 | 0 | 0.27439 | 3429.875 | 0 | 0 | 64000 | 3429.875 | 0 | 32573.625 | -5792.75 | 1263350.125 | 32573.625 | 0
2021091823 | 7 | 0.62414 | 93621 | 0.3762 | 0 | 0.25701 | 3212.625 | 0 | 0 | 64000 | 3212.625 | 0 | 26408.375 | -6165.25 | 1262408 | 26408.375 | 0
2021091824 | 7 | 0.58366 | 87549 | 0.31918 | 0 | 0.24594 | 3074.25 | 0 | 0 | 64000 | 3074.25 | 0 | 20474.75 | -5933.625 | 1267399.5 | 20474.75 | 0
2021091901 | 1 | 0.54603 | 81904.5 | 0.22085 | 0 | 0.21309 | 2663.625 | 0 | 0 | 64000 | 2663.625 | 0 | 15240.875 | -5233.875 | 1277624.875 | 15240.875 | 0
2021091902 | 1 | 0.51659 | 77488.5 | 0.17029 | 0 | 0.19813 | 2476.625 | 0 | 0 | 64000 | 2476.625 | 0 | 11011.875 | -4229 | 1292079.25 | 11011.875 | 0
2021091903 | 1 | 0.49448 | 74172 | 0.15955 | 0 | 0.21165 | 2645.625 | 0 | 0 | 64000 | 2645.625 | 0 | 7526.375 | -3485.5 | 1310019.125 | 7526.375 | 0
2021091904 | 1 | 0.47834 | 71751 | 0.15569 | 0 | 0.22648 | 2831 | 0 | 0 | 64000 | 2831 | 0 | 4920 | -2606.375 | 1330565.375 | 4920 | 0
2021091905 | 1 | 0.47006 | 70509 | 0.12861 | 0 | 0.2579 | 3223.75 | 0 | 0 | 64000 | 3223.75 | 0 | 3285.25 | -1634.75 | 1350000 | 3285.25 | 0
2021091906 | 1 | 0.46686 | 70029 | 0.10611 | 0 | 0.3183 | 3978.75 | 0 | 0 | 64000 | 3978.75 | 0 | 2050.25 | -1235 | 1350000 | 2050.25 | 0
2021091907 | 1 | 0.47084 | 70626 | 0.08469 | 0 | 0.41629 | 5203.625 | 0.00834 | 667.2 | 64000 | 5203.625 | 667.2 | 755.175 | -1295.075 | 1350000 | 755.175 | 0
2021091908 | 1 | 0.47749 | 71623.5 | 0.09279 | 0 | 0.46351 | 5793.875 | 0.0687 | 5496 | 64000 | 5793.875 | 1829.625 | 0 | -755.175 | 1350000 | 0 | 0
2021091909 | 1 | 0.50327 | 75490.5 | 0.07447 | 0 | 0.43944 | 5493 | 0.17836 | 14268.8 | 64000 | 5493 | 5997.5 | 0 | 0 | 1350000 | 0 | 0
2021091910 | 1 | 0.54012 | 81018 | 0.06634 | 0 | 0.4208 | 5260 | 0.26913 | 21530.4 | 64000 | 5260 | 11758 | 0 | 0 | 1350000 | 0 | 0
2021091911 | 1 | 0.57619 | 86428.5 | 0.09495 | 0 | 0.38026 | 4753.25 | 0.24625 | 19700 | 64000 | 4753.25 | 17675.25 | 0 | 0 | 1350000 | 0 | 0
2021091912 | 1 | 0.61497 | 92245.5 | 0.11476 | 0 | 0.35637 | 4454.625 | 0.28088 | 22470.4 | 64000 | 4454.625 | 22470.4 | 1320.475 | 1320.475 | 1350000 | 1320.475 | 0
2021091913 | 1 | 0.65162 | 97743 | 0.07189 | 0 | 0.33762 | 4220.25 | 0.32424 | 25939.2 | 64000 | 4220.25 | 25939.2 | 3583.55 | 2263.075 | 1350000 | 3583.55 | 0
2021091914 | 1 | 0.68432 | 102648 | 0.03827 | 0 | 0.29014 | 3626.75 | 0.4051 | 32408 | 64000 | 3626.75 | 32408 | 2613.25 | -970.3 | 1350000 | 2613.25 | 0
2021091915 | 1 | 0.71014 | 106521 | 0.01481 | 0 | 0.20187 | 2523.375 | 0.47014 | 37611.2 | 64000 | 2523.375 | 37611.2 | 2386.425 | -226.825 | 1350000 | 2386.425 | 0
2021091916 | 1 | 0.72972 | 109458 | 0.00966 | 0 | 0.15309 | 1913.625 | 0.50211 | 40168.8 | 64000 | 1913.625 | 40168.8 | 3375.575 | 989.15 | 1350000 | 3375.575 | 0
2021091917 | 1 | 0.74578 | 111867 | 0.00517 | 0 | 0.07506 | 938.25 | 0.45444 | 36355.2 | 64000 | 938.25 | 36355.2 | 10573.55 | 7197.975 | 1350000 | 10573.55 | 0
2021091918 | 1 | 0.7498 | 112470 | 0.00516 | 0 | 0.07384 | 923 | 0.33006 | 26404.8 | 64000 | 923 | 26404.8 | 21142.2 | 10568.65 | 1350000 | 21142.2 | 0
2021091919 | 1 | 0.72997 | 109495.5 | 0.03276 | 0 | 0.0919 | 1148.75 | 0.11412 | 9129.6 | 64000 | 1148.75 | 9129.6 | 35217.15 | 14074.95 | 1340249.1 | 35217.15 | 0
2021091920 | 1 | 0.7083 | 106245 | 0.09028 | 0 | 0.099 | 1237.5 | 0.00378 | 302.4 | 64000 | 1237.5 | 302.4 | 40705.1 | 5487.95 | 1325010.25 | 40705.1 | 0
2021091921 | 1 | 0.68802 | 103203 | 0.14545 | 0 | 0.13846 | 1730.75 | 0 | 0 | 64000 | 1730.75 | 0 | 37472.25 | -3232.85 | 1313004.25 | 37472.25 | 0
2021091922 | 1 | 0.64799 | 97198.5 | 0.19043 | 0 | 0.15617 | 1952.125 | 0 | 0 | 64000 | 1952.125 | 0 | 31246.375 | -6225.875 | 1307224.125 | 31246.375 | 0
2021091923 | 1 | 0.60378 | 90567 | 0.21299 | 0 | 0.18376 | 2297 | 0 | 0 | 64000 | 2297 | 0 | 24270 | -6976.375 | 1308420.375 | 24270 | 0
2021091924 | 1 | 0.56163 | 84244.5 | 0.27924 | 0 | 0.17419 | 2177.375 | 0 | 0 | 64000 | 2177.375 | 0 | 18067.125 | -6202.875 | 1315819.5 | 18067.125 | 0
2021092001 | 2 | 0.52755 | 79132.5 | 0.36776 | 0 | 0.14656 | 1832 | 0 | 0 | 64000 | 1832 | 0 | 13300.5 | -4766.625 | 1327985.25 | 13300.5 | 0
2021092002 | 2 | 0.5035 | 75525 | 0.46671 | 0 | 0.13618 | 1702.25 | 0 | 0 | 64000 | 1702.25 | 0 | 9822.75 | -3477.75 | 1343628.75 | 9822.75 | 0
2021092003 | 2 | 0.48665 | 72997.5 | 0.52995 | 0 | 0.15116 | 1889.5 | 0 | 0 | 64000 | 1889.5 | 0 | 7108 | -2714.75 | 1350000 | 7108 | 0
2021092004 | 2 | 0.47976 | 71964 | 0.58146 | 0 | 0.10361 | 1295.125 | 0 | 0 | 64000 | 1295.125 | 0 | 6668.875 | -439.125 | 1350000 | 6668.875 | 0
2021092005 | 2 | 0.4837 | 72555 | 0.6318 | 0 | 0.11798 | 1474.75 | 0 | 0 | 64000 | 1474.75 | 0 | 7080.25 | 411.375 | 1350000 | 7080.25 | 0
2021092006 | 2 | 0.50807 | 76210.5 | 0.64517 | 0 | 0.16471 | 2058.875 | 0 | 0 | 64000 | 2058.875 | 0 | 10151.625 | 3071.375 | 1350000 | 10151.625 | 0
2021092007 | 2 | 0.55 | 82500 | 0.65248 | 0 | 0.25973 | 3246.625 | 0.02054 | 1643.2 | 64000 | 3246.625 | 1643.2 | 13610.175 | 3458.55 | 1350000 | 13610.175 | 0
2021092008 | 2 | 0.58066 | 87099 | 0.63666 | 0 | 0.35095 | 4386.875 | 0.19382 | 15505.6 | 64000 | 4386.875 | 15505.6 | 3206.525 | -10403.65 | 1350000 | 3206.525 | 0
2021092009 | 2 | 0.59956 | 89934 | 0.56671 | 0 | 0.40339 | 5042.375 | 0.37483 | 29986.4 | 64000 | 5042.375 | 20891.625 | 0 | -3206.525 | 1350000 | 0 | 0
2021092010 | 2 | 0.61964 | 92946 | 0.47417 | 0 | 0.40382 | 5047.75 | 0.45467 | 36373.6 | 64000 | 5047.75 | 23898.25 | 0 | 0 | 1350000 | 0 | 0
2021092011 | 2 | 0.64204 | 96306 | 0.45991 | 0 | 0.3895 | 4868.75 | 0.4642 | 37136 | 64000 | 4868.75 | 27437.25 | 0 | 0 | 1350000 | 0 | 0
2021092012 | 2 | 0.66657 | 99985.5 | 0.44963 | 0 | 0.38007 | 4750.875 | 0.48854 | 39083.2 | 64000 | 4750.875 | 31234.625 | 0 | 0 | 1350000 | 0 | 0
2021092013 | 2 | 0.69104 | 103656 | 0.41533 | 0 | 0.37501 | 4687.625 | 0.50332 | 40265.6 | 64000 | 4687.625 | 34968.375 | 0 | 0 | 1350000 | 0 | 0
2021092014 | 2 | 0.71036 | 106554 | 0.40845 | 0 | 0.33153 | 4144.125 | 0.50284 | 40227.2 | 64000 | 4144.125 | 38409.875 | 0 | 0 | 1350000 | 0 | 0
2021092015 | 2 | 0.72309 | 108463.5 | 0.44664 | 0 | 0.30068 | 3758.5 | 0.49474 | 39579.2 | 64000 | 3758.5 | 39579.2 | 1125.8 | 1125.8 | 1350000 | 1125.8 | 0
2021092016 | 2 | 0.73332 | 109998 | 0.44079 | 0 | 0.29267 | 3658.375 | 0.45985 | 36788 | 64000 | 3658.375 | 36788 | 5551.625 | 4425.825 | 1350000 | 5551.625 | 0
2021092017 | 2 | 0.74157 | 111235.5 | 0.4436 | 0 | 0.24118 | 3014.75 | 0.39434 | 31547.2 | 64000 | 3014.75 | 31547.2 | 12673.55 | 7121.925 | 1350000 | 12673.55 | 0
2021092018 | 2 | 0.74268 | 111402 | 0.53879 | 0 | 0.21646 | 2705.75 | 0.25405 | 20324 | 64000 | 2705.75 | 20324 | 24372.25 | 11698.7 | 1350000 | 24372.25 | 0
2021092019 | 2 | 0.72626 | 108939 | 0.62152 | 0 | 0.26542 | 3317.75 | 0.08918 | 7134.4 | 64000 | 3317.75 | 7134.4 | 34486.85 | 10114.6 | 1340979.4 | 34486.85 | 0
2021092020 | 2 | 0.71513 | 107269.5 | 0.70684 | 0 | 0.29366 | 3670.75 | 0.00185 | 148 | 64000 | 3670.75 | 148 | 39450.75 | 4963.9 | 1326994.9 | 39450.75 | 0
2021092021 | 2 | 0.69903 | 104854.5 | 0.81196 | 0 | 0.32726 | 4090.75 | 0 | 0 | 64000 | 4090.75 | 0 | 36763.75 | -2687 | 1315697.4 | 36763.75 | 0
2021092022 | 2 | 0.66074 | 99111 | 0.86687 | 0 | 0.30912 | 3864 | 0 | 0 | 64000 | 3864 | 0 | 31247 | -5516.75 | 1309916.65 | 31247 | 0
2021092023 | 2 | 0.61629 | 92443.5 | 0.89695 | 0 | 0.28302 | 3537.75 | 0 | 0 | 64000 | 3537.75 | 0 | 24905.75 | -6341.25 | 1310477.15 | 24905.75 | 0
2021092024 | 2 | 0.57202 | 85803 | 0.90635 | 0 | 0.27523 | 3440.375 | 0 | 0 | 64000 | 3440.375 | 0 | 18362.625 | -6543.125 | 1317580.775 | 18362.625 | 0
2021092101 | 3 | 0.53609 | 80413.5 | 0.914 | 0 | 0.26773 | 3346.625 | 0 | 0 | 64000 | 3346.625 | 0 | 13066.875 | -5295.75 | 1329980.15 | 13066.875 | 0
2021092102 | 3 | 0.51057 | 76585.5 | 0.90562 | 0 | 0.31492 | 3936.5 | 0 | 0 | 64000 | 3936.5 | 0 | 8649 | -4417.875 | 1346797.4 | 8649 | 0
2021092103 | 3 | 0.49356 | 74034 | 0.87394 | 0 | 0.33193 | 4149.125 | 0 | 0 | 64000 | 4149.125 | 0 | 5884.875 | -2764.125 | 1350000 | 5884.875 | 0
2021092104 | 3 | 0.4836 | 72540 | 0.73774 | 0 | 0.30442 | 3805.25 | 0 | 0 | 64000 | 3805.25 | 0 | 4734.75 | -1150.125 | 1350000 | 4734.75 | 0
2021092105 | 3 | 0.48586 | 72879 | 0.58489 | 0 | 0.27663 | 3457.875 | 0 | 0 | 64000 | 3457.875 | 0 | 5421.125 | 686.375 | 1350000 | 5421.125 | 0
2021092106 | 3 | 0.50776 | 76164 | 0.53761 | 0 | 0.28811 | 3601.375 | 0 | 0 | 64000 | 3601.375 | 0 | 8562.625 | 3141.5 | 1350000 | 8562.625 | 0
2021092107 | 3 | 0.54924 | 82386 | 0.57302 | 0 | 0.3931 | 4913.75 | 0.01551 | 1240.8 | 64000 | 4913.75 | 1240.8 | 12231.45 | 3668.825 | 1350000 | 12231.45 | 0
2021092108 | 3 | 0.5786 | 86790 | 0.56256 | 0 | 0.49345 | 6168.125 | 0.14778 | 11822.4 | 64000 | 6168.125 | 11822.4 | 4799.475 | -7431.975 | 1350000 | 4799.475 | 0
2021092109 | 3 | 0.59544 | 89316 | 0.5543 | 0 | 0.53823 | 6727.875 | 0.22774 | 18219.2 | 64000 | 6727.875 | 18219.2 | 368.925 | -4430.55 | 1350000 | 368.925 | 0
2021092110 | 3 | 0.60855 | 91282.5 | 0.62164 | 0 | 0.55183 | 6897.875 | 0.28771 | 23016.8 | 64000 | 6897.875 | 20384.625 | 0 | -368.925 | 1350000 | 0 | 0
2021092111 | 3 | 0.62523 | 93784.5 | 0.6187 | 0 | 0.55049 | 6881.125 | 0.294 | 23520 | 64000 | 6881.125 | 22903.375 | 0 | 0 | 1350000 | 0 | 0
2021092112 | 3 | 0.64444 | 96666 | 0.57015 | 0 | 0.54624 | 6828 | 0.32531 | 26024.8 | 64000 | 6828 | 25838 | 0 | 0 | 1350000 | 0 | 0
2021092113 | 3 | 0.65855 | 98782.5 | 0.57002 | 0 | 0.48586 | 6073.25 | 0.35455 | 28364 | 64000 | 6073.25 | 28364 | 345.25 | 345.25 | 1350000 | 345.25 | 0
2021092114 | 3 | 0.6723 | 100845 | 0.52833 | 0 | 0.38771 | 4846.375 | 0.38369 | 30695.2 | 64000 | 4846.375 | 30695.2 | 1303.425 | 958.175 | 1350000 | 1303.425 | 0
2021092115 | 3 | 0.68033 | 102049.5 | 0.48186 | 0 | 0.32644 | 4080.5 | 0.43464 | 34771.2 | 64000 | 4080.5 | 33969 | 0 | -1303.425 | 1350000 | 0 | 0
2021092116 | 3 | 0.68463 | 102694.5 | 0.45561 | 0 | 0.32613 | 4076.625 | 0.41428 | 33142.4 | 64000 | 4076.625 | 33142.4 | 1475.475 | 1475.475 | 1350000 | 1475.475 | 0
2021092117 | 3 | 0.68779 | 103168.5 | 0.46858 | 0 | 0.28719 | 3589.875 | 0.41573 | 33258.4 | 64000 | 3589.875 | 33258.4 | 2320.225 | 844.75 | 1350000 | 2320.225 | 0
2021092118 | 3 | 0.68637 | 102955.5 | 0.50332 | 0 | 0.27879 | 3484.875 | 0.33161 | 26528.8 | 64000 | 3484.875 | 26528.8 | 8941.825 | 6621.6 | 1350000 | 8941.825 | 0
2021092119 | 3 | 0.67852 | 101778 | 0.54501 | 0 | 0.3271 | 4088.75 | 0.10255 | 8204 | 64000 | 4088.75 | 8204 | 25485.25 | 16543.425 | 1349981 | 25485.25 | 0
2021092120 | 3 | 0.67975 | 101962.5 | 0.60638 | 0 | 0.33109 | 4138.625 | 0.00139 | 111.2 | 64000 | 4138.625 | 111.2 | 33712.675 | 8227.425 | 1341734.575 | 33712.675 | 0
2021092121 | 3 | 0.66949 | 100423.5 | 0.68933 | 0 | 0.30768 | 3846 | 0 | 0 | 64000 | 3846 | 0 | 32577.5 | -1135.175 | 1334623.325 | 32577.5 | 0
2021092122 | 3 | 0.63812 | 95718 | 0.83667 | 0 | 0.28066 | 3508.25 | 0 | 0 | 64000 | 3508.25 | 0 | 28209.75 | -4367.75 | 1331879.825 | 28209.75 | 0
2021092123 | 3 | 0.59861 | 89791.5 | 0.86125 | 0 | 0.27322 | 3415.25 | 0 | 0 | 64000 | 3415.25 | 0 | 22376.25 | -5833.5 | 1334969.825 | 22376.25 | 0
2021092124 | 3 | 0.55963 | 83944.5 | 0.89769 | 0 | 0.29642 | 3705.25 | 0 | 0 | 64000 | 3705.25 | 0 | 16239.25 | -6137 | 1344196.825 | 16239.25 | 0
2021092201 | 4 | 0.52837 | 79255.5 | 0.91488 | 0 | 0.34557 | 4319.625 | 0 | 0 | 64000 | 4319.625 | 0 | 10935.875 | -5303.375 | 1350000 | 10935.875 | 0
2021092202 | 4 | 0.50741 | 76111.5 | 0.87945 | 0 | 0.38155 | 4769.375 | 0 | 0 | 64000 | 4769.375 | 0 | 7342.125 | -3593.75 | 1350000 | 7342.125 | 0
2021092203 | 4 | 0.4948 | 74220 | 0.82908 | 0 | 0.408 | 5100 | 0 | 0 | 64000 | 5100 | 0 | 5120 | -2222.125 | 1350000 | 5120 | 0
2021092204 | 4 | 0.48961 | 73441.5 | 0.84603 | 0 | 0.40913 | 5114.125 | 0 | 0 | 64000 | 5114.125 | 0 | 4327.375 | -792.625 | 1350000 | 4327.375 | 0
2021092205 | 4 | 0.49317 | 73975.5 | 0.81549 | 0 | 0.43577 | 5447.125 | 0 | 0 | 64000 | 5447.125 | 0 | 4528.375 | 201 | 1350000 | 4528.375 | 0
2021092206 | 4 | 0.51769 | 77653.5 | 0.87722 | 0 | 0.45275 | 5659.375 | 0 | 0 | 64000 | 5659.375 | 0 | 7994.125 | 3465.75 | 1350000 | 7994.125 | 0
2021092207 | 4 | 0.56238 | 84357 | 0.90466 | 0 | 0.4766 | 5957.5 | 0.01063 | 850.4 | 64000 | 5957.5 | 850.4 | 13549.1 | 5554.975 | 1350000 | 13549.1 | 0
2021092208 | 4 | 0.59511 | 89266.5 | 0.93494 | 0 | 0.50591 | 6323.875 | 0.13254 | 10603.2 | 64000 | 6323.875 | 10603.2 | 8339.425 | -5209.675 | 1350000 | 8339.425 | 0
2021092209 | 4 | 0.61409 | 92113.5 | 0.92072 | 0 | 0.50677 | 6334.625 | 0.28589 | 22871.2 | 64000 | 6334.625 | 21778.875 | 0 | -8339.425 | 1350000 | 0 | 0
2021092210 | 4 | 0.63151 | 94726.5 | 0.92607 | 0 | 0.51193 | 6399.125 | 0.35642 | 28513.6 | 64000 | 6399.125 | 24327.375 | 0 | 0 | 1350000 | 0 | 0
2021092211 | 4 | 0.65016 | 97524 | 0.92861 | 0 | 0.46341 | 5792.625 | 0.38661 | 30928.8 | 64000 | 5792.625 | 27731.375 | 0 | 0 | 1350000 | 0 | 0
2021092212 | 4 | 0.66449 | 99673.5 | 0.91854 | 0 | 0.41902 | 5237.75 | 0.42012 | 33609.6 | 64000 | 5237.75 | 30435.75 | 0 | 0 | 1350000 | 0 | 0
2021092213 | 4 | 0.67456 | 101184 | 0.92764 | 0 | 0.39672 | 4959 | 0.43138 | 34510.4 | 64000 | 4959 | 32225 | 0 | 0 | 1350000 | 0 | 0
2021092214 | 4 | 0.68531 | 102796.5 | 0.93085 | 0 | 0.39189 | 4898.625 | 0.47397 | 37917.6 | 64000 | 4898.625 | 33897.875 | 0 | 0 | 1350000 | 0 | 0
2021092215 | 4 | 0.69152 | 103728 | 0.93829 | 0 | 0.41184 | 5148 | 0.46241 | 36992.8 | 64000 | 5148 | 34580 | 0 | 0 | 1350000 | 0 | 0
2021092216 | 4 | 0.69149 | 103723.5 | 0.96128 | 0 | 0.40983 | 5122.875 | 0.38837 | 31069.6 | 64000 | 5122.875 | 31069.6 | 3531.025 | 3531.025 | 1350000 | 3531.025 | 0
2021092217 | 4 | 0.68794 | 103191 | 0.98367 | 0 | 0.36288 | 4536 | 0.28797 | 23037.6 | 64000 | 4536 | 23037.6 | 11617.4 | 8086.375 | 1350000 | 11617.4 | 0
2021092218 | 4 | 0.68294 | 102441 | 0.9816 | 0 | 0.30696 | 3837 | 0.2238 | 17904 | 64000 | 3837 | 17904 | 16700 | 5082.6 | 1350000 | 16700 | 0
2021092219 | 4 | 0.6743 | 101145 | 0.97344 | 0 | 0.27438 | 3429.75 | 0.07701 | 6160.8 | 64000 | 3429.75 | 6160.8 | 27554.45 | 10854.45 | 1347911.8 | 27554.45 | 0
2021092220 | 4 | 0.67206 | 100809 | 0.96638 | 0 | 0.30638 | 3829.75 | 0.00039 | 31.2 | 64000 | 3829.75 | 31.2 | 32948.05 | 5393.6 | 1340430 | 32948.05 | 0
2021092221 | 4 | 0.65883 | 98824.5 | 0.9339 | 0 | 0.33932 | 4241.5 | 0 | 0 | 64000 | 4241.5 | 0 | 30583 | -2365.05 | 1335313.25 | 30583 | 0
2021092222 | 4 | 0.62794 | 94191 | 0.88511 | 0 | 0.33393 | 4174.125 | 0 | 0 | 64000 | 4174.125 | 0 | 26016.875 | -4566.125 | 1334762.625 | 26016.875 | 0
2021092223 | 4 | 0.59239 | 88858.5 | 0.87877 | 0 | 0.29685 | 3710.625 | 0 | 0 | 64000 | 3710.625 | 0 | 21147.875 | -4869 | 1339081 | 21147.875 | 0
2021092224 | 4 | 0.55542 | 83313 | 0.85938 | 0 | 0.29252 | 3656.5 | 0 | 0 | 64000 | 3656.5 | 0 | 15656.5 | -5491.375 | 1348890.75 | 15656.5 | 0
2021092301 | 5 | 0.52508 | 78762 | 0.81643 | 0 | 0.29114 | 3639.25 | 0 | 0 | 64000 | 3639.25 | 0 | 11122.75 | -4533.75 | 1350000 | 11122.75 | 0
2021092302 | 5 | 0.50511 | 75766.5 | 0.80571 | 0 | 0.32999 | 4124.875 | 0 | 0 | 64000 | 4124.875 | 0 | 7641.625 | -3481.125 | 1350000 | 7641.625 | 0
2021092303 | 5 | 0.4938 | 74070 | 0.70507 | 0 | 0.35582 | 4447.75 | 0 | 0 | 64000 | 4447.75 | 0 | 5622.25 | -2019.375 | 1350000 | 5622.25 | 0
2021092304 | 5 | 0.48623 | 72934.5 | 0.72055 | 0 | 0.38093 | 4761.625 | 0 | 0 | 64000 | 4761.625 | 0 | 4172.875 | -1449.375 | 1350000 | 4172.875 | 0
2021092305 | 5 | 0.49065 | 73597.5 | 0.69294 | 0 | 0.41222 | 5152.75 | 0 | 0 | 64000 | 5152.75 | 0 | 4444.75 | 271.875 | 1350000 | 4444.75 | 0
2021092306 | 5 | 0.51262 | 76893 | 0.69454 | 0 | 0.44485 | 5560.625 | 0 | 0 | 64000 | 5560.625 | 0 | 7332.375 | 2887.625 | 1350000 | 7332.375 | 0
2021092307 | 5 | 0.55303 | 82954.5 | 0.66909 | 0 | 0.41441 | 5180.125 | 0.00414 | 331.2 | 64000 | 5180.125 | 331.2 | 13443.175 | 6110.8 | 1350000 | 13443.175 | 0
2021092308 | 5 | 0.58278 | 87417 | 0.66703 | 0 | 0.4474 | 5592.5 | 0.06742 | 5393.6 | 64000 | 5592.5 | 5393.6 | 12430.9 | -1012.275 | 1350000 | 12430.9 | 0
2021092309 | 5 | 0.59557 | 89335.5 | 0.63894 | 0 | 0.46453 | 5806.625 | 0.22312 | 17849.6 | 64000 | 5806.625 | 17849.6 | 1679.275 | -10751.625 | 1350000 | 1679.275 | 0
2021092310 | 5 | 0.60609 | 90913.5 | 0.65779 | 0 | 0.49663 | 6207.875 | 0.3601 | 28808 | 64000 | 6207.875 | 20705.625 | 0 | -1679.275 | 1350000 | 0 | 0
2021092311 | 5 | 0.61599 | 92398.5 | 0.60594 | 0 | 0.54345 | 6793.125 | 0.42972 | 34377.6 | 64000 | 6793.125 | 21605.375 | 0 | 0 | 1350000 | 0 | 0
2021092312 | 5 | 0.62104 | 93156 | 0.42309 | 0 | 0.54801 | 6850.125 | 0.44124 | 35299.2 | 64000 | 6850.125 | 22305.875 | 0 | 0 | 1350000 | 0 | 0
2021092313 | 5 | 0.62493 | 93739.5 | 0.40247 | 0 | 0.51747 | 6468.375 | 0.48189 | 38551.2 | 64000 | 6468.375 | 23271.125 | 0 | 0 | 1350000 | 0 | 0
2021092314 | 5 | 0.62706 | 94059 | 0.46962 | 0 | 0.48437 | 6054.625 | 0.47548 | 38038.4 | 64000 | 6054.625 | 24004.375 | 0 | 0 | 1350000 | 0 | 0
2021092315 | 5 | 0.62447 | 93670.5 | 0.5229 | 0 | 0.40848 | 5106 | 0.44458 | 35566.4 | 64000 | 5106 | 24564.5 | 0 | 0 | 1350000 | 0 | 0
2021092316 | 5 | 0.6209 | 93135 | 0.57182 | 0 | 0.32854 | 4106.75 | 0.3965 | 31720 | 64000 | 4106.75 | 25028.25 | 0 | 0 | 1350000 | 0 | 0
2021092317 | 5 | 0.62022 | 93033 | 0.56465 | 0 | 0.31742 | 3967.75 | 0.30575 | 24460 | 64000 | 3967.75 | 24460 | 605.25 | 605.25 | 1350000 | 605.25 | 0
2021092318 | 5 | 0.61698 | 92547 | 0.49748 | 0 | 0.2964 | 3705 | 0.20686 | 16548.8 | 64000 | 3705 | 16548.8 | 8293.2 | 7687.95 | 1350000 | 8293.2 | 0
2021092319 | 5 | 0.60901 | 91351.5 | 0.4084 | 0 | 0.2285 | 2856.25 | 0.05761 | 4608.8 | 64000 | 2856.25 | 4608.8 | 19886.45 | 11593.25 | 1350000 | 19886.45 | 0
2021092320 | 5 | 0.60888 | 91332 | 0.43533 | 0 | 0.18558 | 2319.75 | 0.00079 | 63.2 | 64000 | 2319.75 | 63.2 | 24949.05 | 5062.6 | 1350000 | 24949.05 | 0
2021092321 | 5 | 0.59949 | 89923.5 | 0.5269 | 0 | 0.14694 | 1836.75 | 0 | 0 | 64000 | 1836.75 | 0 | 24086.75 | -862.3 | 1350000 | 24086.75 | 0
2021092322 | 5 | 0.57055 | 85582.5 | 0.64263 | 0 | 0.15284 | 1910.5 | 0 | 0 | 64000 | 1910.5 | 0 | 19672 | -4414.75 | 1350000 | 19672 | 0
2021092323 | 5 | 0.53445 | 80167.5 | 0.71183 | 0 | 0.15255 | 1906.875 | 0 | 0 | 64000 | 1906.875 | 0 | 14260.625 | -5411.375 | 1350000 | 14260.625 | 0
2021092324 | 5 | 0.49955 | 74932.5 | 0.68516 | 0 | 0.14141 | 1767.625 | 0 | 0 | 64000 | 1767.625 | 0 | 9164.875 | -5095.75 | 1350000 | 9164.875 | 0
2021092401 | 6 | 0.47245 | 70867.5 | 0.69702 | 0 | 0.13766 | 1720.75 | 0 | 0 | 64000 | 1720.75 | 0 | 5146.75 | -4018.125 | 1350000 | 5146.75 | 0
2021092402 | 6 | 0.45406 | 68109 | 0.69199 | 0 | 0.17562 | 2195.25 | 0 | 0 | 64000 | 2195.25 | 0 | 1913.75 | -3233 | 1350000 | 1913.75 | 0
2021092403 | 6 | 0.44224 | 66336 | 0.70978 | 0 | 0.22722 | 2840.25 | 0 | 0 | 64000 | 2336 | 0 | 0 | -1913.75 | 1350000 | 0 | 0
2021092404 | 6 | 0.43712 | 65568 | 0.71125 | 0 | 0.2341 | 2926.25 | 0 | 0 | 64000 | 1568 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092405 | 6 | 0.44008 | 66012 | 0.61578 | 0 | 0.24826 | 3103.25 | 0 | 0 | 64000 | 2012 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092406 | 6 | 0.46269 | 69403.5 | 0.60411 | 0 | 0.23931 | 2991.375 | 0 | 0 | 64000 | 2991.375 | 0 | 2412.125 | 2412.125 | 1350000 | 2412.125 | 0
2021092407 | 6 | 0.50265 | 75397.5 | 0.65834 | 0 | 0.32428 | 4053.5 | 0.0075 | 600 | 64000 | 4053.5 | 600 | 6744 | 4331.875 | 1350000 | 6744 | 0
2021092408 | 6 | 0.52825 | 79237.5 | 0.70538 | 0 | 0.45396 | 5674.5 | 0.0639 | 5112 | 64000 | 5674.5 | 5112 | 4451 | -2293 | 1350000 | 4451 | 0
2021092409 | 6 | 0.53936 | 80904 | 0.66525 | 0 | 0.53655 | 6706.875 | 0.18367 | 14693.6 | 64000 | 6706.875 | 10197.125 | 0 | -4451 | 1350000 | 0 | 0
2021092410 | 6 | 0.54455 | 81682.5 | 0.57935 | 0 | 0.60273 | 7534.125 | 0.28276 | 22620.8 | 64000 | 7534.125 | 10148.375 | 0 | 0 | 1350000 | 0 | 0
2021092411 | 6 | 0.5515 | 82725 | 0.60703 | 0 | 0.62607 | 7825.875 | 0.34817 | 27853.6 | 64000 | 7825.875 | 10899.125 | 0 | 0 | 1350000 | 0 | 0
2021092412 | 6 | 0.55753 | 83629.5 | 0.57055 | 0 | 0.61297 | 7662.125 | 0.35677 | 28541.6 | 64000 | 7662.125 | 11967.375 | 0 | 0 | 1350000 | 0 | 0
2021092413 | 6 | 0.56397 | 84595.5 | 0.52573 | 0 | 0.60527 | 7565.875 | 0.35381 | 28304.8 | 64000 | 7565.875 | 13029.625 | 0 | 0 | 1350000 | 0 | 0
2021092414 | 6 | 0.57327 | 85990.5 | 0.42962 | 0 | 0.56901 | 7112.625 | 0.40923 | 32738.4 | 64000 | 7112.625 | 14877.875 | 0 | 0 | 1350000 | 0 | 0
2021092415 | 6 | 0.58045 | 87067.5 | 0.38311 | 0 | 0.50384 | 6298 | 0.41467 | 33173.6 | 64000 | 6298 | 16769.5 | 0 | 0 | 1350000 | 0 | 0
2021092416 | 6 | 0.58842 | 88263 | 0.37805 | 0 | 0.46622 | 5827.75 | 0.37747 | 30197.6 | 64000 | 5827.75 | 18435.25 | 0 | 0 | 1350000 | 0 | 0
2021092417 | 6 | 0.59793 | 89689.5 | 0.29642 | 0 | 0.47015 | 5876.875 | 0.32733 | 26186.4 | 64000 | 5876.875 | 19812.625 | 0 | 0 | 1350000 | 0 | 0
2021092418 | 6 | 0.60081 | 90121.5 | 0.19891 | 0 | 0.50451 | 6306.375 | 0.18766 | 15012.8 | 64000 | 6306.375 | 15012.8 | 4802.325 | 4802.325 | 1350000 | 4802.325 | 0
2021092419 | 6 | 0.58838 | 88257 | 0.1574 | 0 | 0.48464 | 6058 | 0.04322 | 3457.6 | 64000 | 6058 | 3457.6 | 14741.4 | 9939.075 | 1350000 | 14741.4 | 0
2021092420 | 6 | 0.58072 | 87108 | 0.23111 | 0 | 0.51193 | 6399.125 | 0.00062 | 49.6 | 64000 | 6399.125 | 49.6 | 16659.275 | 1917.875 | 1350000 | 16659.275 | 0
2021092421 | 6 | 0.56725 | 85087.5 | 0.29138 | 0 | 0.53905 | 6738.125 | 0 | 0 | 64000 | 6738.125 | 0 | 14349.375 | -2309.9 | 1350000 | 14349.375 | 0
2021092422 | 6 | 0.54337 | 81505.5 | 0.36563 | 0 | 0.57075 | 7134.375 | 0 | 0 | 64000 | 7134.375 | 0 | 10371.125 | -3978.25 | 1350000 | 10371.125 | 0
2021092423 | 6 | 0.51282 | 76923 | 0.44685 | 0 | 0.57965 | 7245.625 | 0 | 0 | 64000 | 7245.625 | 0 | 5677.375 | -4693.75 | 1350000 | 5677.375 | 0
2021092424 | 6 | 0.48261 | 72391.5 | 0.47571 | 0 | 0.55338 | 6917.25 | 0 | 0 | 64000 | 6917.25 | 0 | 1474.25 | -4203.125 | 1350000 | 1474.25 | 0
2021092501 | 7 | 0.45636 | 68454 | 0.46051 | 0 | 0.58523 | 7315.375 | 0 | 0 | 64000 | 4454 | 0 | 0 | -1474.25 | 1350000 | 0 | 0
2021092502 | 7 | 0.43757 | 65635.5 | 0.38344 | 0 | 0.55726 | 6965.75 | 0 | 0 | 64000 | 1635.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092503 | 7 | 0.42582 | 63873 | 0.29724 | 0 | 0.51635 | 6454.375 | 0 | 0 | 63873 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092504 | 7 | 0.41791 | 62686.5 | 0.24682 | 0 | 0.49814 | 6226.75 | 0 | 0 | 62686.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092505 | 7 | 0.4161 | 62415 | 0.1645 | 0 | 0.48875 | 6109.375 | 0 | 0 | 62415 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092506 | 7 | 0.42352 | 63528 | 0.09167 | 0 | 0.55879 | 6984.875 | 0 | 0 | 63528 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092507 | 7 | 0.43913 | 65869.5 | 0.06505 | 0 | 0.61986 | 7748.25 | 0.00507 | 405.6 | 64000 | 1869.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092508 | 7 | 0.45403 | 68104.5 | 0.07837 | 0 | 0.65675 | 8209.375 | 0.09013 | 7210.4 | 64000 | 4104.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092509 | 7 | 0.47078 | 70617 | 0.10119 | 0 | 0.66567 | 8320.875 | 0.28135 | 22508 | 64000 | 6617 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092510 | 7 | 0.48383 | 72574.5 | 0.08949 | 0 | 0.55675 | 6959.375 | 0.43738 | 34990.4 | 64000 | 6959.375 | 1615.125 | 0 | 0 | 1350000 | 0 | 0
2021092511 | 7 | 0.49474 | 74211 | 0.10475 | 0 | 0.50431 | 6303.875 | 0.50935 | 40748 | 64000 | 6303.875 | 3907.125 | 0 | 0 | 1350000 | 0 | 0
2021092512 | 7 | 0.5018 | 75270 | 0.1963 | 0 | 0.44912 | 5614 | 0.55057 | 44045.6 | 64000 | 5614 | 5656 | 0 | 0 | 1350000 | 0 | 0
2021092513 | 7 | 0.5067 | 76005 | 0.24385 | 0 | 0.41492 | 5186.5 | 0.56632 | 45305.6 | 64000 | 5186.5 | 6818.5 | 0 | 0 | 1350000 | 0 | 0
2021092514 | 7 | 0.51292 | 76938 | 0.26864 | 0 | 0.38248 | 4781 | 0.58162 | 46529.6 | 64000 | 4781 | 8157 | 0 | 0 | 1350000 | 0 | 0
2021092515 | 7 | 0.51884 | 77826 | 0.22508 | 0 | 0.35131 | 4391.375 | 0.57564 | 46051.2 | 64000 | 4391.375 | 9434.625 | 0 | 0 | 1350000 | 0 | 0
2021092516 | 7 | 0.52643 | 78964.5 | 0.1624 | 0 | 0.31532 | 3941.5 | 0.54394 | 43515.2 | 64000 | 3941.5 | 11023 | 0 | 0 | 1350000 | 0 | 0
2021092517 | 7 | 0.53575 | 80362.5 | 0.13368 | 0 | 0.31594 | 3949.25 | 0.44677 | 35741.6 | 64000 | 3949.25 | 12413.25 | 0 | 0 | 1350000 | 0 | 0
2021092518 | 7 | 0.53966 | 80949 | 0.17219 | 0 | 0.36755 | 4594.375 | 0.29105 | 23284 | 64000 | 4594.375 | 12354.625 | 0 | 0 | 1350000 | 0 | 0
2021092519 | 7 | 0.53621 | 80431.5 | 0.20684 | 0 | 0.4887 | 6108.75 | 0.07701 | 6160.8 | 64000 | 6108.75 | 6160.8 | 4161.95 | 4161.95 | 1350000 | 4161.95 | 0
2021092520 | 7 | 0.53881 | 80821.5 | 0.41494 | 0 | 0.52523 | 6565.375 | 0.00116 | 92.8 | 64000 | 6565.375 | 92.8 | 10163.325 | 6001.375 | 1350000 | 10163.325 | 0
2021092521 | 7 | 0.53219 | 79828.5 | 0.44743 | 0 | 0.49191 | 6148.875 | 0 | 0 | 64000 | 6148.875 | 0 | 9679.625 | -483.7 | 1350000 | 9679.625 | 0
2021092522 | 7 | 0.51384 | 77076 | 0.44342 | 0 | 0.48741 | 6092.625 | 0 | 0 | 64000 | 6092.625 | 0 | 6983.375 | -2696.25 | 1350000 | 6983.375 | 0
2021092523 | 7 | 0.48854 | 73281 | 0.52022 | 0 | 0.4452 | 5565 | 0 | 0 | 64000 | 5565 | 0 | 3716 | -3267.375 | 1350000 | 3716 | 0
2021092524 | 7 | 0.46313 | 69469.5 | 0.59139 | 0 | 0.3747 | 4683.75 | 0 | 0 | 64000 | 4683.75 | 0 | 785.75 | -2930.25 | 1350000 | 785.75 | 0
2021092601 | 1 | 0.44024 | 66036 | 0.62917 | 0 | 0.34359 | 4294.875 | 0 | 0 | 64000 | 2036 | 0 | 0 | -785.75 | 1350000 | 0 | 0
2021092602 | 1 | 0.42503 | 63754.5 | 0.65874 | 0 | 0.36512 | 4564 | 0 | 0 | 63754.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092603 | 1 | 0.41422 | 62133 | 0.61042 | 0 | 0.48185 | 6023.125 | 0 | 0 | 62133 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092604 | 1 | 0.40733 | 61099.5 | 0.56036 | 0 | 0.47932 | 5991.5 | 0 | 0 | 61099.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092605 | 1 | 0.40522 | 60783 | 0.59371 | 0 | 0.4021 | 5026.25 | 0 | 0 | 60783 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092606 | 1 | 0.40881 | 61321.5 | 0.60793 | 0 | 0.34148 | 4268.5 | 0 | 0 | 61321.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092607 | 1 | 0.41816 | 62724 | 0.63844 | 0 | 0.33459 | 4182.375 | 0.00838 | 670.4 | 62724 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092608 | 1 | 0.42754 | 64131 | 0.58479 | 0 | 0.3188 | 3985 | 0.12835 | 10268 | 64000 | 131 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092609 | 1 | 0.44318 | 66477 | 0.50372 | 0 | 0.26578 | 3322.25 | 0.32031 | 25624.8 | 64000 | 2477 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092610 | 1 | 0.45815 | 68722.5 | 0.39404 | 0 | 0.25156 | 3144.5 | 0.44891 | 35912.8 | 64000 | 3144.5 | 1578 | 0 | 0 | 1350000 | 0 | 0
2021092611 | 1 | 0.46962 | 70443 | 0.44879 | 0 | 0.33377 | 4172.125 | 0.51375 | 41100 | 64000 | 4172.125 | 2270.875 | 0 | 0 | 1350000 | 0 | 0
2021092612 | 1 | 0.48038 | 72057 | 0.66219 | 0 | 0.44867 | 5608.375 | 0.56136 | 44908.8 | 64000 | 5608.375 | 2448.625 | 0 | 0 | 1350000 | 0 | 0
2021092613 | 1 | 0.49118 | 73677 | 0.77776 | 0 | 0.47002 | 5875.25 | 0.56486 | 45188.8 | 64000 | 5875.25 | 3801.75 | 0 | 0 | 1350000 | 0 | 0
2021092614 | 1 | 0.50134 | 75201 | 0.76844 | 0 | 0.46088 | 5761 | 0.54948 | 43958.4 | 64000 | 5761 | 5440 | 0 | 0 | 1350000 | 0 | 0
2021092615 | 1 | 0.51096 | 76644 | 0.72499 | 0 | 0.43316 | 5414.5 | 0.52103 | 41682.4 | 64000 | 5414.5 | 7229.5 | 0 | 0 | 1350000 | 0 | 0
2021092616 | 1 | 0.52402 | 78603 | 0.75322 | 0 | 0.36983 | 4622.875 | 0.48657 | 38925.6 | 64000 | 4622.875 | 9980.125 | 0 | 0 | 1350000 | 0 | 0
2021092617 | 1 | 0.54067 | 81100.5 | 0.75533 | 0 | 0.33555 | 4194.375 | 0.41965 | 33572 | 64000 | 4194.375 | 12906.125 | 0 | 0 | 1350000 | 0 | 0
2021092618 | 1 | 0.55482 | 83223 | 0.70227 | 0 | 0.40921 | 5115.125 | 0.28175 | 22540 | 64000 | 5115.125 | 14107.875 | 0 | 0 | 1350000 | 0 | 0
2021092619 | 1 | 0.55549 | 83323.5 | 0.6003 | 0 | 0.41756 | 5219.5 | 0.07185 | 5748 | 64000 | 5219.5 | 5748 | 8356 | 8356 | 1350000 | 8356 | 0
2021092620 | 1 | 0.56062 | 84093 | 0.65806 | 0 | 0.41901 | 5237.625 | 0.00062 | 49.6 | 64000 | 5237.625 | 49.6 | 14805.775 | 6449.775 | 1350000 | 14805.775 | 0
2021092621 | 1 | 0.55673 | 83509.5 | 0.80235 | 0 | 0.4233 | 5291.25 | 0 | 0 | 64000 | 5291.25 | 0 | 14218.25 | -587.525 | 1350000 | 14218.25 | 0
2021092622 | 1 | 0.5314 | 79710 | 0.84343 | 0 | 0.43564 | 5445.5 | 0 | 0 | 64000 | 5445.5 | 0 | 10264.5 | -3953.75 | 1350000 | 10264.5 | 0
2021092623 | 1 | 0.49992 | 74988 | 0.86805 | 0 | 0.46118 | 5764.75 | 0 | 0 | 64000 | 5764.75 | 0 | 5223.25 | -5041.25 | 1350000 | 5223.25 | 0
2021092624 | 1 | 0.47125 | 70687.5 | 0.8831 | 0 | 0.46122 | 5765.25 | 0 | 0 | 64000 | 5765.25 | 0 | 922.25 | -4301 | 1350000 | 922.25 | 0
2021092701 | 2 | 0.44721 | 67081.5 | 0.88566 | 0 | 0.48999 | 6124.875 | 0 | 0 | 64000 | 3081.5 | 0 | 0 | -922.25 | 1350000 | 0 | 0
2021092702 | 2 | 0.43124 | 64686 | 0.85036 | 0 | 0.50208 | 6276 | 0 | 0 | 64000 | 686 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092703 | 2 | 0.4232 | 63480 | 0.86452 | 0 | 0.47541 | 5942.625 | 0 | 0 | 63480 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092704 | 2 | 0.42086 | 63129 | 0.87783 | 0 | 0.44187 | 5523.375 | 0 | 0 | 63129 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092705 | 2 | 0.42791 | 64186.5 | 0.90209 | 0 | 0.34126 | 4265.75 | 0 | 0 | 64000 | 186.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092706 | 2 | 0.45268 | 67902 | 0.88961 | 0 | 0.28495 | 3561.875 | 0 | 0 | 64000 | 3561.875 | 0 | 340.125 | 340.125 | 1350000 | 340.125 | 0
2021092707 | 2 | 0.49728 | 74592 | 0.85857 | 0 | 0.32624 | 4078 | 0.00974 | 779.2 | 64000 | 4078 | 779.2 | 5734.8 | 5394.675 | 1350000 | 5734.8 | 0
2021092708 | 2 | 0.5278 | 79170 | 0.83664 | 0 | 0.43359 | 5419.875 | 0.13373 | 10698.4 | 64000 | 5419.875 | 9750.125 | 0 | -5734.8 | 1350000 | 0 | 0
2021092709 | 2 | 0.53983 | 80974.5 | 0.79776 | 0 | 0.50422 | 6302.75 | 0.32644 | 26115.2 | 64000 | 6302.75 | 10671.75 | 0 | 0 | 1350000 | 0 | 0
2021092710 | 2 | 0.55051 | 82576.5 | 0.71583 | 0 | 0.52995 | 6624.375 | 0.40548 | 32438.4 | 64000 | 6624.375 | 11952.125 | 0 | 0 | 1350000 | 0 | 0
2021092711 | 2 | 0.56592 | 84888 | 0.71473 | 0 | 0.54918 | 6864.75 | 0.4669 | 37352 | 64000 | 6864.75 | 14023.25 | 0 | 0 | 1350000 | 0 | 0
2021092712 | 2 | 0.58268 | 87402 | 0.70345 | 0 | 0.54006 | 6750.75 | 0.44368 | 35494.4 | 64000 | 6750.75 | 16651.25 | 0 | 0 | 1350000 | 0 | 0
2021092713 | 2 | 0.60218 | 90327 | 0.71411 | 0 | 0.43622 | 5452.75 | 0.50614 | 40491.2 | 64000 | 5452.75 | 20874.25 | 0 | 0 | 1350000 | 0 | 0
2021092714 | 2 | 0.62148 | 93222 | 0.78605 | 0 | 0.3248 | 4060 | 0.6013 | 48104 | 64000 | 4060 | 25162 | 0 | 0 | 1350000 | 0 | 0
2021092715 | 2 | 0.64172 | 96258 | 0.82676 | 0 | 0.29771 | 3721.375 | 0.60183 | 48146.4 | 64000 | 3721.375 | 28536.625 | 0 | 0 | 1350000 | 0 | 0
2021092716 | 2 | 0.66141 | 99211.5 | 0.80146 | 0 | 0.2833 | 3541.25 | 0.57067 | 45653.6 | 64000 | 3541.25 | 31670.25 | 0 | 0 | 1350000 | 0 | 0
2021092717 | 2 | 0.67807 | 101710.5 | 0.79938 | 0 | 0.33037 | 4129.625 | 0.5051 | 40408 | 64000 | 4129.625 | 33580.875 | 0 | 0 | 1350000 | 0 | 0
2021092718 | 2 | 0.68393 | 102589.5 | 0.78997 | 0 | 0.44651 | 5581.375 | 0.32802 | 26241.6 | 64000 | 5581.375 | 26241.6 | 6766.525 | 6766.525 | 1350000 | 6766.525 | 0
2021092719 | 2 | 0.67125 | 100687.5 | 0.81359 | 0 | 0.4947 | 6183.75 | 0.08325 | 6660 | 64000 | 6183.75 | 6660 | 23843.75 | 17077.225 | 1350000 | 23843.75 | 0
2021092720 | 2 | 0.66464 | 99696 | 0.83212 | 0 | 0.5108 | 6385 | 0.00171 | 136.8 | 64000 | 6385 | 136.8 | 29174.2 | 5330.45 | 1346292.05 | 29174.2 | 0
2021092721 | 2 | 0.64808 | 97212 | 0.85726 | 0 | 0.5238 | 6547.5 | 0 | 0 | 64000 | 6547.5 | 0 | 26664.5 | -2509.7 | 1345093.8 | 26664.5 | 0
2021092722 | 2 | 0.6121 | 91815 | 0.9039 | 0 | 0.51752 | 6469 | 0 | 0 | 64000 | 6469 | 0 | 21346 | -5318.5 | 1349214.05 | 21346 | 0
2021092723 | 2 | 0.57001 | 85501.5 | 0.91125 | 0 | 0.52271 | 6533.875 | 0 | 0 | 64000 | 6533.875 | 0 | 14967.625 | -6378.375 | 1350000 | 14967.625 | 0
2021092724 | 2 | 0.52889 | 79333.5 | 0.91913 | 0 | 0.53037 | 6629.625 | 0 | 0 | 64000 | 6629.625 | 0 | 8703.875 | -6263.75 | 1350000 | 8703.875 | 0
2021092801 | 3 | 0.49719 | 74578.5 | 0.92081 | 0 | 0.54519 | 6814.875 | 0 | 0 | 64000 | 6814.875 | 0 | 3763.625 | -4940.25 | 1350000 | 3763.625 | 0
2021092802 | 3 | 0.47593 | 71389.5 | 0.90442 | 0 | 0.52674 | 6584.25 | 0 | 0 | 64000 | 6584.25 | 0 | 805.25 | -2958.375 | 1350000 | 805.25 | 0
2021092803 | 3 | 0.46299 | 69448.5 | 0.8863 | 0 | 0.52212 | 6526.5 | 0 | 0 | 64000 | 5448.5 | 0 | 0 | -805.25 | 1350000 | 0 | 0
2021092804 | 3 | 0.45653 | 68479.5 | 0.84413 | 0 | 0.50837 | 6354.625 | 0 | 0 | 64000 | 4479.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092805 | 3 | 0.45933 | 68899.5 | 0.82554 | 0 | 0.47293 | 5911.625 | 0 | 0 | 64000 | 4899.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092806 | 3 | 0.48149 | 72223.5 | 0.85371 | 0 | 0.39818 | 4977.25 | 0 | 0 | 64000 | 4977.25 | 0 | 3246.25 | 3246.25 | 1350000 | 3246.25 | 0
2021092807 | 3 | 0.52318 | 78477 | 0.7838 | 0 | 0.38449 | 4806.125 | 0.00826 | 660.8 | 64000 | 4806.125 | 660.8 | 9010.075 | 5763.825 | 1350000 | 9010.075 | 0
2021092808 | 3 | 0.55149 | 82723.5 | 0.74493 | 0 | 0.41332 | 5166.5 | 0.14794 | 11835.2 | 64000 | 5166.5 | 11835.2 | 1721.8 | -7288.275 | 1350000 | 1721.8 | 0
2021092809 | 3 | 0.56585 | 84877.5 | 0.74136 | 0 | 0.41386 | 5173.25 | 0.38746 | 30996.8 | 64000 | 5173.25 | 15704.25 | 0 | -1721.8 | 1350000 | 0 | 0
2021092810 | 3 | 0.58267 | 87400.5 | 0.69224 | 0 | 0.42247 | 5280.875 | 0.49677 | 39741.6 | 64000 | 5280.875 | 18119.625 | 0 | 0 | 1350000 | 0 | 0
2021092811 | 3 | 0.60042 | 90063 | 0.63208 | 0 | 0.43374 | 5421.75 | 0.53297 | 42637.6 | 64000 | 5421.75 | 20641.25 | 0 | 0 | 1350000 | 0 | 0
2021092812 | 3 | 0.61692 | 92538 | 0.56645 | 0 | 0.46981 | 5872.625 | 0.57454 | 45963.2 | 64000 | 5872.625 | 22665.375 | 0 | 0 | 1350000 | 0 | 0
2021092813 | 3 | 0.63049 | 94573.5 | 0.52343 | 0 | 0.43866 | 5483.25 | 0.60022 | 48017.6 | 64000 | 5483.25 | 25090.25 | 0 | 0 | 1350000 | 0 | 0
2021092814 | 3 | 0.64244 | 96366 | 0.47442 | 0 | 0.36586 | 4573.25 | 0.61021 | 48816.8 | 64000 | 4573.25 | 27792.75 | 0 | 0 | 1350000 | 0 | 0
2021092815 | 3 | 0.6545 | 98175 | 0.46826 | 0 | 0.29163 | 3645.375 | 0.6033 | 48264 | 64000 | 3645.375 | 30529.625 | 0 | 0 | 1350000 | 0 | 0
2021092816 | 3 | 0.6655 | 99825 | 0.5091 | 0 | 0.2415 | 3018.75 | 0.58637 | 46909.6 | 64000 | 3018.75 | 32806.25 | 0 | 0 | 1350000 | 0 | 0
2021092817 | 3 | 0.67413 | 101119.5 | 0.57443 | 0 | 0.31201 | 3900.125 | 0.53396 | 42716.8 | 64000 | 3900.125 | 33219.375 | 0 | 0 | 1350000 | 0 | 0
2021092818 | 3 | 0.67601 | 101401.5 | 0.53307 | 0 | 0.38945 | 4868.125 | 0.36446 | 29156.8 | 64000 | 4868.125 | 29156.8 | 3376.575 | 3376.575 | 1350000 | 3376.575 | 0
2021092819 | 3 | 0.66619 | 99928.5 | 0.51531 | 0 | 0.36172 | 4521.5 | 0.0924 | 7392 | 64000 | 4521.5 | 7392 | 24015 | 20638.425 | 1350000 | 24015 | 0
2021092820 | 3 | 0.65864 | 98796 | 0.51128 | 0 | 0.32641 | 4080.125 | 0.00165 | 132 | 64000 | 4080.125 | 132 | 30583.875 | 6568.875 | 1344882.375 | 30583.875 | 0
2021092821 | 3 | 0.6399 | 95985 | 0.50617 | 0 | 0.34334 | 4291.75 | 0 | 0 | 64000 | 4291.75 | 0 | 27693.25 | -2890.625 | 1342655.375 | 27693.25 | 0
2021092822 | 3 | 0.60552 | 90828 | 0.50422 | 0 | 0.38765 | 4845.625 | 0 | 0 | 64000 | 4845.625 | 0 | 21982.375 | -5710.875 | 1346139.25 | 21982.375 | 0
2021092823 | 3 | 0.56017 | 84025.5 | 0.4447 | 0 | 0.47181 | 5897.625 | 0 | 0 | 64000 | 5897.625 | 0 | 14127.875 | -7854.5 | 1350000 | 14127.875 | 0
2021092824 | 3 | 0.51913 | 77869.5 | 0.40889 | 0 | 0.53627 | 6703.375 | 0 | 0 | 64000 | 6703.375 | 0 | 7166.125 | -6961.75 | 1350000 | 7166.125 | 0
2021092901 | 4 | 0.48739 | 73108.5 | 0.38556 | 0 | 0.55902 | 6987.75 | 0 | 0 | 64000 | 6987.75 | 0 | 2120.75 | -5045.375 | 1350000 | 2120.75 | 0
2021092902 | 4 | 0.46494 | 69741 | 0.37396 | 0 | 0.55856 | 6982 | 0 | 0 | 64000 | 5741 | 0 | 0 | -2120.75 | 1350000 | 0 | 0
2021092903 | 4 | 0.45099 | 67648.5 | 0.35653 | 0 | 0.54088 | 6761 | 0 | 0 | 64000 | 3648.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092904 | 4 | 0.44405 | 66607.5 | 0.30132 | 0 | 0.50968 | 6371 | 0 | 0 | 64000 | 2607.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092905 | 4 | 0.44776 | 67164 | 0.28118 | 0 | 0.42201 | 5275.125 | 0 | 0 | 64000 | 3164 | 0 | 0 | 0 | 1350000 | 0 | 0
2021092906 | 4 | 0.4683 | 70245 | 0.26018 | 0 | 0.32714 | 4089.25 | 0 | 0 | 64000 | 4089.25 | 0 | 2155.75 | 2155.75 | 1350000 | 2155.75 | 0
2021092907 | 4 | 0.50789 | 76183.5 | 0.29973 | 0 | 0.30779 | 3847.375 | 0.01172 | 937.6 | 64000 | 3847.375 | 937.6 | 7398.525 | 5242.775 | 1350000 | 7398.525 | 0
2021092908 | 4 | 0.53332 | 79998 | 0.25307 | 0 | 0.33261 | 4157.625 | 0.17191 | 13752.8 | 64000 | 4157.625 | 11840.375 | 0 | -7398.525 | 1350000 | 0 | 0
2021092909 | 4 | 0.5413 | 81195 | 0.20118 | 0 | 0.30977 | 3872.125 | 0.43516 | 34812.8 | 64000 | 3872.125 | 13322.875 | 0 | 0 | 1350000 | 0 | 0
2021092910 | 4 | 0.54743 | 82114.5 | 0.1412 | 0 | 0.27422 | 3427.75 | 0.54015 | 43212 | 64000 | 3427.75 | 14686.75 | 0 | 0 | 1350000 | 0 | 0
2021092911 | 4 | 0.55872 | 83808 | 0.16391 | 0 | 0.23049 | 2881.125 | 0.58032 | 46425.6 | 64000 | 2881.125 | 16926.875 | 0 | 0 | 1350000 | 0 | 0
2021092912 | 4 | 0.57101 | 85651.5 | 0.29075 | 0 | 0.18894 | 2361.75 | 0.59694 | 47755.2 | 64000 | 2361.75 | 19289.75 | 0 | 0 | 1350000 | 0 | 0
2021092913 | 4 | 0.58454 | 87681 | 0.27979 | 0 | 0.15775 | 1971.875 | 0.61705 | 49364 | 64000 | 1971.875 | 21709.125 | 0 | 0 | 1350000 | 0 | 0
2021092914 | 4 | 0.60217 | 90325.5 | 0.28911 | 0 | 0.14092 | 1761.5 | 0.61824 | 49459.2 | 64000 | 1761.5 | 24564 | 0 | 0 | 1350000 | 0 | 0
2021092915 | 4 | 0.61477 | 92215.5 | 0.31165 | 0 | 0.09891 | 1236.375 | 0.59559 | 47647.2 | 64000 | 1236.375 | 26979.125 | 0 | 0 | 1350000 | 0 | 0
2021092916 | 4 | 0.62614 | 93921 | 0.29281 | 0 | 0.08853 | 1106.625 | 0.54935 | 43948 | 64000 | 1106.625 | 28814.375 | 0 | 0 | 1350000 | 0 | 0
2021092917 | 4 | 0.63646 | 95469 | 0.30051 | 0 | 0.1316 | 1645 | 0.44594 | 35675.2 | 64000 | 1645 | 29824 | 0 | 0 | 1350000 | 0 | 0
2021092918 | 4 | 0.64191 | 96286.5 | 0.25848 | 0 | 0.2006 | 2507.5 | 0.27995 | 22396 | 64000 | 2507.5 | 22396 | 7383 | 7383 | 1350000 | 7383 | 0
2021092919 | 4 | 0.6314 | 94710 | 0.25335 | 0 | 0.25202 | 3150.25 | 0.0601 | 4808 | 64000 | 3150.25 | 4808 | 22751.75 | 15368.75 | 1350000 | 22751.75 | 0
2021092920 | 4 | 0.62417 | 93625.5 | 0.28037 | 0 | 0.30962 | 3870.25 | 0 | 0 | 64000 | 3870.25 | 0 | 25755.25 | 3003.5 | 1349711 | 25755.25 | 0
2021092921 | 4 | 0.60717 | 91075.5 | 0.31273 | 0 | 0.37541 | 4692.625 | 0 | 0 | 64000 | 4692.625 | 0 | 22382.875 | -3372.375 | 1350000 | 22382.875 | 0
2021092922 | 4 | 0.57385 | 86077.5 | 0.30584 | 0 | 0.42321 | 5290.125 | 0 | 0 | 64000 | 5290.125 | 0 | 16787.375 | -5595.5 | 1350000 | 16787.375 | 0
2021092923 | 4 | 0.53486 | 80229 | 0.29394 | 0 | 0.47892 | 5986.5 | 0 | 0 | 64000 | 5986.5 | 0 | 10242.5 | -6544.875 | 1350000 | 10242.5 | 0
2021092924 | 4 | 0.49745 | 74617.5 | 0.2342 | 0 | 0.51753 | 6469.125 | 0 | 0 | 64000 | 6469.125 | 0 | 4148.375 | -6094.125 | 1350000 | 4148.375 | 0
2021093001 | 5 | 0.47001 | 70501.5 | 0.2106 | 0 | 0.53742 | 6717.75 | 0 | 0 | 64000 | 6501.5 | 0 | 0 | -4148.375 | 1350000 | 0 | 0
2021093002 | 5 | 0.44979 | 67468.5 | 0.15773 | 0 | 0.52309 | 6538.625 | 0 | 0 | 64000 | 3468.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021093003 | 5 | 0.43982 | 65973 | 0.1533 | 0 | 0.50432 | 6304 | 0 | 0 | 64000 | 1973 | 0 | 0 | 0 | 1350000 | 0 | 0
2021093004 | 5 | 0.43379 | 65068.5 | 0.14117 | 0 | 0.47612 | 5951.5 | 0 | 0 | 64000 | 1068.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021093005 | 5 | 0.437 | 65550 | 0.16016 | 0 | 0.44225 | 5528.125 | 0 | 0 | 64000 | 1550 | 0 | 0 | 0 | 1350000 | 0 | 0
2021093006 | 5 | 0.45899 | 68848.5 | 0.16861 | 0 | 0.44014 | 5501.75 | 0 | 0 | 64000 | 4848.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021093007 | 5 | 0.50132 | 75198 | 0.20137 | 0 | 0.50849 | 6356.125 | 0.01122 | 897.6 | 64000 | 6356.125 | 897.6 | 3944.275 | 3944.275 | 1350000 | 3944.275 | 0
2021093008 | 5 | 0.52822 | 79233 | 0.25087 | 0 | 0.60233 | 7529.125 | 0.1869 | 14952 | 64000 | 7529.125 | 7703.875 | 0 | -3944.275 | 1350000 | 0 | 0
2021093009 | 5 | 0.5393 | 80895 | 0.22984 | 0 | 0.63848 | 7981 | 0.43951 | 35160.8 | 64000 | 7981 | 8914 | 0 | 0 | 1350000 | 0 | 0
2021093010 | 5 | 0.54609 | 81913.5 | 0.17224 | 0 | 0.64547 | 8068.375 | 0.5472 | 43776 | 64000 | 8068.375 | 9845.125 | 0 | 0 | 1350000 | 0 | 0
2021093011 | 5 | 0.55642 | 83463 | 0.20291 | 0 | 0.65071 | 8133.875 | 0.6087 | 48696 | 64000 | 8133.875 | 11329.125 | 0 | 0 | 1350000 | 0 | 0
2021093012 | 5 | 0.56729 | 85093.5 | 0.23106 | 0 | 0.64024 | 8003 | 0.62879 | 50303.2 | 64000 | 8003 | 13090.5 | 0 | 0 | 1350000 | 0 | 0
2021093013 | 5 | 0.57977 | 86965.5 | 0.18549 | 0 | 0.65127 | 8140.875 | 0.63684 | 50947.2 | 64000 | 8140.875 | 14824.625 | 0 | 0 | 1350000 | 0 | 0
2021093014 | 5 | 0.59127 | 88690.5 | 0.16968 | 0 | 0.66777 | 8347.125 | 0.63863 | 51090.4 | 64000 | 8347.125 | 16343.375 | 0 | 0 | 1350000 | 0 | 0
2021093015 | 5 | 0.60126 | 90189 | 0.1986 | 0 | 0.68366 | 8545.75 | 0.63265 | 50612 | 64000 | 8545.75 | 17643.25 | 0 | 0 | 1350000 | 0 | 0
2021093016 | 5 | 0.6094 | 91410 | 0.24298 | 0 | 0.68377 | 8547.125 | 0.6153 | 49224 | 64000 | 8547.125 | 18862.875 | 0 | 0 | 1350000 | 0 | 0
2021093017 | 5 | 0.61757 | 92635.5 | 0.27837 | 0 | 0.68449 | 8556.125 | 0.55591 | 44472.8 | 64000 | 8556.125 | 20079.375 | 0 | 0 | 1350000 | 0 | 0
2021093018 | 5 | 0.61837 | 92755.5 | 0.28905 | 0 | 0.71113 | 8889.125 | 0.38986 | 31188.8 | 64000 | 8889.125 | 19866.375 | 0 | 0 | 1350000 | 0 | 0
2021093019 | 5 | 0.61079 | 91618.5 | 0.32693 | 0 | 0.72712 | 9089 | 0.09366 | 7492.8 | 64000 | 9089 | 7492.8 | 11036.7 | 11036.7 | 1350000 | 11036.7 | 0
2021093020 | 5 | 0.60932 | 91398 | 0.29833 | 0 | 0.69627 | 8703.375 | 0.00065 | 52 | 64000 | 8703.375 | 52 | 18642.625 | 7605.925 | 1350000 | 18642.625 | 0
2021093021 | 5 | 0.59496 | 89244 | 0.31062 | 0 | 0.69433 | 8679.125 | 0 | 0 | 64000 | 8679.125 | 0 | 16564.875 | -2077.75 | 1350000 | 16564.875 | 0
2021093022 | 5 | 0.56412 | 84618 | 0.25205 | 0 | 0.67781 | 8472.625 | 0 | 0 | 64000 | 8472.625 | 0 | 12145.375 | -4419.5 | 1350000 | 12145.375 | 0
2021093023 | 5 | 0.52648 | 78972 | 0.2263 | 0 | 0.63146 | 7893.25 | 0 | 0 | 64000 | 7893.25 | 0 | 7078.75 | -5066.625 | 1350000 | 7078.75 | 0
2021093024 | 5 | 0.49135 | 73702.5 | 0.15748 | 0 | 0.62447 | 7805.875 | 0 | 0 | 64000 | 7805.875 | 0 | 1896.625 | -5182.125 | 1350000 | 1896.625 | 0
2021100101 | 6 | 0.46263 | 69394.5 | 0.12796 | 0 | 0.62946 | 7868.25 | 0 | 0 | 64000 | 5394.5 | 0 | 0 | -1896.625 | 1350000 | 0 | 0
2021100102 | 6 | 0.44414 | 66621 | 0.12237 | 0 | 0.62169 | 7771.125 | 0 | 0 | 64000 | 2621 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100103 | 6 | 0.43426 | 65139 | 0.11785 | 0 | 0.6002 | 7502.5 | 0 | 0 | 64000 | 1139 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100104 | 6 | 0.42986 | 64479 | 0.12949 | 0 | 0.55641 | 6955.125 | 0 | 0 | 64000 | 479 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100105 | 6 | 0.43329 | 64993.5 | 0.12323 | 0 | 0.51669 | 6458.625 | 0 | 0 | 64000 | 993.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100106 | 6 | 0.45494 | 68241 | 0.14064 | 0 | 0.45486 | 5685.75 | 0 | 0 | 64000 | 4241 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100107 | 6 | 0.4942 | 74130 | 0.11357 | 0 | 0.43348 | 5418.5 | 0.01246 | 996.8 | 64000 | 5418.5 | 996.8 | 3714.7 | 3714.7 | 1350000 | 3714.7 | 0
2021100108 | 6 | 0.52088 | 78132 | 0.09738 | 0 | 0.42732 | 5341.5 | 0.18734 | 14987.2 | 64000 | 5341.5 | 8790.5 | 0 | -3714.7 | 1350000 | 0 | 0
2021100109 | 6 | 0.53094 | 79641 | 0.07548 | 0 | 0.40773 | 5096.625 | 0.4266 | 34128 | 64000 | 5096.625 | 10544.375 | 0 | 0 | 1350000 | 0 | 0
2021100110 | 6 | 0.53584 | 80376 | 0.04769 | 0 | 0.38983 | 4872.875 | 0.51823 | 41458.4 | 64000 | 4872.875 | 11503.125 | 0 | 0 | 1350000 | 0 | 0
2021100111 | 6 | 0.5454 | 81810 | 0.04366 | 0 | 0.36854 | 4606.75 | 0.55429 | 44343.2 | 64000 | 4606.75 | 13203.25 | 0 | 0 | 1350000 | 0 | 0
2021100112 | 6 | 0.55337 | 83005.5 | 0.04911 | 0 | 0.34876 | 4359.5 | 0.56247 | 44997.6 | 64000 | 4359.5 | 14646 | 0 | 0 | 1350000 | 0 | 0
2021100113 | 6 | 0.56458 | 84687 | 0.02611 | 0 | 0.32526 | 4065.75 | 0.56121 | 44896.8 | 64000 | 4065.75 | 16621.25 | 0 | 0 | 1350000 | 0 | 0
2021100114 | 6 | 0.57713 | 86569.5 | 0.01882 | 0 | 0.31021 | 3877.625 | 0.54567 | 43653.6 | 64000 | 3877.625 | 18691.875 | 0 | 0 | 1350000 | 0 | 0
2021100115 | 6 | 0.58778 | 88167 | 0.02239 | 0 | 0.2779 | 3473.75 | 0.5324 | 42592 | 64000 | 3473.75 | 20693.25 | 0 | 0 | 1350000 | 0 | 0
2021100116 | 6 | 0.59741 | 89611.5 | 0.02912 | 0 | 0.25118 | 3139.75 | 0.52068 | 41654.4 | 64000 | 3139.75 | 22471.75 | 0 | 0 | 1350000 | 0 | 0
2021100117 | 6 | 0.60791 | 91186.5 | 0.04834 | 0 | 0.25122 | 3140.25 | 0.50617 | 40493.6 | 64000 | 3140.25 | 24046.25 | 0 | 0 | 1350000 | 0 | 0
2021100118 | 6 | 0.61117 | 91675.5 | 0.06116 | 0 | 0.27812 | 3476.5 | 0.38353 | 30682.4 | 64000 | 3476.5 | 24199 | 0 | 0 | 1350000 | 0 | 0
2021100119 | 6 | 0.59836 | 89754 | 0.07257 | 0 | 0.26089 | 3261.125 | 0.08322 | 6657.6 | 64000 | 3261.125 | 6657.6 | 15835.275 | 15835.275 | 1350000 | 15835.275 | 0
2021100120 | 6 | 0.58974 | 88461 | 0.12263 | 0 | 0.25678 | 3209.75 | 0.00019 | 15.2 | 64000 | 3209.75 | 15.2 | 21236.05 | 5400.775 | 1350000 | 21236.05 | 0
2021100121 | 6 | 0.57425 | 86137.5 | 0.10489 | 0 | 0.24426 | 3053.25 | 0 | 0 | 64000 | 3053.25 | 0 | 19084.25 | -2151.8 | 1350000 | 19084.25 | 0
2021100122 | 6 | 0.55002 | 82503 | 0.0996 | 0 | 0.24399 | 3049.875 | 0 | 0 | 64000 | 3049.875 | 0 | 15453.125 | -3631.125 | 1350000 | 15453.125 | 0
2021100123 | 6 | 0.51971 | 77956.5 | 0.14081 | 0 | 0.24912 | 3114 | 0 | 0 | 64000 | 3114 | 0 | 10842.5 | -4610.625 | 1350000 | 10842.5 | 0
2021100124 | 6 | 0.48712 | 73068 | 0.15708 | 0 | 0.24221 | 3027.625 | 0 | 0 | 64000 | 3027.625 | 0 | 6040.375 | -4802.125 | 1350000 | 6040.375 | 0
2021100201 | 7 | 0.46032 | 69048 | 0.25527 | 0 | 0.24611 | 3076.375 | 0 | 0 | 64000 | 3076.375 | 0 | 1971.625 | -4068.75 | 1350000 | 1971.625 | 0
2021100202 | 7 | 0.44068 | 66102 | 0.29358 | 0 | 0.26223 | 3277.875 | 0 | 0 | 64000 | 2102 | 0 | 0 | -1971.625 | 1350000 | 0 | 0
2021100203 | 7 | 0.42832 | 64248 | 0.33127 | 0 | 0.26492 | 3311.5 | 0 | 0 | 64000 | 248 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100204 | 7 | 0.422 | 63300 | 0.39417 | 0 | 0.27353 | 3419.125 | 0 | 0 | 63300 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100205 | 7 | 0.42155 | 63232.5 | 0.42553 | 0 | 0.26006 | 3250.75 | 0 | 0 | 63232.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100206 | 7 | 0.42812 | 64218 | 0.39062 | 0 | 0.29412 | 3676.5 | 0 | 0 | 64000 | 218 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100207 | 7 | 0.44306 | 66459 | 0.37314 | 0 | 0.35712 | 4464 | 0.00638 | 510.4 | 64000 | 2459 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100208 | 7 | 0.45905 | 68857.5 | 0.34187 | 0 | 0.40776 | 5097 | 0.08963 | 7170.4 | 64000 | 4857.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100209 | 7 | 0.47352 | 71028 | 0.33617 | 0 | 0.47439 | 5929.875 | 0.18662 | 14929.6 | 64000 | 5929.875 | 1098.125 | 0 | 0 | 1350000 | 0 | 0
2021100210 | 7 | 0.48873 | 73309.5 | 0.20641 | 0 | 0.50013 | 6251.625 | 0.27041 | 21632.8 | 64000 | 6251.625 | 3057.875 | 0 | 0 | 1350000 | 0 | 0
2021100211 | 7 | 0.50102 | 75153 | 0.11219 | 0 | 0.5254 | 6567.5 | 0.36054 | 28843.2 | 64000 | 6567.5 | 4585.5 | 0 | 0 | 1350000 | 0 | 0
2021100212 | 7 | 0.51257 | 76885.5 | 0.07912 | 0 | 0.55247 | 6905.875 | 0.44101 | 35280.8 | 64000 | 6905.875 | 5979.625 | 0 | 0 | 1350000 | 0 | 0
2021100213 | 7 | 0.52581 | 78871.5 | 0.07579 | 0 | 0.56002 | 7000.25 | 0.44487 | 35589.6 | 64000 | 7000.25 | 7871.25 | 0 | 0 | 1350000 | 0 | 0
2021100214 | 7 | 0.53742 | 80613 | 0.0562 | 0 | 0.55492 | 6936.5 | 0.4266 | 34128 | 64000 | 6936.5 | 9676.5 | 0 | 0 | 1350000 | 0 | 0
2021100215 | 7 | 0.5504 | 82560 | 0.05469 | 0 | 0.55316 | 6914.5 | 0.32972 | 26377.6 | 64000 | 6914.5 | 11645.5 | 0 | 0 | 1350000 | 0 | 0
2021100216 | 7 | 0.56329 | 84493.5 | 0.04677 | 0 | 0.58931 | 7366.375 | 0.24354 | 19483.2 | 64000 | 7366.375 | 13127.125 | 0 | 0 | 1350000 | 0 | 0
2021100217 | 7 | 0.57483 | 86224.5 | 0.04453 | 0 | 0.60934 | 7616.75 | 0.16001 | 12800.8 | 64000 | 7616.75 | 12800.8 | 1806.95 | 1806.95 | 1350000 | 1806.95 | 0
2021100218 | 7 | 0.57867 | 86800.5 | 0.06438 | 0 | 0.50596 | 6324.5 | 0.0638 | 5104 | 64000 | 6324.5 | 5104 | 11372 | 9565.05 | 1350000 | 11372 | 0
2021100219 | 7 | 0.574 | 86100 | 0.15031 | 0 | 0.49958 | 6244.75 | 0.00627 | 501.6 | 64000 | 6244.75 | 501.6 | 15353.65 | 3981.65 | 1350000 | 15353.65 | 0
2021100220 | 7 | 0.57591 | 86386.5 | 0.27441 | 0 | 0.50497 | 6312.125 | 0 | 0 | 64000 | 6312.125 | 0 | 16074.375 | 720.725 | 1350000 | 16074.375 | 0
2021100221 | 7 | 0.56409 | 84613.5 | 0.40457 | 0 | 0.47947 | 5993.375 | 0 | 0 | 64000 | 5993.375 | 0 | 14620.125 | -1454.25 | 1350000 | 14620.125 | 0
2021100222 | 7 | 0.54369 | 81553.5 | 0.52727 | 0 | 0.46641 | 5830.125 | 0 | 0 | 64000 | 5830.125 | 0 | 11723.375 | -2896.75 | 1350000 | 11723.375 | 0
2021100223 | 7 | 0.51863 | 77794.5 | 0.56726 | 0 | 0.51323 | 6415.375 | 0 | 0 | 64000 | 6415.375 | 0 | 7379.125 | -4344.25 | 1350000 | 7379.125 | 0
2021100224 | 7 | 0.49083 | 73624.5 | 0.62263 | 0 | 0.56221 | 7027.625 | 0 | 0 | 64000 | 7027.625 | 0 | 2596.875 | -4782.25 | 1350000 | 2596.875 | 0
2021100301 | 1 | 0.46464 | 69696 | 0.66148 | 0 | 0.58263 | 7282.875 | 0 | 0 | 64000 | 5696 | 0 | 0 | -2596.875 | 1350000 | 0 | 0
2021100302 | 1 | 0.44637 | 66955.5 | 0.62925 | 0 | 0.61169 | 7646.125 | 0 | 0 | 64000 | 2955.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100303 | 1 | 0.43358 | 65037 | 0.58809 | 0 | 0.65546 | 8193.25 | 0 | 0 | 64000 | 1037 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100304 | 1 | 0.42542 | 63813 | 0.56236 | 0 | 0.70959 | 8869.875 | 0 | 0 | 63813 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100305 | 1 | 0.4221 | 63315 | 0.54862 | 0 | 0.75875 | 9484.375 | 0 | 0 | 63315 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100306 | 1 | 0.42485 | 63727.5 | 0.48684 | 0 | 0.7776 | 9720 | 0 | 0 | 63727.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100307 | 1 | 0.43511 | 65266.5 | 0.4685 | 0 | 0.75187 | 9398.375 | 0.00372 | 297.6 | 64000 | 1266.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100308 | 1 | 0.44692 | 67038 | 0.43755 | 0 | 0.72052 | 9006.5 | 0.02049 | 1639.2 | 64000 | 3038 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100309 | 1 | 0.46644 | 69966 | 0.41039 | 0 | 0.71436 | 8929.5 | 0.06016 | 4812.8 | 64000 | 5966 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100310 | 1 | 0.48795 | 73192.5 | 0.40281 | 0 | 0.71675 | 8959.375 | 0.11843 | 9474.4 | 64000 | 8959.375 | 233.125 | 0 | 0 | 1350000 | 0 | 0
2021100311 | 1 | 0.50905 | 76357.5 | 0.29219 | 0 | 0.71078 | 8884.75 | 0.15821 | 12656.8 | 64000 | 8884.75 | 3472.75 | 0 | 0 | 1350000 | 0 | 0
2021100312 | 1 | 0.5301 | 79515 | 0.25432 | 0 | 0.69505 | 8688.125 | 0.22103 | 17682.4 | 64000 | 8688.125 | 6826.875 | 0 | 0 | 1350000 | 0 | 0
2021100313 | 1 | 0.55384 | 83076 | 0.28659 | 0 | 0.66653 | 8331.625 | 0.27249 | 21799.2 | 64000 | 8331.625 | 10744.375 | 0 | 0 | 1350000 | 0 | 0
2021100314 | 1 | 0.57419 | 86128.5 | 0.26285 | 0 | 0.66329 | 8291.125 | 0.3114 | 24912 | 64000 | 8291.125 | 13837.375 | 0 | 0 | 1350000 | 0 | 0
2021100315 | 1 | 0.58868 | 88302 | 0.25367 | 0 | 0.64671 | 8083.875 | 0.3159 | 25272 | 64000 | 8083.875 | 16218.125 | 0 | 0 | 1350000 | 0 | 0
2021100316 | 1 | 0.60138 | 90207 | 0.19601 | 0 | 0.62878 | 7859.75 | 0.30911 | 24728.8 | 64000 | 7859.75 | 18347.25 | 0 | 0 | 1350000 | 0 | 0
2021100317 | 1 | 0.61372 | 92058 | 0.13602 | 0 | 0.55463 | 6932.875 | 0.28736 | 22988.8 | 64000 | 6932.875 | 21125.125 | 0 | 0 | 1350000 | 0 | 0
2021100318 | 1 | 0.62201 | 93301.5 | 0.13938 | 0 | 0.49599 | 6199.875 | 0.16005 | 12804 | 64000 | 6199.875 | 12804 | 10297.625 | 10297.625 | 1350000 | 10297.625 | 0
2021100319 | 1 | 0.62151 | 93226.5 | 0.15987 | 0 | 0.53795 | 6724.375 | 0.03562 | 2849.6 | 64000 | 6724.375 | 2849.6 | 19652.525 | 9354.9 | 1350000 | 19652.525 | 0
2021100320 | 1 | 0.62929 | 94393.5 | 0.28287 | 0 | 0.51409 | 6426.125 | 0 | 0 | 64000 | 6426.125 | 0 | 23967.375 | 4314.85 | 1350000 | 23967.375 | 0
2021100321 | 1 | 0.61634 | 92451 | 0.32965 | 0 | 0.58849 | 7356.125 | 0 | 0 | 64000 | 7356.125 | 0 | 21094.875 | -2872.5 | 1350000 | 21094.875 | 0
2021100322 | 1 | 0.58801 | 88201.5 | 0.29261 | 0 | 0.63461 | 7932.625 | 0 | 0 | 64000 | 7932.625 | 0 | 16268.875 | -4826 | 1350000 | 16268.875 | 0
2021100323 | 1 | 0.55481 | 83221.5 | 0.34198 | 0 | 0.68037 | 8504.625 | 0 | 0 | 64000 | 8504.625 | 0 | 10716.875 | -5552 | 1350000 | 10716.875 | 0
2021100324 | 1 | 0.52094 | 78141 | 0.33013 | 0 | 0.70184 | 8773 | 0 | 0 | 64000 | 8773 | 0 | 5368 | -5348.875 | 1350000 | 5368 | 0
2021100401 | 2 | 0.49379 | 74068.5 | 0.3176 | 0 | 0.69652 | 8706.5 | 0 | 0 | 64000 | 8706.5 | 0 | 1362 | -4006 | 1350000 | 1362 | 0
2021100402 | 2 | 0.47539 | 71308.5 | 0.31505 | 0 | 0.64535 | 8066.875 | 0 | 0 | 64000 | 7308.5 | 0 | 0 | -1362 | 1350000 | 0 | 0
2021100403 | 2 | 0.463 | 69450 | 0.28569 | 0 | 0.69315 | 8664.375 | 0 | 0 | 64000 | 5450 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100404 | 2 | 0.4581 | 68715 | 0.26617 | 0 | 0.70428 | 8803.5 | 0 | 0 | 64000 | 4715 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100405 | 2 | 0.46313 | 69469.5 | 0.27384 | 0 | 0.6843 | 8553.75 | 0 | 0 | 64000 | 5469.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100406 | 2 | 0.4881 | 73215 | 0.1761 | 0 | 0.70782 | 8847.75 | 0 | 0 | 64000 | 8847.75 | 0 | 367.25 | 367.25 | 1350000 | 367.25 | 0
2021100407 | 2 | 0.53464 | 80196 | 0.12589 | 0 | 0.64597 | 8074.625 | 0.00629 | 503.2 | 64000 | 8074.625 | 503.2 | 7618.175 | 7250.925 | 1350000 | 7618.175 | 0
2021100408 | 2 | 0.56838 | 85257 | 0.08793 | 0 | 0.64698 | 8087.25 | 0.14214 | 11371.2 | 64000 | 8087.25 | 11371.2 | 1798.55 | -5819.625 | 1350000 | 1798.55 | 0
2021100409 | 2 | 0.58711 | 88066.5 | 0.06468 | 0 | 0.63857 | 7982.125 | 0.38361 | 30688.8 | 64000 | 7982.125 | 16084.375 | 0 | -1798.55 | 1350000 | 0 | 0
2021100410 | 2 | 0.6018 | 90270 | 0.04452 | 0 | 0.69624 | 8703 | 0.50907 | 40725.6 | 64000 | 8703 | 17567 | 0 | 0 | 1350000 | 0 | 0
2021100411 | 2 | 0.6174 | 92610 | 0.04504 | 0 | 0.72032 | 9004 | 0.56503 | 45202.4 | 64000 | 9004 | 19606 | 0 | 0 | 1350000 | 0 | 0
2021100412 | 2 | 0.63313 | 94969.5 | 0.05138 | 0 | 0.72616 | 9077 | 0.5825 | 46600 | 64000 | 9077 | 21892.5 | 0 | 0 | 1350000 | 0 | 0
2021100413 | 2 | 0.65107 | 97660.5 | 0.02326 | 0 | 0.73018 | 9127.25 | 0.58151 | 46520.8 | 64000 | 9127.25 | 24533.25 | 0 | 0 | 1350000 | 0 | 0
2021100414 | 2 | 0.66837 | 100255.5 | 0.03859 | 0 | 0.72766 | 9095.75 | 0.5861 | 46888 | 64000 | 9095.75 | 27159.75 | 0 | 0 | 1350000 | 0 | 0
2021100415 | 2 | 0.67979 | 101968.5 | 0.05717 | 0 | 0.72246 | 9030.75 | 0.58869 | 47095.2 | 64000 | 9030.75 | 28937.75 | 0 | 0 | 1350000 | 0 | 0
2021100416 | 2 | 0.68725 | 103087.5 | 0.05059 | 0 | 0.71924 | 8990.5 | 0.56919 | 45535.2 | 64000 | 8990.5 | 30097 | 0 | 0 | 1350000 | 0 | 0
2021100417 | 2 | 0.69201 | 103801.5 | 0.03347 | 0 | 0.73192 | 9149 | 0.53237 | 42589.6 | 64000 | 9149 | 30652.5 | 0 | 0 | 1350000 | 0 | 0
2021100418 | 2 | 0.69111 | 103666.5 | 0.02117 | 0 | 0.7616 | 9520 | 0.35979 | 28783.2 | 64000 | 9520 | 28783.2 | 1363.3 | 1363.3 | 1350000 | 1363.3 | 0
2021100419 | 2 | 0.68103 | 102154.5 | 0.01132 | 0 | 0.75913 | 9489.125 | 0.0722 | 5776 | 64000 | 9489.125 | 5776 | 22889.375 | 21526.075 | 1350000 | 22889.375 | 0
2021100420 | 2 | 0.67859 | 101788.5 | 0.01228 | 0 | 0.76465 | 9558.125 | 0 | 0 | 64000 | 9558.125 | 0 | 28230.375 | 5341 | 1347235.875 | 28230.375 | 0
2021100421 | 2 | 0.6578 | 98670 | 0.02136 | 0 | 0.75942 | 9492.75 | 0 | 0 | 64000 | 9492.75 | 0 | 25177.25 | -3053.125 | 1347524.875 | 25177.25 | 0
2021100422 | 2 | 0.62233 | 93349.5 | 0.04134 | 0 | 0.7563 | 9453.75 | 0 | 0 | 64000 | 9453.75 | 0 | 19895.75 | -5281.5 | 1350000 | 19895.75 | 0
2021100423 | 2 | 0.58051 | 87076.5 | 0.03956 | 0 | 0.74718 | 9339.75 | 0 | 0 | 64000 | 9339.75 | 0 | 13736.75 | -6159 | 1350000 | 13736.75 | 0
2021100424 | 2 | 0.54087 | 81130.5 | 0.03661 | 0 | 0.746 | 9325 | 0 | 0 | 64000 | 9325 | 0 | 7805.5 | -5931.25 | 1350000 | 7805.5 | 0
2021100501 | 3 | 0.50799 | 76198.5 | 0.03064 | 0 | 0.74665 | 9333.125 | 0 | 0 | 64000 | 9333.125 | 0 | 2865.375 | -4940.125 | 1350000 | 2865.375 | 0
2021100502 | 3 | 0.48505 | 72757.5 | 0.03693 | 0 | 0.72405 | 9050.625 | 0 | 0 | 64000 | 8757.5 | 0 | 0 | -2865.375 | 1350000 | 0 | 0
2021100503 | 3 | 0.47064 | 70596 | 0.03587 | 0 | 0.68547 | 8568.375 | 0 | 0 | 64000 | 6596 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100504 | 3 | 0.4625 | 69375 | 0.01409 | 0 | 0.66454 | 8306.75 | 0 | 0 | 64000 | 5375 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100505 | 3 | 0.46614 | 69921 | 0.03495 | 0 | 0.64903 | 8112.875 | 0 | 0 | 64000 | 5921 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100506 | 3 | 0.48771 | 73156.5 | 0.01791 | 0 | 0.63094 | 7886.75 | 0 | 0 | 64000 | 7886.75 | 0 | 1269.75 | 1269.75 | 1350000 | 1269.75 | 0
2021100507 | 3 | 0.5323 | 79845 | 0.00834 | 0 | 0.61325 | 7665.625 | 0.00755 | 604 | 64000 | 7665.625 | 604 | 7575.375 | 6305.625 | 1350000 | 7575.375 | 0
2021100508 | 3 | 0.56449 | 84673.5 | 0.01564 | 0 | 0.62627 | 7828.375 | 0.17897 | 14317.6 | 64000 | 7828.375 | 12845.125 | 0 | -7575.375 | 1350000 | 0 | 0
2021100509 | 3 | 0.57926 | 86889 | 0.00254 | 0 | 0.61603 | 7700.375 | 0.44986 | 35988.8 | 64000 | 7700.375 | 15188.625 | 0 | 0 | 1350000 | 0 | 0
2021100510 | 3 | 0.59017 | 88525.5 | 0.0059 | 0 | 0.58747 | 7343.375 | 0.55158 | 44126.4 | 64000 | 7343.375 | 17182.125 | 0 | 0 | 1350000 | 0 | 0
2021100511 | 3 | 0.60395 | 90592.5 | 0.00763 | 0 | 0.54856 | 6857 | 0.59289 | 47431.2 | 64000 | 6857 | 19735.5 | 0 | 0 | 1350000 | 0 | 0
2021100512 | 3 | 0.62006 | 93009 | 0.00539 | 0 | 0.53167 | 6645.875 | 0.59899 | 47919.2 | 64000 | 6645.875 | 22363.125 | 0 | 0 | 1350000 | 0 | 0
2021100513 | 3 | 0.63478 | 95217 | 0.00497 | 0 | 0.54389 | 6798.625 | 0.60121 | 48096.8 | 64000 | 6798.625 | 24418.375 | 0 | 0 | 1350000 | 0 | 0
2021100514 | 3 | 0.64849 | 97273.5 | 0.00592 | 0 | 0.55371 | 6921.375 | 0.59367 | 47493.6 | 64000 | 6921.375 | 26352.125 | 0 | 0 | 1350000 | 0 | 0
2021100515 | 3 | 0.65692 | 98538 | 0.02076 | 0 | 0.54579 | 6822.375 | 0.57931 | 46344.8 | 64000 | 6822.375 | 27715.625 | 0 | 0 | 1350000 | 0 | 0
2021100516 | 3 | 0.66217 | 99325.5 | 0.0072 | 0 | 0.49017 | 6127.125 | 0.55109 | 44087.2 | 64000 | 6127.125 | 29198.375 | 0 | 0 | 1350000 | 0 | 0
2021100517 | 3 | 0.66583 | 99874.5 | 0.01165 | 0 | 0.48628 | 6078.5 | 0.50006 | 40004.8 | 64000 | 6078.5 | 29796 | 0 | 0 | 1350000 | 0 | 0
2021100518 | 3 | 0.66562 | 99843 | 0.02635 | 0 | 0.4942 | 6177.5 | 0.34281 | 27424.8 | 64000 | 6177.5 | 27424.8 | 2240.7 | 2240.7 | 1350000 | 2240.7 | 0
2021100519 | 3 | 0.65993 | 98989.5 | 0.06948 | 0 | 0.44742 | 5592.75 | 0.0633 | 5064 | 64000 | 5592.75 | 5064 | 24332.75 | 22092.05 | 1350000 | 24332.75 | 0
2021100520 | 3 | 0.6592 | 98880 | 0.11387 | 0 | 0.3782 | 4727.5 | 0 | 0 | 64000 | 4727.5 | 0 | 30152.5 | 5819.75 | 1345313.75 | 30152.5 | 0
2021100521 | 3 | 0.64108 | 96162 | 0.14878 | 0 | 0.31505 | 3938.125 | 0 | 0 | 64000 | 3938.125 | 0 | 28223.875 | -1928.625 | 1342556.125 | 28223.875 | 0
2021100522 | 3 | 0.61002 | 91503 | 0.17755 | 0 | 0.2717 | 3396.25 | 0 | 0 | 64000 | 3396.25 | 0 | 24106.75 | -4117.125 | 1343915.625 | 24106.75 | 0
2021100523 | 3 | 0.57067 | 85600.5 | 0.21396 | 0 | 0.24167 | 3020.875 | 0 | 0 | 64000 | 3020.875 | 0 | 18579.625 | -5527.125 | 1350000 | 18579.625 | 0
2021100524 | 3 | 0.53262 | 79893 | 0.23084 | 0 | 0.24078 | 3009.75 | 0 | 0 | 64000 | 3009.75 | 0 | 12883.25 | -5696.375 | 1350000 | 12883.25 | 0
2021100601 | 4 | 0.50134 | 75201 | 0.20523 | 0 | 0.29305 | 3663.125 | 0 | 0 | 64000 | 3663.125 | 0 | 7537.875 | -5345.375 | 1350000 | 7537.875 | 0
2021100602 | 4 | 0.481 | 72150 | 0.15495 | 0 | 0.34969 | 4371.125 | 0 | 0 | 64000 | 4371.125 | 0 | 3778.875 | -3759 | 1350000 | 3778.875 | 0
2021100603 | 4 | 0.4675 | 70125 | 0.12741 | 0 | 0.40481 | 5060.125 | 0 | 0 | 64000 | 5060.125 | 0 | 1064.875 | -2714 | 1350000 | 1064.875 | 0
2021100604 | 4 | 0.46244 | 69366 | 0.0904 | 0 | 0.46047 | 5755.875 | 0 | 0 | 64000 | 5366 | 0 | 0 | -1064.875 | 1350000 | 0 | 0
2021100605 | 4 | 0.46614 | 69921 | 0.05155 | 0 | 0.51851 | 6481.375 | 0 | 0 | 64000 | 5921 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100606 | 4 | 0.48976 | 73464 | 0.0497 | 0 | 0.60441 | 7555.125 | 0 | 0 | 64000 | 7555.125 | 0 | 1908.875 | 1908.875 | 1350000 | 1908.875 | 0
2021100607 | 4 | 0.53385 | 80077.5 | 0.05868 | 0 | 0.72729 | 9091.125 | 0.00171 | 136.8 | 64000 | 9091.125 | 136.8 | 6849.575 | 4940.7 | 1350000 | 6849.575 | 0
2021100608 | 4 | 0.56804 | 85206 | 0.03661 | 0 | 0.79991 | 9998.875 | 0.03472 | 2777.6 | 64000 | 9998.875 | 2777.6 | 8429.525 | 1579.95 | 1350000 | 8429.525 | 0
2021100609 | 4 | 0.58224 | 87336 | 0.03381 | 0 | 0.82332 | 10291.5 | 0.08897 | 7117.6 | 64000 | 10291.5 | 7117.6 | 5926.9 | -2502.625 | 1350000 | 5926.9 | 0
2021100610 | 4 | 0.59491 | 89236.5 | 0.03507 | 0 | 0.81826 | 10228.25 | 0.17897 | 14317.6 | 64000 | 10228.25 | 14317.6 | 690.65 | -5236.25 | 1350000 | 690.65 | 0
2021100611 | 4 | 0.60616 | 90924 | 0.04329 | 0 | 0.83103 | 10387.875 | 0.20052 | 16041.6 | 64000 | 10387.875 | 16041.6 | 494.525 | -196.125 | 1350000 | 494.525 | 0
2021100612 | 4 | 0.61629 | 92443.5 | 0.02893 | 0 | 0.8165 | 10206.25 | 0.23956 | 19164.8 | 64000 | 10206.25 | 18237.25 | 0 | -494.525 | 1350000 | 0 | 0
2021100613 | 4 | 0.62716 | 94074 | 0.03056 | 0 | 0.79171 | 9896.375 | 0.27195 | 21756 | 64000 | 9896.375 | 20177.625 | 0 | 0 | 1350000 | 0 | 0
2021100614 | 4 | 0.63747 | 95620.5 | 0.02574 | 0 | 0.78741 | 9842.625 | 0.26133 | 20906.4 | 64000 | 9842.625 | 20906.4 | 871.475 | 871.475 | 1350000 | 871.475 | 0
2021100615 | 4 | 0.64044 | 96066 | 0.02534 | 0 | 0.7952 | 9940 | 0.24679 | 19743.2 | 64000 | 9940 | 19743.2 | 2382.8 | 1511.325 | 1350000 | 2382.8 | 0
2021100616 | 4 | 0.64317 | 96475.5 | 0.02566 | 0 | 0.79363 | 9920.375 | 0.18426 | 14740.8 | 64000 | 9920.375 | 14740.8 | 7814.325 | 5431.525 | 1350000 | 7814.325 | 0
2021100617 | 4 | 0.64592 | 96888 | 0.0326 | 0 | 0.77068 | 9633.5 | 0.0863 | 6904 | 64000 | 9633.5 | 6904 | 16350.5 | 8536.175 | 1350000 | 16350.5 | 0
2021100618 | 4 | 0.647 | 97050 | 0.05076 | 0 | 0.73811 | 9226.375 | 0.02369 | 1895.2 | 64000 | 9226.375 | 1895.2 | 21928.425 | 5577.925 | 1350000 | 21928.425 | 0
2021100619 | 4 | 0.64685 | 97027.5 | 0.07405 | 0 | 0.69568 | 8696 | 0.00286 | 228.8 | 64000 | 8696 | 228.8 | 24102.7 | 2174.275 | 1350000 | 24102.7 | 0
2021100620 | 4 | 0.65107 | 97660.5 | 0.10752 | 0 | 0.70472 | 8809 | 0 | 0 | 64000 | 8809 | 0 | 24851.5 | 748.8 | 1350000 | 24851.5 | 0
2021100621 | 4 | 0.63525 | 95287.5 | 0.13302 | 0 | 0.63731 | 7966.375 | 0 | 0 | 64000 | 7966.375 | 0 | 23321.125 | -1530.375 | 1350000 | 23321.125 | 0
2021100622 | 4 | 0.60563 | 90844.5 | 0.19869 | 0 | 0.61848 | 7731 | 0 | 0 | 64000 | 7731 | 0 | 19113.5 | -4207.625 | 1350000 | 19113.5 | 0
2021100623 | 4 | 0.56828 | 85242 | 0.23305 | 0 | 0.56337 | 7042.125 | 0 | 0 | 64000 | 7042.125 | 0 | 14199.875 | -4913.625 | 1350000 | 14199.875 | 0
2021100624 | 4 | 0.53118 | 79677 | 0.1917 | 0 | 0.54123 | 6765.375 | 0 | 0 | 64000 | 6765.375 | 0 | 8911.625 | -5288.25 | 1350000 | 8911.625 | 0
2021100701 | 5 | 0.49979 | 74968.5 | 0.14054 | 0 | 0.50658 | 6332.25 | 0 | 0 | 64000 | 6332.25 | 0 | 4636.25 | -4275.375 | 1350000 | 4636.25 | 0
2021100702 | 5 | 0.47985 | 71977.5 | 0.12813 | 0 | 0.47412 | 5926.5 | 0 | 0 | 64000 | 5926.5 | 0 | 2051 | -2585.25 | 1350000 | 2051 | 0
2021100703 | 5 | 0.46737 | 70105.5 | 0.09687 | 0 | 0.46804 | 5850.5 | 0 | 0 | 64000 | 5850.5 | 0 | 255 | -1796 | 1350000 | 255 | 0
2021100704 | 5 | 0.45983 | 68974.5 | 0.0726 | 0 | 0.45004 | 5625.5 | 0 | 0 | 64000 | 4974.5 | 0 | 0 | -255 | 1350000 | 0 | 0
2021100705 | 5 | 0.46307 | 69460.5 | 0.06918 | 0 | 0.37664 | 4708 | 0 | 0 | 64000 | 4708 | 0 | 752.5 | 752.5 | 1350000 | 752.5 | 0
2021100706 | 5 | 0.48647 | 72970.5 | 0.07259 | 0 | 0.37063 | 4632.875 | 0 | 0 | 64000 | 4632.875 | 0 | 4337.625 | 3585.125 | 1350000 | 4337.625 | 0
2021100707 | 5 | 0.52979 | 79468.5 | 0.06075 | 0 | 0.3931 | 4913.75 | 0.00208 | 166.4 | 64000 | 4913.75 | 166.4 | 10388.35 | 6050.725 | 1350000 | 10388.35 | 0
2021100708 | 5 | 0.56315 | 84472.5 | 0.0583 | 0 | 0.32133 | 4016.625 | 0.03012 | 2409.6 | 64000 | 4016.625 | 2409.6 | 14046.275 | 3657.925 | 1350000 | 14046.275 | 0
2021100709 | 5 | 0.57708 | 86562 | 0.05926 | 0 | 0.30094 | 3761.75 | 0.07878 | 6302.4 | 64000 | 3761.75 | 6302.4 | 12497.85 | -1548.425 | 1350000 | 12497.85 | 0
2021100710 | 5 | 0.58962 | 88443 | 0.05118 | 0 | 0.35205 | 4400.625 | 0.17793 | 14234.4 | 64000 | 4400.625 | 14234.4 | 5807.975 | -6689.875 | 1350000 | 5807.975 | 0
2021100711 | 5 | 0.6028 | 90420 | 0.01951 | 0 | 0.41614 | 5201.75 | 0.34843 | 27874.4 | 64000 | 5201.75 | 21218.25 | 0 | -5807.975 | 1350000 | 0 | 0
2021100712 | 5 | 0.6131 | 91965 | 0.01559 | 0 | 0.45208 | 5651 | 0.46805 | 37444 | 64000 | 5651 | 22314 | 0 | 0 | 1350000 | 0 | 0
2021100713 | 5 | 0.62482 | 93723 | 0.0077 | 0 | 0.3904 | 4880 | 0.51823 | 41458.4 | 64000 | 4880 | 24843 | 0 | 0 | 1350000 | 0 | 0
2021100714 | 5 | 0.63793 | 95689.5 | 0.00149 | 0 | 0.43467 | 5433.375 | 0.5416 | 43328 | 64000 | 5433.375 | 26256.125 | 0 | 0 | 1350000 | 0 | 0
2021100715 | 5 | 0.64778 | 97167 | 0.01113 | 0 | 0.45575 | 5696.875 | 0.53239 | 42591.2 | 64000 | 5696.875 | 27470.125 | 0 | 0 | 1350000 | 0 | 0
2021100716 | 5 | 0.65351 | 98026.5 | 0.03314 | 0 | 0.44282 | 5535.25 | 0.50321 | 40256.8 | 64000 | 5535.25 | 28491.25 | 0 | 0 | 1350000 | 0 | 0
2021100717 | 5 | 0.6578 | 98670 | 0.05608 | 0 | 0.35982 | 4497.75 | 0.43776 | 35020.8 | 64000 | 4497.75 | 30172.25 | 0 | 0 | 1350000 | 0 | 0
2021100718 | 5 | 0.65571 | 98356.5 | 0.06759 | 0 | 0.38902 | 4862.75 | 0.26102 | 20881.6 | 64000 | 4862.75 | 20881.6 | 8612.15 | 8612.15 | 1350000 | 8612.15 | 0
2021100719 | 5 | 0.64829 | 97243.5 | 0.08723 | 0 | 0.33318 | 4164.75 | 0.0449 | 3592 | 64000 | 4164.75 | 3592 | 25486.75 | 16874.6 | 1349979.5 | 25486.75 | 0
2021100720 | 5 | 0.65131 | 97696.5 | 0.11553 | 0 | 0.28221 | 3527.625 | 0 | 0 | 64000 | 3527.625 | 0 | 30168.875 | 4682.125 | 1345276.875 | 30168.875 | 0
2021100721 | 5 | 0.6348 | 95220 | 0.12134 | 0 | 0.24668 | 3083.5 | 0 | 0 | 64000 | 3083.5 | 0 | 28136.5 | -2032.375 | 1342606.625 | 28136.5 | 0
2021100722 | 5 | 0.60448 | 90672 | 0.15331 | 0 | 0.2094 | 2617.5 | 0 | 0 | 64000 | 2617.5 | 0 | 24054.5 | -4082 | 1344018.375 | 24054.5 | 0
2021100723 | 5 | 0.56584 | 84876 | 0.11518 | 0 | 0.18406 | 2300.75 | 0 | 0 | 64000 | 2300.75 | 0 | 18575.25 | -5479.25 | 1350000 | 18575.25 | 0
2021100724 | 5 | 0.52722 | 79083 | 0.06475 | 0 | 0.16955 | 2119.375 | 0 | 0 | 64000 | 2119.375 | 0 | 12963.625 | -5611.625 | 1350000 | 12963.625 | 0
2021100801 | 6 | 0.49718 | 74577 | 0.07263 | 0 | 0.16771 | 2096.375 | 0 | 0 | 64000 | 2096.375 | 0 | 8480.625 | -4483 | 1350000 | 8480.625 | 0
2021100802 | 6 | 0.47533 | 71299.5 | 0.05876 | 0 | 0.16842 | 2105.25 | 0 | 0 | 64000 | 2105.25 | 0 | 5194.25 | -3286.375 | 1350000 | 5194.25 | 0
2021100803 | 6 | 0.46167 | 69250.5 | 0.05884 | 0 | 0.14016 | 1752 | 0 | 0 | 64000 | 1752 | 0 | 3498.5 | -1695.75 | 1350000 | 3498.5 | 0
2021100804 | 6 | 0.45431 | 68146.5 | 0.06758 | 0 | 0.11949 | 1493.625 | 0 | 0 | 64000 | 1493.625 | 0 | 2652.875 | -845.625 | 1350000 | 2652.875 | 0
2021100805 | 6 | 0.45821 | 68731.5 | 0.07798 | 0 | 0.10544 | 1318 | 0 | 0 | 64000 | 1318 | 0 | 3413.5 | 760.625 | 1350000 | 3413.5 | 0
2021100806 | 6 | 0.47951 | 71926.5 | 0.06092 | 0 | 0.0998 | 1247.5 | 0 | 0 | 64000 | 1247.5 | 0 | 6679 | 3265.5 | 1350000 | 6679 | 0
2021100807 | 6 | 0.51909 | 77863.5 | 0.07247 | 0 | 0.12223 | 1527.875 | 0.00225 | 180 | 64000 | 1527.875 | 180 | 12155.625 | 5476.625 | 1350000 | 12155.625 | 0
2021100808 | 6 | 0.54975 | 82462.5 | 0.09862 | 0 | 0.16257 | 2032.125 | 0.11467 | 9173.6 | 64000 | 2032.125 | 9173.6 | 7256.775 | -4898.85 | 1350000 | 7256.775 | 0
2021100809 | 6 | 0.56505 | 84757.5 | 0.09051 | 0 | 0.19947 | 2493.375 | 0.34998 | 27998.4 | 64000 | 2493.375 | 18264.125 | 0 | -7256.775 | 1350000 | 0 | 0
2021100810 | 6 | 0.58174 | 87261 | 0.07942 | 0 | 0.22363 | 2795.375 | 0.42 | 33600 | 64000 | 2795.375 | 20465.625 | 0 | 0 | 1350000 | 0 | 0
2021100811 | 6 | 0.59771 | 89656.5 | 0.10397 | 0 | 0.22535 | 2816.875 | 0.45016 | 36012.8 | 64000 | 2816.875 | 22839.625 | 0 | 0 | 1350000 | 0 | 0
2021100812 | 6 | 0.61327 | 91990.5 | 0.0908 | 0 | 0.22348 | 2793.5 | 0.44177 | 35341.6 | 64000 | 2793.5 | 25197 | 0 | 0 | 1350000 | 0 | 0
2021100813 | 6 | 0.62878 | 94317 | 0.09711 | 0 | 0.21278 | 2659.75 | 0.42215 | 33772 | 64000 | 2659.75 | 27657.25 | 0 | 0 | 1350000 | 0 | 0
2021100814 | 6 | 0.64204 | 96306 | 0.0791 | 0 | 0.20615 | 2576.875 | 0.41451 | 33160.8 | 64000 | 2576.875 | 29729.125 | 0 | 0 | 1350000 | 0 | 0
2021100815 | 6 | 0.65119 | 97678.5 | 0.0754 | 0 | 0.20166 | 2520.75 | 0.35014 | 28011.2 | 64000 | 2520.75 | 28011.2 | 3146.55 | 3146.55 | 1350000 | 3146.55 | 0
2021100816 | 6 | 0.65313 | 97969.5 | 0.07351 | 0 | 0.21806 | 2725.75 | 0.28168 | 22534.4 | 64000 | 2725.75 | 22534.4 | 8709.35 | 5562.8 | 1350000 | 8709.35 | 0
2021100817 | 6 | 0.65108 | 97662 | 0.13139 | 0 | 0.30054 | 3756.75 | 0.21721 | 17376.8 | 64000 | 3756.75 | 17376.8 | 12528.45 | 3819.1 | 1350000 | 12528.45 | 0
2021100818 | 6 | 0.64485 | 96727.5 | 0.19168 | 0 | 0.35263 | 4407.875 | 0.11164 | 8931.2 | 64000 | 4407.875 | 8931.2 | 19388.425 | 6859.975 | 1350000 | 19388.425 | 0
2021100819 | 6 | 0.63323 | 94984.5 | 0.2745 | 0 | 0.40816 | 5102 | 0.01078 | 862.4 | 64000 | 5102 | 862.4 | 25020.1 | 5631.675 | 1350000 | 25020.1 | 0
2021100820 | 6 | 0.62736 | 94104 | 0.36062 | 0 | 0.43425 | 5428.125 | 9e-05 | 7.2 | 64000 | 5428.125 | 7.2 | 24668.675 | -351.425 | 1350000 | 24668.675 | 0
2021100821 | 6 | 0.61072 | 91608 | 0.41717 | 0 | 0.4958 | 6197.5 | 0 | 0 | 64000 | 6197.5 | 0 | 21410.5 | -3258.175 | 1350000 | 21410.5 | 0
2021100822 | 6 | 0.58567 | 87850.5 | 0.45783 | 0 | 0.53806 | 6725.75 | 0 | 0 | 64000 | 6725.75 | 0 | 17124.75 | -4285.75 | 1350000 | 17124.75 | 0
2021100823 | 6 | 0.55455 | 83182.5 | 0.45319 | 0 | 0.52537 | 6567.125 | 0 | 0 | 64000 | 6567.125 | 0 | 12615.375 | -4509.375 | 1350000 | 12615.375 | 0
2021100824 | 6 | 0.51923 | 77884.5 | 0.48674 | 0 | 0.51984 | 6498 | 0 | 0 | 64000 | 6498 | 0 | 7386.5 | -5228.875 | 1350000 | 7386.5 | 0
2021100901 | 7 | 0.4898 | 73470 | 0.45913 | 0 | 0.55768 | 6971 | 0 | 0 | 64000 | 6971 | 0 | 2499 | -4887.5 | 1350000 | 2499 | 0
2021100902 | 7 | 0.46755 | 70132.5 | 0.46619 | 0 | 0.64351 | 8043.875 | 0 | 0 | 64000 | 6132.5 | 0 | 0 | -2499 | 1350000 | 0 | 0
2021100903 | 7 | 0.45258 | 67887 | 0.53677 | 0 | 0.7288 | 9110 | 0 | 0 | 64000 | 3887 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100904 | 7 | 0.44424 | 66636 | 0.58756 | 0 | 0.73151 | 9143.875 | 0 | 0 | 64000 | 2636 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100905 | 7 | 0.44148 | 66222 | 0.53161 | 0 | 0.68273 | 8534.125 | 0 | 0 | 64000 | 2222 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100906 | 7 | 0.44726 | 67089 | 0.60345 | 0 | 0.58515 | 7314.375 | 0 | 0 | 64000 | 3089 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100907 | 7 | 0.46043 | 69064.5 | 0.6628 | 0 | 0.52293 | 6536.625 | 0.00052 | 41.6 | 64000 | 5064.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021100908 | 7 | 0.4796 | 71940 | 0.63744 | 0 | 0.43452 | 5431.5 | 0.04506 | 3604.8 | 64000 | 5431.5 | 2508.5 | 0 | 0 | 1350000 | 0 | 0
2021100909 | 7 | 0.49806 | 74709 | 0.72568 | 0 | 0.30384 | 3798 | 0.09367 | 7493.6 | 64000 | 3798 | 6911 | 0 | 0 | 1350000 | 0 | 0
2021100910 | 7 | 0.51946 | 77919 | 0.78611 | 0 | 0.26699 | 3337.375 | 0.15577 | 12461.6 | 64000 | 3337.375 | 10581.625 | 0 | 0 | 1350000 | 0 | 0
2021100911 | 7 | 0.53656 | 80484 | 0.76379 | 0 | 0.18599 | 2324.875 | 0.23365 | 18692 | 64000 | 2324.875 | 14159.125 | 0 | 0 | 1350000 | 0 | 0
2021100912 | 7 | 0.54881 | 82321.5 | 0.73135 | 0 | 0.15729 | 1966.125 | 0.28233 | 22586.4 | 64000 | 1966.125 | 16355.375 | 0 | 0 | 1350000 | 0 | 0
2021100913 | 7 | 0.56074 | 84111 | 0.69611 | 0 | 0.15229 | 1903.625 | 0.32013 | 25610.4 | 64000 | 1903.625 | 18207.375 | 0 | 0 | 1350000 | 0 | 0
2021100914 | 7 | 0.57026 | 85539 | 0.62091 | 0 | 0.14846 | 1855.75 | 0.31074 | 24859.2 | 64000 | 1855.75 | 19683.25 | 0 | 0 | 1350000 | 0 | 0
2021100915 | 7 | 0.57679 | 86518.5 | 0.58484 | 0 | 0.11051 | 1381.375 | 0.28892 | 23113.6 | 64000 | 1381.375 | 21137.125 | 0 | 0 | 1350000 | 0 | 0
2021100916 | 7 | 0.58259 | 87388.5 | 0.54889 | 0 | 0.07463 | 932.875 | 0.24724 | 19779.2 | 64000 | 932.875 | 19779.2 | 2676.425 | 2676.425 | 1350000 | 2676.425 | 0
2021100917 | 7 | 0.58778 | 88167 | 0.55892 | 0 | 0.0664 | 830 | 0.20525 | 16420 | 64000 | 830 | 16420 | 6917 | 4240.575 | 1350000 | 6917 | 0
2021100918 | 7 | 0.58761 | 88141.5 | 0.51645 | 0 | 0.0647 | 808.75 | 0.12676 | 10140.8 | 64000 | 808.75 | 10140.8 | 13191.95 | 6274.95 | 1350000 | 13191.95 | 0
2021100919 | 7 | 0.58325 | 87487.5 | 0.47895 | 0 | 0.05467 | 683.375 | 0.0219 | 1752 | 64000 | 683.375 | 1752 | 21052.125 | 7860.175 | 1350000 | 21052.125 | 0
2021100920 | 7 | 0.58378 | 87567 | 0.46805 | 0 | 0.02837 | 354.625 | 0 | 0 | 64000 | 354.625 | 0 | 23212.375 | 2160.25 | 1350000 | 23212.375 | 0
2021100921 | 7 | 0.57035 | 85552.5 | 0.55747 | 0 | 0.04334 | 541.75 | 0 | 0 | 64000 | 541.75 | 0 | 21010.75 | -2201.625 | 1350000 | 21010.75 | 0
2021100922 | 7 | 0.55014 | 82521 | 0.57385 | 0 | 0.08331 | 1041.375 | 0 | 0 | 64000 | 1041.375 | 0 | 17479.625 | -3531.125 | 1350000 | 17479.625 | 0
2021100923 | 7 | 0.52473 | 78709.5 | 0.61475 | 0 | 0.11885 | 1485.625 | 0 | 0 | 64000 | 1485.625 | 0 | 13223.875 | -4255.75 | 1350000 | 13223.875 | 0
2021100924 | 7 | 0.49776 | 74664 | 0.61371 | 0 | 0.19943 | 2492.875 | 0 | 0 | 64000 | 2492.875 | 0 | 8171.125 | -5052.75 | 1350000 | 8171.125 | 0
2021101001 | 1 | 0.47187 | 70780.5 | 0.65006 | 0 | 0.22602 | 2825.25 | 0 | 0 | 64000 | 2825.25 | 0 | 3955.25 | -4215.875 | 1350000 | 3955.25 | 0
2021101002 | 1 | 0.45348 | 68022 | 0.56376 | 0 | 0.24826 | 3103.25 | 0 | 0 | 64000 | 3103.25 | 0 | 918.75 | -3036.5 | 1350000 | 918.75 | 0
2021101003 | 1 | 0.44051 | 66076.5 | 0.49116 | 0 | 0.29702 | 3712.75 | 0 | 0 | 64000 | 2076.5 | 0 | 0 | -918.75 | 1350000 | 0 | 0
2021101004 | 1 | 0.43204 | 64806 | 0.3777 | 0 | 0.39592 | 4949 | 0 | 0 | 64000 | 806 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101005 | 1 | 0.42907 | 64360.5 | 0.32362 | 0 | 0.47406 | 5925.75 | 0 | 0 | 64000 | 360.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101006 | 1 | 0.43271 | 64906.5 | 0.32791 | 0 | 0.53953 | 6744.125 | 0 | 0 | 64000 | 906.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101007 | 1 | 0.44275 | 66412.5 | 0.32115 | 0 | 0.60366 | 7545.75 | 0.00273 | 218.4 | 64000 | 2412.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101008 | 1 | 0.45678 | 68517 | 0.30666 | 0 | 0.658 | 8225 | 0.04856 | 3884.8 | 64000 | 4517 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101009 | 1 | 0.47612 | 71418 | 0.30251 | 0 | 0.68889 | 8611.125 | 0.09571 | 7656.8 | 64000 | 7418 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101010 | 1 | 0.50049 | 75073.5 | 0.28967 | 0 | 0.70057 | 8757.125 | 0.09573 | 7658.4 | 64000 | 8757.125 | 2316.375 | 0 | 0 | 1350000 | 0 | 0
2021101011 | 1 | 0.52031 | 78046.5 | 0.26187 | 0 | 0.68752 | 8594 | 0.11195 | 8956 | 64000 | 8594 | 5452.5 | 0 | 0 | 1350000 | 0 | 0
2021101012 | 1 | 0.53708 | 80562 | 0.23926 | 0 | 0.68063 | 8507.875 | 0.14679 | 11743.2 | 64000 | 8507.875 | 8054.125 | 0 | 0 | 1350000 | 0 | 0
2021101013 | 1 | 0.55174 | 82761 | 0.20549 | 0 | 0.68947 | 8618.375 | 0.16022 | 12817.6 | 64000 | 8618.375 | 10142.625 | 0 | 0 | 1350000 | 0 | 0
2021101014 | 1 | 0.56173 | 84259.5 | 0.1921 | 0 | 0.68538 | 8567.25 | 0.16666 | 13332.8 | 64000 | 8567.25 | 11692.25 | 0 | 0 | 1350000 | 0 | 0
2021101015 | 1 | 0.57037 | 85555.5 | 0.25781 | 0 | 0.65658 | 8207.25 | 0.14253 | 11402.4 | 64000 | 8207.25 | 11402.4 | 1945.85 | 1945.85 | 1350000 | 1945.85 | 0
2021101016 | 1 | 0.58124 | 87186 | 0.23425 | 0 | 0.62344 | 7793 | 0.144 | 11520 | 64000 | 7793 | 11520 | 3873 | 1927.15 | 1350000 | 3873 | 0
2021101017 | 1 | 0.59252 | 88878 | 0.23972 | 0 | 0.60872 | 7609 | 0.08409 | 6727.2 | 64000 | 7609 | 6727.2 | 10541.8 | 6668.8 | 1350000 | 10541.8 | 0
2021101018 | 1 | 0.6027 | 90405 | 0.26021 | 0 | 0.61602 | 7700.25 | 0.03688 | 2950.4 | 64000 | 7700.25 | 2950.4 | 15754.35 | 5212.55 | 1350000 | 15754.35 | 0
2021101019 | 1 | 0.60416 | 90624 | 0.26298 | 0 | 0.58086 | 7260.75 | 0.00308 | 246.4 | 64000 | 7260.75 | 246.4 | 19116.85 | 3362.5 | 1350000 | 19116.85 | 0
2021101020 | 1 | 0.60512 | 90768 | 0.38482 | 0 | 0.55625 | 6953.125 | 0 | 0 | 64000 | 6953.125 | 0 | 19814.875 | 698.025 | 1350000 | 19814.875 | 0
2021101021 | 1 | 0.592 | 88800 | 0.37799 | 0 | 0.52082 | 6510.25 | 0 | 0 | 64000 | 6510.25 | 0 | 18289.75 | -1525.125 | 1350000 | 18289.75 | 0
2021101022 | 1 | 0.56633 | 84949.5 | 0.39971 | 0 | 0.53644 | 6705.5 | 0 | 0 | 64000 | 6705.5 | 0 | 14244 | -4045.75 | 1350000 | 14244 | 0
2021101023 | 1 | 0.53597 | 80395.5 | 0.44425 | 0 | 0.56099 | 7012.375 | 0 | 0 | 64000 | 7012.375 | 0 | 9383.125 | -4860.875 | 1350000 | 9383.125 | 0
2021101024 | 1 | 0.50492 | 75738 | 0.45307 | 0 | 0.59086 | 7385.75 | 0 | 0 | 64000 | 7385.75 | 0 | 4352.25 | -5030.875 | 1350000 | 4352.25 | 0
2021101101 | 2 | 0.4782 | 71730 | 0.48197 | 0 | 0.69603 | 8700.375 | 0 | 0 | 64000 | 7730 | 0 | 0 | -4352.25 | 1350000 | 0 | 0
2021101102 | 2 | 0.45901 | 68851.5 | 0.48937 | 0 | 0.7381 | 9226.25 | 0 | 0 | 64000 | 4851.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101103 | 2 | 0.44872 | 67308 | 0.41236 | 0 | 0.75491 | 9436.375 | 0 | 0 | 64000 | 3308 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101104 | 2 | 0.44445 | 66667.5 | 0.28932 | 0 | 0.75897 | 9487.125 | 0 | 0 | 64000 | 2667.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101105 | 2 | 0.44975 | 67462.5 | 0.19418 | 0 | 0.71155 | 8894.375 | 0 | 0 | 64000 | 3462.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101106 | 2 | 0.47253 | 70879.5 | 0.16873 | 0 | 0.68381 | 8547.625 | 0 | 0 | 64000 | 6879.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101107 | 2 | 0.51135 | 76702.5 | 0.14981 | 0 | 0.64296 | 8037 | 0.00023 | 18.4 | 64000 | 8037 | 18.4 | 4647.1 | 4647.1 | 1350000 | 4647.1 | 0
2021101108 | 2 | 0.54269 | 81403.5 | 0.14596 | 0 | 0.65476 | 8184.5 | 0.02887 | 2309.6 | 64000 | 8184.5 | 2309.6 | 6909.4 | 2262.3 | 1350000 | 6909.4 | 0
2021101109 | 2 | 0.55989 | 83983.5 | 0.15798 | 0 | 0.66589 | 8323.625 | 0.10725 | 8580 | 64000 | 8323.625 | 8580 | 3079.875 | -3829.525 | 1350000 | 3079.875 | 0
2021101110 | 2 | 0.57648 | 86472 | 0.17737 | 0 | 0.62869 | 7858.625 | 0.20087 | 16069.6 | 64000 | 7858.625 | 14613.375 | 0 | -3079.875 | 1350000 | 0 | 0
2021101111 | 2 | 0.59523 | 89284.5 | 0.14541 | 0 | 0.5687 | 7108.75 | 0.27034 | 21627.2 | 64000 | 7108.75 | 18175.75 | 0 | 0 | 1350000 | 0 | 0
2021101112 | 2 | 0.61015 | 91522.5 | 0.12012 | 0 | 0.58473 | 7309.125 | 0.35189 | 28151.2 | 64000 | 7309.125 | 20213.375 | 0 | 0 | 1350000 | 0 | 0
2021101113 | 2 | 0.62498 | 93747 | 0.08585 | 0 | 0.59779 | 7472.375 | 0.40383 | 32306.4 | 64000 | 7472.375 | 22274.625 | 0 | 0 | 1350000 | 0 | 0
2021101114 | 2 | 0.63568 | 95352 | 0.07584 | 0 | 0.54281 | 6785.125 | 0.41954 | 33563.2 | 64000 | 6785.125 | 24566.875 | 0 | 0 | 1350000 | 0 | 0
2021101115 | 2 | 0.64356 | 96534 | 0.05221 | 0 | 0.51331 | 6416.375 | 0.39082 | 31265.6 | 64000 | 6416.375 | 26117.625 | 0 | 0 | 1350000 | 0 | 0
2021101116 | 2 | 0.64525 | 96787.5 | 0.08906 | 0 | 0.51883 | 6485.375 | 0.29007 | 23205.6 | 64000 | 6485.375 | 23205.6 | 3096.525 | 3096.525 | 1350000 | 3096.525 | 0
2021101117 | 2 | 0.64614 | 96921 | 0.12185 | 0 | 0.56273 | 7034.125 | 0.18802 | 15041.6 | 64000 | 7034.125 | 15041.6 | 10845.275 | 7748.75 | 1350000 | 10845.275 | 0
2021101118 | 2 | 0.64558 | 96837 | 0.15228 | 0 | 0.57449 | 7181.125 | 0.10222 | 8177.6 | 64000 | 7181.125 | 8177.6 | 17478.275 | 6633 | 1350000 | 17478.275 | 0
2021101119 | 2 | 0.64432 | 96648 | 0.30795 | 0 | 0.53642 | 6705.25 | 0.01792 | 1433.6 | 64000 | 6705.25 | 1433.6 | 24509.15 | 7030.875 | 1350000 | 24509.15 | 0
2021101120 | 2 | 0.64551 | 96826.5 | 0.51142 | 0 | 0.48519 | 6064.875 | 0 | 0 | 64000 | 6064.875 | 0 | 26761.625 | 2252.475 | 1348704.625 | 26761.625 | 0
2021101121 | 2 | 0.62621 | 93931.5 | 0.69882 | 0 | 0.44423 | 5552.875 | 0 | 0 | 64000 | 5552.875 | 0 | 24378.625 | -2383 | 1349792.25 | 24378.625 | 0
2021101122 | 2 | 0.59338 | 89007 | 0.77162 | 0 | 0.42657 | 5332.125 | 0 | 0 | 64000 | 5332.125 | 0 | 19674.875 | -4703.75 | 1350000 | 19674.875 | 0
2021101123 | 2 | 0.55527 | 83290.5 | 0.74492 | 0 | 0.42323 | 5290.375 | 0 | 0 | 64000 | 5290.375 | 0 | 14000.125 | -5674.75 | 1350000 | 14000.125 | 0
2021101124 | 2 | 0.51792 | 77688 | 0.69389 | 0 | 0.39486 | 4935.75 | 0 | 0 | 64000 | 4935.75 | 0 | 8752.25 | -5247.875 | 1350000 | 8752.25 | 0
2021101201 | 3 | 0.48816 | 73224 | 0.6566 | 0 | 0.35287 | 4410.875 | 0 | 0 | 64000 | 4410.875 | 0 | 4813.125 | -3939.125 | 1350000 | 4813.125 | 0
2021101202 | 3 | 0.46767 | 70150.5 | 0.58743 | 0 | 0.30422 | 3802.75 | 0 | 0 | 64000 | 3802.75 | 0 | 2347.75 | -2465.375 | 1350000 | 2347.75 | 0
2021101203 | 3 | 0.45581 | 68371.5 | 0.55027 | 0 | 0.27437 | 3429.625 | 0 | 0 | 64000 | 3429.625 | 0 | 941.875 | -1405.875 | 1350000 | 941.875 | 0
2021101204 | 3 | 0.45015 | 67522.5 | 0.48837 | 0 | 0.27259 | 3407.375 | 0 | 0 | 64000 | 3407.375 | 0 | 115.125 | -826.75 | 1350000 | 115.125 | 0
2021101205 | 3 | 0.45606 | 68409 | 0.37645 | 0 | 0.27227 | 3403.375 | 0 | 0 | 64000 | 3403.375 | 0 | 1005.625 | 890.5 | 1350000 | 1005.625 | 0
2021101206 | 3 | 0.47791 | 71686.5 | 0.35646 | 0 | 0.27654 | 3456.75 | 0 | 0 | 64000 | 3456.75 | 0 | 4229.75 | 3224.125 | 1350000 | 4229.75 | 0
2021101207 | 3 | 0.52252 | 78378 | 0.35818 | 0 | 0.3106 | 3882.5 | 0.00335 | 268 | 64000 | 3882.5 | 268 | 10227.5 | 5997.75 | 1350000 | 10227.5 | 0
2021101208 | 3 | 0.5544 | 83160 | 0.28142 | 0 | 0.36448 | 4556 | 0.12076 | 9660.8 | 64000 | 4556 | 9660.8 | 4943.2 | -5284.3 | 1350000 | 4943.2 | 0
2021101209 | 3 | 0.56831 | 85246.5 | 0.24132 | 0 | 0.33235 | 4154.375 | 0.34831 | 27864.8 | 64000 | 4154.375 | 17092.125 | 0 | -4943.2 | 1350000 | 0 | 0
2021101210 | 3 | 0.57821 | 86731.5 | 0.22072 | 0 | 0.31412 | 3926.5 | 0.46691 | 37352.8 | 64000 | 3926.5 | 18805 | 0 | 0 | 1350000 | 0 | 0
2021101211 | 3 | 0.58899 | 88348.5 | 0.20159 | 0 | 0.31204 | 3900.5 | 0.49601 | 39680.8 | 64000 | 3900.5 | 20448 | 0 | 0 | 1350000 | 0 | 0
2021101212 | 3 | 0.59816 | 89724 | 0.17246 | 0 | 0.28931 | 3616.375 | 0.51051 | 40840.8 | 64000 | 3616.375 | 22107.625 | 0 | 0 | 1350000 | 0 | 0
2021101213 | 3 | 0.60489 | 90733.5 | 0.1529 | 0 | 0.29565 | 3695.625 | 0.53249 | 42599.2 | 64000 | 3695.625 | 23037.875 | 0 | 0 | 1350000 | 0 | 0
2021101214 | 3 | 0.61077 | 91615.5 | 0.15606 | 0 | 0.26994 | 3374.25 | 0.55572 | 44457.6 | 64000 | 3374.25 | 24241.25 | 0 | 0 | 1350000 | 0 | 0
2021101215 | 3 | 0.61493 | 92239.5 | 0.17184 | 0 | 0.25936 | 3242 | 0.5789 | 46312 | 64000 | 3242 | 24997.5 | 0 | 0 | 1350000 | 0 | 0
2021101216 | 3 | 0.61665 | 92497.5 | 0.17334 | 0 | 0.29849 | 3731.125 | 0.55917 | 44733.6 | 64000 | 3731.125 | 24766.375 | 0 | 0 | 1350000 | 0 | 0
2021101217 | 3 | 0.62193 | 93289.5 | 0.23185 | 0 | 0.41553 | 5194.125 | 0.49404 | 39523.2 | 64000 | 5194.125 | 24095.375 | 0 | 0 | 1350000 | 0 | 0
2021101218 | 3 | 0.62459 | 93688.5 | 0.25226 | 0 | 0.45949 | 5743.625 | 0.26522 | 21217.6 | 64000 | 5743.625 | 21217.6 | 2727.275 | 2727.275 | 1350000 | 2727.275 | 0
2021101219 | 3 | 0.62573 | 93859.5 | 0.28291 | 0 | 0.4654 | 5817.5 | 0.03241 | 2592.8 | 64000 | 5817.5 | 2592.8 | 21449.2 | 18721.925 | 1350000 | 21449.2 | 0
2021101220 | 3 | 0.62686 | 94029 | 0.28289 | 0 | 0.48769 | 6096.125 | 0 | 0 | 64000 | 6096.125 | 0 | 23932.875 | 2483.675 | 1350000 | 23932.875 | 0
2021101221 | 3 | 0.61075 | 91612.5 | 0.22568 | 0 | 0.54129 | 6766.125 | 0 | 0 | 64000 | 6766.125 | 0 | 20846.375 | -3086.5 | 1350000 | 20846.375 | 0
2021101222 | 3 | 0.57973 | 86959.5 | 0.2266 | 0 | 0.58789 | 7348.625 | 0 | 0 | 64000 | 7348.625 | 0 | 15610.875 | -5235.5 | 1350000 | 15610.875 | 0
2021101223 | 3 | 0.54286 | 81429 | 0.20524 | 0 | 0.59327 | 7415.875 | 0 | 0 | 64000 | 7415.875 | 0 | 10013.125 | -5597.75 | 1350000 | 10013.125 | 0
2021101224 | 3 | 0.50661 | 75991.5 | 0.13899 | 0 | 0.61859 | 7732.375 | 0 | 0 | 64000 | 7732.375 | 0 | 4259.125 | -5754 | 1350000 | 4259.125 | 0
2021101301 | 4 | 0.47825 | 71737.5 | 0.1535 | 0 | 0.64719 | 8089.875 | 0 | 0 | 64000 | 7737.5 | 0 | 0 | -4259.125 | 1350000 | 0 | 0
2021101302 | 4 | 0.45986 | 68979 | 0.17422 | 0 | 0.63869 | 7983.625 | 0 | 0 | 64000 | 4979 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101303 | 4 | 0.44812 | 67218 | 0.17787 | 0 | 0.63549 | 7943.625 | 0 | 0 | 64000 | 3218 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101304 | 4 | 0.44323 | 66484.5 | 0.16836 | 0 | 0.60585 | 7573.125 | 0 | 0 | 64000 | 2484.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101305 | 4 | 0.44856 | 67284 | 0.16731 | 0 | 0.53612 | 6701.5 | 0 | 0 | 64000 | 3284 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101306 | 4 | 0.47144 | 70716 | 0.1638 | 0 | 0.48852 | 6106.5 | 0 | 0 | 64000 | 6106.5 | 0 | 609.5 | 609.5 | 1350000 | 609.5 | 0
2021101307 | 4 | 0.51301 | 76951.5 | 0.1342 | 0 | 0.45226 | 5653.25 | 0.00429 | 343.2 | 64000 | 5653.25 | 343.2 | 6955.05 | 6345.55 | 1350000 | 6955.05 | 0
2021101308 | 4 | 0.54566 | 81849 | 0.1229 | 0 | 0.44975 | 5621.875 | 0.11836 | 9468.8 | 64000 | 5621.875 | 9468.8 | 2758.325 | -4196.725 | 1350000 | 2758.325 | 0
2021101309 | 4 | 0.55911 | 83866.5 | 0.09225 | 0 | 0.43646 | 5455.75 | 0.37061 | 29648.8 | 64000 | 5455.75 | 14410.75 | 0 | -2758.325 | 1350000 | 0 | 0
2021101310 | 4 | 0.56915 | 85372.5 | 0.10139 | 0 | 0.39808 | 4976 | 0.50271 | 40216.8 | 64000 | 4976 | 16396.5 | 0 | 0 | 1350000 | 0 | 0
2021101311 | 4 | 0.57949 | 86923.5 | 0.07915 | 0 | 0.35661 | 4457.625 | 0.56258 | 45006.4 | 64000 | 4457.625 | 18465.875 | 0 | 0 | 1350000 | 0 | 0
2021101312 | 4 | 0.59102 | 88653 | 0.06027 | 0 | 0.33022 | 4127.75 | 0.5779 | 46232 | 64000 | 4127.75 | 20525.25 | 0 | 0 | 1350000 | 0 | 0
2021101313 | 4 | 0.60109 | 90163.5 | 0.0805 | 0 | 0.29861 | 3732.625 | 0.57246 | 45796.8 | 64000 | 3732.625 | 22430.875 | 0 | 0 | 1350000 | 0 | 0
2021101314 | 4 | 0.6126 | 91890 | 0.12081 | 0 | 0.26694 | 3336.75 | 0.58342 | 46673.6 | 64000 | 3336.75 | 24553.25 | 0 | 0 | 1350000 | 0 | 0
2021101315 | 4 | 0.61859 | 92788.5 | 0.13975 | 0 | 0.19935 | 2491.875 | 0.56714 | 45371.2 | 64000 | 2491.875 | 26296.625 | 0 | 0 | 1350000 | 0 | 0
2021101316 | 4 | 0.62325 | 93487.5 | 0.13352 | 0 | 0.24434 | 3054.25 | 0.53016 | 42412.8 | 64000 | 3054.25 | 26433.25 | 0 | 0 | 1350000 | 0 | 0
2021101317 | 4 | 0.62789 | 94183.5 | 0.11563 | 0 | 0.36507 | 4563.375 | 0.45983 | 36786.4 | 64000 | 4563.375 | 25620.125 | 0 | 0 | 1350000 | 0 | 0
2021101318 | 4 | 0.62882 | 94323 | 0.10439 | 0 | 0.42113 | 5264.125 | 0.25878 | 20702.4 | 64000 | 5264.125 | 20702.4 | 4356.475 | 4356.475 | 1350000 | 4356.475 | 0
2021101319 | 4 | 0.62859 | 94288.5 | 0.11931 | 0 | 0.43083 | 5385.375 | 0.03089 | 2471.2 | 64000 | 5385.375 | 2471.2 | 22431.925 | 18075.45 | 1350000 | 22431.925 | 0
2021101320 | 4 | 0.62979 | 94468.5 | 0.21396 | 0 | 0.45279 | 5659.875 | 0 | 0 | 64000 | 5659.875 | 0 | 24808.625 | 2376.7 | 1350000 | 24808.625 | 0
2021101321 | 4 | 0.61231 | 91846.5 | 0.21681 | 0 | 0.48889 | 6111.125 | 0 | 0 | 64000 | 6111.125 | 0 | 21735.375 | -3073.25 | 1350000 | 21735.375 | 0
2021101322 | 4 | 0.58249 | 87373.5 | 0.2337 | 0 | 0.52255 | 6531.875 | 0 | 0 | 64000 | 6531.875 | 0 | 16841.625 | -4893.75 | 1350000 | 16841.625 | 0
2021101323 | 4 | 0.54587 | 81880.5 | 0.21029 | 0 | 0.52888 | 6611 | 0 | 0 | 64000 | 6611 | 0 | 11269.5 | -5572.125 | 1350000 | 11269.5 | 0
2021101324 | 4 | 0.51041 | 76561.5 | 0.18631 | 0 | 0.52986 | 6623.25 | 0 | 0 | 64000 | 6623.25 | 0 | 5938.25 | -5331.25 | 1350000 | 5938.25 | 0
2021101401 | 5 | 0.48247 | 72370.5 | 0.17336 | 0 | 0.5011 | 6263.75 | 0 | 0 | 64000 | 6263.75 | 0 | 2106.75 | -3831.5 | 1350000 | 2106.75 | 0
2021101402 | 5 | 0.46449 | 69673.5 | 0.13982 | 0 | 0.4526 | 5657.5 | 0 | 0 | 64000 | 5657.5 | 0 | 16 | -2090.75 | 1350000 | 16 | 0
2021101403 | 5 | 0.45238 | 67857 | 0.12916 | 0 | 0.38822 | 4852.75 | 0 | 0 | 64000 | 3857 | 0 | 0 | -16 | 1350000 | 0 | 0
2021101404 | 5 | 0.44726 | 67089 | 0.14878 | 0 | 0.31103 | 3887.875 | 0 | 0 | 64000 | 3089 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101405 | 5 | 0.45145 | 67717.5 | 0.15666 | 0 | 0.24771 | 3096.375 | 0 | 0 | 64000 | 3096.375 | 0 | 621.125 | 621.125 | 1350000 | 621.125 | 0
2021101406 | 5 | 0.47606 | 71409 | 0.21117 | 0 | 0.18453 | 2306.625 | 0 | 0 | 64000 | 2306.625 | 0 | 5102.375 | 4481.25 | 1350000 | 5102.375 | 0
2021101407 | 5 | 0.51858 | 77787 | 0.23534 | 0 | 0.13854 | 1731.75 | 0 | 0 | 64000 | 1731.75 | 0 | 12055.25 | 6952.875 | 1350000 | 12055.25 | 0
2021101408 | 5 | 0.55008 | 82512 | 0.24443 | 0 | 0.11871 | 1483.875 | 0.0909 | 7272 | 64000 | 1483.875 | 7272 | 9756.125 | -2299.125 | 1350000 | 9756.125 | 0
2021101409 | 5 | 0.56124 | 84186 | 0.24897 | 0 | 0.11207 | 1400.875 | 0.30267 | 24213.6 | 64000 | 1400.875 | 18785.125 | 0 | -9756.125 | 1350000 | 0 | 0
2021101410 | 5 | 0.57244 | 85866 | 0.18835 | 0 | 0.09929 | 1241.125 | 0.44732 | 35785.6 | 64000 | 1241.125 | 20624.875 | 0 | 0 | 1350000 | 0 | 0
2021101411 | 5 | 0.586 | 87900 | 0.09821 | 0 | 0.08116 | 1014.5 | 0.52987 | 42389.6 | 64000 | 1014.5 | 22885.5 | 0 | 0 | 1350000 | 0 | 0
2021101412 | 5 | 0.60109 | 90163.5 | 0.07693 | 0 | 0.0567 | 708.75 | 0.57599 | 46079.2 | 64000 | 708.75 | 25454.75 | 0 | 0 | 1350000 | 0 | 0
2021101413 | 5 | 0.61833 | 92749.5 | 0.06598 | 0 | 0.04553 | 569.125 | 0.58912 | 47129.6 | 64000 | 569.125 | 28180.375 | 0 | 0 | 1350000 | 0 | 0
2021101414 | 5 | 0.63631 | 95446.5 | 0.07473 | 0 | 0.05774 | 721.75 | 0.59054 | 47243.2 | 64000 | 721.75 | 30724.75 | 0 | 0 | 1350000 | 0 | 0
2021101415 | 5 | 0.64898 | 97347 | 0.05554 | 0 | 0.06657 | 832.125 | 0.59443 | 47554.4 | 64000 | 832.125 | 32514.875 | 0 | 0 | 1350000 | 0 | 0
2021101416 | 5 | 0.6605 | 99075 | 0.03923 | 0 | 0.11215 | 1401.875 | 0.5638 | 45104 | 64000 | 1401.875 | 33673.125 | 0 | 0 | 1350000 | 0 | 0
2021101417 | 5 | 0.66672 | 100008 | 0.05877 | 0 | 0.21802 | 2725.25 | 0.4879 | 39032 | 64000 | 2725.25 | 33282.75 | 0 | 0 | 1350000 | 0 | 0
2021101418 | 5 | 0.66584 | 99876 | 0.02975 | 0 | 0.30706 | 3838.25 | 0.24164 | 19331.2 | 64000 | 3838.25 | 19331.2 | 12706.55 | 12706.55 | 1350000 | 12706.55 | 0
2021101419 | 5 | 0.65724 | 98586 | 0.0147 | 0 | 0.35948 | 4493.5 | 0.02713 | 2170.4 | 64000 | 4493.5 | 2170.4 | 27922.1 | 15215.55 | 1347544.15 | 27922.1 | 0
2021101420 | 5 | 0.65474 | 98211 | 0.02674 | 0 | 0.37532 | 4691.5 | 0 | 0 | 64000 | 4691.5 | 0 | 29519.5 | 1597.4 | 1343490.9 | 29519.5 | 0
2021101421 | 5 | 0.63315 | 94972.5 | 0.06491 | 0 | 0.37068 | 4633.5 | 0 | 0 | 64000 | 4633.5 | 0 | 26339 | -3180.5 | 1342618.15 | 26339 | 0
2021101422 | 5 | 0.60071 | 90106.5 | 0.11465 | 0 | 0.38336 | 4792 | 0 | 0 | 64000 | 4792 | 0 | 21314.5 | -5024.5 | 1346769.9 | 21314.5 | 0
2021101423 | 5 | 0.56208 | 84312 | 0.17256 | 0 | 0.36722 | 4590.25 | 0 | 0 | 64000 | 4590.25 | 0 | 15721.75 | -5592.75 | 1350000 | 15721.75 | 0
2021101424 | 5 | 0.52384 | 78576 | 0.22976 | 0 | 0.34253 | 4281.625 | 0 | 0 | 64000 | 4281.625 | 0 | 10294.375 | -5427.375 | 1350000 | 10294.375 | 0
2021101501 | 6 | 0.49247 | 73870.5 | 0.25743 | 0 | 0.31104 | 3888 | 0 | 0 | 64000 | 3888 | 0 | 5982.5 | -4311.875 | 1350000 | 5982.5 | 0
2021101502 | 6 | 0.47057 | 70585.5 | 0.29539 | 0 | 0.30532 | 3816.5 | 0 | 0 | 64000 | 3816.5 | 0 | 2769 | -3213.5 | 1350000 | 2769 | 0
2021101503 | 6 | 0.45799 | 68698.5 | 0.31629 | 0 | 0.29534 | 3691.75 | 0 | 0 | 64000 | 3691.75 | 0 | 1006.75 | -1762.25 | 1350000 | 1006.75 | 0
2021101504 | 6 | 0.44959 | 67438.5 | 0.30153 | 0 | 0.27893 | 3486.625 | 0 | 0 | 64000 | 3438.5 | 0 | 0 | -1006.75 | 1350000 | 0 | 0
2021101505 | 6 | 0.4541 | 68115 | 0.31743 | 0 | 0.25635 | 3204.375 | 0 | 0 | 64000 | 3204.375 | 0 | 910.625 | 910.625 | 1350000 | 910.625 | 0
2021101506 | 6 | 0.47417 | 71125.5 | 0.32236 | 0 | 0.22413 | 2801.625 | 0 | 0 | 64000 | 2801.625 | 0 | 4323.875 | 3413.25 | 1350000 | 4323.875 | 0
2021101507 | 6 | 0.51547 | 77320.5 | 0.29345 | 0 | 0.2078 | 2597.5 | 0.00288 | 230.4 | 64000 | 2597.5 | 230.4 | 10492.6 | 6168.725 | 1350000 | 10492.6 | 0
2021101508 | 6 | 0.54787 | 82180.5 | 0.27441 | 0 | 0.23956 | 2994.5 | 0.12735 | 10188 | 64000 | 2994.5 | 10188 | 4998 | -5494.6 | 1350000 | 4998 | 0
2021101509 | 6 | 0.56102 | 84153 | 0.20375 | 0 | 0.28745 | 3593.125 | 0.38338 | 30670.4 | 64000 | 3593.125 | 16559.875 | 0 | -4998 | 1350000 | 0 | 0
2021101510 | 6 | 0.57365 | 86047.5 | 0.103 | 0 | 0.3234 | 4042.5 | 0.48331 | 38664.8 | 64000 | 4042.5 | 18005 | 0 | 0 | 1350000 | 0 | 0
2021101511 | 6 | 0.59038 | 88557 | 0.0326 | 0 | 0.34557 | 4319.625 | 0.48399 | 38719.2 | 64000 | 4319.625 | 20237.375 | 0 | 0 | 1350000 | 0 | 0
2021101512 | 6 | 0.60891 | 91336.5 | 0.00824 | 0 | 0.37895 | 4736.875 | 0.45902 | 36721.6 | 64000 | 4736.875 | 22599.625 | 0 | 0 | 1350000 | 0 | 0
2021101513 | 6 | 0.62588 | 93882 | 0.03124 | 0 | 0.41543 | 5192.875 | 0.42034 | 33627.2 | 64000 | 5192.875 | 24689.125 | 0 | 0 | 1350000 | 0 | 0
2021101514 | 6 | 0.64575 | 96862.5 | 0.08514 | 0 | 0.43908 | 5488.5 | 0.36958 | 29566.4 | 64000 | 5488.5 | 27374 | 0 | 0 | 1350000 | 0 | 0
2021101515 | 6 | 0.65813 | 98719.5 | 0.1116 | 0 | 0.45117 | 5639.625 | 0.29574 | 23659.2 | 64000 | 5639.625 | 23659.2 | 5420.675 | 5420.675 | 1350000 | 5420.675 | 0
2021101516 | 6 | 0.66366 | 99549 | 0.16745 | 0 | 0.51692 | 6461.5 | 0.21296 | 17036.8 | 64000 | 6461.5 | 17036.8 | 12050.7 | 6630.025 | 1350000 | 12050.7 | 0
2021101517 | 6 | 0.66484 | 99726 | 0.18536 | 0 | 0.55419 | 6927.375 | 0.14082 | 11265.6 | 64000 | 6927.375 | 11265.6 | 17533.025 | 5482.325 | 1350000 | 17533.025 | 0
2021101518 | 6 | 0.65675 | 98512.5 | 0.25763 | 0 | 0.59796 | 7474.5 | 0.05752 | 4601.6 | 64000 | 7474.5 | 4601.6 | 22436.4 | 4903.375 | 1350000 | 22436.4 | 0
2021101519 | 6 | 0.64324 | 96486 | 0.34668 | 0 | 0.63485 | 7935.625 | 0.00578 | 462.4 | 64000 | 7935.625 | 462.4 | 24087.975 | 1651.575 | 1350000 | 24087.975 | 0
2021101520 | 6 | 0.63592 | 95388 | 0.38924 | 0 | 0.66644 | 8330.5 | 0 | 0 | 64000 | 8330.5 | 0 | 23057.5 | -1030.475 | 1350000 | 23057.5 | 0
2021101521 | 6 | 0.61453 | 92179.5 | 0.44384 | 0 | 0.68376 | 8547 | 0 | 0 | 64000 | 8547 | 0 | 19632.5 | -3425 | 1350000 | 19632.5 | 0
2021101522 | 6 | 0.58803 | 88204.5 | 0.52664 | 0 | 0.67969 | 8496.125 | 0 | 0 | 64000 | 8496.125 | 0 | 15708.375 | -3924.125 | 1350000 | 15708.375 | 0
2021101523 | 6 | 0.55694 | 83541 | 0.51278 | 0 | 0.69034 | 8629.25 | 0 | 0 | 64000 | 8629.25 | 0 | 10911.75 | -4796.625 | 1350000 | 10911.75 | 0
2021101524 | 6 | 0.5215 | 78225 | 0.52144 | 0 | 0.69758 | 8719.75 | 0 | 0 | 64000 | 8719.75 | 0 | 5505.25 | -5406.5 | 1350000 | 5505.25 | 0
2021101601 | 7 | 0.49099 | 73648.5 | 0.54826 | 0 | 0.72105 | 9013.125 | 0 | 0 | 64000 | 9013.125 | 0 | 635.375 | -4869.875 | 1350000 | 635.375 | 0
2021101602 | 7 | 0.46679 | 70018.5 | 0.60731 | 0 | 0.73631 | 9203.875 | 0 | 0 | 64000 | 6018.5 | 0 | 0 | -635.375 | 1350000 | 0 | 0
2021101603 | 7 | 0.4512 | 67680 | 0.60777 | 0 | 0.75777 | 9472.125 | 0 | 0 | 64000 | 3680 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101604 | 7 | 0.44256 | 66384 | 0.614 | 0 | 0.76197 | 9524.625 | 0 | 0 | 64000 | 2384 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101605 | 7 | 0.43759 | 65638.5 | 0.63079 | 0 | 0.76376 | 9547 | 0 | 0 | 64000 | 1638.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101606 | 7 | 0.44251 | 66376.5 | 0.57896 | 0 | 0.77798 | 9724.75 | 0 | 0 | 64000 | 2376.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101607 | 7 | 0.45598 | 68397 | 0.61626 | 0 | 0.78168 | 9771 | 0 | 0 | 64000 | 4397 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101608 | 7 | 0.47289 | 70933.5 | 0.58689 | 0 | 0.75391 | 9423.875 | 0.02429 | 1943.2 | 64000 | 6933.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101609 | 7 | 0.49074 | 73611 | 0.61874 | 0 | 0.73674 | 9209.25 | 0.06059 | 4847.2 | 64000 | 9209.25 | 401.75 | 0 | 0 | 1350000 | 0 | 0
2021101610 | 7 | 0.50916 | 76374 | 0.80376 | 0 | 0.70836 | 8854.5 | 0.09254 | 7403.2 | 64000 | 8854.5 | 3519.5 | 0 | 0 | 1350000 | 0 | 0
2021101611 | 7 | 0.52436 | 78654 | 0.87002 | 0 | 0.71291 | 8911.375 | 0.12103 | 9682.4 | 64000 | 8911.375 | 5742.625 | 0 | 0 | 1350000 | 0 | 0
2021101612 | 7 | 0.5366 | 80490 | 0.8201 | 0 | 0.70664 | 8833 | 0.12926 | 10340.8 | 64000 | 8833 | 7657 | 0 | 0 | 1350000 | 0 | 0
2021101613 | 7 | 0.54963 | 82444.5 | 0.82371 | 0 | 0.70229 | 8778.625 | 0.11816 | 9452.8 | 64000 | 8778.625 | 9452.8 | 213.075 | 213.075 | 1350000 | 213.075 | 0
2021101614 | 7 | 0.55354 | 83031 | 0.91103 | 0 | 0.68696 | 8587 | 0.09783 | 7826.4 | 64000 | 8587 | 7826.4 | 2617.6 | 2404.525 | 1350000 | 2617.6 | 0
2021101615 | 7 | 0.55229 | 82843.5 | 0.89985 | 0 | 0.72248 | 9031 | 0.07336 | 5868.8 | 64000 | 9031 | 5868.8 | 3943.7 | 1326.1 | 1350000 | 3943.7 | 0
2021101616 | 7 | 0.54735 | 82102.5 | 0.93984 | 0 | 0.72031 | 9003.875 | 0.04664 | 3731.2 | 64000 | 9003.875 | 3731.2 | 5367.425 | 1423.725 | 1350000 | 5367.425 | 0
2021101617 | 7 | 0.54246 | 81369 | 0.92114 | 0 | 0.71142 | 8892.75 | 0.03085 | 2468 | 64000 | 8892.75 | 2468 | 6008.25 | 640.825 | 1350000 | 6008.25 | 0
2021101618 | 7 | 0.53787 | 80680.5 | 0.89835 | 0 | 0.73108 | 9138.5 | 0.01286 | 1028.8 | 64000 | 9138.5 | 1028.8 | 6513.2 | 504.95 | 1350000 | 6513.2 | 0
2021101619 | 7 | 0.53598 | 80397 | 0.81749 | 0 | 0.75342 | 9417.75 | 0.00047 | 37.6 | 64000 | 9417.75 | 37.6 | 6941.65 | 428.45 | 1350000 | 6941.65 | 0
2021101620 | 7 | 0.53628 | 80442 | 0.82067 | 0 | 0.755 | 9437.5 | 0 | 0 | 64000 | 9437.5 | 0 | 7004.5 | 62.85 | 1350000 | 7004.5 | 0
2021101621 | 7 | 0.52169 | 78253.5 | 0.87116 | 0 | 0.74849 | 9356.125 | 0 | 0 | 64000 | 9356.125 | 0 | 4897.375 | -2107.125 | 1350000 | 4897.375 | 0
2021101622 | 7 | 0.50292 | 75438 | 0.8697 | 0 | 0.73869 | 9233.625 | 0 | 0 | 64000 | 9233.625 | 0 | 2204.375 | -2693 | 1350000 | 2204.375 | 0
2021101623 | 7 | 0.47958 | 71937 | 0.86524 | 0 | 0.72294 | 9036.75 | 0 | 0 | 64000 | 7937 | 0 | 0 | -2204.375 | 1350000 | 0 | 0
2021101624 | 7 | 0.45417 | 68125.5 | 0.85209 | 0 | 0.70349 | 8793.625 | 0 | 0 | 64000 | 4125.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101701 | 1 | 0.43334 | 65001 | 0.82426 | 0 | 0.66879 | 8359.875 | 0 | 0 | 64000 | 1001 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101702 | 1 | 0.41677 | 62515.5 | 0.76051 | 0 | 0.65007 | 8125.875 | 0 | 0 | 62515.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101703 | 1 | 0.4065 | 60975 | 0.72673 | 0 | 0.62408 | 7801 | 0 | 0 | 60975 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101704 | 1 | 0.40056 | 60084 | 0.77178 | 0 | 0.59173 | 7396.625 | 0 | 0 | 60084 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101705 | 1 | 0.39918 | 59877 | 0.76077 | 0 | 0.54155 | 6769.375 | 0 | 0 | 59877 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101706 | 1 | 0.40458 | 60687 | 0.79231 | 0 | 0.54319 | 6789.875 | 0 | 0 | 60687 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101707 | 1 | 0.4161 | 62415 | 0.79768 | 0 | 0.49178 | 6147.25 | 4e-05 | 3.2 | 62415 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101708 | 1 | 0.43203 | 64804.5 | 0.81574 | 0 | 0.44604 | 5575.5 | 0.02005 | 1604 | 64000 | 804.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101709 | 1 | 0.44762 | 67143 | 0.81255 | 0 | 0.39372 | 4921.5 | 0.07015 | 5612 | 64000 | 3143 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101710 | 1 | 0.45755 | 68632.5 | 0.83994 | 0 | 0.31807 | 3975.875 | 0.10646 | 8516.8 | 64000 | 3975.875 | 656.625 | 0 | 0 | 1350000 | 0 | 0
2021101711 | 1 | 0.46167 | 69250.5 | 0.85816 | 0 | 0.23437 | 2929.625 | 0.15413 | 12330.4 | 64000 | 2929.625 | 2320.875 | 0 | 0 | 1350000 | 0 | 0
2021101712 | 1 | 0.46559 | 69838.5 | 0.86974 | 0 | 0.18696 | 2337 | 0.18855 | 15084 | 64000 | 2337 | 3501.5 | 0 | 0 | 1350000 | 0 | 0
2021101713 | 1 | 0.4693 | 70395 | 0.88701 | 0 | 0.1075 | 1343.75 | 0.22484 | 17987.2 | 64000 | 1343.75 | 5051.25 | 0 | 0 | 1350000 | 0 | 0
2021101714 | 1 | 0.47093 | 70639.5 | 0.88812 | 0 | 0.10044 | 1255.5 | 0.21462 | 17169.6 | 64000 | 1255.5 | 5384 | 0 | 0 | 1350000 | 0 | 0
2021101715 | 1 | 0.47137 | 70705.5 | 0.90837 | 0 | 0.12998 | 1624.75 | 0.17573 | 14058.4 | 64000 | 1624.75 | 5080.75 | 0 | 0 | 1350000 | 0 | 0
2021101716 | 1 | 0.47372 | 71058 | 0.8651 | 0 | 0.15912 | 1989 | 0.13901 | 11120.8 | 64000 | 1989 | 5069 | 0 | 0 | 1350000 | 0 | 0
2021101717 | 1 | 0.48328 | 72492 | 0.85938 | 0 | 0.19858 | 2482.25 | 0.0848 | 6784 | 64000 | 2482.25 | 6009.75 | 0 | 0 | 1350000 | 0 | 0
2021101718 | 1 | 0.49721 | 74581.5 | 0.8381 | 0 | 0.24437 | 3054.625 | 0.03466 | 2772.8 | 64000 | 3054.625 | 2772.8 | 4754.075 | 4754.075 | 1350000 | 4754.075 | 0
2021101719 | 1 | 0.51161 | 76741.5 | 0.8334 | 0 | 0.27854 | 3481.75 | 0.00261 | 208.8 | 64000 | 3481.75 | 208.8 | 9050.95 | 4296.875 | 1350000 | 9050.95 | 0
2021101720 | 1 | 0.52515 | 78772.5 | 0.83747 | 0 | 0.24287 | 3035.875 | 0 | 0 | 64000 | 3035.875 | 0 | 11736.625 | 2685.675 | 1350000 | 11736.625 | 0
2021101721 | 1 | 0.52009 | 78013.5 | 0.7981 | 0 | 0.17657 | 2207.125 | 0 | 0 | 64000 | 2207.125 | 0 | 11806.375 | 69.75 | 1350000 | 11806.375 | 0
2021101722 | 1 | 0.50142 | 75213 | 0.80666 | 0 | 0.13138 | 1642.25 | 0 | 0 | 64000 | 1642.25 | 0 | 9570.75 | -2235.625 | 1350000 | 9570.75 | 0
2021101723 | 1 | 0.47646 | 71469 | 0.85606 | 0 | 0.11188 | 1398.5 | 0 | 0 | 64000 | 1398.5 | 0 | 6070.5 | -3500.25 | 1350000 | 6070.5 | 0
2021101724 | 1 | 0.45243 | 67864.5 | 0.86422 | 0 | 0.10291 | 1286.375 | 0 | 0 | 64000 | 1286.375 | 0 | 2578.125 | -3492.375 | 1350000 | 2578.125 | 0
2021101801 | 2 | 0.435 | 65250 | 0.86964 | 0 | 0.10554 | 1319.25 | 0 | 0 | 64000 | 1250 | 0 | 0 | -2578.125 | 1350000 | 0 | 0
2021101802 | 2 | 0.42355 | 63532.5 | 0.85899 | 0 | 0.0897 | 1121.25 | 0 | 0 | 63532.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101803 | 2 | 0.41907 | 62860.5 | 0.83719 | 0 | 0.06616 | 827 | 0 | 0 | 62860.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101804 | 2 | 0.41817 | 62725.5 | 0.82489 | 0 | 0.05835 | 729.375 | 0 | 0 | 62725.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101805 | 2 | 0.42884 | 64326 | 0.84426 | 0 | 0.05567 | 695.875 | 0 | 0 | 64000 | 326 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101806 | 2 | 0.45596 | 68394 | 0.85158 | 0 | 0.05236 | 654.5 | 0 | 0 | 64000 | 654.5 | 0 | 3739.5 | 3739.5 | 1350000 | 3739.5 | 0
2021101807 | 2 | 0.50408 | 75612 | 0.88679 | 0 | 0.04916 | 614.5 | 0 | 0 | 64000 | 614.5 | 0 | 10997.5 | 7258 | 1350000 | 10997.5 | 0
2021101808 | 2 | 0.54142 | 81213 | 0.92146 | 0 | 0.05758 | 719.75 | 0.00936 | 748.8 | 64000 | 719.75 | 748.8 | 15744.45 | 4746.95 | 1350000 | 15744.45 | 0
2021101809 | 2 | 0.55045 | 82567.5 | 0.90143 | 0 | 0.06724 | 840.5 | 0.03327 | 2661.6 | 64000 | 840.5 | 2661.6 | 15065.4 | -679.05 | 1350000 | 15065.4 | 0
2021101810 | 2 | 0.54639 | 81958.5 | 0.90547 | 0 | 0.05476 | 684.5 | 0.06499 | 5199.2 | 64000 | 684.5 | 5199.2 | 12074.8 | -2990.6 | 1350000 | 12074.8 | 0
2021101811 | 2 | 0.54282 | 81423 | 0.93726 | 0 | 0.05538 | 692.25 | 0.08912 | 7129.6 | 64000 | 692.25 | 7129.6 | 9601.15 | -2473.65 | 1350000 | 9601.15 | 0
2021101812 | 2 | 0.54331 | 81496.5 | 0.97208 | 0 | 0.05329 | 666.125 | 0.09831 | 7864.8 | 64000 | 666.125 | 7864.8 | 8965.575 | -635.575 | 1350000 | 8965.575 | 0
2021101813 | 2 | 0.54357 | 81535.5 | 0.96704 | 0 | 0.05143 | 642.875 | 0.10779 | 8623.2 | 64000 | 642.875 | 8623.2 | 8269.425 | -696.15 | 1350000 | 8269.425 | 0
2021101814 | 2 | 0.54477 | 81715.5 | 0.94963 | 0 | 0.05776 | 722 | 0.10493 | 8394.4 | 64000 | 722 | 8394.4 | 8599.1 | 329.675 | 1350000 | 8599.1 | 0
2021101815 | 2 | 0.54355 | 81532.5 | 0.95967 | 0 | 0.06607 | 825.875 | 0.09009 | 7207.2 | 64000 | 825.875 | 7207.2 | 9499.425 | 900.325 | 1350000 | 9499.425 | 0
2021101816 | 2 | 0.54157 | 81235.5 | 0.9627 | 0 | 0.06419 | 802.375 | 0.08022 | 6417.6 | 64000 | 802.375 | 6417.6 | 10015.525 | 516.1 | 1350000 | 10015.525 | 0
2021101817 | 2 | 0.54672 | 82008 | 0.94013 | 0 | 0.07617 | 952.125 | 0.0648 | 5184 | 64000 | 952.125 | 5184 | 11871.875 | 1856.35 | 1350000 | 11871.875 | 0
2021101818 | 2 | 0.55596 | 83394 | 0.89346 | 0 | 0.07872 | 984 | 0.02635 | 2108 | 64000 | 984 | 2108 | 16302 | 4430.125 | 1350000 | 16302 | 0
2021101819 | 2 | 0.5672 | 85080 | 0.86476 | 0 | 0.07312 | 914 | 0.00208 | 166.4 | 64000 | 914 | 166.4 | 19999.6 | 3697.6 | 1350000 | 19999.6 | 0
2021101820 | 2 | 0.57567 | 86350.5 | 0.79496 | 0 | 0.0748 | 935 | 0 | 0 | 64000 | 935 | 0 | 21415.5 | 1415.9 | 1350000 | 21415.5 | 0
2021101821 | 2 | 0.56221 | 84331.5 | 0.81373 | 0 | 0.07176 | 897 | 0 | 0 | 64000 | 897 | 0 | 19434.5 | -1981 | 1350000 | 19434.5 | 0
2021101822 | 2 | 0.53738 | 80607 | 0.83713 | 0 | 0.07399 | 924.875 | 0 | 0 | 64000 | 924.875 | 0 | 15682.125 | -3752.375 | 1350000 | 15682.125 | 0
2021101823 | 2 | 0.50645 | 75967.5 | 0.89502 | 0 | 0.10496 | 1312 | 0 | 0 | 64000 | 1312 | 0 | 10655.5 | -5026.625 | 1350000 | 10655.5 | 0
2021101824 | 2 | 0.47741 | 71611.5 | 0.86165 | 0 | 0.12745 | 1593.125 | 0 | 0 | 64000 | 1593.125 | 0 | 6018.375 | -4637.125 | 1350000 | 6018.375 | 0
2021101901 | 3 | 0.4553 | 68295 | 0.81531 | 0 | 0.15061 | 1882.625 | 0 | 0 | 64000 | 1882.625 | 0 | 2412.375 | -3606 | 1350000 | 2412.375 | 0
2021101902 | 3 | 0.44292 | 66438 | 0.82643 | 0 | 0.19606 | 2450.75 | 0 | 0 | 64000 | 2438 | 0 | 0 | -2412.375 | 1350000 | 0 | 0
2021101903 | 3 | 0.43796 | 65694 | 0.86528 | 0 | 0.21198 | 2649.75 | 0 | 0 | 64000 | 1694 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101904 | 3 | 0.4371 | 65565 | 0.88975 | 0 | 0.25113 | 3139.125 | 0 | 0 | 64000 | 1565 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101905 | 3 | 0.44708 | 67062 | 0.88454 | 0 | 0.26473 | 3309.125 | 0 | 0 | 64000 | 3062 | 0 | 0 | 0 | 1350000 | 0 | 0
2021101906 | 3 | 0.47396 | 71094 | 0.87245 | 0 | 0.31019 | 3877.375 | 0 | 0 | 64000 | 3877.375 | 0 | 3216.625 | 3216.625 | 1350000 | 3216.625 | 0
2021101907 | 3 | 0.52117 | 78175.5 | 0.88206 | 0 | 0.4123 | 5153.75 | 0 | 0 | 64000 | 5153.75 | 0 | 9021.75 | 5805.125 | 1350000 | 9021.75 | 0
2021101908 | 3 | 0.55617 | 83425.5 | 0.89451 | 0 | 0.4728 | 5910 | 0.02539 | 2031.2 | 64000 | 5910 | 2031.2 | 11484.3 | 2462.55 | 1350000 | 11484.3 | 0
2021101909 | 3 | 0.55954 | 83931 | 0.86485 | 0 | 0.51849 | 6481.125 | 0.11975 | 9580 | 64000 | 6481.125 | 9580 | 3869.875 | -7614.425 | 1350000 | 3869.875 | 0
2021101910 | 3 | 0.55173 | 82759.5 | 0.75457 | 0 | 0.54474 | 6809.25 | 0.26631 | 21304.8 | 64000 | 6809.25 | 11950.25 | 0 | -3869.875 | 1350000 | 0 | 0
2021101911 | 3 | 0.54608 | 81912 | 0.68962 | 0 | 0.54037 | 6754.625 | 0.42435 | 33948 | 64000 | 6754.625 | 11157.375 | 0 | 0 | 1350000 | 0 | 0
2021101912 | 3 | 0.54209 | 81313.5 | 0.77064 | 0 | 0.53059 | 6632.375 | 0.5002 | 40016 | 64000 | 6632.375 | 10681.125 | 0 | 0 | 1350000 | 0 | 0
2021101913 | 3 | 0.5413 | 81195 | 0.81648 | 0 | 0.55743 | 6967.875 | 0.51578 | 41262.4 | 64000 | 6967.875 | 10227.125 | 0 | 0 | 1350000 | 0 | 0
2021101914 | 3 | 0.54394 | 81591 | 0.81158 | 0 | 0.55756 | 6969.5 | 0.52995 | 42396 | 64000 | 6969.5 | 10621.5 | 0 | 0 | 1350000 | 0 | 0
2021101915 | 3 | 0.54399 | 81598.5 | 0.80701 | 0 | 0.55296 | 6912 | 0.52138 | 41710.4 | 64000 | 6912 | 10686.5 | 0 | 0 | 1350000 | 0 | 0
2021101916 | 3 | 0.54642 | 81963 | 0.82573 | 0 | 0.638 | 7975 | 0.48357 | 38685.6 | 64000 | 7975 | 9988 | 0 | 0 | 1350000 | 0 | 0
2021101917 | 3 | 0.55434 | 83151 | 0.84081 | 0 | 0.68797 | 8599.625 | 0.3557 | 28456 | 64000 | 8599.625 | 10551.375 | 0 | 0 | 1350000 | 0 | 0
2021101918 | 3 | 0.56234 | 84351 | 0.7732 | 0 | 0.70961 | 8870.125 | 0.16108 | 12886.4 | 64000 | 8870.125 | 11480.875 | 0 | 0 | 1350000 | 0 | 0
2021101919 | 3 | 0.57074 | 85611 | 0.80083 | 0 | 0.70632 | 8829 | 0.01792 | 1433.6 | 64000 | 8829 | 1433.6 | 11348.4 | 11348.4 | 1350000 | 11348.4 | 0
2021101920 | 3 | 0.57817 | 86725.5 | 0.8716 | 0 | 0.71085 | 8885.625 | 0 | 0 | 64000 | 8885.625 | 0 | 13839.875 | 2491.475 | 1350000 | 13839.875 | 0
2021101921 | 3 | 0.56461 | 84691.5 | 0.93975 | 0 | 0.74128 | 9266 | 0 | 0 | 64000 | 9266 | 0 | 11425.5 | -2414.375 | 1350000 | 11425.5 | 0
2021101922 | 3 | 0.53837 | 80755.5 | 0.96814 | 0 | 0.76862 | 9607.75 | 0 | 0 | 64000 | 9607.75 | 0 | 7147.75 | -4277.75 | 1350000 | 7147.75 | 0
2021101923 | 3 | 0.50611 | 75916.5 | 0.98687 | 0 | 0.76957 | 9619.625 | 0 | 0 | 64000 | 9619.625 | 0 | 2296.875 | -4850.875 | 1350000 | 2296.875 | 0
2021101924 | 3 | 0.477 | 71550 | 0.97737 | 0 | 0.78325 | 9790.625 | 0 | 0 | 64000 | 7550 | 0 | 0 | -2296.875 | 1350000 | 0 | 0
2021102001 | 4 | 0.45325 | 67987.5 | 0.96133 | 0 | 0.78501 | 9812.625 | 0 | 0 | 64000 | 3987.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102002 | 4 | 0.44054 | 66081 | 0.94224 | 0 | 0.78649 | 9831.125 | 0 | 0 | 64000 | 2081 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102003 | 4 | 0.43187 | 64780.5 | 0.95334 | 0 | 0.77902 | 9737.75 | 0 | 0 | 64000 | 780.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102004 | 4 | 0.42992 | 64488 | 0.93912 | 0 | 0.78992 | 9874 | 0 | 0 | 64000 | 488 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102005 | 4 | 0.43753 | 65629.5 | 0.91064 | 0 | 0.79065 | 9883.125 | 0 | 0 | 64000 | 1629.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102006 | 4 | 0.46309 | 69463.5 | 0.87542 | 0 | 0.79406 | 9925.75 | 0 | 0 | 64000 | 5463.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102007 | 4 | 0.50979 | 76468.5 | 0.83071 | 0 | 0.79408 | 9926 | 0 | 0 | 64000 | 9926 | 0 | 2542.5 | 2542.5 | 1350000 | 2542.5 | 0
2021102008 | 4 | 0.542 | 81300 | 0.84063 | 0 | 0.74979 | 9372.375 | 0.04381 | 3504.8 | 64000 | 9372.375 | 3504.8 | 4422.825 | 1880.325 | 1350000 | 4422.825 | 0
2021102009 | 4 | 0.54835 | 82252.5 | 0.77918 | 0 | 0.67266 | 8408.25 | 0.17051 | 13640.8 | 64000 | 8408.25 | 9844.25 | 0 | -4422.825 | 1350000 | 0 | 0
2021102010 | 4 | 0.54446 | 81669 | 0.55622 | 0 | 0.6306 | 7882.5 | 0.29237 | 23389.6 | 64000 | 7882.5 | 9786.5 | 0 | 0 | 1350000 | 0 | 0
2021102011 | 4 | 0.54343 | 81514.5 | 0.40542 | 0 | 0.63122 | 7890.25 | 0.40681 | 32544.8 | 64000 | 7890.25 | 9624.25 | 0 | 0 | 1350000 | 0 | 0
2021102012 | 4 | 0.54373 | 81559.5 | 0.43546 | 0 | 0.66918 | 8364.75 | 0.49845 | 39876 | 64000 | 8364.75 | 9194.75 | 0 | 0 | 1350000 | 0 | 0
2021102013 | 4 | 0.54835 | 82252.5 | 0.5123 | 0 | 0.66329 | 8291.125 | 0.51434 | 41147.2 | 64000 | 8291.125 | 9961.375 | 0 | 0 | 1350000 | 0 | 0
2021102014 | 4 | 0.55393 | 83089.5 | 0.47696 | 0 | 0.63069 | 7883.625 | 0.5724 | 45792 | 64000 | 7883.625 | 11205.875 | 0 | 0 | 1350000 | 0 | 0
2021102015 | 4 | 0.55868 | 83802 | 0.45486 | 0 | 0.57861 | 7232.625 | 0.58628 | 46902.4 | 64000 | 7232.625 | 12569.375 | 0 | 0 | 1350000 | 0 | 0
2021102016 | 4 | 0.56223 | 84334.5 | 0.39079 | 0 | 0.49724 | 6215.5 | 0.5634 | 45072 | 64000 | 6215.5 | 14119 | 0 | 0 | 1350000 | 0 | 0
2021102017 | 4 | 0.57056 | 85584 | 0.31385 | 0 | 0.42631 | 5328.875 | 0.48723 | 38978.4 | 64000 | 5328.875 | 16255.125 | 0 | 0 | 1350000 | 0 | 0
2021102018 | 4 | 0.57704 | 86556 | 0.30156 | 0 | 0.36266 | 4533.25 | 0.22733 | 18186.4 | 64000 | 4533.25 | 18022.75 | 0 | 0 | 1350000 | 0 | 0
2021102019 | 4 | 0.58008 | 87012 | 0.34852 | 0 | 0.31233 | 3904.125 | 0.02154 | 1723.2 | 64000 | 3904.125 | 1723.2 | 17384.675 | 17384.675 | 1350000 | 17384.675 | 0
2021102020 | 4 | 0.58451 | 87676.5 | 0.52798 | 0 | 0.28008 | 3501 | 0 | 0 | 64000 | 3501 | 0 | 20175.5 | 2790.825 | 1350000 | 20175.5 | 0
2021102021 | 4 | 0.56842 | 85263 | 0.67745 | 0 | 0.26372 | 3296.5 | 0 | 0 | 64000 | 3296.5 | 0 | 17966.5 | -2209 | 1350000 | 17966.5 | 0
2021102022 | 4 | 0.54323 | 81484.5 | 0.77295 | 0 | 0.24695 | 3086.875 | 0 | 0 | 64000 | 3086.875 | 0 | 14397.625 | -3568.875 | 1350000 | 14397.625 | 0
2021102023 | 4 | 0.50996 | 76494 | 0.82149 | 0 | 0.24898 | 3112.25 | 0 | 0 | 64000 | 3112.25 | 0 | 9381.75 | -5015.875 | 1350000 | 9381.75 | 0
2021102024 | 4 | 0.47915 | 71872.5 | 0.83576 | 0 | 0.25525 | 3190.625 | 0 | 0 | 64000 | 3190.625 | 0 | 4681.875 | -4699.875 | 1350000 | 4681.875 | 0
2021102101 | 5 | 0.45553 | 68329.5 | 0.83145 | 0 | 0.25654 | 3206.75 | 0 | 0 | 64000 | 3206.75 | 0 | 1122.75 | -3559.125 | 1350000 | 1122.75 | 0
2021102102 | 5 | 0.43884 | 65826 | 0.82725 | 0 | 0.24424 | 3053 | 0 | 0 | 64000 | 1826 | 0 | 0 | -1122.75 | 1350000 | 0 | 0
2021102103 | 5 | 0.43141 | 64711.5 | 0.80529 | 0 | 0.20805 | 2600.625 | 0 | 0 | 64000 | 711.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102104 | 5 | 0.42754 | 64131 | 0.77674 | 0 | 0.18796 | 2349.5 | 0 | 0 | 64000 | 131 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102105 | 5 | 0.43394 | 65091 | 0.76036 | 0 | 0.15939 | 1992.375 | 0 | 0 | 64000 | 1091 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102106 | 5 | 0.45855 | 68782.5 | 0.73654 | 0 | 0.11979 | 1497.375 | 0 | 0 | 64000 | 1497.375 | 0 | 3285.125 | 3285.125 | 1350000 | 3285.125 | 0
2021102107 | 5 | 0.50281 | 75421.5 | 0.72202 | 0 | 0.09001 | 1125.125 | 0.00071 | 56.8 | 64000 | 1125.125 | 56.8 | 10239.575 | 6954.45 | 1350000 | 10239.575 | 0
2021102108 | 5 | 0.5358 | 80370 | 0.67159 | 0 | 0.07811 | 976.375 | 0.06118 | 4894.4 | 64000 | 976.375 | 4894.4 | 10499.225 | 259.65 | 1350000 | 10499.225 | 0
2021102109 | 5 | 0.54293 | 81439.5 | 0.63387 | 0 | 0.07536 | 942 | 0.20761 | 16608.8 | 64000 | 942 | 16497.5 | 0 | -10499.225 | 1350000 | 0 | 0
2021102110 | 5 | 0.54406 | 81609 | 0.50906 | 0 | 0.07045 | 880.625 | 0.30973 | 24778.4 | 64000 | 880.625 | 16728.375 | 0 | 0 | 1350000 | 0 | 0
2021102111 | 5 | 0.54781 | 82171.5 | 0.46194 | 0 | 0.06349 | 793.625 | 0.41112 | 32889.6 | 64000 | 793.625 | 17377.875 | 0 | 0 | 1350000 | 0 | 0
2021102112 | 5 | 0.55168 | 82752 | 0.53008 | 0 | 0.05421 | 677.625 | 0.48378 | 38702.4 | 64000 | 677.625 | 18074.375 | 0 | 0 | 1350000 | 0 | 0
2021102113 | 5 | 0.55664 | 83496 | 0.51418 | 0 | 0.04949 | 618.625 | 0.48302 | 38641.6 | 64000 | 618.625 | 18877.375 | 0 | 0 | 1350000 | 0 | 0
2021102114 | 5 | 0.5614 | 84210 | 0.51036 | 0 | 0.05649 | 706.125 | 0.47323 | 37858.4 | 64000 | 706.125 | 19503.875 | 0 | 0 | 1350000 | 0 | 0
2021102115 | 5 | 0.56474 | 84711 | 0.57422 | 0 | 0.06617 | 827.125 | 0.4308 | 34464 | 64000 | 827.125 | 19883.875 | 0 | 0 | 1350000 | 0 | 0
2021102116 | 5 | 0.56745 | 85117.5 | 0.63375 | 0 | 0.0954 | 1192.5 | 0.37393 | 29914.4 | 64000 | 1192.5 | 19925 | 0 | 0 | 1350000 | 0 | 0
2021102117 | 5 | 0.57184 | 85776 | 0.61791 | 0 | 0.16821 | 2102.625 | 0.28961 | 23168.8 | 64000 | 2102.625 | 19673.375 | 0 | 0 | 1350000 | 0 | 0
2021102118 | 5 | 0.57292 | 85938 | 0.53028 | 0 | 0.2336 | 2920 | 0.12109 | 9687.2 | 64000 | 2920 | 9687.2 | 9330.8 | 9330.8 | 1350000 | 9330.8 | 0
2021102119 | 5 | 0.57891 | 86836.5 | 0.53422 | 0 | 0.26896 | 3362 | 0.00897 | 717.6 | 64000 | 3362 | 717.6 | 18756.9 | 9426.1 | 1350000 | 18756.9 | 0
2021102120 | 5 | 0.58272 | 87408 | 0.63595 | 0 | 0.28225 | 3528.125 | 0 | 0 | 64000 | 3528.125 | 0 | 19879.875 | 1122.975 | 1350000 | 19879.875 | 0
2021102121 | 5 | 0.56704 | 85056 | 0.72221 | 0 | 0.29616 | 3702 | 0 | 0 | 64000 | 3702 | 0 | 17354 | -2525.875 | 1350000 | 17354 | 0
2021102122 | 5 | 0.54233 | 81349.5 | 0.80221 | 0 | 0.30835 | 3854.375 | 0 | 0 | 64000 | 3854.375 | 0 | 13495.125 | -3858.875 | 1350000 | 13495.125 | 0
2021102123 | 5 | 0.51065 | 76597.5 | 0.83295 | 0 | 0.31317 | 3914.625 | 0 | 0 | 64000 | 3914.625 | 0 | 8682.875 | -4812.25 | 1350000 | 8682.875 | 0
2021102124 | 5 | 0.47962 | 71943 | 0.82241 | 0 | 0.30083 | 3760.375 | 0 | 0 | 64000 | 3760.375 | 0 | 4182.625 | -4500.25 | 1350000 | 4182.625 | 0
2021102201 | 6 | 0.45646 | 68469 | 0.79919 | 0 | 0.3013 | 3766.25 | 0 | 0 | 64000 | 3766.25 | 0 | 702.75 | -3479.875 | 1350000 | 702.75 | 0
2021102202 | 6 | 0.4395 | 65925 | 0.76998 | 0 | 0.2852 | 3565 | 0 | 0 | 64000 | 1925 | 0 | 0 | -702.75 | 1350000 | 0 | 0
2021102203 | 6 | 0.43165 | 64747.5 | 0.76723 | 0 | 0.28009 | 3501.125 | 0 | 0 | 64000 | 747.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102204 | 6 | 0.42844 | 64266 | 0.76883 | 0 | 0.2856 | 3570 | 0 | 0 | 64000 | 266 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102205 | 6 | 0.43463 | 65194.5 | 0.78675 | 0 | 0.26879 | 3359.875 | 0 | 0 | 64000 | 1194.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102206 | 6 | 0.45784 | 68676 | 0.72739 | 0 | 0.27159 | 3394.875 | 0 | 0 | 64000 | 3394.875 | 0 | 1281.125 | 1281.125 | 1350000 | 1281.125 | 0
2021102207 | 6 | 0.49884 | 74826 | 0.72286 | 0 | 0.27566 | 3445.75 | 0 | 0 | 64000 | 3445.75 | 0 | 7380.25 | 6099.125 | 1350000 | 7380.25 | 0
2021102208 | 6 | 0.53225 | 79837.5 | 0.61851 | 0 | 0.26995 | 3374.375 | 0.06021 | 4816.8 | 64000 | 3374.375 | 4816.8 | 7646.325 | 266.075 | 1350000 | 7646.325 | 0
2021102209 | 6 | 0.54435 | 81652.5 | 0.54457 | 0 | 0.29179 | 3647.375 | 0.19556 | 15644.8 | 64000 | 3647.375 | 14005.125 | 0 | -7646.325 | 1350000 | 0 | 0
2021102210 | 6 | 0.5472 | 82080 | 0.39128 | 0 | 0.31385 | 3923.125 | 0.2941 | 23528 | 64000 | 3923.125 | 14156.875 | 0 | 0 | 1350000 | 0 | 0
2021102211 | 6 | 0.54994 | 82491 | 0.27039 | 0 | 0.27303 | 3412.875 | 0.36204 | 28963.2 | 64000 | 3412.875 | 15078.125 | 0 | 0 | 1350000 | 0 | 0
2021102212 | 6 | 0.55009 | 82513.5 | 0.23509 | 0 | 0.23599 | 2949.875 | 0.4053 | 32424 | 64000 | 2949.875 | 15563.625 | 0 | 0 | 1350000 | 0 | 0
2021102213 | 6 | 0.55077 | 82615.5 | 0.21272 | 0 | 0.20283 | 2535.375 | 0.41956 | 33564.8 | 64000 | 2535.375 | 16080.125 | 0 | 0 | 1350000 | 0 | 0
2021102214 | 6 | 0.55089 | 82633.5 | 0.19774 | 0 | 0.14723 | 1840.375 | 0.40668 | 32534.4 | 64000 | 1840.375 | 16793.125 | 0 | 0 | 1350000 | 0 | 0
2021102215 | 6 | 0.54884 | 82326 | 0.18714 | 0 | 0.13402 | 1675.25 | 0.3986 | 31888 | 64000 | 1675.25 | 16650.75 | 0 | 0 | 1350000 | 0 | 0
2021102216 | 6 | 0.54588 | 81882 | 0.18055 | 0 | 0.15004 | 1875.5 | 0.38188 | 30550.4 | 64000 | 1875.5 | 16006.5 | 0 | 0 | 1350000 | 0 | 0
2021102217 | 6 | 0.54768 | 82152 | 0.12808 | 0 | 0.23702 | 2962.75 | 0.27667 | 22133.6 | 64000 | 2962.75 | 15189.25 | 0 | 0 | 1350000 | 0 | 0
2021102218 | 6 | 0.54899 | 82348.5 | 0.0967 | 0 | 0.30298 | 3787.25 | 0.11579 | 9263.2 | 64000 | 3787.25 | 9263.2 | 5298.05 | 5298.05 | 1350000 | 5298.05 | 0
2021102219 | 6 | 0.55563 | 83344.5 | 0.11332 | 0 | 0.35188 | 4398.5 | 0.0079 | 632 | 64000 | 4398.5 | 632 | 14314 | 9015.95 | 1350000 | 14314 | 0
2021102220 | 6 | 0.55629 | 83443.5 | 0.13183 | 0 | 0.37378 | 4672.25 | 0 | 0 | 64000 | 4672.25 | 0 | 14771.25 | 457.25 | 1350000 | 14771.25 | 0
2021102221 | 6 | 0.54194 | 81291 | 0.12267 | 0 | 0.36849 | 4606.125 | 0 | 0 | 64000 | 4606.125 | 0 | 12684.875 | -2086.375 | 1350000 | 12684.875 | 0
2021102222 | 6 | 0.5242 | 78630 | 0.10146 | 0 | 0.36691 | 4586.375 | 0 | 0 | 64000 | 4586.375 | 0 | 10043.625 | -2641.25 | 1350000 | 10043.625 | 0
2021102223 | 6 | 0.49939 | 74908.5 | 0.14218 | 0 | 0.34399 | 4299.875 | 0 | 0 | 64000 | 4299.875 | 0 | 6608.625 | -3435 | 1350000 | 6608.625 | 0
2021102224 | 6 | 0.47321 | 70981.5 | 0.16536 | 0 | 0.31558 | 3944.75 | 0 | 0 | 64000 | 3944.75 | 0 | 3036.75 | -3571.875 | 1350000 | 3036.75 | 0
2021102301 | 7 | 0.44945 | 67417.5 | 0.10482 | 0 | 0.34331 | 4291.375 | 0 | 0 | 64000 | 3417.5 | 0 | 0 | -3036.75 | 1350000 | 0 | 0
2021102302 | 7 | 0.43456 | 65184 | 0.09465 | 0 | 0.3839 | 4798.75 | 0 | 0 | 64000 | 1184 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102303 | 7 | 0.42439 | 63658.5 | 0.05025 | 0 | 0.39101 | 4887.625 | 0 | 0 | 63658.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102304 | 7 | 0.41975 | 62962.5 | 0.03601 | 0 | 0.36789 | 4598.625 | 0 | 0 | 62962.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102305 | 7 | 0.42042 | 63063 | 0.03807 | 0 | 0.34985 | 4373.125 | 0 | 0 | 63063 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102306 | 7 | 0.42934 | 64401 | 0.02761 | 0 | 0.36398 | 4549.75 | 0 | 0 | 64000 | 401 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102307 | 7 | 0.44568 | 66852 | 0.00456 | 0 | 0.37396 | 4674.5 | 0 | 0 | 64000 | 2852 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102308 | 7 | 0.46721 | 70081.5 | 0.01616 | 0 | 0.43711 | 5463.875 | 0.08691 | 6952.8 | 64000 | 5463.875 | 617.625 | 0 | 0 | 1350000 | 0 | 0
2021102309 | 7 | 0.48652 | 72978 | 0.04115 | 0 | 0.45616 | 5702 | 0.33006 | 26404.8 | 64000 | 5702 | 3276 | 0 | 0 | 1350000 | 0 | 0
2021102310 | 7 | 0.49838 | 74757 | 0.09788 | 0 | 0.4544 | 5680 | 0.47241 | 37792.8 | 64000 | 5680 | 5077 | 0 | 0 | 1350000 | 0 | 0
2021102311 | 7 | 0.50154 | 75231 | 0.11007 | 0 | 0.4759 | 5948.75 | 0.52971 | 42376.8 | 64000 | 5948.75 | 5282.25 | 0 | 0 | 1350000 | 0 | 0
2021102312 | 7 | 0.49726 | 74589 | 0.14552 | 0 | 0.47649 | 5956.125 | 0.54083 | 43266.4 | 64000 | 5956.125 | 4632.875 | 0 | 0 | 1350000 | 0 | 0
2021102313 | 7 | 0.49322 | 73983 | 0.14378 | 0 | 0.49441 | 6180.125 | 0.53393 | 42714.4 | 64000 | 6180.125 | 3802.875 | 0 | 0 | 1350000 | 0 | 0
2021102314 | 7 | 0.49037 | 73555.5 | 0.20192 | 0 | 0.54964 | 6870.5 | 0.55068 | 44054.4 | 64000 | 6870.5 | 2685 | 0 | 0 | 1350000 | 0 | 0
2021102315 | 7 | 0.48473 | 72709.5 | 0.34306 | 0 | 0.61266 | 7658.25 | 0.55359 | 44287.2 | 64000 | 7658.25 | 1051.25 | 0 | 0 | 1350000 | 0 | 0
2021102316 | 7 | 0.48536 | 72804 | 0.38318 | 0 | 0.61859 | 7732.375 | 0.48991 | 39192.8 | 64000 | 7732.375 | 1071.625 | 0 | 0 | 1350000 | 0 | 0
2021102317 | 7 | 0.49098 | 73647 | 0.38089 | 0 | 0.6258 | 7822.5 | 0.38723 | 30978.4 | 64000 | 7822.5 | 1824.5 | 0 | 0 | 1350000 | 0 | 0
2021102318 | 7 | 0.4994 | 74910 | 0.3447 | 0 | 0.61989 | 7748.625 | 0.1486 | 11888 | 64000 | 7748.625 | 3161.375 | 0 | 0 | 1350000 | 0 | 0
2021102319 | 7 | 0.51166 | 76749 | 0.23418 | 0 | 0.65677 | 8209.625 | 0.00691 | 552.8 | 64000 | 8209.625 | 552.8 | 3986.575 | 3986.575 | 1350000 | 3986.575 | 0
2021102320 | 7 | 0.51752 | 77628 | 0.19639 | 0 | 0.69858 | 8732.25 | 0 | 0 | 64000 | 8732.25 | 0 | 4895.75 | 909.175 | 1350000 | 4895.75 | 0
2021102321 | 7 | 0.50863 | 76294.5 | 0.22288 | 0 | 0.72397 | 9049.625 | 0 | 0 | 64000 | 9049.625 | 0 | 3244.875 | -1650.875 | 1350000 | 3244.875 | 0
2021102322 | 7 | 0.49575 | 74362.5 | 0.24441 | 0 | 0.72654 | 9081.75 | 0 | 0 | 64000 | 9081.75 | 0 | 1280.75 | -1964.125 | 1350000 | 1280.75 | 0
2021102323 | 7 | 0.47549 | 71323.5 | 0.23928 | 0 | 0.74781 | 9347.625 | 0 | 0 | 64000 | 7323.5 | 0 | 0 | -1280.75 | 1350000 | 0 | 0
2021102324 | 7 | 0.4544 | 68160 | 0.21464 | 0 | 0.76442 | 9555.25 | 0 | 0 | 64000 | 4160 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102401 | 1 | 0.43472 | 65208 | 0.15812 | 0 | 0.7634 | 9542.5 | 0 | 0 | 64000 | 1208 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102402 | 1 | 0.42082 | 63123 | 0.16962 | 0 | 0.7599 | 9498.75 | 0 | 0 | 63123 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102403 | 1 | 0.41273 | 61909.5 | 0.1811 | 0 | 0.78068 | 9758.5 | 0 | 0 | 61909.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102404 | 1 | 0.40929 | 61393.5 | 0.16625 | 0 | 0.784 | 9800 | 0 | 0 | 61393.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102405 | 1 | 0.40916 | 61374 | 0.17508 | 0 | 0.77442 | 9680.25 | 0 | 0 | 61374 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102406 | 1 | 0.41598 | 62397 | 0.16171 | 0 | 0.77136 | 9642 | 0 | 0 | 62397 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102407 | 1 | 0.42898 | 64347 | 0.14331 | 0 | 0.74449 | 9306.125 | 0 | 0 | 64000 | 347 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102408 | 1 | 0.44584 | 66876 | 0.11319 | 0 | 0.72548 | 9068.5 | 0.06095 | 4876 | 64000 | 2876 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102409 | 1 | 0.46161 | 69241.5 | 0.17432 | 0 | 0.70953 | 8869.125 | 0.30764 | 24611.2 | 64000 | 5241.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102410 | 1 | 0.47535 | 71302.5 | 0.10934 | 0 | 0.67847 | 8480.875 | 0.46988 | 37590.4 | 64000 | 7302.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102411 | 1 | 0.4837 | 72555 | 0.08986 | 0 | 0.70377 | 8797.125 | 0.53589 | 42871.2 | 64000 | 8555 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102412 | 1 | 0.48917 | 73375.5 | 0.08776 | 0 | 0.71543 | 8942.875 | 0.55191 | 44152.8 | 64000 | 8942.875 | 432.625 | 0 | 0 | 1350000 | 0 | 0
2021102413 | 1 | 0.49452 | 74178 | 0.10734 | 0 | 0.71653 | 8956.625 | 0.55809 | 44647.2 | 64000 | 8956.625 | 1221.375 | 0 | 0 | 1350000 | 0 | 0
2021102414 | 1 | 0.49231 | 73846.5 | 0.12105 | 0 | 0.70856 | 8857 | 0.55572 | 44457.6 | 64000 | 8857 | 989.5 | 0 | 0 | 1350000 | 0 | 0
2021102415 | 1 | 0.49155 | 73732.5 | 0.12456 | 0 | 0.70502 | 8812.75 | 0.5567 | 44536 | 64000 | 8812.75 | 919.75 | 0 | 0 | 1350000 | 0 | 0
2021102416 | 1 | 0.49429 | 74143.5 | 0.14022 | 0 | 0.70707 | 8838.375 | 0.53716 | 42972.8 | 64000 | 8838.375 | 1305.125 | 0 | 0 | 1350000 | 0 | 0
2021102417 | 1 | 0.50611 | 75916.5 | 0.20904 | 0 | 0.69694 | 8711.75 | 0.4355 | 34840 | 64000 | 8711.75 | 3204.75 | 0 | 0 | 1350000 | 0 | 0
2021102418 | 1 | 0.52163 | 78244.5 | 0.27785 | 0 | 0.70249 | 8781.125 | 0.18499 | 14799.2 | 64000 | 8781.125 | 5463.375 | 0 | 0 | 1350000 | 0 | 0
2021102419 | 1 | 0.53775 | 80662.5 | 0.44898 | 0 | 0.69187 | 8648.375 | 0.0096 | 768 | 64000 | 8648.375 | 768 | 7246.125 | 7246.125 | 1350000 | 7246.125 | 0
2021102420 | 1 | 0.54377 | 81565.5 | 0.57127 | 0 | 0.66772 | 8346.5 | 0 | 0 | 64000 | 8346.5 | 0 | 9219 | 1972.875 | 1350000 | 9219 | 0
2021102421 | 1 | 0.53144 | 79716 | 0.60613 | 0 | 0.65631 | 8203.875 | 0 | 0 | 64000 | 8203.875 | 0 | 7512.125 | -1706.875 | 1350000 | 7512.125 | 0
2021102422 | 1 | 0.51049 | 76573.5 | 0.68451 | 0 | 0.64861 | 8107.625 | 0 | 0 | 64000 | 8107.625 | 0 | 4465.875 | -3046.25 | 1350000 | 4465.875 | 0
2021102423 | 1 | 0.48438 | 72657 | 0.75614 | 0 | 0.65064 | 8133 | 0 | 0 | 64000 | 8133 | 0 | 524 | -3941.875 | 1350000 | 524 | 0
2021102424 | 1 | 0.45962 | 68943 | 0.82229 | 0 | 0.66575 | 8321.875 | 0 | 0 | 64000 | 4943 | 0 | 0 | -524 | 1350000 | 0 | 0
2021102501 | 2 | 0.44074 | 66111 | 0.84021 | 0 | 0.66173 | 8271.625 | 0 | 0 | 64000 | 2111 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102502 | 2 | 0.42859 | 64288.5 | 0.86458 | 0 | 0.67053 | 8381.625 | 0 | 0 | 64000 | 288.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102503 | 2 | 0.42228 | 63342 | 0.86961 | 0 | 0.67442 | 8430.25 | 0 | 0 | 63342 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102504 | 2 | 0.42144 | 63216 | 0.90329 | 0 | 0.66518 | 8314.75 | 0 | 0 | 63216 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102505 | 2 | 0.43003 | 64504.5 | 0.91995 | 0 | 0.63805 | 7975.625 | 0 | 0 | 64000 | 504.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102506 | 2 | 0.45696 | 68544 | 0.90031 | 0 | 0.59604 | 7450.5 | 0 | 0 | 64000 | 4544 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102507 | 2 | 0.50383 | 75574.5 | 0.8777 | 0 | 0.56689 | 7086.125 | 0 | 0 | 64000 | 7086.125 | 0 | 4488.375 | 4488.375 | 1350000 | 4488.375 | 0
2021102508 | 2 | 0.54177 | 81265.5 | 0.8613 | 0 | 0.59409 | 7426.125 | 0.06122 | 4897.6 | 64000 | 7426.125 | 4897.6 | 4941.775 | 453.4 | 1350000 | 4941.775 | 0
2021102509 | 2 | 0.55313 | 82969.5 | 0.81806 | 0 | 0.61401 | 7675.125 | 0.2716 | 21728 | 64000 | 7675.125 | 11294.375 | 0 | -4941.775 | 1350000 | 0 | 0
2021102510 | 2 | 0.55921 | 83881.5 | 0.71962 | 0 | 0.61398 | 7674.75 | 0.42861 | 34288.8 | 64000 | 7674.75 | 12206.75 | 0 | 0 | 1350000 | 0 | 0
2021102511 | 2 | 0.56447 | 84670.5 | 0.61504 | 0 | 0.59494 | 7436.75 | 0.48471 | 38776.8 | 64000 | 7436.75 | 13233.75 | 0 | 0 | 1350000 | 0 | 0
2021102512 | 2 | 0.56869 | 85303.5 | 0.53886 | 0 | 0.51626 | 6453.25 | 0.51848 | 41478.4 | 64000 | 6453.25 | 14850.25 | 0 | 0 | 1350000 | 0 | 0
2021102513 | 2 | 0.57209 | 85813.5 | 0.49417 | 0 | 0.31839 | 3979.875 | 0.53985 | 43188 | 64000 | 3979.875 | 17833.625 | 0 | 0 | 1350000 | 0 | 0
2021102514 | 2 | 0.57503 | 86254.5 | 0.47579 | 0 | 0.23356 | 2919.5 | 0.54745 | 43796 | 64000 | 2919.5 | 19335 | 0 | 0 | 1350000 | 0 | 0
2021102515 | 2 | 0.57567 | 86350.5 | 0.39408 | 0 | 0.2267 | 2833.75 | 0.54113 | 43290.4 | 64000 | 2833.75 | 19516.75 | 0 | 0 | 1350000 | 0 | 0
2021102516 | 2 | 0.57525 | 86287.5 | 0.38615 | 0 | 0.32366 | 4045.75 | 0.52137 | 41709.6 | 64000 | 4045.75 | 18241.75 | 0 | 0 | 1350000 | 0 | 0
2021102517 | 2 | 0.57716 | 86574 | 0.37675 | 0 | 0.38586 | 4823.25 | 0.42325 | 33860 | 64000 | 4823.25 | 17750.75 | 0 | 0 | 1350000 | 0 | 0
2021102518 | 2 | 0.58544 | 87816 | 0.46666 | 0 | 0.40342 | 5042.75 | 0.16989 | 13591.2 | 64000 | 5042.75 | 13591.2 | 5182.05 | 5182.05 | 1350000 | 5182.05 | 0
2021102519 | 2 | 0.59602 | 89403 | 0.47116 | 0 | 0.42454 | 5306.75 | 0.00831 | 664.8 | 64000 | 5306.75 | 664.8 | 19431.45 | 14249.4 | 1350000 | 19431.45 | 0
2021102520 | 2 | 0.59539 | 89308.5 | 0.3636 | 0 | 0.47033 | 5879.125 | 0 | 0 | 64000 | 5879.125 | 0 | 19429.375 | -2.075 | 1350000 | 19429.375 | 0
2021102521 | 2 | 0.57779 | 86668.5 | 0.32571 | 0 | 0.55459 | 6932.375 | 0 | 0 | 64000 | 6932.375 | 0 | 15736.125 | -3693.25 | 1350000 | 15736.125 | 0
2021102522 | 2 | 0.55101 | 82651.5 | 0.23265 | 0 | 0.61583 | 7697.875 | 0 | 0 | 64000 | 7697.875 | 0 | 10953.625 | -4782.5 | 1350000 | 10953.625 | 0
2021102523 | 2 | 0.51834 | 77751 | 0.19787 | 0 | 0.66071 | 8258.875 | 0 | 0 | 64000 | 8258.875 | 0 | 5492.125 | -5461.5 | 1350000 | 5492.125 | 0
2021102524 | 2 | 0.48753 | 73129.5 | 0.34784 | 0 | 0.68496 | 8562 | 0 | 0 | 64000 | 8562 | 0 | 567.5 | -4924.625 | 1350000 | 567.5 | 0
2021102601 | 3 | 0.46412 | 69618 | 0.28803 | 0 | 0.68055 | 8506.875 | 0 | 0 | 64000 | 5618 | 0 | 0 | -567.5 | 1350000 | 0 | 0
2021102602 | 3 | 0.44867 | 67300.5 | 0.2916 | 0 | 0.66039 | 8254.875 | 0 | 0 | 64000 | 3300.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102603 | 3 | 0.44076 | 66114 | 0.31323 | 0 | 0.64295 | 8036.875 | 0 | 0 | 64000 | 2114 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102604 | 3 | 0.43824 | 65736 | 0.31763 | 0 | 0.61758 | 7719.75 | 0 | 0 | 64000 | 1736 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102605 | 3 | 0.44451 | 66676.5 | 0.36665 | 0 | 0.55933 | 6991.625 | 0 | 0 | 64000 | 2676.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102606 | 3 | 0.46835 | 70252.5 | 0.37065 | 0 | 0.47637 | 5954.625 | 0 | 0 | 64000 | 5954.625 | 0 | 297.875 | 297.875 | 1350000 | 297.875 | 0
2021102607 | 3 | 0.5128 | 76920 | 0.36953 | 0 | 0.40834 | 5104.25 | 0 | 0 | 64000 | 5104.25 | 0 | 7815.75 | 7517.875 | 1350000 | 7815.75 | 0
2021102608 | 3 | 0.54921 | 82381.5 | 0.52655 | 0 | 0.45507 | 5688.375 | 0.08591 | 6872.8 | 64000 | 5688.375 | 6872.8 | 5820.325 | -1995.425 | 1350000 | 5820.325 | 0
2021102609 | 3 | 0.55933 | 83899.5 | 0.69556 | 0 | 0.53807 | 6725.875 | 0.36276 | 29020.8 | 64000 | 6725.875 | 13173.625 | 0 | -5820.325 | 1350000 | 0 | 0
2021102610 | 3 | 0.56142 | 84213 | 0.79733 | 0 | 0.58069 | 7258.625 | 0.5219 | 41752 | 64000 | 7258.625 | 12954.375 | 0 | 0 | 1350000 | 0 | 0
2021102611 | 3 | 0.56152 | 84228 | 0.86413 | 0 | 0.5957 | 7446.25 | 0.55827 | 44661.6 | 64000 | 7446.25 | 12781.75 | 0 | 0 | 1350000 | 0 | 0
2021102612 | 3 | 0.56231 | 84346.5 | 0.90115 | 0 | 0.598 | 7475 | 0.56332 | 45065.6 | 64000 | 7475 | 12871.5 | 0 | 0 | 1350000 | 0 | 0
2021102613 | 3 | 0.56243 | 84364.5 | 0.95579 | 0 | 0.58817 | 7352.125 | 0.56708 | 45366.4 | 64000 | 7352.125 | 13012.375 | 0 | 0 | 1350000 | 0 | 0
2021102614 | 3 | 0.56154 | 84231 | 0.98258 | 0 | 0.5571 | 6963.75 | 0.58806 | 47044.8 | 64000 | 6963.75 | 13267.25 | 0 | 0 | 1350000 | 0 | 0
2021102615 | 3 | 0.55665 | 83497.5 | 0.98782 | 0 | 0.53755 | 6719.375 | 0.59266 | 47412.8 | 64000 | 6719.375 | 12778.125 | 0 | 0 | 1350000 | 0 | 0
2021102616 | 3 | 0.55399 | 83098.5 | 0.98942 | 0 | 0.5832 | 7290 | 0.57102 | 45681.6 | 64000 | 7290 | 11808.5 | 0 | 0 | 1350000 | 0 | 0
2021102617 | 3 | 0.5533 | 82995 | 0.98868 | 0 | 0.68051 | 8506.375 | 0.46992 | 37593.6 | 64000 | 8506.375 | 10488.625 | 0 | 0 | 1350000 | 0 | 0
2021102618 | 3 | 0.56289 | 84433.5 | 0.9856 | 0 | 0.72553 | 9069.125 | 0.19838 | 15870.4 | 64000 | 9069.125 | 11364.375 | 0 | 0 | 1350000 | 0 | 0
2021102619 | 3 | 0.57884 | 86826 | 0.98124 | 0 | 0.72819 | 9102.375 | 0.01035 | 828 | 64000 | 9102.375 | 828 | 12895.625 | 12895.625 | 1350000 | 12895.625 | 0
2021102620 | 3 | 0.58441 | 87661.5 | 0.96862 | 0 | 0.70947 | 8868.375 | 0 | 0 | 64000 | 8868.375 | 0 | 14793.125 | 1897.5 | 1350000 | 14793.125 | 0
2021102621 | 3 | 0.57231 | 85846.5 | 0.93327 | 0 | 0.68797 | 8599.625 | 0 | 0 | 64000 | 8599.625 | 0 | 13246.875 | -1546.25 | 1350000 | 13246.875 | 0
2021102622 | 3 | 0.54949 | 82423.5 | 0.91231 | 0 | 0.67038 | 8379.75 | 0 | 0 | 64000 | 8379.75 | 0 | 10043.75 | -3203.125 | 1350000 | 10043.75 | 0
2021102623 | 3 | 0.52034 | 78051 | 0.89535 | 0 | 0.63784 | 7973 | 0 | 0 | 64000 | 7973 | 0 | 6078 | -3965.75 | 1350000 | 6078 | 0
2021102624 | 3 | 0.49304 | 73956 | 0.85996 | 0 | 0.59992 | 7499 | 0 | 0 | 64000 | 7499 | 0 | 2457 | -3621 | 1350000 | 2457 | 0
2021102701 | 4 | 0.4727 | 70905 | 0.80692 | 0 | 0.58308 | 7288.5 | 0 | 0 | 64000 | 6905 | 0 | 0 | -2457 | 1350000 | 0 | 0
2021102702 | 4 | 0.45983 | 68974.5 | 0.82693 | 0 | 0.55204 | 6900.5 | 0 | 0 | 64000 | 4974.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102703 | 4 | 0.45357 | 68035.5 | 0.7865 | 0 | 0.52484 | 6560.5 | 0 | 0 | 64000 | 4035.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102704 | 4 | 0.45205 | 67807.5 | 0.74546 | 0 | 0.4993 | 6241.25 | 0 | 0 | 64000 | 3807.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102705 | 4 | 0.45996 | 68994 | 0.73904 | 0 | 0.45342 | 5667.75 | 0 | 0 | 64000 | 4994 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102706 | 4 | 0.48624 | 72936 | 0.76089 | 0 | 0.37571 | 4696.375 | 0 | 0 | 64000 | 4696.375 | 0 | 4239.625 | 4239.625 | 1350000 | 4239.625 | 0
2021102707 | 4 | 0.53303 | 79954.5 | 0.78107 | 0 | 0.26857 | 3357.125 | 0 | 0 | 64000 | 3357.125 | 0 | 12597.375 | 8357.75 | 1350000 | 12597.375 | 0
2021102708 | 4 | 0.56909 | 85363.5 | 0.82146 | 0 | 0.24326 | 3040.75 | 0.09264 | 7411.2 | 64000 | 3040.75 | 7411.2 | 10911.55 | -1685.825 | 1350000 | 10911.55 | 0
2021102709 | 4 | 0.57495 | 86242.5 | 0.84453 | 0 | 0.22617 | 2827.125 | 0.38683 | 30946.4 | 64000 | 2827.125 | 19415.375 | 0 | -10911.55 | 1350000 | 0 | 0
2021102710 | 4 | 0.57063 | 85594.5 | 0.76588 | 0 | 0.21555 | 2694.375 | 0.5435 | 43480 | 64000 | 2694.375 | 18900.125 | 0 | 0 | 1350000 | 0 | 0
2021102711 | 4 | 0.56531 | 84796.5 | 0.72496 | 0 | 0.19994 | 2499.25 | 0.58383 | 46706.4 | 64000 | 2499.25 | 18297.25 | 0 | 0 | 1350000 | 0 | 0
2021102712 | 4 | 0.55968 | 83952 | 0.66924 | 0 | 0.19798 | 2474.75 | 0.59866 | 47892.8 | 64000 | 2474.75 | 17477.25 | 0 | 0 | 1350000 | 0 | 0
2021102713 | 4 | 0.55534 | 83301 | 0.63033 | 0 | 0.18865 | 2358.125 | 0.60271 | 48216.8 | 64000 | 2358.125 | 16942.875 | 0 | 0 | 1350000 | 0 | 0
2021102714 | 4 | 0.5544 | 83160 | 0.60847 | 0 | 0.18606 | 2325.75 | 0.60013 | 48010.4 | 64000 | 2325.75 | 16834.25 | 0 | 0 | 1350000 | 0 | 0
2021102715 | 4 | 0.55157 | 82735.5 | 0.60387 | 0 | 0.17917 | 2239.625 | 0.5973 | 47784 | 64000 | 2239.625 | 16495.875 | 0 | 0 | 1350000 | 0 | 0
2021102716 | 4 | 0.55037 | 82555.5 | 0.60214 | 0 | 0.19976 | 2497 | 0.57986 | 46388.8 | 64000 | 2497 | 16058.5 | 0 | 0 | 1350000 | 0 | 0
2021102717 | 4 | 0.55443 | 83164.5 | 0.55267 | 0 | 0.24939 | 3117.375 | 0.48061 | 38448.8 | 64000 | 3117.375 | 16047.125 | 0 | 0 | 1350000 | 0 | 0
2021102718 | 4 | 0.56329 | 84493.5 | 0.50267 | 0 | 0.24098 | 3012.25 | 0.1916 | 15328 | 64000 | 3012.25 | 15328 | 2153.25 | 2153.25 | 1350000 | 2153.25 | 0
2021102719 | 4 | 0.57754 | 86631 | 0.47626 | 0 | 0.2466 | 3082.5 | 0.00874 | 699.2 | 64000 | 3082.5 | 699.2 | 18849.3 | 16696.05 | 1350000 | 18849.3 | 0
2021102720 | 4 | 0.58292 | 87438 | 0.48433 | 0 | 0.22515 | 2814.375 | 0 | 0 | 64000 | 2814.375 | 0 | 20623.625 | 1774.325 | 1350000 | 20623.625 | 0
2021102721 | 4 | 0.57069 | 85603.5 | 0.47727 | 0 | 0.1723 | 2153.75 | 0 | 0 | 64000 | 2153.75 | 0 | 19449.75 | -1173.875 | 1350000 | 19449.75 | 0
2021102722 | 4 | 0.549 | 82350 | 0.4778 | 0 | 0.13633 | 1704.125 | 0 | 0 | 64000 | 1704.125 | 0 | 16645.875 | -2803.875 | 1350000 | 16645.875 | 0
2021102723 | 4 | 0.51848 | 77772 | 0.4083 | 0 | 0.14165 | 1770.625 | 0 | 0 | 64000 | 1770.625 | 0 | 12001.375 | -4644.5 | 1350000 | 12001.375 | 0
2021102724 | 4 | 0.48866 | 73299 | 0.35957 | 0 | 0.15654 | 1956.75 | 0 | 0 | 64000 | 1956.75 | 0 | 7342.25 | -4659.125 | 1350000 | 7342.25 | 0
2021102801 | 5 | 0.46766 | 70149 | 0.23571 | 0 | 0.17262 | 2157.75 | 0 | 0 | 64000 | 2157.75 | 0 | 3991.25 | -3351 | 1350000 | 3991.25 | 0
2021102802 | 5 | 0.45246 | 67869 | 0.16071 | 0 | 0.19433 | 2429.125 | 0 | 0 | 64000 | 2429.125 | 0 | 1439.875 | -2551.375 | 1350000 | 1439.875 | 0
2021102803 | 5 | 0.44531 | 66796.5 | 0.12783 | 0 | 0.22999 | 2874.875 | 0 | 0 | 64000 | 2796.5 | 0 | 0 | -1439.875 | 1350000 | 0 | 0
2021102804 | 5 | 0.44434 | 66651 | 0.18042 | 0 | 0.24589 | 3073.625 | 0 | 0 | 64000 | 2651 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102805 | 5 | 0.45287 | 67930.5 | 0.28461 | 0 | 0.23055 | 2881.875 | 0 | 0 | 64000 | 2881.875 | 0 | 1048.625 | 1048.625 | 1350000 | 1048.625 | 0
2021102806 | 5 | 0.47978 | 71967 | 0.29976 | 0 | 0.18169 | 2271.125 | 0 | 0 | 64000 | 2271.125 | 0 | 5695.875 | 4647.25 | 1350000 | 5695.875 | 0
2021102807 | 5 | 0.52592 | 78888 | 0.25066 | 0 | 0.17354 | 2169.25 | 0 | 0 | 64000 | 2169.25 | 0 | 12718.75 | 7022.875 | 1350000 | 12718.75 | 0
2021102808 | 5 | 0.55972 | 83958 | 0.29553 | 0 | 0.20915 | 2614.375 | 0.08339 | 6671.2 | 64000 | 2614.375 | 6671.2 | 10672.425 | -2046.325 | 1350000 | 10672.425 | 0
2021102809 | 5 | 0.56655 | 84982.5 | 0.37229 | 0 | 0.21489 | 2686.125 | 0.33804 | 27043.2 | 64000 | 2686.125 | 18296.375 | 0 | -10672.425 | 1350000 | 0 | 0
2021102810 | 5 | 0.56025 | 84037.5 | 0.40385 | 0 | 0.204 | 2550 | 0.46311 | 37048.8 | 64000 | 2550 | 17487.5 | 0 | 0 | 1350000 | 0 | 0
2021102811 | 5 | 0.55819 | 83728.5 | 0.37153 | 0 | 0.18637 | 2329.625 | 0.49847 | 39877.6 | 64000 | 2329.625 | 17398.875 | 0 | 0 | 1350000 | 0 | 0
2021102812 | 5 | 0.55425 | 83137.5 | 0.41298 | 0 | 0.16688 | 2086 | 0.50751 | 40600.8 | 64000 | 2086 | 17051.5 | 0 | 0 | 1350000 | 0 | 0
2021102813 | 5 | 0.55125 | 82687.5 | 0.42898 | 0 | 0.15956 | 1994.5 | 0.51265 | 41012 | 64000 | 1994.5 | 16693 | 0 | 0 | 1350000 | 0 | 0
2021102814 | 5 | 0.55083 | 82624.5 | 0.4222 | 0 | 0.152 | 1900 | 0.51756 | 41404.8 | 64000 | 1900 | 16724.5 | 0 | 0 | 1350000 | 0 | 0
2021102815 | 5 | 0.55089 | 82633.5 | 0.47912 | 0 | 0.14001 | 1750.125 | 0.50258 | 40206.4 | 64000 | 1750.125 | 16883.375 | 0 | 0 | 1350000 | 0 | 0
2021102816 | 5 | 0.55088 | 82632 | 0.58055 | 0 | 0.1523 | 1903.75 | 0.48389 | 38711.2 | 64000 | 1903.75 | 16728.25 | 0 | 0 | 1350000 | 0 | 0
2021102817 | 5 | 0.55541 | 83311.5 | 0.63572 | 0 | 0.15503 | 1937.875 | 0.34544 | 27635.2 | 64000 | 1937.875 | 17373.625 | 0 | 0 | 1350000 | 0 | 0
2021102818 | 5 | 0.56106 | 84159 | 0.67977 | 0 | 0.16914 | 2114.25 | 0.11992 | 9593.6 | 64000 | 2114.25 | 9593.6 | 8451.15 | 8451.15 | 1350000 | 8451.15 | 0
2021102819 | 5 | 0.57567 | 86350.5 | 0.73577 | 0 | 0.19476 | 2434.5 | 0.00514 | 411.2 | 64000 | 2434.5 | 411.2 | 19504.8 | 11053.65 | 1350000 | 19504.8 | 0
2021102820 | 5 | 0.57719 | 86578.5 | 0.82604 | 0 | 0.22941 | 2867.625 | 0 | 0 | 64000 | 2867.625 | 0 | 19710.875 | 206.075 | 1350000 | 19710.875 | 0
2021102821 | 5 | 0.56453 | 84679.5 | 0.88264 | 0 | 0.24349 | 3043.625 | 0 | 0 | 64000 | 3043.625 | 0 | 17635.875 | -2075 | 1350000 | 17635.875 | 0
2021102822 | 5 | 0.54298 | 81447 | 0.9056 | 0 | 0.23354 | 2919.25 | 0 | 0 | 64000 | 2919.25 | 0 | 14527.75 | -3108.125 | 1350000 | 14527.75 | 0
2021102823 | 5 | 0.51282 | 76923 | 0.93657 | 0 | 0.22927 | 2865.875 | 0 | 0 | 64000 | 2865.875 | 0 | 10057.125 | -4470.625 | 1350000 | 10057.125 | 0
2021102824 | 5 | 0.48409 | 72613.5 | 0.9153 | 0 | 0.21863 | 2732.875 | 0 | 0 | 64000 | 2732.875 | 0 | 5880.625 | -4176.5 | 1350000 | 5880.625 | 0
2021102901 | 6 | 0.46229 | 69343.5 | 0.87695 | 0 | 0.25162 | 3145.25 | 0 | 0 | 64000 | 3145.25 | 0 | 2198.25 | -3682.375 | 1350000 | 2198.25 | 0
2021102902 | 6 | 0.44778 | 67167 | 0.86811 | 0 | 0.30237 | 3779.625 | 0 | 0 | 64000 | 3167 | 0 | 0 | -2198.25 | 1350000 | 0 | 0
2021102903 | 6 | 0.43875 | 65812.5 | 0.89375 | 0 | 0.35819 | 4477.375 | 0 | 0 | 64000 | 1812.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102904 | 6 | 0.43628 | 65442 | 0.9016 | 0 | 0.39238 | 4904.75 | 0 | 0 | 64000 | 1442 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102905 | 6 | 0.44277 | 66415.5 | 0.90158 | 0 | 0.39316 | 4914.5 | 0 | 0 | 64000 | 2415.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021102906 | 6 | 0.46519 | 69778.5 | 0.9379 | 0 | 0.34883 | 4360.375 | 0 | 0 | 64000 | 4360.375 | 0 | 1418.125 | 1418.125 | 1350000 | 1418.125 | 0
2021102907 | 6 | 0.50762 | 76143 | 0.95647 | 0 | 0.29289 | 3661.125 | 0 | 0 | 64000 | 3661.125 | 0 | 8481.875 | 7063.75 | 1350000 | 8481.875 | 0
2021102908 | 6 | 0.54407 | 81610.5 | 0.96347 | 0 | 0.30182 | 3772.75 | 0.08203 | 6562.4 | 64000 | 3772.75 | 6562.4 | 7275.35 | -1206.525 | 1350000 | 7275.35 | 0
2021102909 | 6 | 0.55877 | 83815.5 | 0.95107 | 0 | 0.31939 | 3992.375 | 0.36641 | 29312.8 | 64000 | 3992.375 | 15823.125 | 0 | -7275.35 | 1350000 | 0 | 0
2021102910 | 6 | 0.56505 | 84757.5 | 0.93424 | 0 | 0.29952 | 3744 | 0.5321 | 42568 | 64000 | 3744 | 17013.5 | 0 | 0 | 1350000 | 0 | 0
2021102911 | 6 | 0.56932 | 85398 | 0.92593 | 0 | 0.2536 | 3170 | 0.57418 | 45934.4 | 64000 | 3170 | 18228 | 0 | 0 | 1350000 | 0 | 0
2021102912 | 6 | 0.56915 | 85372.5 | 0.92932 | 0 | 0.21709 | 2713.625 | 0.59025 | 47220 | 64000 | 2713.625 | 18658.875 | 0 | 0 | 1350000 | 0 | 0
2021102913 | 6 | 0.56798 | 85197 | 0.90383 | 0 | 0.19145 | 2393.125 | 0.59608 | 47686.4 | 64000 | 2393.125 | 18803.875 | 0 | 0 | 1350000 | 0 | 0
2021102914 | 6 | 0.56741 | 85111.5 | 0.8879 | 0 | 0.18285 | 2285.625 | 0.60228 | 48182.4 | 64000 | 2285.625 | 18825.875 | 0 | 0 | 1350000 | 0 | 0
2021102915 | 6 | 0.56357 | 84535.5 | 0.90399 | 0 | 0.1742 | 2177.5 | 0.60032 | 48025.6 | 64000 | 2177.5 | 18358 | 0 | 0 | 1350000 | 0 | 0
2021102916 | 6 | 0.56103 | 84154.5 | 0.95325 | 0 | 0.18104 | 2263 | 0.5774 | 46192 | 64000 | 2263 | 17891.5 | 0 | 0 | 1350000 | 0 | 0
2021102917 | 6 | 0.56019 | 84028.5 | 0.92962 | 0 | 0.23195 | 2899.375 | 0.47175 | 37740 | 64000 | 2899.375 | 17129.125 | 0 | 0 | 1350000 | 0 | 0
2021102918 | 6 | 0.56499 | 84748.5 | 0.85736 | 0 | 0.26706 | 3338.25 | 0.17415 | 13932 | 64000 | 3338.25 | 13932 | 3478.25 | 3478.25 | 1350000 | 3478.25 | 0
2021102919 | 6 | 0.57045 | 85567.5 | 0.82106 | 0 | 0.30701 | 3837.625 | 0.00589 | 471.2 | 64000 | 3837.625 | 471.2 | 17258.675 | 13780.425 | 1350000 | 17258.675 | 0
2021102920 | 6 | 0.56468 | 84702 | 0.74277 | 0 | 0.32336 | 4042 | 0 | 0 | 64000 | 4042 | 0 | 16660 | -598.675 | 1350000 | 16660 | 0
2021102921 | 6 | 0.55033 | 82549.5 | 0.67087 | 0 | 0.31481 | 3935.125 | 0 | 0 | 64000 | 3935.125 | 0 | 14614.375 | -2045.625 | 1350000 | 14614.375 | 0
2021102922 | 6 | 0.53164 | 79746 | 0.62723 | 0 | 0.29209 | 3651.125 | 0 | 0 | 64000 | 3651.125 | 0 | 12094.875 | -2519.5 | 1350000 | 12094.875 | 0
2021102923 | 6 | 0.50636 | 75954 | 0.68083 | 0 | 0.30714 | 3839.25 | 0 | 0 | 64000 | 3839.25 | 0 | 8114.75 | -3980.125 | 1350000 | 8114.75 | 0
2021102924 | 6 | 0.47997 | 71995.5 | 0.70638 | 0 | 0.33212 | 4151.5 | 0 | 0 | 64000 | 4151.5 | 0 | 3844 | -4270.75 | 1350000 | 3844 | 0
2021103001 | 7 | 0.4579 | 68685 | 0.71063 | 0 | 0.37034 | 4629.25 | 0 | 0 | 64000 | 4629.25 | 0 | 55.75 | -3788.25 | 1350000 | 55.75 | 0
2021103002 | 7 | 0.44232 | 66348 | 0.69294 | 0 | 0.41278 | 5159.75 | 0 | 0 | 64000 | 2348 | 0 | 0 | -55.75 | 1350000 | 0 | 0
2021103003 | 7 | 0.43136 | 64704 | 0.67336 | 0 | 0.45099 | 5637.375 | 0 | 0 | 64000 | 704 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103004 | 7 | 0.42738 | 64107 | 0.57289 | 0 | 0.4558 | 5697.5 | 0 | 0 | 64000 | 107 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103005 | 7 | 0.42658 | 63987 | 0.47123 | 0 | 0.46464 | 5808 | 0 | 0 | 63987 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103006 | 7 | 0.43352 | 65028 | 0.39208 | 0 | 0.46551 | 5818.875 | 0 | 0 | 64000 | 1028 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103007 | 7 | 0.45138 | 67707 | 0.30929 | 0 | 0.47552 | 5944 | 0.00162 | 129.6 | 64000 | 3707 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103008 | 7 | 0.47295 | 70942.5 | 0.25727 | 0 | 0.46049 | 5756.125 | 0.06511 | 5208.8 | 64000 | 5756.125 | 1186.375 | 0 | 0 | 1350000 | 0 | 0
2021103009 | 7 | 0.49134 | 73701 | 0.19949 | 0 | 0.42233 | 5279.125 | 0.30111 | 24088.8 | 64000 | 5279.125 | 4421.875 | 0 | 0 | 1350000 | 0 | 0
2021103010 | 7 | 0.50331 | 75496.5 | 0.16746 | 0 | 0.38865 | 4858.125 | 0.4348 | 34784 | 64000 | 4858.125 | 6638.375 | 0 | 0 | 1350000 | 0 | 0
2021103011 | 7 | 0.50824 | 76236 | 0.18013 | 0 | 0.35596 | 4449.5 | 0.50184 | 40147.2 | 64000 | 4449.5 | 7786.5 | 0 | 0 | 1350000 | 0 | 0
2021103012 | 7 | 0.50643 | 75964.5 | 0.17845 | 0 | 0.33567 | 4195.875 | 0.54508 | 43606.4 | 64000 | 4195.875 | 7768.625 | 0 | 0 | 1350000 | 0 | 0
2021103013 | 7 | 0.50377 | 75565.5 | 0.20547 | 0 | 0.32738 | 4092.25 | 0.55449 | 44359.2 | 64000 | 4092.25 | 7473.25 | 0 | 0 | 1350000 | 0 | 0
2021103014 | 7 | 0.50198 | 75297 | 0.16824 | 0 | 0.35275 | 4409.375 | 0.53638 | 42910.4 | 64000 | 4409.375 | 6887.625 | 0 | 0 | 1350000 | 0 | 0
2021103015 | 7 | 0.49841 | 74761.5 | 0.13059 | 0 | 0.4031 | 5038.75 | 0.52744 | 42195.2 | 64000 | 5038.75 | 5722.75 | 0 | 0 | 1350000 | 0 | 0
2021103016 | 7 | 0.49783 | 74674.5 | 0.1453 | 0 | 0.42677 | 5334.625 | 0.52691 | 42152.8 | 64000 | 5334.625 | 5339.875 | 0 | 0 | 1350000 | 0 | 0
2021103017 | 7 | 0.50097 | 75145.5 | 0.20232 | 0 | 0.40148 | 5018.5 | 0.42174 | 33739.2 | 64000 | 5018.5 | 6127 | 0 | 0 | 1350000 | 0 | 0
2021103018 | 7 | 0.50689 | 76033.5 | 0.15134 | 0 | 0.36382 | 4547.75 | 0.16009 | 12807.2 | 64000 | 4547.75 | 7485.75 | 0 | 0 | 1350000 | 0 | 0
2021103019 | 7 | 0.51998 | 77997 | 0.12036 | 0 | 0.28706 | 3588.25 | 0.01003 | 802.4 | 64000 | 3588.25 | 802.4 | 9606.35 | 9606.35 | 1350000 | 9606.35 | 0
2021103020 | 7 | 0.52154 | 78231 | 0.12553 | 0 | 0.2454 | 3067.5 | 0 | 0 | 64000 | 3067.5 | 0 | 11163.5 | 1557.15 | 1350000 | 11163.5 | 0
2021103021 | 7 | 0.51148 | 76722 | 0.0799 | 0 | 0.23667 | 2958.375 | 0 | 0 | 64000 | 2958.375 | 0 | 9763.625 | -1399.875 | 1350000 | 9763.625 | 0
2021103022 | 7 | 0.49863 | 74794.5 | 0.04779 | 0 | 0.23305 | 2913.125 | 0 | 0 | 64000 | 2913.125 | 0 | 7881.375 | -1882.25 | 1350000 | 7881.375 | 0
2021103023 | 7 | 0.48072 | 72108 | 0.02544 | 0 | 0.24184 | 3023 | 0 | 0 | 64000 | 3023 | 0 | 5085 | -2796.375 | 1350000 | 5085 | 0
2021103024 | 7 | 0.45914 | 68871 | 0.03182 | 0 | 0.23621 | 2952.625 | 0 | 0 | 64000 | 2952.625 | 0 | 1918.375 | -3166.625 | 1350000 | 1918.375 | 0
2021103101 | 1 | 0.44109 | 66163.5 | 0.04231 | 0 | 0.24656 | 3082 | 0 | 0 | 64000 | 2163.5 | 0 | 0 | -1918.375 | 1350000 | 0 | 0
2021103102 | 1 | 0.42639 | 63958.5 | 0.09859 | 0 | 0.27338 | 3417.25 | 0 | 0 | 63958.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103103 | 1 | 0.41821 | 62731.5 | 0.17319 | 0 | 0.29885 | 3735.625 | 0 | 0 | 62731.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103104 | 1 | 0.41338 | 62007 | 0.31027 | 0 | 0.3276 | 4095 | 0 | 0 | 62007 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103105 | 1 | 0.41431 | 62146.5 | 0.36098 | 0 | 0.30115 | 3764.375 | 0 | 0 | 62146.5 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103106 | 1 | 0.41968 | 62952 | 0.36934 | 0 | 0.24833 | 3104.125 | 0 | 0 | 62952 | 0 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103107 | 1 | 0.43207 | 64810.5 | 0.47926 | 0 | 0.20267 | 2533.375 | 0 | 0 | 64000 | 810.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021103108 | 1 | 0.44891 | 67336.5 | 0.5039 | 0 | 0.1979 | 2473.75 | 0.07872 | 6297.6 | 64000 | 2473.75 | 862.75 | 0 | 0 | 1350000 | 0 | 0
2021103109 | 1 | 0.46409 | 69613.5 | 0.52207 | 0 | 0.19933 | 2491.625 | 0.36612 | 29289.6 | 64000 | 2491.625 | 3121.875 | 0 | 0 | 1350000 | 0 | 0
2021103110 | 1 | 0.47446 | 71169 | 0.64548 | 0 | 0.18616 | 2327 | 0.53273 | 42618.4 | 64000 | 2327 | 4842 | 0 | 0 | 1350000 | 0 | 0
2021103111 | 1 | 0.4784 | 71760 | 0.69946 | 0 | 0.17929 | 2241.125 | 0.57354 | 45883.2 | 64000 | 2241.125 | 5518.875 | 0 | 0 | 1350000 | 0 | 0
2021103112 | 1 | 0.48173 | 72259.5 | 0.73126 | 0 | 0.14938 | 1867.25 | 0.58382 | 46705.6 | 64000 | 1867.25 | 6392.25 | 0 | 0 | 1350000 | 0 | 0
2021103113 | 1 | 0.48588 | 72882 | 0.78709 | 0 | 0.13745 | 1718.125 | 0.58858 | 47086.4 | 64000 | 1718.125 | 7163.875 | 0 | 0 | 1350000 | 0 | 0
2021103114 | 1 | 0.48688 | 73032 | 0.78656 | 0 | 0.18254 | 2281.75 | 0.57922 | 46337.6 | 64000 | 2281.75 | 6750.25 | 0 | 0 | 1350000 | 0 | 0
2021103115 | 1 | 0.48696 | 73044 | 0.84364 | 0 | 0.24486 | 3060.75 | 0.5428 | 43424 | 64000 | 3060.75 | 5983.25 | 0 | 0 | 1350000 | 0 | 0
2021103116 | 1 | 0.48639 | 72958.5 | 0.8797 | 0 | 0.35159 | 4394.875 | 0.47923 | 38338.4 | 64000 | 4394.875 | 4563.625 | 0 | 0 | 1350000 | 0 | 0
2021103117 | 1 | 0.49286 | 73929 | 0.86516 | 0 | 0.51764 | 6470.5 | 0.33817 | 27053.6 | 64000 | 6470.5 | 3458.5 | 0 | 0 | 1350000 | 0 | 0
2021103118 | 1 | 0.4994 | 74910 | 0.86047 | 0 | 0.64696 | 8087 | 0.12051 | 9640.8 | 64000 | 8087 | 2823 | 0 | 0 | 1350000 | 0 | 0
2021103119 | 1 | 0.51066 | 76599 | 0.8801 | 0 | 0.71629 | 8953.625 | 0.00411 | 328.8 | 64000 | 8953.625 | 328.8 | 3316.575 | 3316.575 | 1350000 | 3316.575 | 0
2021103120 | 1 | 0.51815 | 77722.5 | 0.88457 | 0 | 0.75748 | 9468.5 | 0 | 0 | 64000 | 9468.5 | 0 | 4254 | 937.425 | 1350000 | 4254 | 0
2021103121 | 1 | 0.51762 | 77643 | 0.91637 | 0 | 0.7891 | 9863.75 | 0 | 0 | 64000 | 9863.75 | 0 | 3779.25 | -474.75 | 1350000 | 3779.25 | 0
2021103122 | 1 | 0.50359 | 75538.5 | 0.90119 | 0 | 0.79828 | 9978.5 | 0 | 0 | 64000 | 9978.5 | 0 | 1560 | -2219.25 | 1350000 | 1560 | 0
2021103123 | 1 | 0.48198 | 72297 | 0.82656 | 0 | 0.78719 | 9839.875 | 0 | 0 | 64000 | 8297 | 0 | 0 | -1560 | 1350000 | 0 | 0
2021103124 | 1 | 0.4604 | 69060 | 0.84428 | 0 | 0.76285 | 9535.625 | 0 | 0 | 64000 | 5060 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110101 | 2 | 0.44434 | 66651 | 0.88917 | 0 | 0.7378 | 9222.5 | 0 | 0 | 64000 | 2651 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110102 | 2 | 0.43291 | 64936.5 | 0.88262 | 0 | 0.7013 | 8766.25 | 0 | 0 | 64000 | 936.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110103 | 2 | 0.43029 | 64543.5 | 0.88301 | 0 | 0.69683 | 8710.375 | 0 | 0 | 64000 | 543.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110104 | 2 | 0.43267 | 64900.5 | 0.92698 | 0 | 0.67856 | 8482 | 0 | 0 | 64000 | 900.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110105 | 2 | 0.4436 | 66540 | 0.94353 | 0 | 0.53631 | 6703.875 | 0 | 0 | 64000 | 2540 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110106 | 2 | 0.47318 | 70977 | 0.93609 | 0 | 0.37618 | 4702.25 | 0 | 0 | 64000 | 4702.25 | 0 | 2274.75 | 2274.75 | 1350000 | 2274.75 | 0
2021110107 | 2 | 0.52127 | 78190.5 | 0.87759 | 0 | 0.2481 | 3101.25 | 0 | 0 | 64000 | 3101.25 | 0 | 11089.25 | 8814.5 | 1350000 | 11089.25 | 0
2021110108 | 2 | 0.56068 | 84102 | 0.80344 | 0 | 0.21189 | 2648.625 | 0.05012 | 4009.6 | 64000 | 2648.625 | 4009.6 | 13443.775 | 2354.525 | 1350000 | 13443.775 | 0
2021110109 | 2 | 0.57002 | 85503 | 0.7483 | 0 | 0.25236 | 3154.5 | 0.18815 | 15052 | 64000 | 3154.5 | 15052 | 3296.5 | -10147.275 | 1350000 | 3296.5 | 0
2021110110 | 2 | 0.56519 | 84778.5 | 0.63868 | 0 | 0.30634 | 3829.25 | 0.35057 | 28045.6 | 64000 | 3829.25 | 16949.25 | 0 | -3296.5 | 1350000 | 0 | 0
2021110111 | 2 | 0.55916 | 83874 | 0.78908 | 0 | 0.29493 | 3686.625 | 0.47523 | 38018.4 | 64000 | 3686.625 | 16187.375 | 0 | 0 | 1350000 | 0 | 0
2021110112 | 2 | 0.55244 | 82866 | 0.81261 | 0 | 0.26047 | 3255.875 | 0.52769 | 42215.2 | 64000 | 3255.875 | 15610.125 | 0 | 0 | 1350000 | 0 | 0
2021110113 | 2 | 0.54544 | 81816 | 0.72228 | 0 | 0.30749 | 3843.625 | 0.57233 | 45786.4 | 64000 | 3843.625 | 13972.375 | 0 | 0 | 1350000 | 0 | 0
2021110114 | 2 | 0.54189 | 81283.5 | 0.64586 | 0 | 0.35382 | 4422.75 | 0.58537 | 46829.6 | 64000 | 4422.75 | 12860.75 | 0 | 0 | 1350000 | 0 | 0
2021110115 | 2 | 0.53895 | 80842.5 | 0.61507 | 0 | 0.37182 | 4647.75 | 0.58711 | 46968.8 | 64000 | 4647.75 | 12194.75 | 0 | 0 | 1350000 | 0 | 0
2021110116 | 2 | 0.53723 | 80584.5 | 0.54826 | 0 | 0.36818 | 4602.25 | 0.57609 | 46087.2 | 64000 | 4602.25 | 11982.25 | 0 | 0 | 1350000 | 0 | 0
2021110117 | 2 | 0.54334 | 81501 | 0.43873 | 0 | 0.3199 | 3998.75 | 0.43772 | 35017.6 | 64000 | 3998.75 | 13502.25 | 0 | 0 | 1350000 | 0 | 0
2021110118 | 2 | 0.55735 | 83602.5 | 0.34917 | 0 | 0.29726 | 3715.75 | 0.13485 | 10788 | 64000 | 3715.75 | 10788 | 5098.75 | 5098.75 | 1350000 | 5098.75 | 0
2021110119 | 2 | 0.57898 | 86847 | 0.2882 | 0 | 0.27656 | 3457 | 0.00374 | 299.2 | 64000 | 3457 | 299.2 | 19090.8 | 13992.05 | 1350000 | 19090.8 | 0
2021110120 | 2 | 0.58542 | 87813 | 0.31309 | 0 | 0.25907 | 3238.375 | 0 | 0 | 64000 | 3238.375 | 0 | 20574.625 | 1483.825 | 1350000 | 20574.625 | 0
2021110121 | 2 | 0.57335 | 86002.5 | 0.34691 | 0 | 0.22374 | 2796.75 | 0 | 0 | 64000 | 2796.75 | 0 | 19205.75 | -1368.875 | 1350000 | 19205.75 | 0
2021110122 | 2 | 0.55259 | 82888.5 | 0.35294 | 0 | 0.21247 | 2655.875 | 0 | 0 | 64000 | 2655.875 | 0 | 16232.625 | -2973.125 | 1350000 | 16232.625 | 0
2021110123 | 2 | 0.52474 | 78711 | 0.34398 | 0 | 0.22986 | 2873.25 | 0 | 0 | 64000 | 2873.25 | 0 | 11837.75 | -4394.875 | 1350000 | 11837.75 | 0
2021110124 | 2 | 0.49783 | 74674.5 | 0.35074 | 0 | 0.24466 | 3058.25 | 0 | 0 | 64000 | 3058.25 | 0 | 7616.25 | -4221.5 | 1350000 | 7616.25 | 0
2021110201 | 3 | 0.47564 | 71346 | 0.34671 | 0 | 0.26186 | 3273.25 | 0 | 0 | 64000 | 3273.25 | 0 | 4072.75 | -3543.5 | 1350000 | 4072.75 | 0
2021110202 | 3 | 0.46405 | 69607.5 | 0.31182 | 0 | 0.28157 | 3519.625 | 0 | 0 | 64000 | 3519.625 | 0 | 2087.875 | -1984.875 | 1350000 | 2087.875 | 0
2021110203 | 3 | 0.45828 | 68742 | 0.33603 | 0 | 0.31745 | 3968.125 | 0 | 0 | 64000 | 3968.125 | 0 | 773.875 | -1314 | 1350000 | 773.875 | 0
2021110204 | 3 | 0.45845 | 68767.5 | 0.36319 | 0 | 0.34494 | 4311.75 | 0 | 0 | 64000 | 4311.75 | 0 | 455.75 | -318.125 | 1350000 | 455.75 | 0
2021110205 | 3 | 0.46766 | 70149 | 0.33893 | 0 | 0.34714 | 4339.25 | 0 | 0 | 64000 | 4339.25 | 0 | 1809.75 | 1354 | 1350000 | 1809.75 | 0
2021110206 | 3 | 0.495 | 74250 | 0.27658 | 0 | 0.37151 | 4643.875 | 0 | 0 | 64000 | 4643.875 | 0 | 5606.125 | 3796.375 | 1350000 | 5606.125 | 0
2021110207 | 3 | 0.54103 | 81154.5 | 0.22534 | 0 | 0.40693 | 5086.625 | 0 | 0 | 64000 | 5086.625 | 0 | 12067.875 | 6461.75 | 1350000 | 12067.875 | 0
2021110208 | 3 | 0.57754 | 86631 | 0.27877 | 0 | 0.41994 | 5249.25 | 0.02014 | 1611.2 | 64000 | 5249.25 | 1611.2 | 15770.55 | 3702.675 | 1350000 | 15770.55 | 0
2021110209 | 3 | 0.58908 | 88362 | 0.22752 | 0 | 0.45233 | 5654.125 | 0.06982 | 5585.6 | 64000 | 5654.125 | 5585.6 | 13122.275 | -2648.275 | 1350000 | 13122.275 | 0
2021110210 | 3 | 0.59117 | 88675.5 | 0.19993 | 0 | 0.49756 | 6219.5 | 0.08285 | 6628 | 64000 | 6219.5 | 6628 | 11828 | -1294.275 | 1350000 | 11828 | 0
2021110211 | 3 | 0.5892 | 88380 | 0.23096 | 0 | 0.50629 | 6328.625 | 0.11922 | 9537.6 | 64000 | 6328.625 | 9537.6 | 8513.775 | -3314.225 | 1350000 | 8513.775 | 0
2021110212 | 3 | 0.58505 | 87757.5 | 0.28912 | 0 | 0.4772 | 5965 | 0.14604 | 11683.2 | 64000 | 5965 | 11683.2 | 6109.3 | -2404.475 | 1350000 | 6109.3 | 0
2021110213 | 3 | 0.58312 | 87468 | 0.31011 | 0 | 0.44472 | 5559 | 0.14114 | 11291.2 | 64000 | 5559 | 11291.2 | 6617.8 | 508.5 | 1350000 | 6617.8 | 0
2021110214 | 3 | 0.58042 | 87063 | 0.3304 | 0 | 0.41119 | 5139.875 | 0.12306 | 9844.8 | 64000 | 5139.875 | 9844.8 | 8078.325 | 1460.525 | 1350000 | 8078.325 | 0
2021110215 | 3 | 0.57736 | 86604 | 0.29227 | 0 | 0.38519 | 4814.875 | 0.09022 | 7217.6 | 64000 | 4814.875 | 7217.6 | 10571.525 | 2493.2 | 1350000 | 10571.525 | 0
2021110216 | 3 | 0.57651 | 86476.5 | 0.26827 | 0 | 0.4213 | 5266.25 | 0.06495 | 5196 | 64000 | 5266.25 | 5196 | 12014.25 | 1442.725 | 1350000 | 12014.25 | 0
2021110217 | 3 | 0.58125 | 87187.5 | 0.28974 | 0 | 0.44057 | 5507.125 | 0.05693 | 4554.4 | 64000 | 5507.125 | 4554.4 | 13125.975 | 1111.725 | 1350000 | 13125.975 | 0
2021110218 | 3 | 0.59314 | 88971 | 0.34556 | 0 | 0.47607 | 5950.875 | 0.01956 | 1564.8 | 64000 | 5950.875 | 1564.8 | 17455.325 | 4329.35 | 1350000 | 17455.325 | 0
2021110219 | 3 | 0.61207 | 91810.5 | 0.36116 | 0 | 0.50614 | 6326.75 | 0 | 0 | 64000 | 6326.75 | 0 | 21483.75 | 4028.425 | 1350000 | 21483.75 | 0
2021110220 | 3 | 0.61541 | 92311.5 | 0.37059 | 0 | 0.54639 | 6829.875 | 0 | 0 | 64000 | 6829.875 | 0 | 21481.625 | -2.125 | 1350000 | 21481.625 | 0
2021110221 | 3 | 0.60576 | 90864 | 0.39409 | 0 | 0.57695 | 7211.875 | 0 | 0 | 64000 | 7211.875 | 0 | 19652.125 | -1829.5 | 1350000 | 19652.125 | 0
2021110222 | 3 | 0.5849 | 87735 | 0.37453 | 0 | 0.59319 | 7414.875 | 0 | 0 | 64000 | 7414.875 | 0 | 16320.125 | -3332 | 1350000 | 16320.125 | 0
2021110223 | 3 | 0.55756 | 83634 | 0.29086 | 0 | 0.59912 | 7489 | 0 | 0 | 64000 | 7489 | 0 | 12145 | -4175.125 | 1350000 | 12145 | 0
2021110224 | 3 | 0.53096 | 79644 | 0.29397 | 0 | 0.61876 | 7734.5 | 0 | 0 | 64000 | 7734.5 | 0 | 7909.5 | -4235.5 | 1350000 | 7909.5 | 0
2021110301 | 4 | 0.51202 | 76803 | 0.42241 | 0 | 0.67063 | 8382.875 | 0 | 0 | 64000 | 8382.875 | 0 | 4420.125 | -3489.375 | 1350000 | 4420.125 | 0
2021110302 | 4 | 0.50153 | 75229.5 | 0.50026 | 0 | 0.70838 | 8854.75 | 0 | 0 | 64000 | 8854.75 | 0 | 2374.75 | -2045.375 | 1350000 | 2374.75 | 0
2021110303 | 4 | 0.49855 | 74782.5 | 0.52021 | 0 | 0.71507 | 8938.375 | 0 | 0 | 64000 | 8938.375 | 0 | 1844.125 | -530.625 | 1350000 | 1844.125 | 0
2021110304 | 4 | 0.50068 | 75102 | 0.54125 | 0 | 0.71138 | 8892.25 | 0 | 0 | 64000 | 8892.25 | 0 | 2209.75 | 365.625 | 1350000 | 2209.75 | 0
2021110305 | 4 | 0.51322 | 76983 | 0.56239 | 0 | 0.74057 | 9257.125 | 0 | 0 | 64000 | 9257.125 | 0 | 3725.875 | 1516.125 | 1350000 | 3725.875 | 0
2021110306 | 4 | 0.54491 | 81736.5 | 0.55553 | 0 | 0.73284 | 9160.5 | 0 | 0 | 64000 | 9160.5 | 0 | 8576 | 4850.125 | 1350000 | 8576 | 0
2021110307 | 4 | 0.59943 | 89914.5 | 0.58126 | 0 | 0.75124 | 9390.5 | 0 | 0 | 64000 | 9390.5 | 0 | 16524 | 7948 | 1350000 | 16524 | 0
2021110308 | 4 | 0.63945 | 95917.5 | 0.61128 | 0 | 0.75251 | 9406.375 | 0.0159 | 1272 | 64000 | 9406.375 | 1272 | 21239.125 | 4715.125 | 1350000 | 21239.125 | 0
2021110309 | 4 | 0.64326 | 96489 | 0.51895 | 0 | 0.70538 | 8817.25 | 0.08351 | 6680.8 | 64000 | 8817.25 | 6680.8 | 16990.95 | -4248.175 | 1350000 | 16990.95 | 0
2021110310 | 4 | 0.62571 | 93856.5 | 0.41427 | 0 | 0.68589 | 8573.625 | 0.12079 | 9663.2 | 64000 | 8573.625 | 9663.2 | 11619.675 | -5371.275 | 1350000 | 11619.675 | 0
2021110311 | 4 | 0.60423 | 90634.5 | 0.43798 | 0 | 0.64501 | 8062.625 | 0.13863 | 11090.4 | 64000 | 8062.625 | 11090.4 | 7481.475 | -4138.2 | 1350000 | 7481.475 | 0
2021110312 | 4 | 0.58818 | 88227 | 0.48833 | 0 | 0.59542 | 7442.75 | 0.14184 | 11347.2 | 64000 | 7442.75 | 11347.2 | 5437.05 | -2044.425 | 1350000 | 5437.05 | 0
2021110313 | 4 | 0.57643 | 86464.5 | 0.41154 | 0 | 0.61494 | 7686.75 | 0.13315 | 10652 | 64000 | 7686.75 | 10652 | 4125.75 | -1311.3 | 1350000 | 4125.75 | 0
2021110314 | 4 | 0.56931 | 85396.5 | 0.34642 | 0 | 0.55797 | 6974.625 | 0.11872 | 9497.6 | 64000 | 6974.625 | 9497.6 | 4924.275 | 798.525 | 1350000 | 4924.275 | 0
2021110315 | 4 | 0.5649 | 84735 | 0.29897 | 0 | 0.55414 | 6926.75 | 0.07711 | 6168.8 | 64000 | 6926.75 | 6168.8 | 7639.45 | 2715.175 | 1350000 | 7639.45 | 0
2021110316 | 4 | 0.56263 | 84394.5 | 0.26007 | 0 | 0.58548 | 7318.5 | 0.05954 | 4763.2 | 64000 | 7318.5 | 4763.2 | 8312.8 | 673.35 | 1350000 | 8312.8 | 0
2021110317 | 4 | 0.57147 | 85720.5 | 0.22641 | 0 | 0.53662 | 6707.75 | 0.05714 | 4571.2 | 64000 | 6707.75 | 4571.2 | 10441.55 | 2128.75 | 1350000 | 10441.55 | 0
2021110318 | 4 | 0.58945 | 88417.5 | 0.13422 | 0 | 0.4989 | 6236.25 | 0.01904 | 1523.2 | 64000 | 6236.25 | 1523.2 | 16658.05 | 6216.5 | 1350000 | 16658.05 | 0
2021110319 | 4 | 0.6158 | 92370 | 0.1121 | 0 | 0.42206 | 5275.75 | 0 | 0 | 64000 | 5275.75 | 0 | 23094.25 | 6436.2 | 1350000 | 23094.25 | 0
2021110320 | 4 | 0.62397 | 93595.5 | 0.10421 | 0 | 0.38002 | 4750.25 | 0 | 0 | 64000 | 4750.25 | 0 | 24845.25 | 1751 | 1350000 | 24845.25 | 0
2021110321 | 4 | 0.61563 | 92344.5 | 0.07687 | 0 | 0.43365 | 5420.625 | 0 | 0 | 64000 | 5420.625 | 0 | 22923.875 | -1921.375 | 1350000 | 22923.875 | 0
2021110322 | 4 | 0.59788 | 89682 | 0.07608 | 0 | 0.49342 | 6167.75 | 0 | 0 | 64000 | 6167.75 | 0 | 19514.25 | -3409.625 | 1350000 | 19514.25 | 0
2021110323 | 4 | 0.56996 | 85494 | 0.05569 | 0 | 0.53832 | 6729 | 0 | 0 | 64000 | 6729 | 0 | 14765 | -4749.25 | 1350000 | 14765 | 0
2021110324 | 4 | 0.54394 | 81591 | 0.01914 | 0 | 0.53558 | 6694.75 | 0 | 0 | 64000 | 6694.75 | 0 | 10896.25 | -3868.75 | 1350000 | 10896.25 | 0
2021110401 | 5 | 0.5239 | 78585 | 0.0269 | 0 | 0.52428 | 6553.5 | 0 | 0 | 64000 | 6553.5 | 0 | 8031.5 | -2864.75 | 1350000 | 8031.5 | 0
2021110402 | 5 | 0.51342 | 77013 | 0.04159 | 0 | 0.53879 | 6734.875 | 0 | 0 | 64000 | 6734.875 | 0 | 6278.125 | -1753.375 | 1350000 | 6278.125 | 0
2021110403 | 5 | 0.512 | 76800 | 0.02973 | 0 | 0.54805 | 6850.625 | 0 | 0 | 64000 | 6850.625 | 0 | 5949.375 | -328.75 | 1350000 | 5949.375 | 0
2021110404 | 5 | 0.51621 | 77431.5 | 0.02336 | 0 | 0.5613 | 7016.25 | 0 | 0 | 64000 | 7016.25 | 0 | 6415.25 | 465.875 | 1350000 | 6415.25 | 0
2021110405 | 5 | 0.52807 | 79210.5 | 0.03047 | 0 | 0.44394 | 5549.25 | 0 | 0 | 64000 | 5549.25 | 0 | 9661.25 | 3246 | 1350000 | 9661.25 | 0
2021110406 | 5 | 0.55792 | 83688 | 0.03544 | 0 | 0.29412 | 3676.5 | 0 | 0 | 64000 | 3676.5 | 0 | 16011.5 | 6350.25 | 1350000 | 16011.5 | 0
2021110407 | 5 | 0.60951 | 91426.5 | 0.02185 | 0 | 0.18016 | 2252 | 0 | 0 | 64000 | 2252 | 0 | 25174.5 | 9163 | 1350000 | 25174.5 | 0
2021110408 | 5 | 0.64697 | 97045.5 | 0.0197 | 0 | 0.13828 | 1728.5 | 0.03478 | 2782.4 | 64000 | 1728.5 | 2782.4 | 28534.6 | 3360.1 | 1346931.65 | 28534.6 | 0
2021110409 | 5 | 0.65742 | 98613 | 0.03076 | 0 | 0.133 | 1662.5 | 0.18295 | 14636 | 64000 | 1662.5 | 14636 | 18314.5 | -10220.1 | 1350000 | 18314.5 | 0
2021110410 | 5 | 0.64626 | 96939 | 0.00983 | 0 | 0.1287 | 1608.75 | 0.28825 | 23060 | 64000 | 1608.75 | 23060 | 8270.25 | -10044.25 | 1350000 | 8270.25 | 0
2021110411 | 5 | 0.62697 | 94045.5 | 0.0036 | 0 | 0.15136 | 1892 | 0.28642 | 22913.6 | 64000 | 1892 | 22913.6 | 5239.9 | -3030.35 | 1350000 | 5239.9 | 0
2021110412 | 5 | 0.60713 | 91069.5 | 0.00441 | 0 | 0.17065 | 2133.125 | 0.28553 | 22842.4 | 64000 | 2133.125 | 22842.4 | 2093.975 | -3145.925 | 1350000 | 2093.975 | 0
2021110413 | 5 | 0.5937 | 89055 | 0.00413 | 0 | 0.17858 | 2232.25 | 0.27036 | 21628.8 | 64000 | 2232.25 | 21628.8 | 1193.95 | -900.025 | 1350000 | 1193.95 | 0
2021110414 | 5 | 0.58549 | 87823.5 | 0.00224 | 0 | 0.16965 | 2120.625 | 0.24064 | 19251.2 | 64000 | 2120.625 | 19251.2 | 2451.675 | 1257.725 | 1350000 | 2451.675 | 0
2021110415 | 5 | 0.57853 | 86779.5 | 0.00438 | 0 | 0.16815 | 2101.875 | 0.15058 | 12046.4 | 64000 | 2101.875 | 12046.4 | 8631.225 | 6179.55 | 1350000 | 8631.225 | 0
2021110416 | 5 | 0.57687 | 86530.5 | 0.00605 | 0 | 0.19443 | 2430.375 | 0.08334 | 6667.2 | 64000 | 2430.375 | 6667.2 | 13432.925 | 4801.7 | 1350000 | 13432.925 | 0
2021110417 | 5 | 0.58067 | 87100.5 | 0.0069 | 0 | 0.21451 | 2681.375 | 0.03271 | 2616.8 | 64000 | 2681.375 | 2616.8 | 17802.325 | 4369.4 | 1350000 | 17802.325 | 0
2021110418 | 5 | 0.59355 | 89032.5 | 0.00639 | 0 | 0.24311 | 3038.875 | 0.00781 | 624.8 | 64000 | 3038.875 | 624.8 | 21368.825 | 3566.5 | 1350000 | 21368.825 | 0
2021110419 | 5 | 0.61799 | 92698.5 | 0.00599 | 0 | 0.31592 | 3949 | 0 | 0 | 64000 | 3949 | 0 | 24749.5 | 3380.675 | 1350000 | 24749.5 | 0
2021110420 | 5 | 0.62734 | 94101 | 0.00649 | 0 | 0.39114 | 4889.25 | 0 | 0 | 64000 | 4889.25 | 0 | 25211.75 | 462.25 | 1350000 | 25211.75 | 0
2021110421 | 5 | 0.62017 | 93025.5 | 0.00469 | 0 | 0.43847 | 5480.875 | 0 | 0 | 64000 | 5480.875 | 0 | 23544.625 | -1667.125 | 1350000 | 23544.625 | 0
2021110422 | 5 | 0.60442 | 90663 | 0.00723 | 0 | 0.46135 | 5766.875 | 0 | 0 | 64000 | 5766.875 | 0 | 20896.125 | -2648.5 | 1350000 | 20896.125 | 0
2021110423 | 5 | 0.57833 | 86749.5 | 0.02014 | 0 | 0.46 | 5750 | 0 | 0 | 64000 | 5750 | 0 | 16999.5 | -3896.625 | 1350000 | 16999.5 | 0
2021110424 | 5 | 0.55514 | 83271 | 0.04698 | 0 | 0.44232 | 5529 | 0 | 0 | 64000 | 5529 | 0 | 13742 | -3257.5 | 1350000 | 13742 | 0
2021110501 | 6 | 0.53965 | 80947.5 | 0.03815 | 0 | 0.44432 | 5554 | 0 | 0 | 64000 | 5554 | 0 | 11393.5 | -2348.5 | 1350000 | 11393.5 | 0
2021110502 | 6 | 0.53041 | 79561.5 | 0.08392 | 0 | 0.44453 | 5556.625 | 0 | 0 | 64000 | 5556.625 | 0 | 10004.875 | -1388.625 | 1350000 | 10004.875 | 0
2021110503 | 6 | 0.52918 | 79377 | 0.13107 | 0 | 0.52882 | 6610.25 | 0 | 0 | 64000 | 6610.25 | 0 | 8766.75 | -1238.125 | 1350000 | 8766.75 | 0
2021110504 | 6 | 0.53194 | 79791 | 0.12871 | 0 | 0.54115 | 6764.375 | 0 | 0 | 64000 | 6764.375 | 0 | 9026.625 | 259.875 | 1350000 | 9026.625 | 0
2021110505 | 6 | 0.54612 | 81918 | 0.12272 | 0 | 0.53606 | 6700.75 | 0 | 0 | 64000 | 6700.75 | 0 | 11217.25 | 2190.625 | 1350000 | 11217.25 | 0
2021110506 | 6 | 0.57788 | 86682 | 0.11507 | 0 | 0.56683 | 7085.375 | 0 | 0 | 64000 | 7085.375 | 0 | 15596.625 | 4379.375 | 1350000 | 15596.625 | 0
2021110507 | 6 | 0.62646 | 93969 | 0.09699 | 0 | 0.53761 | 6720.125 | 0 | 0 | 64000 | 6720.125 | 0 | 23248.875 | 7652.25 | 1350000 | 23248.875 | 0
2021110508 | 6 | 0.665 | 99750 | 0.07934 | 0 | 0.48131 | 6016.375 | 0.0064 | 512 | 64000 | 6016.375 | 512 | 29221.625 | 5972.75 | 1346244.625 | 29221.625 | 0
2021110509 | 6 | 0.67047 | 100570.5 | 0.0374 | 0 | 0.39107 | 4888.375 | 0.03685 | 2948 | 64000 | 4888.375 | 2948 | 28734.125 | -487.5 | 1342976.75 | 28734.125 | 0
2021110510 | 6 | 0.64987 | 97480.5 | 0.01734 | 0 | 0.29151 | 3643.875 | 0.07185 | 5748 | 64000 | 3643.875 | 5748 | 24088.625 | -4645.5 | 1344354.375 | 24088.625 | 0
2021110511 | 6 | 0.6226 | 93390 | 0.02416 | 0 | 0.29116 | 3639.5 | 0.13462 | 10769.6 | 64000 | 3639.5 | 10769.6 | 14980.9 | -9107.725 | 1350000 | 14980.9 | 0
2021110512 | 6 | 0.59897 | 89845.5 | 0.01298 | 0 | 0.34064 | 4258 | 0.23094 | 18475.2 | 64000 | 4258 | 18475.2 | 3112.3 | -11868.6 | 1350000 | 3112.3 | 0
2021110513 | 6 | 0.58124 | 87186 | 0.01262 | 0 | 0.34625 | 4328.125 | 0.29847 | 23877.6 | 64000 | 4328.125 | 18857.875 | 0 | -3112.3 | 1350000 | 0 | 0
2021110514 | 6 | 0.57095 | 85642.5 | 0.01726 | 0 | 0.3064 | 3830 | 0.31488 | 25190.4 | 64000 | 3830 | 17812.5 | 0 | 0 | 1350000 | 0 | 0
2021110515 | 6 | 0.56009 | 84013.5 | 0.01929 | 0 | 0.29349 | 3668.625 | 0.26314 | 21051.2 | 64000 | 3668.625 | 16344.875 | 0 | 0 | 1350000 | 0 | 0
2021110516 | 6 | 0.55427 | 83140.5 | 0.02119 | 0 | 0.34429 | 4303.625 | 0.21016 | 16812.8 | 64000 | 4303.625 | 14836.875 | 0 | 0 | 1350000 | 0 | 0
2021110517 | 6 | 0.55926 | 83889 | 0.01534 | 0 | 0.41349 | 5168.625 | 0.1384 | 11072 | 64000 | 5168.625 | 11072 | 3648.375 | 3648.375 | 1350000 | 3648.375 | 0
2021110518 | 6 | 0.5729 | 85935 | 0.0127 | 0 | 0.47414 | 5926.75 | 0.04174 | 3339.2 | 64000 | 5926.75 | 3339.2 | 12669.05 | 9020.675 | 1350000 | 12669.05 | 0
2021110519 | 6 | 0.59463 | 89194.5 | 0.01435 | 0 | 0.42212 | 5276.5 | 9e-05 | 7.2 | 64000 | 5276.5 | 7.2 | 19910.8 | 7241.75 | 1350000 | 19910.8 | 0
2021110520 | 6 | 0.60284 | 90426 | 0.02046 | 0 | 0.25112 | 3139 | 0 | 0 | 64000 | 3139 | 0 | 23287 | 3376.2 | 1350000 | 23287 | 0
2021110521 | 6 | 0.59853 | 89779.5 | 0.02425 | 0 | 0.15875 | 1984.375 | 0 | 0 | 64000 | 1984.375 | 0 | 23795.125 | 508.125 | 1350000 | 23795.125 | 0
2021110522 | 6 | 0.58624 | 87936 | 0.03895 | 0 | 0.1115 | 1393.75 | 0 | 0 | 64000 | 1393.75 | 0 | 22542.25 | -1252.875 | 1350000 | 22542.25 | 0
2021110523 | 6 | 0.56737 | 85105.5 | 0.04802 | 0 | 0.09836 | 1229.5 | 0 | 0 | 64000 | 1229.5 | 0 | 19876 | -2666.25 | 1350000 | 19876 | 0
2021110524 | 6 | 0.5477 | 82155 | 0.10801 | 0 | 0.12109 | 1513.625 | 0 | 0 | 64000 | 1513.625 | 0 | 16641.375 | -3234.625 | 1350000 | 16641.375 | 0
2021110601 | 7 | 0.53259 | 79888.5 | 0.12468 | 0 | 0.1211 | 1513.75 | 0 | 0 | 64000 | 1513.75 | 0 | 14374.75 | -2266.625 | 1350000 | 14374.75 | 0
2021110602 | 7 | 0.52304 | 78456 | 0.1764 | 0 | 0.11199 | 1399.875 | 0 | 0 | 64000 | 1399.875 | 0 | 13056.125 | -1318.625 | 1350000 | 13056.125 | 0
2021110603 | 7 | 0.52032 | 78048 | 0.23942 | 0 | 0.10708 | 1338.5 | 0 | 0 | 64000 | 1338.5 | 0 | 12709.5 | -346.625 | 1350000 | 12709.5 | 0
2021110604 | 7 | 0.52212 | 78318 | 0.27089 | 0 | 0.08936 | 1117 | 0 | 0 | 64000 | 1117 | 0 | 13201 | 491.5 | 1350000 | 13201 | 0
2021110605 | 7 | 0.52772 | 79158 | 0.26331 | 0 | 0.08832 | 1104 | 0 | 0 | 64000 | 1104 | 0 | 14054 | 853 | 1350000 | 14054 | 0
2021110606 | 7 | 0.54234 | 81351 | 0.20987 | 0 | 0.09039 | 1129.875 | 0 | 0 | 64000 | 1129.875 | 0 | 16221.125 | 2167.125 | 1350000 | 16221.125 | 0
2021110607 | 7 | 0.56527 | 84790.5 | 0.17927 | 0 | 0.08729 | 1091.125 | 0 | 0 | 64000 | 1091.125 | 0 | 19699.375 | 3478.25 | 1350000 | 19699.375 | 0
2021110608 | 7 | 0.5923 | 88845 | 0.17711 | 0 | 0.10659 | 1332.375 | 0.06602 | 5281.6 | 64000 | 1332.375 | 5281.6 | 18231.025 | -1468.35 | 1350000 | 18231.025 | 0
2021110609 | 7 | 0.60735 | 91102.5 | 0.25696 | 0 | 0.12785 | 1598.125 | 0.32096 | 25676.8 | 64000 | 1598.125 | 25504.375 | 0 | -18231.025 | 1350000 | 0 | 0
2021110610 | 7 | 0.60111 | 90166.5 | 0.25515 | 0 | 0.14557 | 1819.625 | 0.49825 | 39860 | 64000 | 1819.625 | 24346.875 | 0 | 0 | 1350000 | 0 | 0
2021110611 | 7 | 0.57794 | 86691 | 0.22126 | 0 | 0.13297 | 1662.125 | 0.54518 | 43614.4 | 64000 | 1662.125 | 21028.875 | 0 | 0 | 1350000 | 0 | 0
2021110612 | 7 | 0.55402 | 83103 | 0.19312 | 0 | 0.09782 | 1222.75 | 0.5481 | 43848 | 64000 | 1222.75 | 17880.25 | 0 | 0 | 1350000 | 0 | 0
2021110613 | 7 | 0.53539 | 80308.5 | 0.13432 | 0 | 0.07447 | 930.875 | 0.55948 | 44758.4 | 64000 | 930.875 | 15377.625 | 0 | 0 | 1350000 | 0 | 0
2021110614 | 7 | 0.52081 | 78121.5 | 0.06339 | 0 | 0.0654 | 817.5 | 0.56673 | 45338.4 | 64000 | 817.5 | 13304 | 0 | 0 | 1350000 | 0 | 0
2021110615 | 7 | 0.51173 | 76759.5 | 0.04905 | 0 | 0.08846 | 1105.75 | 0.56979 | 45583.2 | 64000 | 1105.75 | 11653.75 | 0 | 0 | 1350000 | 0 | 0
2021110616 | 7 | 0.51064 | 76596 | 0.04151 | 0 | 0.1294 | 1617.5 | 0.532 | 42560 | 64000 | 1617.5 | 10978.5 | 0 | 0 | 1350000 | 0 | 0
2021110617 | 7 | 0.51683 | 77524.5 | 0.06033 | 0 | 0.1689 | 2111.25 | 0.37288 | 29830.4 | 64000 | 2111.25 | 11413.25 | 0 | 0 | 1350000 | 0 | 0
2021110618 | 7 | 0.53092 | 79638 | 0.08366 | 0 | 0.17322 | 2165.25 | 0.09104 | 7283.2 | 64000 | 2165.25 | 7283.2 | 6189.55 | 6189.55 | 1350000 | 6189.55 | 0
2021110619 | 7 | 0.55456 | 83184 | 0.17695 | 0 | 0.18482 | 2310.25 | 0.00073 | 58.4 | 64000 | 2310.25 | 58.4 | 16815.35 | 10625.8 | 1350000 | 16815.35 | 0
2021110620 | 7 | 0.56308 | 84462 | 0.19641 | 0 | 0.18877 | 2359.625 | 0 | 0 | 64000 | 2359.625 | 0 | 18102.375 | 1287.025 | 1350000 | 18102.375 | 0
2021110621 | 7 | 0.5588 | 83820 | 0.25813 | 0 | 0.24486 | 3060.75 | 0 | 0 | 64000 | 3060.75 | 0 | 16759.25 | -1343.125 | 1350000 | 16759.25 | 0
2021110622 | 7 | 0.54952 | 82428 | 0.35127 | 0 | 0.28347 | 3543.375 | 0 | 0 | 64000 | 3543.375 | 0 | 14884.625 | -1874.625 | 1350000 | 14884.625 | 0
2021110623 | 7 | 0.53363 | 80044.5 | 0.36792 | 0 | 0.31664 | 3958 | 0 | 0 | 64000 | 3958 | 0 | 12086.5 | -2798.125 | 1350000 | 12086.5 | 0
2021110624 | 7 | 0.51602 | 77403 | 0.35987 | 0 | 0.36413 | 4551.625 | 0 | 0 | 64000 | 4551.625 | 0 | 8851.375 | -3235.125 | 1350000 | 8851.375 | 0
2021110701 | 1 | 0.50076 | 75114 | 0.3548 | 0 | 0.37712 | 4714 | 0 | 0 | 64000 | 4714 | 0 | 6400 | -2451.375 | 1350000 | 6400 | 0
2021110702 | 1 | 0.49213 | 73819.5 | 0.25131 | 0 | 0.38323 | 4790.375 | 0 | 0 | 64000 | 4790.375 | 0 | 5029.125 | -1370.875 | 1350000 | 5029.125 | 0
2021110702 | 1 | 0.48744 | 73116 | 0.23702 | 0 | 0.40284 | 5035.5 | 0 | 0 | 64000 | 5035.5 | 0 | 4080.5 | -948.625 | 1350000 | 4080.5 | 0
2021110703 | 1 | 0.48615 | 72922.5 | 0.19006 | 0 | 0.40921 | 5115.125 | 0 | 0 | 64000 | 5115.125 | 0 | 3807.375 | -273.125 | 1350000 | 3807.375 | 0
2021110704 | 1 | 0.48944 | 73416 | 0.13773 | 0 | 0.4362 | 5452.5 | 0 | 0 | 64000 | 5452.5 | 0 | 3963.5 | 156.125 | 1350000 | 3963.5 | 0
2021110705 | 1 | 0.49803 | 74704.5 | 0.14473 | 0 | 0.4551 | 5688.75 | 0 | 0 | 64000 | 5688.75 | 0 | 5015.75 | 1052.25 | 1350000 | 5015.75 | 0
2021110706 | 1 | 0.51245 | 76867.5 | 0.20459 | 0 | 0.51996 | 6499.5 | 0 | 0 | 64000 | 6499.5 | 0 | 6368 | 1352.25 | 1350000 | 6368 | 0
2021110707 | 1 | 0.53245 | 79867.5 | 0.21944 | 0 | 0.58428 | 7303.5 | 0.04914 | 3931.2 | 64000 | 7303.5 | 3931.2 | 4632.8 | -1735.2 | 1350000 | 4632.8 | 0
2021110708 | 1 | 0.54853 | 82279.5 | 0.17866 | 0 | 0.65256 | 8157 | 0.30845 | 24676 | 64000 | 8157 | 10122.5 | 0 | -4632.8 | 1350000 | 0 | 0
2021110709 | 1 | 0.55356 | 83034 | 0.19782 | 0 | 0.69014 | 8626.75 | 0.49694 | 39755.2 | 64000 | 8626.75 | 10407.25 | 0 | 0 | 1350000 | 0 | 0
2021110710 | 1 | 0.54166 | 81249 | 0.05861 | 0 | 0.69409 | 8676.125 | 0.54127 | 43301.6 | 64000 | 8676.125 | 8572.875 | 0 | 0 | 1350000 | 0 | 0
2021110711 | 1 | 0.52473 | 78709.5 | 0.02559 | 0 | 0.67176 | 8397 | 0.54892 | 43913.6 | 64000 | 8397 | 6312.5 | 0 | 0 | 1350000 | 0 | 0
2021110712 | 1 | 0.51269 | 76903.5 | 0.0339 | 0 | 0.64734 | 8091.75 | 0.54935 | 43948 | 64000 | 8091.75 | 4811.75 | 0 | 0 | 1350000 | 0 | 0
2021110713 | 1 | 0.50645 | 75967.5 | 0.03913 | 0 | 0.62117 | 7764.625 | 0.54682 | 43745.6 | 64000 | 7764.625 | 4202.875 | 0 | 0 | 1350000 | 0 | 0
2021110714 | 1 | 0.50019 | 75028.5 | 0.0562 | 0 | 0.60819 | 7602.375 | 0.49195 | 39356 | 64000 | 7602.375 | 3426.125 | 0 | 0 | 1350000 | 0 | 0
2021110715 | 1 | 0.49929 | 74893.5 | 0.07762 | 0 | 0.64494 | 8061.75 | 0.40498 | 32398.4 | 64000 | 8061.75 | 2831.75 | 0 | 0 | 1350000 | 0 | 0
2021110716 | 1 | 0.50452 | 75678 | 0.12941 | 0 | 0.68946 | 8618.25 | 0.30327 | 24261.6 | 64000 | 8618.25 | 3059.75 | 0 | 0 | 1350000 | 0 | 0
2021110717 | 1 | 0.52342 | 78513 | 0.16354 | 0 | 0.70558 | 8819.75 | 0.10673 | 8538.4 | 64000 | 8819.75 | 5693.25 | 0 | 0 | 1350000 | 0 | 0
2021110718 | 1 | 0.55728 | 83592 | 0.22418 | 0 | 0.71509 | 8938.625 | 0.00164 | 131.2 | 64000 | 8938.625 | 131.2 | 10522.175 | 10522.175 | 1350000 | 10522.175 | 0
2021110719 | 1 | 0.56989 | 85483.5 | 0.3675 | 0 | 0.71346 | 8918.25 | 0 | 0 | 64000 | 8918.25 | 0 | 12565.25 | 2043.075 | 1350000 | 12565.25 | 0
2021110720 | 1 | 0.56649 | 84973.5 | 0.47445 | 0 | 0.69801 | 8725.125 | 0 | 0 | 64000 | 8725.125 | 0 | 12248.375 | -316.875 | 1350000 | 12248.375 | 0
2021110721 | 1 | 0.55485 | 83227.5 | 0.59276 | 0 | 0.7236 | 9045 | 0 | 0 | 64000 | 9045 | 0 | 10182.5 | -2065.875 | 1350000 | 10182.5 | 0
2021110722 | 1 | 0.5388 | 80820 | 0.65383 | 0 | 0.75999 | 9499.875 | 0 | 0 | 64000 | 9499.875 | 0 | 7320.125 | -2862.375 | 1350000 | 7320.125 | 0
2021110723 | 1 | 0.51976 | 77964 | 0.67288 | 0 | 0.79408 | 9926 | 0 | 0 | 64000 | 9926 | 0 | 4038 | -3282.125 | 1350000 | 4038 | 0
2021110724 | 1 | 0.50127 | 75190.5 | 0.62496 | 0 | 0.78631 | 9828.875 | 0 | 0 | 64000 | 9828.875 | 0 | 1361.625 | -2676.375 | 1350000 | 1361.625 | 0
2021110801 | 2 | 0.48968 | 73452 | 0.59671 | 0 | 0.78127 | 9765.875 | 0 | 0 | 64000 | 9452 | 0 | 0 | -1361.625 | 1350000 | 0 | 0
2021110802 | 2 | 0.48513 | 72769.5 | 0.60445 | 0 | 0.76769 | 9596.125 | 0 | 0 | 64000 | 8769.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110803 | 2 | 0.4855 | 72825 | 0.63559 | 0 | 0.71516 | 8939.5 | 0 | 0 | 64000 | 8825 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110804 | 2 | 0.48948 | 73422 | 0.6025 | 0 | 0.62591 | 7823.875 | 0 | 0 | 64000 | 7823.875 | 0 | 1598.125 | 1598.125 | 1350000 | 1598.125 | 0
2021110805 | 2 | 0.50583 | 75874.5 | 0.56451 | 0 | 0.45455 | 5681.875 | 0 | 0 | 64000 | 5681.875 | 0 | 6192.625 | 4594.5 | 1350000 | 6192.625 | 0
2021110806 | 2 | 0.53987 | 80980.5 | 0.6545 | 0 | 0.37225 | 4653.125 | 0.00044 | 35.2 | 64000 | 4653.125 | 35.2 | 12292.175 | 6099.55 | 1350000 | 12292.175 | 0
2021110807 | 2 | 0.59147 | 88720.5 | 0.6746 | 0 | 0.35473 | 4434.125 | 0.0563 | 4504 | 64000 | 4434.125 | 4504 | 15782.375 | 3490.2 | 1350000 | 15782.375 | 0
2021110808 | 2 | 0.61433 | 92149.5 | 0.64301 | 0 | 0.31522 | 3940.25 | 0.27579 | 22063.2 | 64000 | 3940.25 | 22063.2 | 2146.05 | -13636.325 | 1350000 | 2146.05 | 0
2021110809 | 2 | 0.60237 | 90355.5 | 0.45076 | 0 | 0.34156 | 4269.5 | 0.42848 | 34278.4 | 64000 | 4269.5 | 22086 | 0 | -2146.05 | 1350000 | 0 | 0
2021110810 | 2 | 0.58508 | 87762 | 0.31507 | 0 | 0.37243 | 4655.375 | 0.46599 | 37279.2 | 64000 | 4655.375 | 19106.625 | 0 | 0 | 1350000 | 0 | 0
2021110811 | 2 | 0.57169 | 85753.5 | 0.21239 | 0 | 0.41557 | 5194.625 | 0.44788 | 35830.4 | 64000 | 5194.625 | 16558.875 | 0 | 0 | 1350000 | 0 | 0
2021110812 | 2 | 0.56182 | 84273 | 0.15899 | 0 | 0.4707 | 5883.75 | 0.43155 | 34524 | 64000 | 5883.75 | 14389.25 | 0 | 0 | 1350000 | 0 | 0
2021110813 | 2 | 0.55652 | 83478 | 0.18825 | 0 | 0.47711 | 5963.875 | 0.422 | 33760 | 64000 | 5963.875 | 13514.125 | 0 | 0 | 1350000 | 0 | 0
2021110814 | 2 | 0.5538 | 83070 | 0.1488 | 0 | 0.57639 | 7204.875 | 0.43603 | 34882.4 | 64000 | 7204.875 | 11865.125 | 0 | 0 | 1350000 | 0 | 0
2021110815 | 2 | 0.55301 | 82951.5 | 0.11131 | 0 | 0.66756 | 8344.5 | 0.42855 | 34284 | 64000 | 8344.5 | 10607 | 0 | 0 | 1350000 | 0 | 0
2021110816 | 2 | 0.55561 | 83341.5 | 0.12444 | 0 | 0.73721 | 9215.125 | 0.32747 | 26197.6 | 64000 | 9215.125 | 10126.375 | 0 | 0 | 1350000 | 0 | 0
2021110817 | 2 | 0.56584 | 84876 | 0.09807 | 0 | 0.76768 | 9596 | 0.09077 | 7261.6 | 64000 | 9596 | 7261.6 | 4018.4 | 4018.4 | 1350000 | 4018.4 | 0
2021110818 | 2 | 0.5912 | 88680 | 0.19783 | 0 | 0.77489 | 9686.125 | 0.00026 | 20.8 | 64000 | 9686.125 | 20.8 | 14973.075 | 10954.675 | 1350000 | 14973.075 | 0
2021110819 | 2 | 0.59783 | 89674.5 | 0.36224 | 0 | 0.77751 | 9718.875 | 0 | 0 | 64000 | 9718.875 | 0 | 15955.625 | 982.55 | 1350000 | 15955.625 | 0
2021110820 | 2 | 0.58755 | 88132.5 | 0.50685 | 0 | 0.78405 | 9800.625 | 0 | 0 | 64000 | 9800.625 | 0 | 14331.875 | -1623.75 | 1350000 | 14331.875 | 0
2021110821 | 2 | 0.57297 | 85945.5 | 0.65455 | 0 | 0.77694 | 9711.75 | 0 | 0 | 64000 | 9711.75 | 0 | 12233.75 | -2098.125 | 1350000 | 12233.75 | 0
2021110822 | 2 | 0.54992 | 82488 | 0.72945 | 0 | 0.74473 | 9309.125 | 0 | 0 | 64000 | 9309.125 | 0 | 9178.875 | -3054.875 | 1350000 | 9178.875 | 0
2021110823 | 2 | 0.52179 | 78268.5 | 0.77848 | 0 | 0.77032 | 9629 | 0 | 0 | 64000 | 9629 | 0 | 4639.5 | -4539.375 | 1350000 | 4639.5 | 0
2021110824 | 2 | 0.49854 | 74781 | 0.80634 | 0 | 0.78908 | 9863.5 | 0 | 0 | 64000 | 9863.5 | 0 | 917.5 | -3722 | 1350000 | 917.5 | 0
2021110901 | 3 | 0.48158 | 72237 | 0.82807 | 0 | 0.82187 | 10273.375 | 0 | 0 | 64000 | 8237 | 0 | 0 | -917.5 | 1350000 | 0 | 0
2021110902 | 3 | 0.47312 | 70968 | 0.84483 | 0 | 0.82256 | 10282 | 0 | 0 | 64000 | 6968 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110903 | 3 | 0.46995 | 70492.5 | 0.88914 | 0 | 0.83917 | 10489.625 | 0 | 0 | 64000 | 6492.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110904 | 3 | 0.47286 | 70929 | 0.88864 | 0 | 0.8386 | 10482.5 | 0 | 0 | 64000 | 6929 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110905 | 3 | 0.48689 | 73033.5 | 0.87901 | 0 | 0.81698 | 10212.25 | 0 | 0 | 64000 | 9033.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021110906 | 3 | 0.51962 | 77943 | 0.82322 | 0 | 0.79857 | 9982.125 | 0 | 0 | 64000 | 9982.125 | 0 | 3960.875 | 3960.875 | 1350000 | 3960.875 | 0
2021110907 | 3 | 0.56912 | 85368 | 0.73483 | 0 | 0.76822 | 9602.75 | 0.01807 | 1445.6 | 64000 | 9602.75 | 1445.6 | 10319.65 | 6358.775 | 1350000 | 10319.65 | 0
2021110908 | 3 | 0.59297 | 88945.5 | 0.58413 | 0 | 0.76273 | 9534.125 | 0.06336 | 5068.8 | 64000 | 9534.125 | 5068.8 | 10342.575 | 22.925 | 1350000 | 10342.575 | 0
2021110909 | 3 | 0.58418 | 87627 | 0.35703 | 0 | 0.76044 | 9505.5 | 0.04304 | 3443.2 | 64000 | 9505.5 | 3443.2 | 10678.3 | 335.725 | 1350000 | 10678.3 | 0
2021110910 | 3 | 0.5705 | 85575 | 0.13923 | 0 | 0.77266 | 9658.25 | 0.04924 | 3939.2 | 64000 | 9658.25 | 3939.2 | 7977.55 | -2700.75 | 1350000 | 7977.55 | 0
2021110911 | 3 | 0.56296 | 84444 | 0.10084 | 0 | 0.74859 | 9357.375 | 0.11675 | 9340 | 64000 | 9357.375 | 9340 | 1746.625 | -6230.925 | 1350000 | 1746.625 | 0
2021110912 | 3 | 0.55543 | 83314.5 | 0.11083 | 0 | 0.69963 | 8745.375 | 0.15194 | 12155.2 | 64000 | 8745.375 | 10569.125 | 0 | -1746.625 | 1350000 | 0 | 0
2021110913 | 3 | 0.55268 | 82902 | 0.16222 | 0 | 0.65942 | 8242.75 | 0.14429 | 11543.2 | 64000 | 8242.75 | 10659.25 | 0 | 0 | 1350000 | 0 | 0
2021110914 | 3 | 0.55184 | 82776 | 0.20588 | 0 | 0.60315 | 7539.375 | 0.10738 | 8590.4 | 64000 | 7539.375 | 8590.4 | 2646.225 | 2646.225 | 1350000 | 2646.225 | 0
2021110915 | 3 | 0.55121 | 82681.5 | 0.17235 | 0 | 0.63982 | 7997.75 | 0.07302 | 5841.6 | 64000 | 7997.75 | 5841.6 | 4842.15 | 2195.925 | 1350000 | 4842.15 | 0
2021110916 | 3 | 0.55356 | 83034 | 0.14604 | 0 | 0.72398 | 9049.75 | 0.04363 | 3490.4 | 64000 | 9049.75 | 3490.4 | 6493.85 | 1651.7 | 1350000 | 6493.85 | 0
2021110917 | 3 | 0.56332 | 84498 | 0.16589 | 0 | 0.76331 | 9541.375 | 0.01339 | 1071.2 | 64000 | 9541.375 | 1071.2 | 9885.425 | 3391.575 | 1350000 | 9885.425 | 0
2021110918 | 3 | 0.58934 | 88401 | 0.16717 | 0 | 0.74743 | 9342.875 | 0 | 0 | 64000 | 9342.875 | 0 | 15058.125 | 5172.7 | 1350000 | 15058.125 | 0
2021110919 | 3 | 0.59372 | 89058 | 0.23785 | 0 | 0.75101 | 9387.625 | 0 | 0 | 64000 | 9387.625 | 0 | 15670.375 | 612.25 | 1350000 | 15670.375 | 0
2021110920 | 3 | 0.58187 | 87280.5 | 0.28982 | 0 | 0.77333 | 9666.625 | 0 | 0 | 64000 | 9666.625 | 0 | 13613.875 | -2056.5 | 1350000 | 13613.875 | 0
2021110921 | 3 | 0.56557 | 84835.5 | 0.32834 | 0 | 0.78738 | 9842.25 | 0 | 0 | 64000 | 9842.25 | 0 | 10993.25 | -2620.625 | 1350000 | 10993.25 | 0
2021110922 | 3 | 0.54099 | 81148.5 | 0.30116 | 0 | 0.78394 | 9799.25 | 0 | 0 | 64000 | 9799.25 | 0 | 7349.25 | -3644 | 1350000 | 7349.25 | 0
2021110923 | 3 | 0.51196 | 76794 | 0.36436 | 0 | 0.77696 | 9712 | 0 | 0 | 64000 | 9712 | 0 | 3082 | -4267.25 | 1350000 | 3082 | 0
2021110924 | 3 | 0.48541 | 72811.5 | 0.48872 | 0 | 0.76443 | 9555.375 | 0 | 0 | 64000 | 8811.5 | 0 | 0 | -3082 | 1350000 | 0 | 0
2021111001 | 4 | 0.46638 | 69957 | 0.57 | 0 | 0.75892 | 9486.5 | 0 | 0 | 64000 | 5957 | 0 | 0 | 0 | 1350000 | 0 | 0
2021111002 | 4 | 0.45624 | 68436 | 0.5747 | 0 | 0.77272 | 9659 | 0 | 0 | 64000 | 4436 | 0 | 0 | 0 | 1350000 | 0 | 0
2021111003 | 4 | 0.45295 | 67942.5 | 0.65981 | 0 | 0.76269 | 9533.625 | 0 | 0 | 64000 | 3942.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021111004 | 4 | 0.45403 | 68104.5 | 0.70495 | 0 | 0.75762 | 9470.25 | 0 | 0 | 64000 | 4104.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021111005 | 4 | 0.46615 | 69922.5 | 0.64627 | 0 | 0.71734 | 8966.75 | 0 | 0 | 64000 | 5922.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021111006 | 4 | 0.49499 | 74248.5 | 0.58365 | 0 | 0.6848 | 8560 | 0.00032 | 25.6 | 64000 | 8560 | 25.6 | 1662.9 | 1662.9 | 1350000 | 1662.9 | 0
2021111007 | 4 | 0.5433 | 81495 | 0.58892 | 0 | 0.65346 | 8168.25 | 0.0418 | 3344 | 64000 | 8168.25 | 3344 | 5982.75 | 4319.85 | 1350000 | 5982.75 | 0
2021111008 | 4 | 0.57005 | 85507.5 | 0.53649 | 0 | 0.6371 | 7963.75 | 0.2394 | 19152 | 64000 | 7963.75 | 13543.75 | 0 | -5982.75 | 1350000 | 0 | 0
2021111009 | 4 | 0.56994 | 85491 | 0.50693 | 0 | 0.60905 | 7613.125 | 0.41044 | 32835.2 | 64000 | 7613.125 | 13877.875 | 0 | 0 | 1350000 | 0 | 0
2021111010 | 4 | 0.56088 | 84132 | 0.38002 | 0 | 0.59789 | 7473.625 | 0.45901 | 36720.8 | 64000 | 7473.625 | 12658.375 | 0 | 0 | 1350000 | 0 | 0
2021111011 | 4 | 0.55565 | 83347.5 | 0.21843 | 0 | 0.5718 | 7147.5 | 0.49973 | 39978.4 | 64000 | 7147.5 | 12200 | 0 | 0 | 1350000 | 0 | 0
2021111012 | 4 | 0.5491 | 82365 | 0.18396 | 0 | 0.56938 | 7117.25 | 0.5106 | 40848 | 64000 | 7117.25 | 11247.75 | 0 | 0 | 1350000 | 0 | 0
2021111013 | 4 | 0.54735 | 82102.5 | 0.18963 | 0 | 0.5609 | 7011.25 | 0.51057 | 40845.6 | 64000 | 7011.25 | 11091.25 | 0 | 0 | 1350000 | 0 | 0
2021111014 | 4 | 0.54943 | 82414.5 | 0.16054 | 0 | 0.56236 | 7029.5 | 0.50788 | 40630.4 | 64000 | 7029.5 | 11385 | 0 | 0 | 1350000 | 0 | 0
2021111015 | 4 | 0.5504 | 82560 | 0.17385 | 0 | 0.58786 | 7348.25 | 0.48295 | 38636 | 64000 | 7348.25 | 11211.75 | 0 | 0 | 1350000 | 0 | 0
2021111016 | 4 | 0.55387 | 83080.5 | 0.17752 | 0 | 0.56877 | 7109.625 | 0.35324 | 28259.2 | 64000 | 7109.625 | 11970.875 | 0 | 0 | 1350000 | 0 | 0
2021111017 | 4 | 0.56469 | 84703.5 | 0.12734 | 0 | 0.56248 | 7031 | 0.09232 | 7385.6 | 64000 | 7031 | 7385.6 | 6286.9 | 6286.9 | 1350000 | 6286.9 | 0
2021111018 | 4 | 0.58915 | 88372.5 | 0.17708 | 0 | 0.5505 | 6881.25 | 0 | 0 | 64000 | 6881.25 | 0 | 17491.25 | 11204.35 | 1350000 | 17491.25 | 0
2021111019 | 4 | 0.5906 | 88590 | 0.14465 | 0 | 0.54166 | 6770.75 | 0 | 0 | 64000 | 6770.75 | 0 | 17819.25 | 328 | 1350000 | 17819.25 | 0
2021111020 | 4 | 0.57917 | 86875.5 | 0.08018 | 0 | 0.55026 | 6878.25 | 0 | 0 | 64000 | 6878.25 | 0 | 15997.25 | -1822 | 1350000 | 15997.25 | 0
2021111021 | 4 | 0.56352 | 84528 | 0.18797 | 0 | 0.559 | 6987.5 | 0 | 0 | 64000 | 6987.5 | 0 | 13540.5 | -2456.75 | 1350000 | 13540.5 | 0
2021111022 | 4 | 0.54304 | 81456 | 0.29613 | 0 | 0.55363 | 6920.375 | 0 | 0 | 64000 | 6920.375 | 0 | 10535.625 | -3004.875 | 1350000 | 10535.625 | 0
2021111023 | 4 | 0.51686 | 77529 | 0.37917 | 0 | 0.55844 | 6980.5 | 0 | 0 | 64000 | 6980.5 | 0 | 6548.5 | -3987.125 | 1350000 | 6548.5 | 0
2021111024 | 4 | 0.49156 | 73734 | 0.4623 | 0 | 0.53803 | 6725.375 | 0 | 0 | 64000 | 6725.375 | 0 | 3008.625 | -3539.875 | 1350000 | 3008.625 | 0
2021111101 | 5 | 0.47382 | 71073 | 0.60745 | 0 | 0.53791 | 6723.875 | 0 | 0 | 64000 | 6723.875 | 0 | 349.125 | -2659.5 | 1350000 | 349.125 | 0
2021111102 | 5 | 0.46479 | 69718.5 | 0.69161 | 0 | 0.52338 | 6542.25 | 0 | 0 | 64000 | 5718.5 | 0 | 0 | -349.125 | 1350000 | 0 | 0
2021111103 | 5 | 0.4604 | 69060 | 0.72038 | 0 | 0.48636 | 6079.5 | 0 | 0 | 64000 | 5060 | 0 | 0 | 0 | 1350000 | 0 | 0
2021111104 | 5 | 0.46122 | 69183 | 0.77904 | 0 | 0.42175 | 5271.875 | 0 | 0 | 64000 | 5183 | 0 | 0 | 0 | 1350000 | 0 | 0
2021111105 | 5 | 0.4716 | 70740 | 0.83477 | 0 | 0.33138 | 4142.25 | 0 | 0 | 64000 | 4142.25 | 0 | 2597.75 | 2597.75 | 1350000 | 2597.75 | 0
2021111106 | 5 | 0.50022 | 75033 | 0.89918 | 0 | 0.22364 | 2795.5 | 0.00748 | 598.4 | 64000 | 2795.5 | 598.4 | 7639.1 | 5041.35 | 1350000 | 7639.1 | 0
2021111107 | 5 | 0.54402 | 81603 | 0.93034 | 0 | 0.14602 | 1825.25 | 0.04595 | 3676 | 64000 | 1825.25 | 3676 | 12101.75 | 4462.65 | 1350000 | 12101.75 | 0
2021111108 | 5 | 0.5703 | 85545 | 0.94897 | 0 | 0.12954 | 1619.25 | 0.2684 | 21472 | 64000 | 1619.25 | 19925.75 | 0 | -12101.75 | 1350000 | 0 | 0
2021111109 | 5 | 0.5715 | 85725 | 0.94401 | 0 | 0.11571 | 1446.375 | 0.41931 | 33544.8 | 64000 | 1446.375 | 20278.625 | 0 | 0 | 1350000 | 0 | 0
2021111110 | 5 | 0.56707 | 85060.5 | 0.92895 | 0 | 0.09532 | 1191.5 | 0.41143 | 32914.4 | 64000 | 1191.5 | 19869 | 0 | 0 | 1350000 | 0 | 0
2021111111 | 5 | 0.56266 | 84399 | 0.92391 | 0 | 0.09554 | 1194.25 | 0.40553 | 32442.4 | 64000 | 1194.25 | 19204.75 | 0 | 0 | 1350000 | 0 | 0
2021111112 | 5 | 0.55854 | 83781 | 0.90985 | 0 | 0.09748 | 1218.5 | 0.41716 | 33372.8 | 64000 | 1218.5 | 18562.5 | 0 | 0 | 1350000 | 0 | 0
2021111113 | 5 | 0.55753 | 83629.5 | 0.92292 | 0 | 0.10681 | 1335.125 | 0.42677 | 34141.6 | 64000 | 1335.125 | 18294.375 | 0 | 0 | 1350000 | 0 | 0
2021111114 | 5 | 0.55871 | 83806.5 | 0.94095 | 0 | 0.1217 | 1521.25 | 0.40453 | 32362.4 | 64000 | 1521.25 | 18285.25 | 0 | 0 | 1350000 | 0 | 0
2021111115 | 5 | 0.55683 | 83524.5 | 0.91097 | 0 | 0.11184 | 1398 | 0.37698 | 30158.4 | 64000 | 1398 | 18126.5 | 0 | 0 | 1350000 | 0 | 0
2021111116 | 5 | 0.55835 | 83752.5 | 0.97033 | 0 | 0.10301 | 1287.625 | 0.25687 | 20549.6 | 64000 | 1287.625 | 18464.875 | 0 | 0 | 1350000 | 0 | 0
2021111117 | 5 | 0.56994 | 85491 | 0.97762 | 0 | 0.12707 | 1588.375 | 0.05597 | 4477.6 | 64000 | 1588.375 | 4477.6 | 15425.025 | 15425.025 | 1350000 | 15425.025 | 0
2021111118 | 5 | 0.59428 | 89142 | 0.99593 | 0 | 0.13724 | 1715.5 | 0.00148 | 118.4 | 64000 | 1715.5 | 118.4 | 23308.1 | 7883.075 | 1350000 | 23308.1 | 0
2021111119 | 5 | 0.59633 | 89449.5 | 0.99701 | 0 | 0.1464 | 1830 | 0 | 0 | 64000 | 1830 | 0 | 23619.5 | 311.4 | 1350000 | 23619.5 | 0
2021111120 | 5 | 0.58382 | 87573 | 0.99685 | 0 | 0.16477 | 2059.625 | 0 | 0 | 64000 | 2059.625 | 0 | 21513.375 | -2106.125 | 1350000 | 21513.375 | 0
2021111121 | 5 | 0.56796 | 85194 | 0.99512 | 0 | 0.16418 | 2052.25 | 0 | 0 | 64000 | 2052.25 | 0 | 19141.75 | -2371.625 | 1350000 | 19141.75 | 0
2021111122 | 5 | 0.54513 | 81769.5 | 0.985 | 0 | 0.17719 | 2214.875 | 0 | 0 | 64000 | 2214.875 | 0 | 15554.625 | -3587.125 | 1350000 | 15554.625 | 0
2021111123 | 5 | 0.51602 | 77403 | 0.96219 | 0 | 0.1971 | 2463.75 | 0 | 0 | 64000 | 2463.75 | 0 | 10939.25 | -4615.375 | 1350000 | 10939.25 | 0
2021111124 | 5 | 0.48911 | 73366.5 | 0.97025 | 0 | 0.24353 | 3044.125 | 0 | 0 | 64000 | 3044.125 | 0 | 6322.375 | -4616.875 | 1350000 | 6322.375 | 0
2021111201 | 6 | 0.46861 | 70291.5 | 0.94203 | 0 | 0.26577 | 3322.125 | 0 | 0 | 64000 | 3322.125 | 0 | 2969.375 | -3353 | 1350000 | 2969.375 | 0
2021111202 | 6 | 0.45715 | 68572.5 | 0.88625 | 0 | 0.27435 | 3429.375 | 0 | 0 | 64000 | 3429.375 | 0 | 1143.125 | -1826.25 | 1350000 | 1143.125 | 0
2021111203 | 6 | 0.45172 | 67758 | 0.86368 | 0 | 0.27457 | 3432.125 | 0 | 0 | 64000 | 3432.125 | 0 | 325.875 | -817.25 | 1350000 | 325.875 | 0
2021111204 | 6 | 0.45104 | 67656 | 0.88634 | 0 | 0.27881 | 3485.125 | 0 | 0 | 64000 | 3485.125 | 0 | 170.875 | -155 | 1350000 | 170.875 | 0
2021111205 | 6 | 0.46087 | 69130.5 | 0.93233 | 0 | 0.28436 | 3554.5 | 0 | 0 | 64000 | 3554.5 | 0 | 1576 | 1405.125 | 1350000 | 1576 | 0
2021111206 | 6 | 0.48686 | 73029 | 0.93827 | 0 | 0.24628 | 3078.5 | 0 | 0 | 64000 | 3078.5 | 0 | 5950.5 | 4374.5 | 1350000 | 5950.5 | 0
2021111207 | 6 | 0.53119 | 79678.5 | 0.88685 | 0 | 0.23139 | 2892.375 | 0.02285 | 1828 | 64000 | 2892.375 | 1828 | 10958.125 | 5007.625 | 1350000 | 10958.125 | 0
2021111208 | 6 | 0.56191 | 84286.5 | 0.76632 | 0 | 0.22414 | 2801.75 | 0.0809 | 6472 | 64000 | 2801.75 | 6472 | 11012.75 | 54.625 | 1350000 | 11012.75 | 0
2021111209 | 6 | 0.57441 | 86161.5 | 0.47541 | 0 | 0.18164 | 2270.5 | 0.10169 | 8135.2 | 64000 | 2270.5 | 8135.2 | 11755.8 | 743.05 | 1350000 | 11755.8 | 0
2021111210 | 6 | 0.57552 | 86328 | 0.39246 | 0 | 0.13395 | 1674.375 | 0.1149 | 9192 | 64000 | 1674.375 | 9192 | 11461.625 | -294.175 | 1350000 | 11461.625 | 0
2021111211 | 6 | 0.57242 | 85863 | 0.35095 | 0 | 0.09209 | 1151.125 | 0.13308 | 10646.4 | 64000 | 1151.125 | 10646.4 | 10065.475 | -1396.15 | 1350000 | 10065.475 | 0
2021111212 | 6 | 0.56786 | 85179 | 0.41656 | 0 | 0.07378 | 922.25 | 0.1217 | 9736 | 64000 | 922.25 | 9736 | 10520.75 | 455.275 | 1350000 | 10520.75 | 0
2021111213 | 6 | 0.56234 | 84351 | 0.5673 | 0 | 0.09009 | 1126.125 | 0.09427 | 7541.6 | 64000 | 1126.125 | 7541.6 | 11683.275 | 1162.525 | 1350000 | 11683.275 | 0
2021111214 | 6 | 0.55717 | 83575.5 | 0.60448 | 0 | 0.10566 | 1320.75 | 0.07046 | 5636.8 | 64000 | 1320.75 | 5636.8 | 12617.95 | 934.675 | 1350000 | 12617.95 | 0
2021111215 | 6 | 0.55467 | 83200.5 | 0.54541 | 0 | 0.11869 | 1483.625 | 0.03452 | 2761.6 | 64000 | 1483.625 | 2761.6 | 14955.275 | 2337.325 | 1350000 | 14955.275 | 0
2021111216 | 6 | 0.55717 | 83575.5 | 0.49169 | 0 | 0.13432 | 1679 | 0.01698 | 1358.4 | 64000 | 1679 | 1358.4 | 16538.1 | 1582.825 | 1350000 | 16538.1 | 0
2021111217 | 6 | 0.56798 | 85197 | 0.35072 | 0 | 0.15409 | 1926.125 | 0.00193 | 154.4 | 64000 | 1926.125 | 154.4 | 19116.475 | 2578.375 | 1350000 | 19116.475 | 0
2021111218 | 6 | 0.58919 | 88378.5 | 0.31454 | 0 | 0.1789 | 2236.25 | 0 | 0 | 64000 | 2236.25 | 0 | 22142.25 | 3025.775 | 1350000 | 22142.25 | 0
2021111219 | 6 | 0.58804 | 88206 | 0.40943 | 0 | 0.21136 | 2642 | 0 | 0 | 64000 | 2642 | 0 | 21564 | -578.25 | 1350000 | 21564 | 0
2021111220 | 6 | 0.57683 | 86524.5 | 0.5203 | 0 | 0.23078 | 2884.75 | 0 | 0 | 64000 | 2884.75 | 0 | 19639.75 | -1924.25 | 1350000 | 19639.75 | 0
2021111221 | 6 | 0.56416 | 84624 | 0.58689 | 0 | 0.25251 | 3156.375 | 0 | 0 | 64000 | 3156.375 | 0 | 17467.625 | -2172.125 | 1350000 | 17467.625 | 0
2021111222 | 6 | 0.5489 | 82335 | 0.62078 | 0 | 0.24882 | 3110.25 | 0 | 0 | 64000 | 3110.25 | 0 | 15224.75 | -2242.875 | 1350000 | 15224.75 | 0
2021111223 | 6 | 0.52744 | 79116 | 0.66666 | 0 | 0.23284 | 2910.5 | 0 | 0 | 64000 | 2910.5 | 0 | 12205.5 | -3019.25 | 1350000 | 12205.5 | 0
2021111224 | 6 | 0.50549 | 75823.5 | 0.65092 | 0 | 0.25259 | 3157.375 | 0 | 0 | 64000 | 3157.375 | 0 | 8666.125 | -3539.375 | 1350000 | 8666.125 | 0
2021111301 | 7 | 0.48689 | 73033.5 | 0.7013 | 0 | 0.27083 | 3385.375 | 0 | 0 | 64000 | 3385.375 | 0 | 5648.125 | -3018 | 1350000 | 5648.125 | 0
2021111302 | 7 | 0.47694 | 71541 | 0.67356 | 0 | 0.29016 | 3627 | 0 | 0 | 64000 | 3627 | 0 | 3914 | -1734.125 | 1350000 | 3914 | 0
2021111303 | 7 | 0.47166 | 70749 | 0.57929 | 0 | 0.23619 | 2952.375 | 0 | 0 | 64000 | 2952.375 | 0 | 3796.625 | -117.375 | 1350000 | 3796.625 | 0
2021111304 | 7 | 0.47111 | 70666.5 | 0.56642 | 0 | 0.19308 | 2413.5 | 0 | 0 | 64000 | 2413.5 | 0 | 4253 | 456.375 | 1350000 | 4253 | 0
2021111305 | 7 | 0.47659 | 71488.5 | 0.58282 | 0 | 0.14974 | 1871.75 | 0 | 0 | 64000 | 1871.75 | 0 | 5616.75 | 1363.75 | 1350000 | 5616.75 | 0
2021111306 | 7 | 0.48992 | 73488 | 0.64646 | 0 | 0.13003 | 1625.375 | 0 | 0 | 64000 | 1625.375 | 0 | 7862.625 | 2245.875 | 1350000 | 7862.625 | 0
2021111307 | 7 | 0.51016 | 76524 | 0.63005 | 0 | 0.09956 | 1244.5 | 0.00314 | 251.2 | 64000 | 1244.5 | 251.2 | 11028.3 | 3165.675 | 1350000 | 11028.3 | 0
2021111308 | 7 | 0.52829 | 79243.5 | 0.55083 | 0 | 0.10341 | 1292.625 | 0.02045 | 1636 | 64000 | 1292.625 | 1636 | 12314.875 | 1286.575 | 1350000 | 12314.875 | 0
2021111309 | 7 | 0.5418 | 81270 | 0.67166 | 0 | 0.10583 | 1322.875 | 0.03471 | 2776.8 | 64000 | 1322.875 | 2776.8 | 13170.325 | 855.45 | 1350000 | 13170.325 | 0
2021111310 | 7 | 0.54962 | 82443 | 0.75844 | 0 | 0.08521 | 1065.125 | 0.0562 | 4496 | 64000 | 1065.125 | 4496 | 12881.875 | -288.45 | 1350000 | 12881.875 | 0
2021111311 | 7 | 0.55268 | 82902 | 0.83575 | 0 | 0.08293 | 1036.625 | 0.07283 | 5826.4 | 64000 | 1036.625 | 5826.4 | 12038.975 | -842.9 | 1350000 | 12038.975 | 0
2021111312 | 7 | 0.55224 | 82836 | 0.91737 | 0 | 0.0937 | 1171.25 | 0.07744 | 6195.2 | 64000 | 1171.25 | 6195.2 | 11469.55 | -569.425 | 1350000 | 11469.55 | 0
2021111313 | 7 | 0.55072 | 82608 | 0.93307 | 0 | 0.10993 | 1374.125 | 0.07074 | 5659.2 | 64000 | 1374.125 | 5659.2 | 11574.675 | 105.125 | 1350000 | 11574.675 | 0
2021111314 | 7 | 0.54645 | 81967.5 | 0.94371 | 0 | 0.14593 | 1824.125 | 0.04869 | 3895.2 | 64000 | 1824.125 | 3895.2 | 12248.175 | 673.5 | 1350000 | 12248.175 | 0
2021111315 | 7 | 0.54173 | 81259.5 | 0.93373 | 0 | 0.21748 | 2718.5 | 0.02279 | 1823.2 | 64000 | 2718.5 | 1823.2 | 12717.8 | 469.625 | 1350000 | 12717.8 | 0
2021111316 | 7 | 0.54439 | 81658.5 | 0.942 | 0 | 0.23276 | 2909.5 | 0.01459 | 1167.2 | 64000 | 2909.5 | 1167.2 | 13581.8 | 864 | 1350000 | 13581.8 | 0
2021111317 | 7 | 0.56238 | 84357 | 0.90153 | 0 | 0.22806 | 2850.75 | 0.00242 | 193.6 | 64000 | 2850.75 | 193.6 | 17312.65 | 3730.85 | 1350000 | 17312.65 | 0
2021111318 | 7 | 0.59098 | 88647 | 0.87411 | 0 | 0.16556 | 2069.5 | 0 | 0 | 64000 | 2069.5 | 0 | 22577.5 | 5264.85 | 1350000 | 22577.5 | 0
2021111319 | 7 | 0.59478 | 89217 | 0.84451 | 0 | 0.14301 | 1787.625 | 0 | 0 | 64000 | 1787.625 | 0 | 23429.375 | 851.875 | 1350000 | 23429.375 | 0
2021111320 | 7 | 0.58914 | 88371 | 0.84558 | 0 | 0.14849 | 1856.125 | 0 | 0 | 64000 | 1856.125 | 0 | 22514.875 | -914.5 | 1350000 | 22514.875 | 0
2021111321 | 7 | 0.58024 | 87036 | 0.87675 | 0 | 0.13526 | 1690.75 | 0 | 0 | 64000 | 1690.75 | 0 | 21345.25 | -1169.625 | 1350000 | 21345.25 | 0
2021111322 | 7 | 0.56815 | 85222.5 | 0.9 | 0 | 0.10716 | 1339.5 | 0 | 0 | 64000 | 1339.5 | 0 | 19883 | -1462.25 | 1350000 | 19883 | 0
2021111323 | 7 | 0.55119 | 82678.5 | 0.88254 | 0 | 0.11524 | 1440.5 | 0 | 0 | 64000 | 1440.5 | 0 | 17238 | -2645 | 1350000 | 17238 | 0
2021111324 | 7 | 0.53204 | 79806 | 0.86915 | 0 | 0.11232 | 1404 | 0 | 0 | 64000 | 1404 | 0 | 14402 | -2836 | 1350000 | 14402 | 0
2021111401 | 1 | 0.51661 | 77491.5 | 0.82195 | 0 | 0.13034 | 1629.25 | 0 | 0 | 64000 | 1629.25 | 0 | 11862.25 | -2539.75 | 1350000 | 11862.25 | 0
2021111402 | 1 | 0.50764 | 76146 | 0.80675 | 0 | 0.15505 | 1938.125 | 0 | 0 | 64000 | 1938.125 | 0 | 10207.875 | -1654.375 | 1350000 | 10207.875 | 0
2021111403 | 1 | 0.5041 | 75615 | 0.72625 | 0 | 0.16428 | 2053.5 | 0 | 0 | 64000 | 2053.5 | 0 | 9561.5 | -646.375 | 1350000 | 9561.5 | 0
2021111404 | 1 | 0.50429 | 75643.5 | 0.66811 | 0 | 0.15566 | 1945.75 | 0 | 0 | 64000 | 1945.75 | 0 | 9697.75 | 136.25 | 1350000 | 9697.75 | 0
2021111405 | 1 | 0.50928 | 76392 | 0.5746 | 0 | 0.12373 | 1546.625 | 0 | 0 | 64000 | 1546.625 | 0 | 10845.375 | 1147.625 | 1350000 | 10845.375 | 0
2021111406 | 1 | 0.52073 | 78109.5 | 0.50274 | 0 | 0.07906 | 988.25 | 0 | 0 | 64000 | 988.25 | 0 | 13121.25 | 2275.875 | 1350000 | 13121.25 | 0
2021111407 | 1 | 0.5377 | 80655 | 0.53917 | 0 | 0.0454 | 567.5 | 0.02952 | 2361.6 | 64000 | 567.5 | 2361.6 | 13725.9 | 604.65 | 1350000 | 13725.9 | 0
2021111408 | 1 | 0.55275 | 82912.5 | 0.50852 | 0 | 0.02889 | 361.125 | 0.25215 | 20172 | 64000 | 361.125 | 18551.375 | 0 | -13725.9 | 1350000 | 0 | 0
2021111409 | 1 | 0.56036 | 84054 | 0.39933 | 0 | 0.01518 | 189.75 | 0.46242 | 36993.6 | 64000 | 189.75 | 19864.25 | 0 | 0 | 1350000 | 0 | 0
2021111410 | 1 | 0.56376 | 84564 | 0.20863 | 0 | 0.01041 | 130.125 | 0.48952 | 39161.6 | 64000 | 130.125 | 20433.875 | 0 | 0 | 1350000 | 0 | 0
2021111411 | 1 | 0.56366 | 84549 | 0.11481 | 0 | 0.00407 | 50.875 | 0.49815 | 39852 | 64000 | 50.875 | 20498.125 | 0 | 0 | 1350000 | 0 | 0
2021111412 | 1 | 0.56325 | 84487.5 | 0.15499 | 0 | 0.00401 | 50.125 | 0.49732 | 39785.6 | 64000 | 50.125 | 20437.375 | 0 | 0 | 1350000 | 0 | 0
2021111413 | 1 | 0.56152 | 84228 | 0.24229 | 0 | 0.01071 | 133.875 | 0.51016 | 40812.8 | 64000 | 133.875 | 20094.125 | 0 | 0 | 1350000 | 0 | 0
2021111414 | 1 | 0.55927 | 83890.5 | 0.35683 | 0 | 0.02236 | 279.5 | 0.51808 | 41446.4 | 64000 | 279.5 | 19611 | 0 | 0 | 1350000 | 0 | 0
2021111415 | 1 | 0.5586 | 83790 | 0.39473 | 0 | 0.03133 | 391.625 | 0.45774 | 36619.2 | 64000 | 391.625 | 19398.375 | 0 | 0 | 1350000 | 0 | 0
2021111416 | 1 | 0.5659 | 84885 | 0.32515 | 0 | 0.04008 | 501 | 0.2795 | 22360 | 64000 | 501 | 20384 | 0 | 0 | 1350000 | 0 | 0
2021111417 | 1 | 0.58735 | 88102.5 | 0.27459 | 0 | 0.05617 | 702.125 | 0.05544 | 4435.2 | 64000 | 702.125 | 4435.2 | 18965.175 | 18965.175 | 1350000 | 18965.175 | 0
2021111418 | 1 | 0.61523 | 92284.5 | 0.37418 | 0 | 0.06662 | 832.75 | 0 | 0 | 64000 | 832.75 | 0 | 27451.75 | 8486.575 | 1348014.5 | 27451.75 | 0
2021111419 | 1 | 0.61811 | 92716.5 | 0.51925 | 0 | 0.07532 | 941.5 | 0 | 0 | 64000 | 941.5 | 0 | 27775 | 323.25 | 1345705.75 | 27775 | 0
2021111420 | 1 | 0.61043 | 91564.5 | 0.64007 | 0 | 0.07332 | 916.5 | 0 | 0 | 64000 | 916.5 | 0 | 26648 | -1127 | 1344524 | 26648 | 0
2021111421 | 1 | 0.59721 | 89581.5 | 0.68338 | 0 | 0.08286 | 1035.75 | 0 | 0 | 64000 | 1035.75 | 0 | 24545.75 | -2102.25 | 1345444.5 | 24545.75 | 0
2021111422 | 1 | 0.57829 | 86743.5 | 0.68588 | 0 | 0.10636 | 1329.5 | 0 | 0 | 64000 | 1329.5 | 0 | 21414 | -3131.75 | 1349496.75 | 21414 | 0
2021111423 | 1 | 0.55419 | 83128.5 | 0.57171 | 0 | 0.11006 | 1375.75 | 0 | 0 | 64000 | 1375.75 | 0 | 17752.75 | -3661.25 | 1350000 | 17752.75 | 0
2021111424 | 1 | 0.53162 | 79743 | 0.62506 | 0 | 0.13985 | 1748.125 | 0 | 0 | 64000 | 1748.125 | 0 | 13994.875 | -3757.875 | 1350000 | 13994.875 | 0
2021111501 | 2 | 0.51767 | 77650.5 | 0.75573 | 0 | 0.16675 | 2084.375 | 0 | 0 | 64000 | 2084.375 | 0 | 11566.125 | -2428.75 | 1350000 | 11566.125 | 0
2021111502 | 2 | 0.50959 | 76438.5 | 0.82348 | 0 | 0.18887 | 2360.875 | 0 | 0 | 64000 | 2360.875 | 0 | 10077.625 | -1488.5 | 1350000 | 10077.625 | 0
2021111503 | 2 | 0.50788 | 76182 | 0.78276 | 0 | 0.22014 | 2751.75 | 0 | 0 | 64000 | 2751.75 | 0 | 9430.25 | -647.375 | 1350000 | 9430.25 | 0
2021111504 | 2 | 0.51226 | 76839 | 0.81516 | 0 | 0.23019 | 2877.375 | 0 | 0 | 64000 | 2877.375 | 0 | 9961.625 | 531.375 | 1350000 | 9961.625 | 0
2021111505 | 2 | 0.52612 | 78918 | 0.85283 | 0 | 0.24834 | 3104.25 | 0 | 0 | 64000 | 3104.25 | 0 | 11813.75 | 1852.125 | 1350000 | 11813.75 | 0
2021111506 | 2 | 0.55927 | 83890.5 | 0.86382 | 0 | 0.24421 | 3052.625 | 0 | 0 | 64000 | 3052.625 | 0 | 16837.875 | 5024.125 | 1350000 | 16837.875 | 0
2021111507 | 2 | 0.61073 | 91609.5 | 0.86776 | 0 | 0.25282 | 3160.25 | 0.0349 | 2792 | 64000 | 3160.25 | 2792 | 21657.25 | 4819.375 | 1350000 | 21657.25 | 0
2021111508 | 2 | 0.6418 | 96270 | 0.84355 | 0 | 0.25027 | 3128.375 | 0.24164 | 19331.2 | 64000 | 3128.375 | 19331.2 | 9810.425 | -11846.825 | 1350000 | 9810.425 | 0
2021111509 | 2 | 0.64623 | 96934.5 | 0.89223 | 0 | 0.24044 | 3005.5 | 0.39367 | 31493.6 | 64000 | 3005.5 | 29929 | 0 | -9810.425 | 1350000 | 0 | 0
2021111510 | 2 | 0.64073 | 96109.5 | 0.91656 | 0 | 0.23547 | 2943.375 | 0.43313 | 34650.4 | 64000 | 2943.375 | 29166.125 | 0 | 0 | 1350000 | 0 | 0
2021111511 | 2 | 0.63482 | 95223 | 0.93474 | 0 | 0.2375 | 2968.75 | 0.44749 | 35799.2 | 64000 | 2968.75 | 28254.25 | 0 | 0 | 1350000 | 0 | 0
2021111512 | 2 | 0.62906 | 94359 | 0.93117 | 0 | 0.23403 | 2925.375 | 0.41789 | 33431.2 | 64000 | 2925.375 | 27433.625 | 0 | 0 | 1350000 | 0 | 0
2021111513 | 2 | 0.62458 | 93687 | 0.92492 | 0 | 0.28257 | 3532.125 | 0.40112 | 32089.6 | 64000 | 3532.125 | 26154.875 | 0 | 0 | 1350000 | 0 | 0
2021111514 | 2 | 0.62115 | 93172.5 | 0.91123 | 0 | 0.30297 | 3787.125 | 0.30821 | 24656.8 | 64000 | 3787.125 | 24656.8 | 728.575 | 728.575 | 1350000 | 728.575 | 0
2021111515 | 2 | 0.61555 | 92332.5 | 0.91955 | 0 | 0.31588 | 3948.5 | 0.15792 | 12633.6 | 64000 | 3948.5 | 12633.6 | 11750.4 | 11021.825 | 1350000 | 11750.4 | 0
2021111516 | 2 | 0.62 | 93000 | 0.93202 | 0 | 0.30462 | 3807.75 | 0.06884 | 5507.2 | 64000 | 3807.75 | 5507.2 | 19685.05 | 7934.65 | 1350000 | 19685.05 | 0
2021111517 | 2 | 0.6378 | 95670 | 0.87908 | 0 | 0.32713 | 4089.125 | 0.01173 | 938.4 | 64000 | 4089.125 | 938.4 | 26642.475 | 6957.425 | 1348823.775 | 26642.475 | 0
2021111518 | 2 | 0.66979 | 100468.5 | 0.88768 | 0 | 0.35436 | 4429.5 | 0 | 0 | 64000 | 4429.5 | 0 | 32039 | 5396.525 | 1342251.025 | 32039 | 0
2021111519 | 2 | 0.67217 | 100825.5 | 0.87917 | 0 | 0.3779 | 4723.75 | 0 | 0 | 64000 | 4723.75 | 0 | 32101.75 | 62.75 | 1335615.525 | 32101.75 | 0
2021111520 | 2 | 0.66406 | 99609 | 0.84059 | 0 | 0.41474 | 5184.25 | 0 | 0 | 64000 | 5184.25 | 0 | 30424.75 | -1677 | 1330657.025 | 30424.75 | 0
2021111521 | 2 | 0.65109 | 97663.5 | 0.83922 | 0 | 0.47026 | 5878.25 | 0 | 0 | 64000 | 5878.25 | 0 | 27785.25 | -2639.5 | 1328338.025 | 27785.25 | 0
2021111522 | 2 | 0.62924 | 94386 | 0.81146 | 0 | 0.52419 | 6552.375 | 0 | 0 | 64000 | 6552.375 | 0 | 23833.625 | -3951.625 | 1329970.65 | 23833.625 | 0
2021111523 | 2 | 0.59823 | 89734.5 | 0.77487 | 0 | 0.53473 | 6684.125 | 0 | 0 | 64000 | 6684.125 | 0 | 19050.375 | -4783.25 | 1336386.525 | 19050.375 | 0
2021111524 | 2 | 0.56957 | 85435.5 | 0.74534 | 0 | 0.59285 | 7410.625 | 0 | 0 | 64000 | 7410.625 | 0 | 14024.875 | -5025.5 | 1347827.9 | 14024.875 | 0
2021111601 | 3 | 0.54974 | 82461 | 0.74481 | 0 | 0.60982 | 7622.75 | 0 | 0 | 64000 | 7622.75 | 0 | 10838.25 | -3186.625 | 1350000 | 10838.25 | 0
2021111602 | 3 | 0.54003 | 81004.5 | 0.70772 | 0 | 0.5951 | 7438.75 | 0 | 0 | 64000 | 7438.75 | 0 | 9565.75 | -1272.5 | 1350000 | 9565.75 | 0
2021111603 | 3 | 0.53595 | 80392.5 | 0.69861 | 0 | 0.56559 | 7069.875 | 0 | 0 | 64000 | 7069.875 | 0 | 9322.625 | -243.125 | 1350000 | 9322.625 | 0
2021111604 | 3 | 0.53844 | 80766 | 0.67892 | 0 | 0.534 | 6675 | 0 | 0 | 64000 | 6675 | 0 | 10091 | 768.375 | 1350000 | 10091 | 0
2021111605 | 3 | 0.55128 | 82692 | 0.61764 | 0 | 0.55933 | 6991.625 | 0 | 0 | 64000 | 6991.625 | 0 | 11700.375 | 1609.375 | 1350000 | 11700.375 | 0
2021111606 | 3 | 0.58367 | 87550.5 | 0.56024 | 0 | 0.54726 | 6840.75 | 0 | 0 | 64000 | 6840.75 | 0 | 16709.75 | 5009.375 | 1350000 | 16709.75 | 0
2021111607 | 3 | 0.63347 | 95020.5 | 0.53492 | 0 | 0.58654 | 7331.75 | 0.00249 | 199.2 | 64000 | 7331.75 | 199.2 | 23489.55 | 6779.8 | 1350000 | 23489.55 | 0
2021111608 | 3 | 0.65846 | 98769 | 0.46692 | 0 | 0.51459 | 6432.375 | 0.02318 | 1854.4 | 64000 | 6432.375 | 1854.4 | 26482.225 | 2992.675 | 1348984.025 | 26482.225 | 0
2021111609 | 3 | 0.64806 | 97209 | 0.34797 | 0 | 0.49912 | 6239 | 0.0512 | 4096 | 64000 | 6239 | 4096 | 22874 | -3608.225 | 1350000 | 22874 | 0
2021111610 | 3 | 0.62929 | 94393.5 | 0.24914 | 0 | 0.50307 | 6288.375 | 0.08896 | 7116.8 | 64000 | 6288.375 | 7116.8 | 16988.325 | -5885.675 | 1350000 | 16988.325 | 0
2021111611 | 3 | 0.61199 | 91798.5 | 0.1822 | 0 | 0.4426 | 5532.5 | 0.12837 | 10269.6 | 64000 | 5532.5 | 10269.6 | 11996.4 | -4991.925 | 1350000 | 11996.4 | 0
2021111612 | 3 | 0.59849 | 89773.5 | 0.19141 | 0 | 0.3329 | 4161.25 | 0.15109 | 12087.2 | 64000 | 4161.25 | 12087.2 | 9525.05 | -2471.35 | 1350000 | 9525.05 | 0
2021111613 | 3 | 0.5875 | 88125 | 0.19493 | 0 | 0.27507 | 3438.375 | 0.14556 | 11644.8 | 64000 | 3438.375 | 11644.8 | 9041.825 | -483.225 | 1350000 | 9041.825 | 0
2021111614 | 3 | 0.58095 | 87142.5 | 0.19409 | 0 | 0.27932 | 3491.5 | 0.11574 | 9259.2 | 64000 | 3491.5 | 9259.2 | 10391.8 | 1349.975 | 1350000 | 10391.8 | 0
2021111615 | 3 | 0.57719 | 86578.5 | 0.20996 | 0 | 0.32915 | 4114.375 | 0.07343 | 5874.4 | 64000 | 4114.375 | 5874.4 | 12589.725 | 2197.925 | 1350000 | 12589.725 | 0
2021111616 | 3 | 0.57887 | 86830.5 | 0.20535 | 0 | 0.33357 | 4169.625 | 0.0381 | 3048 | 64000 | 4169.625 | 3048 | 15612.875 | 3023.15 | 1350000 | 15612.875 | 0
2021111617 | 3 | 0.59655 | 89482.5 | 0.14944 | 0 | 0.31437 | 3929.625 | 0.00724 | 579.2 | 64000 | 3929.625 | 579.2 | 20973.675 | 5360.8 | 1350000 | 20973.675 | 0
2021111618 | 3 | 0.63334 | 95001 | 0.12716 | 0 | 0.34163 | 4270.375 | 0 | 0 | 64000 | 4270.375 | 0 | 26730.625 | 5756.95 | 1348735.625 | 26730.625 | 0
2021111619 | 3 | 0.64152 | 96228 | 0.15278 | 0 | 0.3393 | 4241.25 | 0 | 0 | 64000 | 4241.25 | 0 | 27986.75 | 1256.125 | 1346215.125 | 27986.75 | 0
2021111620 | 3 | 0.63748 | 95622 | 0.12512 | 0 | 0.36855 | 4606.875 | 0 | 0 | 64000 | 4606.875 | 0 | 27015.125 | -971.625 | 1344666.25 | 27015.125 | 0
2021111621 | 3 | 0.62525 | 93787.5 | 0.12386 | 0 | 0.36703 | 4587.875 | 0 | 0 | 64000 | 4587.875 | 0 | 25199.625 | -1815.5 | 1344932.875 | 25199.625 | 0
2021111622 | 3 | 0.60492 | 90738 | 0.14853 | 0 | 0.35933 | 4491.625 | 0 | 0 | 64000 | 4491.625 | 0 | 22246.375 | -2953.25 | 1348152.75 | 22246.375 | 0
2021111623 | 3 | 0.57624 | 86436 | 0.23127 | 0 | 0.34989 | 4373.625 | 0 | 0 | 64000 | 4373.625 | 0 | 18062.375 | -4184 | 1350000 | 18062.375 | 0
2021111624 | 3 | 0.54828 | 82242 | 0.34436 | 0 | 0.33732 | 4216.5 | 0 | 0 | 64000 | 4216.5 | 0 | 14025.5 | -4036.875 | 1350000 | 14025.5 | 0
2021111701 | 4 | 0.52872 | 79308 | 0.45614 | 0 | 0.34434 | 4304.25 | 0 | 0 | 64000 | 4304.25 | 0 | 11003.75 | -3021.75 | 1350000 | 11003.75 | 0
2021111702 | 4 | 0.51871 | 77806.5 | 0.5474 | 0 | 0.35393 | 4424.125 | 0 | 0 | 64000 | 4424.125 | 0 | 9382.375 | -1621.375 | 1350000 | 9382.375 | 0
2021111703 | 4 | 0.51362 | 77043 | 0.5889 | 0 | 0.34005 | 4250.625 | 0 | 0 | 64000 | 4250.625 | 0 | 8792.375 | -590 | 1350000 | 8792.375 | 0
2021111704 | 4 | 0.51423 | 77134.5 | 0.63564 | 0 | 0.30454 | 3806.75 | 0 | 0 | 64000 | 3806.75 | 0 | 9327.75 | 535.375 | 1350000 | 9327.75 | 0
2021111705 | 4 | 0.52484 | 78726 | 0.6804 | 0 | 0.28699 | 3587.375 | 0 | 0 | 64000 | 3587.375 | 0 | 11138.625 | 1810.875 | 1350000 | 11138.625 | 0
2021111706 | 4 | 0.55339 | 83008.5 | 0.72595 | 0 | 0.27003 | 3375.375 | 0 | 0 | 64000 | 3375.375 | 0 | 15633.125 | 4494.5 | 1350000 | 15633.125 | 0
2021111707 | 4 | 0.59961 | 89941.5 | 0.76247 | 0 | 0.28132 | 3516.5 | 0.00418 | 334.4 | 64000 | 3516.5 | 334.4 | 22090.6 | 6457.475 | 1350000 | 22090.6 | 0
2021111708 | 4 | 0.62333 | 93499.5 | 0.8164 | 0 | 0.30623 | 3827.875 | 0.02386 | 1908.8 | 64000 | 3827.875 | 1908.8 | 23762.825 | 1672.225 | 1350000 | 23762.825 | 0
2021111709 | 4 | 0.61554 | 92331 | 0.84381 | 0 | 0.35713 | 4464.125 | 0.05754 | 4603.2 | 64000 | 4464.125 | 4603.2 | 19263.675 | -4499.15 | 1350000 | 19263.675 | 0
2021111710 | 4 | 0.60224 | 90336 | 0.83729 | 0 | 0.37946 | 4743.25 | 0.09895 | 7916 | 64000 | 4743.25 | 7916 | 13676.75 | -5586.925 | 1350000 | 13676.75 | 0
2021111711 | 4 | 0.59282 | 88923 | 0.79845 | 0 | 0.32813 | 4101.625 | 0.13309 | 10647.2 | 64000 | 4101.625 | 10647.2 | 10174.175 | -3502.575 | 1350000 | 10174.175 | 0
2021111712 | 4 | 0.58249 | 87373.5 | 0.76586 | 0 | 0.25297 | 3162.125 | 0.14035 | 11228 | 64000 | 3162.125 | 11228 | 8983.375 | -1190.8 | 1350000 | 8983.375 | 0
2021111713 | 4 | 0.57424 | 86136 | 0.72845 | 0 | 0.26131 | 3266.375 | 0.12558 | 10046.4 | 64000 | 3266.375 | 10046.4 | 8823.225 | -160.15 | 1350000 | 8823.225 | 0
2021111714 | 4 | 0.57229 | 85843.5 | 0.68185 | 0 | 0.31459 | 3932.375 | 0.08864 | 7091.2 | 64000 | 3932.375 | 7091.2 | 10819.925 | 1996.7 | 1350000 | 10819.925 | 0
2021111715 | 4 | 0.57018 | 85527 | 0.64918 | 0 | 0.32043 | 4005.375 | 0.05954 | 4763.2 | 64000 | 4005.375 | 4763.2 | 12758.425 | 1938.5 | 1350000 | 12758.425 | 0
2021111716 | 4 | 0.57179 | 85768.5 | 0.65504 | 0 | 0.28688 | 3586 | 0.02857 | 2285.6 | 64000 | 3586 | 2285.6 | 15896.9 | 3138.475 | 1350000 | 15896.9 | 0
2021111717 | 4 | 0.5844 | 87660 | 0.69994 | 0 | 0.24055 | 3006.875 | 0.00424 | 339.2 | 64000 | 3006.875 | 339.2 | 20313.925 | 4417.025 | 1350000 | 20313.925 | 0
2021111718 | 4 | 0.60956 | 91434 | 0.66171 | 0 | 0.25988 | 3248.5 | 0 | 0 | 64000 | 3248.5 | 0 | 24185.5 | 3871.575 | 1350000 | 24185.5 | 0
2021111719 | 4 | 0.61129 | 91693.5 | 0.6841 | 0 | 0.30166 | 3770.75 | 0 | 0 | 64000 | 3770.75 | 0 | 23922.75 | -262.75 | 1350000 | 23922.75 | 0
2021111720 | 4 | 0.60168 | 90252 | 0.75606 | 0 | 0.38384 | 4798 | 0 | 0 | 64000 | 4798 | 0 | 21454 | -2468.75 | 1350000 | 21454 | 0
2021111721 | 4 | 0.5884 | 88260 | 0.78272 | 0 | 0.41311 | 5163.875 | 0 | 0 | 64000 | 5163.875 | 0 | 19096.125 | -2357.875 | 1350000 | 19096.125 | 0
2021111722 | 4 | 0.5657 | 84855 | 0.77622 | 0 | 0.39727 | 4965.875 | 0 | 0 | 64000 | 4965.875 | 0 | 15889.125 | -3207 | 1350000 | 15889.125 | 0
2021111723 | 4 | 0.5346 | 80190 | 0.83763 | 0 | 0.37911 | 4738.875 | 0 | 0 | 64000 | 4738.875 | 0 | 11451.125 | -4438 | 1350000 | 11451.125 | 0
2021111724 | 4 | 0.50633 | 75949.5 | 0.90809 | 0 | 0.38295 | 4786.875 | 0 | 0 | 64000 | 4786.875 | 0 | 7162.625 | -4288.5 | 1350000 | 7162.625 | 0
2021111801 | 5 | 0.48625 | 72937.5 | 0.92324 | 0 | 0.38442 | 4805.25 | 0 | 0 | 64000 | 4805.25 | 0 | 4132.25 | -3030.375 | 1350000 | 4132.25 | 0
2021111802 | 5 | 0.47324 | 70986 | 0.93615 | 0 | 0.38922 | 4865.25 | 0 | 0 | 64000 | 4865.25 | 0 | 2120.75 | -2011.5 | 1350000 | 2120.75 | 0
2021111803 | 5 | 0.46911 | 70366.5 | 0.94158 | 0 | 0.3734 | 4667.5 | 0 | 0 | 64000 | 4667.5 | 0 | 1699 | -421.75 | 1350000 | 1699 | 0
2021111804 | 5 | 0.47 | 70500 | 0.93357 | 0 | 0.37765 | 4720.625 | 0 | 0 | 64000 | 4720.625 | 0 | 1779.375 | 80.375 | 1350000 | 1779.375 | 0
2021111805 | 5 | 0.48167 | 72250.5 | 0.92422 | 0 | 0.37869 | 4733.625 | 0 | 0 | 64000 | 4733.625 | 0 | 3516.875 | 1737.5 | 1350000 | 3516.875 | 0
2021111806 | 5 | 0.51061 | 76591.5 | 0.9046 | 0 | 0.36515 | 4564.375 | 0 | 0 | 64000 | 4564.375 | 0 | 8027.125 | 4510.25 | 1350000 | 8027.125 | 0
2021111807 | 5 | 0.5596 | 83940 | 0.90194 | 0 | 0.37734 | 4716.75 | 0.00206 | 164.8 | 64000 | 4716.75 | 164.8 | 15058.45 | 7031.325 | 1350000 | 15058.45 | 0
2021111808 | 5 | 0.58865 | 88297.5 | 0.89461 | 0 | 0.36311 | 4538.875 | 0.01586 | 1268.8 | 64000 | 4538.875 | 1268.8 | 18489.825 | 3431.375 | 1350000 | 18489.825 | 0
2021111809 | 5 | 0.58787 | 88180.5 | 0.8775 | 0 | 0.3603 | 4503.75 | 0.03365 | 2692 | 64000 | 4503.75 | 2692 | 16984.75 | -1505.075 | 1350000 | 16984.75 | 0
2021111810 | 5 | 0.58111 | 87166.5 | 0.88912 | 0 | 0.35029 | 4378.625 | 0.05748 | 4598.4 | 64000 | 4378.625 | 4598.4 | 14189.475 | -2795.275 | 1350000 | 14189.475 | 0
2021111811 | 5 | 0.57687 | 86530.5 | 0.90331 | 0 | 0.30851 | 3856.375 | 0.064 | 5120 | 64000 | 3856.375 | 5120 | 13554.125 | -635.35 | 1350000 | 13554.125 | 0
2021111812 | 5 | 0.5757 | 86355 | 0.87527 | 0 | 0.24766 | 3095.75 | 0.07214 | 5771.2 | 64000 | 3095.75 | 5771.2 | 13488.05 | -66.075 | 1350000 | 13488.05 | 0
2021111813 | 5 | 0.5765 | 86475 | 0.75798 | 0 | 0.23589 | 2948.625 | 0.06687 | 5349.6 | 64000 | 2948.625 | 5349.6 | 14176.775 | 688.725 | 1350000 | 14176.775 | 0
2021111814 | 5 | 0.57854 | 86781 | 0.74644 | 0 | 0.27211 | 3401.375 | 0.05127 | 4101.6 | 64000 | 3401.375 | 4101.6 | 15278.025 | 1101.25 | 1350000 | 15278.025 | 0
2021111815 | 5 | 0.57922 | 86883 | 0.82845 | 0 | 0.30094 | 3761.75 | 0.03541 | 2832.8 | 64000 | 3761.75 | 2832.8 | 16288.45 | 1010.425 | 1350000 | 16288.45 | 0
2021111816 | 5 | 0.58364 | 87546 | 0.81392 | 0 | 0.32986 | 4123.25 | 0.02023 | 1618.4 | 64000 | 4123.25 | 1618.4 | 17804.35 | 1515.9 | 1350000 | 17804.35 | 0
2021111817 | 5 | 0.59892 | 89838 | 0.89959 | 0 | 0.33954 | 4244.25 | 0.00246 | 196.8 | 64000 | 4244.25 | 196.8 | 21396.95 | 3592.6 | 1350000 | 21396.95 | 0
2021111818 | 5 | 0.62525 | 93787.5 | 0.90885 | 0 | 0.35837 | 4479.625 | 0 | 0 | 64000 | 4479.625 | 0 | 25307.875 | 3910.925 | 1350000 | 25307.875 | 0
2021111819 | 5 | 0.62697 | 94045.5 | 0.9275 | 0 | 0.40648 | 5081 | 0 | 0 | 64000 | 5081 | 0 | 24964.5 | -343.375 | 1350000 | 24964.5 | 0
2021111820 | 5 | 0.61804 | 92706 | 0.93626 | 0 | 0.39484 | 4935.5 | 0 | 0 | 64000 | 4935.5 | 0 | 23770.5 | -1194 | 1350000 | 23770.5 | 0
2021111821 | 5 | 0.60659 | 90988.5 | 0.93227 | 0 | 0.33642 | 4205.25 | 0 | 0 | 64000 | 4205.25 | 0 | 22783.25 | -987.25 | 1350000 | 22783.25 | 0
2021111822 | 5 | 0.58575 | 87862.5 | 0.9517 | 0 | 0.31139 | 3892.375 | 0 | 0 | 64000 | 3892.375 | 0 | 19970.125 | -2813.125 | 1350000 | 19970.125 | 0
2021111823 | 5 | 0.55651 | 83476.5 | 0.955 | 0 | 0.28203 | 3525.375 | 0 | 0 | 64000 | 3525.375 | 0 | 15951.125 | -4019 | 1350000 | 15951.125 | 0
2021111824 | 5 | 0.53197 | 79795.5 | 0.95752 | 0 | 0.26402 | 3300.25 | 0 | 0 | 64000 | 3300.25 | 0 | 12495.25 | -3455.875 | 1350000 | 12495.25 | 0
2021111901 | 6 | 0.51335 | 77002.5 | 0.94617 | 0 | 0.246 | 3075 | 0 | 0 | 64000 | 3075 | 0 | 9927.5 | -2567.75 | 1350000 | 9927.5 | 0
2021111902 | 6 | 0.50432 | 75648 | 0.93763 | 0 | 0.23715 | 2964.375 | 0 | 0 | 64000 | 2964.375 | 0 | 8683.625 | -1243.875 | 1350000 | 8683.625 | 0
2021111903 | 6 | 0.50178 | 75267 | 0.91269 | 0 | 0.21898 | 2737.25 | 0 | 0 | 64000 | 2737.25 | 0 | 8529.75 | -153.875 | 1350000 | 8529.75 | 0
2021111904 | 6 | 0.50551 | 75826.5 | 0.93995 | 0 | 0.21237 | 2654.625 | 0 | 0 | 64000 | 2654.625 | 0 | 9171.875 | 642.125 | 1350000 | 9171.875 | 0
2021111905 | 6 | 0.5197 | 77955 | 0.91975 | 0 | 0.2203 | 2753.75 | 0 | 0 | 64000 | 2753.75 | 0 | 11201.25 | 2029.375 | 1350000 | 11201.25 | 0
2021111906 | 6 | 0.55376 | 83064 | 0.92769 | 0 | 0.26881 | 3360.125 | 0 | 0 | 64000 | 3360.125 | 0 | 15703.875 | 4502.625 | 1350000 | 15703.875 | 0
2021111907 | 6 | 0.60605 | 90907.5 | 0.95439 | 0 | 0.31379 | 3922.375 | 0.00224 | 179.2 | 64000 | 3922.375 | 179.2 | 22805.925 | 7102.05 | 1350000 | 22805.925 | 0
2021111908 | 6 | 0.6394 | 95910 | 0.93771 | 0 | 0.30268 | 3783.5 | 0.0182 | 1456 | 64000 | 3783.5 | 1456 | 26670.5 | 3864.575 | 1348795.75 | 26670.5 | 0
2021111909 | 6 | 0.63972 | 95958 | 0.93746 | 0 | 0.29759 | 3719.875 | 0.03956 | 3164.8 | 64000 | 3719.875 | 3164.8 | 25073.325 | -1597.175 | 1349188.675 | 25073.325 | 0
2021111910 | 6 | 0.6291 | 94365 | 0.94576 | 0 | 0.27807 | 3475.875 | 0.06269 | 5015.2 | 64000 | 3475.875 | 5015.2 | 21873.925 | -3199.4 | 1350000 | 21873.925 | 0
2021111911 | 6 | 0.61812 | 92718 | 0.94291 | 0 | 0.28951 | 3618.875 | 0.08125 | 6500 | 64000 | 3618.875 | 6500 | 18599.125 | -3274.8 | 1350000 | 18599.125 | 0
2021111912 | 6 | 0.60911 | 91366.5 | 0.90885 | 0 | 0.24457 | 3057.125 | 0.0892 | 7136 | 64000 | 3057.125 | 7136 | 17173.375 | -1425.75 | 1350000 | 17173.375 | 0
2021111913 | 6 | 0.60223 | 90334.5 | 0.90113 | 0 | 0.22134 | 2766.75 | 0.08326 | 6660.8 | 64000 | 2766.75 | 6660.8 | 16906.95 | -266.425 | 1350000 | 16906.95 | 0
2021111914 | 6 | 0.59616 | 89424 | 0.86967 | 0 | 0.27165 | 3395.625 | 0.0694 | 5552 | 64000 | 3395.625 | 5552 | 16476.375 | -430.575 | 1350000 | 16476.375 | 0
2021111915 | 6 | 0.59425 | 89137.5 | 0.83843 | 0 | 0.26047 | 3255.875 | 0.05067 | 4053.6 | 64000 | 3255.875 | 4053.6 | 17828.025 | 1351.65 | 1350000 | 17828.025 | 0
2021111916 | 6 | 0.59942 | 89913 | 0.73011 | 0 | 0.30077 | 3759.625 | 0.02235 | 1788 | 64000 | 3759.625 | 1788 | 20365.375 | 2537.35 | 1350000 | 20365.375 | 0
2021111917 | 6 | 0.62045 | 93067.5 | 0.61543 | 0 | 0.33379 | 4172.375 | 0.00113 | 90.4 | 64000 | 4172.375 | 90.4 | 24804.725 | 4439.35 | 1350000 | 24804.725 | 0
2021111918 | 6 | 0.65259 | 97888.5 | 0.55657 | 0 | 0.32566 | 4070.75 | 0 | 0 | 64000 | 4070.75 | 0 | 29817.75 | 5013.025 | 1345648.5 | 29817.75 | 0
2021111919 | 6 | 0.65593 | 98389.5 | 0.48856 | 0 | 0.31073 | 3884.125 | 0 | 0 | 64000 | 3884.125 | 0 | 30505.375 | 687.625 | 1340609.375 | 30505.375 | 0
2021111920 | 6 | 0.65047 | 97570.5 | 0.45642 | 0 | 0.38806 | 4850.75 | 0 | 0 | 64000 | 4850.75 | 0 | 28719.75 | -1785.625 | 1337355.875 | 28719.75 | 0
2021111921 | 6 | 0.64181 | 96271.5 | 0.35836 | 0 | 0.42808 | 5351 | 0 | 0 | 64000 | 5351 | 0 | 26920.5 | -1799.25 | 1335901.625 | 26920.5 | 0
2021111922 | 6 | 0.62669 | 94003.5 | 0.28143 | 0 | 0.39825 | 4978.125 | 0 | 0 | 64000 | 4978.125 | 0 | 25025.375 | -1895.125 | 1336342.5 | 25025.375 | 0
2021111923 | 6 | 0.60405 | 90607.5 | 0.31038 | 0 | 0.33128 | 4141 | 0 | 0 | 64000 | 4141 | 0 | 22466.5 | -2558.875 | 1339342.25 | 22466.5 | 0
2021111924 | 6 | 0.58147 | 87220.5 | 0.20673 | 0 | 0.30911 | 3863.875 | 0 | 0 | 64000 | 3863.875 | 0 | 19356.625 | -3109.875 | 1345451.875 | 19356.625 | 0
2021112001 | 7 | 0.56393 | 84589.5 | 0.18248 | 0 | 0.3132 | 3915 | 0 | 0 | 64000 | 3915 | 0 | 16674.5 | -2682.125 | 1350000 | 16674.5 | 0
2021112002 | 7 | 0.55527 | 83290.5 | 0.28699 | 0 | 0.27985 | 3498.125 | 0 | 0 | 64000 | 3498.125 | 0 | 15792.375 | -882.125 | 1350000 | 15792.375 | 0
2021112003 | 7 | 0.55191 | 82786.5 | 0.34053 | 0 | 0.25565 | 3195.625 | 0 | 0 | 64000 | 3195.625 | 0 | 15590.875 | -201.5 | 1350000 | 15590.875 | 0
2021112004 | 7 | 0.554 | 83100 | 0.25568 | 0 | 0.28217 | 3527.125 | 0 | 0 | 64000 | 3527.125 | 0 | 15572.875 | -18 | 1350000 | 15572.875 | 0
2021112005 | 7 | 0.56126 | 84189 | 0.37192 | 0 | 0.27454 | 3431.75 | 0 | 0 | 64000 | 3431.75 | 0 | 16757.25 | 1184.375 | 1350000 | 16757.25 | 0
2021112006 | 7 | 0.57751 | 86626.5 | 0.50872 | 0 | 0.25338 | 3167.25 | 0 | 0 | 64000 | 3167.25 | 0 | 19459.25 | 2702 | 1350000 | 19459.25 | 0
2021112007 | 7 | 0.60191 | 90286.5 | 0.59945 | 0 | 0.27847 | 3480.875 | 0.0023 | 184 | 64000 | 3480.875 | 184 | 22621.625 | 3162.375 | 1350000 | 22621.625 | 0
2021112008 | 7 | 0.62079 | 93118.5 | 0.65628 | 0 | 0.23808 | 2976 | 0.01837 | 1469.6 | 64000 | 2976 | 1469.6 | 24672.9 | 2051.275 | 1350000 | 24672.9 | 0
2021112009 | 7 | 0.62112 | 93168 | 0.71437 | 0 | 0.19269 | 2408.625 | 0.03476 | 2780.8 | 64000 | 2408.625 | 2780.8 | 23978.575 | -694.325 | 1350000 | 23978.575 | 0
2021112010 | 7 | 0.60919 | 91378.5 | 0.73503 | 0 | 0.1503 | 1878.75 | 0.05638 | 4510.4 | 64000 | 1878.75 | 4510.4 | 20989.35 | -2989.225 | 1350000 | 20989.35 | 0
2021112011 | 7 | 0.59426 | 89139 | 0.80343 | 0 | 0.14821 | 1852.625 | 0.08253 | 6602.4 | 64000 | 1852.625 | 6602.4 | 16683.975 | -4305.375 | 1350000 | 16683.975 | 0
2021112012 | 7 | 0.57855 | 86782.5 | 0.77927 | 0 | 0.16444 | 2055.5 | 0.09313 | 7450.4 | 64000 | 2055.5 | 7450.4 | 13276.6 | -3407.375 | 1350000 | 13276.6 | 0
2021112013 | 7 | 0.56621 | 84931.5 | 0.66068 | 0 | 0.2057 | 2571.25 | 0.09224 | 7379.2 | 64000 | 2571.25 | 7379.2 | 10981.05 | -2295.55 | 1350000 | 10981.05 | 0
2021112014 | 7 | 0.55624 | 83436 | 0.64438 | 0 | 0.23516 | 2939.5 | 0.08211 | 6568.8 | 64000 | 2939.5 | 6568.8 | 9927.7 | -1053.35 | 1350000 | 9927.7 | 0
2021112015 | 7 | 0.55025 | 82537.5 | 0.64662 | 0 | 0.28294 | 3536.75 | 0.05281 | 4224.8 | 64000 | 3536.75 | 4224.8 | 10775.95 | 848.25 | 1350000 | 10775.95 | 0
2021112016 | 7 | 0.55543 | 83314.5 | 0.75558 | 0 | 0.31315 | 3914.375 | 0.03278 | 2622.4 | 64000 | 3914.375 | 2622.4 | 12777.725 | 2001.775 | 1350000 | 12777.725 | 0
2021112017 | 7 | 0.57425 | 86137.5 | 0.76577 | 0 | 0.32036 | 4004.5 | 0.00541 | 432.8 | 64000 | 4004.5 | 432.8 | 17700.2 | 4922.475 | 1350000 | 17700.2 | 0
2021112018 | 7 | 0.60354 | 90531 | 0.74537 | 0 | 0.34235 | 4279.375 | 0 | 0 | 64000 | 4279.375 | 0 | 22251.625 | 4551.425 | 1350000 | 22251.625 | 0
2021112019 | 7 | 0.60713 | 91069.5 | 0.76794 | 0 | 0.31996 | 3999.5 | 0 | 0 | 64000 | 3999.5 | 0 | 23070 | 818.375 | 1350000 | 23070 | 0
2021112020 | 7 | 0.60187 | 90280.5 | 0.78719 | 0 | 0.30878 | 3859.75 | 0 | 0 | 64000 | 3859.75 | 0 | 22420.75 | -649.25 | 1350000 | 22420.75 | 0
2021112021 | 7 | 0.59526 | 89289 | 0.79098 | 0 | 0.30299 | 3787.375 | 0 | 0 | 64000 | 3787.375 | 0 | 21501.625 | -919.125 | 1350000 | 21501.625 | 0
2021112022 | 7 | 0.58279 | 87418.5 | 0.83868 | 0 | 0.29794 | 3724.25 | 0 | 0 | 64000 | 3724.25 | 0 | 19694.25 | -1807.375 | 1350000 | 19694.25 | 0
2021112023 | 7 | 0.56454 | 84681 | 0.7725 | 0 | 0.30528 | 3816 | 0 | 0 | 64000 | 3816 | 0 | 16865 | -2829.25 | 1350000 | 16865 | 0
2021112024 | 7 | 0.54427 | 81640.5 | 0.66116 | 0 | 0.25271 | 3158.875 | 0 | 0 | 64000 | 3158.875 | 0 | 14481.625 | -2383.375 | 1350000 | 14481.625 | 0
2021112101 | 1 | 0.52724 | 79086 | 0.58434 | 0 | 0.20977 | 2622.125 | 0 | 0 | 64000 | 2622.125 | 0 | 12463.875 | -2017.75 | 1350000 | 12463.875 | 0
2021112102 | 1 | 0.51799 | 77698.5 | 0.52166 | 0 | 0.2365 | 2956.25 | 0 | 0 | 64000 | 2956.25 | 0 | 10742.25 | -1721.625 | 1350000 | 10742.25 | 0
2021112103 | 1 | 0.51272 | 76908 | 0.43526 | 0 | 0.24395 | 3049.375 | 0 | 0 | 64000 | 3049.375 | 0 | 9858.625 | -883.625 | 1350000 | 9858.625 | 0
2021112104 | 1 | 0.51078 | 76617 | 0.40408 | 0 | 0.25418 | 3177.25 | 0 | 0 | 64000 | 3177.25 | 0 | 9439.75 | -418.875 | 1350000 | 9439.75 | 0
2021112105 | 1 | 0.51362 | 77043 | 0.36695 | 0 | 0.26541 | 3317.625 | 0 | 0 | 64000 | 3317.625 | 0 | 9725.375 | 285.625 | 1350000 | 9725.375 | 0
2021112106 | 1 | 0.52247 | 78370.5 | 0.3551 | 0 | 0.22358 | 2794.75 | 0 | 0 | 64000 | 2794.75 | 0 | 11575.75 | 1850.375 | 1350000 | 11575.75 | 0
2021112107 | 1 | 0.53946 | 80919 | 0.34474 | 0 | 0.20403 | 2550.375 | 0.00694 | 555.2 | 64000 | 2550.375 | 555.2 | 13813.425 | 2237.675 | 1350000 | 13813.425 | 0
2021112108 | 1 | 0.55518 | 83277 | 0.29457 | 0 | 0.2143 | 2678.75 | 0.03861 | 3088.8 | 64000 | 2678.75 | 3088.8 | 13509.45 | -303.975 | 1350000 | 13509.45 | 0
2021112109 | 1 | 0.5632 | 84480 | 0.24464 | 0 | 0.19949 | 2493.625 | 0.08929 | 7143.2 | 64000 | 2493.625 | 7143.2 | 10843.175 | -2666.275 | 1350000 | 10843.175 | 0
2021112110 | 1 | 0.5617 | 84255 | 0.19735 | 0 | 0.15972 | 1996.5 | 0.17358 | 13886.4 | 64000 | 1996.5 | 13886.4 | 4372.1 | -6471.075 | 1350000 | 4372.1 | 0
2021112111 | 1 | 0.5543 | 83145 | 0.18892 | 0 | 0.13496 | 1687 | 0.24525 | 19620 | 64000 | 1687 | 17458 | 0 | -4372.1 | 1350000 | 0 | 0
2021112112 | 1 | 0.54994 | 82491 | 0.23099 | 0 | 0.11926 | 1490.75 | 0.28137 | 22509.6 | 64000 | 1490.75 | 17000.25 | 0 | 0 | 1350000 | 0 | 0
2021112113 | 1 | 0.54969 | 82453.5 | 0.36321 | 0 | 0.0909 | 1136.25 | 0.287 | 22960 | 64000 | 1136.25 | 17317.25 | 0 | 0 | 1350000 | 0 | 0
2021112114 | 1 | 0.54906 | 82359 | 0.46681 | 0 | 0.08873 | 1109.125 | 0.23087 | 18469.6 | 64000 | 1109.125 | 17249.875 | 0 | 0 | 1350000 | 0 | 0
2021112115 | 1 | 0.55109 | 82663.5 | 0.55885 | 0 | 0.08836 | 1104.5 | 0.16602 | 13281.6 | 64000 | 1104.5 | 13281.6 | 4277.4 | 4277.4 | 1350000 | 4277.4 | 0
2021112116 | 1 | 0.55759 | 83638.5 | 0.57644 | 0 | 0.08964 | 1120.5 | 0.08356 | 6684.8 | 64000 | 1120.5 | 6684.8 | 11833.2 | 7555.8 | 1350000 | 11833.2 | 0
2021112117 | 1 | 0.57364 | 86046 | 0.57799 | 0 | 0.10347 | 1293.375 | 0.01829 | 1463.2 | 64000 | 1293.375 | 1463.2 | 19289.425 | 7456.225 | 1350000 | 19289.425 | 0
2021112118 | 1 | 0.59937 | 89905.5 | 0.79069 | 0 | 0.15018 | 1877.25 | 0 | 0 | 64000 | 1877.25 | 0 | 24028.25 | 4738.825 | 1350000 | 24028.25 | 0
2021112119 | 1 | 0.60193 | 90289.5 | 0.78662 | 0 | 0.16941 | 2117.625 | 0 | 0 | 64000 | 2117.625 | 0 | 24171.875 | 143.625 | 1350000 | 24171.875 | 0
2021112120 | 1 | 0.59454 | 89181 | 0.82367 | 0 | 0.14904 | 1863 | 0 | 0 | 64000 | 1863 | 0 | 23318 | -853.875 | 1350000 | 23318 | 0
2021112121 | 1 | 0.58287 | 87430.5 | 0.84349 | 0 | 0.14316 | 1789.5 | 0 | 0 | 64000 | 1789.5 | 0 | 21641 | -1677 | 1350000 | 21641 | 0
2021112122 | 1 | 0.56362 | 84543 | 0.84587 | 0 | 0.13894 | 1736.75 | 0 | 0 | 64000 | 1736.75 | 0 | 18806.25 | -2834.75 | 1350000 | 18806.25 | 0
2021112123 | 1 | 0.53831 | 80746.5 | 0.8377 | 0 | 0.10075 | 1259.375 | 0 | 0 | 64000 | 1259.375 | 0 | 15487.125 | -3319.125 | 1350000 | 15487.125 | 0
2021112124 | 1 | 0.51364 | 77046 | 0.8591 | 0 | 0.08908 | 1113.5 | 0 | 0 | 64000 | 1113.5 | 0 | 11932.5 | -3554.625 | 1350000 | 11932.5 | 0
2021112201 | 2 | 0.49775 | 74662.5 | 0.85687 | 0 | 0.10133 | 1266.625 | 0 | 0 | 64000 | 1266.625 | 0 | 9395.875 | -2536.625 | 1350000 | 9395.875 | 0
2021112202 | 2 | 0.48714 | 73071 | 0.80957 | 0 | 0.12293 | 1536.625 | 0 | 0 | 64000 | 1536.625 | 0 | 7534.375 | -1861.5 | 1350000 | 7534.375 | 0
2021112203 | 2 | 0.48459 | 72688.5 | 0.70392 | 0 | 0.1252 | 1565 | 0 | 0 | 64000 | 1565 | 0 | 7123.5 | -410.875 | 1350000 | 7123.5 | 0
2021112204 | 2 | 0.48682 | 73023 | 0.66983 | 0 | 0.14131 | 1766.375 | 0 | 0 | 64000 | 1766.375 | 0 | 7256.625 | 133.125 | 1350000 | 7256.625 | 0
2021112205 | 2 | 0.50225 | 75337.5 | 0.69171 | 0 | 0.1094 | 1367.5 | 0 | 0 | 64000 | 1367.5 | 0 | 9970 | 2713.375 | 1350000 | 9970 | 0
2021112206 | 2 | 0.53345 | 80017.5 | 0.69765 | 0 | 0.07944 | 993 | 0 | 0 | 64000 | 993 | 0 | 15024.5 | 5054.5 | 1350000 | 15024.5 | 0
2021112207 | 2 | 0.58284 | 87426 | 0.71655 | 0 | 0.07088 | 886 | 0.01968 | 1574.4 | 64000 | 886 | 1574.4 | 20965.6 | 5941.1 | 1350000 | 20965.6 | 0
2021112208 | 2 | 0.61722 | 92583 | 0.73881 | 0 | 0.06805 | 850.625 | 0.15785 | 12628 | 64000 | 850.625 | 12628 | 15104.375 | -5861.225 | 1350000 | 15104.375 | 0
2021112209 | 2 | 0.62702 | 94053 | 0.755 | 0 | 0.07907 | 988.375 | 0.27937 | 22349.6 | 64000 | 988.375 | 22349.6 | 6715.025 | -8389.35 | 1350000 | 6715.025 | 0
2021112210 | 2 | 0.62859 | 94288.5 | 0.77498 | 0 | 0.10073 | 1259.125 | 0.27504 | 22003.2 | 64000 | 1259.125 | 22003.2 | 7026.175 | 311.15 | 1350000 | 7026.175 | 0
2021112211 | 2 | 0.62775 | 94162.5 | 0.78122 | 0 | 0.08787 | 1098.375 | 0.2501 | 20008 | 64000 | 1098.375 | 20008 | 9056.125 | 2029.95 | 1350000 | 9056.125 | 0
2021112212 | 2 | 0.62266 | 93399 | 0.79924 | 0 | 0.09202 | 1150.25 | 0.26012 | 20809.6 | 64000 | 1150.25 | 20809.6 | 7439.15 | -1616.975 | 1350000 | 7439.15 | 0
2021112213 | 2 | 0.61746 | 92619 | 0.82436 | 0 | 0.11628 | 1453.5 | 0.25809 | 20647.2 | 64000 | 1453.5 | 20647.2 | 6518.3 | -920.85 | 1350000 | 6518.3 | 0
2021112214 | 2 | 0.61165 | 91747.5 | 0.85081 | 0 | 0.13796 | 1724.5 | 0.19267 | 15413.6 | 64000 | 1724.5 | 15413.6 | 10609.4 | 4091.1 | 1350000 | 10609.4 | 0
2021112215 | 2 | 0.6075 | 91125 | 0.81183 | 0 | 0.16973 | 2121.625 | 0.13621 | 10896.8 | 64000 | 2121.625 | 10896.8 | 14106.575 | 3497.175 | 1350000 | 14106.575 | 0
2021112216 | 2 | 0.60926 | 91389 | 0.75886 | 0 | 0.19906 | 2488.25 | 0.0538 | 4304 | 64000 | 2488.25 | 4304 | 20596.75 | 6490.175 | 1350000 | 20596.75 | 0
2021112217 | 2 | 0.63006 | 94509 | 0.70991 | 0 | 0.19824 | 2478 | 0.00575 | 460 | 64000 | 2478 | 460 | 27571 | 6974.25 | 1347895.25 | 27571 | 0
2021112218 | 2 | 0.66588 | 99882 | 0.65526 | 0 | 0.18897 | 2362.125 | 0 | 0 | 64000 | 2362.125 | 0 | 33519.875 | 5948.875 | 1339841.625 | 33519.875 | 0
2021112219 | 2 | 0.67579 | 101368.5 | 0.60661 | 0 | 0.16633 | 2079.125 | 0 | 0 | 64000 | 2079.125 | 0 | 35289.375 | 1769.5 | 1330018.5 | 35289.375 | 0
2021112220 | 2 | 0.67183 | 100774.5 | 0.6471 | 0 | 0.15144 | 1893 | 0 | 0 | 64000 | 1893 | 0 | 34881.5 | -407.875 | 1320603.25 | 34881.5 | 0
2021112221 | 2 | 0.66213 | 99319.5 | 0.68847 | 0 | 0.14519 | 1814.875 | 0 | 0 | 64000 | 1814.875 | 0 | 33504.625 | -1376.875 | 1312564.875 | 33504.625 | 0
2021112222 | 2 | 0.64367 | 96550.5 | 0.65057 | 0 | 0.12311 | 1538.875 | 0 | 0 | 64000 | 1538.875 | 0 | 31011.625 | -2493 | 1307019.5 | 31011.625 | 0
2021112223 | 2 | 0.61677 | 92515.5 | 0.60841 | 0 | 0.1087 | 1358.75 | 0 | 0 | 64000 | 1358.75 | 0 | 27156.75 | -3854.875 | 1305329 | 27156.75 | 0
2021112224 | 2 | 0.59201 | 88801.5 | 0.65959 | 0 | 0.11558 | 1444.75 | 0 | 0 | 64000 | 1444.75 | 0 | 23356.75 | -3800 | 1307438.5 | 23356.75 | 0
2021112301 | 3 | 0.57601 | 86401.5 | 0.71587 | 0 | 0.11056 | 1382 | 0 | 0 | 64000 | 1382 | 0 | 21019.5 | -2337.25 | 1311885.25 | 21019.5 | 0
2021112302 | 3 | 0.56792 | 85188 | 0.69603 | 0 | 0.10474 | 1309.25 | 0 | 0 | 64000 | 1309.25 | 0 | 19878.75 | -1140.75 | 1317472.75 | 19878.75 | 0
2021112303 | 3 | 0.56833 | 85249.5 | 0.65384 | 0 | 0.10596 | 1324.5 | 0 | 0 | 64000 | 1324.5 | 0 | 19925 | 46.25 | 1323014 | 19925 | 0
2021112304 | 3 | 0.57339 | 86008.5 | 0.61915 | 0 | 0.09322 | 1165.25 | 0 | 0 | 64000 | 1165.25 | 0 | 20843.25 | 918.25 | 1327637 | 20843.25 | 0
2021112305 | 3 | 0.58842 | 88263 | 0.62017 | 0 | 0.06508 | 813.5 | 0 | 0 | 64000 | 813.5 | 0 | 23449.5 | 2606.25 | 1329653.75 | 23449.5 | 0
2021112306 | 3 | 0.62344 | 93516 | 0.71749 | 0 | 0.05617 | 702.125 | 0 | 0 | 64000 | 702.125 | 0 | 28813.875 | 5364.375 | 1326306.125 | 28813.875 | 0
2021112307 | 3 | 0.67289 | 100933.5 | 0.68014 | 0 | 0.03678 | 459.75 | 0.01557 | 1245.6 | 64000 | 459.75 | 1245.6 | 35228.15 | 6414.275 | 1316544.225 | 35228.15 | 0
2021112308 | 3 | 0.70315 | 105472.5 | 0.65627 | 0 | 0.02255 | 281.875 | 0.18635 | 14908 | 64000 | 281.875 | 14908 | 26282.625 | -8945.525 | 1315727.85 | 26282.625 | 0
2021112309 | 3 | 0.69215 | 103822.5 | 0.63179 | 0 | 0.01214 | 151.75 | 0.37478 | 29982.4 | 64000 | 151.75 | 29982.4 | 9688.35 | -16594.275 | 1331505.75 | 9688.35 | 0
2021112310 | 3 | 0.66992 | 100488 | 0.65572 | 0 | 0.00826 | 103.25 | 0.42561 | 34048.8 | 64000 | 103.25 | 34048.8 | 2335.95 | -7352.4 | 1350000 | 2335.95 | 0
2021112311 | 3 | 0.65335 | 98002.5 | 0.66672 | 0 | 0.00662 | 82.75 | 0.41471 | 33176.8 | 64000 | 82.75 | 33176.8 | 742.95 | -1593 | 1350000 | 742.95 | 0
2021112312 | 3 | 0.64092 | 96138 | 0.70341 | 0 | 0.00728 | 91 | 0.39995 | 31996 | 64000 | 91 | 31996 | 51 | -691.95 | 1350000 | 51 | 0
2021112313 | 3 | 0.63146 | 94719 | 0.70357 | 0 | 0.01044 | 130.5 | 0.39932 | 31945.6 | 64000 | 130.5 | 30588.5 | 0 | -51 | 1350000 | 0 | 0
2021112314 | 3 | 0.62586 | 93879 | 0.72644 | 0 | 0.02145 | 268.125 | 0.39623 | 31698.4 | 64000 | 268.125 | 29610.875 | 0 | 0 | 1350000 | 0 | 0
2021112315 | 3 | 0.6239 | 93585 | 0.76048 | 0 | 0.02916 | 364.5 | 0.37666 | 30132.8 | 64000 | 364.5 | 29220.5 | 0 | 0 | 1350000 | 0 | 0
2021112316 | 3 | 0.62908 | 94362 | 0.75171 | 0 | 0.04598 | 574.75 | 0.2316 | 18528 | 64000 | 574.75 | 18528 | 11259.25 | 11259.25 | 1350000 | 11259.25 | 0
2021112317 | 3 | 0.65134 | 97701 | 0.69495 | 0 | 0.04684 | 585.5 | 0.03508 | 2806.4 | 64000 | 585.5 | 2806.4 | 30309.1 | 19049.85 | 1345157.15 | 30309.1 | 0
2021112318 | 3 | 0.69021 | 103531.5 | 0.60114 | 0 | 0.04421 | 552.625 | 0 | 0 | 64000 | 552.625 | 0 | 38978.875 | 8669.775 | 1331644.525 | 38978.875 | 0
2021112319 | 3 | 0.699 | 104850 | 0.51753 | 0 | 0.05927 | 740.875 | 0 | 0 | 64000 | 740.875 | 0 | 40109.125 | 1130.25 | 1317001.65 | 40109.125 | 0
2021112320 | 3 | 0.69476 | 104214 | 0.53537 | 0 | 0.05845 | 730.625 | 0 | 0 | 64000 | 730.625 | 0 | 39483.375 | -625.75 | 1302984.525 | 39483.375 | 0
2021112321 | 3 | 0.68632 | 102948 | 0.54314 | 0 | 0.05221 | 652.625 | 0 | 0 | 64000 | 652.625 | 0 | 38295.375 | -1188 | 1290155.4 | 38295.375 | 0
2021112322 | 3 | 0.66863 | 100294.5 | 0.56622 | 0 | 0.07336 | 917 | 0 | 0 | 64000 | 917 | 0 | 35377.5 | -2917.875 | 1280244.15 | 35377.5 | 0
2021112323 | 3 | 0.64244 | 96366 | 0.58854 | 0 | 0.08476 | 1059.5 | 0 | 0 | 64000 | 1059.5 | 0 | 31306.5 | -4071 | 1274403.9 | 31306.5 | 0
2021112324 | 3 | 0.61661 | 92491.5 | 0.57611 | 0 | 0.10216 | 1277 | 0 | 0 | 64000 | 1277 | 0 | 27214.5 | -4092 | 1272655.65 | 27214.5 | 0
2021112401 | 4 | 0.59783 | 89674.5 | 0.54496 | 0 | 0.13006 | 1625.75 | 0 | 0 | 64000 | 1625.75 | 0 | 24048.75 | -3165.75 | 1274073.15 | 24048.75 | 0
2021112402 | 4 | 0.58861 | 88291.5 | 0.52571 | 0 | 0.12911 | 1613.875 | 0 | 0 | 64000 | 1613.875 | 0 | 22677.625 | -1371.125 | 1276861.775 | 22677.625 | 0
2021112403 | 4 | 0.58598 | 87897 | 0.5756 | 0 | 0.15129 | 1891.125 | 0 | 0 | 64000 | 1891.125 | 0 | 22005.875 | -671.75 | 1280322.15 | 22005.875 | 0
2021112404 | 4 | 0.58946 | 88419 | 0.64095 | 0 | 0.16449 | 2056.125 | 0 | 0 | 64000 | 2056.125 | 0 | 22362.875 | 357 | 1283425.525 | 22362.875 | 0
2021112405 | 4 | 0.60238 | 90357 | 0.64909 | 0 | 0.17439 | 2179.875 | 0 | 0 | 64000 | 2179.875 | 0 | 24177.125 | 1814.25 | 1284714.65 | 24177.125 | 0
2021112406 | 4 | 0.63182 | 94773 | 0.62816 | 0 | 0.19389 | 2423.625 | 0 | 0 | 64000 | 2423.625 | 0 | 28349.375 | 4172.25 | 1281831.525 | 28349.375 | 0
2021112407 | 4 | 0.67466 | 101199 | 0.63456 | 0 | 0.19461 | 2432.625 | 0.0124 | 992 | 64000 | 2432.625 | 992 | 33774.375 | 5425 | 1273523.4 | 33774.375 | 0
2021112408 | 4 | 0.70203 | 105304.5 | 0.57535 | 0 | 0.19154 | 2394.25 | 0.13228 | 10582.4 | 64000 | 2394.25 | 10582.4 | 28327.85 | -5446.525 | 1270661.8 | 28327.85 | 0
2021112409 | 4 | 0.69434 | 104151 | 0.43659 | 0 | 0.16892 | 2111.5 | 0.19281 | 15424.8 | 64000 | 2111.5 | 15424.8 | 22614.7 | -5713.15 | 1273513.35 | 22614.7 | 0
2021112410 | 4 | 0.67026 | 100539 | 0.23208 | 0 | 0.16723 | 2090.375 | 0.16676 | 13340.8 | 64000 | 2090.375 | 13340.8 | 21107.825 | -1506.875 | 1277871.775 | 21107.825 | 0
2021112411 | 4 | 0.6489 | 97335 | 0.06523 | 0 | 0.1348 | 1685 | 0.16453 | 13162.4 | 64000 | 1685 | 13162.4 | 18487.6 | -2620.225 | 1284850.425 | 18487.6 | 0
2021112412 | 4 | 0.6311 | 94665 | 0.04155 | 0 | 0.13344 | 1668 | 0.14832 | 11865.6 | 64000 | 1668 | 11865.6 | 17131.4 | -1356.2 | 1293185.275 | 17131.4 | 0
2021112413 | 4 | 0.61496 | 92244 | 0.01554 | 0 | 0.16178 | 2022.25 | 0.1058 | 8464 | 64000 | 2022.25 | 8464 | 17757.75 | 626.35 | 1300893.775 | 17757.75 | 0
2021112414 | 4 | 0.60446 | 90669 | 0.01453 | 0 | 0.17161 | 2145.125 | 0.06554 | 5243.2 | 64000 | 2145.125 | 5243.2 | 19280.675 | 1522.925 | 1307079.35 | 19280.675 | 0
2021112415 | 4 | 0.59867 | 89800.5 | 0.0102 | 0 | 0.20717 | 2589.625 | 0.03537 | 2829.6 | 64000 | 2589.625 | 2829.6 | 20381.275 | 1100.6 | 1312164.325 | 20381.275 | 0
2021112416 | 4 | 0.59933 | 89899.5 | 0.03561 | 0 | 0.24995 | 3124.375 | 0.01568 | 1254.4 | 64000 | 3124.375 | 1254.4 | 21520.725 | 1139.45 | 1316109.85 | 21520.725 | 0
2021112417 | 4 | 0.61727 | 92590.5 | 0.0954 | 0 | 0.31374 | 3921.75 | 0.00182 | 145.6 | 64000 | 3921.75 | 145.6 | 24523.15 | 3002.425 | 1317052.95 | 24523.15 | 0
2021112418 | 4 | 0.65015 | 97522.5 | 0.2121 | 0 | 0.37925 | 4740.625 | 0 | 0 | 64000 | 4740.625 | 0 | 28781.875 | 4258.725 | 1313737.325 | 28781.875 | 0
2021112419 | 4 | 0.65217 | 97825.5 | 0.36386 | 0 | 0.39437 | 4929.625 | 0 | 0 | 64000 | 4929.625 | 0 | 28895.875 | 114 | 1310307.7 | 28895.875 | 0
2021112420 | 4 | 0.64494 | 96741 | 0.48267 | 0 | 0.42456 | 5307 | 0 | 0 | 64000 | 5307 | 0 | 27434 | -1461.875 | 1308339.95 | 27434 | 0
2021112421 | 4 | 0.63417 | 95125.5 | 0.53605 | 0 | 0.45716 | 5714.5 | 0 | 0 | 64000 | 5714.5 | 0 | 25411 | -2023 | 1308395.2 | 25411 | 0
2021112422 | 4 | 0.61764 | 92646 | 0.59348 | 0 | 0.46601 | 5825.125 | 0 | 0 | 64000 | 5825.125 | 0 | 22820.875 | -2590.125 | 1311040.575 | 22820.875 | 0
2021112423 | 4 | 0.59128 | 88692 | 0.6002 | 0 | 0.45491 | 5686.375 | 0 | 0 | 64000 | 5686.375 | 0 | 19005.625 | -3815.25 | 1317501.2 | 19005.625 | 0
2021112424 | 4 | 0.56273 | 84409.5 | 0.66031 | 0 | 0.44427 | 5553.375 | 0 | 0 | 64000 | 5553.375 | 0 | 14856.125 | -4149.5 | 1328111.325 | 14856.125 | 0
2021112501 | 5 | 0.54006 | 81009 | 0.71482 | 0 | 0.41766 | 5220.75 | 0 | 0 | 64000 | 5220.75 | 0 | 11788.25 | -3067.875 | 1341789.325 | 11788.25 | 0
2021112502 | 5 | 0.52614 | 78921 | 0.71421 | 0 | 0.38161 | 4770.125 | 0 | 0 | 64000 | 4770.125 | 0 | 10150.875 | -1637.375 | 1350000 | 10150.875 | 0
2021112503 | 5 | 0.51724 | 77586 | 0.74881 | 0 | 0.33196 | 4149.5 | 0 | 0 | 64000 | 4149.5 | 0 | 9436.5 | -714.375 | 1350000 | 9436.5 | 0
2021112504 | 5 | 0.51434 | 77151 | 0.74857 | 0 | 0.24101 | 3012.625 | 0 | 0 | 64000 | 3012.625 | 0 | 10138.375 | 701.875 | 1350000 | 10138.375 | 0
2021112505 | 5 | 0.51817 | 77725.5 | 0.74752 | 0 | 0.19048 | 2381 | 0 | 0 | 64000 | 2381 | 0 | 11344.5 | 1206.125 | 1350000 | 11344.5 | 0
2021112506 | 5 | 0.52939 | 79408.5 | 0.78024 | 0 | 0.13959 | 1744.875 | 0 | 0 | 64000 | 1744.875 | 0 | 13663.625 | 2319.125 | 1350000 | 13663.625 | 0
2021112507 | 5 | 0.54665 | 81997.5 | 0.72681 | 0 | 0.10608 | 1326 | 0.00447 | 357.6 | 64000 | 1326 | 357.6 | 16313.9 | 2650.275 | 1350000 | 16313.9 | 0
2021112508 | 5 | 0.56275 | 84412.5 | 0.64729 | 0 | 0.12092 | 1511.5 | 0.07432 | 5945.6 | 64000 | 1511.5 | 5945.6 | 12955.4 | -3358.5 | 1350000 | 12955.4 | 0
2021112509 | 5 | 0.57378 | 86067 | 0.60169 | 0 | 0.16606 | 2075.75 | 0.23418 | 18734.4 | 64000 | 2075.75 | 18734.4 | 1256.85 | -11698.55 | 1350000 | 1256.85 | 0
2021112510 | 5 | 0.57637 | 86455.5 | 0.4655 | 0 | 0.2141 | 2676.25 | 0.36078 | 28862.4 | 64000 | 2676.25 | 19779.25 | 0 | -1256.85 | 1350000 | 0 | 0
2021112511 | 5 | 0.57698 | 86547 | 0.34413 | 0 | 0.25873 | 3234.125 | 0.38551 | 30840.8 | 64000 | 3234.125 | 19312.875 | 0 | 0 | 1350000 | 0 | 0
2021112512 | 5 | 0.57392 | 86088 | 0.373 | 0 | 0.27608 | 3451 | 0.42732 | 34185.6 | 64000 | 3451 | 18637 | 0 | 0 | 1350000 | 0 | 0
2021112513 | 5 | 0.56173 | 84259.5 | 0.46954 | 0 | 0.27403 | 3425.375 | 0.45389 | 36311.2 | 64000 | 3425.375 | 16834.125 | 0 | 0 | 1350000 | 0 | 0
2021112514 | 5 | 0.54703 | 82054.5 | 0.46244 | 0 | 0.32563 | 4070.375 | 0.45348 | 36278.4 | 64000 | 4070.375 | 13984.125 | 0 | 0 | 1350000 | 0 | 0
2021112515 | 5 | 0.53424 | 80136 | 0.35339 | 0 | 0.36628 | 4578.5 | 0.40967 | 32773.6 | 64000 | 4578.5 | 11557.5 | 0 | 0 | 1350000 | 0 | 0
2021112516 | 5 | 0.52822 | 79233 | 0.46092 | 0 | 0.39711 | 4963.875 | 0.25712 | 20569.6 | 64000 | 4963.875 | 10269.125 | 0 | 0 | 1350000 | 0 | 0
2021112517 | 5 | 0.53192 | 79788 | 0.45749 | 0 | 0.43069 | 5383.625 | 0.04166 | 3332.8 | 64000 | 5383.625 | 3332.8 | 7071.575 | 7071.575 | 1350000 | 7071.575 | 0
2021112518 | 5 | 0.54116 | 81174 | 0.4816 | 0 | 0.50272 | 6284 | 0 | 0 | 64000 | 6284 | 0 | 10890 | 3818.425 | 1350000 | 10890 | 0
2021112519 | 5 | 0.53678 | 80517 | 0.53256 | 0 | 0.54063 | 6757.875 | 0 | 0 | 64000 | 6757.875 | 0 | 9759.125 | -1130.875 | 1350000 | 9759.125 | 0
2021112520 | 5 | 0.53242 | 79863 | 0.58883 | 0 | 0.57369 | 7171.125 | 0 | 0 | 64000 | 7171.125 | 0 | 8691.875 | -1067.25 | 1350000 | 8691.875 | 0
2021112521 | 5 | 0.52891 | 79336.5 | 0.60204 | 0 | 0.61361 | 7670.125 | 0 | 0 | 64000 | 7670.125 | 0 | 7666.375 | -1025.5 | 1350000 | 7666.375 | 0
2021112522 | 5 | 0.52264 | 78396 | 0.53554 | 0 | 0.65767 | 8220.875 | 0 | 0 | 64000 | 8220.875 | 0 | 6175.125 | -1491.25 | 1350000 | 6175.125 | 0
2021112523 | 5 | 0.50946 | 76419 | 0.49779 | 0 | 0.69199 | 8649.875 | 0 | 0 | 64000 | 8649.875 | 0 | 3769.125 | -2406 | 1350000 | 3769.125 | 0
2021112524 | 5 | 0.49191 | 73786.5 | 0.51055 | 0 | 0.71609 | 8951.125 | 0 | 0 | 64000 | 8951.125 | 0 | 835.375 | -2933.75 | 1350000 | 835.375 | 0
2021112601 | 6 | 0.47824 | 71736 | 0.63137 | 0 | 0.72257 | 9032.125 | 0 | 0 | 64000 | 7736 | 0 | 0 | -835.375 | 1350000 | 0 | 0
2021112602 | 6 | 0.47066 | 70599 | 0.65767 | 0 | 0.73274 | 9159.25 | 0 | 0 | 64000 | 6599 | 0 | 0 | 0 | 1350000 | 0 | 0
2021112603 | 6 | 0.46791 | 70186.5 | 0.75993 | 0 | 0.71181 | 8897.625 | 0 | 0 | 64000 | 6186.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021112604 | 6 | 0.47087 | 70630.5 | 0.83879 | 0 | 0.70209 | 8776.125 | 0 | 0 | 64000 | 6630.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021112605 | 6 | 0.47945 | 71917.5 | 0.88403 | 0 | 0.68066 | 8508.25 | 0 | 0 | 64000 | 7917.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021112606 | 6 | 0.49953 | 74929.5 | 0.93395 | 0 | 0.67819 | 8477.375 | 0 | 0 | 64000 | 8477.375 | 0 | 2452.125 | 2452.125 | 1350000 | 2452.125 | 0
2021112607 | 6 | 0.52591 | 78886.5 | 0.9715 | 0 | 0.72101 | 9012.625 | 0.00537 | 429.6 | 64000 | 9012.625 | 429.6 | 5444.275 | 2992.15 | 1350000 | 5444.275 | 0
2021112608 | 6 | 0.5488 | 82320 | 0.98467 | 0 | 0.75279 | 9409.875 | 0.0659 | 5272 | 64000 | 9409.875 | 5272 | 3638.125 | -1806.15 | 1350000 | 3638.125 | 0
2021112609 | 6 | 0.56209 | 84313.5 | 0.9813 | 0 | 0.77358 | 9669.75 | 0.1292 | 10336 | 64000 | 9669.75 | 10336 | 307.75 | -3330.375 | 1350000 | 307.75 | 0
2021112610 | 6 | 0.57154 | 85731 | 0.97684 | 0 | 0.79346 | 9918.25 | 0.18659 | 14927.2 | 64000 | 9918.25 | 11812.75 | 0 | -307.75 | 1350000 | 0 | 0
2021112611 | 6 | 0.57542 | 86313 | 0.97832 | 0 | 0.77736 | 9717 | 0.22652 | 18121.6 | 64000 | 9717 | 12596 | 0 | 0 | 1350000 | 0 | 0
2021112612 | 6 | 0.57569 | 86353.5 | 0.98454 | 0 | 0.75553 | 9444.125 | 0.23848 | 19078.4 | 64000 | 9444.125 | 12909.375 | 0 | 0 | 1350000 | 0 | 0
2021112613 | 6 | 0.57492 | 86238 | 0.99342 | 0 | 0.73406 | 9175.75 | 0.25028 | 20022.4 | 64000 | 9175.75 | 13062.25 | 0 | 0 | 1350000 | 0 | 0
2021112614 | 6 | 0.57421 | 86131.5 | 0.99494 | 0 | 0.71756 | 8969.5 | 0.20406 | 16324.8 | 64000 | 8969.5 | 13162 | 0 | 0 | 1350000 | 0 | 0
2021112615 | 6 | 0.57589 | 86383.5 | 0.99176 | 0 | 0.7232 | 9040 | 0.13004 | 10403.2 | 64000 | 9040 | 10403.2 | 2940.3 | 2940.3 | 1350000 | 2940.3 | 0
2021112616 | 6 | 0.58656 | 87984 | 0.98912 | 0 | 0.68968 | 8621 | 0.05538 | 4430.4 | 64000 | 8621 | 4430.4 | 10932.6 | 7992.3 | 1350000 | 10932.6 | 0
2021112617 | 6 | 0.60933 | 91399.5 | 0.9889 | 0 | 0.70146 | 8768.25 | 0.0034 | 272 | 64000 | 8768.25 | 272 | 18359.25 | 7426.65 | 1350000 | 18359.25 | 0
2021112618 | 6 | 0.64045 | 96067.5 | 0.99078 | 0 | 0.76786 | 9598.25 | 0 | 0 | 64000 | 9598.25 | 0 | 22469.25 | 4110 | 1350000 | 22469.25 | 0
2021112619 | 6 | 0.644 | 96600 | 0.99047 | 0 | 0.75763 | 9470.375 | 0 | 0 | 64000 | 9470.375 | 0 | 23129.625 | 660.375 | 1350000 | 23129.625 | 0
2021112620 | 6 | 0.63748 | 95622 | 0.99325 | 0 | 0.76666 | 9583.25 | 0 | 0 | 64000 | 9583.25 | 0 | 22038.75 | -1090.875 | 1350000 | 22038.75 | 0
2021112621 | 6 | 0.62937 | 94405.5 | 0.99669 | 0 | 0.76448 | 9556 | 0 | 0 | 64000 | 9556 | 0 | 20849.5 | -1189.25 | 1350000 | 20849.5 | 0
2021112622 | 6 | 0.61582 | 92373 | 0.99624 | 0 | 0.78382 | 9797.75 | 0 | 0 | 64000 | 9797.75 | 0 | 18575.25 | -2274.25 | 1350000 | 18575.25 | 0
2021112623 | 6 | 0.59658 | 89487 | 0.99713 | 0 | 0.78667 | 9833.375 | 0 | 0 | 64000 | 9833.375 | 0 | 15653.625 | -2921.625 | 1350000 | 15653.625 | 0
2021112624 | 6 | 0.57575 | 86362.5 | 0.99503 | 0 | 0.7945 | 9931.25 | 0 | 0 | 64000 | 9931.25 | 0 | 12431.25 | -3222.375 | 1350000 | 12431.25 | 0
2021112701 | 7 | 0.55835 | 83752.5 | 0.99504 | 0 | 0.7822 | 9777.5 | 0 | 0 | 64000 | 9777.5 | 0 | 9975 | -2456.25 | 1350000 | 9975 | 0
2021112702 | 7 | 0.54777 | 82165.5 | 0.99276 | 0 | 0.78351 | 9793.875 | 0 | 0 | 64000 | 9793.875 | 0 | 8371.625 | -1603.375 | 1350000 | 8371.625 | 0
2021112703 | 7 | 0.54292 | 81438 | 0.98597 | 0 | 0.77203 | 9650.375 | 0 | 0 | 64000 | 9650.375 | 0 | 7787.625 | -584 | 1350000 | 7787.625 | 0
2021112704 | 7 | 0.54284 | 81426 | 0.96991 | 0 | 0.74507 | 9313.375 | 0 | 0 | 64000 | 9313.375 | 0 | 8112.625 | 325 | 1350000 | 8112.625 | 0
2021112705 | 7 | 0.54801 | 82201.5 | 0.9716 | 0 | 0.74129 | 9266.125 | 0 | 0 | 64000 | 9266.125 | 0 | 8935.375 | 822.75 | 1350000 | 8935.375 | 0
2021112706 | 7 | 0.56156 | 84234 | 0.9603 | 0 | 0.74047 | 9255.875 | 0 | 0 | 64000 | 9255.875 | 0 | 10978.125 | 2042.75 | 1350000 | 10978.125 | 0
2021112707 | 7 | 0.58039 | 87058.5 | 0.94379 | 0 | 0.71603 | 8950.375 | 0.00838 | 670.4 | 64000 | 8950.375 | 670.4 | 13437.725 | 2459.6 | 1350000 | 13437.725 | 0
2021112708 | 7 | 0.59777 | 89665.5 | 0.92912 | 0 | 0.65088 | 8136 | 0.1102 | 8816 | 64000 | 8136 | 8816 | 8713.5 | -4724.225 | 1350000 | 8713.5 | 0
2021112709 | 7 | 0.60579 | 90868.5 | 0.91002 | 0 | 0.63439 | 7929.875 | 0.34654 | 27723.2 | 64000 | 7929.875 | 18938.625 | 0 | -8713.5 | 1350000 | 0 | 0
2021112710 | 7 | 0.60715 | 91072.5 | 0.87987 | 0 | 0.62889 | 7861.125 | 0.42906 | 34324.8 | 64000 | 7861.125 | 19211.375 | 0 | 0 | 1350000 | 0 | 0
2021112711 | 7 | 0.60119 | 90178.5 | 0.84937 | 0 | 0.64174 | 8021.75 | 0.43186 | 34548.8 | 64000 | 8021.75 | 18156.75 | 0 | 0 | 1350000 | 0 | 0
2021112712 | 7 | 0.59077 | 88615.5 | 0.75528 | 0 | 0.62849 | 7856.125 | 0.43142 | 34513.6 | 64000 | 7856.125 | 16759.375 | 0 | 0 | 1350000 | 0 | 0
2021112713 | 7 | 0.57664 | 86496 | 0.62364 | 0 | 0.63859 | 7982.375 | 0.42362 | 33889.6 | 64000 | 7982.375 | 14513.625 | 0 | 0 | 1350000 | 0 | 0
2021112714 | 7 | 0.56545 | 84817.5 | 0.53093 | 0 | 0.67003 | 8375.375 | 0.41429 | 33143.2 | 64000 | 8375.375 | 12442.125 | 0 | 0 | 1350000 | 0 | 0
2021112715 | 7 | 0.56364 | 84546 | 0.40606 | 0 | 0.73626 | 9203.25 | 0.37449 | 29959.2 | 64000 | 9203.25 | 11342.75 | 0 | 0 | 1350000 | 0 | 0
2021112716 | 7 | 0.56967 | 85450.5 | 0.27598 | 0 | 0.74598 | 9324.75 | 0.24426 | 19540.8 | 64000 | 9324.75 | 12125.75 | 0 | 0 | 1350000 | 0 | 0
2021112717 | 7 | 0.59194 | 88791 | 0.20126 | 0 | 0.74555 | 9319.375 | 0.03372 | 2697.6 | 64000 | 9319.375 | 2697.6 | 12774.025 | 12774.025 | 1350000 | 12774.025 | 0
2021112718 | 7 | 0.62448 | 93672 | 0.15316 | 0 | 0.70052 | 8756.5 | 0 | 0 | 64000 | 8756.5 | 0 | 20915.5 | 8141.475 | 1350000 | 20915.5 | 0
2021112719 | 7 | 0.62926 | 94389 | 0.20924 | 0 | 0.65236 | 8154.5 | 0 | 0 | 64000 | 8154.5 | 0 | 22234.5 | 1319 | 1350000 | 22234.5 | 0
2021112720 | 7 | 0.62537 | 93805.5 | 0.1504 | 0 | 0.62662 | 7832.75 | 0 | 0 | 64000 | 7832.75 | 0 | 21972.75 | -261.75 | 1350000 | 21972.75 | 0
2021112721 | 7 | 0.61751 | 92626.5 | 0.12717 | 0 | 0.62293 | 7786.625 | 0 | 0 | 64000 | 7786.625 | 0 | 20839.875 | -1132.875 | 1350000 | 20839.875 | 0
2021112722 | 7 | 0.60318 | 90477 | 0.17683 | 0 | 0.65147 | 8143.375 | 0 | 0 | 64000 | 8143.375 | 0 | 18333.625 | -2506.25 | 1350000 | 18333.625 | 0
2021112723 | 7 | 0.5813 | 87195 | 0.20463 | 0 | 0.66458 | 8307.25 | 0 | 0 | 64000 | 8307.25 | 0 | 14887.75 | -3445.875 | 1350000 | 14887.75 | 0
2021112724 | 7 | 0.55827 | 83740.5 | 0.22971 | 0 | 0.64259 | 8032.375 | 0 | 0 | 64000 | 8032.375 | 0 | 11708.125 | -3179.625 | 1350000 | 11708.125 | 0
2021112801 | 1 | 0.53815 | 80722.5 | 0.30183 | 0 | 0.62636 | 7829.5 | 0 | 0 | 64000 | 7829.5 | 0 | 8893 | -2815.125 | 1350000 | 8893 | 0
2021112802 | 1 | 0.52472 | 78708 | 0.39499 | 0 | 0.59428 | 7428.5 | 0 | 0 | 64000 | 7428.5 | 0 | 7279.5 | -1613.5 | 1350000 | 7279.5 | 0
2021112803 | 1 | 0.51664 | 77496 | 0.34278 | 0 | 0.50904 | 6363 | 0 | 0 | 64000 | 6363 | 0 | 7133 | -146.5 | 1350000 | 7133 | 0
2021112804 | 1 | 0.51297 | 76945.5 | 0.37485 | 0 | 0.45763 | 5720.375 | 0 | 0 | 64000 | 5720.375 | 0 | 7225.125 | 92.125 | 1350000 | 7225.125 | 0
2021112805 | 1 | 0.51602 | 77403 | 0.48054 | 0 | 0.41601 | 5200.125 | 0 | 0 | 64000 | 5200.125 | 0 | 8202.875 | 977.75 | 1350000 | 8202.875 | 0
2021112806 | 1 | 0.52605 | 78907.5 | 0.56844 | 0 | 0.34497 | 4312.125 | 0 | 0 | 64000 | 4312.125 | 0 | 10595.375 | 2392.5 | 1350000 | 10595.375 | 0
2021112807 | 1 | 0.54305 | 81457.5 | 0.58406 | 0 | 0.27158 | 3394.75 | 0.01338 | 1070.4 | 64000 | 3394.75 | 1070.4 | 12992.35 | 2396.975 | 1350000 | 12992.35 | 0
2021112808 | 1 | 0.55907 | 83860.5 | 0.63058 | 0 | 0.24065 | 3008.125 | 0.1705 | 13640 | 64000 | 3008.125 | 13640 | 3212.375 | -9779.975 | 1350000 | 3212.375 | 0
2021112809 | 1 | 0.56725 | 85087.5 | 0.68501 | 0 | 0.22997 | 2874.625 | 0.31517 | 25213.6 | 64000 | 2874.625 | 18212.875 | 0 | -3212.375 | 1350000 | 0 | 0
2021112810 | 1 | 0.56848 | 85272 | 0.70611 | 0 | 0.21782 | 2722.75 | 0.31881 | 25504.8 | 64000 | 2722.75 | 18549.25 | 0 | 0 | 1350000 | 0 | 0
2021112811 | 1 | 0.56426 | 84639 | 0.74291 | 0 | 0.2031 | 2538.75 | 0.3137 | 25096 | 64000 | 2538.75 | 18100.25 | 0 | 0 | 1350000 | 0 | 0
2021112812 | 1 | 0.5585 | 83775 | 0.74142 | 0 | 0.19603 | 2450.375 | 0.30567 | 24453.6 | 64000 | 2450.375 | 17324.625 | 0 | 0 | 1350000 | 0 | 0
2021112813 | 1 | 0.55441 | 83161.5 | 0.6803 | 0 | 0.19639 | 2454.875 | 0.28831 | 23064.8 | 64000 | 2454.875 | 16706.625 | 0 | 0 | 1350000 | 0 | 0
2021112814 | 1 | 0.54901 | 82351.5 | 0.61 | 0 | 0.20012 | 2501.5 | 0.28259 | 22607.2 | 64000 | 2501.5 | 15850 | 0 | 0 | 1350000 | 0 | 0
2021112815 | 1 | 0.54765 | 82147.5 | 0.53894 | 0 | 0.21918 | 2739.75 | 0.22678 | 18142.4 | 64000 | 2739.75 | 15407.75 | 0 | 0 | 1350000 | 0 | 0
2021112816 | 1 | 0.55495 | 83242.5 | 0.55075 | 0 | 0.2507 | 3133.75 | 0.07928 | 6342.4 | 64000 | 3133.75 | 6342.4 | 9766.35 | 9766.35 | 1350000 | 9766.35 | 0
2021112817 | 1 | 0.57838 | 86757 | 0.52151 | 0 | 0.29216 | 3652 | 0.01087 | 869.6 | 64000 | 3652 | 869.6 | 18235.4 | 8469.05 | 1350000 | 18235.4 | 0
2021112818 | 1 | 0.61702 | 92553 | 0.4754 | 0 | 0.31015 | 3876.875 | 0 | 0 | 64000 | 3876.875 | 0 | 24676.125 | 6440.725 | 1350000 | 24676.125 | 0
2021112819 | 1 | 0.62877 | 94315.5 | 0.57061 | 0 | 0.32694 | 4086.75 | 0 | 0 | 64000 | 4086.75 | 0 | 26228.75 | 1552.625 | 1349237.5 | 26228.75 | 0
2021112820 | 1 | 0.62685 | 94027.5 | 0.65357 | 0 | 0.34275 | 4284.375 | 0 | 0 | 64000 | 4284.375 | 0 | 25743.125 | -485.625 | 1348960.625 | 25743.125 | 0
2021112821 | 1 | 0.61744 | 92616 | 0.63299 | 0 | 0.31296 | 3912 | 0 | 0 | 64000 | 3912 | 0 | 24704 | -1039.125 | 1349722.875 | 24704 | 0
2021112822 | 1 | 0.60176 | 90264 | 0.5904 | 0 | 0.30934 | 3866.75 | 0 | 0 | 64000 | 3866.75 | 0 | 22397.25 | -2306.75 | 1350000 | 22397.25 | 0
2021112823 | 1 | 0.57766 | 86649 | 0.51666 | 0 | 0.34077 | 4259.625 | 0 | 0 | 64000 | 4259.625 | 0 | 18389.375 | -4007.875 | 1350000 | 18389.375 | 0
2021112824 | 1 | 0.55492 | 83238 | 0.61515 | 0 | 0.35104 | 4388 | 0 | 0 | 64000 | 4388 | 0 | 14850 | -3539.375 | 1350000 | 14850 | 0
2021112901 | 2 | 0.537 | 80550 | 0.63405 | 0 | 0.36875 | 4609.375 | 0 | 0 | 64000 | 4609.375 | 0 | 11940.625 | -2909.375 | 1350000 | 11940.625 | 0
2021112902 | 2 | 0.53004 | 79506 | 0.6695 | 0 | 0.38243 | 4780.375 | 0 | 0 | 64000 | 4780.375 | 0 | 10725.625 | -1215 | 1350000 | 10725.625 | 0
2021112903 | 2 | 0.52937 | 79405.5 | 0.70724 | 0 | 0.38418 | 4802.25 | 0 | 0 | 64000 | 4802.25 | 0 | 10603.25 | -122.375 | 1350000 | 10603.25 | 0
2021112904 | 2 | 0.53431 | 80146.5 | 0.69234 | 0 | 0.38928 | 4866 | 0 | 0 | 64000 | 4866 | 0 | 11280.5 | 677.25 | 1350000 | 11280.5 | 0
2021112905 | 2 | 0.55099 | 82648.5 | 0.65678 | 0 | 0.37746 | 4718.25 | 0 | 0 | 64000 | 4718.25 | 0 | 13930.25 | 2649.75 | 1350000 | 13930.25 | 0
2021112906 | 2 | 0.58683 | 88024.5 | 0.68072 | 0 | 0.38689 | 4836.125 | 0 | 0 | 64000 | 4836.125 | 0 | 19188.375 | 5258.125 | 1350000 | 19188.375 | 0
2021112907 | 2 | 0.63875 | 95812.5 | 0.68301 | 0 | 0.39669 | 4958.625 | 0.00581 | 464.8 | 64000 | 4958.625 | 464.8 | 26389.075 | 7200.7 | 1349077.175 | 26389.075 | 0
2021112908 | 2 | 0.67354 | 101031 | 0.69182 | 0 | 0.39704 | 4963 | 0.06011 | 4808.8 | 64000 | 4963 | 4808.8 | 27259.2 | 870.125 | 1347284.225 | 27259.2 | 0
2021112909 | 2 | 0.67051 | 100576.5 | 0.68649 | 0 | 0.37996 | 4749.5 | 0.09521 | 7616.8 | 64000 | 4749.5 | 7616.8 | 24210.2 | -3049 | 1348540.275 | 24210.2 | 0
2021112910 | 2 | 0.65688 | 98532 | 0.66038 | 0 | 0.36918 | 4614.75 | 0.12332 | 9865.6 | 64000 | 4614.75 | 9865.6 | 20051.65 | -4158.55 | 1350000 | 20051.65 | 0
2021112911 | 2 | 0.64671 | 97006.5 | 0.66524 | 0 | 0.34622 | 4327.75 | 0.15384 | 12307.2 | 64000 | 4327.75 | 12307.2 | 16371.55 | -3680.1 | 1350000 | 16371.55 | 0
2021112912 | 2 | 0.64057 | 96085.5 | 0.71057 | 0 | 0.30896 | 3862 | 0.17207 | 13765.6 | 64000 | 3862 | 13765.6 | 14457.9 | -1913.65 | 1350000 | 14457.9 | 0
2021112913 | 2 | 0.63863 | 95794.5 | 0.67572 | 0 | 0.31336 | 3917 | 0.16367 | 13093.6 | 64000 | 3917 | 13093.6 | 14783.9 | 326 | 1350000 | 14783.9 | 0
2021112914 | 2 | 0.63664 | 95496 | 0.64585 | 0 | 0.35 | 4375 | 0.13023 | 10418.4 | 64000 | 4375 | 10418.4 | 16702.6 | 1918.7 | 1350000 | 16702.6 | 0
2021112915 | 2 | 0.63373 | 95059.5 | 0.59644 | 0 | 0.38773 | 4846.625 | 0.09226 | 7380.8 | 64000 | 4846.625 | 7380.8 | 18832.075 | 2129.475 | 1350000 | 18832.075 | 0
2021112916 | 2 | 0.63692 | 95538 | 0.52744 | 0 | 0.44975 | 5621.875 | 0.03144 | 2515.2 | 64000 | 5621.875 | 2515.2 | 23400.925 | 4568.85 | 1350000 | 23400.925 | 0
2021112917 | 2 | 0.65907 | 98860.5 | 0.45606 | 0 | 0.46692 | 5836.5 | 0.0027 | 216 | 64000 | 5836.5 | 216 | 28808 | 5407.075 | 1346658.25 | 28808 | 0
2021112918 | 2 | 0.6978 | 104670 | 0.47174 | 0 | 0.48639 | 6079.875 | 0 | 0 | 64000 | 6079.875 | 0 | 34590.125 | 5782.125 | 1337534.375 | 34590.125 | 0
2021112919 | 2 | 0.70437 | 105655.5 | 0.43269 | 0 | 0.52854 | 6606.75 | 0 | 0 | 64000 | 6606.75 | 0 | 35048.75 | 458.625 | 1327951.875 | 35048.75 | 0
2021112920 | 2 | 0.6987 | 104805 | 0.38414 | 0 | 0.52124 | 6515.5 | 0 | 0 | 64000 | 6515.5 | 0 | 34289.5 | -759.25 | 1319128.625 | 34289.5 | 0
2021112921 | 2 | 0.68753 | 103129.5 | 0.35566 | 0 | 0.53201 | 6650.125 | 0 | 0 | 64000 | 6650.125 | 0 | 32479.375 | -1810.125 | 1312115.5 | 32479.375 | 0
2021112922 | 2 | 0.66675 | 100012.5 | 0.33783 | 0 | 0.52371 | 6546.375 | 0 | 0 | 64000 | 6546.375 | 0 | 29466.125 | -3013.25 | 1308115.625 | 29466.125 | 0
2021112923 | 2 | 0.63637 | 95455.5 | 0.2844 | 0 | 0.50324 | 6290.5 | 0 | 0 | 64000 | 6290.5 | 0 | 25165 | -4301.125 | 1308416.875 | 25165 | 0
2021112924 | 2 | 0.60759 | 91138.5 | 0.25264 | 0 | 0.49757 | 6219.625 | 0 | 0 | 64000 | 6219.625 | 0 | 20918.875 | -4246.125 | 1312964.25 | 20918.875 | 0
2021113001 | 3 | 0.58672 | 88008 | 0.29095 | 0 | 0.505 | 6312.5 | 0 | 0 | 64000 | 6312.5 | 0 | 17695.5 | -3223.375 | 1320735 | 17695.5 | 0
2021113002 | 3 | 0.57488 | 86232 | 0.30821 | 0 | 0.50978 | 6372.25 | 0 | 0 | 64000 | 6372.25 | 0 | 15859.75 | -1835.75 | 1330341.5 | 15859.75 | 0
2021113003 | 3 | 0.56839 | 85258.5 | 0.32991 | 0 | 0.50401 | 6300.125 | 0 | 0 | 64000 | 6300.125 | 0 | 14958.375 | -901.375 | 1340849.375 | 14958.375 | 0
2021113004 | 3 | 0.56791 | 85186.5 | 0.27495 | 0 | 0.52155 | 6519.375 | 0 | 0 | 64000 | 6519.375 | 0 | 14667.125 | -291.25 | 1350000 | 14667.125 | 0
2021113005 | 3 | 0.57802 | 86703 | 0.22744 | 0 | 0.50662 | 6332.75 | 0 | 0 | 64000 | 6332.75 | 0 | 16370.25 | 1703.125 | 1350000 | 16370.25 | 0
2021113006 | 3 | 0.60762 | 91143 | 0.24081 | 0 | 0.48934 | 6116.75 | 0 | 0 | 64000 | 6116.75 | 0 | 21026.25 | 4656 | 1350000 | 21026.25 | 0
2021113007 | 3 | 0.65596 | 98394 | 0.26843 | 0 | 0.47576 | 5947 | 0.00136 | 108.8 | 64000 | 5947 | 108.8 | 28338.2 | 7311.95 | 1347128.05 | 28338.2 | 0
2021113008 | 3 | 0.68466 | 102699 | 0.32772 | 0 | 0.47508 | 5938.5 | 0.01741 | 1392.8 | 64000 | 5938.5 | 1392.8 | 31367.7 | 3029.5 | 1341226.6 | 31367.7 | 0
2021113009 | 3 | 0.68382 | 102573 | 0.36718 | 0 | 0.47375 | 5921.875 | 0.03759 | 3007.2 | 64000 | 5921.875 | 3007.2 | 29643.925 | -1723.775 | 1337048.925 | 29643.925 | 0
2021113010 | 3 | 0.67035 | 100552.5 | 0.39264 | 0 | 0.44584 | 5573 | 0.05679 | 4543.2 | 64000 | 5573 | 4543.2 | 26436.3 | -3207.625 | 1336078.875 | 26436.3 | 0
2021113011 | 3 | 0.65911 | 98866.5 | 0.4638 | 0 | 0.42302 | 5287.75 | 0.07662 | 6129.6 | 64000 | 5287.75 | 6129.6 | 23449.15 | -2987.15 | 1338095.975 | 23449.15 | 0
2021113012 | 3 | 0.64575 | 96862.5 | 0.50282 | 0 | 0.40663 | 5082.875 | 0.08954 | 7163.2 | 64000 | 5082.875 | 7163.2 | 20616.425 | -2832.725 | 1342945.8 | 20616.425 | 0
2021113013 | 3 | 0.63282 | 94923 | 0.57141 | 0 | 0.43752 | 5469 | 0.08287 | 6629.6 | 64000 | 5469 | 6629.6 | 18824.4 | -1792.025 | 1349587.65 | 18824.4 | 0
2021113014 | 3 | 0.62307 | 93460.5 | 0.62534 | 0 | 0.50333 | 6291.625 | 0.0632 | 5056 | 64000 | 6291.625 | 5056 | 18112.875 | -711.525 | 1350000 | 18112.875 | 0
2021113015 | 3 | 0.61374 | 92061 | 0.61293 | 0 | 0.54131 | 6766.375 | 0.03742 | 2993.6 | 64000 | 6766.375 | 2993.6 | 18301.025 | 188.15 | 1350000 | 18301.025 | 0
2021113016 | 3 | 0.61254 | 91881 | 0.61204 | 0 | 0.56067 | 7008.375 | 0.01687 | 1349.6 | 64000 | 7008.375 | 1349.6 | 19523.025 | 1222 | 1350000 | 19523.025 | 0
2021113017 | 3 | 0.63119 | 94678.5 | 0.74474 | 0 | 0.56279 | 7034.875 | 0.00212 | 169.6 | 64000 | 7034.875 | 169.6 | 23474.025 | 3951 | 1350000 | 23474.025 | 0
2021113018 | 3 | 0.66867 | 100300.5 | 0.77644 | 0 | 0.55791 | 6973.875 | 0 | 0 | 64000 | 6973.875 | 0 | 29326.625 | 5852.6 | 1346139.625 | 29326.625 | 0
2021113019 | 3 | 0.67768 | 101652 | 0.84419 | 0 | 0.56458 | 7057.25 | 0 | 0 | 64000 | 7057.25 | 0 | 30594.75 | 1268.125 | 1341011.125 | 30594.75 | 0
2021113020 | 3 | 0.67195 | 100792.5 | 0.88081 | 0 | 0.5932 | 7415 | 0 | 0 | 64000 | 7415 | 0 | 29377.5 | -1217.25 | 1337099.875 | 29377.5 | 0
2021113021 | 3 | 0.66061 | 99091.5 | 0.91016 | 0 | 0.59518 | 7439.75 | 0 | 0 | 64000 | 7439.75 | 0 | 27651.75 | -1725.75 | 1334914.375 | 27651.75 | 0
2021113022 | 3 | 0.63974 | 95961 | 0.93753 | 0 | 0.58735 | 7341.875 | 0 | 0 | 64000 | 7341.875 | 0 | 24619.125 | -3032.625 | 1335761.5 | 24619.125 | 0
2021113023 | 3 | 0.6102 | 91530 | 0.96697 | 0 | 0.58667 | 7333.375 | 0 | 0 | 64000 | 7333.375 | 0 | 20196.625 | -4422.5 | 1341031.125 | 20196.625 | 0
2021113024 | 3 | 0.58167 | 87250.5 | 0.98668 | 0 | 0.59542 | 7442.75 | 0 | 0 | 64000 | 7442.75 | 0 | 15807.75 | -4388.875 | 1350000 | 15807.75 | 0
2021120101 | 4 | 0.56015 | 84022.5 | 0.97351 | 0 | 0.59964 | 7495.5 | 0 | 0 | 64000 | 7495.5 | 0 | 12527 | -3280.75 | 1350000 | 12527 | 0
2021120102 | 4 | 0.55065 | 82597.5 | 0.87802 | 0 | 0.62334 | 7791.75 | 0 | 0 | 64000 | 7791.75 | 0 | 10805.75 | -1721.25 | 1350000 | 10805.75 | 0
2021120103 | 4 | 0.54931 | 82396.5 | 0.84994 | 0 | 0.6502 | 8127.5 | 0 | 0 | 64000 | 8127.5 | 0 | 10269 | -536.75 | 1350000 | 10269 | 0
2021120104 | 4 | 0.55308 | 82962 | 0.80202 | 0 | 0.65511 | 8188.875 | 0 | 0 | 64000 | 8188.875 | 0 | 10773.125 | 504.125 | 1350000 | 10773.125 | 0
2021120105 | 4 | 0.56752 | 85128 | 0.63444 | 0 | 0.66714 | 8339.25 | 0 | 0 | 64000 | 8339.25 | 0 | 12788.75 | 2015.625 | 1350000 | 12788.75 | 0
2021120106 | 4 | 0.59967 | 89950.5 | 0.51327 | 0 | 0.65699 | 8212.375 | 0 | 0 | 64000 | 8212.375 | 0 | 17738.125 | 4949.375 | 1350000 | 17738.125 | 0
2021120107 | 4 | 0.6502 | 97530 | 0.44235 | 0 | 0.64417 | 8052.125 | 0.00012 | 9.6 | 64000 | 8052.125 | 9.6 | 25468.275 | 7730.15 | 1349997.975 | 25468.275 | 0
2021120108 | 4 | 0.67866 | 101799 | 0.43137 | 0 | 0.64667 | 8083.375 | 0.01044 | 835.2 | 64000 | 8083.375 | 835.2 | 28880.425 | 3412.15 | 1346583.8 | 28880.425 | 0
2021120109 | 4 | 0.6696 | 100440 | 0.5575 | 0 | 0.63067 | 7883.375 | 0.02652 | 2121.6 | 64000 | 7883.375 | 2121.6 | 26435.025 | -2445.4 | 1345615.025 | 26435.025 | 0
2021120110 | 4 | 0.6487 | 97305 | 0.44074 | 0 | 0.59828 | 7478.5 | 0.03621 | 2896.8 | 64000 | 7478.5 | 2896.8 | 22929.7 | -3505.325 | 1348151.575 | 22929.7 | 0
2021120111 | 4 | 0.62918 | 94377 | 0.33819 | 0 | 0.58351 | 7293.875 | 0.04697 | 3757.6 | 64000 | 7293.875 | 3757.6 | 19325.525 | -3604.175 | 1350000 | 19325.525 | 0
2021120112 | 4 | 0.61472 | 92208 | 0.16941 | 0 | 0.56618 | 7077.25 | 0.05649 | 4519.2 | 64000 | 7077.25 | 4519.2 | 16611.55 | -2713.975 | 1350000 | 16611.55 | 0
2021120113 | 4 | 0.60672 | 91008 | 0.04716 | 0 | 0.54964 | 6870.5 | 0.05503 | 4402.4 | 64000 | 6870.5 | 4402.4 | 15735.1 | -876.45 | 1350000 | 15735.1 | 0
2021120114 | 4 | 0.60423 | 90634.5 | 0.00877 | 0 | 0.53618 | 6702.25 | 0.043 | 3440 | 64000 | 6702.25 | 3440 | 16492.25 | 757.15 | 1350000 | 16492.25 | 0
2021120115 | 4 | 0.60165 | 90247.5 | 0.06011 | 0 | 0.55355 | 6919.375 | 0.02615 | 2092 | 64000 | 6919.375 | 2092 | 17236.125 | 743.875 | 1350000 | 17236.125 | 0
2021120116 | 4 | 0.60748 | 91122 | 0.13905 | 0 | 0.5784 | 7230 | 0.00939 | 751.2 | 64000 | 7230 | 751.2 | 19140.8 | 1904.675 | 1350000 | 19140.8 | 0
2021120117 | 4 | 0.62746 | 94119 | 0.17818 | 0 | 0.57652 | 7206.5 | 0.00051 | 40.8 | 64000 | 7206.5 | 40.8 | 22871.7 | 3730.9 | 1350000 | 22871.7 | 0
2021120118 | 4 | 0.66039 | 99058.5 | 0.3342 | 0 | 0.57152 | 7144 | 0 | 0 | 64000 | 7144 | 0 | 27914.5 | 5042.8 | 1347551.75 | 27914.5 | 0
2021120119 | 4 | 0.66173 | 99259.5 | 0.46691 | 0 | 0.58929 | 7366.125 | 0 | 0 | 64000 | 7366.125 | 0 | 27893.375 | -21.125 | 1345124.625 | 27893.375 | 0
2021120120 | 4 | 0.65114 | 97671 | 0.63376 | 0 | 0.60992 | 7624 | 0 | 0 | 64000 | 7624 | 0 | 26047 | -1846.375 | 1344543.875 | 26047 | 0
2021120121 | 4 | 0.63717 | 95575.5 | 0.77054 | 0 | 0.61483 | 7685.375 | 0 | 0 | 64000 | 7685.375 | 0 | 23890.125 | -2156.875 | 1346120 | 23890.125 | 0
2021120122 | 4 | 0.61394 | 92091 | 0.81789 | 0 | 0.62261 | 7782.625 | 0 | 0 | 64000 | 7782.625 | 0 | 20308.375 | -3581.75 | 1350000 | 20308.375 | 0
2021120123 | 4 | 0.57929 | 86893.5 | 0.8873 | 0 | 0.6404 | 8005 | 0 | 0 | 64000 | 8005 | 0 | 14888.5 | -5419.875 | 1350000 | 14888.5 | 0
2021120124 | 4 | 0.54703 | 82054.5 | 0.90434 | 0 | 0.66138 | 8267.25 | 0 | 0 | 64000 | 8267.25 | 0 | 9787.25 | -5101.25 | 1350000 | 9787.25 | 0
2021120201 | 5 | 0.52191 | 78286.5 | 0.91843 | 0 | 0.67724 | 8465.5 | 0 | 0 | 64000 | 8465.5 | 0 | 5821 | -3966.25 | 1350000 | 5821 | 0
2021120202 | 5 | 0.5073 | 76095 | 0.94258 | 0 | 0.69876 | 8734.5 | 0 | 0 | 64000 | 8734.5 | 0 | 3360.5 | -2460.5 | 1350000 | 3360.5 | 0
2021120203 | 5 | 0.49937 | 74905.5 | 0.94248 | 0 | 0.70262 | 8782.75 | 0 | 0 | 64000 | 8782.75 | 0 | 2122.75 | -1237.75 | 1350000 | 2122.75 | 0
2021120204 | 5 | 0.49885 | 74827.5 | 0.94397 | 0 | 0.68102 | 8512.75 | 0 | 0 | 64000 | 8512.75 | 0 | 2314.75 | 192 | 1350000 | 2314.75 | 0
2021120205 | 5 | 0.5092 | 76380 | 0.93416 | 0 | 0.67953 | 8494.125 | 0 | 0 | 64000 | 8494.125 | 0 | 3885.875 | 1571.125 | 1350000 | 3885.875 | 0
2021120206 | 5 | 0.53708 | 80562 | 0.93927 | 0 | 0.64595 | 8074.375 | 0 | 0 | 64000 | 8074.375 | 0 | 8487.625 | 4601.75 | 1350000 | 8487.625 | 0
2021120207 | 5 | 0.58361 | 87541.5 | 0.92192 | 0 | 0.62776 | 7847 | 0.00391 | 312.8 | 64000 | 7847 | 312.8 | 15381.7 | 6894.075 | 1350000 | 15381.7 | 0
2021120208 | 5 | 0.61227 | 91840.5 | 0.95014 | 0 | 0.59917 | 7489.625 | 0.09399 | 7519.2 | 64000 | 7489.625 | 7519.2 | 12831.675 | -2550.025 | 1350000 | 12831.675 | 0
2021120209 | 5 | 0.61157 | 91735.5 | 0.95531 | 0 | 0.58991 | 7373.875 | 0.26901 | 21520.8 | 64000 | 7373.875 | 20361.625 | 0 | -12831.675 | 1350000 | 0 | 0
2021120210 | 5 | 0.60418 | 90627 | 0.92711 | 0 | 0.60845 | 7605.625 | 0.34547 | 27637.6 | 64000 | 7605.625 | 19021.375 | 0 | 0 | 1350000 | 0 | 0
2021120211 | 5 | 0.59816 | 89724 | 0.93697 | 0 | 0.59455 | 7431.875 | 0.44332 | 35465.6 | 64000 | 7431.875 | 18292.125 | 0 | 0 | 1350000 | 0 | 0
2021120212 | 5 | 0.58833 | 88249.5 | 0.97725 | 0 | 0.59705 | 7463.125 | 0.48616 | 38892.8 | 64000 | 7463.125 | 16786.375 | 0 | 0 | 1350000 | 0 | 0
2021120213 | 5 | 0.5818 | 87270 | 0.97645 | 0 | 0.60214 | 7526.75 | 0.4845 | 38760 | 64000 | 7526.75 | 15743.25 | 0 | 0 | 1350000 | 0 | 0
2021120214 | 5 | 0.57646 | 86469 | 0.97283 | 0 | 0.60315 | 7539.375 | 0.49076 | 39260.8 | 64000 | 7539.375 | 14929.625 | 0 | 0 | 1350000 | 0 | 0
2021120215 | 5 | 0.57285 | 85927.5 | 0.96405 | 0 | 0.62791 | 7848.875 | 0.45255 | 36204 | 64000 | 7848.875 | 14078.625 | 0 | 0 | 1350000 | 0 | 0
2021120216 | 5 | 0.57336 | 86004 | 0.94806 | 0 | 0.61198 | 7649.75 | 0.2513 | 20104 | 64000 | 7649.75 | 14354.25 | 0 | 0 | 1350000 | 0 | 0
2021120217 | 5 | 0.58883 | 88324.5 | 0.92353 | 0 | 0.61263 | 7657.875 | 0.02824 | 2259.2 | 64000 | 7657.875 | 2259.2 | 14407.425 | 14407.425 | 1350000 | 14407.425 | 0
2021120218 | 5 | 0.61739 | 92608.5 | 0.94046 | 0 | 0.58916 | 7364.5 | 0 | 0 | 64000 | 7364.5 | 0 | 21244 | 6836.575 | 1350000 | 21244 | 0
2021120219 | 5 | 0.62196 | 93294 | 0.98207 | 0 | 0.56795 | 7099.375 | 0 | 0 | 64000 | 7099.375 | 0 | 22194.625 | 950.625 | 1350000 | 22194.625 | 0
2021120220 | 5 | 0.61429 | 92143.5 | 0.99068 | 0 | 0.57467 | 7183.375 | 0 | 0 | 64000 | 7183.375 | 0 | 20960.125 | -1234.5 | 1350000 | 20960.125 | 0
2021120221 | 5 | 0.60231 | 90346.5 | 0.9959 | 0 | 0.59763 | 7470.375 | 0 | 0 | 64000 | 7470.375 | 0 | 18876.125 | -2084 | 1350000 | 18876.125 | 0
2021120222 | 5 | 0.58122 | 87183 | 0.98829 | 0 | 0.59589 | 7448.625 | 0 | 0 | 64000 | 7448.625 | 0 | 15734.375 | -3141.75 | 1350000 | 15734.375 | 0
2021120223 | 5 | 0.55153 | 82729.5 | 0.96898 | 0 | 0.58962 | 7370.25 | 0 | 0 | 64000 | 7370.25 | 0 | 11359.25 | -4375.125 | 1350000 | 11359.25 | 0
2021120224 | 5 | 0.52151 | 78226.5 | 0.97518 | 0 | 0.57536 | 7192 | 0 | 0 | 64000 | 7192 | 0 | 7034.5 | -4324.75 | 1350000 | 7034.5 | 0
2021120301 | 6 | 0.49915 | 74872.5 | 0.97547 | 0 | 0.53569 | 6696.125 | 0 | 0 | 64000 | 6696.125 | 0 | 4176.375 | -2858.125 | 1350000 | 4176.375 | 0
2021120302 | 6 | 0.48838 | 73257 | 0.98202 | 0 | 0.49921 | 6240.125 | 0 | 0 | 64000 | 6240.125 | 0 | 3016.875 | -1159.5 | 1350000 | 3016.875 | 0
2021120303 | 6 | 0.48333 | 72499.5 | 0.98794 | 0 | 0.48618 | 6077.25 | 0 | 0 | 64000 | 6077.25 | 0 | 2422.25 | -594.625 | 1350000 | 2422.25 | 0
2021120304 | 6 | 0.48577 | 72865.5 | 0.98482 | 0 | 0.46455 | 5806.875 | 0 | 0 | 64000 | 5806.875 | 0 | 3058.625 | 636.375 | 1350000 | 3058.625 | 0
2021120305 | 6 | 0.49881 | 74821.5 | 0.96312 | 0 | 0.44124 | 5515.5 | 0 | 0 | 64000 | 5515.5 | 0 | 5306 | 2247.375 | 1350000 | 5306 | 0
2021120306 | 6 | 0.53077 | 79615.5 | 0.96387 | 0 | 0.38766 | 4845.75 | 0 | 0 | 64000 | 4845.75 | 0 | 10769.75 | 5463.75 | 1350000 | 10769.75 | 0
2021120307 | 6 | 0.58034 | 87051 | 0.93314 | 0 | 0.32789 | 4098.625 | 0.01002 | 801.6 | 64000 | 4098.625 | 801.6 | 18150.775 | 7381.025 | 1350000 | 18150.775 | 0
2021120308 | 6 | 0.61389 | 92083.5 | 0.90806 | 0 | 0.34172 | 4271.5 | 0.16471 | 13176.8 | 64000 | 4271.5 | 13176.8 | 10635.2 | -7515.575 | 1350000 | 10635.2 | 0
2021120309 | 6 | 0.61575 | 92362.5 | 0.93776 | 0 | 0.3365 | 4206.25 | 0.37814 | 30251.2 | 64000 | 4206.25 | 24156.25 | 0 | -10635.2 | 1350000 | 0 | 0
2021120310 | 6 | 0.60624 | 90936 | 0.945 | 0 | 0.34402 | 4300.25 | 0.43766 | 35012.8 | 64000 | 4300.25 | 22635.75 | 0 | 0 | 1350000 | 0 | 0
2021120311 | 6 | 0.59806 | 89709 | 0.89395 | 0 | 0.3532 | 4415 | 0.45054 | 36043.2 | 64000 | 4415 | 21294 | 0 | 0 | 1350000 | 0 | 0
2021120312 | 6 | 0.5897 | 88455 | 0.85292 | 0 | 0.36842 | 4605.25 | 0.46146 | 36916.8 | 64000 | 4605.25 | 19849.75 | 0 | 0 | 1350000 | 0 | 0
2021120313 | 6 | 0.5839 | 87585 | 0.7902 | 0 | 0.3653 | 4566.25 | 0.47124 | 37699.2 | 64000 | 4566.25 | 19018.75 | 0 | 0 | 1350000 | 0 | 0
2021120314 | 6 | 0.58162 | 87243 | 0.69863 | 0 | 0.36178 | 4522.25 | 0.46716 | 37372.8 | 64000 | 4522.25 | 18720.75 | 0 | 0 | 1350000 | 0 | 0
2021120315 | 6 | 0.57902 | 86853 | 0.53116 | 0 | 0.37304 | 4663 | 0.43341 | 34672.8 | 64000 | 4663 | 18190 | 0 | 0 | 1350000 | 0 | 0
2021120316 | 6 | 0.58058 | 87087 | 0.32742 | 0 | 0.38386 | 4798.25 | 0.22929 | 18343.2 | 64000 | 4798.25 | 18288.75 | 0 | 0 | 1350000 | 0 | 0
2021120317 | 6 | 0.59742 | 89613 | 0.18842 | 0 | 0.35232 | 4404 | 0.0254 | 2032 | 64000 | 4404 | 2032 | 19177 | 19177 | 1350000 | 19177 | 0
2021120318 | 6 | 0.62476 | 93714 | 0.15866 | 0 | 0.32476 | 4059.5 | 0 | 0 | 64000 | 4059.5 | 0 | 25654.5 | 6477.5 | 1349811.75 | 25654.5 | 0
2021120319 | 6 | 0.62771 | 94156.5 | 0.17422 | 0 | 0.29977 | 3747.125 | 0 | 0 | 64000 | 3747.125 | 0 | 26409.375 | 754.875 | 1348868.625 | 26409.375 | 0
2021120320 | 6 | 0.61951 | 92926.5 | 0.19413 | 0 | 0.2885 | 3606.25 | 0 | 0 | 64000 | 3606.25 | 0 | 25320.25 | -1089.125 | 1349014.625 | 25320.25 | 0
2021120321 | 6 | 0.61005 | 91507.5 | 0.20709 | 0 | 0.26742 | 3342.75 | 0 | 0 | 64000 | 3342.75 | 0 | 24164.75 | -1155.5 | 1350000 | 24164.75 | 0
2021120322 | 6 | 0.5947 | 89205 | 0.20096 | 0 | 0.25526 | 3190.75 | 0 | 0 | 64000 | 3190.75 | 0 | 22014.25 | -2150.5 | 1350000 | 22014.25 | 0
2021120323 | 6 | 0.57209 | 85813.5 | 0.16191 | 0 | 0.24885 | 3110.625 | 0 | 0 | 64000 | 3110.625 | 0 | 18702.875 | -3311.375 | 1350000 | 18702.875 | 0
2021120324 | 6 | 0.54579 | 81868.5 | 0.15494 | 0 | 0.24702 | 3087.75 | 0 | 0 | 64000 | 3087.75 | 0 | 14780.75 | -3922.125 | 1350000 | 14780.75 | 0
2021120401 | 7 | 0.5248 | 78720 | 0.15334 | 0 | 0.24501 | 3062.625 | 0 | 0 | 64000 | 3062.625 | 0 | 11657.375 | -3123.375 | 1350000 | 11657.375 | 0
2021120402 | 7 | 0.51144 | 76716 | 0.11283 | 0 | 0.22938 | 2867.25 | 0 | 0 | 64000 | 2867.25 | 0 | 9848.75 | -1808.625 | 1350000 | 9848.75 | 0
2021120403 | 7 | 0.50379 | 75568.5 | 0.09726 | 0 | 0.21721 | 2715.125 | 0 | 0 | 64000 | 2715.125 | 0 | 8853.375 | -995.375 | 1350000 | 8853.375 | 0
2021120404 | 7 | 0.50285 | 75427.5 | 0.06576 | 0 | 0.21032 | 2629 | 0 | 0 | 64000 | 2629 | 0 | 8798.5 | -54.875 | 1350000 | 8798.5 | 0
2021120405 | 7 | 0.50703 | 76054.5 | 0.04623 | 0 | 0.20772 | 2596.5 | 0 | 0 | 64000 | 2596.5 | 0 | 9458 | 659.5 | 1350000 | 9458 | 0
2021120406 | 7 | 0.52175 | 78262.5 | 0.03892 | 0 | 0.21314 | 2664.25 | 0 | 0 | 64000 | 2664.25 | 0 | 11598.25 | 2140.25 | 1350000 | 11598.25 | 0
2021120407 | 7 | 0.54316 | 81474 | 0.03957 | 0 | 0.23096 | 2887 | 0.00817 | 653.6 | 64000 | 2887 | 653.6 | 13933.4 | 2335.15 | 1350000 | 13933.4 | 0
2021120408 | 7 | 0.567 | 85050 | 0.08073 | 0 | 0.25364 | 3170.5 | 0.14958 | 11966.4 | 64000 | 3170.5 | 11966.4 | 5913.1 | -8020.3 | 1350000 | 5913.1 | 0
2021120409 | 7 | 0.58015 | 87022.5 | 0.13511 | 0 | 0.25779 | 3222.375 | 0.36825 | 29460 | 64000 | 3222.375 | 19800.125 | 0 | -5913.1 | 1350000 | 0 | 0
2021120410 | 7 | 0.57703 | 86554.5 | 0.24238 | 0 | 0.26396 | 3299.5 | 0.42173 | 33738.4 | 64000 | 3299.5 | 19255 | 0 | 0 | 1350000 | 0 | 0
2021120411 | 7 | 0.56441 | 84661.5 | 0.33247 | 0 | 0.25094 | 3136.75 | 0.41706 | 33364.8 | 64000 | 3136.75 | 17524.75 | 0 | 0 | 1350000 | 0 | 0
2021120412 | 7 | 0.55297 | 82945.5 | 0.42437 | 0 | 0.24811 | 3101.375 | 0.40581 | 32464.8 | 64000 | 3101.375 | 15844.125 | 0 | 0 | 1350000 | 0 | 0
2021120413 | 7 | 0.54224 | 81336 | 0.6172 | 0 | 0.22617 | 2827.125 | 0.35161 | 28128.8 | 64000 | 2827.125 | 14508.875 | 0 | 0 | 1350000 | 0 | 0
2021120414 | 7 | 0.53205 | 79807.5 | 0.70378 | 0 | 0.21743 | 2717.875 | 0.25145 | 20116 | 64000 | 2717.875 | 13089.625 | 0 | 0 | 1350000 | 0 | 0
2021120415 | 7 | 0.52907 | 79360.5 | 0.76812 | 0 | 0.21311 | 2663.875 | 0.10628 | 8502.4 | 64000 | 2663.875 | 8502.4 | 4194.225 | 4194.225 | 1350000 | 4194.225 | 0
2021120416 | 7 | 0.53408 | 80112 | 0.7589 | 0 | 0.23465 | 2933.125 | 0.02614 | 2091.2 | 64000 | 2933.125 | 2091.2 | 11087.675 | 6893.45 | 1350000 | 11087.675 | 0
2021120417 | 7 | 0.55599 | 83398.5 | 0.71819 | 0 | 0.23688 | 2961 | 0.0014 | 112 | 64000 | 2961 | 112 | 16325.5 | 5237.825 | 1350000 | 16325.5 | 0
2021120418 | 7 | 0.59191 | 88786.5 | 0.78229 | 0 | 0.25994 | 3249.25 | 0 | 0 | 64000 | 3249.25 | 0 | 21537.25 | 5211.75 | 1350000 | 21537.25 | 0
2021120419 | 7 | 0.60015 | 90022.5 | 0.77863 | 0 | 0.31341 | 3917.625 | 0 | 0 | 64000 | 3917.625 | 0 | 22104.875 | 567.625 | 1350000 | 22104.875 | 0
2021120420 | 7 | 0.59762 | 89643 | 0.86305 | 0 | 0.29562 | 3695.25 | 0 | 0 | 64000 | 3695.25 | 0 | 21947.75 | -157.125 | 1350000 | 21947.75 | 0
2021120421 | 7 | 0.59329 | 88993.5 | 0.81933 | 0 | 0.25441 | 3180.125 | 0 | 0 | 64000 | 3180.125 | 0 | 21813.375 | -134.375 | 1350000 | 21813.375 | 0
2021120422 | 7 | 0.58345 | 87517.5 | 0.71965 | 0 | 0.24104 | 3013 | 0 | 0 | 64000 | 3013 | 0 | 20504.5 | -1308.875 | 1350000 | 20504.5 | 0
2021120423 | 7 | 0.5659 | 84885 | 0.69903 | 0 | 0.22175 | 2771.875 | 0 | 0 | 64000 | 2771.875 | 0 | 18113.125 | -2391.375 | 1350000 | 18113.125 | 0
2021120424 | 7 | 0.54486 | 81729 | 0.51085 | 0 | 0.21816 | 2727 | 0 | 0 | 64000 | 2727 | 0 | 15002 | -3111.125 | 1350000 | 15002 | 0
2021120501 | 1 | 0.52821 | 79231.5 | 0.43758 | 0 | 0.27518 | 3439.75 | 0 | 0 | 64000 | 3439.75 | 0 | 11791.75 | -3210.25 | 1350000 | 11791.75 | 0
2021120502 | 1 | 0.51614 | 77421 | 0.43165 | 0 | 0.27869 | 3483.625 | 0 | 0 | 64000 | 3483.625 | 0 | 9937.375 | -1854.375 | 1350000 | 9937.375 | 0
2021120503 | 1 | 0.51261 | 76891.5 | 0.36282 | 0 | 0.28449 | 3556.125 | 0 | 0 | 64000 | 3556.125 | 0 | 9335.375 | -602 | 1350000 | 9335.375 | 0
2021120504 | 1 | 0.51281 | 76921.5 | 0.3492 | 0 | 0.28731 | 3591.375 | 0 | 0 | 64000 | 3591.375 | 0 | 9330.125 | -5.25 | 1350000 | 9330.125 | 0
2021120505 | 1 | 0.51736 | 77604 | 0.18372 | 0 | 0.24352 | 3044 | 0 | 0 | 64000 | 3044 | 0 | 10560 | 1229.875 | 1350000 | 10560 | 0
2021120506 | 1 | 0.52863 | 79294.5 | 0.06112 | 0 | 0.18896 | 2362 | 0 | 0 | 64000 | 2362 | 0 | 12932.5 | 2372.5 | 1350000 | 12932.5 | 0
2021120507 | 1 | 0.54568 | 81852 | 0.02326 | 0 | 0.17653 | 2206.625 | 0.00175 | 140 | 64000 | 2206.625 | 140 | 15505.375 | 2572.875 | 1350000 | 15505.375 | 0
2021120508 | 1 | 0.56197 | 84295.5 | 0.00931 | 0 | 0.16083 | 2010.375 | 0.04771 | 3816.8 | 64000 | 2010.375 | 3816.8 | 14468.325 | -1037.05 | 1350000 | 14468.325 | 0
2021120509 | 1 | 0.56939 | 85408.5 | 0.0639 | 0 | 0.13664 | 1708 | 0.125 | 10000 | 64000 | 1708 | 10000 | 9700.5 | -4767.825 | 1350000 | 9700.5 | 0
2021120510 | 1 | 0.56629 | 84943.5 | 0.17715 | 0 | 0.13045 | 1630.625 | 0.1682 | 13456 | 64000 | 1630.625 | 13456 | 5856.875 | -3843.625 | 1350000 | 5856.875 | 0
2021120511 | 1 | 0.55938 | 83907 | 0.33494 | 0 | 0.14531 | 1816.375 | 0.18806 | 15044.8 | 64000 | 1816.375 | 15044.8 | 3045.825 | -2811.05 | 1350000 | 3045.825 | 0
2021120512 | 1 | 0.55387 | 83080.5 | 0.48698 | 0 | 0.17586 | 2198.25 | 0.18946 | 15156.8 | 64000 | 2198.25 | 15156.8 | 1725.45 | -1320.375 | 1350000 | 1725.45 | 0
2021120513 | 1 | 0.5525 | 82875 | 0.60731 | 0 | 0.18794 | 2349.25 | 0.18277 | 14621.6 | 64000 | 2349.25 | 14621.6 | 1904.15 | 178.7 | 1350000 | 1904.15 | 0
2021120514 | 1 | 0.5516 | 82740 | 0.69999 | 0 | 0.19727 | 2465.875 | 0.11107 | 8885.6 | 64000 | 2465.875 | 8885.6 | 7388.525 | 5484.375 | 1350000 | 7388.525 | 0
2021120515 | 1 | 0.55159 | 82738.5 | 0.77993 | 0 | 0.20992 | 2624 | 0.08628 | 6902.4 | 64000 | 2624 | 6902.4 | 9212.1 | 1823.575 | 1350000 | 9212.1 | 0
2021120516 | 1 | 0.55853 | 83779.5 | 0.87222 | 0 | 0.23286 | 2910.75 | 0.04366 | 3492.8 | 64000 | 2910.75 | 3492.8 | 13375.95 | 4163.85 | 1350000 | 13375.95 | 0
2021120517 | 1 | 0.58067 | 87100.5 | 0.95285 | 0 | 0.24746 | 3093.25 | 0.00449 | 359.2 | 64000 | 3093.25 | 359.2 | 19648.05 | 6272.1 | 1350000 | 19648.05 | 0
2021120518 | 1 | 0.6145 | 92175 | 0.97921 | 0 | 0.23732 | 2966.5 | 0 | 0 | 64000 | 2966.5 | 0 | 25208.5 | 5560.45 | 1350000 | 25208.5 | 0
2021120519 | 1 | 0.61805 | 92707.5 | 0.98867 | 0 | 0.28532 | 3566.5 | 0 | 0 | 64000 | 3566.5 | 0 | 25141 | -67.5 | 1350000 | 25141 | 0
2021120520 | 1 | 0.61192 | 91788 | 0.99264 | 0 | 0.37892 | 4736.5 | 0 | 0 | 64000 | 4736.5 | 0 | 23051.5 | -2089.5 | 1350000 | 23051.5 | 0
2021120521 | 1 | 0.60084 | 90126 | 0.9975 | 0 | 0.31014 | 3876.75 | 0 | 0 | 64000 | 3876.75 | 0 | 22249.25 | -802.25 | 1350000 | 22249.25 | 0
2021120522 | 1 | 0.57892 | 86838 | 0.99642 | 0 | 0.27033 | 3379.125 | 0 | 0 | 64000 | 3379.125 | 0 | 19458.875 | -2790.375 | 1350000 | 19458.875 | 0
2021120523 | 1 | 0.54736 | 82104 | 0.9935 | 0 | 0.2499 | 3123.75 | 0 | 0 | 64000 | 3123.75 | 0 | 14980.25 | -4478.625 | 1350000 | 14980.25 | 0
2021120524 | 1 | 0.51858 | 77787 | 0.9878 | 0 | 0.25937 | 3242.125 | 0 | 0 | 64000 | 3242.125 | 0 | 10544.875 | -4435.375 | 1350000 | 10544.875 | 0
2021120601 | 2 | 0.49809 | 74713.5 | 0.97498 | 0 | 0.30468 | 3808.5 | 0 | 0 | 64000 | 3808.5 | 0 | 6905 | -3639.875 | 1350000 | 6905 | 0
2021120602 | 2 | 0.48578 | 72867 | 0.95869 | 0 | 0.30724 | 3840.5 | 0 | 0 | 64000 | 3840.5 | 0 | 5026.5 | -1878.5 | 1350000 | 5026.5 | 0
2021120603 | 2 | 0.47997 | 71995.5 | 0.94318 | 0 | 0.30836 | 3854.5 | 0 | 0 | 64000 | 3854.5 | 0 | 4141 | -885.5 | 1350000 | 4141 | 0
2021120604 | 2 | 0.48183 | 72274.5 | 0.93961 | 0 | 0.31818 | 3977.25 | 0 | 0 | 64000 | 3977.25 | 0 | 4297.25 | 156.25 | 1350000 | 4297.25 | 0
2021120605 | 2 | 0.49392 | 74088 | 0.93002 | 0 | 0.3179 | 3973.75 | 0 | 0 | 64000 | 3973.75 | 0 | 6114.25 | 1817 | 1350000 | 6114.25 | 0
2021120606 | 2 | 0.52428 | 78642 | 0.93504 | 0 | 0.30589 | 3823.625 | 0 | 0 | 64000 | 3823.625 | 0 | 10818.375 | 4704.125 | 1350000 | 10818.375 | 0
2021120607 | 2 | 0.57274 | 85911 | 0.93399 | 0 | 0.33398 | 4174.75 | 0.00043 | 34.4 | 64000 | 4174.75 | 34.4 | 17701.85 | 6883.475 | 1350000 | 17701.85 | 0
2021120608 | 2 | 0.60621 | 90931.5 | 0.92145 | 0 | 0.33604 | 4200.5 | 0.01995 | 1596 | 64000 | 4200.5 | 1596 | 21135 | 3433.15 | 1350000 | 21135 | 0
2021120609 | 2 | 0.61411 | 92116.5 | 0.92348 | 0 | 0.3373 | 4216.25 | 0.04875 | 3900 | 64000 | 4216.25 | 3900 | 20000.25 | -1134.75 | 1350000 | 20000.25 | 0
2021120610 | 2 | 0.61661 | 92491.5 | 0.91714 | 0 | 0.32034 | 4004.25 | 0.07126 | 5700.8 | 64000 | 4004.25 | 5700.8 | 18786.45 | -1213.8 | 1350000 | 18786.45 | 0
2021120611 | 2 | 0.61505 | 92257.5 | 0.93072 | 0 | 0.29286 | 3660.75 | 0.09007 | 7205.6 | 64000 | 3660.75 | 7205.6 | 17391.15 | -1395.3 | 1350000 | 17391.15 | 0
2021120612 | 2 | 0.60774 | 91161 | 0.90632 | 0 | 0.25548 | 3193.5 | 0.09575 | 7660 | 64000 | 3193.5 | 7660 | 16307.5 | -1083.65 | 1350000 | 16307.5 | 0
2021120613 | 2 | 0.60419 | 90628.5 | 0.95138 | 0 | 0.22174 | 2771.75 | 0.08444 | 6755.2 | 64000 | 2771.75 | 6755.2 | 17101.55 | 794.05 | 1350000 | 17101.55 | 0
2021120614 | 2 | 0.60296 | 90444 | 0.94344 | 0 | 0.19762 | 2470.25 | 0.0535 | 4280 | 64000 | 2470.25 | 4280 | 19693.75 | 2592.2 | 1350000 | 19693.75 | 0
2021120615 | 2 | 0.60365 | 90547.5 | 0.94406 | 0 | 0.19772 | 2471.5 | 0.03204 | 2563.2 | 64000 | 2471.5 | 2563.2 | 21512.8 | 1819.05 | 1350000 | 21512.8 | 0
2021120616 | 2 | 0.60766 | 91149 | 0.97583 | 0 | 0.19463 | 2432.875 | 0.0136 | 1088 | 64000 | 2432.875 | 1088 | 23628.125 | 2115.325 | 1350000 | 23628.125 | 0
2021120617 | 2 | 0.62822 | 94233 | 0.97864 | 0 | 0.183 | 2287.5 | 0.00042 | 33.6 | 64000 | 2287.5 | 33.6 | 27911.9 | 4283.775 | 1347554.35 | 27911.9 | 0
2021120618 | 2 | 0.66264 | 99396 | 0.9903 | 0 | 0.15631 | 1953.875 | 0 | 0 | 64000 | 1953.875 | 0 | 33442.125 | 5530.225 | 1339578.475 | 33442.125 | 0
2021120619 | 2 | 0.66884 | 100326 | 0.99769 | 0 | 0.13024 | 1628 | 0 | 0 | 64000 | 1628 | 0 | 34698 | 1255.875 | 1330346.725 | 34698 | 0
2021120620 | 2 | 0.66144 | 99216 | 0.99739 | 0 | 0.12549 | 1568.625 | 0 | 0 | 64000 | 1568.625 | 0 | 33647.375 | -1050.625 | 1322165.6 | 33647.375 | 0
2021120621 | 2 | 0.65094 | 97641 | 0.99899 | 0 | 0.15464 | 1933 | 0 | 0 | 64000 | 1933 | 0 | 31708 | -1939.375 | 1315923.85 | 31708 | 0
2021120622 | 2 | 0.63184 | 94776 | 0.9953 | 0 | 0.2111 | 2638.75 | 0 | 0 | 64000 | 2638.75 | 0 | 28137.25 | -3570.75 | 1313252.85 | 28137.25 | 0
2021120623 | 2 | 0.60438 | 90657 | 0.99185 | 0 | 0.26694 | 3336.75 | 0 | 0 | 64000 | 3336.75 | 0 | 23320.25 | -4817 | 1315398.85 | 23320.25 | 0
2021120624 | 2 | 0.57873 | 86809.5 | 0.98878 | 0 | 0.3431 | 4288.75 | 0 | 0 | 64000 | 4288.75 | 0 | 18520.75 | -4799.5 | 1322344.35 | 18520.75 | 0
2021120701 | 3 | 0.55968 | 83952 | 0.98691 | 0 | 0.43528 | 5441 | 0 | 0 | 64000 | 5441 | 0 | 14511 | -4009.75 | 1333299.6 | 14511 | 0
2021120702 | 3 | 0.55056 | 82584 | 0.9746 | 0 | 0.48107 | 6013.375 | 0 | 0 | 64000 | 6013.375 | 0 | 12570.625 | -1940.375 | 1346195.225 | 12570.625 | 0
2021120703 | 3 | 0.54979 | 82468.5 | 0.91832 | 0 | 0.54971 | 6871.375 | 0 | 0 | 64000 | 6871.375 | 0 | 11597.125 | -973.5 | 1350000 | 11597.125 | 0
2021120704 | 3 | 0.55646 | 83469 | 0.88882 | 0 | 0.5937 | 7421.25 | 0 | 0 | 64000 | 7421.25 | 0 | 12047.75 | 450.625 | 1350000 | 12047.75 | 0
2021120705 | 3 | 0.5714 | 85710 | 0.80873 | 0 | 0.60803 | 7600.375 | 0 | 0 | 64000 | 7600.375 | 0 | 14109.625 | 2061.875 | 1350000 | 14109.625 | 0
2021120706 | 3 | 0.60872 | 91308 | 0.70637 | 0 | 0.5979 | 7473.75 | 0 | 0 | 64000 | 7473.75 | 0 | 19834.25 | 5724.625 | 1350000 | 19834.25 | 0
2021120707 | 3 | 0.66288 | 99432 | 0.51573 | 0 | 0.59692 | 7461.5 | 0 | 0 | 64000 | 7461.5 | 0 | 27970.5 | 8136.25 | 1347495.75 | 27970.5 | 0
2021120708 | 3 | 0.6975 | 104625 | 0.37806 | 0 | 0.57985 | 7248.125 | 0.00977 | 781.6 | 64000 | 7248.125 | 781.6 | 32595.275 | 4624.775 | 1340366.725 | 32595.275 | 0
2021120709 | 3 | 0.70062 | 105093 | 0.28587 | 0 | 0.53521 | 6690.125 | 0.03564 | 2851.2 | 64000 | 6690.125 | 2851.2 | 31551.675 | -1043.6 | 1334281.3 | 31551.675 | 0
2021120710 | 3 | 0.69128 | 103692 | 0.25764 | 0 | 0.51062 | 6382.75 | 0.07218 | 5774.4 | 64000 | 6382.75 | 5774.4 | 27534.85 | -4016.825 | 1332212.7 | 27534.85 | 0
2021120711 | 3 | 0.67984 | 101976 | 0.23244 | 0 | 0.46659 | 5832.375 | 0.10091 | 8072.8 | 64000 | 5832.375 | 8072.8 | 24070.825 | -3464.025 | 1333608.125 | 24070.825 | 0
2021120712 | 3 | 0.66797 | 100195.5 | 0.17926 | 0 | 0.44856 | 5607 | 0.1183 | 9464 | 64000 | 5607 | 9464 | 21124.5 | -2946.325 | 1337949.875 | 21124.5 | 0
2021120713 | 3 | 0.66009 | 99013.5 | 0.07863 | 0 | 0.35471 | 4433.875 | 0.11784 | 9427.2 | 64000 | 4433.875 | 9427.2 | 21152.425 | 27.925 | 1342263.7 | 21152.425 | 0
2021120714 | 3 | 0.6562 | 98430 | 0.04272 | 0 | 0.29982 | 3747.75 | 0.09213 | 7370.4 | 64000 | 3747.75 | 7370.4 | 23311.85 | 2159.425 | 1344418.1 | 23311.85 | 0
2021120715 | 3 | 0.65142 | 97713 | 0.06243 | 0 | 0.31949 | 3993.625 | 0.06556 | 5244.8 | 64000 | 3993.625 | 5244.8 | 24474.575 | 1162.725 | 1345409.775 | 24474.575 | 0
2021120716 | 3 | 0.65833 | 98749.5 | 0.05733 | 0 | 0.24405 | 3050.625 | 0.0361 | 2888 | 64000 | 3050.625 | 2888 | 28810.875 | 4336.3 | 1342065.15 | 28810.875 | 0
2021120717 | 3 | 0.68344 | 102516 | 0.03387 | 0 | 0.25878 | 3234.75 | 0.00444 | 355.2 | 64000 | 3234.75 | 355.2 | 34926.05 | 6115.175 | 1332605.35 | 34926.05 | 0
2021120718 | 3 | 0.72389 | 108583.5 | 0.01516 | 0 | 0.14529 | 1816.125 | 0 | 0 | 64000 | 1816.125 | 0 | 42767.375 | 7841.325 | 1315304.225 | 42767.375 | 0
2021120719 | 3 | 0.73013 | 109519.5 | 0.03718 | 0 | 0.12956 | 1619.5 | 0 | 0 | 64000 | 1619.5 | 0 | 43900 | 1132.625 | 1296870.475 | 43900 | 0
2021120720 | 3 | 0.72552 | 108828 | 0.06912 | 0 | 0.11137 | 1392.125 | 0 | 0 | 64000 | 1392.125 | 0 | 43435.875 | -464.125 | 1278900.85 | 43435.875 | 0
2021120721 | 3 | 0.7139 | 107085 | 0.08035 | 0 | 0.08105 | 1013.125 | 0 | 0 | 64000 | 1013.125 | 0 | 42071.875 | -1364 | 1262295.225 | 42071.875 | 0
2021120722 | 3 | 0.69165 | 103747.5 | 0.05089 | 0 | 0.06604 | 825.5 | 0 | 0 | 64000 | 825.5 | 0 | 38922 | -3149.875 | 1248839.475 | 38922 | 0
2021120723 | 3 | 0.65707 | 98560.5 | 0.01947 | 0 | 0.05199 | 649.875 | 0 | 0 | 64000 | 649.875 | 0 | 33910.625 | -5011.375 | 1240395.1 | 33910.625 | 0
2021120724 | 3 | 0.62288 | 93432 | 0.02909 | 0 | 0.07652 | 956.5 | 0 | 0 | 64000 | 956.5 | 0 | 28475.5 | -5435.125 | 1237385.85 | 28475.5 | 0
2021120801 | 4 | 0.5983 | 89745 | 0.09621 | 0 | 0.09356 | 1169.5 | 0 | 0 | 64000 | 1169.5 | 0 | 24575.5 | -3900 | 1238276.6 | 24575.5 | 0
2021120802 | 4 | 0.58426 | 87639 | 0.14616 | 0 | 0.09335 | 1166.875 | 0 | 0 | 64000 | 1166.875 | 0 | 22472.125 | -2103.375 | 1241270.725 | 22472.125 | 0
2021120803 | 4 | 0.57771 | 86656.5 | 0.18517 | 0 | 0.08218 | 1027.25 | 0 | 0 | 64000 | 1027.25 | 0 | 21629.25 | -842.875 | 1245107.725 | 21629.25 | 0
2021120804 | 4 | 0.57807 | 86710.5 | 0.17649 | 0 | 0.05165 | 645.625 | 0 | 0 | 64000 | 645.625 | 0 | 22064.875 | 435.625 | 1248509.1 | 22064.875 | 0
2021120805 | 4 | 0.58897 | 88345.5 | 0.18 | 0 | 0.03393 | 424.125 | 0 | 0 | 64000 | 424.125 | 0 | 23921.375 | 1856.5 | 1250053.975 | 23921.375 | 0
2021120806 | 4 | 0.61886 | 92829 | 0.087 | 0 | 0.04138 | 517.25 | 0 | 0 | 64000 | 517.25 | 0 | 28311.75 | 4390.375 | 1247208.475 | 28311.75 | 0
2021120807 | 4 | 0.66509 | 99763.5 | 0.02801 | 0 | 0.04498 | 562.25 | 0.00058 | 46.4 | 64000 | 562.25 | 46.4 | 35154.85 | 6843.1 | 1237519.875 | 35154.85 | 0
2021120808 | 4 | 0.69701 | 104551.5 | 0.07916 | 0 | 0.0328 | 410 | 0.03262 | 2609.6 | 64000 | 410 | 2609.6 | 37531.9 | 2377.05 | 1225454.225 | 37531.9 | 0
2021120809 | 4 | 0.70319 | 105478.5 | 0.15839 | 0 | 0.02014 | 251.75 | 0.13704 | 10963.2 | 64000 | 251.75 | 10963.2 | 30263.55 | -7268.35 | 1220656.925 | 30263.55 | 0
2021120810 | 4 | 0.70182 | 105273 | 0.2531 | 0 | 0.0266 | 332.5 | 0.23706 | 18964.8 | 64000 | 332.5 | 18964.8 | 21975.7 | -8287.85 | 1224147.475 | 21975.7 | 0
2021120811 | 4 | 0.69579 | 104368.5 | 0.27137 | 0 | 0.04086 | 510.75 | 0.39103 | 31282.4 | 64000 | 510.75 | 31282.4 | 8575.35 | -13400.35 | 1241038.375 | 8575.35 | 0
2021120812 | 4 | 0.68849 | 103273.5 | 0.21912 | 0 | 0.06877 | 859.625 | 0.43431 | 34744.8 | 64000 | 859.625 | 34744.8 | 3669.075 | -4906.275 | 1262835.55 | 3669.075 | 0
2021120813 | 4 | 0.67545 | 101317.5 | 0.24756 | 0 | 0.09501 | 1187.625 | 0.46049 | 36839.2 | 64000 | 1187.625 | 36129.875 | 0 | -3669.075 | 1288301.8 | 0 | 0
2021120814 | 4 | 0.66299 | 99448.5 | 0.21593 | 0 | 0.12976 | 1622 | 0.47548 | 38038.4 | 64000 | 1622 | 33826.5 | 0 | 0 | 1313768.05 | 0 | 0
2021120815 | 4 | 0.65585 | 98377.5 | 0.22204 | 0 | 0.17607 | 2200.875 | 0.40074 | 32059.2 | 64000 | 2200.875 | 32059.2 | 117.425 | 117.425 | 1339116.875 | 117.425 | 0
2021120816 | 4 | 0.65784 | 98676 | 0.38853 | 0 | 0.20229 | 2528.625 | 0.19729 | 15783.2 | 64000 | 2528.625 | 15783.2 | 16364.175 | 16246.75 | 1348218.95 | 16364.175 | 0
2021120817 | 4 | 0.67795 | 101692.5 | 0.5422 | 0 | 0.25296 | 3162 | 0.02064 | 1651.2 | 64000 | 3162 | 1651.2 | 32879.3 | 16515.125 | 1340805.9 | 32879.3 | 0
2021120818 | 4 | 0.71649 | 107473.5 | 0.64468 | 0 | 0.28689 | 3586.125 | 0 | 0 | 64000 | 3586.125 | 0 | 39887.375 | 7008.075 | 1326384.775 | 39887.375 | 0
2021120819 | 4 | 0.72163 | 108244.5 | 0.73005 | 0 | 0.32466 | 4058.25 | 0 | 0 | 64000 | 4058.25 | 0 | 40186.25 | 298.875 | 1311664.775 | 40186.25 | 0
2021120820 | 4 | 0.71784 | 107676 | 0.76463 | 0 | 0.36967 | 4620.875 | 0 | 0 | 64000 | 4620.875 | 0 | 39055.125 | -1131.125 | 1298075.9 | 39055.125 | 0
2021120821 | 4 | 0.70728 | 106092 | 0.80921 | 0 | 0.42904 | 5363 | 0 | 0 | 64000 | 5363 | 0 | 36729 | -2326.125 | 1286813.15 | 36729 | 0
2021120822 | 4 | 0.68649 | 102973.5 | 0.84885 | 0 | 0.44497 | 5562.125 | 0 | 0 | 64000 | 5562.125 | 0 | 33411.375 | -3317.625 | 1278868.025 | 33411.375 | 0
2021120823 | 4 | 0.65394 | 98091 | 0.85496 | 0 | 0.47068 | 5883.5 | 0 | 0 | 64000 | 5883.5 | 0 | 28207.5 | -5203.875 | 1276126.775 | 28207.5 | 0
2021120824 | 4 | 0.62403 | 93604.5 | 0.66574 | 0 | 0.4974 | 6217.5 | 0 | 0 | 64000 | 6217.5 | 0 | 23387 | -4820.5 | 1278206.025 | 23387 | 0
2021120901 | 5 | 0.606 | 90900 | 0.56982 | 0 | 0.50262 | 6282.75 | 0 | 0 | 64000 | 6282.75 | 0 | 20617.25 | -2769.75 | 1283055.025 | 20617.25 | 0
2021120902 | 5 | 0.59676 | 89514 | 0.61643 | 0 | 0.49916 | 6239.5 | 0 | 0 | 64000 | 6239.5 | 0 | 19274.5 | -1342.75 | 1289246.775 | 19274.5 | 0
2021120903 | 5 | 0.59501 | 89251.5 | 0.59161 | 0 | 0.47112 | 5889 | 0 | 0 | 64000 | 5889 | 0 | 19362.5 | 88 | 1295350.525 | 19362.5 | 0
2021120904 | 5 | 0.59936 | 89904 | 0.43393 | 0 | 0.43865 | 5483.125 | 0 | 0 | 64000 | 5483.125 | 0 | 20420.875 | 1058.375 | 1300395.9 | 20420.875 | 0
2021120905 | 5 | 0.61512 | 92268 | 0.33367 | 0 | 0.37329 | 4666.125 | 0 | 0 | 64000 | 4666.125 | 0 | 23601.875 | 3181 | 1302260.275 | 23601.875 | 0
2021120906 | 5 | 0.64991 | 97486.5 | 0.18763 | 0 | 0.28383 | 3547.875 | 0 | 0 | 64000 | 3547.875 | 0 | 29938.625 | 6336.75 | 1297787.9 | 29938.625 | 0
2021120907 | 5 | 0.70267 | 105400.5 | 0.13046 | 0 | 0.23331 | 2916.375 | 0.00503 | 402.4 | 64000 | 2916.375 | 402.4 | 38081.725 | 8143.1 | 1285172.425 | 38081.725 | 0
2021120908 | 5 | 0.73333 | 109999.5 | 0.19064 | 0 | 0.20711 | 2588.875 | 0.14437 | 11549.6 | 64000 | 2588.875 | 11549.6 | 31861.025 | -6220.7 | 1278777.65 | 31861.025 | 0
2021120909 | 5 | 0.72972 | 109458 | 0.15141 | 0 | 0.19371 | 2421.375 | 0.40468 | 32374.4 | 64000 | 2421.375 | 32374.4 | 10662.225 | -21198.8 | 1293581.675 | 10662.225 | 0
2021120910 | 5 | 0.71018 | 106527 | 0.08625 | 0 | 0.18742 | 2342.75 | 0.49464 | 39571.2 | 64000 | 2342.75 | 39571.2 | 613.05 | -10049.175 | 1318434.875 | 613.05 | 0
2021120911 | 5 | 0.69046 | 103569 | 0.05316 | 0 | 0.19696 | 2462 | 0.49475 | 39580 | 64000 | 2462 | 37107 | 0 | -613.05 | 1343901.125 | 0 | 0
2021120912 | 5 | 0.6753 | 101295 | 0.03788 | 0 | 0.21058 | 2632.25 | 0.48378 | 38702.4 | 64000 | 2632.25 | 34662.75 | 0 | 0 | 1350000 | 0 | 0
2021120913 | 5 | 0.66697 | 100045.5 | 0.00568 | 0 | 0.22788 | 2848.5 | 0.4787 | 38296 | 64000 | 2848.5 | 33197 | 0 | 0 | 1350000 | 0 | 0
2021120914 | 5 | 0.66237 | 99355.5 | 0.01924 | 0 | 0.22412 | 2801.5 | 0.47103 | 37682.4 | 64000 | 2801.5 | 32554 | 0 | 0 | 1350000 | 0 | 0
2021120915 | 5 | 0.65855 | 98782.5 | 0.21448 | 0 | 0.20937 | 2617.125 | 0.43206 | 34564.8 | 64000 | 2617.125 | 32165.375 | 0 | 0 | 1350000 | 0 | 0
2021120916 | 5 | 0.65956 | 98934 | 0.30948 | 0 | 0.20683 | 2585.375 | 0.21483 | 17186.4 | 64000 | 2585.375 | 17186.4 | 15162.225 | 15162.225 | 1350000 | 15162.225 | 0
2021120917 | 5 | 0.67662 | 101493 | 0.36423 | 0 | 0.20334 | 2541.75 | 0.01905 | 1524 | 64000 | 2541.75 | 1524 | 33427.25 | 18265.025 | 1342039 | 33427.25 | 0
2021120918 | 5 | 0.70927 | 106390.5 | 0.51212 | 0 | 0.19318 | 2414.75 | 0 | 0 | 64000 | 2414.75 | 0 | 39975.75 | 6548.5 | 1327529.5 | 39975.75 | 0
2021120919 | 5 | 0.71159 | 106738.5 | 0.6709 | 0 | 0.18819 | 2352.375 | 0 | 0 | 64000 | 2352.375 | 0 | 40386.125 | 410.375 | 1312609.625 | 40386.125 | 0
2021120920 | 5 | 0.70223 | 105334.5 | 0.83747 | 0 | 0.18862 | 2357.75 | 0 | 0 | 64000 | 2357.75 | 0 | 38976.75 | -1409.375 | 1299099.125 | 38976.75 | 0
2021120921 | 5 | 0.69046 | 103569 | 0.91587 | 0 | 0.19704 | 2463 | 0 | 0 | 64000 | 2463 | 0 | 37106 | -1870.75 | 1287459.375 | 37106 | 0
2021120922 | 5 | 0.66728 | 100092 | 0.93312 | 0 | 0.21809 | 2726.125 | 0 | 0 | 64000 | 2726.125 | 0 | 33365.875 | -3740.125 | 1279559.75 | 33365.875 | 0
2021120923 | 5 | 0.63167 | 94750.5 | 0.93861 | 0 | 0.27342 | 3417.75 | 0 | 0 | 64000 | 3417.75 | 0 | 27332.75 | -6033.125 | 1277693.25 | 27332.75 | 0
2021120924 | 5 | 0.59833 | 89749.5 | 0.90663 | 0 | 0.32216 | 4027 | 0 | 0 | 64000 | 4027 | 0 | 21722.5 | -5610.25 | 1281437 | 21722.5 | 0
2021121001 | 6 | 0.57294 | 85941 | 0.85023 | 0 | 0.35011 | 4376.375 | 0 | 0 | 64000 | 4376.375 | 0 | 17564.625 | -4157.875 | 1289338.625 | 17564.625 | 0
2021121002 | 6 | 0.55586 | 83379 | 0.80884 | 0 | 0.40992 | 5124 | 0 | 0 | 64000 | 5124 | 0 | 14255 | -3309.625 | 1300549.875 | 14255 | 0
2021121003 | 6 | 0.54657 | 81985.5 | 0.79622 | 0 | 0.43428 | 5428.5 | 0 | 0 | 64000 | 5428.5 | 0 | 12557 | -1698 | 1313459.125 | 12557 | 0
2021121004 | 6 | 0.54197 | 81295.5 | 0.7662 | 0 | 0.42393 | 5299.125 | 0 | 0 | 64000 | 5299.125 | 0 | 11996.375 | -560.625 | 1326929 | 11996.375 | 0
2021121005 | 6 | 0.54994 | 82491 | 0.67701 | 0 | 0.41316 | 5164.5 | 0 | 0 | 64000 | 5164.5 | 0 | 13326.5 | 1330.125 | 1339068.75 | 13326.5 | 0
2021121006 | 6 | 0.57579 | 86368.5 | 0.60887 | 0 | 0.41184 | 5148 | 0.00062 | 49.6 | 64000 | 5148 | 49.6 | 17170.9 | 3844.4 | 1347364.1 | 17170.9 | 0
2021121007 | 6 | 0.61937 | 92905.5 | 0.56781 | 0 | 0.43024 | 5378 | 0.00338 | 270.4 | 64000 | 5378 | 270.4 | 23257.1 | 6086.2 | 1349573.25 | 23257.1 | 0
2021121008 | 6 | 0.6508 | 97620 | 0.46595 | 0 | 0.45608 | 5701 | 0.11279 | 9023.2 | 64000 | 5701 | 9023.2 | 18895.8 | -4361.3 | 1350000 | 18895.8 | 0
2021121009 | 6 | 0.65407 | 98110.5 | 0.40067 | 0 | 0.46344 | 5793 | 0.30759 | 24607.2 | 64000 | 5793 | 24607.2 | 3710.3 | -15185.5 | 1350000 | 3710.3 | 0
2021121010 | 6 | 0.64906 | 97359 | 0.34784 | 0 | 0.45138 | 5642.25 | 0.34417 | 27533.6 | 64000 | 5642.25 | 27533.6 | 183.15 | -3527.15 | 1350000 | 183.15 | 0
2021121011 | 6 | 0.63824 | 95736 | 0.20149 | 0 | 0.44035 | 5504.375 | 0.3692 | 29536 | 64000 | 5504.375 | 26231.625 | 0 | -183.15 | 1350000 | 0 | 0
2021121012 | 6 | 0.62667 | 94000.5 | 0.10502 | 0 | 0.46631 | 5828.875 | 0.36183 | 28946.4 | 64000 | 5828.875 | 24171.625 | 0 | 0 | 1350000 | 0 | 0
2021121013 | 6 | 0.61635 | 92452.5 | 0.08993 | 0 | 0.52124 | 6515.5 | 0.38394 | 30715.2 | 64000 | 6515.5 | 21937 | 0 | 0 | 1350000 | 0 | 0
2021121014 | 6 | 0.60913 | 91369.5 | 0.11102 | 0 | 0.58085 | 7260.625 | 0.38296 | 30636.8 | 64000 | 7260.625 | 20108.875 | 0 | 0 | 1350000 | 0 | 0
2021121015 | 6 | 0.60125 | 90187.5 | 0.06332 | 0 | 0.60128 | 7516 | 0.29977 | 23981.6 | 64000 | 7516 | 18671.5 | 0 | 0 | 1350000 | 0 | 0
2021121016 | 6 | 0.60282 | 90423 | 0.12146 | 0 | 0.60351 | 7543.875 | 0.12848 | 10278.4 | 64000 | 7543.875 | 10278.4 | 8600.725 | 8600.725 | 1350000 | 8600.725 | 0
2021121017 | 6 | 0.62151 | 93226.5 | 0.26137 | 0 | 0.63666 | 7958.25 | 0.01005 | 804 | 64000 | 7958.25 | 804 | 20464.25 | 11863.525 | 1350000 | 20464.25 | 0
2021121018 | 6 | 0.6468 | 97020 | 0.377 | 0 | 0.67007 | 8375.875 | 0 | 0 | 64000 | 8375.875 | 0 | 24644.125 | 4179.875 | 1350000 | 24644.125 | 0
2021121019 | 6 | 0.64092 | 96138 | 0.4771 | 0 | 0.69952 | 8744 | 0 | 0 | 64000 | 8744 | 0 | 23394 | -1250.125 | 1350000 | 23394 | 0
2021121020 | 6 | 0.62833 | 94249.5 | 0.55329 | 0 | 0.73932 | 9241.5 | 0 | 0 | 64000 | 9241.5 | 0 | 21008 | -2386 | 1350000 | 21008 | 0
2021121021 | 6 | 0.61328 | 91992 | 0.64617 | 0 | 0.76132 | 9516.5 | 0 | 0 | 64000 | 9516.5 | 0 | 18475.5 | -2532.5 | 1350000 | 18475.5 | 0
2021121022 | 6 | 0.59378 | 89067 | 0.76993 | 0 | 0.76498 | 9562.25 | 0 | 0 | 64000 | 9562.25 | 0 | 15504.75 | -2970.75 | 1350000 | 15504.75 | 0
2021121023 | 6 | 0.56605 | 84907.5 | 0.80081 | 0 | 0.78768 | 9846 | 0 | 0 | 64000 | 9846 | 0 | 11061.5 | -4443.25 | 1350000 | 11061.5 | 0
2021121024 | 6 | 0.53395 | 80092.5 | 0.83323 | 0 | 0.8048 | 10060 | 0 | 0 | 64000 | 10060 | 0 | 6032.5 | -5029 | 1350000 | 6032.5 | 0
2021121101 | 7 | 0.50709 | 76063.5 | 0.87112 | 0 | 0.83115 | 10389.375 | 0 | 0 | 64000 | 10389.375 | 0 | 1674.125 | -4358.375 | 1350000 | 1674.125 | 0
2021121102 | 7 | 0.48851 | 73276.5 | 0.89386 | 0 | 0.83421 | 10427.625 | 0 | 0 | 64000 | 9276.5 | 0 | 0 | -1674.125 | 1350000 | 0 | 0
2021121103 | 7 | 0.47791 | 71686.5 | 0.91519 | 0 | 0.83828 | 10478.5 | 0 | 0 | 64000 | 7686.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021121104 | 7 | 0.47197 | 70795.5 | 0.93744 | 0 | 0.84474 | 10559.25 | 0 | 0 | 64000 | 6795.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021121105 | 7 | 0.47121 | 70681.5 | 0.97128 | 0 | 0.82282 | 10285.25 | 0 | 0 | 64000 | 6681.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021121106 | 7 | 0.48094 | 72141 | 0.97459 | 0 | 0.80038 | 10004.75 | 0.00022 | 17.6 | 64000 | 8141 | 0 | 0 | 0 | 1350000 | 0 | 0
2021121107 | 7 | 0.4985 | 74775 | 0.98233 | 0 | 0.75724 | 9465.5 | 0.00301 | 240.8 | 64000 | 9465.5 | 240.8 | 1068.7 | 1068.7 | 1350000 | 1068.7 | 0
2021121108 | 7 | 0.51919 | 77878.5 | 0.9637 | 0 | 0.74242 | 9280.25 | 0.08595 | 6876 | 64000 | 9280.25 | 4598.25 | 0 | -1068.7 | 1350000 | 0 | 0
2021121109 | 7 | 0.53832 | 80748 | 0.943 | 0 | 0.75401 | 9425.125 | 0.29612 | 23689.6 | 64000 | 9425.125 | 7322.875 | 0 | 0 | 1350000 | 0 | 0
2021121110 | 7 | 0.55317 | 82975.5 | 0.95853 | 0 | 0.75461 | 9432.625 | 0.37048 | 29638.4 | 64000 | 9432.625 | 9542.875 | 0 | 0 | 1350000 | 0 | 0
2021121111 | 7 | 0.56235 | 84352.5 | 0.94432 | 0 | 0.73369 | 9171.125 | 0.38687 | 30949.6 | 64000 | 9171.125 | 11181.375 | 0 | 0 | 1350000 | 0 | 0
2021121112 | 7 | 0.56223 | 84334.5 | 0.91601 | 0 | 0.65927 | 8240.875 | 0.36262 | 29009.6 | 64000 | 8240.875 | 12093.625 | 0 | 0 | 1350000 | 0 | 0
2021121113 | 7 | 0.55878 | 83817 | 0.96772 | 0 | 0.6229 | 7786.25 | 0.31885 | 25508 | 64000 | 7786.25 | 12030.75 | 0 | 0 | 1350000 | 0 | 0
2021121114 | 7 | 0.5523 | 82845 | 0.99798 | 0 | 0.63371 | 7921.375 | 0.23463 | 18770.4 | 64000 | 7921.375 | 10923.625 | 0 | 0 | 1350000 | 0 | 0
2021121115 | 7 | 0.54939 | 82408.5 | 0.99577 | 0 | 0.70548 | 8818.5 | 0.11619 | 9295.2 | 64000 | 8818.5 | 9295.2 | 294.8 | 294.8 | 1350000 | 294.8 | 0
2021121116 | 7 | 0.55256 | 82884 | 0.99659 | 0 | 0.7539 | 9423.75 | 0.04839 | 3871.2 | 64000 | 9423.75 | 3871.2 | 5589.05 | 5294.25 | 1350000 | 5589.05 | 0
2021121117 | 7 | 0.56882 | 85323 | 0.99417 | 0 | 0.74692 | 9336.5 | 0.00324 | 259.2 | 64000 | 9336.5 | 259.2 | 11727.3 | 6138.25 | 1350000 | 11727.3 | 0
2021121118 | 7 | 0.59322 | 88983 | 0.98159 | 0 | 0.72108 | 9013.5 | 0 | 0 | 64000 | 9013.5 | 0 | 15969.5 | 4242.2 | 1350000 | 15969.5 | 0
2021121119 | 7 | 0.59468 | 89202 | 0.97236 | 0 | 0.69825 | 8728.125 | 0 | 0 | 64000 | 8728.125 | 0 | 16473.875 | 504.375 | 1350000 | 16473.875 | 0
2021121120 | 7 | 0.58799 | 88198.5 | 0.98497 | 0 | 0.74662 | 9332.75 | 0 | 0 | 64000 | 9332.75 | 0 | 14865.75 | -1608.125 | 1350000 | 14865.75 | 0
2021121121 | 7 | 0.57836 | 86754 | 0.99361 | 0 | 0.77186 | 9648.25 | 0 | 0 | 64000 | 9648.25 | 0 | 13105.75 | -1760 | 1350000 | 13105.75 | 0
2021121122 | 7 | 0.56502 | 84753 | 0.99366 | 0 | 0.78713 | 9839.125 | 0 | 0 | 64000 | 9839.125 | 0 | 10913.875 | -2191.875 | 1350000 | 10913.875 | 0
2021121123 | 7 | 0.54596 | 81894 | 0.9907 | 0 | 0.79887 | 9985.875 | 0 | 0 | 64000 | 9985.875 | 0 | 7908.125 | -3005.75 | 1350000 | 7908.125 | 0
2021121124 | 7 | 0.52411 | 78616.5 | 0.99067 | 0 | 0.79289 | 9911.125 | 0 | 0 | 64000 | 9911.125 | 0 | 4705.375 | -3202.75 | 1350000 | 4705.375 | 0
2021121201 | 1 | 0.50795 | 76192.5 | 0.98464 | 0 | 0.79343 | 9917.875 | 0 | 0 | 64000 | 9917.875 | 0 | 2274.625 | -2430.75 | 1350000 | 2274.625 | 0
2021121202 | 1 | 0.49747 | 74620.5 | 0.97889 | 0 | 0.77402 | 9675.25 | 0 | 0 | 64000 | 9675.25 | 0 | 945.25 | -1329.375 | 1350000 | 945.25 | 0
2021121203 | 1 | 0.49376 | 74064 | 0.97359 | 0 | 0.75044 | 9380.5 | 0 | 0 | 64000 | 9380.5 | 0 | 683.5 | -261.75 | 1350000 | 683.5 | 0
2021121204 | 1 | 0.49467 | 74200.5 | 0.95798 | 0 | 0.74577 | 9322.125 | 0 | 0 | 64000 | 9322.125 | 0 | 878.375 | 194.875 | 1350000 | 878.375 | 0
2021121205 | 1 | 0.50106 | 75159 | 0.94393 | 0 | 0.70519 | 8814.875 | 0 | 0 | 64000 | 8814.875 | 0 | 2344.125 | 1465.75 | 1350000 | 2344.125 | 0
2021121206 | 1 | 0.51351 | 77026.5 | 0.96453 | 0 | 0.64685 | 8085.625 | 0.0004 | 32 | 64000 | 8085.625 | 32 | 4908.875 | 2564.75 | 1350000 | 4908.875 | 0
2021121207 | 1 | 0.53305 | 79957.5 | 0.96088 | 0 | 0.64924 | 8115.5 | 0.00353 | 282.4 | 64000 | 8115.5 | 282.4 | 7559.6 | 2650.725 | 1350000 | 7559.6 | 0
2021121208 | 1 | 0.55724 | 83586 | 0.91932 | 0 | 0.72405 | 9050.625 | 0.11972 | 9577.6 | 64000 | 9050.625 | 9577.6 | 957.775 | -6601.825 | 1350000 | 957.775 | 0
2021121209 | 1 | 0.56838 | 85257 | 0.85352 | 0 | 0.72237 | 9029.625 | 0.35051 | 28040.8 | 64000 | 9029.625 | 12227.375 | 0 | -957.775 | 1350000 | 0 | 0
2021121210 | 1 | 0.5633 | 84495 | 0.86365 | 0 | 0.65276 | 8159.5 | 0.41801 | 33440.8 | 64000 | 8159.5 | 12335.5 | 0 | 0 | 1350000 | 0 | 0
2021121211 | 1 | 0.55368 | 83052 | 0.91362 | 0 | 0.56022 | 7002.75 | 0.40559 | 32447.2 | 64000 | 7002.75 | 12049.25 | 0 | 0 | 1350000 | 0 | 0
2021121212 | 1 | 0.54536 | 81804 | 0.89914 | 0 | 0.41072 | 5134 | 0.38795 | 31036 | 64000 | 5134 | 12670 | 0 | 0 | 1350000 | 0 | 0
2021121213 | 1 | 0.54004 | 81006 | 0.81559 | 0 | 0.36349 | 4543.625 | 0.39058 | 31246.4 | 64000 | 4543.625 | 12462.375 | 0 | 0 | 1350000 | 0 | 0
2021121214 | 1 | 0.53442 | 80163 | 0.74336 | 0 | 0.33701 | 4212.625 | 0.40232 | 32185.6 | 64000 | 4212.625 | 11950.375 | 0 | 0 | 1350000 | 0 | 0
2021121215 | 1 | 0.53291 | 79936.5 | 0.70913 | 0 | 0.27962 | 3495.25 | 0.36047 | 28837.6 | 64000 | 3495.25 | 12441.25 | 0 | 0 | 1350000 | 0 | 0
2021121216 | 1 | 0.54209 | 81313.5 | 0.6001 | 0 | 0.25709 | 3213.625 | 0.16708 | 13366.4 | 64000 | 3213.625 | 13366.4 | 733.475 | 733.475 | 1350000 | 733.475 | 0
2021121217 | 1 | 0.57252 | 85878 | 0.47274 | 0 | 0.26326 | 3290.75 | 0.00819 | 655.2 | 64000 | 3290.75 | 655.2 | 17932.05 | 17198.575 | 1350000 | 17932.05 | 0
2021121218 | 1 | 0.6231 | 93465 | 0.55916 | 0 | 0.30994 | 3874.25 | 0 | 0 | 64000 | 3874.25 | 0 | 25590.75 | 7658.7 | 1349875.5 | 25590.75 | 0
2021121219 | 1 | 0.64289 | 96433.5 | 0.75215 | 0 | 0.37801 | 4725.125 | 0 | 0 | 64000 | 4725.125 | 0 | 27708.375 | 2117.625 | 1347633.375 | 27708.375 | 0
2021121220 | 1 | 0.6455 | 96825 | 0.87137 | 0 | 0.51144 | 6393 | 0 | 0 | 64000 | 6393 | 0 | 26432 | -1276.375 | 1346667.625 | 26432 | 0
2021121221 | 1 | 0.64312 | 96468 | 0.89277 | 0 | 0.63716 | 7964.5 | 0 | 0 | 64000 | 7964.5 | 0 | 24503.5 | -1928.5 | 1347630.375 | 24503.5 | 0
2021121222 | 1 | 0.63133 | 94699.5 | 0.90711 | 0 | 0.71926 | 8990.75 | 0 | 0 | 64000 | 8990.75 | 0 | 21708.75 | -2794.75 | 1350000 | 21708.75 | 0
2021121223 | 1 | 0.60902 | 91353 | 0.88505 | 0 | 0.77847 | 9730.875 | 0 | 0 | 64000 | 9730.875 | 0 | 17622.125 | -4086.625 | 1350000 | 17622.125 | 0
2021121224 | 1 | 0.58504 | 87756 | 0.89165 | 0 | 0.79005 | 9875.625 | 0 | 0 | 64000 | 9875.625 | 0 | 13880.375 | -3741.75 | 1350000 | 13880.375 | 0
2021121301 | 2 | 0.56867 | 85300.5 | 0.92571 | 0 | 0.78984 | 9873 | 0 | 0 | 64000 | 9873 | 0 | 11427.5 | -2452.875 | 1350000 | 11427.5 | 0
2021121302 | 2 | 0.56156 | 84234 | 0.94772 | 0 | 0.78329 | 9791.125 | 0 | 0 | 64000 | 9791.125 | 0 | 10442.875 | -984.625 | 1350000 | 10442.875 | 0
2021121303 | 2 | 0.56144 | 84216 | 0.90611 | 0 | 0.76323 | 9540.375 | 0 | 0 | 64000 | 9540.375 | 0 | 10675.625 | 232.75 | 1350000 | 10675.625 | 0
2021121304 | 2 | 0.56634 | 84951 | 0.86115 | 0 | 0.70017 | 8752.125 | 0 | 0 | 64000 | 8752.125 | 0 | 12198.875 | 1523.25 | 1350000 | 12198.875 | 0
2021121305 | 2 | 0.58179 | 87268.5 | 0.81713 | 0 | 0.65068 | 8133.5 | 0 | 0 | 64000 | 8133.5 | 0 | 15135 | 2936.125 | 1350000 | 15135 | 0
2021121306 | 2 | 0.61796 | 92694 | 0.82433 | 0 | 0.59555 | 7444.375 | 0 | 0 | 64000 | 7444.375 | 0 | 21249.625 | 6114.625 | 1350000 | 21249.625 | 0
2021121307 | 2 | 0.67192 | 100788 | 0.85073 | 0 | 0.56924 | 7115.5 | 0.00124 | 99.2 | 64000 | 7115.5 | 99.2 | 29573.3 | 8323.675 | 1345892.95 | 29573.3 | 0
2021121308 | 2 | 0.70666 | 105999 | 0.82167 | 0 | 0.51978 | 6497.25 | 0.09929 | 7943.2 | 64000 | 6497.25 | 7943.2 | 27558.55 | -2014.75 | 1343800.65 | 27558.55 | 0
2021121309 | 2 | 0.69914 | 104871 | 0.83046 | 0 | 0.50097 | 6262.125 | 0.30448 | 24358.4 | 64000 | 6262.125 | 24358.4 | 10250.475 | -17308.075 | 1350000 | 10250.475 | 0
2021121310 | 2 | 0.6678 | 100170 | 0.75236 | 0 | 0.46768 | 5846 | 0.38923 | 31138.4 | 64000 | 5846 | 30324 | 0 | -10250.475 | 1350000 | 0 | 0
2021121311 | 2 | 0.64041 | 96061.5 | 0.62553 | 0 | 0.39166 | 4895.75 | 0.3956 | 31648 | 64000 | 4895.75 | 27165.75 | 0 | 0 | 1350000 | 0 | 0
2021121312 | 2 | 0.62018 | 93027 | 0.58994 | 0 | 0.31383 | 3922.875 | 0.39083 | 31266.4 | 64000 | 3922.875 | 25104.125 | 0 | 0 | 1350000 | 0 | 0
2021121313 | 2 | 0.6046 | 90690 | 0.62528 | 0 | 0.25075 | 3134.375 | 0.42383 | 33906.4 | 64000 | 3134.375 | 23555.625 | 0 | 0 | 1350000 | 0 | 0
2021121314 | 2 | 0.59526 | 89289 | 0.59057 | 0 | 0.20599 | 2574.875 | 0.42306 | 33844.8 | 64000 | 2574.875 | 22714.125 | 0 | 0 | 1350000 | 0 | 0
2021121315 | 2 | 0.5882 | 88230 | 0.6324 | 0 | 0.2304 | 2880 | 0.36336 | 29068.8 | 64000 | 2880 | 21350 | 0 | 0 | 1350000 | 0 | 0
2021121316 | 2 | 0.59194 | 88791 | 0.61744 | 0 | 0.23266 | 2908.25 | 0.17427 | 13941.6 | 64000 | 2908.25 | 13941.6 | 7941.15 | 7941.15 | 1350000 | 7941.15 | 0
2021121317 | 2 | 0.61628 | 92442 | 0.59271 | 0 | 0.20557 | 2569.625 | 0.01558 | 1246.4 | 64000 | 2569.625 | 1246.4 | 24625.975 | 16684.825 | 1350000 | 24625.975 | 0
2021121318 | 2 | 0.66159 | 99238.5 | 0.76686 | 0 | 0.21084 | 2635.5 | 0 | 0 | 64000 | 2635.5 | 0 | 32603 | 7977.025 | 1342863.25 | 32603 | 0
2021121319 | 2 | 0.6745 | 101175 | 0.90857 | 0 | 0.27236 | 3404.5 | 0 | 0 | 64000 | 3404.5 | 0 | 33770.5 | 1167.5 | 1334559 | 33770.5 | 0
2021121320 | 2 | 0.67215 | 100822.5 | 0.95664 | 0 | 0.34065 | 4258.125 | 0 | 0 | 64000 | 4258.125 | 0 | 32564.375 | -1206.125 | 1327460.875 | 32564.375 | 0
2021121321 | 2 | 0.66485 | 99727.5 | 0.97887 | 0 | 0.35815 | 4476.875 | 0 | 0 | 64000 | 4476.875 | 0 | 31250.625 | -1313.75 | 1321676.5 | 31250.625 | 0
2021121322 | 2 | 0.64724 | 97086 | 0.99024 | 0 | 0.3841 | 4801.25 | 0 | 0 | 64000 | 4801.25 | 0 | 28284.75 | -2965.875 | 1318858 | 28284.75 | 0
2021121323 | 2 | 0.61682 | 92523 | 0.98554 | 0 | 0.3937 | 4921.25 | 0 | 0 | 64000 | 4921.25 | 0 | 23601.75 | -4683 | 1320722.5 | 23601.75 | 0
2021121324 | 2 | 0.58825 | 88237.5 | 0.97765 | 0 | 0.39229 | 4903.625 | 0 | 0 | 64000 | 4903.625 | 0 | 19333.875 | -4267.875 | 1326854.875 | 19333.875 | 0
2021121401 | 3 | 0.56845 | 85267.5 | 0.95397 | 0 | 0.36937 | 4617.125 | 0 | 0 | 64000 | 4617.125 | 0 | 16650.375 | -2683.5 | 1335670.75 | 16650.375 | 0
2021121402 | 3 | 0.55832 | 83748 | 0.92499 | 0 | 0.34843 | 4355.375 | 0 | 0 | 64000 | 4355.375 | 0 | 15392.625 | -1257.75 | 1345744.375 | 15392.625 | 0
2021121403 | 3 | 0.55764 | 83646 | 0.88594 | 0 | 0.32043 | 4005.375 | 0 | 0 | 64000 | 4005.375 | 0 | 15640.625 | 248 | 1350000 | 15640.625 | 0
2021121404 | 3 | 0.56119 | 84178.5 | 0.76376 | 0 | 0.27648 | 3456 | 0 | 0 | 64000 | 3456 | 0 | 16722.5 | 1081.875 | 1350000 | 16722.5 | 0
2021121405 | 3 | 0.57684 | 86526 | 0.5685 | 0 | 0.24458 | 3057.25 | 0 | 0 | 64000 | 3057.25 | 0 | 19468.75 | 2746.25 | 1350000 | 19468.75 | 0
2021121406 | 3 | 0.61162 | 91743 | 0.44717 | 0 | 0.26908 | 3363.5 | 0 | 0 | 64000 | 3363.5 | 0 | 24379.5 | 4910.75 | 1350000 | 24379.5 | 0
2021121407 | 3 | 0.66344 | 99516 | 0.38758 | 0 | 0.28176 | 3522 | 0.00015 | 12 | 64000 | 3522 | 12 | 31982 | 7602.5 | 1343484.25 | 31982 | 0
2021121408 | 3 | 0.69577 | 104365.5 | 0.42282 | 0 | 0.33562 | 4195.25 | 0.05109 | 4087.2 | 64000 | 4195.25 | 4087.2 | 32083.05 | 101.05 | 1336867.45 | 32083.05 | 0
2021121409 | 3 | 0.6866 | 102990 | 0.3708 | 0 | 0.36975 | 4621.875 | 0.15014 | 12011.2 | 64000 | 4621.875 | 12011.2 | 22356.925 | -9726.125 | 1339976.775 | 22356.925 | 0
2021121410 | 3 | 0.65551 | 98326.5 | 0.27574 | 0 | 0.37889 | 4736.125 | 0.16817 | 13453.6 | 64000 | 4736.125 | 13453.6 | 16136.775 | -6220.15 | 1349306.25 | 16136.775 | 0
2021121411 | 3 | 0.62924 | 94386 | 0.16089 | 0 | 0.33817 | 4227.125 | 0.23401 | 18720.8 | 64000 | 4227.125 | 18720.8 | 7438.075 | -8698.7 | 1350000 | 7438.075 | 0
2021121412 | 3 | 0.60952 | 91428 | 0.06495 | 0 | 0.3073 | 3841.25 | 0.33959 | 27167.2 | 64000 | 3841.25 | 23586.75 | 0 | -7438.075 | 1350000 | 0 | 0
2021121413 | 3 | 0.59546 | 89319 | 0.01992 | 0 | 0.25999 | 3249.875 | 0.36463 | 29170.4 | 64000 | 3249.875 | 22069.125 | 0 | 0 | 1350000 | 0 | 0
2021121414 | 3 | 0.58764 | 88146 | 0.01286 | 0 | 0.22925 | 2865.625 | 0.37005 | 29604 | 64000 | 2865.625 | 21280.375 | 0 | 0 | 1350000 | 0 | 0
2021121415 | 3 | 0.58304 | 87456 | 0.01727 | 0 | 0.21798 | 2724.75 | 0.31989 | 25591.2 | 64000 | 2724.75 | 20731.25 | 0 | 0 | 1350000 | 0 | 0
2021121416 | 3 | 0.58747 | 88120.5 | 0.04275 | 0 | 0.20525 | 2565.625 | 0.14437 | 11549.6 | 64000 | 2565.625 | 11549.6 | 10005.275 | 10005.275 | 1350000 | 10005.275 | 0
2021121417 | 3 | 0.60953 | 91429.5 | 0.12704 | 0 | 0.21289 | 2661.125 | 0.01397 | 1117.6 | 64000 | 2661.125 | 1117.6 | 23650.775 | 13645.5 | 1350000 | 23650.775 | 0
2021121418 | 3 | 0.65393 | 98089.5 | 0.24999 | 0 | 0.20213 | 2526.625 | 0 | 0 | 64000 | 2526.625 | 0 | 31562.875 | 7912.1 | 1343903.375 | 31562.875 | 0
2021121419 | 3 | 0.66325 | 99487.5 | 0.41107 | 0 | 0.19687 | 2460.875 | 0 | 0 | 64000 | 2460.875 | 0 | 33026.625 | 1463.75 | 1336343 | 33026.625 | 0
2021121420 | 3 | 0.66066 | 99099 | 0.54786 | 0 | 0.19754 | 2469.25 | 0 | 0 | 64000 | 2469.25 | 0 | 32629.75 | -396.875 | 1329179.5 | 32629.75 | 0
2021121421 | 3 | 0.65389 | 98083.5 | 0.61514 | 0 | 0.20221 | 2527.625 | 0 | 0 | 64000 | 2527.625 | 0 | 31555.875 | -1073.875 | 1323089.875 | 31555.875 | 0
2021121422 | 3 | 0.63607 | 95410.5 | 0.66225 | 0 | 0.23636 | 2954.5 | 0 | 0 | 64000 | 2954.5 | 0 | 28456 | -3099.875 | 1320100.125 | 28456 | 0
2021121423 | 3 | 0.60674 | 91011 | 0.78411 | 0 | 0.27502 | 3437.75 | 0 | 0 | 64000 | 3437.75 | 0 | 23573.25 | -4882.75 | 1321993.125 | 23573.25 | 0
2021121424 | 3 | 0.5767 | 86505 | 0.83701 | 0 | 0.28673 | 3584.125 | 0 | 0 | 64000 | 3584.125 | 0 | 18920.875 | -4652.375 | 1328538.5 | 18920.875 | 0
2021121501 | 4 | 0.55561 | 83341.5 | 0.83078 | 0 | 0.28699 | 3587.375 | 0 | 0 | 64000 | 3587.375 | 0 | 15754.125 | -3166.75 | 1338250.625 | 15754.125 | 0
2021121502 | 4 | 0.54442 | 81663 | 0.87927 | 0 | 0.29009 | 3626.125 | 0 | 0 | 64000 | 3626.125 | 0 | 14036.875 | -1717.25 | 1349680 | 14036.875 | 0
2021121503 | 4 | 0.54092 | 81138 | 0.9266 | 0 | 0.27371 | 3421.375 | 0 | 0 | 64000 | 3421.375 | 0 | 13716.625 | -320.25 | 1350000 | 13716.625 | 0
2021121504 | 4 | 0.54347 | 81520.5 | 0.93507 | 0 | 0.29323 | 3665.375 | 0 | 0 | 64000 | 3665.375 | 0 | 13855.125 | 138.5 | 1350000 | 13855.125 | 0
2021121505 | 4 | 0.55492 | 83238 | 0.95889 | 0 | 0.25893 | 3236.625 | 0 | 0 | 64000 | 3236.625 | 0 | 16001.375 | 2146.25 | 1350000 | 16001.375 | 0
2021121506 | 4 | 0.58425 | 87637.5 | 0.96385 | 0 | 0.22187 | 2773.375 | 0 | 0 | 64000 | 2773.375 | 0 | 20864.125 | 4862.75 | 1350000 | 20864.125 | 0
2021121507 | 4 | 0.63175 | 94762.5 | 0.97379 | 0 | 0.20283 | 2535.375 | 0.00026 | 20.8 | 64000 | 2535.375 | 20.8 | 28206.325 | 7342.2 | 1347259.925 | 28206.325 | 0
2021121508 | 4 | 0.66014 | 99021 | 0.98516 | 0 | 0.20985 | 2623.125 | 0.07114 | 5691.2 | 64000 | 2623.125 | 5691.2 | 26706.675 | -1499.65 | 1346019.5 | 26706.675 | 0
2021121509 | 4 | 0.65683 | 98524.5 | 0.9882 | 0 | 0.22212 | 2776.5 | 0.21358 | 17086.4 | 64000 | 2776.5 | 17086.4 | 14661.6 | -12045.075 | 1350000 | 14661.6 | 0
2021121510 | 4 | 0.63673 | 95509.5 | 0.96325 | 0 | 0.23007 | 2875.875 | 0.26448 | 21158.4 | 64000 | 2875.875 | 21158.4 | 7475.225 | -7186.375 | 1350000 | 7475.225 | 0
2021121511 | 4 | 0.6176 | 92640 | 0.95024 | 0 | 0.22922 | 2865.25 | 0.33579 | 26863.2 | 64000 | 2865.25 | 25774.75 | 0 | -7475.225 | 1350000 | 0 | 0
2021121512 | 4 | 0.60376 | 90564 | 0.95644 | 0 | 0.20341 | 2542.625 | 0.39126 | 31300.8 | 64000 | 2542.625 | 24021.375 | 0 | 0 | 1350000 | 0 | 0
2021121513 | 4 | 0.59478 | 89217 | 0.90744 | 0 | 0.21345 | 2668.125 | 0.4003 | 32024 | 64000 | 2668.125 | 22548.875 | 0 | 0 | 1350000 | 0 | 0
2021121514 | 4 | 0.59188 | 88782 | 0.8227 | 0 | 0.22488 | 2811 | 0.3916 | 31328 | 64000 | 2811 | 21971 | 0 | 0 | 1350000 | 0 | 0
2021121515 | 4 | 0.58892 | 88338 | 0.83109 | 0 | 0.21431 | 2678.875 | 0.33763 | 27010.4 | 64000 | 2678.875 | 21659.125 | 0 | 0 | 1350000 | 0 | 0
2021121516 | 4 | 0.59167 | 88750.5 | 0.80544 | 0 | 0.22278 | 2784.75 | 0.16829 | 13463.2 | 64000 | 2784.75 | 13463.2 | 8502.55 | 8502.55 | 1350000 | 8502.55 | 0
2021121517 | 4 | 0.60952 | 91428 | 0.8705 | 0 | 0.25246 | 3155.75 | 0.01339 | 1071.2 | 64000 | 3155.75 | 1071.2 | 23201.05 | 14698.5 | 1350000 | 23201.05 | 0
2021121518 | 4 | 0.64092 | 96138 | 0.89303 | 0 | 0.27994 | 3499.25 | 0 | 0 | 64000 | 3499.25 | 0 | 28638.75 | 5437.7 | 1346827.5 | 28638.75 | 0
2021121519 | 4 | 0.64367 | 96550.5 | 0.91493 | 0 | 0.28931 | 3616.375 | 0 | 0 | 64000 | 3616.375 | 0 | 28934.125 | 295.375 | 1343359.625 | 28934.125 | 0
2021121520 | 4 | 0.63591 | 95386.5 | 0.92318 | 0 | 0.32282 | 4035.25 | 0 | 0 | 64000 | 4035.25 | 0 | 27351.25 | -1582.875 | 1341474.625 | 27351.25 | 0
2021121521 | 4 | 0.6249 | 93735 | 0.9171 | 0 | 0.34765 | 4345.625 | 0 | 0 | 64000 | 4345.625 | 0 | 25389.375 | -1961.875 | 1341551.5 | 25389.375 | 0
2021121522 | 4 | 0.60285 | 90427.5 | 0.90061 | 0 | 0.37833 | 4729.125 | 0 | 0 | 64000 | 4729.125 | 0 | 21698.375 | -3691 | 1345319.375 | 21698.375 | 0
2021121523 | 4 | 0.5713 | 85695 | 0.92392 | 0 | 0.37789 | 4723.625 | 0 | 0 | 64000 | 4723.625 | 0 | 16971.375 | -4727 | 1350000 | 16971.375 | 0
2021121524 | 4 | 0.53817 | 80725.5 | 0.92068 | 0 | 0.4097 | 5121.25 | 0 | 0 | 64000 | 5121.25 | 0 | 11604.25 | -5367.125 | 1350000 | 11604.25 | 0
2021121601 | 5 | 0.51529 | 77293.5 | 0.92767 | 0 | 0.45691 | 5711.375 | 0 | 0 | 64000 | 5711.375 | 0 | 7582.125 | -4022.125 | 1350000 | 7582.125 | 0
2021121602 | 5 | 0.5015 | 75225 | 0.93537 | 0 | 0.49842 | 6230.25 | 0 | 0 | 64000 | 6230.25 | 0 | 4994.75 | -2587.375 | 1350000 | 4994.75 | 0
2021121603 | 5 | 0.49492 | 74238 | 0.91736 | 0 | 0.47733 | 5966.625 | 0 | 0 | 64000 | 5966.625 | 0 | 4271.375 | -723.375 | 1350000 | 4271.375 | 0
2021121604 | 5 | 0.49399 | 74098.5 | 0.91544 | 0 | 0.46857 | 5857.125 | 0 | 0 | 64000 | 5857.125 | 0 | 4241.375 | -30 | 1350000 | 4241.375 | 0
2021121605 | 5 | 0.50531 | 75796.5 | 0.91593 | 0 | 0.48181 | 6022.625 | 0 | 0 | 64000 | 6022.625 | 0 | 5773.875 | 1532.5 | 1350000 | 5773.875 | 0
2021121606 | 5 | 0.53319 | 79978.5 | 0.92787 | 0 | 0.50084 | 6260.5 | 0 | 0 | 64000 | 6260.5 | 0 | 9718 | 3944.125 | 1350000 | 9718 | 0
2021121607 | 5 | 0.58079 | 87118.5 | 0.93429 | 0 | 0.53304 | 6663 | 0 | 0 | 64000 | 6663 | 0 | 16455.5 | 6737.5 | 1350000 | 16455.5 | 0
2021121608 | 5 | 0.61382 | 92073 | 0.94317 | 0 | 0.53217 | 6652.125 | 0.04024 | 3219.2 | 64000 | 6652.125 | 3219.2 | 18201.675 | 1746.175 | 1350000 | 18201.675 | 0
2021121609 | 5 | 0.61401 | 92101.5 | 0.9366 | 0 | 0.51654 | 6456.75 | 0.11787 | 9429.6 | 64000 | 6456.75 | 9429.6 | 12215.15 | -5986.525 | 1350000 | 12215.15 | 0
2021121610 | 5 | 0.60149 | 90223.5 | 0.9163 | 0 | 0.48112 | 6014 | 0.15115 | 12092 | 64000 | 6014 | 12092 | 8117.5 | -4097.65 | 1350000 | 8117.5 | 0
2021121611 | 5 | 0.5917 | 88755 | 0.86343 | 0 | 0.42704 | 5338 | 0.16543 | 13234.4 | 64000 | 5338 | 13234.4 | 6182.6 | -1934.9 | 1350000 | 6182.6 | 0
2021121612 | 5 | 0.58126 | 87189 | 0.82933 | 0 | 0.37434 | 4679.25 | 0.21198 | 16958.4 | 64000 | 4679.25 | 16958.4 | 1551.35 | -4631.25 | 1350000 | 1551.35 | 0
2021121613 | 5 | 0.57405 | 86107.5 | 0.81237 | 0 | 0.35395 | 4424.375 | 0.25079 | 20063.2 | 64000 | 4424.375 | 17683.125 | 0 | -1551.35 | 1350000 | 0 | 0
2021121614 | 5 | 0.57012 | 85518 | 0.81264 | 0 | 0.31513 | 3939.125 | 0.25933 | 20746.4 | 64000 | 3939.125 | 17578.875 | 0 | 0 | 1350000 | 0 | 0
2021121615 | 5 | 0.5679 | 85185 | 0.77621 | 0 | 0.30417 | 3802.125 | 0.13859 | 11087.2 | 64000 | 3802.125 | 11087.2 | 6295.675 | 6295.675 | 1350000 | 6295.675 | 0
2021121616 | 5 | 0.57051 | 85576.5 | 0.7183 | 0 | 0.28697 | 3587.125 | 0.06602 | 5281.6 | 64000 | 3587.125 | 5281.6 | 12707.775 | 6412.1 | 1350000 | 12707.775 | 0
2021121617 | 5 | 0.5877 | 88155 | 0.81952 | 0 | 0.23393 | 2924.125 | 0.00661 | 528.8 | 64000 | 2924.125 | 528.8 | 20702.075 | 7994.3 | 1350000 | 20702.075 | 0
2021121618 | 5 | 0.6205 | 93075 | 0.87599 | 0 | 0.21986 | 2748.25 | 0 | 0 | 64000 | 2748.25 | 0 | 26326.75 | 5624.675 | 1349139.5 | 26326.75 | 0
2021121619 | 5 | 0.62402 | 93603 | 0.87717 | 0 | 0.19931 | 2491.375 | 0 | 0 | 64000 | 2491.375 | 0 | 27111.625 | 784.875 | 1347494.125 | 27111.625 | 0
2021121620 | 5 | 0.61723 | 92584.5 | 0.93573 | 0 | 0.16136 | 2017 | 0 | 0 | 64000 | 2017 | 0 | 26567.5 | -544.125 | 1346392.875 | 26567.5 | 0
2021121621 | 5 | 0.60649 | 90973.5 | 0.94472 | 0 | 0.10084 | 1260.5 | 0 | 0 | 64000 | 1260.5 | 0 | 25713 | -854.5 | 1346146.125 | 25713 | 0
2021121622 | 5 | 0.58741 | 88111.5 | 0.95224 | 0 | 0.06638 | 829.75 | 0 | 0 | 64000 | 829.75 | 0 | 23281.75 | -2431.25 | 1348330.625 | 23281.75 | 0
2021121623 | 5 | 0.5554 | 83310 | 0.96617 | 0 | 0.08541 | 1067.625 | 0 | 0 | 64000 | 1067.625 | 0 | 18242.375 | -5039.375 | 1350000 | 18242.375 | 0
2021121624 | 5 | 0.52452 | 78678 | 0.96305 | 0 | 0.08726 | 1090.75 | 0 | 0 | 64000 | 1090.75 | 0 | 13587.25 | -4655.125 | 1350000 | 13587.25 | 0
2021121701 | 6 | 0.49963 | 74944.5 | 0.92224 | 0 | 0.07146 | 893.25 | 0 | 0 | 64000 | 893.25 | 0 | 10051.25 | -3536 | 1350000 | 10051.25 | 0
2021121702 | 6 | 0.48453 | 72679.5 | 0.9154 | 0 | 0.06705 | 838.125 | 0 | 0 | 64000 | 838.125 | 0 | 7841.375 | -2209.875 | 1350000 | 7841.375 | 0
2021121703 | 6 | 0.47818 | 71727 | 0.92391 | 0 | 0.0744 | 930 | 0 | 0 | 64000 | 930 | 0 | 6797 | -1044.375 | 1350000 | 6797 | 0
2021121704 | 6 | 0.47962 | 71943 | 0.95947 | 0 | 0.07747 | 968.375 | 0 | 0 | 64000 | 968.375 | 0 | 6974.625 | 177.625 | 1350000 | 6974.625 | 0
2021121705 | 6 | 0.48909 | 73363.5 | 0.97587 | 0 | 0.07775 | 971.875 | 0 | 0 | 64000 | 971.875 | 0 | 8391.625 | 1417 | 1350000 | 8391.625 | 0
2021121706 | 6 | 0.51824 | 77736 | 0.93827 | 0 | 0.07942 | 992.75 | 0 | 0 | 64000 | 992.75 | 0 | 12743.25 | 4351.625 | 1350000 | 12743.25 | 0
2021121707 | 6 | 0.56468 | 84702 | 0.89515 | 0 | 0.09571 | 1196.375 | 0 | 0 | 64000 | 1196.375 | 0 | 19505.625 | 6762.375 | 1350000 | 19505.625 | 0
2021121708 | 6 | 0.59976 | 89964 | 0.83156 | 0 | 0.15922 | 1990.25 | 0.01564 | 1251.2 | 64000 | 1990.25 | 1251.2 | 22722.55 | 3216.925 | 1350000 | 22722.55 | 0
2021121709 | 6 | 0.60714 | 91071 | 0.74045 | 0 | 0.18683 | 2335.375 | 0.08938 | 7150.4 | 64000 | 2335.375 | 7150.4 | 17585.225 | -5137.325 | 1350000 | 17585.225 | 0
2021121710 | 6 | 0.60332 | 90498 | 0.63179 | 0 | 0.29137 | 3642.125 | 0.19656 | 15724.8 | 64000 | 3642.125 | 15724.8 | 7131.075 | -10454.15 | 1350000 | 7131.075 | 0
2021121711 | 6 | 0.59605 | 89407.5 | 0.51853 | 0 | 0.34069 | 4258.625 | 0.29186 | 23348.8 | 64000 | 4258.625 | 21148.875 | 0 | -7131.075 | 1350000 | 0 | 0
2021121712 | 6 | 0.58824 | 88236 | 0.45547 | 0 | 0.37113 | 4639.125 | 0.3291 | 26328 | 64000 | 4639.125 | 19596.875 | 0 | 0 | 1350000 | 0 | 0
2021121713 | 6 | 0.58184 | 87276 | 0.41242 | 0 | 0.35699 | 4462.375 | 0.34199 | 27359.2 | 64000 | 4462.375 | 18813.625 | 0 | 0 | 1350000 | 0 | 0
2021121714 | 6 | 0.58029 | 87043.5 | 0.36405 | 0 | 0.33961 | 4245.125 | 0.35328 | 28262.4 | 64000 | 4245.125 | 18798.375 | 0 | 0 | 1350000 | 0 | 0
2021121715 | 6 | 0.57885 | 86827.5 | 0.31082 | 0 | 0.35992 | 4499 | 0.28883 | 23106.4 | 64000 | 4499 | 18328.5 | 0 | 0 | 1350000 | 0 | 0
2021121716 | 6 | 0.58295 | 87442.5 | 0.27234 | 0 | 0.37937 | 4742.125 | 0.11344 | 9075.2 | 64000 | 4742.125 | 9075.2 | 9625.175 | 9625.175 | 1350000 | 9625.175 | 0
2021121717 | 6 | 0.6007 | 90105 | 0.25078 | 0 | 0.35425 | 4428.125 | 0.00891 | 712.8 | 64000 | 4428.125 | 712.8 | 20964.075 | 11338.9 | 1350000 | 20964.075 | 0
2021121718 | 6 | 0.63054 | 94581 | 0.30414 | 0 | 0.28949 | 3618.625 | 0 | 0 | 64000 | 3618.625 | 0 | 26962.375 | 5998.3 | 1348503.875 | 26962.375 | 0
2021121719 | 6 | 0.62828 | 94242 | 0.29432 | 0 | 0.30988 | 3873.5 | 0 | 0 | 64000 | 3873.5 | 0 | 26368.5 | -593.875 | 1347601.625 | 26368.5 | 0
2021121720 | 6 | 0.61774 | 92661 | 0.28894 | 0 | 0.33013 | 4126.625 | 0 | 0 | 64000 | 4126.625 | 0 | 24534.375 | -1834.125 | 1348533.5 | 24534.375 | 0
2021121721 | 6 | 0.60587 | 90880.5 | 0.26023 | 0 | 0.34916 | 4364.5 | 0 | 0 | 64000 | 4364.5 | 0 | 22516 | -2018.375 | 1350000 | 22516 | 0
2021121722 | 6 | 0.58879 | 88318.5 | 0.16424 | 0 | 0.38879 | 4859.875 | 0 | 0 | 64000 | 4859.875 | 0 | 19458.625 | -3057.375 | 1350000 | 19458.625 | 0
2021121723 | 6 | 0.56275 | 84412.5 | 0.13949 | 0 | 0.39326 | 4915.75 | 0 | 0 | 64000 | 4915.75 | 0 | 15496.75 | -3961.875 | 1350000 | 15496.75 | 0
2021121724 | 6 | 0.53226 | 79839 | 0.05763 | 0 | 0.41969 | 5246.125 | 0 | 0 | 64000 | 5246.125 | 0 | 10592.875 | -4903.875 | 1350000 | 10592.875 | 0
2021121801 | 7 | 0.50712 | 76068 | 0.1808 | 0 | 0.48294 | 6036.75 | 0 | 0 | 64000 | 6036.75 | 0 | 6031.25 | -4561.625 | 1350000 | 6031.25 | 0
2021121802 | 7 | 0.49122 | 73683 | 0.33741 | 0 | 0.50366 | 6295.75 | 0 | 0 | 64000 | 6295.75 | 0 | 3387.25 | -2644 | 1350000 | 3387.25 | 0
2021121803 | 7 | 0.48197 | 72295.5 | 0.39843 | 0 | 0.51068 | 6383.5 | 0 | 0 | 64000 | 6383.5 | 0 | 1912 | -1475.25 | 1350000 | 1912 | 0
2021121804 | 7 | 0.47985 | 71977.5 | 0.33974 | 0 | 0.50047 | 6255.875 | 0 | 0 | 64000 | 6255.875 | 0 | 1721.625 | -190.375 | 1350000 | 1721.625 | 0
2021121805 | 7 | 0.48336 | 72504 | 0.30527 | 0 | 0.46239 | 5779.875 | 0 | 0 | 64000 | 5779.875 | 0 | 2724.125 | 1002.5 | 1350000 | 2724.125 | 0
2021121806 | 7 | 0.49496 | 74244 | 0.3143 | 0 | 0.44756 | 5594.5 | 0 | 0 | 64000 | 5594.5 | 0 | 4649.5 | 1925.375 | 1350000 | 4649.5 | 0
2021121807 | 7 | 0.5154 | 77310 | 0.32703 | 0 | 0.43102 | 5387.75 | 0.00015 | 12 | 64000 | 5387.75 | 12 | 7910.25 | 3260.75 | 1350000 | 7910.25 | 0
2021121808 | 7 | 0.53968 | 80952 | 0.35811 | 0 | 0.40977 | 5122.125 | 0.07966 | 6372.8 | 64000 | 5122.125 | 6372.8 | 5457.075 | -2453.175 | 1350000 | 5457.075 | 0
2021121809 | 7 | 0.5603 | 84045 | 0.39302 | 0 | 0.37021 | 4627.625 | 0.29837 | 23869.6 | 64000 | 4627.625 | 15417.375 | 0 | -5457.075 | 1350000 | 0 | 0
2021121810 | 7 | 0.57738 | 86607 | 0.44856 | 0 | 0.27169 | 3396.125 | 0.37948 | 30358.4 | 64000 | 3396.125 | 19210.875 | 0 | 0 | 1350000 | 0 | 0
2021121811 | 7 | 0.58564 | 87846 | 0.51214 | 0 | 0.22322 | 2790.25 | 0.38897 | 31117.6 | 64000 | 2790.25 | 21055.75 | 0 | 0 | 1350000 | 0 | 0
2021121812 | 7 | 0.58544 | 87816 | 0.58153 | 0 | 0.23716 | 2964.5 | 0.35892 | 28713.6 | 64000 | 2964.5 | 20851.5 | 0 | 0 | 1350000 | 0 | 0
2021121813 | 7 | 0.58158 | 87237 | 0.62081 | 0 | 0.29603 | 3700.375 | 0.34362 | 27489.6 | 64000 | 3700.375 | 19536.625 | 0 | 0 | 1350000 | 0 | 0
2021121814 | 7 | 0.57401 | 86101.5 | 0.66666 | 0 | 0.34723 | 4340.375 | 0.32177 | 25741.6 | 64000 | 4340.375 | 17761.125 | 0 | 0 | 1350000 | 0 | 0
2021121815 | 7 | 0.56931 | 85396.5 | 0.74124 | 0 | 0.39697 | 4962.125 | 0.23126 | 18500.8 | 64000 | 4962.125 | 16434.375 | 0 | 0 | 1350000 | 0 | 0
2021121816 | 7 | 0.57039 | 85558.5 | 0.76487 | 0 | 0.41216 | 5152 | 0.10611 | 8488.8 | 64000 | 5152 | 8488.8 | 7917.7 | 7917.7 | 1350000 | 7917.7 | 0
2021121817 | 7 | 0.58456 | 87684 | 0.74794 | 0 | 0.39106 | 4888.25 | 0.00759 | 607.2 | 64000 | 4888.25 | 607.2 | 18188.55 | 10270.85 | 1350000 | 18188.55 | 0
2021121818 | 7 | 0.60871 | 91306.5 | 0.76247 | 0 | 0.39814 | 4976.75 | 0 | 0 | 64000 | 4976.75 | 0 | 22329.75 | 4141.2 | 1350000 | 22329.75 | 0
2021121819 | 7 | 0.60774 | 91161 | 0.72431 | 0 | 0.47107 | 5888.375 | 0 | 0 | 64000 | 5888.375 | 0 | 21272.625 | -1057.125 | 1350000 | 21272.625 | 0
2021121820 | 7 | 0.59983 | 89974.5 | 0.66369 | 0 | 0.51651 | 6456.375 | 0 | 0 | 64000 | 6456.375 | 0 | 19518.125 | -1754.5 | 1350000 | 19518.125 | 0
2021121821 | 7 | 0.59108 | 88662 | 0.64777 | 0 | 0.52134 | 6516.75 | 0 | 0 | 64000 | 6516.75 | 0 | 18145.25 | -1372.875 | 1350000 | 18145.25 | 0
2021121822 | 7 | 0.57596 | 86394 | 0.67044 | 0 | 0.52212 | 6526.5 | 0 | 0 | 64000 | 6526.5 | 0 | 15867.5 | -2277.75 | 1350000 | 15867.5 | 0
2021121823 | 7 | 0.55503 | 83254.5 | 0.72132 | 0 | 0.56122 | 7015.25 | 0 | 0 | 64000 | 7015.25 | 0 | 12239.25 | -3628.25 | 1350000 | 12239.25 | 0
2021121824 | 7 | 0.52817 | 79225.5 | 0.80376 | 0 | 0.58377 | 7297.125 | 0 | 0 | 64000 | 7297.125 | 0 | 7928.375 | -4310.875 | 1350000 | 7928.375 | 0
2021121901 | 1 | 0.50605 | 75907.5 | 0.83923 | 0 | 0.58697 | 7337.125 | 0 | 0 | 64000 | 7337.125 | 0 | 4570.375 | -3358 | 1350000 | 4570.375 | 0
2021121902 | 1 | 0.49214 | 73821 | 0.90831 | 0 | 0.59249 | 7406.125 | 0 | 0 | 64000 | 7406.125 | 0 | 2414.875 | -2155.5 | 1350000 | 2414.875 | 0
2021121903 | 1 | 0.48281 | 72421.5 | 0.92724 | 0 | 0.63041 | 7880.125 | 0 | 0 | 64000 | 7880.125 | 0 | 541.375 | -1873.5 | 1350000 | 541.375 | 0
2021121904 | 1 | 0.48109 | 72163.5 | 0.91251 | 0 | 0.6124 | 7655 | 0 | 0 | 64000 | 7655 | 0 | 508.5 | -32.875 | 1350000 | 508.5 | 0
2021121905 | 1 | 0.48436 | 72654 | 0.88675 | 0 | 0.59064 | 7383 | 0 | 0 | 64000 | 7383 | 0 | 1271 | 762.5 | 1350000 | 1271 | 0
2021121906 | 1 | 0.49663 | 74494.5 | 0.88053 | 0 | 0.55033 | 6879.125 | 0 | 0 | 64000 | 6879.125 | 0 | 3615.375 | 2344.375 | 1350000 | 3615.375 | 0
2021121907 | 1 | 0.51561 | 77341.5 | 0.87261 | 0 | 0.46668 | 5833.5 | 0 | 0 | 64000 | 5833.5 | 0 | 7508 | 3892.625 | 1350000 | 7508 | 0
2021121908 | 1 | 0.53936 | 80904 | 0.8582 | 0 | 0.38608 | 4826 | 0.08077 | 6461.6 | 64000 | 4826 | 6461.6 | 5616.4 | -1891.6 | 1350000 | 5616.4 | 0
2021121909 | 1 | 0.56257 | 84385.5 | 0.84387 | 0 | 0.34134 | 4266.75 | 0.29381 | 23504.8 | 64000 | 4266.75 | 16118.75 | 0 | -5616.4 | 1350000 | 0 | 0
2021121910 | 1 | 0.58109 | 87163.5 | 0.85372 | 0 | 0.32674 | 4084.25 | 0.38419 | 30735.2 | 64000 | 4084.25 | 19079.25 | 0 | 0 | 1350000 | 0 | 0
2021121911 | 1 | 0.58838 | 88257 | 0.85042 | 0 | 0.34904 | 4363 | 0.39172 | 31337.6 | 64000 | 4363 | 19894 | 0 | 0 | 1350000 | 0 | 0
2021121912 | 1 | 0.59204 | 88806 | 0.81122 | 0 | 0.3898 | 4872.5 | 0.38685 | 30948 | 64000 | 4872.5 | 19933.5 | 0 | 0 | 1350000 | 0 | 0
2021121913 | 1 | 0.59102 | 88653 | 0.7288 | 0 | 0.4143 | 5178.75 | 0.39507 | 31605.6 | 64000 | 5178.75 | 19474.25 | 0 | 0 | 1350000 | 0 | 0
2021121914 | 1 | 0.58943 | 88414.5 | 0.67523 | 0 | 0.44772 | 5596.5 | 0.40098 | 32078.4 | 64000 | 5596.5 | 18818 | 0 | 0 | 1350000 | 0 | 0
2021121915 | 1 | 0.58855 | 88282.5 | 0.66276 | 0 | 0.52501 | 6562.625 | 0.33483 | 26786.4 | 64000 | 6562.625 | 17719.875 | 0 | 0 | 1350000 | 0 | 0
2021121916 | 1 | 0.59338 | 89007 | 0.62688 | 0 | 0.59257 | 7407.125 | 0.15214 | 12171.2 | 64000 | 7407.125 | 12171.2 | 5428.675 | 5428.675 | 1350000 | 5428.675 | 0
2021121917 | 1 | 0.61749 | 92623.5 | 0.5969 | 0 | 0.62164 | 7770.5 | 0.01134 | 907.2 | 64000 | 7770.5 | 907.2 | 19945.8 | 14517.125 | 1350000 | 19945.8 | 0
2021121918 | 1 | 0.66106 | 99159 | 0.56275 | 0 | 0.61055 | 7631.875 | 0 | 0 | 64000 | 7631.875 | 0 | 27527.125 | 7581.325 | 1347939.125 | 27527.125 | 0
2021121919 | 1 | 0.67147 | 100720.5 | 0.58503 | 0 | 0.59598 | 7449.75 | 0 | 0 | 64000 | 7449.75 | 0 | 29270.75 | 1743.625 | 1344134.625 | 29270.75 | 0
2021121920 | 1 | 0.67089 | 100633.5 | 0.59238 | 0 | 0.61194 | 7649.25 | 0 | 0 | 64000 | 7649.25 | 0 | 28984.25 | -286.5 | 1340616.625 | 28984.25 | 0
2021121921 | 1 | 0.66747 | 100120.5 | 0.49388 | 0 | 0.61893 | 7736.625 | 0 | 0 | 64000 | 7736.625 | 0 | 28383.875 | -600.375 | 1337699 | 28383.875 | 0
2021121922 | 1 | 0.65323 | 97984.5 | 0.32869 | 0 | 0.65187 | 8148.375 | 0 | 0 | 64000 | 8148.375 | 0 | 25836.125 | -2547.75 | 1337329.125 | 25836.125 | 0
2021121923 | 1 | 0.63171 | 94756.5 | 0.30068 | 0 | 0.64781 | 8097.625 | 0 | 0 | 64000 | 8097.625 | 0 | 22658.875 | -3177.25 | 1340136.5 | 22658.875 | 0
2021121924 | 1 | 0.60746 | 91119 | 0.25459 | 0 | 0.62787 | 7848.375 | 0 | 0 | 64000 | 7848.375 | 0 | 19270.625 | -3388.25 | 1346332.125 | 19270.625 | 0
2021122001 | 2 | 0.59067 | 88600.5 | 0.21534 | 0 | 0.59749 | 7468.625 | 0 | 0 | 64000 | 7468.625 | 0 | 17131.875 | -2138.75 | 1350000 | 17131.875 | 0
2021122002 | 2 | 0.58262 | 87393 | 0.14516 | 0 | 0.55173 | 6896.625 | 0 | 0 | 64000 | 6896.625 | 0 | 16496.375 | -635.5 | 1350000 | 16496.375 | 0
2021122003 | 2 | 0.58486 | 87729 | 0.12838 | 0 | 0.50323 | 6290.375 | 0 | 0 | 64000 | 6290.375 | 0 | 17438.625 | 942.25 | 1350000 | 17438.625 | 0
2021122004 | 2 | 0.59058 | 88587 | 0.11886 | 0 | 0.44426 | 5553.25 | 0 | 0 | 64000 | 5553.25 | 0 | 19033.75 | 1595.125 | 1350000 | 19033.75 | 0
2021122005 | 2 | 0.61001 | 91501.5 | 0.23 | 0 | 0.40013 | 5001.625 | 0 | 0 | 64000 | 5001.625 | 0 | 22499.875 | 3466.125 | 1350000 | 22499.875 | 0
2021122006 | 2 | 0.64512 | 96768 | 0.23887 | 0 | 0.37032 | 4629 | 0 | 0 | 64000 | 4629 | 0 | 28139 | 5639.125 | 1347327.25 | 28139 | 0
2021122007 | 2 | 0.69729 | 104593.5 | 0.19092 | 0 | 0.33264 | 4158 | 0.00117 | 93.6 | 64000 | 4158 | 93.6 | 36341.9 | 8202.9 | 1336451.6 | 36341.9 | 0
2021122008 | 2 | 0.73446 | 110169 | 0.16474 | 0 | 0.30985 | 3873.125 | 0.07399 | 5919.2 | 64000 | 3873.125 | 5919.2 | 36376.675 | 34.775 | 1325541.175 | 36376.675 | 0
2021122009 | 2 | 0.73377 | 110065.5 | 0.15395 | 0 | 0.28666 | 3583.25 | 0.27431 | 21944.8 | 64000 | 3583.25 | 21944.8 | 20537.45 | -15839.225 | 1330469.975 | 20537.45 | 0
2021122010 | 2 | 0.70941 | 106411.5 | 0.08958 | 0 | 0.26253 | 3281.625 | 0.36599 | 29279.2 | 64000 | 3281.625 | 29279.2 | 9850.675 | -10686.775 | 1346085.55 | 9850.675 | 0
2021122011 | 2 | 0.68352 | 102528 | 0.05831 | 0 | 0.25968 | 3246 | 0.37398 | 29918.4 | 64000 | 3246 | 29918.4 | 5363.6 | -4487.075 | 1350000 | 5363.6 | 0
2021122012 | 2 | 0.66218 | 99327 | 0.05498 | 0 | 0.24812 | 3101.5 | 0.35597 | 28477.6 | 64000 | 3101.5 | 28477.6 | 3747.9 | -1615.7 | 1350000 | 3747.9 | 0
2021122013 | 2 | 0.64474 | 96711 | 0.06135 | 0 | 0.2988 | 3735 | 0.35 | 28000 | 64000 | 3735 | 28000 | 976 | -2771.9 | 1350000 | 976 | 0
2021122014 | 2 | 0.63469 | 95203.5 | 0.07435 | 0 | 0.39872 | 4984 | 0.30424 | 24339.2 | 64000 | 4984 | 24339.2 | 1880.3 | 904.3 | 1350000 | 1880.3 | 0
2021122015 | 2 | 0.62847 | 94270.5 | 0.13892 | 0 | 0.48571 | 6071.375 | 0.21922 | 17537.6 | 64000 | 6071.375 | 17537.6 | 6661.525 | 4781.225 | 1350000 | 6661.525 | 0
2021122016 | 2 | 0.63251 | 94876.5 | 0.19077 | 0 | 0.53102 | 6637.75 | 0.07346 | 5876.8 | 64000 | 6637.75 | 5876.8 | 18361.95 | 11700.425 | 1350000 | 18361.95 | 0
2021122017 | 2 | 0.65703 | 98554.5 | 0.28531 | 0 | 0.54938 | 6867.25 | 0.00487 | 389.6 | 64000 | 6867.25 | 389.6 | 27297.65 | 8935.7 | 1348168.6 | 27297.65 | 0
2021122018 | 2 | 0.70582 | 105873 | 0.45332 | 0 | 0.56972 | 7121.5 | 0 | 0 | 64000 | 7121.5 | 0 | 34751.5 | 7453.85 | 1338883.35 | 34751.5 | 0
2021122019 | 2 | 0.71974 | 107961 | 0.54726 | 0 | 0.57626 | 7203.25 | 0 | 0 | 64000 | 7203.25 | 0 | 36757.75 | 2006.25 | 1327591.85 | 36757.75 | 0
2021122020 | 2 | 0.71801 | 107701.5 | 0.6426 | 0 | 0.57079 | 7134.875 | 0 | 0 | 64000 | 7134.875 | 0 | 36566.625 | -191.125 | 1316491.475 | 36566.625 | 0
2021122021 | 2 | 0.71225 | 106837.5 | 0.77641 | 0 | 0.59744 | 7468 | 0 | 0 | 64000 | 7468 | 0 | 35369.5 | -1197.125 | 1306588.225 | 35369.5 | 0
2021122022 | 2 | 0.69666 | 104499 | 0.86247 | 0 | 0.61849 | 7731.125 | 0 | 0 | 64000 | 7731.125 | 0 | 32767.875 | -2601.625 | 1299286.6 | 32767.875 | 0
2021122023 | 2 | 0.6674 | 100110 | 0.90594 | 0 | 0.60481 | 7560.125 | 0 | 0 | 64000 | 7560.125 | 0 | 28549.875 | -4218 | 1296202.975 | 28549.875 | 0
2021122024 | 2 | 0.63652 | 95478 | 0.93037 | 0 | 0.57016 | 7127 | 0 | 0 | 64000 | 7127 | 0 | 24351 | -4198.875 | 1297318.225 | 24351 | 0
2021122101 | 3 | 0.6163 | 92445 | 0.92538 | 0 | 0.55964 | 6995.5 | 0 | 0 | 64000 | 6995.5 | 0 | 21449.5 | -2901.5 | 1301334.975 | 21449.5 | 0
2021122102 | 3 | 0.60591 | 90886.5 | 0.89764 | 0 | 0.54245 | 6780.625 | 0 | 0 | 64000 | 6780.625 | 0 | 20105.875 | -1343.625 | 1306695.35 | 20105.875 | 0
2021122103 | 3 | 0.60208 | 90312 | 0.88394 | 0 | 0.53919 | 6739.875 | 0 | 0 | 64000 | 6739.875 | 0 | 19572.125 | -533.75 | 1312589.475 | 19572.125 | 0
2021122104 | 3 | 0.60615 | 90922.5 | 0.85608 | 0 | 0.51516 | 6439.5 | 0 | 0 | 64000 | 6439.5 | 0 | 20483 | 910.875 | 1317572.725 | 20483 | 0
2021122105 | 3 | 0.61782 | 92673 | 0.74812 | 0 | 0.51611 | 6451.375 | 0 | 0 | 64000 | 6451.375 | 0 | 22221.625 | 1738.625 | 1320817.35 | 22221.625 | 0
2021122106 | 3 | 0.64622 | 96933 | 0.55873 | 0 | 0.47638 | 5954.75 | 0 | 0 | 64000 | 5954.75 | 0 | 26978.25 | 4756.625 | 1319305.35 | 26978.25 | 0
2021122107 | 3 | 0.69117 | 103675.5 | 0.44079 | 0 | 0.41319 | 5164.875 | 0 | 0 | 64000 | 5164.875 | 0 | 34510.625 | 7532.375 | 1310260.975 | 34510.625 | 0
2021122108 | 3 | 0.72444 | 108666 | 0.23502 | 0 | 0.38282 | 4785.25 | 0.01298 | 1038.4 | 64000 | 4785.25 | 1038.4 | 38842.35 | 4331.725 | 1296884.875 | 38842.35 | 0
2021122109 | 3 | 0.72998 | 109497 | 0.10226 | 0 | 0.33945 | 4243.125 | 0.04178 | 3342.4 | 64000 | 4243.125 | 3342.4 | 37911.475 | -930.875 | 1284439.65 | 37911.475 | 0
2021122110 | 3 | 0.71874 | 107811 | 0.02761 | 0 | 0.32164 | 4020.5 | 0.07587 | 6069.6 | 64000 | 4020.5 | 6069.6 | 33720.9 | -4190.575 | 1276185 | 33720.9 | 0
2021122111 | 3 | 0.70097 | 105145.5 | 0.00382 | 0 | 0.29652 | 3706.5 | 0.10962 | 8769.6 | 64000 | 3706.5 | 8769.6 | 28669.4 | -5051.5 | 1272981.85 | 28669.4 | 0
2021122112 | 3 | 0.68324 | 102486 | 0.03761 | 0 | 0.23161 | 2895.125 | 0.15429 | 12343.2 | 64000 | 2895.125 | 12343.2 | 23247.675 | -5421.725 | 1275200.425 | 23247.675 | 0
2021122113 | 3 | 0.66781 | 100171.5 | 0.08821 | 0 | 0.17094 | 2136.75 | 0.19647 | 15717.6 | 64000 | 2136.75 | 15717.6 | 18317.15 | -4930.525 | 1282349.525 | 18317.15 | 0
2021122114 | 3 | 0.65977 | 98965.5 | 0.09532 | 0 | 0.14681 | 1835.125 | 0.17096 | 13676.8 | 64000 | 1835.125 | 13676.8 | 19453.575 | 1136.425 | 1288362.2 | 19453.575 | 0
2021122115 | 3 | 0.65347 | 98020.5 | 0.13548 | 0 | 0.12545 | 1568.125 | 0.10709 | 8567.2 | 64000 | 1568.125 | 8567.2 | 23885.175 | 4431.6 | 1289943.275 | 23885.175 | 0
2021122116 | 3 | 0.6531 | 97965 | 0.23622 | 0 | 0.10903 | 1362.875 | 0.0613 | 4904 | 64000 | 1362.875 | 4904 | 27698.125 | 3812.95 | 1287711.4 | 27698.125 | 0
2021122117 | 3 | 0.67009 | 100513.5 | 0.24681 | 0 | 0.0985 | 1231.25 | 0.00811 | 648.8 | 64000 | 1231.25 | 648.8 | 34633.45 | 6935.325 | 1278544.2 | 34633.45 | 0
2021122118 | 3 | 0.70403 | 105604.5 | 0.48238 | 0 | 0.08006 | 1000.75 | 0 | 0 | 64000 | 1000.75 | 0 | 40603.75 | 5970.3 | 1263406.7 | 40603.75 | 0
2021122119 | 3 | 0.70817 | 106225.5 | 0.67581 | 0 | 0.08512 | 1064 | 0 | 0 | 64000 | 1064 | 0 | 41161.5 | 557.75 | 1247711.45 | 41161.5 | 0
2021122120 | 3 | 0.70104 | 105156 | 0.74381 | 0 | 0.09304 | 1163 | 0 | 0 | 64000 | 1163 | 0 | 39993 | -1168.5 | 1233184.7 | 39993 | 0
2021122121 | 3 | 0.68926 | 103389 | 0.7878 | 0 | 0.09012 | 1126.5 | 0 | 0 | 64000 | 1126.5 | 0 | 38262.5 | -1730.5 | 1220388.45 | 38262.5 | 0
2021122122 | 3 | 0.66845 | 100267.5 | 0.77373 | 0 | 0.07345 | 918.125 | 0 | 0 | 64000 | 918.125 | 0 | 35349.375 | -2913.125 | 1210505.325 | 35349.375 | 0
2021122123 | 3 | 0.6373 | 95595 | 0.75819 | 0 | 0.04801 | 600.125 | 0 | 0 | 64000 | 600.125 | 0 | 30994.875 | -4354.5 | 1204976.7 | 30994.875 | 0
2021122124 | 3 | 0.6049 | 90735 | 0.85275 | 0 | 0.04312 | 539 | 0 | 0 | 64000 | 539 | 0 | 26196 | -4798.875 | 1204246.95 | 26196 | 0
2021122201 | 4 | 0.58087 | 87130.5 | 0.88616 | 0 | 0.03612 | 451.5 | 0 | 0 | 64000 | 451.5 | 0 | 22679 | -3517 | 1207034.2 | 22679 | 0
2021122202 | 4 | 0.5658 | 84870 | 0.90871 | 0 | 0.03708 | 463.5 | 0 | 0 | 64000 | 463.5 | 0 | 20406.5 | -2272.5 | 1212093.95 | 20406.5 | 0
2021122203 | 4 | 0.56055 | 84082.5 | 0.91006 | 0 | 0.04185 | 523.125 | 0 | 0 | 64000 | 523.125 | 0 | 19559.375 | -847.125 | 1218000.825 | 19559.375 | 0
2021122204 | 4 | 0.56228 | 84342 | 0.89185 | 0 | 0.04886 | 610.75 | 0 | 0 | 64000 | 610.75 | 0 | 19731.25 | 171.875 | 1223735.825 | 19731.25 | 0
2021122205 | 4 | 0.57475 | 86212.5 | 0.86314 | 0 | 0.0404 | 505 | 0 | 0 | 64000 | 505 | 0 | 21707.5 | 1976.25 | 1227494.575 | 21707.5 | 0
2021122206 | 4 | 0.60335 | 90502.5 | 0.89023 | 0 | 0.04392 | 549 | 0 | 0 | 64000 | 549 | 0 | 25953.5 | 4246 | 1227007.325 | 25953.5 | 0
2021122207 | 4 | 0.64594 | 96891 | 0.8908 | 0 | 0.04726 | 590.75 | 0.0006 | 48 | 64000 | 590.75 | 48 | 32252.25 | 6298.75 | 1220221.325 | 32252.25 | 0
2021122208 | 4 | 0.68058 | 102087 | 0.92083 | 0 | 0.04023 | 502.875 | 0.07524 | 6019.2 | 64000 | 502.875 | 6019.2 | 31564.925 | -687.325 | 1214122.65 | 31564.925 | 0
2021122209 | 4 | 0.68838 | 103257 | 0.93364 | 0 | 0.04351 | 543.875 | 0.29788 | 23830.4 | 64000 | 543.875 | 23830.4 | 14882.725 | -16682.2 | 1224706.175 | 14882.725 | 0
2021122210 | 4 | 0.67538 | 101307 | 0.94438 | 0 | 0.05651 | 706.375 | 0.40759 | 32607.2 | 64000 | 706.375 | 32607.2 | 3993.425 | -10889.3 | 1246179 | 3993.425 | 0
2021122211 | 4 | 0.6601 | 99015 | 0.97528 | 0 | 0.05126 | 640.75 | 0.43025 | 34420 | 64000 | 640.75 | 34374.25 | 0 | -3993.425 | 1271645.25 | 0 | 0
2021122212 | 4 | 0.64573 | 96859.5 | 0.99259 | 0 | 0.06165 | 770.625 | 0.43655 | 34924 | 64000 | 770.625 | 32088.875 | 0 | 0 | 1297111.5 | 0 | 0
2021122213 | 4 | 0.63428 | 95142 | 0.99252 | 0 | 0.07359 | 919.875 | 0.44532 | 35625.6 | 64000 | 919.875 | 30222.125 | 0 | 0 | 1322577.75 | 0 | 0
2021122214 | 4 | 0.62781 | 94171.5 | 0.99663 | 0 | 0.09035 | 1129.375 | 0.44638 | 35710.4 | 64000 | 1129.375 | 29042.125 | 0 | 0 | 1348044 | 0 | 0
2021122215 | 4 | 0.62558 | 93837 | 0.99772 | 0 | 0.11773 | 1471.625 | 0.39044 | 31235.2 | 64000 | 1471.625 | 28365.375 | 0 | 0 | 1350000 | 0 | 0
2021122216 | 4 | 0.63248 | 94872 | 0.99632 | 0 | 0.14386 | 1798.25 | 0.18266 | 14612.8 | 64000 | 1798.25 | 14612.8 | 14460.95 | 14460.95 | 1350000 | 14460.95 | 0
2021122217 | 4 | 0.65647 | 98470.5 | 0.99142 | 0 | 0.1595 | 1993.75 | 0.01382 | 1105.6 | 64000 | 1993.75 | 1105.6 | 31371.15 | 16910.2 | 1344095.1 | 31371.15 | 0
2021122218 | 4 | 0.70045 | 105067.5 | 0.97474 | 0 | 0.17423 | 2177.875 | 0 | 0 | 64000 | 2177.875 | 0 | 38889.625 | 7518.475 | 1330671.725 | 38889.625 | 0
2021122219 | 4 | 0.71054 | 106581 | 0.9743 | 0 | 0.17908 | 2238.5 | 0 | 0 | 64000 | 2238.5 | 0 | 40342.5 | 1452.875 | 1315795.475 | 40342.5 | 0
2021122220 | 4 | 0.70772 | 106158 | 0.97903 | 0 | 0.18343 | 2292.875 | 0 | 0 | 64000 | 2292.875 | 0 | 39865.125 | -477.375 | 1301396.6 | 39865.125 | 0
2021122221 | 4 | 0.70195 | 105292.5 | 0.98559 | 0 | 0.17368 | 2171 | 0 | 0 | 64000 | 2171 | 0 | 39121.5 | -743.625 | 1287741.35 | 39121.5 | 0
2021122222 | 4 | 0.6868 | 103020 | 0.98128 | 0 | 0.17837 | 2229.625 | 0 | 0 | 64000 | 2229.625 | 0 | 36790.375 | -2331.125 | 1276417.225 | 36790.375 | 0
2021122223 | 4 | 0.65988 | 98982 | 0.95002 | 0 | 0.18471 | 2308.875 | 0 | 0 | 64000 | 2308.875 | 0 | 32673.125 | -4117.25 | 1269210.35 | 32673.125 | 0
2021122224 | 4 | 0.63124 | 94686 | 0.90621 | 0 | 0.19231 | 2403.875 | 0 | 0 | 64000 | 2403.875 | 0 | 28282.125 | -4391 | 1266394.475 | 28282.125 | 0
2021122301 | 5 | 0.61019 | 91528.5 | 0.86393 | 0 | 0.19434 | 2429.25 | 0 | 0 | 64000 | 2429.25 | 0 | 25099.25 | -3182.875 | 1266761.475 | 25099.25 | 0
2021122302 | 5 | 0.59893 | 89839.5 | 0.77284 | 0 | 0.18929 | 2366.125 | 0 | 0 | 64000 | 2366.125 | 0 | 23473.375 | -1625.875 | 1268754.35 | 23473.375 | 0
2021122303 | 5 | 0.59579 | 89368.5 | 0.66508 | 0 | 0.18065 | 2258.125 | 0 | 0 | 64000 | 2258.125 | 0 | 23110.375 | -363 | 1271110.225 | 23110.375 | 0
2021122304 | 5 | 0.59885 | 89827.5 | 0.56202 | 0 | 0.17494 | 2186.75 | 0 | 0 | 64000 | 2186.75 | 0 | 23640.75 | 530.375 | 1272935.725 | 23640.75 | 0
2021122305 | 5 | 0.61159 | 91738.5 | 0.5945 | 0 | 0.16977 | 2122.125 | 0 | 0 | 64000 | 2122.125 | 0 | 25616.375 | 1975.625 | 1272785.6 | 25616.375 | 0
2021122306 | 5 | 0.63858 | 95787 | 0.59598 | 0 | 0.16251 | 2031.375 | 0 | 0 | 64000 | 2031.375 | 0 | 29755.625 | 4139.25 | 1268496.225 | 29755.625 | 0
2021122307 | 5 | 0.67613 | 101419.5 | 0.59087 | 0 | 0.15774 | 1971.75 | 0 | 0 | 64000 | 1971.75 | 0 | 35447.75 | 5692.125 | 1258514.725 | 35447.75 | 0
2021122308 | 5 | 0.70688 | 106032 | 0.49447 | 0 | 0.14389 | 1798.625 | 0.07167 | 5733.6 | 64000 | 1798.625 | 5733.6 | 34499.775 | -947.975 | 1249481.2 | 34499.775 | 0
2021122309 | 5 | 0.71013 | 106519.5 | 0.27947 | 0 | 0.13725 | 1715.625 | 0.29113 | 23290.4 | 64000 | 1715.625 | 23290.4 | 17513.475 | -16986.3 | 1257433.975 | 17513.475 | 0
2021122310 | 5 | 0.69195 | 103792.5 | 0.24342 | 0 | 0.12481 | 1560.125 | 0.38136 | 30508.8 | 64000 | 1560.125 | 30508.8 | 7723.575 | -9789.9 | 1275176.65 | 7723.575 | 0
2021122311 | 5 | 0.67217 | 100825.5 | 0.23921 | 0 | 0.11557 | 1444.625 | 0.39956 | 31964.8 | 64000 | 1444.625 | 31964.8 | 3416.075 | -4307.5 | 1297226.825 | 3416.075 | 0
2021122312 | 5 | 0.65346 | 98019 | 0.18194 | 0 | 0.11867 | 1483.375 | 0.41834 | 33467.2 | 64000 | 1483.375 | 32535.625 | 0 | -3416.075 | 1322693.075 | 0 | 0
2021122313 | 5 | 0.63549 | 95323.5 | 0.10589 | 0 | 0.12664 | 1583 | 0.43556 | 34844.8 | 64000 | 1583 | 29740.5 | 0 | 0 | 1348159.325 | 0 | 0
2021122314 | 5 | 0.62561 | 93841.5 | 0.05788 | 0 | 0.14174 | 1771.75 | 0.42779 | 34223.2 | 64000 | 1771.75 | 28069.75 | 0 | 0 | 1350000 | 0 | 0
2021122315 | 5 | 0.61908 | 92862 | 0.03058 | 0 | 0.15629 | 1953.625 | 0.36307 | 29045.6 | 64000 | 1953.625 | 26908.375 | 0 | 0 | 1350000 | 0 | 0
2021122316 | 5 | 0.62187 | 93280.5 | 0.03712 | 0 | 0.18266 | 2283.25 | 0.16186 | 12948.8 | 64000 | 2283.25 | 12948.8 | 14048.45 | 14048.45 | 1350000 | 14048.45 | 0
2021122317 | 5 | 0.64374 | 96561 | 0.12124 | 0 | 0.19952 | 2494 | 0.00962 | 769.6 | 64000 | 2494 | 769.6 | 29297.4 | 15248.95 | 1346168.85 | 29297.4 | 0
2021122318 | 5 | 0.68287 | 102430.5 | 0.35736 | 0 | 0.21416 | 2677 | 0 | 0 | 64000 | 2677 | 0 | 35753.5 | 6456.1 | 1335881.6 | 35753.5 | 0
2021122319 | 5 | 0.68782 | 103173 | 0.51446 | 0 | 0.21989 | 2748.625 | 0 | 0 | 64000 | 2748.625 | 0 | 36424.375 | 670.875 | 1324923.475 | 36424.375 | 0
2021122320 | 5 | 0.6798 | 101970 | 0.64929 | 0 | 0.22902 | 2862.75 | 0 | 0 | 64000 | 2862.75 | 0 | 35107.25 | -1317.125 | 1315282.475 | 35107.25 | 0
2021122321 | 5 | 0.66976 | 100464 | 0.76206 | 0 | 0.23232 | 2904 | 0 | 0 | 64000 | 2904 | 0 | 33560 | -1547.25 | 1307188.725 | 33560 | 0
2021122322 | 5 | 0.6506 | 97590 | 0.75247 | 0 | 0.23677 | 2959.625 | 0 | 0 | 64000 | 2959.625 | 0 | 30630.375 | -2929.625 | 1302024.6 | 30630.375 | 0
2021122323 | 5 | 0.62159 | 93238.5 | 0.79742 | 0 | 0.23005 | 2875.625 | 0 | 0 | 64000 | 2875.625 | 0 | 26362.875 | -4267.5 | 1301127.975 | 26362.875 | 0
2021122324 | 5 | 0.58882 | 88323 | 0.79671 | 0 | 0.24242 | 3030.25 | 0 | 0 | 64000 | 3030.25 | 0 | 21292.75 | -5070.125 | 1305301.475 | 21292.75 | 0
2021122401 | 6 | 0.55986 | 83979 | 0.73832 | 0 | 0.24567 | 3070.875 | 0 | 0 | 64000 | 3070.875 | 0 | 16908.125 | -4384.625 | 1313859.6 | 16908.125 | 0
2021122402 | 6 | 0.5411 | 81165 | 0.84711 | 0 | 0.24517 | 3064.625 | 0 | 0 | 64000 | 3064.625 | 0 | 14100.375 | -2807.75 | 1325225.475 | 14100.375 | 0
2021122403 | 6 | 0.52927 | 79390.5 | 0.83738 | 0 | 0.24394 | 3049.25 | 0 | 0 | 64000 | 3049.25 | 0 | 12341.25 | -1759.125 | 1338350.475 | 12341.25 | 0
2021122404 | 6 | 0.52413 | 78619.5 | 0.80172 | 0 | 0.24481 | 3060.125 | 0 | 0 | 64000 | 3060.125 | 0 | 11559.375 | -781.875 | 1350000 | 11559.375 | 0
2021122405 | 6 | 0.52566 | 78849 | 0.74157 | 0 | 0.29205 | 3650.625 | 0 | 0 | 64000 | 3650.625 | 0 | 11198.375 | -361 | 1350000 | 11198.375 | 0
2021122406 | 6 | 0.53569 | 80353.5 | 0.71725 | 0 | 0.34773 | 4346.625 | 0 | 0 | 64000 | 4346.625 | 0 | 12006.875 | 808.5 | 1350000 | 12006.875 | 0
2021122407 | 6 | 0.55255 | 82882.5 | 0.76721 | 0 | 0.3563 | 4453.75 | 0 | 0 | 64000 | 4453.75 | 0 | 14428.75 | 2421.875 | 1350000 | 14428.75 | 0
2021122408 | 6 | 0.56972 | 85458 | 0.76045 | 0 | 0.36224 | 4528 | 0.01526 | 1220.8 | 64000 | 4528 | 1220.8 | 15709.2 | 1280.45 | 1350000 | 15709.2 | 0
2021122409 | 6 | 0.58187 | 87280.5 | 0.74665 | 0 | 0.34807 | 4350.875 | 0.05532 | 4425.6 | 64000 | 4350.875 | 4425.6 | 14504.025 | -1205.175 | 1350000 | 14504.025 | 0
2021122410 | 6 | 0.58285 | 87427.5 | 0.67677 | 0 | 0.32334 | 4041.75 | 0.10408 | 8326.4 | 64000 | 4041.75 | 8326.4 | 11059.35 | -3444.675 | 1350000 | 11059.35 | 0
2021122411 | 6 | 0.57383 | 86074.5 | 0.5304 | 0 | 0.30135 | 3766.875 | 0.14952 | 11961.6 | 64000 | 3766.875 | 11961.6 | 6346.025 | -4713.325 | 1350000 | 6346.025 | 0
2021122412 | 6 | 0.56179 | 84268.5 | 0.31045 | 0 | 0.27719 | 3464.875 | 0.1668 | 13344 | 64000 | 3464.875 | 13344 | 3459.625 | -2886.4 | 1350000 | 3459.625 | 0
2021122413 | 6 | 0.5485 | 82275 | 0.1348 | 0 | 0.24356 | 3044.5 | 0.17465 | 13972 | 64000 | 3044.5 | 13972 | 1258.5 | -2201.125 | 1350000 | 1258.5 | 0
2021122414 | 6 | 0.53967 | 80950.5 | 0.06094 | 0 | 0.22869 | 2858.625 | 0.15589 | 12471.2 | 64000 | 2858.625 | 12471.2 | 1620.675 | 362.175 | 1350000 | 1620.675 | 0
2021122415 | 6 | 0.53846 | 80769 | 0.06406 | 0 | 0.23007 | 2875.875 | 0.09502 | 7601.6 | 64000 | 2875.875 | 7601.6 | 6291.525 | 4670.85 | 1350000 | 6291.525 | 0
2021122416 | 6 | 0.54298 | 81447 | 0.16779 | 0 | 0.24196 | 3024.5 | 0.03356 | 2684.8 | 64000 | 3024.5 | 2684.8 | 11737.7 | 5446.175 | 1350000 | 11737.7 | 0
2021122417 | 6 | 0.55827 | 83740.5 | 0.3836 | 0 | 0.25816 | 3227 | 0.00236 | 188.8 | 64000 | 3227 | 188.8 | 16324.7 | 4587 | 1350000 | 16324.7 | 0
2021122418 | 6 | 0.58078 | 87117 | 0.67562 | 0 | 0.26857 | 3357.125 | 0 | 0 | 64000 | 3357.125 | 0 | 19759.875 | 3435.175 | 1350000 | 19759.875 | 0
2021122419 | 6 | 0.57415 | 86122.5 | 0.76796 | 0 | 0.24433 | 3054.125 | 0 | 0 | 64000 | 3054.125 | 0 | 19068.375 | -691.5 | 1350000 | 19068.375 | 0
2021122420 | 6 | 0.56244 | 84366 | 0.79934 | 0 | 0.2508 | 3135 | 0 | 0 | 64000 | 3135 | 0 | 17231 | -1837.375 | 1350000 | 17231 | 0
2021122421 | 6 | 0.55249 | 82873.5 | 0.83161 | 0 | 0.26817 | 3352.125 | 0 | 0 | 64000 | 3352.125 | 0 | 15521.375 | -1709.625 | 1350000 | 15521.375 | 0
2021122422 | 6 | 0.54088 | 81132 | 0.83934 | 0 | 0.27006 | 3375.75 | 0 | 0 | 64000 | 3375.75 | 0 | 13756.25 | -1765.125 | 1350000 | 13756.25 | 0
2021122423 | 6 | 0.52353 | 78529.5 | 0.81459 | 0 | 0.2654 | 3317.5 | 0 | 0 | 64000 | 3317.5 | 0 | 11212 | -2544.25 | 1350000 | 11212 | 0
2021122424 | 6 | 0.50064 | 75096 | 0.80953 | 0 | 0.23633 | 2954.125 | 0 | 0 | 64000 | 2954.125 | 0 | 8141.875 | -3070.125 | 1350000 | 8141.875 | 0
2021122501 | 7 | 0.47788 | 71682 | 0.85045 | 0 | 0.24172 | 3021.5 | 0 | 0 | 64000 | 3021.5 | 0 | 4660.5 | -3481.375 | 1350000 | 4660.5 | 0
2021122502 | 7 | 0.46157 | 69235.5 | 0.85651 | 0 | 0.27489 | 3436.125 | 0 | 0 | 64000 | 3436.125 | 0 | 1799.375 | -2861.125 | 1350000 | 1799.375 | 0
2021122503 | 7 | 0.4515 | 67725 | 0.91373 | 0 | 0.29284 | 3660.5 | 0 | 0 | 64000 | 3660.5 | 0 | 64.5 | -1734.875 | 1350000 | 64.5 | 0
2021122504 | 7 | 0.44583 | 66874.5 | 0.9198 | 0 | 0.29883 | 3735.375 | 0 | 0 | 64000 | 2874.5 | 0 | 0 | -64.5 | 1350000 | 0 | 0
2021122505 | 7 | 0.44494 | 66741 | 0.94769 | 0 | 0.30231 | 3778.875 | 0 | 0 | 64000 | 2741 | 0 | 0 | 0 | 1350000 | 0 | 0
2021122506 | 7 | 0.45074 | 67611 | 0.95156 | 0 | 0.29129 | 3641.125 | 0 | 0 | 64000 | 3611 | 0 | 0 | 0 | 1350000 | 0 | 0
2021122507 | 7 | 0.46353 | 69529.5 | 0.95437 | 0 | 0.28773 | 3596.625 | 0 | 0 | 64000 | 3596.625 | 0 | 1932.875 | 1932.875 | 1350000 | 1932.875 | 0
2021122508 | 7 | 0.48159 | 72238.5 | 0.93818 | 0 | 0.26117 | 3264.625 | 0.03808 | 3046.4 | 64000 | 3264.625 | 3046.4 | 1927.475 | -5.4 | 1350000 | 1927.475 | 0
2021122509 | 7 | 0.49889 | 74833.5 | 0.90585 | 0 | 0.2156 | 2695 | 0.19891 | 15912.8 | 64000 | 2695 | 8138.5 | 0 | -1927.475 | 1350000 | 0 | 0
2021122510 | 7 | 0.51062 | 76593 | 0.94258 | 0 | 0.19989 | 2498.625 | 0.34299 | 27439.2 | 64000 | 2498.625 | 10094.375 | 0 | 0 | 1350000 | 0 | 0
2021122511 | 7 | 0.51426 | 77139 | 0.90631 | 0 | 0.19937 | 2492.125 | 0.38897 | 31117.6 | 64000 | 2492.125 | 10646.875 | 0 | 0 | 1350000 | 0 | 0
2021122512 | 7 | 0.51426 | 77139 | 0.90225 | 0 | 0.17483 | 2185.375 | 0.3974 | 31792 | 64000 | 2185.375 | 10953.625 | 0 | 0 | 1350000 | 0 | 0
2021122513 | 7 | 0.5072 | 76080 | 0.86898 | 0 | 0.16591 | 2073.875 | 0.40567 | 32453.6 | 64000 | 2073.875 | 10006.125 | 0 | 0 | 1350000 | 0 | 0
2021122514 | 7 | 0.49638 | 74457 | 0.86467 | 0 | 0.17575 | 2196.875 | 0.40754 | 32603.2 | 64000 | 2196.875 | 8260.125 | 0 | 0 | 1350000 | 0 | 0
2021122515 | 7 | 0.48979 | 73468.5 | 0.79068 | 0 | 0.19605 | 2450.625 | 0.35355 | 28284 | 64000 | 2450.625 | 7017.875 | 0 | 0 | 1350000 | 0 | 0
2021122516 | 7 | 0.49037 | 73555.5 | 0.80302 | 0 | 0.22437 | 2804.625 | 0.16377 | 13101.6 | 64000 | 2804.625 | 6750.875 | 0 | 0 | 1350000 | 0 | 0
2021122517 | 7 | 0.49925 | 74887.5 | 0.69374 | 0 | 0.22948 | 2868.5 | 0.0114 | 912 | 64000 | 2868.5 | 912 | 7107 | 7107 | 1350000 | 7107 | 0
2021122518 | 7 | 0.51897 | 77845.5 | 0.61221 | 0 | 0.22593 | 2824.125 | 0 | 0 | 64000 | 2824.125 | 0 | 11021.375 | 3914.375 | 1350000 | 11021.375 | 0
2021122519 | 7 | 0.52083 | 78124.5 | 0.54196 | 0 | 0.22984 | 2873 | 0 | 0 | 64000 | 2873 | 0 | 11251.5 | 230.125 | 1350000 | 11251.5 | 0
2021122520 | 7 | 0.51525 | 77287.5 | 0.65247 | 0 | 0.2341 | 2926.25 | 0 | 0 | 64000 | 2926.25 | 0 | 10361.25 | -890.25 | 1350000 | 10361.25 | 0
2021122521 | 7 | 0.50971 | 76456.5 | 0.76077 | 0 | 0.2324 | 2905 | 0 | 0 | 64000 | 2905 | 0 | 9551.5 | -809.75 | 1350000 | 9551.5 | 0
2021122522 | 7 | 0.50092 | 75138 | 0.84812 | 0 | 0.21786 | 2723.25 | 0 | 0 | 64000 | 2723.25 | 0 | 8414.75 | -1136.75 | 1350000 | 8414.75 | 0
2021122523 | 7 | 0.48611 | 72916.5 | 0.87412 | 0 | 0.22902 | 2862.75 | 0 | 0 | 64000 | 2862.75 | 0 | 6053.75 | -2361 | 1350000 | 6053.75 | 0
2021122524 | 7 | 0.46573 | 69859.5 | 0.85132 | 0 | 0.2576 | 3220 | 0 | 0 | 64000 | 3220 | 0 | 2639.5 | -3414.25 | 1350000 | 2639.5 | 0
2021122601 | 1 | 0.44661 | 66991.5 | 0.85029 | 0 | 0.27068 | 3383.5 | 0 | 0 | 64000 | 2991.5 | 0 | 0 | -2639.5 | 1350000 | 0 | 0
2021122602 | 1 | 0.43398 | 65097 | 0.81876 | 0 | 0.26446 | 3305.75 | 0 | 0 | 64000 | 1097 | 0 | 0 | 0 | 1350000 | 0 | 0
2021122603 | 1 | 0.42841 | 64261.5 | 0.82186 | 0 | 0.23836 | 2979.5 | 0 | 0 | 64000 | 261.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021122604 | 1 | 0.42691 | 64036.5 | 0.87394 | 0 | 0.20941 | 2617.625 | 0 | 0 | 64000 | 36.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021122605 | 1 | 0.43095 | 64642.5 | 0.87396 | 0 | 0.17806 | 2225.75 | 0 | 0 | 64000 | 642.5 | 0 | 0 | 0 | 1350000 | 0 | 0
2021122606 | 1 | 0.44151 | 66226.5 | 0.78861 | 0 | 0.15305 | 1913.125 | 0 | 0 | 64000 | 1913.125 | 0 | 313.375 | 313.375 | 1350000 | 313.375 | 0
2021122607 | 1 | 0.45807 | 68710.5 | 0.82095 | 0 | 0.13166 | 1645.75 | 0 | 0 | 64000 | 1645.75 | 0 | 3064.75 | 2751.375 | 1350000 | 3064.75 | 0
2021122608 | 1 | 0.47875 | 71812.5 | 0.77051 | 0 | 0.13299 | 1662.375 | 0.04132 | 3305.6 | 64000 | 1662.375 | 3305.6 | 2844.525 | -220.225 | 1350000 | 2844.525 | 0
2021122609 | 1 | 0.492 | 73800 | 0.71742 | 0 | 0.12295 | 1536.875 | 0.1256 | 10048 | 64000 | 1536.875 | 8263.125 | 0 | -2844.525 | 1350000 | 0 | 0
2021122610 | 1 | 0.49728 | 74592 | 0.64567 | 0 | 0.12043 | 1505.375 | 0.14294 | 11435.2 | 64000 | 1505.375 | 9086.625 | 0 | 0 | 1350000 | 0 | 0
2021122611 | 1 | 0.4981 | 74715 | 0.70843 | 0 | 0.1223 | 1528.75 | 0.18651 | 14920.8 | 64000 | 1528.75 | 9186.25 | 0 | 0 | 1350000 | 0 | 0
2021122612 | 1 | 0.4963 | 74445 | 0.661 | 0 | 0.11428 | 1428.5 | 0.20598 | 16478.4 | 64000 | 1428.5 | 9016.5 | 0 | 0 | 1350000 | 0 | 0
2021122613 | 1 | 0.49601 | 74401.5 | 0.5992 | 0 | 0.10122 | 1265.25 | 0.21488 | 17190.4 | 64000 | 1265.25 | 9136.25 | 0 | 0 | 1350000 | 0 | 0
2021122614 | 1 | 0.49304 | 73956 | 0.68753 | 0 | 0.08875 | 1109.375 | 0.17431 | 13944.8 | 64000 | 1109.375 | 8846.625 | 0 | 0 | 1350000 | 0 | 0
2021122615 | 1 | 0.49346 | 74019 | 0.71267 | 0 | 0.08857 | 1107.125 | 0.12582 | 10065.6 | 64000 | 1107.125 | 8911.875 | 0 | 0 | 1350000 | 0 | 0
2021122616 | 1 | 0.50203 | 75304.5 | 0.67846 | 0 | 0.0899 | 1123.75 | 0.05213 | 4170.4 | 64000 | 1123.75 | 4170.4 | 6010.35 | 6010.35 | 1350000 | 6010.35 | 0
2021122617 | 1 | 0.52482 | 78723 | 0.67767 | 0 | 0.08111 | 1013.875 | 0.00403 | 322.4 | 64000 | 1013.875 | 322.4 | 13386.725 | 7376.375 | 1350000 | 13386.725 | 0
2021122618 | 1 | 0.56503 | 84754.5 | 0.68592 | 0 | 0.08067 | 1008.375 | 0 | 0 | 64000 | 1008.375 | 0 | 19746.125 | 6359.4 | 1350000 | 19746.125 | 0
2021122619 | 1 | 0.57814 | 86721 | 0.65362 | 0 | 0.08156 | 1019.5 | 0 | 0 | 64000 | 1019.5 | 0 | 21701.5 | 1955.375 | 1350000 | 21701.5 | 0
2021122620 | 1 | 0.57726 | 86589 | 0.56524 | 0 | 0.08309 | 1038.625 | 0 | 0 | 64000 | 1038.625 | 0 | 21550.375 | -151.125 | 1350000 | 21550.375 | 0
2021122621 | 1 | 0.57111 | 85666.5 | 0.51805 | 0 | 0.08492 | 1061.5 | 0 | 0 | 64000 | 1061.5 | 0 | 20605 | -945.375 | 1350000 | 20605 | 0
2021122622 | 1 | 0.55878 | 83817 | 0.55004 | 0 | 0.07855 | 981.875 | 0 | 0 | 64000 | 981.875 | 0 | 18835.125 | -1769.875 | 1350000 | 18835.125 | 0
2021122623 | 1 | 0.54064 | 81096 | 0.46763 | 0 | 0.07046 | 880.75 | 0 | 0 | 64000 | 880.75 | 0 | 16215.25 | -2619.875 | 1350000 | 16215.25 | 0
2021122624 | 1 | 0.51876 | 77814 | 0.42695 | 0 | 0.06806 | 850.75 | 0 | 0 | 64000 | 850.75 | 0 | 12963.25 | -3252 | 1350000 | 12963.25 | 0
2021122701 | 2 | 0.50255 | 75382.5 | 0.31543 | 0 | 0.06424 | 803 | 0 | 0 | 64000 | 803 | 0 | 10579.5 | -2383.75 | 1350000 | 10579.5 | 0
2021122702 | 2 | 0.49244 | 73866 | 0.26559 | 0 | 0.06388 | 798.5 | 0 | 0 | 64000 | 798.5 | 0 | 9067.5 | -1512 | 1350000 | 9067.5 | 0
2021122703 | 2 | 0.48984 | 73476 | 0.2101 | 0 | 0.0709 | 886.25 | 0 | 0 | 64000 | 886.25 | 0 | 8589.75 | -477.75 | 1350000 | 8589.75 | 0
2021122704 | 2 | 0.49224 | 73836 | 0.26858 | 0 | 0.07846 | 980.75 | 0 | 0 | 64000 | 980.75 | 0 | 8855.25 | 265.5 | 1350000 | 8855.25 | 0
2021122705 | 2 | 0.504 | 75600 | 0.31513 | 0 | 0.08179 | 1022.375 | 0 | 0 | 64000 | 1022.375 | 0 | 10577.625 | 1722.375 | 1350000 | 10577.625 | 0
2021122706 | 2 | 0.52554 | 78831 | 0.47648 | 0 | 0.08273 | 1034.125 | 0 | 0 | 64000 | 1034.125 | 0 | 13796.875 | 3219.25 | 1350000 | 13796.875 | 0
2021122707 | 2 | 0.55782 | 83673 | 0.56861 | 0 | 0.07524 | 940.5 | 0 | 0 | 64000 | 940.5 | 0 | 18732.5 | 4935.625 | 1350000 | 18732.5 | 0
2021122708 | 2 | 0.58626 | 87939 | 0.55566 | 0 | 0.06225 | 778.125 | 0.0278 | 2224 | 64000 | 778.125 | 2224 | 20936.875 | 2204.375 | 1350000 | 20936.875 | 0
2021122709 | 2 | 0.60227 | 90340.5 | 0.47689 | 0 | 0.05102 | 637.75 | 0.09356 | 7484.8 | 64000 | 637.75 | 7484.8 | 18217.95 | -2718.925 | 1350000 | 18217.95 | 0
2021122710 | 2 | 0.61576 | 92364 | 0.5476 | 0 | 0.04992 | 624 | 0.13704 | 10963.2 | 64000 | 624 | 10963.2 | 16776.8 | -1441.15 | 1350000 | 16776.8 | 0
2021122711 | 2 | 0.625 | 93750 | 0.53936 | 0 | 0.04486 | 560.75 | 0.15302 | 12241.6 | 64000 | 560.75 | 12241.6 | 16947.65 | 170.85 | 1350000 | 16947.65 | 0
2021122712 | 2 | 0.62753 | 94129.5 | 0.56233 | 0 | 0.0403 | 503.75 | 0.18493 | 14794.4 | 64000 | 503.75 | 14794.4 | 14831.35 | -2116.3 | 1350000 | 14831.35 | 0
2021122713 | 2 | 0.62477 | 93715.5 | 0.45231 | 0 | 0.04085 | 510.625 | 0.17755 | 14204 | 64000 | 510.625 | 14204 | 15000.875 | 169.525 | 1350000 | 15000.875 | 0
2021122714 | 2 | 0.62311 | 93466.5 | 0.41911 | 0 | 0.04477 | 559.625 | 0.18147 | 14517.6 | 64000 | 559.625 | 14517.6 | 14389.275 | -611.6 | 1350000 | 14389.275 | 0
2021122715 | 2 | 0.61992 | 92988 | 0.43274 | 0 | 0.06274 | 784.25 | 0.15475 | 12380 | 64000 | 784.25 | 12380 | 15823.75 | 1434.475 | 1350000 | 15823.75 | 0
2021122716 | 2 | 0.61755 | 92632.5 | 0.50065 | 0 | 0.07396 | 924.5 | 0.0709 | 5672 | 64000 | 924.5 | 5672 | 22036 | 6212.25 | 1350000 | 22036 | 0
2021122717 | 2 | 0.62792 | 94188 | 0.61861 | 0 | 0.10255 | 1281.875 | 0.00667 | 533.6 | 64000 | 1281.875 | 533.6 | 28372.525 | 6336.525 | 1347093.725 | 28372.525 | 0
2021122718 | 2 | 0.6516 | 97740 | 0.61829 | 0 | 0.11838 | 1479.75 | 0 | 0 | 64000 | 1479.75 | 0 | 32260.25 | 3887.725 | 1340299.725 | 32260.25 | 0
2021122719 | 2 | 0.6507 | 97605 | 0.6897 | 0 | 0.1256 | 1570 | 0 | 0 | 64000 | 1570 | 0 | 32035 | -225.25 | 1333730.975 | 32035 | 0
2021122720 | 2 | 0.6374 | 95610 | 0.7179 | 0 | 0.13703 | 1712.875 | 0 | 0 | 64000 | 1712.875 | 0 | 29897.125 | -2137.875 | 1329300.1 | 29897.125 | 0
2021122721 | 2 | 0.6221 | 93315 | 0.65872 | 0 | 0.12763 | 1595.375 | 0 | 0 | 64000 | 1595.375 | 0 | 27719.625 | -2177.5 | 1327046.725 | 27719.625 | 0
2021122722 | 2 | 0.6006 | 90090 | 0.59802 | 0 | 0.12489 | 1561.125 | 0 | 0 | 64000 | 1561.125 | 0 | 24528.875 | -3190.75 | 1327984.1 | 24528.875 | 0
2021122723 | 2 | 0.57194 | 85791 | 0.61688 | 0 | 0.13246 | 1655.75 | 0 | 0 | 64000 | 1655.75 | 0 | 20135.25 | -4393.625 | 1333315.1 | 20135.25 | 0
2021122724 | 2 | 0.54267 | 81400.5 | 0.64822 | 0 | 0.11682 | 1460.25 | 0 | 0 | 64000 | 1460.25 | 0 | 15940.25 | -4195 | 1342841.1 | 15940.25 | 0
2021122801 | 3 | 0.5204 | 78060 | 0.68526 | 0 | 0.08766 | 1095.75 | 0 | 0 | 64000 | 1095.75 | 0 | 12964.25 | -2976 | 1350000 | 12964.25 | 0
2021122802 | 3 | 0.50535 | 75802.5 | 0.72431 | 0 | 0.07358 | 919.75 | 0 | 0 | 64000 | 919.75 | 0 | 10882.75 | -2081.5 | 1350000 | 10882.75 | 0
2021122803 | 3 | 0.49829 | 74743.5 | 0.78675 | 0 | 0.05079 | 634.875 | 0 | 0 | 64000 | 634.875 | 0 | 10108.625 | -774.125 | 1350000 | 10108.625 | 0
2021122804 | 3 | 0.49858 | 74787 | 0.8024 | 0 | 0.03344 | 418 | 0 | 0 | 64000 | 418 | 0 | 10369 | 260.375 | 1350000 | 10369 | 0
2021122805 | 3 | 0.50809 | 76213.5 | 0.8146 | 0 | 0.02698 | 337.25 | 0 | 0 | 64000 | 337.25 | 0 | 11876.25 | 1507.25 | 1350000 | 11876.25 | 0
2021122806 | 3 | 0.53232 | 79848 | 0.77064 | 0 | 0.02429 | 303.625 | 0 | 0 | 64000 | 303.625 | 0 | 15544.375 | 3668.125 | 1350000 | 15544.375 | 0
2021122807 | 3 | 0.56655 | 84982.5 | 0.7511 | 0 | 0.02162 | 270.25 | 0 | 0 | 64000 | 270.25 | 0 | 20712.25 | 5167.875 | 1350000 | 20712.25 | 0
2021122808 | 3 | 0.59601 | 89401.5 | 0.77167 | 0 | 0.01529 | 191.125 | 0.01223 | 978.4 | 64000 | 191.125 | 978.4 | 24231.975 | 3519.725 | 1350000 | 24231.975 | 0
2021122809 | 3 | 0.609 | 91350 | 0.72449 | 0 | 0.0096 | 120 | 0.04212 | 3369.6 | 64000 | 120 | 3369.6 | 23860.4 | -371.575 | 1350000 | 23860.4 | 0
2021122810 | 3 | 0.6136 | 92040 | 0.58733 | 0 | 0.01413 | 176.625 | 0.09388 | 7510.4 | 64000 | 176.625 | 7510.4 | 20352.975 | -3507.425 | 1350000 | 20352.975 | 0
2021122811 | 3 | 0.61644 | 92466 | 0.42411 | 0 | 0.01805 | 225.625 | 0.16232 | 12985.6 | 64000 | 225.625 | 12985.6 | 15254.775 | -5098.2 | 1350000 | 15254.775 | 0
2021122812 | 3 | 0.61501 | 92251.5 | 0.27944 | 0 | 0.02418 | 302.25 | 0.20902 | 16721.6 | 64000 | 302.25 | 16721.6 | 11227.65 | -4027.125 | 1350000 | 11227.65 | 0
2021122813 | 3 | 0.61377 | 92065.5 | 0.22494 | 0 | 0.02284 | 285.5 | 0.23797 | 19037.6 | 64000 | 285.5 | 19037.6 | 8742.4 | -2485.25 | 1350000 | 8742.4 | 0
2021122814 | 3 | 0.61308 | 91962 | 0.20617 | 0 | 0.02525 | 315.625 | 0.24944 | 19955.2 | 64000 | 315.625 | 19955.2 | 7691.175 | -1051.225 | 1350000 | 7691.175 | 0
2021122815 | 3 | 0.6089 | 91335 | 0.12945 | 0 | 0.02936 | 367 | 0.23577 | 18861.6 | 64000 | 367 | 18861.6 | 8106.4 | 415.225 | 1350000 | 8106.4 | 0
2021122816 | 3 | 0.61122 | 91683 | 0.24112 | 0 | 0.03018 | 377.25 | 0.11072 | 8857.6 | 64000 | 377.25 | 8857.6 | 18448.15 | 10341.75 | 1350000 | 18448.15 | 0
2021122817 | 3 | 0.62579 | 93868.5 | 0.34053 | 0 | 0.03078 | 384.75 | 0.00546 | 436.8 | 64000 | 384.75 | 436.8 | 29046.95 | 10598.8 | 1346419.3 | 29046.95 | 0
2021122818 | 3 | 0.64858 | 97287 | 0.46286 | 0 | 0.03547 | 443.375 | 0 | 0 | 64000 | 443.375 | 0 | 32843.625 | 3796.675 | 1339041.925 | 32843.625 | 0
2021122819 | 3 | 0.64679 | 97018.5 | 0.61164 | 0 | 0.04524 | 565.5 | 0 | 0 | 64000 | 565.5 | 0 | 32453 | -390.625 | 1332055.175 | 32453 | 0
2021122820 | 3 | 0.63344 | 95016 | 0.64016 | 0 | 0.0452 | 565 | 0 | 0 | 64000 | 565 | 0 | 30451 | -2002 | 1327070.425 | 30451 | 0
2021122821 | 3 | 0.61853 | 92779.5 | 0.59748 | 0 | 0.04095 | 511.875 | 0 | 0 | 64000 | 511.875 | 0 | 28267.625 | -2183.375 | 1324269.05 | 28267.625 | 0
2021122822 | 3 | 0.5956 | 89340 | 0.55296 | 0 | 0.03854 | 481.75 | 0 | 0 | 64000 | 481.75 | 0 | 24858.25 | -3409.375 | 1324877.05 | 24858.25 | 0
2021122823 | 3 | 0.56549 | 84823.5 | 0.54738 | 0 | 0.04466 | 558.25 | 0 | 0 | 64000 | 558.25 | 0 | 20265.25 | -4593 | 1330078.05 | 20265.25 | 0
2021122824 | 3 | 0.53425 | 80137.5 | 0.53565 | 0 | 0.04989 | 623.625 | 0 | 0 | 64000 | 623.625 | 0 | 15513.875 | -4751.375 | 1340030.425 | 15513.875 | 0
2021122901 | 4 | 0.50994 | 76491 | 0.48402 | 0 | 0.05096 | 637 | 0 | 0 | 64000 | 637 | 0 | 11854 | -3659.875 | 1350000 | 11854 | 0
2021122902 | 4 | 0.49509 | 74263.5 | 0.47428 | 0 | 0.05692 | 711.5 | 0 | 0 | 64000 | 711.5 | 0 | 9552 | -2302 | 1350000 | 9552 | 0
2021122903 | 4 | 0.48553 | 72829.5 | 0.53094 | 0 | 0.0642 | 802.5 | 0 | 0 | 64000 | 802.5 | 0 | 8027 | -1525 | 1350000 | 8027 | 0
2021122904 | 4 | 0.48363 | 72544.5 | 0.50097 | 0 | 0.07329 | 916.125 | 0 | 0 | 64000 | 916.125 | 0 | 7628.375 | -398.625 | 1350000 | 7628.375 | 0
2021122905 | 4 | 0.49037 | 73555.5 | 0.46172 | 0 | 0.07897 | 987.125 | 0 | 0 | 64000 | 987.125 | 0 | 8568.375 | 940 | 1350000 | 8568.375 | 0
2021122906 | 4 | 0.51004 | 76506 | 0.49312 | 0 | 0.0886 | 1107.5 | 0 | 0 | 64000 | 1107.5 | 0 | 11398.5 | 2830.125 | 1350000 | 11398.5 | 0
2021122907 | 4 | 0.54125 | 81187.5 | 0.51631 | 0 | 0.09058 | 1132.25 | 0 | 0 | 64000 | 1132.25 | 0 | 16055.25 | 4656.75 | 1350000 | 16055.25 | 0
2021122908 | 4 | 0.56828 | 85242 | 0.62655 | 0 | 0.09601 | 1200.125 | 0.00618 | 494.4 | 64000 | 1200.125 | 494.4 | 19547.475 | 3492.225 | 1350000 | 19547.475 | 0
2021122909 | 4 | 0.58292 | 87438 | 0.59711 | 0 | 0.10965 | 1370.625 | 0.0224 | 1792 | 64000 | 1370.625 | 1792 | 20275.375 | 727.9 | 1350000 | 20275.375 | 0
2021122910 | 4 | 0.59318 | 88977 | 0.58755 | 0 | 0.13569 | 1696.125 | 0.04906 | 3924.8 | 64000 | 1696.125 | 3924.8 | 19356.075 | -919.3 | 1350000 | 19356.075 | 0
2021122911 | 4 | 0.59934 | 89901 | 0.50579 | 0 | 0.1503 | 1878.75 | 0.07759 | 6207.2 | 64000 | 1878.75 | 6207.2 | 17815.05 | -1541.025 | 1350000 | 17815.05 | 0
2021122912 | 4 | 0.59885 | 89827.5 | 0.39495 | 0 | 0.14038 | 1754.75 | 0.08686 | 6948.8 | 64000 | 1754.75 | 6948.8 | 17123.95 | -691.1 | 1350000 | 17123.95 | 0
2021122913 | 4 | 0.59139 | 88708.5 | 0.33084 | 0 | 0.1278 | 1597.5 | 0.07956 | 6364.8 | 64000 | 1597.5 | 6364.8 | 16746.2 | -377.75 | 1350000 | 16746.2 | 0
2021122914 | 4 | 0.58773 | 88159.5 | 0.29594 | 0 | 0.11742 | 1467.75 | 0.06035 | 4828 | 64000 | 1467.75 | 4828 | 17863.75 | 1117.55 | 1350000 | 17863.75 | 0
2021122915 | 4 | 0.58552 | 87828 | 0.29358 | 0 | 0.13102 | 1637.75 | 0.0399 | 3192 | 64000 | 1637.75 | 3192 | 18998.25 | 1134.5 | 1350000 | 18998.25 | 0
2021122916 | 4 | 0.58612 | 87918 | 0.21579 | 0 | 0.1409 | 1761.25 | 0.01458 | 1166.4 | 64000 | 1761.25 | 1166.4 | 20990.35 | 1992.1 | 1350000 | 20990.35 | 0
2021122917 | 4 | 0.60033 | 90049.5 | 0.15225 | 0 | 0.13464 | 1683 | 0.00013 | 10.4 | 64000 | 1683 | 10.4 | 24356.1 | 3365.75 | 1350000 | 24356.1 | 0
2021122918 | 4 | 0.62959 | 94438.5 | 0.17578 | 0 | 0.11426 | 1428.25 | 0 | 0 | 64000 | 1428.25 | 0 | 29010.25 | 4654.15 | 1346456 | 29010.25 | 0
2021122919 | 4 | 0.62879 | 94318.5 | 0.20586 | 0 | 0.09139 | 1142.375 | 0 | 0 | 64000 | 1142.375 | 0 | 29176.125 | 165.875 | 1342746.125 | 29176.125 | 0
2021122920 | 4 | 0.61685 | 92527.5 | 0.17505 | 0 | 0.08673 | 1084.125 | 0 | 0 | 64000 | 1084.125 | 0 | 27443.375 | -1732.75 | 1340769 | 27443.375 | 0
2021122921 | 4 | 0.60335 | 90502.5 | 0.07204 | 0 | 0.10886 | 1360.75 | 0 | 0 | 64000 | 1360.75 | 0 | 25141.75 | -2301.625 | 1341093.5 | 25141.75 | 0
2021122922 | 4 | 0.58349 | 87523.5 | 0.06778 | 0 | 0.1322 | 1652.5 | 0 | 0 | 64000 | 1652.5 | 0 | 21871 | -3270.75 | 1344688.75 | 21871 | 0
2021122923 | 4 | 0.55555 | 83332.5 | 0.09863 | 0 | 0.11454 | 1431.75 | 0 | 0 | 64000 | 1431.75 | 0 | 17900.75 | -3970.25 | 1350000 | 17900.75 | 0
2021122924 | 4 | 0.5263 | 78945 | 0.12899 | 0 | 0.09709 | 1213.625 | 0.00201 | 160.8 | 64000 | 1213.625 | 160.8 | 13570.575 | -4330.175 | 1350000 | 13570.575 | 0
2021123001 | 5 | 0.50203 | 75304.5 | 0.21328 | 0 | 0.07645 | 955.625 | 0 | 0 | 64000 | 955.625 | 0 | 10348.875 | -3221.7 | 1350000 | 10348.875 | 0
2021123002 | 5 | 0.48804 | 73206 | 0.16273 | 0 | 0.07721 | 965.125 | 0 | 0 | 64000 | 965.125 | 0 | 8240.875 | -2108 | 1350000 | 8240.875 | 0
2021123003 | 5 | 0.47944 | 71916 | 0.13376 | 0 | 0.06226 | 778.25 | 0 | 0 | 64000 | 778.25 | 0 | 7137.75 | -1103.125 | 1350000 | 7137.75 | 0
2021123004 | 5 | 0.47702 | 71553 | 0.12321 | 0 | 0.04013 | 501.625 | 0 | 0 | 64000 | 501.625 | 0 | 7051.375 | -86.375 | 1350000 | 7051.375 | 0
2021123005 | 5 | 0.4831 | 72465 | 0.14896 | 0 | 0.03055 | 381.875 | 0 | 0 | 64000 | 381.875 | 0 | 8083.125 | 1031.75 | 1350000 | 8083.125 | 0
2021123006 | 5 | 0.5016 | 75240 | 0.13062 | 0 | 0.03672 | 459 | 0 | 0 | 64000 | 459 | 0 | 10781 | 2697.875 | 1350000 | 10781 | 0
2021123007 | 5 | 0.53276 | 79914 | 0.09906 | 0 | 0.04482 | 560.25 | 0 | 0 | 64000 | 560.25 | 0 | 15353.75 | 4572.75 | 1350000 | 15353.75 | 0
2021123008 | 5 | 0.56007 | 84010.5 | 0.0856 | 0 | 0.05652 | 706.5 | 0.01507 | 1205.6 | 64000 | 706.5 | 1205.6 | 18098.4 | 2744.65 | 1350000 | 18098.4 | 0
2021123009 | 5 | 0.57617 | 86425.5 | 0.04881 | 0 | 0.06117 | 764.625 | 0.08024 | 6419.2 | 64000 | 764.625 | 6419.2 | 15241.675 | -2856.725 | 1350000 | 15241.675 | 0
2021123010 | 5 | 0.58562 | 87843 | 0.02941 | 0 | 0.06967 | 870.875 | 0.18938 | 15150.4 | 64000 | 870.875 | 15150.4 | 7821.725 | -7419.95 | 1350000 | 7821.725 | 0
2021123011 | 5 | 0.5915 | 88725 | 0.02815 | 0 | 0.09624 | 1203 | 0.25958 | 20766.4 | 64000 | 1203 | 20766.4 | 2755.6 | -5066.125 | 1350000 | 2755.6 | 0
2021123012 | 5 | 0.59184 | 88776 | 0.03426 | 0 | 0.13067 | 1633.375 | 0.2843 | 22744 | 64000 | 1633.375 | 22744 | 398.625 | -2356.975 | 1350000 | 398.625 | 0
2021123013 | 5 | 0.58672 | 88008 | 0.02823 | 0 | 0.15162 | 1895.25 | 0.27274 | 21819.2 | 64000 | 1895.25 | 21819.2 | 293.55 | -105.075 | 1350000 | 293.55 | 0
2021123014 | 5 | 0.58361 | 87541.5 | 0.06713 | 0 | 0.16574 | 2071.75 | 0.21773 | 17418.4 | 64000 | 2071.75 | 17418.4 | 4051.35 | 3757.8 | 1350000 | 4051.35 | 0
2021123015 | 5 | 0.5783 | 86745 | 0.08951 | 0 | 0.16372 | 2046.5 | 0.12836 | 10268.8 | 64000 | 2046.5 | 10268.8 | 10429.7 | 6378.35 | 1350000 | 10429.7 | 0
2021123016 | 5 | 0.57672 | 86508 | 0.13893 | 0 | 0.15856 | 1982 | 0.04056 | 3244.8 | 64000 | 1982 | 3244.8 | 17281.2 | 6851.5 | 1350000 | 17281.2 | 0
2021123017 | 5 | 0.58938 | 88407 | 0.1717 | 0 | 0.15489 | 1936.125 | 0.00223 | 178.4 | 64000 | 1936.125 | 178.4 | 22292.475 | 5011.275 | 1350000 | 22292.475 | 0
2021123018 | 5 | 0.61419 | 92128.5 | 0.17318 | 0 | 0.16252 | 2031.5 | 0 | 0 | 64000 | 2031.5 | 0 | 26097 | 3804.525 | 1349369.25 | 26097 | 0
2021123019 | 5 | 0.61414 | 92121 | 0.23827 | 0 | 0.20059 | 2507.375 | 0 | 0 | 64000 | 2507.375 | 0 | 25613.625 | -483.375 | 1349221.875 | 25613.625 | 0
2021123020 | 5 | 0.60112 | 90168 | 0.22954 | 0 | 0.21637 | 2704.625 | 0 | 0 | 64000 | 2704.625 | 0 | 23463.375 | -2150.25 | 1350000 | 23463.375 | 0
2021123021 | 5 | 0.58859 | 88288.5 | 0.19375 | 0 | 0.23308 | 2913.5 | 0 | 0 | 64000 | 2913.5 | 0 | 21375 | -2088.375 | 1350000 | 21375 | 0
2021123022 | 5 | 0.56851 | 85276.5 | 0.19426 | 0 | 0.26195 | 3274.375 | 0 | 0 | 64000 | 3274.375 | 0 | 18002.125 | -3372.875 | 1350000 | 18002.125 | 0
2021123023 | 5 | 0.54313 | 81469.5 | 0.19675 | 0 | 0.2539 | 3173.75 | 0 | 0 | 64000 | 3173.75 | 0 | 14295.75 | -3706.375 | 1350000 | 14295.75 | 0
2021123024 | 5 | 0.5141 | 77115 | 0.20835 | 0 | 0.23024 | 2878 | 0 | 0 | 64000 | 2878 | 0 | 10237 | -4058.75 | 1350000 | 10237 | 0
2021123101 | 6 | 0.49036 | 73554 | 0.20598 | 0 | 0.23602 | 2950.25 | 0 | 0 | 64000 | 2950.25 | 0 | 6603.75 | -3633.25 | 1350000 | 6603.75 | 0
2021123102 | 6 | 0.4747 | 71205 | 0.11524 | 0 | 0.25266 | 3158.25 | 0 | 0 | 64000 | 3158.25 | 0 | 4046.75 | -2557 | 1350000 | 4046.75 | 0
2021123103 | 6 | 0.4646 | 69690 | 0.11128 | 0 | 0.22875 | 2859.375 | 0 | 0 | 64000 | 2859.375 | 0 | 2830.625 | -1216.125 | 1350000 | 2830.625 | 0
2021123104 | 6 | 0.46086 | 69129 | 0.15939 | 0 | 0.17978 | 2247.25 | 0 | 0 | 64000 | 2247.25 | 0 | 2881.75 | 51.125 | 1350000 | 2881.75 | 0
2021123105 | 6 | 0.46502 | 69753 | 0.26416 | 0 | 0.1302 | 1627.5 | 0 | 0 | 64000 | 1627.5 | 0 | 4125.5 | 1243.75 | 1350000 | 4125.5 | 0
2021123106 | 6 | 0.47664 | 71496 | 0.39705 | 0 | 0.12255 | 1531.875 | 0 | 0 | 64000 | 1531.875 | 0 | 5964.125 | 1838.625 | 1350000 | 5964.125 | 0
2021123107 | 6 | 0.49519 | 74278.5 | 0.39316 | 0 | 0.16556 | 2069.5 | 0 | 0 | 64000 | 2069.5 | 0 | 8209 | 2244.875 | 1350000 | 8209 | 0
2021123108 | 6 | 0.51205 | 76807.5 | 0.39013 | 0 | 0.20032 | 2504 | 0.00084 | 67.2 | 64000 | 2504 | 67.2 | 10236.3 | 2027.3 | 1350000 | 10236.3 | 0
2021123109 | 6 | 0.52537 | 78805.5 | 0.36785 | 0 | 0.22257 | 2782.125 | 0.01134 | 907.2 | 64000 | 2782.125 | 907.2 | 11116.175 | 879.875 | 1350000 | 11116.175 | 0
2021123110 | 6 | 0.53725 | 80587.5 | 0.32567 | 0 | 0.2369 | 2961.25 | 0.02652 | 2121.6 | 64000 | 2961.25 | 2121.6 | 11504.65 | 388.475 | 1350000 | 11504.65 | 0
2021123111 | 6 | 0.54493 | 81739.5 | 0.25736 | 0 | 0.25255 | 3156.875 | 0.04992 | 3993.6 | 64000 | 3156.875 | 3993.6 | 10589.025 | -915.625 | 1350000 | 10589.025 | 0
2021123112 | 6 | 0.54723 | 82084.5 | 0.20014 | 0 | 0.2834 | 3542.5 | 0.07253 | 5802.4 | 64000 | 3542.5 | 5802.4 | 8739.6 | -1849.425 | 1350000 | 8739.6 | 0
2021123113 | 6 | 0.54493 | 81739.5 | 0.24997 | 0 | 0.36509 | 4563.625 | 0.08159 | 6527.2 | 64000 | 4563.625 | 6527.2 | 6648.675 | -2090.925 | 1350000 | 6648.675 | 0
2021123114 | 6 | 0.54042 | 81063 | 0.27799 | 0 | 0.4089 | 5111.25 | 0.0766 | 6128 | 64000 | 5111.25 | 6128 | 5823.75 | -824.925 | 1350000 | 5823.75 | 0
2021123115 | 6 | 0.53816 | 80724 | 0.14986 | 0 | 0.508 | 6350 | 0.07404 | 5923.2 | 64000 | 6350 | 5923.2 | 4450.8 | -1372.95 | 1350000 | 4450.8 | 0
2021123116 | 6 | 0.5403 | 81045 | 0.09271 | 0 | 0.56766 | 7095.75 | 0.03502 | 2801.6 | 64000 | 7095.75 | 2801.6 | 7147.65 | 2696.85 | 1350000 | 7147.65 | 0
2021123117 | 6 | 0.55533 | 83299.5 | 0.10886 | 0 | 0.54639 | 6829.875 | 0.00449 | 359.2 | 64000 | 6829.875 | 359.2 | 12110.425 | 4962.775 | 1350000 | 12110.425 | 0
2021123118 | 6 | 0.58266 | 87399 | 0.19342 | 0 | 0.56127 | 7015.875 | 0 | 0 | 64000 | 7015.875 | 0 | 16383.125 | 4272.7 | 1350000 | 16383.125 | 0
2021123119 | 6 | 0.57877 | 86815.5 | 0.25501 | 0 | 0.50154 | 6269.25 | 0 | 0 | 64000 | 6269.25 | 0 | 16546.25 | 163.125 | 1350000 | 16546.25 | 0
2021123120 | 6 | 0.56365 | 84547.5 | 0.33196 | 0 | 0.37815 | 4726.875 | 0 | 0 | 64000 | 4726.875 | 0 | 15820.625 | -725.625 | 1350000 | 15820.625 | 0
2021123121 | 6 | 0.54634 | 81951 | 0.40324 | 0 | 0.38286 | 4785.75 | 0 | 0 | 64000 | 4785.75 | 0 | 13165.25 | -2655.375 | 1350000 | 13165.25 | 0
2021123122 | 6 | 0.52874 | 79311 | 0.42957 | 0 | 0.33217 | 4152.125 | 0 | 0 | 64000 | 4152.125 | 0 | 11158.875 | -2006.375 | 1350000 | 11158.875 | 0
2021123123 | 6 | 0.50858 | 76287 | 0.48988 | 0 | 0.29173 | 3646.625 | 0 | 0 | 64000 | 3646.625 | 0 | 8640.375 | -2518.5 | 1350000 | 8640.375 | 0
2021123124 | 6 | 0.48942 | 73413 | 0.57599 | 0 | 0.255 | 3187.5 | 0 | 0 | 64000 | 3187.5 | 0 | 6225.5 | -2414.875 | 1350000 | 6225.5 | 0
Note on T4: PJM 2021 hourly demand wind and solar. This file is used to create all the variable resources input data for this spreadsheet.
Note on C17: Base loaded nuclear net maximum power output in MW, i.e. the total nameplate MWs.
Note on P17: Nuclear Thermal Nameplate MWs in electrical output if the nuclear were conventional nuclear power but in this instance all the heat goes to thermal storage.
Note on R17: The number of hours storage when discharged or charged at the nuclear nameplate rating MWs.
Note on D18: New annual peak demand forecast.
Note on F18: Installed nameplate MW generation capacity of either offshore wind or hydro generation capacity.
Note on H18: Installed nameplate MW generation capacity of onshore wind.
Note on J18: Installed nameplate MW generation capacity of solar.
Note on Q18: This is the electrical energy that can serve MWh of load. Actual thermal energy is about three times greater.
Note on R18: This is the electrical MWs serving load from thermal storage.
Note on A19: This integer format of year month day hour allows for easy sorting of the date time stamp in text editors.
Note on B19: D is the day of the week Sunday is day 1
Note on C19: The historical test year 2021 hourly loads profile is in per unit with the annual peak having 1 per unit. See reference 1.
Note on D19: The per unit loads to the left are multiplied times the annual peak forecast for this simulation which is simply scaling up the historical data to the new load forecast.
Note on E19: OSW is off shore wind. It could be relabled Hydro. In either case this column is the per unit profile of historcal data for the test year of 2021. Its important the same test year be used for all historical weather and load data.
Note on F19: The per unit OSW values to the left are multiplied times the installed nameplate OSW capacity to produce hourly MWs. Its important this column's values are always less than the hourly load MWs because this column is assumed to be 100% dispatched.
Note on G19: On shore wind per unit hourly profile for the historical 2021 year from actual data posted by PJM. See Reference 1.
Note on H19: The per unit on shore wind values to the left are multiplied times the on shore wind capacity.
Note on I19: Solar per unit hourly profile for the historical 2021 year from actual data posted by PJM. See Reference 1.
Note on J19: The per unit solar values to the left are multiplied times the solar MW capacity.
Note on L19: If (Demand - OSW > Nucl Pmax, then Nucl Pmax, otherwise Demand - OSW).
Note on M19: If (Demand - OSW - Nucl > Wind, then Wind, otherwise Demand - OSW - Nuclear).
Note on N19: If (Demand - OSW - Nucl - Wind> Solar, then Solar, otherwise Demand - OSW - Nucl - Wind).
Note on O19: Demand - OSW - Nucl - Wind - Solar, i.e. the remaining unserved load.
Note on P19: The rate of change this hour, i.e. Peaking MW this hour minus Peaking MW last hour.
Note on Q19: The MWHs electrical energy storage that can serve load. When charging, some nuclear energy is lost. There is also a continuous drain of energy. See Reference 3 for details.
Note on R19: IF (Storage MWh out + Nuclear - Shunt Loss is < Peaking Load, then use this formula, otherwise use Peaking Load.
Note on S19: Any remaining unserved load, i.e. Peaking - Thermal MWs is served by gas turbines.