## HDATA
NoFossilFuelinTexas.xlsx helps find solutions for the amount of solar-wind-nuclear-storage needed to serve ERCOT load. | [12 empty] | 35 GW of new nuclear the wind at 40 and solar at 70 and storage of 700 the energy cost is 16.8 c/kWh.
The solar profile is 2019 ERCOT hourly solar data with adjustments I made so the per unit values < 1. Capacity Factor is 26%.
Copy the historical demand solar and wind per unit hourly profiles into their columns. The demand must have a 1 per unit max.
Yellow blocks are input data Red are output calculations. Also read the notes. | [9 empty] | flat rate
100 | GW peak demand for the year - set to about a 2030 level. | [6 empty] | payback |  | cent/kWh | Act % CF | Max % CF | $Bn invested
70 | GW Solar - maximum powr rating at a cost of --> |  |  |  |  | 1500 | $/kw | 7 | years = | 14.3884 | 17.0011 | 26.1363 | 105 | This amount of solar is designed to require minimal new transmission.
40 | GW Wind - maximum powr rating at a cost of --> |  |  |  |  | 2000 | $/kw | 7 | years = | 19.0835 | 17.0911 | 36.2043 | 80 | This amount of wind is designed to not require a buildout of new transmission.
40 | GW Nuclear - maxim power rating at a cost of --> |  |  |  |  | 10000 | $/kW | 10 | years = | 11.4215 | 99.9476 | 100 | 400 | This amount of nuclear is substantial and will require competely new rules at the federal and state levels.
700 | GWh Battery - rated energy capacty at cost of --> |  |  |  |  | 200 | $/kWh | 7 | years = | 3.8883 | 6.5582 | 100 | 140 | This amount of storage is minimal utilizing the overlapping power supply of all the resources.
demand | solar | wind | batt GWh | nuclear | solar | wind |  |  | annual = | 16.8031 |  | total $Bn | 725 | <= 16.8 c/kwh is the best I can do with minimizing the energy cost adjusting wind solar nuclear and storage.
per unit | per unit | per unit | 700 | GW | GW | GW |  | min hour GWh = |  | 48.0504 | last hour GWh = |  | 694.0826
0.49594 | 0 | 0.62494 | 700 | 40 | 0 | 9.594
0.49793 | 0 | 0.62976 | 700 | 40 | 0 | 9.793 | battery level eqn. |  | IF: storage + sources - load < max storage
0.49903 | 0 | 0.61985 | 700 | 40 | 0 | 9.903 |  |  | Then: storage is = storage + sources - load
0.49911 | 0 | 0.59937 | 700 | 40 | 0 | 9.911 |  |  | Else: storage is = max storage
0.50163 | 0 | 0.58951 | 700 | 40 | 0 | 10.163
0.51329 | 0 | 0.57111 | 700 | 40 | 0 | 11.329 | Methodology: |  | Each hour the above equation either uses or charges up
0.52648 | 0 | 0.52422 | 700 | 40 | 0 | 12.648 |  |  | the battery. A valid solution has the min hour GWh > 0.
0.5389 | 0.0009 | 0.4837 | 700 | 40 | 0.063 | 13.827 |  |  | When solving this problem try to get the lowest energy
0.54528 | 0.0245 | 0.44035 | 700 | 40 | 1.715 | 12.813 |  |  | cost in the box while keeping the min hour GWh > 0.
0.55379 | 0.064 | 0.38736 | 700 | 40 | 4.48 | 10.899
0.56319 | 0.1175 | 0.32791 | 700 | 40 | 8.225 | 8.094 |  | Notes: | Add solar-wind-nuclear-battery until min hour GWh > 0.
0.56581 | 0.1655 | 0.28624 | 700 | 40 | 11.585 | 4.996 |  |  | Try reducing the battery size while increasing the sources.
0.56251 | 0.1889 | 0.25505 | 700 | 40 | 13.223 | 3.028 |  |  | Try to keep dumped energies as low as possible.
0.55679 | 0.1475 | 0.23325 | 700 | 40 | 10.325 | 5.354 |  |  | The last hour kWh will be a little less than battery kWh.
0.55229 | 0.1118 | 0.21414 | 700 | 40 | 7.826 | 7.403 |  |  | Program by Eugene Preston on Nov 30, 2020
0.54817 | 0.0643 | 0.18574 | 697.1136 | 40 | 4.501 | 7.4296 |  |  | Posted on web page |  | https://egpreston.com
0.55255 | 0.0276 | 0.16181 | 690.263 | 40 | 1.932 | 6.4724
0.57089 | 0.0041 | 0.14863 | 679.4062 | 40 | 0.287 | 5.9452 | Disussion: |  | The nuclear cost is high on purpose. The payback is
0.60716 | 0 | 0.13518 | 664.0974 | 40 | 0 | 5.4072 |  |  | short to represent a high expectation for return profit.
0.60843 | 0 | 0.12912 | 648.4192 | 40 | 0 | 5.1648 |  |  | The solar cost $/kW cost is higher than actual plant cost
0.60462 | 0 | 0.12098 | 632.7964 | 40 | 0 | 4.8392 |  |  | to include new transmission line costs for future solar.
0.59649 | 0 | 0.11917 | 617.9142 | 40 | 0 | 4.7668 |  |  | The wind $/kWh should also include transmission costs.
0.58062 | 0 | 0.10966 | 604.2386 | 40 | 0 | 4.3864 |  |  | The cents/kWh of each source is based on Act % CF.
0.55399 | 0 | 0.11014 | 593.2452 | 40 | 0 | 4.4056 |  |  | The annual cents per kWh is a flat energy fee paying for
0.53424 | 0 | 0.11247 | 584.32 | 40 | 0 | 4.4988 |  |  | all capital costs for the year, i.e. no demand charges.
0.52151 | 0 | 0.10659 | 576.4326 | 40 | 0 | 4.2636
0.5156 | 0 | 0.11544 | 569.4902 | 40 | 0 | 4.6176
0.51723 | 0 | 0.13522 | 563.176 | 40 | 0 | 5.4088
0.5263 | 0 | 0.14906 | 556.5084 | 40 | 0 | 5.9624
0.54786 | 0 | 0.16203 | 548.2036 | 40 | 0 | 6.4812
0.58562 | 0 | 0.12973 | 534.8308 | 40 | 0 | 5.1892
0.6232 | 0 | 0.11725 | 517.2008 | 40 | 0 | 4.69
0.6463 | 0.0065 | 0.09123 | 496.675 | 40 | 0.455 | 3.6492
0.6578 | 0.0336 | 0.09053 | 476.8682 | 40 | 2.352 | 3.6212
0.67272 | 0.0775 | 0.08508 | 458.4244 | 40 | 5.425 | 3.4032
0.68372 | 0.0848 | 0.05668 | 438.2556 | 40 | 5.936 | 2.2672
0.68941 | 0.1 | 0.05606 | 418.557 | 40 | 7 | 2.2424
0.68984 | 0.1264 | 0.05796 | 400.7394 | 40 | 8.848 | 2.3184
0.68849 | 0.1007 | 0.06097 | 381.3782 | 40 | 7.049 | 2.4388
0.68577 | 0.0662 | 0.09367 | 361.182 | 40 | 4.634 | 3.7468
0.68476 | 0.0324 | 0.07823 | 338.1032 | 40 | 2.268 | 3.1292
0.69277 | 0.0051 | 0.07553 | 312.2044 | 40 | 0.357 | 3.0212
0.72099 | 0 | 0.0577 | 282.4134 | 40 | 0 | 2.308
0.71125 | 0 | 0.03907 | 252.8512 | 40 | 0 | 1.5628
0.69454 | 0 | 0.02646 | 224.4556 | 40 | 0 | 1.0584
0.67392 | 0 | 0.03513 | 198.4688 | 40 | 0 | 1.4052
0.64527 | 0 | 0.04579 | 175.7734 | 40 | 0 | 1.8316
0.60721 | 0 | 0.02827 | 156.1832 | 40 | 0 | 1.1308
0.58212 | 0 | 0.04322 | 139.7 | 40 | 0 | 1.7288
0.56054 | 0 | 0.06427 | 126.2168 | 40 | 0 | 2.5708
0.5518 | 0 | 0.09249 | 114.7364 | 40 | 0 | 3.6996
0.54904 | 0 | 0.13151 | 105.0928 | 40 | 0 | 5.2604
0.55465 | 0 | 0.15508 | 95.831 | 40 | 0 | 6.2032
0.57279 | 0 | 0.14633 | 84.4052 | 40 | 0 | 5.8532
0.60396 | 0 | 0.16681 | 70.6816 | 40 | 0 | 6.6724
0.63754 | 0.0004 | 0.16535 | 53.5696 | 40 | 0.028 | 6.614
0.65069 | 0.1827 | 0.16902 | 48.0504 | 40 | 12.789 | 6.7608
0.65419 | 0.6171 | 0.16915 | 72.5944 | 40 | 49.963 | 0
0.65785 | 0.7136 | 0.18565 | 104.1874 | 40 | 57.378 | 0
0.65477 | 0.7311 | 0.22011 | 138.6918 | 40 | 59.9814 | 1.4211e-14
0.64457 | 0.7208 | 0.26054 | 175.1124 | 40 | 60.8776 | 0
0.62769 | 0.7159 | 0.29049 | 214.076 | 40 | 61.7326 | 0
0.61347 | 0.7341 | 0.33658 | 257.5792 | 40 | 64.8502 | 0
0.60035 | 0.7261 | 0.36095 | 302.8092 | 40 | 65.265 | 0
0.59679 | 0.5402 | 0.29663 | 332.8094 | 40 | 49.6792 | 5.6843e-14
0.60603 | 0.1048 | 0.23506 | 328.9448 | 40 | 7.336 | 9.4024
0.64346 | 0 | 0.18928 | 312.17 | 40 | 0 | 7.5712
0.65371 | 0 | 0.18623 | 294.2482 | 40 | 0 | 7.4492
0.65607 | 0 | 0.26249 | 279.1408 | 40 | 0 | 10.4996
0.65017 | 0 | 0.26801 | 264.8442 | 40 | 0 | 10.7204
0.63196 | 0 | 0.23931 | 251.2206 | 40 | 0 | 9.5724
0.60391 | 0 | 0.24461 | 240.614 | 40 | 0 | 9.7844
0.58393 | 0 | 0.29867 | 234.1678 | 40 | 0 | 11.9468
0.57226 | 0 | 0.36918 | 231.709 | 40 | 0 | 14.7672
0.56938 | 0 | 0.41965 | 231.557 | 40 | 0 | 16.786
0.57115 | 0 | 0.45543 | 232.6592 | 40 | 0 | 18.2172
0.57637 | 0 | 0.48202 | 234.303 | 40 | 0 | 19.2808
0.59731 | 0 | 0.47401 | 233.5324 | 40 | 0 | 18.9604
0.63298 | 0 | 0.42367 | 227.1812 | 40 | 0 | 16.9468
0.66668 | 0.0019 | 0.37272 | 215.555 | 40 | 0.133 | 14.9088
0.67099 | 0.2436 | 0.32516 | 218.5144 | 40 | 17.052 | 13.0064
0.64554 | 0.749 | 0.25156 | 256.4528 | 40 | 62.4924 | 2.8422e-14
0.61762 | 0.8337 | 0.09639 | 296.9054 | 40 | 62.2146 | 0
0.58693 | 0.8343 | 0.0449 | 338.4094 | 40 | 60.197 | 0
0.55772 | 0.8227 | 0.05082 | 382.2592 | 40 | 59.6218 | 0
0.53412 | 0.8256 | 0.05622 | 428.888 | 40 | 60.0408 | -5.6843e-14
0.51683 | 0.8343 | 0.06865 | 478.352 | 40 | 61.147 | 0
0.50183 | 0.8081 | 0.08046 | 527.9544 | 40 | 59.7854 | 0
0.49408 | 0.6037 | 0.06631 | 563.4578 | 40 | 44.9114 | 0
0.49373 | 0.1199 | 0.0522 | 564.5658 | 40 | 8.393 | 2.088
0.53057 | 0 | 0.06241 | 554.0052 | 40 | 0 | 2.4964
0.54218 | 0 | 0.10364 | 543.9328 | 40 | 0 | 4.1456
0.54422 | 0 | 0.14695 | 535.3888 | 40 | 0 | 5.878
0.54503 | 0 | 0.1734 | 527.8218 | 40 | 0 | 6.936
0.53988 | 0 | 0.1937 | 521.5818 | 40 | 0 | 7.748
0.52594 | 0 | 0.20556 | 517.2102 | 40 | 0 | 8.2224
0.50882 | 0 | 0.18875 | 513.8782 | 40 | 0 | 7.55
0.50256 | 0 | 0.20954 | 512.0038 | 40 | 0 | 8.3816
0.50298 | 0 | 0.22847 | 510.8446 | 40 | 0 | 9.1388
0.50631 | 0 | 0.23006 | 509.416 | 40 | 0 | 9.2024
0.51503 | 0 | 0.23661 | 507.3774 | 40 | 0 | 9.4644
0.52881 | 0 | 0.19985 | 502.4904 | 40 | 0 | 7.994
0.55069 | 0 | 0.16933 | 494.1946 | 40 | 0 | 6.7732
0.57847 | 0.0025 | 0.17433 | 483.4958 | 40 | 0.175 | 6.9732
0.59424 | 0.2225 | 0.17994 | 486.8444 | 40 | 15.575 | 7.1976
0.57807 | 0.7315 | 0.16508 | 526.8456 | 40 | 57.8082 | 0
0.54688 | 0.7669 | 0.1281 | 570.9646 | 40 | 58.807 | 0
0.51822 | 0.751 | 0.11045 | 616.1306 | 40 | 56.988 | 0
0.49561 | 0.7459 | 0.14491 | 664.579 | 40 | 58.0094 | 0
0.47546 | 0.7519 | 0.21042 | 700 | 40 | 42.967 | 0
0.46397 | 0.7621 | 0.26448 | 700 | 40 | 6.397 | 0
0.458 | 0.7238 | 0.28655 | 700 | 40 | 5.8 | 0
0.45311 | 0.5162 | 0.31764 | 700 | 40 | 5.311 | 0
0.45549 | 0.0843 | 0.30411 | 700 | 40 | 5.549 | 0
0.48646 | 0 | 0.41014 | 700 | 40 | 0 | 8.646
0.49491 | 0 | 0.58101 | 700 | 40 | 0 | 9.491
0.488 | 0 | 0.67209 | 700 | 40 | 0 | 8.8
0.48898 | 0 | 0.70925 | 700 | 40 | 0 | 8.898
0.47876 | 0 | 0.70199 | 700 | 40 | 0 | 7.876
0.47224 | 0 | 0.69363 | 700 | 40 | 0 | 7.224
0.45411 | 0 | 0.67223 | 700 | 40 | 0 | 5.411
0.4451 | 0 | 0.66931 | 700 | 40 | 0 | 4.51
0.44008 | 0 | 0.6613 | 700 | 40 | 0 | 4.008
0.43996 | 0 | 0.66356 | 700 | 40 | 0 | 3.996
0.44337 | 0 | 0.67453 | 700 | 40 | 0 | 4.337
0.45057 | 0 | 0.6655 | 700 | 40 | 0 | 5.057
0.46769 | 0 | 0.67727 | 700 | 40 | 0 | 6.769
0.48703 | 0.0014 | 0.72765 | 700 | 40 | 0.098 | 8.605
0.49806 | 0.083 | 0.73185 | 700 | 40 | 5.81 | 3.996
0.49861 | 0.3186 | 0.67762 | 700 | 40 | 9.861 | 0
0.48898 | 0.46 | 0.65245 | 700 | 40 | 8.898 | 0
0.47876 | 0.3699 | 0.69739 | 700 | 40 | 7.876 | 0
0.47348 | 0.3268 | 0.73026 | 700 | 40 | 7.348 | 0
0.46684 | 0.3082 | 0.7123 | 700 | 40 | 6.684 | 0
0.46252 | 0.2743 | 0.70332 | 700 | 40 | 6.252 | 0
0.45693 | 0.2502 | 0.6893 | 700 | 40 | 5.693 | 0
0.45839 | 0.1537 | 0.69717 | 700 | 40 | 5.839 | 0
0.4627 | 0.023 | 0.70368 | 700 | 40 | 1.61 | 4.66
0.49384 | 0 | 0.7422 | 700 | 40 | 0 | 9.384
0.49975 | 0 | 0.7403 | 700 | 40 | 0 | 9.975
0.49528 | 0 | 0.7541 | 700 | 40 | 0 | 9.528
0.48494 | 0 | 0.74875 | 700 | 40 | 0 | 8.494
0.46416 | 0 | 0.72035 | 700 | 40 | 0 | 6.416
0.43784 | 0 | 0.6839 | 700 | 40 | 0 | 3.784
0.41024 | 0 | 0.63759 | 700 | 40 | 0 | 1.024
0.39411 | 0 | 0.60707 | 700 | 39.411 | 0 | 0
0.38579 | 0 | 0.57301 | 700 | 38.579 | 0 | 0
0.38175 | 0 | 0.56297 | 700 | 38.175 | 0 | 0
0.38273 | 0 | 0.57106 | 700 | 38.273 | 0 | 0
0.40054 | 0 | 0.56394 | 700 | 40 | 0 | 0.054
0.43606 | 0 | 0.52842 | 700 | 40 | 0 | 3.606
0.4741 | 0.0002 | 0.53399 | 700 | 40 | 0.014 | 7.396
0.47915 | 0.1298 | 0.51303 | 700 | 40 | 7.915 | 0
0.48359 | 0.5768 | 0.45504 | 700 | 40 | 8.359 | 0
0.48882 | 0.7081 | 0.37298 | 700 | 40 | 8.882 | 0
0.49502 | 0.7075 | 0.31964 | 700 | 40 | 9.502 | 0
0.49522 | 0.6959 | 0.28341 | 700 | 40 | 9.522 | 0
0.49842 | 0.6584 | 0.30415 | 700 | 40 | 9.842 | 0
0.50223 | 0.6695 | 0.3337 | 700 | 40 | 10.223 | 0
0.5004 | 0.7093 | 0.3291 | 700 | 40 | 10.04 | 0
0.49754 | 0.5451 | 0.29279 | 700 | 40 | 9.754 | 0
0.49444 | 0.1131 | 0.29168 | 700 | 40 | 7.917 | 1.527
0.52244 | 0 | 0.34365 | 700 | 40 | 0 | 12.244
0.53004 | 0 | 0.39196 | 700 | 40 | 0 | 13.004
0.51981 | 0 | 0.42089 | 700 | 40 | 0 | 11.981
0.50358 | 0 | 0.46136 | 700 | 40 | 0 | 10.358
0.47927 | 0 | 0.51099 | 700 | 40 | 0 | 7.927
0.44916 | 0 | 0.50617 | 700 | 40 | 0 | 4.916
0.41843 | 0 | 0.46379 | 700 | 40 | 0 | 1.843
0.40266 | 0 | 0.4173 | 700 | 40 | 0 | 0.266
0.39567 | 0 | 0.36285 | 700 | 39.567 | 0 | 0
0.39318 | 0 | 0.3245 | 700 | 39.318 | 0 | 0
0.39873 | 0 | 0.33795 | 700 | 39.873 | 0 | 0
0.4179 | 0 | 0.36188 | 700 | 40 | 0 | 1.79
0.45913 | 0 | 0.38068 | 700 | 40 | 0 | 5.913
0.50807 | 0.0016 | 0.35989 | 700 | 40 | 0.112 | 10.695
0.50509 | 0.0954 | 0.36396 | 700 | 40 | 6.678 | 3.831
0.50238 | 0.2518 | 0.40541 | 700 | 40 | 10.238 | 0
0.50376 | 0.3692 | 0.44212 | 700 | 40 | 10.376 | 0
0.50367 | 0.5117 | 0.48494 | 700 | 40 | 10.367 | 0
0.50521 | 0.5904 | 0.48604 | 700 | 40 | 10.521 | 0
0.50253 | 0.6513 | 0.45119 | 700 | 40 | 10.253 | 0
0.50323 | 0.6773 | 0.39284 | 700 | 40 | 10.323 | 0
0.50077 | 0.5615 | 0.39373 | 700 | 40 | 10.077 | 0
0.49523 | 0.3875 | 0.36776 | 700 | 40 | 9.523 | 0
0.49816 | 0.042 | 0.33445 | 700 | 40 | 2.94 | 6.876
0.52772 | 0 | 0.32419 | 700 | 40 | 0 | 12.772
0.53675 | 0 | 0.38776 | 700 | 40 | 0 | 13.675
0.52999 | 0 | 0.40837 | 700 | 40 | 0 | 12.999
0.51487 | 0 | 0.39081 | 700 | 40 | 0 | 11.487
0.4926 | 0 | 0.37984 | 700 | 40 | 0 | 9.26
0.45812 | 0 | 0.34874 | 700 | 40 | 0 | 5.812
0.43604 | 0 | 0.35294 | 700 | 40 | 0 | 3.604
0.42035 | 0 | 0.33538 | 700 | 40 | 0 | 2.035
0.41671 | 0 | 0.33587 | 700 | 40 | 0 | 1.671
0.41507 | 0 | 0.32003 | 700 | 40 | 0 | 1.507
0.42295 | 0 | 0.30141 | 700 | 40 | 0 | 2.295
0.44327 | 0 | 0.26116 | 700 | 40 | 0 | 4.327
0.48935 | 0 | 0.20175 | 699.135 | 40 | 0 | 8.07
0.54217 | 0.0014 | 0.1979 | 692.932 | 40 | 0.098 | 7.916
0.54166 | 0.0694 | 0.1903 | 691.236 | 40 | 4.858 | 7.612
0.53781 | 0.2124 | 0.17074 | 699.1526 | 40 | 21.6976 | 0
0.53191 | 0.3191 | 0.1661 | 700 | 40 | 14.0384 | 0
0.52413 | 0.3989 | 0.19609 | 700 | 40 | 12.413 | 0
0.51056 | 0.4447 | 0.1868 | 700 | 40 | 11.056 | 0
0.50154 | 0.489 | 0.16889 | 700 | 40 | 10.154 | 0
0.49554 | 0.4266 | 0.16787 | 700 | 40 | 9.554 | 0
0.48804 | 0.3419 | 0.19295 | 700 | 40 | 8.804 | 0
0.48772 | 0.148 | 0.19874 | 700 | 40 | 8.772 | 0
0.4973 | 0.0292 | 0.1872 | 699.802 | 40 | 2.044 | 7.488
0.53486 | 0 | 0.17411 | 693.2804 | 40 | 0 | 6.9644
0.54928 | 0 | 0.21246 | 686.8508 | 40 | 0 | 8.4984
0.55041 | 0 | 0.22356 | 680.7522 | 40 | 0 | 8.9424
0.54445 | 0 | 0.25417 | 676.474 | 40 | 0 | 10.1668
0.52476 | 0 | 0.26633 | 674.6512 | 40 | 0 | 10.6532
0.49437 | 0 | 0.29225 | 676.9042 | 40 | 0 | 11.69
0.47056 | 0 | 0.29601 | 681.6886 | 40 | 0 | 11.8404
0.45967 | 0 | 0.29681 | 687.594 | 40 | 0 | 11.8724
0.45575 | 0 | 0.29969 | 694.0066 | 40 | 0 | 11.9876
0.45579 | 0 | 0.28805 | 699.9496 | 40 | 0 | 11.522
0.46307 | 0 | 0.31649 | 700 | 40 | 0 | 6.3574
0.48483 | 0 | 0.37126 | 700 | 40 | 0 | 8.483
0.53059 | 0 | 0.37656 | 700 | 40 | 0 | 13.059
0.58179 | 0.0008 | 0.3767 | 696.945 | 40 | 0.056 | 15.068
0.57465 | 0.0757 | 0.4127 | 700 | 40 | 5.299 | 15.221
0.56737 | 0.3935 | 0.40996 | 700 | 40 | 16.737 | 0
0.5596 | 0.5627 | 0.44314 | 700 | 40 | 15.96 | 0
0.54928 | 0.6195 | 0.45831 | 700 | 40 | 14.928 | 0
0.53727 | 0.6195 | 0.45415 | 700 | 40 | 13.727 | 0
0.52779 | 0.622 | 0.42788 | 700 | 40 | 12.779 | 0
0.51808 | 0.5706 | 0.41814 | 700 | 40 | 11.808 | 0
0.51118 | 0.4546 | 0.40912 | 700 | 40 | 11.118 | 0
0.51258 | 0.247 | 0.4499 | 700 | 40 | 11.258 | 0
0.5215 | 0.046 | 0.44818 | 700 | 40 | 3.22 | 8.93
0.55289 | 0 | 0.45933 | 700 | 40 | 0 | 15.289
0.56086 | 0 | 0.52953 | 700 | 40 | 0 | 16.086
0.56064 | 0 | 0.60371 | 700 | 40 | 0 | 16.064
0.55144 | 0 | 0.64378 | 700 | 40 | 0 | 15.144
0.52715 | 0 | 0.6674 | 700 | 40 | 0 | 12.715
0.49459 | 0 | 0.64825 | 700 | 40 | 0 | 9.459
0.46954 | 0 | 0.64352 | 700 | 40 | 0 | 6.954
0.45468 | 0 | 0.63644 | 700 | 40 | 0 | 5.468
0.4481 | 0 | 0.62821 | 700 | 40 | 0 | 4.81
0.44571 | 0 | 0.60176 | 700 | 40 | 0 | 4.571
0.45309 | 0 | 0.57597 | 700 | 40 | 0 | 5.309
0.46961 | 0 | 0.59818 | 700 | 40 | 0 | 6.961
0.51318 | 0 | 0.61065 | 700 | 40 | 0 | 11.318
0.56023 | 0.0001 | 0.593 | 700 | 40 | 0.007 | 16.016
0.55819 | 0.0151 | 0.58172 | 700 | 40 | 1.057 | 14.762
0.55305 | 0.0552 | 0.5677 | 700 | 40 | 3.864 | 11.441
0.55709 | 0.0982 | 0.5903 | 700 | 40 | 6.874 | 8.835
0.55219 | 0.1869 | 0.59221 | 700 | 40 | 13.083 | 2.136
0.54231 | 0.2657 | 0.55686 | 700 | 40 | 14.231 | 0
0.5331 | 0.3123 | 0.53851 | 700 | 40 | 13.31 | 0
0.52988 | 0.3567 | 0.58557 | 700 | 40 | 12.988 | 0
0.52127 | 0.3466 | 0.57925 | 700 | 40 | 12.127 | 0
0.52328 | 0.2818 | 0.55669 | 700 | 40 | 12.328 | 0
0.53051 | 0.1169 | 0.51988 | 700 | 40 | 8.183 | 4.868
0.54994 | 0.0001 | 0.56089 | 700 | 40 | 0.007 | 14.987
0.54392 | 0 | 0.55664 | 700 | 40 | 0 | 14.392
0.53337 | 0 | 0.44141 | 700 | 40 | 0 | 13.337
0.51973 | 0 | 0.42195 | 700 | 40 | 0 | 11.973
0.49825 | 0 | 0.43663 | 700 | 40 | 0 | 9.825
0.47609 | 0 | 0.42266 | 700 | 40 | 0 | 7.609
0.44861 | 0 | 0.43717 | 700 | 40 | 0 | 4.861
0.43257 | 0 | 0.46172 | 700 | 40 | 0 | 3.257
0.42141 | 0 | 0.48021 | 700 | 40 | 0 | 2.141
0.41735 | 0 | 0.52148 | 700 | 40 | 0 | 1.735
0.41977 | 0 | 0.56385 | 700 | 40 | 0 | 1.977
0.4306 | 0 | 0.5915 | 700 | 40 | 0 | 3.06
0.45139 | 0 | 0.59499 | 700 | 40 | 0 | 5.139
0.47689 | 0.0018 | 0.58982 | 700 | 40 | 0.126 | 7.563
0.49732 | 0.2209 | 0.57889 | 700 | 40 | 9.732 | 0
0.51024 | 0.6863 | 0.55483 | 700 | 40 | 11.024 | 0
0.51769 | 0.6567 | 0.59588 | 700 | 40 | 11.769 | 0
0.52312 | 0.6512 | 0.65334 | 700 | 40 | 12.312 | 0
0.52373 | 0.6827 | 0.64064 | 700 | 40 | 12.373 | 0
0.52144 | 0.6926 | 0.63078 | 700 | 40 | 12.144 | 0
0.51267 | 0.7351 | 0.6041 | 700 | 40 | 11.267 | 0
0.50968 | 0.7497 | 0.54651 | 700 | 40 | 10.968 | 0
0.50959 | 0.6116 | 0.46003 | 700 | 40 | 10.959 | 0
0.5164 | 0.1565 | 0.3456 | 700 | 40 | 10.955 | 0.685
0.53377 | 0.0001 | 0.22559 | 695.6536 | 40 | 0.007 | 9.0236
0.5455 | 0 | 0.21047 | 689.5224 | 40 | 0 | 8.4188
0.53973 | 0 | 0.22612 | 684.5942 | 40 | 0 | 9.0448
0.53611 | 0 | 0.21794 | 679.7008 | 40 | 0 | 8.7176
0.52277 | 0 | 0.1876 | 674.9278 | 40 | 0 | 7.504
0.5124 | 0 | 0.19392 | 671.4446 | 40 | 0 | 7.7568
0.49593 | 0 | 0.1922 | 669.5396 | 40 | 0 | 7.688
0.48457 | 0 | 0.21263 | 669.5878 | 40 | 0 | 8.5052
0.48357 | 0 | 0.24236 | 670.9252 | 40 | 0 | 9.6944
0.48415 | 0 | 0.24404 | 672.2718 | 40 | 0 | 9.7616
0.48887 | 0 | 0.25227 | 673.4756 | 40 | 0 | 10.0908
0.49754 | 0 | 0.25302 | 673.8424 | 40 | 0 | 10.1208
0.51521 | 0 | 0.25249 | 672.421 | 40 | 0 | 10.0996
0.54161 | 0.0016 | 0.267 | 669.052 | 40 | 0.112 | 10.68
0.56172 | 0.1835 | 0.24585 | 675.559 | 40 | 12.845 | 9.834
0.5733 | 0.443 | 0.19392 | 696.9958 | 40 | 38.7668 | 0
0.57656 | 0.4242 | 0.15672 | 700 | 40 | 20.6602 | 0
0.5655 | 0.418 | 0.09466 | 700 | 40 | 16.55 | 0
0.55457 | 0.5286 | 0.06246 | 700 | 40 | 15.457 | 0
0.54084 | 0.6588 | 0.0522 | 700 | 40 | 14.084 | 0
0.5302 | 0.6847 | 0.05348 | 700 | 40 | 13.02 | 0
0.52319 | 0.676 | 0.05874 | 700 | 40 | 12.319 | 0
0.52736 | 0.5444 | 0.07524 | 700 | 40 | 12.736 | 0
0.53962 | 0.1474 | 0.09201 | 700 | 40 | 10.318 | 3.644
0.57998 | 0.0001 | 0.10116 | 686.0554 | 40 | 0.007 | 4.0464
0.59963 | 0 | 0.10833 | 670.4256 | 40 | 0 | 4.3332
0.602 | 0 | 0.09855 | 654.1676 | 40 | 0 | 3.942
0.59409 | 0 | 0.08688 | 638.2338 | 40 | 0 | 3.4752
0.57478 | 0 | 0.07944 | 623.9334 | 40 | 0 | 3.1776
0.54452 | 0 | 0.0756 | 612.5054 | 40 | 0 | 3.024
0.52468 | 0 | 0.05923 | 602.4066 | 40 | 0 | 2.3692
0.5114 | 0 | 0.05458 | 593.4498 | 40 | 0 | 2.1832
0.50851 | 0 | 0.05357 | 584.7416 | 40 | 0 | 2.1428
0.51254 | 0 | 0.05082 | 575.5204 | 40 | 0 | 2.0328
0.52234 | 0 | 0.05122 | 565.3352 | 40 | 0 | 2.0488
0.55011 | 0 | 0.05578 | 552.5554 | 40 | 0 | 2.2312
0.6049 | 0 | 0.06498 | 534.6646 | 40 | 0 | 2.5992
0.65707 | 0.0004 | 0.07414 | 511.9512 | 40 | 0.028 | 2.9656
0.6547 | 0.0223 | 0.08573 | 491.4714 | 40 | 1.561 | 3.4292
0.64852 | 0.0785 | 0.0901 | 475.7184 | 40 | 5.495 | 3.604
0.64206 | 0.1497 | 0.07462 | 464.9762 | 40 | 10.479 | 2.9848
0.63069 | 0.2531 | 0.08922 | 463.193 | 40 | 17.717 | 3.5688
0.60926 | 0.274 | 0.10006 | 465.4494 | 40 | 19.18 | 4.0024
0.58746 | 0.2925 | 0.0974 | 471.0744 | 40 | 24.371 | 0
0.56885 | 0.2987 | 0.10638 | 479.3536 | 40 | 25.1642 | 0
0.5526 | 0.2238 | 0.09895 | 483.7176 | 40 | 19.624 | 0
0.55395 | 0.119 | 0.08546 | 480.071 | 40 | 8.33 | 3.4184
0.56957 | 0.0178 | 0.07122 | 467.2088 | 40 | 1.246 | 2.8488
0.61747 | 0.0001 | 0.08396 | 448.8272 | 40 | 0.007 | 3.3584
0.6315 | 0 | 0.14221 | 431.3656 | 40 | 0 | 5.6884
0.63138 | 0 | 0.18393 | 415.5848 | 40 | 0 | 7.3572
0.61934 | 0 | 0.1949 | 401.4468 | 40 | 0 | 7.796
0.58875 | 0 | 0.18945 | 390.1498 | 40 | 0 | 7.578
0.55583 | 0 | 0.17057 | 381.3896 | 40 | 0 | 6.8228
0.53152 | 0 | 0.15597 | 374.4764 | 40 | 0 | 6.2388
0.51869 | 0 | 0.17791 | 369.7238 | 40 | 0 | 7.1164
0.50835 | 0 | 0.17074 | 365.7184 | 40 | 0 | 6.8296
0.50736 | 0 | 0.16017 | 361.3892 | 40 | 0 | 6.4068
0.51136 | 0 | 0.15783 | 356.5664 | 40 | 0 | 6.3132
0.53191 | 0 | 0.17012 | 350.1802 | 40 | 0 | 6.8048
0.57851 | 0 | 0.15429 | 338.5008 | 40 | 0 | 6.1716
0.62634 | 0.0002 | 0.13783 | 321.394 | 40 | 0.014 | 5.5132
0.62009 | 0.0198 | 0.15433 | 306.9442 | 40 | 1.386 | 6.1732
0.60657 | 0.0688 | 0.15708 | 297.3864 | 40 | 4.816 | 6.2832
0.60422 | 0.1287 | 0.12585 | 291.0074 | 40 | 9.009 | 5.034
0.59642 | 0.2474 | 0.14208 | 294.3666 | 40 | 17.318 | 5.6832
0.58404 | 0.3839 | 0.18627 | 310.2864 | 40 | 34.3238 | 0
0.57258 | 0.4591 | 0.2148 | 333.7574 | 40 | 40.729 | 0
0.56283 | 0.5876 | 0.23448 | 367.9856 | 40 | 50.5112 | 0
0.55671 | 0.5829 | 0.24267 | 402.8244 | 40 | 50.5098 | 0
0.55901 | 0.4819 | 0.22369 | 429.604 | 40 | 42.6806 | 0
0.57486 | 0.1542 | 0.22104 | 431.7536 | 40 | 10.794 | 8.8416
0.60773 | 0.0002 | 0.25054 | 421.0162 | 40 | 0.014 | 10.0216
0.61195 | 0 | 0.33905 | 413.3832 | 40 | 0 | 13.562
0.60378 | 0 | 0.41655 | 409.6672 | 40 | 0 | 16.662
0.58534 | 0 | 0.44159 | 408.7968 | 40 | 0 | 17.6636
0.55677 | 0 | 0.4542 | 411.2878 | 40 | 0 | 18.168
0.52136 | 0 | 0.46835 | 417.8858 | 40 | 0 | 18.734
0.4928 | 0 | 0.45694 | 426.8834 | 40 | 0 | 18.2776
0.47577 | 0 | 0.45827 | 437.6372 | 40 | 0 | 18.3308
0.47013 | 0 | 0.4687 | 449.3722 | 40 | 0 | 18.748
0.46785 | 0 | 0.43544 | 460.0048 | 40 | 0 | 17.4176
0.47332 | 0 | 0.41368 | 469.22 | 40 | 0 | 16.5472
0.49155 | 0 | 0.40089 | 476.1006 | 40 | 0 | 16.0356
0.53516 | 0 | 0.36303 | 477.1058 | 40 | 0 | 14.5212
0.57817 | 0.0008 | 0.33127 | 472.5956 | 40 | 0.056 | 13.2508
0.571 | 0.1794 | 0.32048 | 480.8728 | 40 | 12.558 | 12.8192
0.56478 | 0.5531 | 0.32428 | 516.083 | 40 | 51.6882 | 5.6843e-14
0.5617 | 0.6448 | 0.30084 | 557.0826 | 40 | 57.1696 | 0
0.55196 | 0.6853 | 0.29849 | 601.7972 | 40 | 59.9106 | 0
0.53976 | 0.6919 | 0.33799 | 649.7738 | 40 | 61.9526 | 0
0.53125 | 0.6974 | 0.3732 | 700 | 40 | 63.3512 | 0
0.51865 | 0.707 | 0.38585 | 700 | 40 | 11.865 | 0
0.50972 | 0.6576 | 0.42093 | 700 | 40 | 10.972 | 0
0.50971 | 0.5293 | 0.43217 | 700 | 40 | 10.971 | 0
0.5208 | 0.1316 | 0.4419 | 700 | 40 | 9.212 | 2.868
0.54488 | 0.0001 | 0.43867 | 700 | 40 | 0.007 | 14.481
0.55289 | 0 | 0.50812 | 700 | 40 | 0 | 15.289
0.54652 | 0 | 0.53107 | 700 | 40 | 0 | 14.652
0.5307 | 0 | 0.54067 | 700 | 40 | 0 | 13.07
0.50578 | 0 | 0.54974 | 700 | 40 | 0 | 10.578
0.46998 | 0 | 0.5435 | 700 | 40 | 0 | 6.998
0.43977 | 0 | 0.53324 | 700 | 40 | 0 | 3.977
0.42501 | 0 | 0.50493 | 700 | 40 | 0 | 2.501
0.41646 | 0 | 0.47362 | 700 | 40 | 0 | 1.646
0.41332 | 0 | 0.45495 | 700 | 40 | 0 | 1.332
0.41715 | 0 | 0.44531 | 700 | 40 | 0 | 1.715
0.43544 | 0 | 0.44659 | 700 | 40 | 0 | 3.544
0.47893 | 0 | 0.40157 | 700 | 40 | 0 | 7.893
0.52699 | 0.0012 | 0.34318 | 700 | 40 | 0.084 | 12.615
0.52336 | 0.1829 | 0.31377 | 700 | 40 | 12.336 | 0
0.52098 | 0.4498 | 0.22641 | 700 | 40 | 12.098 | 0
0.51822 | 0.6012 | 0.11239 | 700 | 40 | 11.822 | 0
0.51275 | 0.7001 | 0.0533 | 700 | 40 | 11.275 | 0
0.50368 | 0.7339 | 0.02181 | 700 | 40 | 10.368 | 0
0.49503 | 0.7857 | 0.01327 | 700 | 40 | 9.503 | 0
0.48948 | 0.7563 | 0.02309 | 700 | 40 | 8.948 | 0
0.48086 | 0.7299 | 0.03724 | 700 | 40 | 8.086 | 0
0.4821 | 0.589 | 0.04856 | 700 | 40 | 8.21 | 0
0.48554 | 0.1624 | 0.07846 | 700 | 40 | 8.554 | 0
0.51533 | 0.0002 | 0.13101 | 693.7214 | 40 | 0.014 | 5.2404
0.52967 | 0 | 0.23725 | 690.2444 | 40 | 0 | 9.49
0.53041 | 0 | 0.30643 | 689.4606 | 40 | 0 | 12.2572
0.52234 | 0 | 0.36861 | 691.971 | 40 | 0 | 14.7444
0.50127 | 0 | 0.42881 | 698.9964 | 40 | 0 | 17.1524
0.47275 | 0 | 0.522 | 700 | 40 | 0 | 8.2786
0.45144 | 0 | 0.57667 | 700 | 40 | 0 | 5.144
0.4383 | 0 | 0.60268 | 700 | 40 | 0 | 3.83
0.4332 | 0 | 0.61829 | 700 | 40 | 0 | 3.32
0.43336 | 0 | 0.62661 | 700 | 40 | 0 | 3.336
0.4394 | 0 | 0.62926 | 700 | 40 | 0 | 3.94
0.45854 | 0 | 0.61683 | 700 | 40 | 0 | 5.854
0.50312 | 0 | 0.61949 | 700 | 40 | 0 | 10.312
0.55111 | 0.0004 | 0.62855 | 700 | 40 | 0.028 | 15.083
0.54602 | 0.137 | 0.64859 | 700 | 40 | 9.59 | 5.012
0.54358 | 0.5125 | 0.6347 | 700 | 40 | 14.358 | 0
0.53918 | 0.6655 | 0.61175 | 700 | 40 | 13.918 | 0
0.52877 | 0.6742 | 0.61781 | 700 | 40 | 12.877 | 0
0.5177 | 0.5785 | 0.66973 | 700 | 40 | 11.77 | 0
0.51353 | 0.4904 | 0.70251 | 700 | 40 | 11.353 | 0
0.50574 | 0.4772 | 0.72949 | 700 | 40 | 10.574 | 0
0.49956 | 0.5077 | 0.72082 | 700 | 40 | 9.956 | 0
0.49518 | 0.3897 | 0.70246 | 700 | 40 | 9.518 | 0
0.49849 | 0.1058 | 0.6761 | 700 | 40 | 7.406 | 2.443
0.51435 | 0.001 | 0.67517 | 700 | 40 | 0.07 | 11.365
0.51615 | 0 | 0.75519 | 700 | 40 | 0 | 11.615
0.50561 | 0 | 0.76638 | 700 | 40 | 0 | 10.561
0.4952 | 0 | 0.77571 | 700 | 40 | 0 | 9.52
0.47805 | 0 | 0.7804 | 700 | 40 | 0 | 7.805
0.45598 | 0 | 0.79022 | 700 | 40 | 0 | 5.598
0.43231 | 0 | 0.74745 | 700 | 40 | 0 | 3.231
0.41903 | 0 | 0.7436 | 700 | 40 | 0 | 1.903
0.41294 | 0 | 0.74377 | 700 | 40 | 0 | 1.294
0.41667 | 0 | 0.76731 | 700 | 40 | 0 | 1.667
0.42544 | 0 | 0.77341 | 700 | 40 | 0 | 2.544
0.4479 | 0 | 0.7685 | 700 | 40 | 0 | 4.79
0.47949 | 0 | 0.78655 | 700 | 40 | 0 | 7.949
0.51856 | 0.0017 | 0.80269 | 700 | 40 | 0.119 | 11.737
0.55254 | 0.201 | 0.76288 | 700 | 40 | 14.07 | 1.184
0.58104 | 0.6775 | 0.75129 | 700 | 40 | 18.104 | 0
0.59853 | 0.8404 | 0.80335 | 700 | 40 | 19.853 | 0
0.59453 | 0.8407 | 0.79946 | 700 | 40 | 19.453 | 0
0.58699 | 0.8298 | 0.77115 | 700 | 40 | 18.699 | 0
0.56994 | 0.8333 | 0.75297 | 700 | 40 | 16.994 | 0
0.55581 | 0.8356 | 0.74926 | 700 | 40 | 15.581 | 0
0.54491 | 0.8211 | 0.72126 | 700 | 40 | 14.491 | 0
0.54283 | 0.6802 | 0.63846 | 700 | 40 | 14.283 | 0
0.54873 | 0.2099 | 0.55341 | 700 | 40 | 14.693 | 0.18
0.58379 | 0.0009 | 0.36733 | 696.3772 | 40 | 0.063 | 14.6932
0.61054 | 0 | 0.33 | 688.5232 | 40 | 0 | 13.2
0.61007 | 0 | 0.32076 | 680.3466 | 40 | 0 | 12.8304
0.61208 | 0 | 0.28077 | 670.3694 | 40 | 0 | 11.2308
0.60492 | 0 | 0.25733 | 660.1706 | 40 | 0 | 10.2932
0.59312 | 0 | 0.27449 | 651.8382 | 40 | 0 | 10.9796
0.58057 | 0 | 0.24464 | 643.5668 | 40 | 0 | 9.7856
0.57521 | 0 | 0.24862 | 635.9906 | 40 | 0 | 9.9448
0.57672 | 0 | 0.24764 | 628.2242 | 40 | 0 | 9.9056
0.57727 | 0 | 0.28891 | 622.0536 | 40 | 0 | 11.5564
0.58447 | 0 | 0.30023 | 615.6158 | 40 | 0 | 12.0092
0.59821 | 0 | 0.3051 | 607.9988 | 40 | 0 | 12.204
0.61779 | 0 | 0.33973 | 599.809 | 40 | 0 | 13.5892
0.64394 | 0.0049 | 0.37507 | 590.7608 | 40 | 0.343 | 15.0028
0.66161 | 0.2356 | 0.3986 | 597.0358 | 40 | 16.492 | 15.944
0.65646 | 0.7106 | 0.36003 | 635.533 | 40 | 64.1432 | 0
0.63155 | 0.7619 | 0.28896 | 677.2694 | 40 | 64.8914 | 0
0.59786 | 0.8104 | 0.30497 | 700 | 40 | 42.5166 | 0
0.56779 | 0.812 | 0.31465 | 700 | 40 | 16.779 | 0
0.53847 | 0.7906 | 0.29059 | 700 | 40 | 13.847 | 0
0.51392 | 0.7857 | 0.27458 | 700 | 40 | 11.392 | 0
0.50056 | 0.7595 | 0.25746 | 700 | 40 | 10.056 | 0
0.48972 | 0.6142 | 0.27781 | 700 | 40 | 8.972 | 0
0.50052 | 0.1699 | 0.30594 | 700 | 40 | 10.052 | 0
0.54311 | 0.0006 | 0.37675 | 700 | 40 | 0.042 | 14.269
0.57124 | 0 | 0.56137 | 700 | 40 | 0 | 17.124
0.57799 | 0 | 0.69185 | 700 | 40 | 0 | 17.799
0.57607 | 0 | 0.73409 | 700 | 40 | 0 | 17.607
0.5774 | 0 | 0.75134 | 700 | 40 | 0 | 17.74
0.55412 | 0 | 0.75638 | 700 | 40 | 0 | 15.412
0.53799 | 0 | 0.76602 | 700 | 40 | 0 | 13.799
0.53062 | 0 | 0.75098 | 700 | 40 | 0 | 13.062
0.52709 | 0 | 0.73723 | 700 | 40 | 0 | 12.709
0.53266 | 0 | 0.75439 | 700 | 40 | 0 | 13.266
0.54491 | 0 | 0.75912 | 700 | 40 | 0 | 14.491
0.56625 | 0 | 0.74276 | 700 | 40 | 0 | 16.625
0.61127 | 0 | 0.75266 | 700 | 40 | 0 | 21.127
0.64909 | 0.0044 | 0.77217 | 700 | 40 | 0.308 | 24.601
0.65805 | 0.1557 | 0.79322 | 700 | 40 | 10.899 | 14.906
0.64192 | 0.4476 | 0.74249 | 700 | 40 | 24.192 | 0
0.62661 | 0.5682 | 0.73931 | 700 | 40 | 22.661 | 0
0.60084 | 0.6161 | 0.79517 | 700 | 40 | 20.084 | 0
0.56911 | 0.5316 | 0.8126 | 700 | 40 | 16.911 | 0
0.545 | 0.5239 | 0.80994 | 700 | 40 | 14.5 | 0
0.52575 | 0.4957 | 0.80366 | 700 | 40 | 12.575 | 0
0.51221 | 0.4347 | 0.80402 | 700 | 40 | 11.221 | 0
0.50824 | 0.3448 | 0.80203 | 700 | 40 | 10.824 | 0
0.51419 | 0.1262 | 0.82467 | 700 | 40 | 8.834 | 2.585
0.54714 | 0.001 | 0.84524 | 700 | 40 | 0.07 | 14.644
0.56286 | 0 | 0.86749 | 700 | 40 | 0 | 16.286
0.55942 | 0 | 0.86284 | 700 | 40 | 0 | 15.942
0.54362 | 0 | 0.86687 | 700 | 40 | 0 | 14.362
0.51611 | 0 | 0.85232 | 700 | 40 | 0 | 11.611
0.47966 | 0 | 0.77942 | 700 | 40 | 0 | 7.966
0.45359 | 0 | 0.75134 | 700 | 40 | 0 | 5.359
0.43638 | 0 | 0.72803 | 700 | 40 | 0 | 3.638
0.42602 | 0 | 0.71242 | 700 | 40 | 0 | 2.602
0.42408 | 0 | 0.71357 | 700 | 40 | 0 | 2.408
0.42711 | 0 | 0.7267 | 700 | 40 | 0 | 2.711
0.44428 | 0 | 0.72891 | 700 | 40 | 0 | 4.428
0.48361 | 0 | 0.68128 | 700 | 40 | 0 | 8.361
0.52815 | 0.0008 | 0.63081 | 700 | 40 | 0.056 | 12.759
0.51979 | 0.0707 | 0.53726 | 700 | 40 | 4.949 | 7.03
0.51526 | 0.3949 | 0.52156 | 700 | 40 | 11.526 | 0
0.5122 | 0.5731 | 0.45884 | 700 | 40 | 11.22 | 0
0.50883 | 0.5733 | 0.4741 | 700 | 40 | 10.883 | 0
0.50941 | 0.4953 | 0.52121 | 700 | 40 | 10.941 | 0
0.50671 | 0.5443 | 0.5293 | 700 | 40 | 10.671 | 0
0.50622 | 0.3929 | 0.64864 | 700 | 40 | 10.622 | 0
0.50443 | 0.1888 | 0.73665 | 700 | 40 | 10.443 | 0
0.5082 | 0.102 | 0.76421 | 700 | 40 | 7.14 | 3.68
0.51694 | 0.0225 | 0.7788 | 700 | 40 | 1.575 | 10.119
0.54811 | 0.0002 | 0.79517 | 700 | 40 | 0.014 | 14.797
0.55852 | 0 | 0.78075 | 700 | 40 | 0 | 15.852
0.56635 | 0 | 0.77978 | 700 | 40 | 0 | 16.635
0.55928 | 0 | 0.75545 | 700 | 40 | 0 | 15.928
0.54088 | 0 | 0.6934 | 700 | 40 | 0 | 14.088
0.51829 | 0 | 0.63612 | 700 | 40 | 0 | 11.829
0.50111 | 0 | 0.60644 | 700 | 40 | 0 | 10.111
0.4964 | 0 | 0.56557 | 700 | 40 | 0 | 9.64
0.49672 | 0 | 0.58154 | 700 | 40 | 0 | 9.672
0.50608 | 0 | 0.59335 | 700 | 40 | 0 | 10.608
0.52847 | 0 | 0.62037 | 700 | 40 | 0 | 12.847
0.56098 | 0 | 0.59428 | 700 | 40 | 0 | 16.098
0.62054 | 0 | 0.50944 | 698.3236 | 40 | 0 | 20.3776
0.68659 | 0.0014 | 0.46486 | 688.357 | 40 | 0.098 | 18.5944
0.69377 | 0.2469 | 0.43562 | 693.6878 | 40 | 17.283 | 17.4248
0.68247 | 0.7741 | 0.33748 | 700 | 40 | 34.5592 | 0
0.6696 | 0.8726 | 0.2997 | 700 | 40 | 26.96 | 0
0.65202 | 0.8897 | 0.29245 | 700 | 40 | 25.202 | 0
0.6291 | 0.88 | 0.26927 | 700 | 40 | 22.91 | 0
0.60639 | 0.8772 | 0.27463 | 700 | 40 | 20.639 | 0
0.58565 | 0.8864 | 0.27653 | 700 | 40 | 18.565 | 0
0.56612 | 0.8721 | 0.2748 | 700 | 40 | 16.612 | 0
0.56103 | 0.7283 | 0.26153 | 700 | 40 | 16.103 | 0
0.56678 | 0.2345 | 0.20824 | 700 | 40 | 16.415 | 0.263
0.60647 | 0.0019 | 0.11004 | 683.8876 | 40 | 0.133 | 4.4016
0.63738 | 0 | 0.11349 | 664.6892 | 40 | 0 | 4.5396
0.64952 | 0 | 0.14742 | 645.634 | 40 | 0 | 5.8968
0.65039 | 0 | 0.19134 | 628.2486 | 40 | 0 | 7.6536
0.63362 | 0 | 0.23415 | 614.2526 | 40 | 0 | 9.366
0.60624 | 0 | 0.26812 | 604.3534 | 40 | 0 | 10.7248
0.58727 | 0 | 0.3258 | 598.6584 | 40 | 0 | 13.032
0.58055 | 0 | 0.35875 | 594.9534 | 40 | 0 | 14.35
0.58038 | 0 | 0.43009 | 594.119 | 40 | 0 | 17.2036
0.58705 | 0 | 0.50688 | 595.6892 | 40 | 0 | 20.2752
0.59853 | 0 | 0.53328 | 597.1674 | 40 | 0 | 21.3312
0.62745 | 0 | 0.53293 | 595.7396 | 40 | 0 | 21.3172
0.68383 | 0 | 0.53151 | 588.617 | 40 | 0 | 21.2604
0.73877 | 0.0046 | 0.53311 | 576.3864 | 40 | 0.322 | 21.3244
0.71656 | 0.2738 | 0.50621 | 584.1448 | 40 | 19.166 | 20.2484
0.67264 | 0.7849 | 0.39144 | 627.4814 | 40 | 70.6006 | 0
0.62964 | 0.8615 | 0.32487 | 677.8172 | 40 | 73.2998 | 1.1369e-13
0.58961 | 0.8449 | 0.35565 | 700 | 40 | 41.1438 | 0
0.55573 | 0.8215 | 0.35097 | 700 | 40 | 15.573 | 0
0.53155 | 0.8258 | 0.35654 | 700 | 40 | 13.155 | 0
0.51498 | 0.8453 | 0.37295 | 700 | 40 | 11.498 | 0
0.50037 | 0.8366 | 0.4051 | 700 | 40 | 10.037 | 0
0.49977 | 0.7161 | 0.40303 | 700 | 40 | 9.977 | 0
0.50544 | 0.2405 | 0.41298 | 700 | 40 | 10.544 | 0
0.5393 | 0.0023 | 0.40484 | 700 | 40 | 0.161 | 13.769
0.56749 | 0 | 0.463 | 700 | 40 | 0 | 16.749
0.57668 | 0 | 0.50237 | 700 | 40 | 0 | 17.668
0.57835 | 0 | 0.54315 | 700 | 40 | 0 | 17.835
0.56058 | 0 | 0.52174 | 700 | 40 | 0 | 16.058
0.53584 | 0 | 0.46605 | 700 | 40 | 0 | 13.584
0.51945 | 0 | 0.44071 | 700 | 40 | 0 | 11.945
0.51564 | 0 | 0.4504 | 700 | 40 | 0 | 11.564
0.51721 | 0 | 0.41245 | 700 | 40 | 0 | 11.721
0.52715 | 0 | 0.32752 | 700 | 40 | 0 | 12.715
0.54286 | 0 | 0.2618 | 696.186 | 40 | 0 | 10.472
0.56958 | 0 | 0.22725 | 688.318 | 40 | 0 | 9.09
0.62319 | 0 | 0.20266 | 674.1054 | 40 | 0 | 8.1064
0.67721 | 0.002 | 0.19267 | 654.2312 | 40 | 0.14 | 7.7068
0.66625 | 0.2294 | 0.19988 | 651.6594 | 40 | 16.058 | 7.9952
0.64017 | 0.6633 | 0.13787 | 679.5882 | 40 | 51.9458 | 0
0.61323 | 0.7613 | 0.13676 | 700 | 40 | 41.7348 | 0
0.5832 | 0.7674 | 0.12641 | 700 | 40 | 18.32 | 0
0.55623 | 0.7701 | 0.11013 | 700 | 40 | 15.623 | 0
0.53489 | 0.7621 | 0.09952 | 700 | 40 | 13.489 | 0
0.51962 | 0.7881 | 0.11588 | 700 | 40 | 11.962 | 0
0.50437 | 0.8121 | 0.13645 | 700 | 40 | 10.437 | 0
0.50288 | 0.7016 | 0.13158 | 700 | 40 | 10.288 | 0
0.50912 | 0.2561 | 0.12858 | 700 | 40 | 10.912 | 0
0.53592 | 0.0027 | 0.13313 | 691.9222 | 40 | 0.189 | 5.3252
0.55584 | 0 | 0.18285 | 683.6522 | 40 | 0 | 7.314
0.55501 | 0 | 0.19771 | 676.0596 | 40 | 0 | 7.9084
0.55219 | 0 | 0.19638 | 668.6958 | 40 | 0 | 7.8552
0.54402 | 0 | 0.20111 | 662.3382 | 40 | 0 | 8.0444
0.52316 | 0 | 0.19143 | 657.6794 | 40 | 0 | 7.6572
0.5071 | 0 | 0.18267 | 654.2762 | 40 | 0 | 7.3068
0.4962 | 0 | 0.16741 | 651.3526 | 40 | 0 | 6.6964
0.49113 | 0 | 0.15887 | 648.5944 | 40 | 0 | 6.3548
0.48957 | 0 | 0.15158 | 645.7006 | 40 | 0 | 6.0632
0.49114 | 0 | 0.16666 | 643.253 | 40 | 0 | 6.6664
0.5036 | 0 | 0.15786 | 639.2074 | 40 | 0 | 6.3144
0.52421 | 0 | 0.14061 | 632.4108 | 40 | 0 | 5.6244
0.54935 | 0.0015 | 0.14273 | 623.29 | 40 | 0.105 | 5.7092
0.56715 | 0.124 | 0.13393 | 620.6122 | 40 | 8.68 | 5.3572
0.56843 | 0.3679 | 0.13366 | 634.8686 | 40 | 31.0994 | 0
0.55669 | 0.4283 | 0.09501 | 652.981 | 40 | 33.7814 | 0
0.53317 | 0.5693 | 0.11323 | 684.0442 | 40 | 44.3802 | 0
0.51156 | 0.7154 | 0.17834 | 700 | 40 | 27.1118 | 0
0.49143 | 0.7473 | 0.17551 | 700 | 40 | 9.143 | 0
0.47834 | 0.7644 | 0.16042 | 700 | 40 | 7.834 | 0
0.46379 | 0.7157 | 0.1315 | 700 | 40 | 6.379 | 0
0.46388 | 0.5966 | 0.12902 | 700 | 40 | 6.388 | 0
0.46851 | 0.2337 | 0.12712 | 700 | 40 | 6.851 | 0
0.4981 | 0.0031 | 0.10655 | 694.669 | 40 | 0.217 | 4.262
0.51141 | 0 | 0.10606 | 687.7704 | 40 | 0 | 4.2424
0.51177 | 0 | 0.13795 | 682.1114 | 40 | 0 | 5.518
0.51128 | 0 | 0.17206 | 677.8658 | 40 | 0 | 6.8824
0.50328 | 0 | 0.17444 | 674.5154 | 40 | 0 | 6.9776
0.48787 | 0 | 0.14238 | 671.4236 | 40 | 0 | 5.6952
0.47782 | 0 | 0.16317 | 670.1684 | 40 | 0 | 6.5268
0.46717 | 0 | 0.16078 | 669.8826 | 40 | 0 | 6.4312
0.46605 | 0 | 0.18692 | 670.7544 | 40 | 0 | 7.4768
0.46527 | 0 | 0.17298 | 671.1466 | 40 | 0 | 6.9192
0.46996 | 0 | 0.22907 | 673.3134 | 40 | 0 | 9.1628
0.48049 | 0 | 0.26476 | 675.8548 | 40 | 0 | 10.5904
0.49903 | 0 | 0.27051 | 676.7722 | 40 | 0 | 10.8204
0.52257 | 0.004 | 0.28091 | 676.0316 | 40 | 0.28 | 11.2364
0.53831 | 0.2592 | 0.27255 | 691.2466 | 40 | 29.046 | 0
0.53744 | 0.7952 | 0.24123 | 700 | 40 | 22.4974 | 0
0.51788 | 0.8947 | 0.14437 | 700 | 40 | 11.788 | 0
0.50014 | 0.8749 | 0.16184 | 700 | 40 | 10.014 | 0
0.48491 | 0.8501 | 0.15662 | 700 | 40 | 8.491 | 0
0.46874 | 0.8599 | 0.15883 | 700 | 40 | 6.874 | 0
0.4591 | 0.8618 | 0.1913 | 700 | 40 | 5.91 | 0
0.45446 | 0.8424 | 0.22664 | 700 | 40 | 5.446 | 0
0.45151 | 0.7225 | 0.24579 | 700 | 40 | 5.151 | 0
0.45677 | 0.2128 | 0.26565 | 700 | 40 | 5.677 | 0
0.4811 | 0.0014 | 0.27166 | 700 | 40 | 0.098 | 8.012
0.51518 | 0 | 0.34871 | 700 | 40 | 0 | 11.518
0.51967 | 0 | 0.41585 | 700 | 40 | 0 | 11.967
0.519 | 0 | 0.51594 | 700 | 40 | 0 | 11.9
0.50678 | 0 | 0.61551 | 700 | 40 | 0 | 10.678
0.48486 | 0 | 0.69061 | 700 | 40 | 0 | 8.486
0.46841 | 0 | 0.69118 | 700 | 40 | 0 | 6.841
0.45545 | 0 | 0.67478 | 700 | 40 | 0 | 5.545
0.45394 | 0 | 0.68137 | 700 | 40 | 0 | 5.394
0.45878 | 0 | 0.70963 | 700 | 40 | 0 | 5.878
0.46813 | 0 | 0.72714 | 700 | 40 | 0 | 6.813
0.49532 | 0 | 0.74174 | 700 | 40 | 0 | 9.532
0.54697 | 0 | 0.71418 | 700 | 40 | 0 | 14.697
0.60042 | 0.0042 | 0.63576 | 700 | 40 | 0.294 | 19.748
0.58471 | 0.274 | 0.62957 | 700 | 40 | 18.471 | 0
0.56578 | 0.7569 | 0.66027 | 700 | 40 | 16.578 | 0
0.54345 | 0.8408 | 0.68349 | 700 | 40 | 14.345 | 0
0.5237 | 0.8258 | 0.75227 | 700 | 40 | 12.37 | 0
0.5087 | 0.8181 | 0.77288 | 700 | 40 | 10.87 | 0
0.50092 | 0.8035 | 0.75961 | 700 | 40 | 10.092 | 0
0.49752 | 0.8107 | 0.74563 | 700 | 40 | 9.752 | 0
0.49184 | 0.7365 | 0.72476 | 700 | 40 | 9.184 | 0
0.49315 | 0.4582 | 0.70998 | 700 | 40 | 9.315 | 0
0.50382 | 0.2162 | 0.70653 | 700 | 40 | 10.382 | 0
0.53003 | 0.003 | 0.68022 | 700 | 40 | 0.21 | 12.793
0.55759 | 0 | 0.65173 | 700 | 40 | 0 | 15.759
0.55713 | 0 | 0.64457 | 700 | 40 | 0 | 15.713
0.55321 | 0 | 0.61223 | 700 | 40 | 0 | 15.321
0.53356 | 0 | 0.51621 | 700 | 40 | 0 | 13.356
0.5101 | 0 | 0.45548 | 700 | 40 | 0 | 11.01
0.49447 | 0 | 0.43969 | 700 | 40 | 0 | 9.447
0.49235 | 0 | 0.42421 | 700 | 40 | 0 | 9.235
0.4942 | 0 | 0.32368 | 700 | 40 | 0 | 9.42
0.50514 | 0 | 0.21151 | 697.9464 | 40 | 0 | 8.4604
0.52752 | 0 | 0.17002 | 691.9952 | 40 | 0 | 6.8008
0.56519 | 0 | 0.14308 | 681.1994 | 40 | 0 | 5.7232
0.63129 | 0 | 0.14653 | 663.9316 | 40 | 0 | 5.8612
0.68954 | 0.0057 | 0.15065 | 641.4026 | 40 | 0.399 | 6.026
0.68442 | 0.152 | 0.18422 | 630.9694 | 40 | 10.64 | 7.3688
0.66021 | 0.389 | 0.19691 | 640.0548 | 40 | 35.1064 | 0
0.63762 | 0.4705 | 0.19607 | 657.0706 | 40 | 40.7778 | 0
0.61366 | 0.6222 | 0.21306 | 687.781 | 40 | 52.0764 | 0
0.58914 | 0.6808 | 0.20965 | 700 | 40 | 31.133 | 0
0.56609 | 0.6634 | 0.22664 | 700 | 40 | 16.609 | 0
0.54726 | 0.5594 | 0.2254 | 700 | 40 | 14.726 | 0
0.53283 | 0.4097 | 0.23159 | 700 | 40 | 13.283 | 0
0.5324 | 0.2059 | 0.22938 | 700 | 40 | 13.24 | 0
0.55297 | 0.0577 | 0.18271 | 696.0504 | 40 | 4.039 | 7.3084
0.59975 | 0.0005 | 0.14322 | 681.8392 | 40 | 0.035 | 5.7288
0.62692 | 0 | 0.15883 | 665.5004 | 40 | 0 | 6.3532
0.63069 | 0 | 0.21354 | 650.973 | 40 | 0 | 8.5416
0.6216 | 0 | 0.26715 | 639.499 | 40 | 0 | 10.686
0.59857 | 0 | 0.31222 | 632.1308 | 40 | 0 | 12.4888
0.56494 | 0 | 0.37525 | 630.6468 | 40 | 0 | 15.01
0.54441 | 0 | 0.39422 | 631.9746 | 40 | 0 | 15.7688
0.53262 | 0 | 0.36103 | 633.1538 | 40 | 0 | 14.4412
0.52987 | 0 | 0.30495 | 632.3648 | 40 | 0 | 12.198
0.53341 | 0 | 0.24157 | 628.6866 | 40 | 0 | 9.6628
0.54428 | 0 | 0.19132 | 621.9114 | 40 | 0 | 7.6528
0.57017 | 0 | 0.19097 | 612.5332 | 40 | 0 | 7.6388
0.62421 | 0 | 0.19287 | 597.827 | 40 | 0 | 7.7148
0.67179 | 0.0016 | 0.18677 | 578.2308 | 40 | 0.112 | 7.4708
0.65897 | 0.0767 | 0.20674 | 565.9724 | 40 | 5.369 | 8.2696
0.64527 | 0.2806 | 0.19676 | 568.9578 | 40 | 19.642 | 7.8704
0.63362 | 0.4876 | 0.19141 | 587.3842 | 40 | 41.7884 | 0
0.61471 | 0.6715 | 0.26862 | 623.663 | 40 | 57.7498 | 0
0.59065 | 0.7021 | 0.32528 | 666.7562 | 40 | 62.1582 | -1.1369e-13
0.57434 | 0.6226 | 0.36797 | 700 | 40 | 50.6778 | 0
0.56247 | 0.6871 | 0.40257 | 700 | 40 | 16.247 | 0
0.54876 | 0.6729 | 0.40911 | 700 | 40 | 14.876 | 0
0.54842 | 0.4135 | 0.38759 | 700 | 40 | 14.842 | 0
0.56039 | 0.1141 | 0.3624 | 700 | 40 | 7.987 | 8.052
0.59414 | 0.002 | 0.3102 | 693.134 | 40 | 0.14 | 12.408
0.61875 | 0 | 0.4012 | 687.307 | 40 | 0 | 16.048
0.621 | 0 | 0.54828 | 687.1382 | 40 | 0 | 21.9312
0.61241 | 0 | 0.61418 | 690.4644 | 40 | 0 | 24.5672
0.58397 | 0 | 0.65227 | 698.1582 | 40 | 0 | 26.0908
0.54705 | 0 | 0.6429 | 700 | 40 | 0 | 16.5468
0.52187 | 0 | 0.6547 | 700 | 40 | 0 | 12.187
0.51083 | 0 | 0.6574 | 700 | 40 | 0 | 11.083
0.5032 | 0 | 0.64494 | 700 | 40 | 0 | 10.32
0.49881 | 0 | 0.64604 | 700 | 40 | 0 | 9.881
0.49999 | 0 | 0.63477 | 700 | 40 | 0 | 9.999
0.52029 | 0 | 0.63163 | 700 | 40 | 0 | 12.029
0.56174 | 0 | 0.60839 | 700 | 40 | 0 | 16.174
0.60705 | 0.0006 | 0.57436 | 700 | 40 | 0.042 | 20.663
0.59477 | 0.0705 | 0.56729 | 700 | 40 | 4.935 | 14.542
0.58847 | 0.2632 | 0.53127 | 700 | 40 | 18.424 | 0.423
0.58228 | 0.5423 | 0.50042 | 700 | 40 | 18.228 | 0
0.57284 | 0.5504 | 0.46316 | 700 | 40 | 17.284 | 0
0.55983 | 0.5605 | 0.41084 | 700 | 40 | 15.983 | 0
0.54803 | 0.6963 | 0.37221 | 700 | 40 | 14.803 | 0
0.53941 | 0.7098 | 0.32545 | 700 | 40 | 13.941 | 0
0.53148 | 0.7239 | 0.28342 | 700 | 40 | 13.148 | 0
0.53117 | 0.6325 | 0.23211 | 700 | 40 | 13.117 | 0
0.53825 | 0.2519 | 0.19835 | 700 | 40 | 13.825 | 0
0.55952 | 0.005 | 0.19552 | 692.2188 | 40 | 0.35 | 7.8208
0.56573 | 0 | 0.29748 | 687.545 | 40 | 0 | 11.8992
0.5587 | 0 | 0.37654 | 686.7366 | 40 | 0 | 15.0616
0.543 | 0 | 0.418 | 689.1566 | 40 | 0 | 16.72
0.51336 | 0 | 0.41963 | 694.6058 | 40 | 0 | 16.7852
0.47737 | 0 | 0.41309 | 700 | 40 | 0 | 13.1312
0.4481 | 0 | 0.40677 | 700 | 40 | 0 | 4.81
0.43359 | 0 | 0.39183 | 700 | 40 | 0 | 3.359
0.42391 | 0 | 0.37579 | 700 | 40 | 0 | 2.391
0.42196 | 0 | 0.33668 | 700 | 40 | 0 | 2.196
0.42578 | 0 | 0.30724 | 700 | 40 | 0 | 2.578
0.44043 | 0 | 0.26429 | 700 | 40 | 0 | 4.043
0.48259 | 0 | 0.22433 | 700 | 40 | 0 | 8.259
0.52644 | 0.0022 | 0.20674 | 695.7796 | 40 | 0.154 | 8.2696
0.52308 | 0.1441 | 0.18924 | 700 | 40 | 10.087 | 6.4414
0.52134 | 0.3729 | 0.18005 | 700 | 40 | 12.134 | 0
0.51817 | 0.4967 | 0.16365 | 700 | 40 | 11.817 | 0
0.5164 | 0.5073 | 0.1549 | 700 | 40 | 11.64 | 0
0.50477 | 0.6601 | 0.15146 | 700 | 40 | 10.477 | 0
0.49726 | 0.6754 | 0.16388 | 700 | 40 | 9.726 | 0
0.49355 | 0.6741 | 0.1793 | 700 | 40 | 9.355 | 0
0.48819 | 0.6437 | 0.21227 | 700 | 40 | 8.819 | 0
0.48749 | 0.5512 | 0.19861 | 700 | 40 | 8.749 | 0
0.48568 | 0.1951 | 0.20259 | 700 | 40 | 8.568 | 0
0.50121 | 0.0025 | 0.22743 | 699.1512 | 40 | 0.175 | 9.0972
0.51196 | 0 | 0.30419 | 700 | 40 | 0 | 12.0448
0.50159 | 0 | 0.41013 | 700 | 40 | 0 | 10.159
0.49506 | 0 | 0.48791 | 700 | 40 | 0 | 9.506
0.48125 | 0 | 0.55624 | 700 | 40 | 0 | 8.125
0.45841 | 0 | 0.54148 | 700 | 40 | 0 | 5.841
0.43381 | 0 | 0.45141 | 700 | 40 | 0 | 3.381
0.41644 | 0 | 0.47333 | 700 | 40 | 0 | 1.644
0.40857 | 0 | 0.46608 | 700 | 40 | 0 | 0.857
0.40261 | 0 | 0.47006 | 700 | 40 | 0 | 0.261
0.40241 | 0 | 0.45813 | 700 | 40 | 0 | 0.241
0.41027 | 0 | 0.45455 | 700 | 40 | 0 | 1.027
0.42429 | 0 | 0.46878 | 700 | 40 | 0 | 2.429
0.44263 | 0.0018 | 0.46303 | 700 | 40 | 0.126 | 4.137
0.4602 | 0.1738 | 0.44085 | 700 | 40 | 6.02 | 0
0.47835 | 0.4795 | 0.39882 | 700 | 40 | 7.835 | 0
0.48808 | 0.5485 | 0.39926 | 700 | 40 | 8.808 | 0
0.49237 | 0.5733 | 0.44544 | 700 | 40 | 9.237 | 0
0.48876 | 0.6525 | 0.45273 | 700 | 40 | 8.876 | 0
0.48265 | 0.6293 | 0.4256 | 700 | 40 | 8.265 | 0
0.47232 | 0.5773 | 0.38697 | 700 | 40 | 7.232 | 0
0.46616 | 0.5826 | 0.38375 | 700 | 40 | 6.616 | 0
0.46374 | 0.4618 | 0.37769 | 700 | 40 | 6.374 | 0
0.46462 | 0.1591 | 0.37959 | 700 | 40 | 6.462 | 0
0.48004 | 0.003 | 0.34534 | 700 | 40 | 0.21 | 7.794
0.48909 | 0 | 0.41283 | 700 | 40 | 0 | 8.909
0.48489 | 0 | 0.50705 | 700 | 40 | 0 | 8.489
0.47489 | 0 | 0.55421 | 700 | 40 | 0 | 7.489
0.46393 | 0 | 0.57405 | 700 | 40 | 0 | 6.393
0.44341 | 0 | 0.60353 | 700 | 40 | 0 | 4.341
0.42324 | 0 | 0.61192 | 700 | 40 | 0 | 2.324
0.4054 | 0 | 0.59522 | 700 | 40 | 0 | 0.54
0.39471 | 0 | 0.5904 | 700 | 39.471 | 0 | 0
0.38989 | 0 | 0.579 | 700 | 38.989 | 0 | 0
0.38441 | 0 | 0.57025 | 700 | 38.441 | 0 | 0
0.38858 | 0 | 0.56234 | 700 | 38.858 | 0 | 0
0.39526 | 0 | 0.56247 | 700 | 39.526 | 0 | 0
0.41173 | 0.0018 | 0.56609 | 700 | 40 | 0.126 | 1.047
0.4243 | 0.1164 | 0.56755 | 700 | 40 | 2.43 | 0
0.44579 | 0.47 | 0.53878 | 700 | 40 | 4.579 | 0
0.4589 | 0.567 | 0.52985 | 700 | 40 | 5.89 | 0
0.4677 | 0.6087 | 0.58978 | 700 | 40 | 6.77 | 0
0.47068 | 0.655 | 0.62337 | 700 | 40 | 7.068 | 0
0.47163 | 0.6146 | 0.65015 | 700 | 40 | 7.163 | 0
0.47299 | 0.6194 | 0.6353 | 700 | 40 | 7.299 | 0
0.47477 | 0.5362 | 0.64476 | 700 | 40 | 7.477 | 0
0.47842 | 0.3398 | 0.64931 | 700 | 40 | 7.842 | 0
0.48191 | 0.162 | 0.63972 | 700 | 40 | 8.191 | 0
0.48577 | 0.0062 | 0.60273 | 700 | 40 | 0.434 | 8.143
0.49629 | 0 | 0.60901 | 700 | 40 | 0 | 9.629
0.49274 | 0 | 0.67088 | 700 | 40 | 0 | 9.274
0.4816 | 0 | 0.67517 | 700 | 40 | 0 | 8.16
0.47701 | 0 | 0.67605 | 700 | 40 | 0 | 7.701
0.4428 | 0 | 0.6734 | 700 | 40 | 0 | 4.28
0.41455 | 0 | 0.65298 | 700 | 40 | 0 | 1.455
0.39291 | 0 | 0.6254 | 700 | 39.291 | 0 | 0
0.38353 | 0 | 0.61435 | 700 | 38.353 | 0 | 0
0.38182 | 0 | 0.5923 | 700 | 38.182 | 0 | 0
0.38162 | 0 | 0.51112 | 700 | 38.162 | 0 | 0
0.39522 | 0 | 0.45512 | 700 | 39.522 | 0 | 0
0.43408 | 0 | 0.37738 | 700 | 40 | 0 | 3.408
0.48113 | 0.0036 | 0.33195 | 700 | 40 | 0.252 | 7.861
0.48084 | 0.1404 | 0.31356 | 700 | 40 | 8.084 | 0
0.48934 | 0.3874 | 0.22005 | 700 | 40 | 8.934 | 0
0.49606 | 0.5505 | 0.13599 | 700 | 40 | 9.606 | 0
0.50245 | 0.67 | 0.12525 | 700 | 40 | 10.245 | 0
0.50812 | 0.6425 | 0.11195 | 700 | 40 | 10.812 | 0
0.5156 | 0.6579 | 0.13152 | 700 | 40 | 11.56 | 0
0.51745 | 0.6751 | 0.18071 | 700 | 40 | 11.745 | 0
0.51861 | 0.6478 | 0.22986 | 700 | 40 | 11.861 | 0
0.52043 | 0.6122 | 0.29107 | 700 | 40 | 12.043 | 0
0.52115 | 0.2882 | 0.35007 | 700 | 40 | 12.115 | 0
0.53289 | 0.0074 | 0.35162 | 700 | 40 | 0.518 | 12.771
0.54742 | 0 | 0.38308 | 700 | 40 | 0 | 14.742
0.53809 | 0 | 0.45715 | 700 | 40 | 0 | 13.809
0.52253 | 0 | 0.50952 | 700 | 40 | 0 | 12.253
0.49609 | 0 | 0.5272 | 700 | 40 | 0 | 9.609
0.45877 | 0 | 0.51271 | 700 | 40 | 0 | 5.877
0.42634 | 0 | 0.49485 | 700 | 40 | 0 | 2.634
0.40586 | 0 | 0.51637 | 700 | 40 | 0 | 0.586
0.39569 | 0 | 0.52084 | 700 | 39.569 | 0 | 0
0.38897 | 0 | 0.5082 | 700 | 38.897 | 0 | 0
0.39028 | 0 | 0.46962 | 700 | 39.028 | 0 | 0
0.40185 | 0 | 0.47311 | 700 | 40 | 0 | 0.185
0.44262 | 0 | 0.44823 | 700 | 40 | 0 | 4.262
0.48972 | 0.0033 | 0.48044 | 700 | 40 | 0.231 | 8.741
0.4896 | 0.125 | 0.48407 | 700 | 40 | 8.75 | 0.21
0.49294 | 0.3414 | 0.42723 | 700 | 40 | 9.294 | 0
0.50221 | 0.4748 | 0.36152 | 700 | 40 | 10.221 | 0
0.51169 | 0.4504 | 0.35992 | 700 | 40 | 11.169 | 0
0.51466 | 0.4267 | 0.40394 | 700 | 40 | 11.466 | 0
0.51923 | 0.4691 | 0.46665 | 700 | 40 | 11.923 | 0
0.52292 | 0.3495 | 0.50506 | 700 | 40 | 12.292 | 0
0.52429 | 0.3352 | 0.54307 | 700 | 40 | 12.429 | 0
0.52415 | 0.2484 | 0.47421 | 700 | 40 | 12.415 | 0
0.52203 | 0.0759 | 0.39082 | 700 | 40 | 5.313 | 6.89
0.5314 | 0.0056 | 0.33022 | 700 | 40 | 0.392 | 12.748
0.54979 | 0 | 0.35979 | 699.4126 | 40 | 0 | 14.3916
0.541 | 0 | 0.4229 | 700 | 40 | 0 | 14.6874
0.52163 | 0 | 0.47072 | 700 | 40 | 0 | 12.163
0.49899 | 0 | 0.46025 | 700 | 40 | 0 | 9.899
0.46271 | 0 | 0.54908 | 700 | 40 | 0 | 6.271
0.43274 | 0 | 0.58815 | 700 | 40 | 0 | 3.274
0.41055 | 0 | 0.58457 | 700 | 40 | 0 | 1.055
0.40136 | 0 | 0.5584 | 700 | 40 | 0 | 0.136
0.39287 | 0 | 0.54819 | 700 | 39.287 | 0 | 0
0.39704 | 0 | 0.52601 | 700 | 39.704 | 0 | 0
0.40886 | 0 | 0.51567 | 700 | 40 | 0 | 0.886
0.44369 | 0 | 0.46997 | 700 | 40 | 0 | 4.369
0.49374 | 0.0001 | 0.43099 | 700 | 40 | 0.007 | 9.367
0.49235 | 0.0232 | 0.4336 | 700 | 40 | 1.624 | 7.611
0.49785 | 0.0942 | 0.4054 | 700 | 40 | 6.594 | 3.191
0.50973 | 0.197 | 0.41119 | 700 | 40 | 10.973 | 0
0.52021 | 0.315 | 0.43815 | 700 | 40 | 12.021 | 0
0.52611 | 0.4713 | 0.50656 | 700 | 40 | 12.611 | 0
0.53544 | 0.5363 | 0.56013 | 700 | 40 | 13.544 | 0
0.53958 | 0.5637 | 0.61431 | 700 | 40 | 13.958 | 0
0.53919 | 0.4614 | 0.63044 | 700 | 40 | 13.919 | 0
0.54056 | 0.4594 | 0.65457 | 700 | 40 | 14.056 | 0
0.54053 | 0.1752 | 0.67959 | 700 | 40 | 12.264 | 1.789
0.54976 | 0.0059 | 0.69488 | 700 | 40 | 0.413 | 14.563
0.56337 | 0 | 0.66447 | 700 | 40 | 0 | 16.337
0.55505 | 0 | 0.70456 | 700 | 40 | 0 | 15.505
0.54083 | 0 | 0.72002 | 700 | 40 | 0 | 14.083
0.51141 | 0 | 0.69364 | 700 | 40 | 0 | 11.141
0.47552 | 0 | 0.69987 | 700 | 40 | 0 | 7.552
0.44229 | 0 | 0.67539 | 700 | 40 | 0 | 4.229
0.42295 | 0 | 0.66014 | 700 | 40 | 0 | 2.295
0.4121 | 0 | 0.66239 | 700 | 40 | 0 | 1.21
0.4059 | 0 | 0.66186 | 700 | 40 | 0 | 0.59
0.40571 | 0 | 0.61444 | 700 | 40 | 0 | 0.571
0.41542 | 0 | 0.58461 | 700 | 40 | 0 | 1.542
0.45002 | 0 | 0.5261 | 700 | 40 | 0 | 5.002
0.49455 | 0.0019 | 0.44283 | 700 | 40 | 0.133 | 9.322
0.50064 | 0.2741 | 0.39753 | 700 | 40 | 10.064 | 0
0.51285 | 0.6714 | 0.36828 | 700 | 40 | 11.285 | 0
0.52897 | 0.7233 | 0.39519 | 700 | 40 | 12.897 | 0
0.54056 | 0.7415 | 0.40681 | 700 | 40 | 14.056 | 0
0.54251 | 0.7394 | 0.42259 | 700 | 40 | 14.251 | 0
0.5385 | 0.7591 | 0.40209 | 700 | 40 | 13.85 | 0
0.53427 | 0.7849 | 0.42374 | 700 | 40 | 13.427 | 0
0.52798 | 0.8136 | 0.43232 | 700 | 40 | 12.798 | 0
0.52745 | 0.7413 | 0.45101 | 700 | 40 | 12.745 | 0
0.53784 | 0.3654 | 0.45176 | 700 | 40 | 13.784 | 0
0.56833 | 0.0135 | 0.44482 | 700 | 40 | 0.945 | 15.888
0.60035 | 0 | 0.48013 | 699.1702 | 40 | 0 | 19.2052
0.60738 | 0 | 0.51827 | 699.163 | 40 | 0 | 20.7308
0.60569 | 0 | 0.50113 | 698.6392 | 40 | 0 | 20.0452
0.59052 | 0 | 0.48858 | 699.1304 | 40 | 0 | 19.5432
0.56734 | 0 | 0.48482 | 700 | 40 | 0 | 17.6036
0.54889 | 0 | 0.46228 | 700 | 40 | 0 | 14.889
0.54396 | 0 | 0.44217 | 700 | 40 | 0 | 14.396
0.5448 | 0 | 0.44602 | 700 | 40 | 0 | 14.48
0.55494 | 0 | 0.42692 | 700 | 40 | 0 | 15.494
0.56664 | 0 | 0.40761 | 699.6404 | 40 | 0 | 16.3044
0.59786 | 0 | 0.36496 | 694.4528 | 40 | 0 | 14.5984
0.65761 | 0 | 0.3342 | 682.0598 | 40 | 0 | 13.368
0.71528 | 0.0042 | 0.31312 | 663.3506 | 40 | 0.294 | 12.5248
0.71981 | 0.1377 | 0.30773 | 653.3178 | 40 | 9.639 | 12.3092
0.72146 | 0.3767 | 0.25545 | 657.7588 | 40 | 26.369 | 10.218
0.71595 | 0.3209 | 0.20935 | 657.0008 | 40 | 22.463 | 8.374
0.70753 | 0.333 | 0.17324 | 656.4874 | 40 | 23.31 | 6.9296
0.69538 | 0.3806 | 0.21642 | 662.2482 | 40 | 26.642 | 8.6568
0.68662 | 0.3725 | 0.25823 | 669.9904 | 40 | 26.075 | 10.3292
0.68396 | 0.3662 | 0.29297 | 678.9472 | 40 | 25.634 | 11.7188
0.67701 | 0.2991 | 0.31949 | 684.9628 | 40 | 20.937 | 12.7796
0.68219 | 0.2135 | 0.31529 | 684.3004 | 40 | 14.945 | 12.6116
0.69389 | 0.139 | 0.30503 | 676.8426 | 40 | 9.73 | 12.2012
0.71378 | 0.0125 | 0.29124 | 657.9892 | 40 | 0.875 | 11.6496
0.7206 | 0 | 0.28002 | 637.13 | 40 | 0 | 11.2008
0.70984 | 0 | 0.28285 | 617.46 | 40 | 0 | 11.314
0.6968 | 0 | 0.27591 | 598.8164 | 40 | 0 | 11.0364
0.67698 | 0 | 0.27715 | 582.2044 | 40 | 0 | 11.086
0.64669 | 0 | 0.2828 | 568.8474 | 40 | 0 | 11.312
0.62354 | 0 | 0.2573 | 556.7854 | 40 | 0 | 10.292
0.60864 | 0 | 0.25478 | 546.1126 | 40 | 0 | 10.1912
0.60003 | 0 | 0.24303 | 535.8308 | 40 | 0 | 9.7212
0.59302 | 0 | 0.23909 | 526.0924 | 40 | 0 | 9.5636
0.593 | 0 | 0.23552 | 516.2132 | 40 | 0 | 9.4208
0.59994 | 0 | 0.24648 | 506.0784 | 40 | 0 | 9.8592
0.6162 | 0 | 0.23582 | 493.8912 | 40 | 0 | 9.4328
0.64209 | 0.0027 | 0.21877 | 478.622 | 40 | 0.189 | 8.7508
0.65966 | 0.0866 | 0.17908 | 465.8812 | 40 | 6.062 | 7.1632
0.67807 | 0.1396 | 0.1679 | 454.5622 | 40 | 9.772 | 6.716
0.68676 | 0.1863 | 0.18116 | 446.1736 | 40 | 13.041 | 7.2464
0.68502 | 0.3447 | 0.2059 | 450.0366 | 40 | 24.129 | 8.236
0.67332 | 0.3799 | 0.25766 | 459.604 | 40 | 26.593 | 10.3064
0.66098 | 0.4829 | 0.29041 | 478.9254 | 40 | 45.4194 | 0
0.64912 | 0.5491 | 0.30932 | 504.8232 | 40 | 50.8098 | -5.6843e-14
0.64428 | 0.5502 | 0.35184 | 532.9828 | 40 | 52.5876 | 0
0.6437 | 0.3984 | 0.35939 | 550.8764 | 40 | 42.2636 | 0
0.65031 | 0.1573 | 0.34711 | 550.7408 | 40 | 11.011 | 13.8844
0.66848 | 0.0065 | 0.31763 | 537.053 | 40 | 0.455 | 12.7052
0.67619 | 0 | 0.28351 | 520.7744 | 40 | 0 | 11.3404
0.66877 | 0 | 0.28563 | 505.3226 | 40 | 0 | 11.4252
0.658 | 0 | 0.28276 | 490.833 | 40 | 0 | 11.3104
0.63943 | 0 | 0.322 | 479.77 | 40 | 0 | 12.88
0.60972 | 0 | 0.26181 | 469.2704 | 40 | 0 | 10.4724
0.58892 | 0 | 0.25337 | 460.5132 | 40 | 0 | 10.1348
0.57276 | 0 | 0.2379 | 452.7532 | 40 | 0 | 9.516
0.56174 | 0 | 0.22111 | 445.4236 | 40 | 0 | 8.8444
0.55658 | 0 | 0.21041 | 438.182 | 40 | 0 | 8.4164
0.55116 | 0 | 0.21024 | 431.4756 | 40 | 0 | 8.4096
0.55632 | 0 | 0.23087 | 425.0784 | 40 | 0 | 9.2348
0.56861 | 0 | 0.25227 | 418.3082 | 40 | 0 | 10.0908
0.58203 | 0.0013 | 0.25863 | 410.5414 | 40 | 0.091 | 10.3452
0.59485 | 0.0376 | 0.25328 | 403.8196 | 40 | 2.632 | 10.1312
0.60765 | 0.1049 | 0.21907 | 399.1604 | 40 | 7.343 | 8.7628
0.60771 | 0.17 | 0.20811 | 398.6138 | 40 | 11.9 | 8.3244
0.60105 | 0.1795 | 0.17117 | 397.9206 | 40 | 12.565 | 6.8468
0.58871 | 0.2044 | 0.14478 | 399.1488 | 40 | 14.308 | 5.7912
0.5765 | 0.2366 | 0.12697 | 403.1396 | 40 | 16.562 | 5.0788
0.56511 | 0.1655 | 0.10876 | 402.564 | 40 | 11.585 | 4.3504
0.55622 | 0.1077 | 0.09696 | 398.3594 | 40 | 7.539 | 3.8784
0.55219 | 0.0661 | 0.11261 | 392.2718 | 40 | 4.627 | 4.5044
0.55824 | 0.0273 | 0.14863 | 384.304 | 40 | 1.911 | 5.9452
0.57755 | 0.0014 | 0.20617 | 374.8938 | 40 | 0.098 | 8.2468
0.59154 | 0 | 0.29513 | 367.545 | 40 | 0 | 11.8052
0.58682 | 0 | 0.33862 | 362.4078 | 40 | 0 | 13.5448
0.57073 | 0 | 0.35016 | 359.3412 | 40 | 0 | 14.0064
0.54872 | 0 | 0.34534 | 358.2828 | 40 | 0 | 13.8136
0.51432 | 0 | 0.36744 | 361.5484 | 40 | 0 | 14.6976
0.48493 | 0 | 0.3529 | 367.1714 | 40 | 0 | 14.116
0.4686 | 0 | 0.35413 | 374.4766 | 40 | 0 | 14.1652
0.45841 | 0 | 0.32528 | 381.6468 | 40 | 0 | 13.0112
0.45525 | 0 | 0.35621 | 390.3702 | 40 | 0 | 14.2484
0.45965 | 0 | 0.37115 | 399.2512 | 40 | 0 | 14.846
0.47959 | 0 | 0.39113 | 406.9374 | 40 | 0 | 15.6452
0.52466 | 0 | 0.39634 | 410.325 | 40 | 0 | 15.8536
0.56228 | 0.0002 | 0.39351 | 409.8514 | 40 | 0.014 | 15.7404
0.56113 | 0.0125 | 0.42242 | 411.5102 | 40 | 0.875 | 16.8968
0.55763 | 0.0403 | 0.44778 | 416.4794 | 40 | 2.821 | 17.9112
0.55421 | 0.0836 | 0.40788 | 423.2256 | 40 | 5.852 | 16.3152
0.55231 | 0.1139 | 0.42613 | 433.0128 | 40 | 7.973 | 17.0452
0.5468 | 0.1506 | 0.48818 | 448.402 | 40 | 10.542 | 19.5272
0.54208 | 0.2009 | 0.59115 | 471.903 | 40 | 14.063 | 23.646
0.53503 | 0.2233 | 0.60065 | 498.057 | 40 | 39.657 | 0
0.53258 | 0.2523 | 0.64383 | 528.2132 | 40 | 43.4142 | -5.6843e-14
0.52952 | 0.1998 | 0.6433 | 554.9792 | 40 | 39.718 | 0
0.53434 | 0.1866 | 0.65011 | 580.6116 | 40 | 13.062 | 26.0044
0.54991 | 0.017 | 0.68025 | 594.0206 | 40 | 1.19 | 27.21
0.56207 | 0 | 0.64092 | 603.4504 | 40 | 0 | 25.6368
0.55642 | 0 | 0.64136 | 613.4628 | 40 | 0 | 25.6544
0.53965 | 0 | 0.65188 | 625.573 | 40 | 0 | 26.0752
0.51134 | 0 | 0.65722 | 640.7278 | 40 | 0 | 26.2888
0.47788 | 0 | 0.68171 | 660.2082 | 40 | 0 | 27.2684
0.45143 | 0 | 0.66332 | 681.598 | 40 | 0 | 26.5328
0.43624 | 0 | 0.63292 | 700 | 40 | 0 | 22.026
0.43018 | 0 | 0.60423 | 700 | 40 | 0 | 3.018
0.43072 | 0 | 0.59208 | 700 | 40 | 0 | 3.072
0.43619 | 0 | 0.55885 | 700 | 40 | 0 | 3.619
0.45704 | 0 | 0.54554 | 700 | 40 | 0 | 5.704
0.50977 | 0 | 0.55332 | 700 | 40 | 0 | 10.977
0.56656 | 0.0149 | 0.48265 | 700 | 40 | 1.043 | 15.613
0.56235 | 0.3829 | 0.39219 | 700 | 40 | 16.235 | 0
0.55037 | 0.8712 | 0.24736 | 700 | 40 | 15.037 | 0
0.54172 | 0.9475 | 0.22234 | 700 | 40 | 14.172 | 0
0.53074 | 0.9478 | 0.1846 | 700 | 40 | 13.074 | 0
0.51476 | 0.9275 | 0.16944 | 700 | 40 | 11.476 | 0
0.50461 | 0.9308 | 0.16909 | 700 | 40 | 10.461 | 0
0.49516 | 0.9435 | 0.14655 | 700 | 40 | 9.516 | 0
0.48757 | 0.9383 | 0.13873 | 700 | 40 | 8.757 | 0
0.48569 | 0.8451 | 0.14134 | 700 | 40 | 8.569 | 0
0.4894 | 0.4289 | 0.13281 | 700 | 40 | 8.94 | 0
0.50783 | 0.0224 | 0.15331 | 696.9174 | 40 | 1.568 | 6.1324
0.54491 | 0 | 0.23012 | 691.6312 | 40 | 0 | 9.2048
0.55455 | 0 | 0.35824 | 690.5058 | 40 | 0 | 14.3296
0.5556 | 0 | 0.48464 | 694.3314 | 40 | 0 | 19.3856
0.54272 | 0 | 0.58991 | 700 | 40 | 0 | 19.9406
0.51746 | 0 | 0.64321 | 700 | 40 | 0 | 11.746
0.50273 | 0 | 0.6658 | 700 | 40 | 0 | 10.273
0.49426 | 0 | 0.67583 | 700 | 40 | 0 | 9.426
0.50038 | 0 | 0.68157 | 700 | 40 | 0 | 10.038
0.50667 | 0 | 0.6863 | 700 | 40 | 0 | 10.667
0.52195 | 0 | 0.70074 | 700 | 40 | 0 | 12.195
0.55246 | 0 | 0.70702 | 700 | 40 | 0 | 15.246
0.613 | 0 | 0.70644 | 700 | 40 | 0 | 21.3
0.66889 | 0.02 | 0.68493 | 700 | 40 | 1.4 | 25.489
0.65196 | 0.2495 | 0.68347 | 700 | 40 | 17.465 | 7.731
0.61404 | 0.6134 | 0.64985 | 700 | 40 | 21.404 | 0
0.5798 | 0.7035 | 0.64601 | 700 | 40 | 17.98 | 0
0.55391 | 0.718 | 0.66734 | 700 | 40 | 15.391 | 0
0.53089 | 0.59 | 0.65555 | 700 | 40 | 13.089 | 0
0.5155 | 0.4932 | 0.66328 | 700 | 40 | 11.55 | 0
0.50718 | 0.4493 | 0.66893 | 700 | 40 | 10.718 | 0
0.50227 | 0.4635 | 0.69222 | 700 | 40 | 10.227 | 0
0.50485 | 0.4525 | 0.7269 | 700 | 40 | 10.485 | 0
0.51056 | 0.2476 | 0.74262 | 700 | 40 | 11.056 | 0
0.52872 | 0.0099 | 0.75278 | 700 | 40 | 0.693 | 12.179
0.55624 | 0 | 0.79281 | 700 | 40 | 0 | 15.624
0.55671 | 0 | 0.83433 | 700 | 40 | 0 | 15.671
0.54956 | 0 | 0.86349 | 700 | 40 | 0 | 14.956
0.52496 | 0 | 0.84017 | 700 | 40 | 0 | 12.496
0.49327 | 0 | 0.81127 | 700 | 40 | 0 | 9.327
0.46742 | 0 | 0.79011 | 700 | 40 | 0 | 6.742
0.45135 | 0 | 0.7838 | 700 | 40 | 0 | 5.135
0.4439 | 0 | 0.77907 | 700 | 40 | 0 | 4.39
0.44388 | 0 | 0.77094 | 700 | 40 | 0 | 4.388
0.44761 | 0 | 0.7576 | 700 | 40 | 0 | 4.761
0.46839 | 0 | 0.75998 | 700 | 40 | 0 | 6.839
0.51352 | 0 | 0.76891 | 700 | 40 | 0 | 11.352
0.5589 | 0.0081 | 0.7728 | 700 | 40 | 0.567 | 15.323
0.54447 | 0.1845 | 0.74655 | 700 | 40 | 12.915 | 1.532
0.529 | 0.4681 | 0.65109 | 700 | 40 | 12.9 | 0
0.51853 | 0.5549 | 0.60872 | 700 | 40 | 11.853 | 0
0.50677 | 0.5104 | 0.62334 | 700 | 40 | 10.677 | 0
0.49642 | 0.5358 | 0.60209 | 700 | 40 | 9.642 | 0
0.49137 | 0.4884 | 0.51308 | 700 | 40 | 9.137 | 0
0.49186 | 0.5049 | 0.50141 | 700 | 40 | 9.186 | 0
0.48903 | 0.4868 | 0.40104 | 700 | 40 | 8.903 | 0
0.48855 | 0.4624 | 0.34374 | 700 | 40 | 8.855 | 0
0.48842 | 0.2108 | 0.2496 | 700 | 40 | 8.842 | 0
0.49503 | 0.0121 | 0.22049 | 700 | 40 | 0.847 | 8.656
0.5138 | 0 | 0.26091 | 699.0564 | 40 | 0 | 10.4364
0.50717 | 0 | 0.33266 | 700 | 40 | 0 | 11.6606
0.49495 | 0 | 0.33261 | 700 | 40 | 0 | 9.495
0.4734 | 0 | 0.38969 | 700 | 40 | 0 | 7.34
0.44017 | 0 | 0.38359 | 700 | 40 | 0 | 4.017
0.41632 | 0 | 0.40952 | 700 | 40 | 0 | 1.632
0.39904 | 0 | 0.43873 | 700 | 39.904 | 0 | 0
0.39256 | 0 | 0.42627 | 700 | 39.256 | 0 | 0
0.38979 | 0 | 0.41946 | 700 | 38.979 | 0 | 0
0.39482 | 0 | 0.43851 | 700 | 39.482 | 0 | 0
0.41079 | 0 | 0.4442 | 700 | 40 | 0 | 1.079
0.45142 | 0 | 0.45953 | 700 | 40 | 0 | 5.142
0.49951 | 0.0083 | 0.47619 | 700 | 40 | 0.581 | 9.37
0.4971 | 0.1644 | 0.44306 | 700 | 40 | 9.71 | 0
0.49979 | 0.4707 | 0.36844 | 700 | 40 | 9.979 | 0
0.50083 | 0.7001 | 0.41611 | 700 | 40 | 10.083 | 0
0.50206 | 0.576 | 0.49854 | 700 | 40 | 10.206 | 0
0.50379 | 0.7209 | 0.53631 | 700 | 40 | 10.379 | 0
0.50948 | 0.7516 | 0.5417 | 700 | 40 | 10.948 | 0
0.51651 | 0.7143 | 0.49412 | 700 | 40 | 11.651 | 0
0.51708 | 0.5669 | 0.47734 | 700 | 40 | 11.708 | 0
0.51788 | 0.4506 | 0.45185 | 700 | 40 | 11.788 | 0
0.51663 | 0.2315 | 0.46488 | 700 | 40 | 11.663 | 0
0.51632 | 0.0207 | 0.46196 | 700 | 40 | 1.449 | 10.183
0.53155 | 0 | 0.50429 | 700 | 40 | 0 | 13.155
0.52382 | 0 | 0.50618 | 700 | 40 | 0 | 12.382
0.51293 | 0 | 0.44045 | 700 | 40 | 0 | 11.293
0.49982 | 0 | 0.37268 | 700 | 40 | 0 | 9.982
0.47784 | 0 | 0.29904 | 700 | 40 | 0 | 7.784
0.45853 | 0 | 0.23737 | 700 | 40 | 0 | 5.853
0.44502 | 0 | 0.21691 | 700 | 40 | 0 | 4.502
0.43881 | 0 | 0.15118 | 700 | 40 | 0 | 3.881
0.43822 | 0 | 0.11822 | 700 | 40 | 0 | 3.822
0.44056 | 0 | 0.11071 | 700 | 40 | 0 | 4.056
0.44864 | 0 | 0.11248 | 699.6352 | 40 | 0 | 4.4992
0.46608 | 0 | 0.13094 | 698.2648 | 40 | 0 | 5.2376
0.49621 | 0.0165 | 0.11159 | 694.2624 | 40 | 1.155 | 4.4636
0.52296 | 0.2546 | 0.08526 | 700 | 40 | 18.0336 | 0
0.54625 | 0.5377 | 0.0679 | 700 | 40 | 14.625 | 0
0.55877 | 0.6731 | 0.06145 | 700 | 40 | 15.877 | 0
0.56472 | 0.738 | 0.11455 | 700 | 40 | 16.472 | 0
0.55846 | 0.7841 | 0.18064 | 700 | 40 | 15.846 | 0
0.54787 | 0.7695 | 0.24311 | 700 | 40 | 14.787 | 0
0.5385 | 0.7991 | 0.33168 | 700 | 40 | 13.85 | 0
0.53156 | 0.7947 | 0.40656 | 700 | 40 | 13.156 | 0
0.52641 | 0.6923 | 0.45816 | 700 | 40 | 12.641 | 0
0.52823 | 0.3551 | 0.5429 | 700 | 40 | 12.823 | 0
0.53899 | 0.0251 | 0.57126 | 700 | 40 | 1.757 | 12.142
0.5531 | 0 | 0.52668 | 700 | 40 | 0 | 15.31
0.54559 | 0 | 0.49086 | 700 | 40 | 0 | 14.559
0.53686 | 0 | 0.50517 | 700 | 40 | 0 | 13.686
0.5208 | 0 | 0.53556 | 700 | 40 | 0 | 12.08
0.49587 | 0 | 0.54506 | 700 | 40 | 0 | 9.587
0.47382 | 0 | 0.55995 | 700 | 40 | 0 | 7.382
0.45681 | 0 | 0.4526 | 700 | 40 | 0 | 5.681
0.44423 | 0 | 0.4332 | 700 | 40 | 0 | 4.423
0.43658 | 0 | 0.45472 | 700 | 40 | 0 | 3.658
0.43748 | 0 | 0.40564 | 700 | 40 | 0 | 3.748
0.44227 | 0 | 0.28596 | 700 | 40 | 0 | 4.227
0.45308 | 0 | 0.2394 | 700 | 40 | 0 | 5.308
0.47318 | 0.0173 | 0.24713 | 700 | 40 | 1.211 | 6.107
0.49143 | 0.3551 | 0.20993 | 700 | 40 | 9.143 | 0
0.5116 | 0.6377 | 0.18824 | 700 | 40 | 11.16 | 0
0.52279 | 0.7397 | 0.19535 | 700 | 40 | 12.279 | 0
0.5134 | 0.8205 | 0.21709 | 700 | 40 | 11.34 | 0
0.50112 | 0.8399 | 0.20812 | 700 | 40 | 10.112 | 0
0.4893 | 0.834 | 0.17393 | 700 | 40 | 8.93 | 0
0.47806 | 0.7703 | 0.1476 | 700 | 40 | 7.806 | 0
0.46762 | 0.7983 | 0.14044 | 700 | 40 | 6.762 | 0
0.46993 | 0.7295 | 0.1487 | 700 | 40 | 6.993 | 0
0.47677 | 0.3453 | 0.15617 | 700 | 40 | 7.677 | 0
0.49487 | 0.0107 | 0.23281 | 700 | 40 | 0.749 | 8.738
0.5272 | 0 | 0.3547 | 700 | 40 | 0 | 12.72
0.5321 | 0 | 0.43833 | 700 | 40 | 0 | 13.21
0.5292 | 0 | 0.50897 | 700 | 40 | 0 | 12.92
0.51671 | 0 | 0.56649 | 700 | 40 | 0 | 11.671
0.49633 | 0 | 0.55955 | 700 | 40 | 0 | 9.633
0.47662 | 0 | 0.57409 | 700 | 40 | 0 | 7.662
0.46544 | 0 | 0.57559 | 700 | 40 | 0 | 6.544
0.46187 | 0 | 0.57599 | 700 | 40 | 0 | 6.187
0.46876 | 0 | 0.59436 | 700 | 40 | 0 | 6.876
0.48109 | 0 | 0.59569 | 700 | 40 | 0 | 8.109
0.50494 | 0 | 0.57046 | 700 | 40 | 0 | 10.494
0.55086 | 0 | 0.53256 | 700 | 40 | 0 | 15.086
0.60003 | 0.011 | 0.49222 | 700 | 40 | 0.77 | 19.233
0.61386 | 0.1446 | 0.45026 | 700 | 40 | 10.122 | 11.264
0.6172 | 0.3473 | 0.46192 | 700 | 40 | 21.72 | 0
0.61168 | 0.4363 | 0.43228 | 700 | 40 | 21.168 | 0
0.60188 | 0.4687 | 0.38452 | 700 | 40 | 20.188 | 0
0.58181 | 0.5202 | 0.32638 | 700 | 40 | 18.181 | 0
0.56574 | 0.4893 | 0.29793 | 700 | 40 | 16.574 | 0
0.55418 | 0.3721 | 0.3111 | 700 | 40 | 15.418 | 0
0.54649 | 0.2561 | 0.33464 | 700 | 40 | 14.649 | 0
0.55104 | 0.1487 | 0.36623 | 700 | 40 | 10.409 | 4.695
0.5609 | 0.0611 | 0.41699 | 700 | 40 | 4.277 | 11.813
0.5845 | 0.0044 | 0.43643 | 699.3152 | 40 | 0.308 | 17.4572
0.61722 | 0 | 0.42927 | 694.764 | 40 | 0 | 17.1708
0.61716 | 0 | 0.43767 | 690.5548 | 40 | 0 | 17.5068
0.60188 | 0 | 0.46916 | 689.1332 | 40 | 0 | 18.7664
0.58089 | 0 | 0.46134 | 689.4978 | 40 | 0 | 18.4536
0.54606 | 0 | 0.46643 | 693.549 | 40 | 0 | 18.6572
0.5241 | 0 | 0.40734 | 697.4326 | 40 | 0 | 16.2936
0.51014 | 0 | 0.35669 | 700 | 40 | 0 | 13.5814
0.50521 | 0 | 0.34317 | 700 | 40 | 0 | 10.521
0.50017 | 0 | 0.32651 | 700 | 40 | 0 | 10.017
0.5091 | 0 | 0.3266 | 700 | 40 | 0 | 10.91
0.52851 | 0 | 0.31405 | 699.711 | 40 | 0 | 12.562
0.57704 | 0 | 0.29094 | 693.6446 | 40 | 0 | 11.6376
0.63043 | 0.0009 | 0.27119 | 681.5122 | 40 | 0.063 | 10.8476
0.62847 | 0.0293 | 0.25139 | 670.7718 | 40 | 2.051 | 10.0556
0.62926 | 0.1293 | 0.23394 | 666.2544 | 40 | 9.051 | 9.3576
0.63719 | 0.2285 | 0.18931 | 666.1028 | 40 | 15.995 | 7.5724
0.64005 | 0.3093 | 0.13928 | 669.32 | 40 | 21.651 | 5.5712
0.63671 | 0.3798 | 0.08515 | 675.641 | 40 | 29.992 | 0
0.63624 | 0.3536 | 0.07371 | 679.7174 | 40 | 27.7004 | 0
0.63203 | 0.3459 | 0.0392 | 682.2954 | 40 | 25.781 | 0
0.626 | 0.286 | 0.02921 | 680.8838 | 40 | 20.02 | 1.1684
0.62901 | 0.2759 | 0.04481 | 679.0882 | 40 | 19.313 | 1.7924
0.63988 | 0.2551 | 0.04768 | 674.8644 | 40 | 17.857 | 1.9072
0.65399 | 0.0248 | 0.04459 | 652.985 | 40 | 1.736 | 1.7836
0.66629 | 0 | 0.04278 | 628.0672 | 40 | 0 | 1.7112
0.65689 | 0 | 0.04406 | 604.1406 | 40 | 0 | 1.7624
0.64143 | 0 | 0.05373 | 582.1468 | 40 | 0 | 2.1492
0.60869 | 0 | 0.07225 | 564.1678 | 40 | 0 | 2.89
0.56953 | 0 | 0.12258 | 552.118 | 40 | 0 | 4.9032
0.54307 | 0 | 0.2075 | 546.111 | 40 | 0 | 8.3
0.52735 | 0 | 0.2925 | 545.076 | 40 | 0 | 11.7
0.52217 | 0 | 0.38275 | 548.169 | 40 | 0 | 15.31
0.52529 | 0 | 0.4139 | 552.196 | 40 | 0 | 16.556
0.53448 | 0 | 0.45936 | 557.1224 | 40 | 0 | 18.3744
0.5611 | 0 | 0.50791 | 561.3288 | 40 | 0 | 20.3164
0.60846 | 0 | 0.46497 | 559.0816 | 40 | 0 | 18.5988
0.66068 | 0.0187 | 0.4571 | 552.6066 | 40 | 1.309 | 18.284
0.64661 | 0.3892 | 0.47363 | 574.1348 | 40 | 46.1892 | -1.1369e-13
0.6238 | 0.7526 | 0.37697 | 619.5156 | 40 | 67.7608 | 0
0.59801 | 0.6981 | 0.32886 | 661.736 | 40 | 62.0214 | 0
0.56989 | 0.7363 | 0.32691 | 700 | 40 | 55.253 | 0
0.54229 | 0.807 | 0.30655 | 700 | 40 | 14.229 | 0
0.52081 | 0.8439 | 0.2838 | 700 | 40 | 12.081 | 0
0.5047 | 0.7916 | 0.25808 | 700 | 40 | 10.47 | 0
0.49401 | 0.7195 | 0.25097 | 700 | 40 | 9.401 | 0
0.49283 | 0.5061 | 0.23255 | 700 | 40 | 9.283 | 0
0.49567 | 0.2706 | 0.21033 | 700 | 40 | 9.567 | 0
0.51454 | 0.01 | 0.22535 | 698.26 | 40 | 0.7 | 9.014
0.54825 | 0 | 0.2728 | 694.347 | 40 | 0 | 10.912
0.5516 | 0 | 0.35342 | 693.3238 | 40 | 0 | 14.1368
0.54951 | 0 | 0.43175 | 695.6428 | 40 | 0 | 17.27
0.52913 | 0 | 0.46629 | 700 | 40 | 0 | 17.2702
0.50217 | 0 | 0.50155 | 700 | 40 | 0 | 10.217
0.4809 | 0 | 0.51696 | 700 | 40 | 0 | 8.09
0.46856 | 0 | 0.54992 | 700 | 40 | 0 | 6.856
0.46539 | 0 | 0.53503 | 700 | 40 | 0 | 6.539
0.46682 | 0 | 0.58014 | 700 | 40 | 0 | 6.682
0.47189 | 0 | 0.56737 | 700 | 40 | 0 | 7.189
0.49367 | 0 | 0.56764 | 700 | 40 | 0 | 9.367
0.53969 | 0 | 0.54427 | 700 | 40 | 0 | 13.969
0.58542 | 0.0041 | 0.53684 | 700 | 40 | 0.287 | 18.255
0.57665 | 0.0651 | 0.49943 | 700 | 40 | 4.557 | 13.108
0.57609 | 0.1812 | 0.44831 | 700 | 40 | 12.684 | 4.925
0.57668 | 0.3238 | 0.48379 | 700 | 40 | 17.668 | 0
0.57491 | 0.437 | 0.52399 | 700 | 40 | 17.491 | 0
0.56987 | 0.505 | 0.54979 | 700 | 40 | 16.987 | 0
0.56192 | 0.5765 | 0.55138 | 700 | 40 | 16.192 | 0
0.55457 | 0.7209 | 0.5493 | 700 | 40 | 15.457 | 0
0.5444 | 0.7103 | 0.53075 | 700 | 40 | 14.44 | 0
0.54575 | 0.6229 | 0.53786 | 700 | 40 | 14.575 | 0
0.55611 | 0.3787 | 0.55173 | 700 | 40 | 15.611 | 0
0.57185 | 0.0308 | 0.54475 | 700 | 40 | 2.156 | 15.029
0.59096 | 0 | 0.52266 | 700 | 40 | 0 | 19.096
0.58408 | 0 | 0.52425 | 700 | 40 | 0 | 18.408
0.57123 | 0 | 0.53684 | 700 | 40 | 0 | 17.123
0.54244 | 0 | 0.5273 | 700 | 40 | 0 | 14.244
0.50792 | 0 | 0.50738 | 700 | 40 | 0 | 10.792
0.48278 | 0 | 0.50632 | 700 | 40 | 0 | 8.278
0.46794 | 0 | 0.44093 | 700 | 40 | 0 | 6.794
0.45957 | 0 | 0.38134 | 700 | 40 | 0 | 5.957
0.45798 | 0 | 0.30836 | 700 | 40 | 0 | 5.798
0.46291 | 0 | 0.26811 | 700 | 40 | 0 | 6.291
0.48241 | 0 | 0.19058 | 699.3822 | 40 | 0 | 7.6232
0.52732 | 0 | 0.12299 | 691.5698 | 40 | 0 | 4.9196
0.56856 | 0.0166 | 0.12913 | 681.041 | 40 | 1.162 | 5.1652
0.56486 | 0.2907 | 0.12202 | 689.7848 | 40 | 25.2298 | 0
0.56215 | 0.5601 | 0.10408 | 700 | 40 | 26.4302 | 0
0.56144 | 0.5729 | 0.07652 | 700 | 40 | 16.144 | 0
0.55474 | 0.5688 | 0.06101 | 700 | 40 | 15.474 | 0
0.5509 | 0.6112 | 0.06415 | 700 | 40 | 15.09 | 0
0.54404 | 0.6393 | 0.06101 | 700 | 40 | 14.404 | 0
0.53952 | 0.6165 | 0.07055 | 700 | 40 | 13.952 | 0
0.5314 | 0.5363 | 0.09812 | 700 | 40 | 13.14 | 0
0.53133 | 0.4403 | 0.13355 | 700 | 40 | 13.133 | 0
0.53285 | 0.2416 | 0.21567 | 700 | 40 | 13.285 | 0
0.53925 | 0.0253 | 0.25906 | 698.2084 | 40 | 1.771 | 10.3624
0.54734 | 0 | 0.33358 | 696.8176 | 40 | 0 | 13.3432
0.5376 | 0 | 0.41743 | 699.7548 | 40 | 0 | 16.6972
0.52987 | 0 | 0.48418 | 700 | 40 | 0 | 13.2322
0.51146 | 0 | 0.5163 | 700 | 40 | 0 | 11.146
0.48838 | 0 | 0.54612 | 700 | 40 | 0 | 8.838
0.46511 | 0 | 0.54727 | 700 | 40 | 0 | 6.511
0.44781 | 0 | 0.61208 | 700 | 40 | 0 | 4.781
0.43681 | 0 | 0.60254 | 700 | 40 | 0 | 3.681
0.43345 | 0 | 0.63602 | 700 | 40 | 0 | 3.345
0.43054 | 0 | 0.65626 | 700 | 40 | 0 | 3.054
0.43614 | 0 | 0.69509 | 700 | 40 | 0 | 3.614
0.44979 | 0 | 0.68912 | 700 | 40 | 0 | 4.979
0.47338 | 0.0256 | 0.71408 | 700 | 40 | 1.792 | 5.546
0.48588 | 0.3933 | 0.70096 | 700 | 40 | 8.588 | 0
0.49989 | 0.6308 | 0.67808 | 700 | 40 | 9.989 | 0
0.50925 | 0.6828 | 0.66871 | 700 | 40 | 10.925 | 0
0.50604 | 0.7224 | 0.65347 | 700 | 40 | 10.604 | 0
0.49724 | 0.7448 | 0.62979 | 700 | 40 | 9.724 | 0
0.4896 | 0.7882 | 0.65272 | 700 | 40 | 8.96 | 0
0.48169 | 0.787 | 0.69146 | 700 | 40 | 8.169 | 0
0.4735 | 0.501 | 0.70193 | 700 | 40 | 7.35 | 0
0.47077 | 0.3683 | 0.70622 | 700 | 40 | 7.077 | 0
0.46907 | 0.2649 | 0.68188 | 700 | 40 | 6.907 | 0
0.47464 | 0.0379 | 0.60276 | 700 | 40 | 2.653 | 4.811
0.49266 | 0 | 0.46453 | 700 | 40 | 0 | 9.266
0.48948 | 0 | 0.37931 | 700 | 40 | 0 | 8.948
0.48835 | 0 | 0.33009 | 700 | 40 | 0 | 8.835
0.47834 | 0 | 0.29365 | 700 | 40 | 0 | 7.834
0.46281 | 0 | 0.25769 | 700 | 40 | 0 | 6.281
0.44569 | 0 | 0.214 | 700 | 40 | 0 | 4.569
0.43718 | 0 | 0.19292 | 700 | 40 | 0 | 3.718
0.4347 | 0 | 0.21749 | 700 | 40 | 0 | 3.47
0.43628 | 0 | 0.2466 | 700 | 40 | 0 | 3.628
0.44448 | 0 | 0.27006 | 700 | 40 | 0 | 4.448
0.45659 | 0 | 0.27757 | 700 | 40 | 0 | 5.659
0.47767 | 0 | 0.28759 | 700 | 40 | 0 | 7.767
0.50041 | 0.0436 | 0.26166 | 700 | 40 | 3.052 | 6.989
0.51648 | 0.4583 | 0.24161 | 700 | 40 | 11.648 | 0
0.5181 | 0.7369 | 0.16646 | 700 | 40 | 11.81 | 0
0.50969 | 0.8262 | 0.1942 | 700 | 40 | 10.969 | 0
0.49295 | 0.8689 | 0.19544 | 700 | 40 | 9.295 | 0
0.48165 | 0.8816 | 0.21753 | 700 | 40 | 8.165 | 0
0.4686 | 0.8891 | 0.22433 | 700 | 40 | 6.86 | 0
0.45693 | 0.8757 | 0.23935 | 700 | 40 | 5.693 | 0
0.45076 | 0.8398 | 0.28852 | 700 | 40 | 5.076 | 0
0.44934 | 0.76 | 0.32828 | 700 | 40 | 4.934 | 0
0.45584 | 0.4478 | 0.37321 | 700 | 40 | 5.584 | 0
0.47098 | 0.039 | 0.40427 | 700 | 40 | 2.73 | 4.368
0.50874 | 0 | 0.4355 | 700 | 40 | 0 | 10.874
0.51922 | 0 | 0.55562 | 700 | 40 | 0 | 11.922
0.51696 | 0 | 0.61376 | 700 | 40 | 0 | 11.696
0.50335 | 0 | 0.61703 | 700 | 40 | 0 | 10.335
0.48173 | 0 | 0.65316 | 700 | 40 | 0 | 8.173
0.46336 | 0 | 0.66518 | 700 | 40 | 0 | 6.336
0.45494 | 0 | 0.67401 | 700 | 40 | 0 | 5.494
0.45504 | 0 | 0.68104 | 700 | 40 | 0 | 5.504
0.45916 | 0 | 0.68351 | 700 | 40 | 0 | 5.916
0.47099 | 0 | 0.68077 | 700 | 40 | 0 | 7.099
0.4986 | 0 | 0.70004 | 700 | 40 | 0 | 9.86
0.55076 | 0 | 0.673 | 700 | 40 | 0 | 15.076
0.60235 | 0.0274 | 0.66964 | 700 | 40 | 1.918 | 18.317
0.58837 | 0.2873 | 0.66231 | 700 | 40 | 18.837 | 0
0.57067 | 0.5886 | 0.60267 | 700 | 40 | 17.067 | 0
0.5592 | 0.6503 | 0.64954 | 700 | 40 | 15.92 | 0
0.54146 | 0.5171 | 0.68577 | 700 | 40 | 14.146 | 0
0.5235 | 0.5834 | 0.6673 | 700 | 40 | 12.35 | 0
0.51319 | 0.7024 | 0.64883 | 700 | 40 | 11.319 | 0
0.50202 | 0.6885 | 0.61177 | 700 | 40 | 10.202 | 0
0.49669 | 0.6536 | 0.59622 | 700 | 40 | 9.669 | 0
0.4919 | 0.557 | 0.58137 | 700 | 40 | 9.19 | 0
0.49479 | 0.277 | 0.57422 | 700 | 40 | 9.479 | 0
0.51042 | 0.0194 | 0.55628 | 700 | 40 | 1.358 | 9.684
0.53953 | 0 | 0.58924 | 700 | 40 | 0 | 13.953
0.54106 | 0 | 0.67216 | 700 | 40 | 0 | 14.106
0.53059 | 0 | 0.69076 | 700 | 40 | 0 | 13.059
0.50446 | 0 | 0.69831 | 700 | 40 | 0 | 10.446
0.46915 | 0 | 0.68952 | 700 | 40 | 0 | 6.915
0.44566 | 0 | 0.66931 | 700 | 40 | 0 | 4.566
0.43267 | 0 | 0.64429 | 700 | 40 | 0 | 3.267
0.42201 | 0 | 0.59925 | 700 | 40 | 0 | 2.201
0.42226 | 0 | 0.56398 | 700 | 40 | 0 | 2.226
0.42598 | 0 | 0.54929 | 700 | 40 | 0 | 2.598
0.44182 | 0 | 0.52509 | 700 | 40 | 0 | 4.182
0.481 | 0 | 0.47809 | 700 | 40 | 0 | 8.1
0.52774 | 0.0202 | 0.41597 | 700 | 40 | 1.414 | 11.36
0.52098 | 0.2771 | 0.35929 | 700 | 40 | 12.098 | 0
0.51855 | 0.5587 | 0.2976 | 700 | 40 | 11.855 | 0
0.51486 | 0.5945 | 0.26555 | 700 | 40 | 11.486 | 0
0.51483 | 0.66 | 0.20251 | 700 | 40 | 11.483 | 0
0.50846 | 0.6799 | 0.17382 | 700 | 40 | 10.846 | 0
0.50575 | 0.7055 | 0.13642 | 700 | 40 | 10.575 | 0
0.5034 | 0.6918 | 0.12343 | 700 | 40 | 10.34 | 0
0.49852 | 0.6978 | 0.14365 | 700 | 40 | 9.852 | 0
0.50073 | 0.6838 | 0.16275 | 700 | 40 | 10.073 | 0
0.50551 | 0.4286 | 0.19405 | 700 | 40 | 10.551 | 0
0.51843 | 0.0468 | 0.2176 | 700 | 40 | 3.276 | 8.567
0.53396 | 0 | 0.27514 | 697.6096 | 40 | 0 | 11.0056
0.53008 | 0 | 0.35135 | 698.6556 | 40 | 0 | 14.054
0.51623 | 0 | 0.39866 | 700 | 40 | 0 | 12.9674
0.4886 | 0 | 0.43663 | 700 | 40 | 0 | 8.86
0.45429 | 0 | 0.45525 | 700 | 40 | 0 | 5.429
0.42696 | 0 | 0.46863 | 700 | 40 | 0 | 2.696
0.41096 | 0 | 0.44252 | 700 | 40 | 0 | 1.096
0.40246 | 0 | 0.40463 | 700 | 40 | 0 | 0.246
0.39632 | 0 | 0.35986 | 700 | 39.632 | 0 | 0
0.39965 | 0 | 0.34529 | 700 | 39.965 | 0 | 0
0.41495 | 0 | 0.29123 | 700 | 40 | 0 | 1.495
0.45823 | 0 | 0.23682 | 700 | 40 | 0 | 5.823
0.50124 | 0.0177 | 0.21694 | 699.7926 | 40 | 1.239 | 8.6776
0.49614 | 0.254 | 0.22104 | 700 | 40 | 9.8214 | 0
0.49917 | 0.418 | 0.22845 | 700 | 40 | 9.917 | 0
0.50257 | 0.5371 | 0.2087 | 700 | 40 | 10.257 | 0
0.50536 | 0.5991 | 0.19004 | 700 | 40 | 10.536 | 0
0.50433 | 0.5817 | 0.29036 | 700 | 40 | 10.433 | 0
0.50492 | 0.526 | 0.32938 | 700 | 40 | 10.492 | 0
0.50992 | 0.5764 | 0.33296 | 700 | 40 | 10.992 | 0
0.51562 | 0.4458 | 0.37062 | 700 | 40 | 11.562 | 0
0.52356 | 0.3279 | 0.40807 | 700 | 40 | 12.356 | 0
0.53646 | 0.1686 | 0.37503 | 700 | 40 | 11.802 | 1.844
0.55156 | 0.012 | 0.34324 | 699.4136 | 40 | 0.84 | 13.7296
0.5759 | 0 | 0.32493 | 694.8208 | 40 | 0 | 12.9972
0.58016 | 0 | 0.30671 | 689.0732 | 40 | 0 | 12.2684
0.57372 | 0 | 0.23342 | 681.038 | 40 | 0 | 9.3368
0.55088 | 0 | 0.20094 | 673.9876 | 40 | 0 | 8.0376
0.51942 | 0 | 0.20133 | 670.0988 | 40 | 0 | 8.0532
0.49626 | 0 | 0.18254 | 667.7744 | 40 | 0 | 7.3016
0.48351 | 0 | 0.14248 | 665.1226 | 40 | 0 | 5.6992
0.48127 | 0 | 0.1321 | 662.2796 | 40 | 0 | 5.284
0.48026 | 0 | 0.10581 | 658.486 | 40 | 0 | 4.2324
0.48603 | 0 | 0.10581 | 654.1154 | 40 | 0 | 4.2324
0.5073 | 0 | 0.08637 | 646.8402 | 40 | 0 | 3.4548
0.55524 | 0 | 0.07451 | 634.2966 | 40 | 0 | 2.9804
0.60776 | 0.006 | 0.07215 | 616.8266 | 40 | 0.42 | 2.886
0.61152 | 0.1553 | 0.07058 | 609.3688 | 40 | 10.871 | 2.8232
0.61845 | 0.3116 | 0.05001 | 611.3362 | 40 | 21.812 | 2.0004
0.62233 | 0.4878 | 0.06003 | 625.6504 | 40 | 36.5472 | 1.1369e-13
0.6235 | 0.6947 | 0.0637 | 654.4774 | 40 | 51.177 | 0
0.61885 | 0.7153 | 0.05363 | 684.8086 | 40 | 52.2162 | 0
0.61121 | 0.7191 | 0.05755 | 700 | 40 | 36.3124 | 0
0.60595 | 0.7216 | 0.0623 | 700 | 40 | 20.595 | 0
0.59688 | 0.7309 | 0.08262 | 700 | 40 | 19.688 | 0
0.59335 | 0.6908 | 0.07726 | 700 | 40 | 19.335 | 0
0.59903 | 0.4426 | 0.10956 | 700 | 40 | 19.903 | 0
0.61914 | 0.0532 | 0.13223 | 687.0992 | 40 | 3.724 | 5.2892
0.64209 | 0 | 0.16851 | 669.6306 | 40 | 0 | 6.7404
0.64189 | 0 | 0.21707 | 654.1244 | 40 | 0 | 8.6828
0.63022 | 0 | 0.26952 | 641.8832 | 40 | 0 | 10.7808
0.60302 | 0 | 0.28517 | 632.988 | 40 | 0 | 11.4068
0.56767 | 0 | 0.2618 | 626.693 | 40 | 0 | 10.472
0.53937 | 0 | 0.25383 | 622.9092 | 40 | 0 | 10.1532
0.5234 | 0 | 0.22052 | 619.39 | 40 | 0 | 8.8208
0.51482 | 0 | 0.18603 | 615.3492 | 40 | 0 | 7.4412
0.51334 | 0 | 0.15974 | 610.4048 | 40 | 0 | 6.3896
0.51698 | 0 | 0.14575 | 604.5368 | 40 | 0 | 5.83
0.53707 | 0 | 0.1406 | 596.4538 | 40 | 0 | 5.624
0.58082 | 0 | 0.14697 | 584.2506 | 40 | 0 | 5.8788
0.62084 | 0.0368 | 0.12281 | 569.655 | 40 | 2.576 | 4.9124
0.61683 | 0.3355 | 0.11841 | 576.1934 | 40 | 28.2214 | 0
0.61283 | 0.5607 | 0.10376 | 598.3098 | 40 | 43.3994 | 0
0.60698 | 0.6725 | 0.0756 | 627.7108 | 40 | 50.099 | 0
0.59343 | 0.6727 | 0.07943 | 658.634 | 40 | 50.2662 | 0
0.57822 | 0.6837 | 0.08092 | 691.9078 | 40 | 51.0958 | 0
0.56058 | 0.64 | 0.08663 | 700 | 40 | 24.1502 | 0
0.54526 | 0.6377 | 0.11035 | 700 | 40 | 14.526 | 0
0.53907 | 0.6545 | 0.11628 | 700 | 40 | 13.907 | 0
0.53969 | 0.5397 | 0.11074 | 700 | 40 | 13.969 | 0
0.54469 | 0.3246 | 0.09657 | 700 | 40 | 14.469 | 0
0.55097 | 0.0476 | 0.09186 | 691.9094 | 40 | 3.332 | 3.6744
0.56759 | 0 | 0.14287 | 680.8652 | 40 | 0 | 5.7148
0.55818 | 0 | 0.25195 | 675.1252 | 40 | 0 | 10.078
0.54642 | 0 | 0.31957 | 673.266 | 40 | 0 | 12.7828
0.529 | 0 | 0.38632 | 675.8188 | 40 | 0 | 15.4528
0.50395 | 0 | 0.38771 | 680.9322 | 40 | 0 | 15.5084
0.48318 | 0 | 0.36474 | 687.2038 | 40 | 0 | 14.5896
0.46568 | 0 | 0.35916 | 695.0022 | 40 | 0 | 14.3664
0.4569 | 0 | 0.3456 | 700 | 40 | 0 | 10.6878
0.45413 | 0 | 0.30436 | 700 | 40 | 0 | 5.413
0.45568 | 0 | 0.25928 | 700 | 40 | 0 | 5.568
0.46498 | 0 | 0.25622 | 700 | 40 | 0 | 6.498
0.48259 | 0 | 0.2332 | 700 | 40 | 0 | 8.259
0.5047 | 0.0158 | 0.19462 | 698.4208 | 40 | 1.106 | 7.7848
0.52511 | 0.1327 | 0.14614 | 700 | 40 | 9.289 | 4.8012
0.54586 | 0.2834 | 0.12757 | 700 | 40 | 14.586 | 0
0.5545 | 0.472 | 0.11322 | 700 | 40 | 15.45 | 0
0.55827 | 0.4714 | 0.10747 | 700 | 40 | 15.827 | 0
0.55276 | 0.5279 | 0.10328 | 700 | 40 | 15.276 | 0
0.54836 | 0.4621 | 0.12216 | 700 | 40 | 14.836 | 0
0.54339 | 0.3842 | 0.12744 | 700 | 40 | 14.339 | 0
0.54158 | 0.2499 | 0.15935 | 700 | 40 | 14.158 | 0
0.54472 | 0.1721 | 0.19401 | 700 | 40 | 12.047 | 2.425
0.54822 | 0.0716 | 0.20452 | 698.3708 | 40 | 5.012 | 8.1808
0.55539 | 0.0195 | 0.20526 | 692.4072 | 40 | 1.365 | 8.2104
0.56627 | 0 | 0.24759 | 685.6838 | 40 | 0 | 9.9036
0.56031 | 0 | 0.28277 | 680.9636 | 40 | 0 | 11.3108
0.54612 | 0 | 0.29886 | 678.306 | 40 | 0 | 11.9544
0.5318 | 0 | 0.28565 | 676.552 | 40 | 0 | 11.426
0.51026 | 0 | 0.23408 | 674.8892 | 40 | 0 | 9.3632
0.49058 | 0 | 0.19288 | 673.5464 | 40 | 0 | 7.7152
0.4752 | 0 | 0.16196 | 672.5048 | 40 | 0 | 6.4784
0.46557 | 0 | 0.21857 | 674.6906 | 40 | 0 | 8.7428
0.46278 | 0 | 0.32641 | 681.469 | 40 | 0 | 13.0564
0.46715 | 0 | 0.28006 | 685.9564 | 40 | 0 | 11.2024
0.47272 | 0 | 0.26593 | 689.3216 | 40 | 0 | 10.6372
0.48895 | 0 | 0.24569 | 690.2542 | 40 | 0 | 9.8276
0.51109 | 0.0052 | 0.25524 | 689.7188 | 40 | 0.364 | 10.2096
0.53593 | 0.0619 | 0.25782 | 690.7716 | 40 | 4.333 | 10.3128
0.56195 | 0.1302 | 0.26327 | 694.2214 | 40 | 9.114 | 10.5308
0.58132 | 0.222 | 0.27225 | 700 | 40 | 15.54 | 8.3706
0.59275 | 0.3218 | 0.27286 | 700 | 40 | 19.275 | 0
0.59441 | 0.3649 | 0.29702 | 700 | 40 | 19.441 | 0
0.59244 | 0.3553 | 0.31922 | 700 | 40 | 19.244 | 0
0.58486 | 0.3114 | 0.36331 | 700 | 40 | 18.486 | 0
0.58208 | 0.2252 | 0.37617 | 700 | 40 | 15.764 | 2.444
0.58917 | 0.1651 | 0.40495 | 700 | 40 | 11.557 | 7.36
0.60308 | 0.0732 | 0.39859 | 700 | 40 | 5.124 | 15.184
0.62941 | 0.0059 | 0.42109 | 694.3156 | 40 | 0.413 | 16.8436
0.66594 | 0 | 0.42737 | 684.8164 | 40 | 0 | 17.0948
0.67924 | 0 | 0.44643 | 674.7496 | 40 | 0 | 17.8572
0.67669 | 0 | 0.46684 | 665.7542 | 40 | 0 | 18.6736
0.66012 | 0 | 0.4589 | 658.0982 | 40 | 0 | 18.356
0.63534 | 0 | 0.46771 | 653.2726 | 40 | 0 | 18.7084
0.61672 | 0 | 0.46881 | 650.353 | 40 | 0 | 18.7524
0.60885 | 0 | 0.46881 | 648.2204 | 40 | 0 | 18.7524
0.61056 | 0 | 0.46641 | 645.8208 | 40 | 0 | 18.6564
0.61896 | 0 | 0.46854 | 642.6664 | 40 | 0 | 18.7416
0.63679 | 0 | 0.46837 | 637.7222 | 40 | 0 | 18.7348
0.66861 | 0 | 0.44313 | 628.5864 | 40 | 0 | 17.7252
0.72753 | 0 | 0.43314 | 613.159 | 40 | 0 | 17.3256
0.78602 | 0.0103 | 0.42608 | 592.3212 | 40 | 0.721 | 17.0432
0.78476 | 0.0694 | 0.38867 | 574.25 | 40 | 4.858 | 15.5468
0.78393 | 0.1547 | 0.36204 | 561.1676 | 40 | 10.829 | 14.4816
0.78126 | 0.2685 | 0.31613 | 554.4818 | 40 | 18.795 | 12.6452
0.76883 | 0.421 | 0.27022 | 557.8776 | 40 | 29.47 | 10.8088
0.75105 | 0.5761 | 0.2554 | 573.3156 | 40 | 50.543 | 0
0.7368 | 0.6908 | 0.22012 | 596.7964 | 40 | 57.1608 | 0
0.72368 | 0.7253 | 0.18961 | 622.7838 | 40 | 58.3554 | 0
0.70656 | 0.8081 | 0.18655 | 656.1568 | 40 | 64.029 | 0
0.70501 | 0.7965 | 0.17683 | 688.484 | 40 | 62.8282 | 0
0.71691 | 0.5294 | 0.14788 | 699.7662 | 40 | 42.9732 | 0
0.74752 | 0.0653 | 0.12696 | 674.6636 | 40 | 4.571 | 5.0784
0.78258 | 0 | 0.10163 | 640.4708 | 40 | 0 | 4.0652
0.78482 | 0 | 0.111 | 606.4288 | 40 | 0 | 4.44
0.77314 | 0 | 0.10869 | 573.4624 | 40 | 0 | 4.3476
0.74454 | 0 | 0.10228 | 543.0996 | 40 | 0 | 4.0912
0.70958 | 0 | 0.10328 | 516.2728 | 40 | 0 | 4.1312
0.68639 | 0 | 0.09391 | 491.3902 | 40 | 0 | 3.7564
0.67917 | 0 | 0.09605 | 467.3152 | 40 | 0 | 3.842
0.67953 | 0 | 0.09653 | 443.2234 | 40 | 0 | 3.8612
0.68678 | 0 | 0.0892 | 418.1134 | 40 | 0 | 3.568
0.69962 | 0 | 0.07848 | 391.2906 | 40 | 0 | 3.1392
0.72724 | 0 | 0.08798 | 362.0858 | 40 | 0 | 3.5192
0.78145 | 0.0001 | 0.09775 | 327.8578 | 40 | 0.007 | 3.91
0.82123 | 0.0504 | 0.09823 | 293.192 | 40 | 3.528 | 3.9292
0.79802 | 0.3924 | 0.12186 | 285.7324 | 40 | 27.468 | 4.8744
0.76838 | 0.7374 | 0.11231 | 305.0048 | 40 | 56.1104 | 0
0.73747 | 0.7919 | 0.1127 | 331.1988 | 40 | 59.941 | 0
0.70675 | 0.826 | 0.11937 | 363.1186 | 40 | 62.5948 | 0
0.67317 | 0.8512 | 0.11941 | 400.162 | 40 | 64.3604 | 0
0.64036 | 0.8322 | 0.1059 | 438.616 | 40 | 62.49 | 0
0.61035 | 0.7536 | 0.10224 | 474.4226 | 40 | 56.8416 | 5.6843e-14
0.58671 | 0.6479 | 0.0933 | 504.8366 | 40 | 49.085 | 0
0.5821 | 0.5943 | 0.08737 | 531.7224 | 40 | 45.0958 | -5.6843e-14
0.58992 | 0.3917 | 0.08196 | 543.4278 | 40 | 30.6974 | 0
0.61707 | 0.0547 | 0.06845 | 528.2878 | 40 | 3.829 | 2.738
0.66799 | 0 | 0.07407 | 504.4516 | 40 | 0 | 2.9628
0.68208 | 0 | 0.10302 | 480.3644 | 40 | 0 | 4.1208
0.67991 | 0 | 0.14235 | 458.0674 | 40 | 0 | 5.694
0.66048 | 0 | 0.17391 | 438.9758 | 40 | 0 | 6.9564
0.63554 | 0 | 0.20761 | 423.7262 | 40 | 0 | 8.3044
0.62042 | 0 | 0.25305 | 411.8062 | 40 | 0 | 10.122
0.61577 | 0 | 0.28976 | 401.8196 | 40 | 0 | 11.5904
0.61559 | 0 | 0.29943 | 392.2378 | 40 | 0 | 11.9772
0.62535 | 0 | 0.29466 | 381.4892 | 40 | 0 | 11.7864
0.63945 | 0 | 0.29978 | 369.5354 | 40 | 0 | 11.9912
0.66763 | 0 | 0.32078 | 355.6036 | 40 | 0 | 12.8312
0.72146 | 0.0001 | 0.33329 | 336.7962 | 40 | 0.007 | 13.3316
0.76583 | 0.0348 | 0.37494 | 317.6468 | 40 | 2.436 | 14.9976
0.72783 | 0.2059 | 0.41659 | 315.9404 | 40 | 14.413 | 16.6636
0.67913 | 0.3734 | 0.37656 | 329.2278 | 40 | 26.138 | 15.0624
0.64448 | 0.4694 | 0.41607 | 354.2806 | 40 | 49.5008 | 5.6843e-14
0.61463 | 0.6131 | 0.47465 | 394.7206 | 40 | 61.903 | 0
0.58597 | 0.7301 | 0.43597 | 444.6694 | 40 | 68.5458 | 0
0.56027 | 0.752 | 0.45273 | 499.3916 | 40 | 70.7492 | 0
0.54551 | 0.7525 | 0.4907 | 557.1436 | 40 | 72.303 | -5.6843e-14
0.53016 | 0.7207 | 0.53423 | 615.9458 | 40 | 71.8182 | 0
0.52913 | 0.5253 | 0.57168 | 662.671 | 40 | 59.6382 | 0
0.53725 | 0.2425 | 0.60205 | 690.003 | 40 | 41.057 | 0
0.55901 | 0.0506 | 0.63014 | 700 | 40 | 3.542 | 22.356
0.59127 | 0 | 0.61062 | 700 | 40 | 0 | 19.127
0.59597 | 0 | 0.65267 | 700 | 40 | 0 | 19.597
0.59088 | 0 | 0.67161 | 700 | 40 | 0 | 19.088
0.56828 | 0 | 0.66846 | 700 | 40 | 0 | 16.828
0.52937 | 0 | 0.63875 | 700 | 40 | 0 | 12.937
0.50344 | 0 | 0.63105 | 700 | 40 | 0 | 10.344
0.49161 | 0 | 0.6272 | 700 | 40 | 0 | 9.161
0.48211 | 0 | 0.61452 | 700 | 40 | 0 | 8.211
0.47956 | 0 | 0.61316 | 700 | 40 | 0 | 7.956
0.48245 | 0 | 0.61894 | 700 | 40 | 0 | 8.245
0.50089 | 0 | 0.61005 | 700 | 40 | 0 | 10.089
0.54232 | 0 | 0.62073 | 700 | 40 | 0 | 14.232
0.58152 | 0.0444 | 0.61023 | 700 | 40 | 3.108 | 15.044
0.56686 | 0.2804 | 0.58442 | 700 | 40 | 16.686 | 0
0.55602 | 0.4057 | 0.49442 | 700 | 40 | 15.602 | 0
0.54288 | 0.6515 | 0.35407 | 700 | 40 | 14.288 | 0
0.52739 | 0.6303 | 0.31155 | 700 | 40 | 12.739 | 0
0.51043 | 0.5219 | 0.31706 | 700 | 40 | 11.043 | 0
0.50065 | 0.4067 | 0.31618 | 700 | 40 | 10.065 | 0
0.49418 | 0.3855 | 0.36006 | 700 | 40 | 9.418 | 0
0.48954 | 0.33 | 0.41751 | 700 | 40 | 8.954 | 0
0.49107 | 0.3247 | 0.44433 | 700 | 40 | 9.107 | 0
0.49589 | 0.1062 | 0.48331 | 700 | 40 | 7.434 | 2.155
0.50615 | 0.0098 | 0.57645 | 700 | 40 | 0.686 | 9.929
0.52835 | 0 | 0.62856 | 700 | 40 | 0 | 12.835
0.52591 | 0 | 0.64536 | 700 | 40 | 0 | 12.591
0.51519 | 0 | 0.66317 | 700 | 40 | 0 | 11.519
0.49239 | 0 | 0.6797 | 700 | 40 | 0 | 9.239
0.45696 | 0 | 0.67235 | 700 | 40 | 0 | 5.696
0.43018 | 0 | 0.62467 | 700 | 40 | 0 | 3.018
0.41286 | 0 | 0.61478 | 700 | 40 | 0 | 1.286
0.4054 | 0 | 0.61242 | 700 | 40 | 0 | 0.54
0.39875 | 0 | 0.52321 | 700 | 39.875 | 0 | 0
0.39998 | 0 | 0.47342 | 700 | 39.998 | 0 | 0
0.41175 | 0 | 0.42591 | 700 | 40 | 0 | 1.175
0.44938 | 0 | 0.3717 | 700 | 40 | 0 | 4.938
0.49142 | 0.0131 | 0.33425 | 700 | 40 | 0.917 | 8.225
0.49255 | 0.0816 | 0.25524 | 700 | 40 | 5.712 | 3.543
0.50143 | 0.1816 | 0.2251 | 700 | 40 | 10.143 | 0
0.5034 | 0.2713 | 0.21871 | 700 | 40 | 10.34 | 0
0.5094 | 0.3397 | 0.21569 | 700 | 40 | 10.94 | 0
0.51042 | 0.4258 | 0.21775 | 700 | 40 | 11.042 | 0
0.51717 | 0.4059 | 0.26001 | 700 | 40 | 11.717 | 0
0.52589 | 0.3499 | 0.32082 | 700 | 40 | 12.589 | 0
0.5299 | 0.2956 | 0.3703 | 700 | 40 | 12.99 | 0
0.5291 | 0.1593 | 0.35175 | 700 | 40 | 11.151 | 1.759
0.52621 | 0.0631 | 0.41003 | 700 | 40 | 4.417 | 8.204
0.52678 | 0.0047 | 0.46616 | 700 | 40 | 0.329 | 12.349
0.54126 | 0 | 0.53393 | 700 | 40 | 0 | 14.126
0.53483 | 0 | 0.62139 | 700 | 40 | 0 | 13.483
0.52257 | 0 | 0.69322 | 700 | 40 | 0 | 12.257
0.50413 | 0 | 0.68767 | 700 | 40 | 0 | 10.413
0.4787 | 0 | 0.63534 | 700 | 40 | 0 | 7.87
0.44943 | 0 | 0.5307 | 700 | 40 | 0 | 4.943
0.42987 | 0 | 0.52707 | 700 | 40 | 0 | 2.987
0.4151 | 0 | 0.59035 | 700 | 40 | 0 | 1.51
0.40939 | 0 | 0.62474 | 700 | 40 | 0 | 0.939
0.40535 | 0 | 0.63288 | 700 | 40 | 0 | 0.535
0.40662 | 0 | 0.64763 | 700 | 40 | 0 | 0.662
0.4171 | 0 | 0.62251 | 700 | 40 | 0 | 1.71
0.43098 | 0.0347 | 0.63656 | 700 | 40 | 2.429 | 0.669
0.45103 | 0.2579 | 0.6363 | 700 | 40 | 5.103 | 0
0.47917 | 0.4527 | 0.60579 | 700 | 40 | 7.917 | 0
0.49841 | 0.5299 | 0.59354 | 700 | 40 | 9.841 | 0
0.51692 | 0.574 | 0.54868 | 700 | 40 | 11.692 | 0
0.52088 | 0.7553 | 0.46978 | 700 | 40 | 12.088 | 0
0.52534 | 0.7531 | 0.39578 | 700 | 40 | 12.534 | 0
0.52786 | 0.7433 | 0.32266 | 700 | 40 | 12.786 | 0
0.53062 | 0.6204 | 0.25067 | 700 | 40 | 13.062 | 0
0.53418 | 0.4618 | 0.22192 | 700 | 40 | 13.418 | 0
0.53155 | 0.2248 | 0.20896 | 700 | 40 | 13.155 | 0
0.52189 | 0.0214 | 0.19233 | 697.0022 | 40 | 1.498 | 7.6932
0.52815 | 0 | 0.16625 | 690.8372 | 40 | 0 | 6.65
0.51657 | 0 | 0.19111 | 686.8246 | 40 | 0 | 7.6444
0.49706 | 0 | 0.19141 | 684.775 | 40 | 0 | 7.6564
0.48061 | 0 | 0.18389 | 684.0696 | 40 | 0 | 7.3556
0.45371 | 0 | 0.22113 | 687.5438 | 40 | 0 | 8.8452
0.4312 | 0 | 0.28048 | 695.643 | 40 | 0 | 11.2192
0.41289 | 0 | 0.35438 | 700 | 40 | 0 | 5.646
0.40248 | 0 | 0.3367 | 700 | 40 | 0 | 0.248
0.39706 | 0 | 0.27506 | 700 | 39.706 | 0 | 0
0.39562 | 0 | 0.31316 | 700 | 39.562 | 0 | 0
0.40177 | 0 | 0.34742 | 700 | 40 | 0 | 0.177
0.41236 | 0 | 0.34987 | 700 | 40 | 0 | 1.236
0.42813 | 0.0099 | 0.37437 | 700 | 40 | 0.693 | 2.12
0.44378 | 0.054 | 0.38133 | 700 | 40 | 3.78 | 0.598
0.46544 | 0.1037 | 0.44275 | 700 | 40 | 6.544 | 0
0.48089 | 0.2691 | 0.43212 | 700 | 40 | 8.089 | 0
0.49184 | 0.3214 | 0.37993 | 700 | 40 | 9.184 | 0
0.49892 | 0.2912 | 0.36024 | 700 | 40 | 9.892 | 0
0.50277 | 0.3318 | 0.29741 | 700 | 40 | 10.277 | 0
0.50442 | 0.289 | 0.26828 | 700 | 40 | 10.442 | 0
0.50684 | 0.2404 | 0.26272 | 700 | 40 | 10.684 | 0
0.51314 | 0.1732 | 0.30678 | 700 | 40 | 11.314 | 0
0.51165 | 0.0768 | 0.30603 | 700 | 40 | 5.376 | 5.789
0.51639 | 0.0101 | 0.2807 | 700 | 40 | 0.707 | 10.932
0.53424 | 0 | 0.29527 | 698.3868 | 40 | 0 | 11.8108
0.5279 | 0 | 0.24299 | 695.3164 | 40 | 0 | 9.7196
0.51024 | 0 | 0.21499 | 692.892 | 40 | 0 | 8.5996
0.48128 | 0 | 0.21236 | 693.2584 | 40 | 0 | 8.4944
0.45413 | 0 | 0.20523 | 696.0546 | 40 | 0 | 8.2092
0.43285 | 0 | 0.20326 | 700 | 40 | 0 | 7.2304
0.41778 | 0 | 0.18344 | 700 | 40 | 0 | 1.778
0.41078 | 0 | 0.17679 | 700 | 40 | 0 | 1.078
0.41287 | 0 | 0.17259 | 700 | 40 | 0 | 1.287
0.42471 | 0 | 0.15085 | 700 | 40 | 0 | 2.471
0.45109 | 0 | 0.12469 | 699.8786 | 40 | 0 | 4.9876
0.48659 | 0 | 0.13024 | 696.4292 | 40 | 0 | 5.2096
0.50158 | 0.0059 | 0.13401 | 692.0446 | 40 | 0.413 | 5.3604
0.50587 | 0.0371 | 0.15593 | 690.2918 | 40 | 2.597 | 6.2372
0.51962 | 0.0874 | 0.16415 | 691.0138 | 40 | 6.118 | 6.566
0.53137 | 0.134 | 0.17224 | 694.1464 | 40 | 9.38 | 6.8896
0.53341 | 0.1665 | 0.16306 | 698.9828 | 40 | 11.655 | 6.5224
0.53997 | 0.1702 | 0.17211 | 700 | 40 | 11.914 | 3.1002
0.54256 | 0.1592 | 0.16861 | 700 | 40 | 11.144 | 3.112
0.5384 | 0.1303 | 0.14324 | 700 | 40 | 9.121 | 4.719
0.54051 | 0.1208 | 0.14538 | 700 | 40 | 8.456 | 5.595
0.53674 | 0.0913 | 0.17194 | 699.5946 | 40 | 6.391 | 6.8776
0.53431 | 0.0436 | 0.17539 | 696.2312 | 40 | 3.052 | 7.0156
0.53506 | 0.0062 | 0.18931 | 690.7316 | 40 | 0.434 | 7.5724
0.54469 | 0 | 0.20326 | 684.393 | 40 | 0 | 8.1304
0.53529 | 0 | 0.21683 | 679.5372 | 40 | 0 | 8.6732
0.51103 | 0 | 0.22855 | 677.5762 | 40 | 0 | 9.142
0.481 | 0 | 0.22461 | 678.4606 | 40 | 0 | 8.9844
0.44888 | 0 | 0.24373 | 683.3218 | 40 | 0 | 9.7492
0.42806 | 0 | 0.2475 | 690.4158 | 40 | 0 | 9.9
0.41662 | 0 | 0.25353 | 698.895 | 40 | 0 | 10.1412
0.40485 | 0 | 0.24723 | 700 | 40 | 0 | 1.59
0.4058 | 0 | 0.24321 | 700 | 40 | 0 | 0.58
0.4155 | 0 | 0.24623 | 700 | 40 | 0 | 1.55
0.44553 | 0 | 0.27851 | 700 | 40 | 0 | 4.553
0.47611 | 0 | 0.33001 | 700 | 40 | 0 | 7.611
0.49414 | 0.0023 | 0.35258 | 700 | 40 | 0.161 | 9.253
0.49998 | 0.0278 | 0.35267 | 700 | 40 | 1.946 | 8.052
0.51216 | 0.0629 | 0.43374 | 700 | 40 | 4.403 | 6.813
0.52334 | 0.1107 | 0.46861 | 700 | 40 | 7.749 | 4.585
0.52776 | 0.1485 | 0.54242 | 700 | 40 | 10.395 | 2.381
0.53262 | 0.1922 | 0.60432 | 700 | 40 | 13.262 | 0
0.53332 | 0.2055 | 0.66859 | 700 | 40 | 13.332 | 0
0.53328 | 0.2088 | 0.69957 | 700 | 40 | 13.328 | 0
0.52995 | 0.1315 | 0.7158 | 700 | 40 | 9.205 | 3.79
0.53008 | 0.1195 | 0.73146 | 700 | 40 | 8.365 | 4.643
0.52803 | 0.0948 | 0.71807 | 700 | 40 | 6.636 | 6.167
0.52613 | 0.0149 | 0.73347 | 700 | 40 | 1.043 | 11.57
0.5391 | 0 | 0.74227 | 700 | 40 | 0 | 13.91
0.52978 | 0 | 0.73671 | 700 | 40 | 0 | 12.978
0.50929 | 0 | 0.73448 | 700 | 40 | 0 | 10.929
0.47661 | 0 | 0.70731 | 700 | 40 | 0 | 7.661
0.44537 | 0 | 0.67069 | 700 | 40 | 0 | 4.537
0.4266 | 0 | 0.68141 | 700 | 40 | 0 | 2.66
0.41128 | 0 | 0.66308 | 700 | 40 | 0 | 1.128
0.40751 | 0 | 0.65735 | 700 | 40 | 0 | 0.751
0.40394 | 0 | 0.6307 | 700 | 40 | 0 | 0.394
0.40944 | 0 | 0.5957 | 700 | 40 | 0 | 0.944
0.43487 | 0 | 0.57812 | 700 | 40 | 0 | 3.487
0.46491 | 0 | 0.58827 | 700 | 40 | 0 | 6.491
0.48133 | 0.0321 | 0.5607 | 700 | 40 | 2.247 | 5.886
0.48906 | 0.1791 | 0.55383 | 700 | 40 | 8.906 | 0
0.50345 | 0.3659 | 0.52863 | 700 | 40 | 10.345 | 0
0.50814 | 0.5478 | 0.47176 | 700 | 40 | 10.814 | 0
0.50937 | 0.7345 | 0.49818 | 700 | 40 | 10.937 | 0
0.51111 | 0.7782 | 0.48239 | 700 | 40 | 11.111 | 0
0.51793 | 0.7996 | 0.47806 | 700 | 40 | 11.793 | 0
0.52009 | 0.7658 | 0.45369 | 700 | 40 | 12.009 | 0
0.52351 | 0.7063 | 0.46655 | 700 | 40 | 12.351 | 0
0.52474 | 0.6209 | 0.47053 | 700 | 40 | 12.474 | 0
0.52783 | 0.4241 | 0.5142 | 700 | 40 | 12.783 | 0
0.5259 | 0.0598 | 0.57772 | 700 | 40 | 4.186 | 8.404
0.53415 | 0 | 0.62279 | 700 | 40 | 0 | 13.415
0.53082 | 0 | 0.67074 | 700 | 40 | 0 | 13.082
0.51158 | 0 | 0.68981 | 700 | 40 | 0 | 11.158
0.48478 | 0 | 0.69545 | 700 | 40 | 0 | 8.478
0.45433 | 0 | 0.69685 | 700 | 40 | 0 | 5.433
0.43565 | 0 | 0.69118 | 700 | 40 | 0 | 3.565
0.41982 | 0 | 0.66329 | 700 | 40 | 0 | 1.982
0.40913 | 0 | 0.63458 | 700 | 40 | 0 | 0.913
0.40623 | 0 | 0.59699 | 700 | 40 | 0 | 0.623
0.41518 | 0 | 0.56131 | 700 | 40 | 0 | 1.518
0.4408 | 0 | 0.51139 | 700 | 40 | 0 | 4.08
0.47186 | 0.0002 | 0.4706 | 700 | 40 | 0.014 | 7.172
0.48163 | 0.1071 | 0.43613 | 700 | 40 | 7.497 | 0.666
0.48588 | 0.5829 | 0.40725 | 700 | 40 | 8.588 | 0
0.49512 | 0.7301 | 0.43981 | 700 | 40 | 9.512 | 0
0.50151 | 0.6826 | 0.45518 | 700 | 40 | 10.151 | 0
0.50207 | 0.7827 | 0.48645 | 700 | 40 | 10.207 | 0
0.5034 | 0.8058 | 0.49216 | 700 | 40 | 10.34 | 0
0.50362 | 0.7916 | 0.49346 | 700 | 40 | 10.362 | 0
0.50108 | 0.7734 | 0.46731 | 700 | 40 | 10.108 | 0
0.50093 | 0.7831 | 0.43284 | 700 | 40 | 10.093 | 0
0.49765 | 0.7342 | 0.42106 | 700 | 40 | 9.765 | 0
0.49524 | 0.4924 | 0.42799 | 700 | 40 | 9.524 | 0
0.48749 | 0.0668 | 0.42782 | 700 | 40 | 4.676 | 4.073
0.505 | 0 | 0.40998 | 700 | 40 | 0 | 10.5
0.50175 | 0 | 0.48653 | 700 | 40 | 0 | 10.175
0.48635 | 0 | 0.56075 | 700 | 40 | 0 | 8.635
0.46055 | 0 | 0.59323 | 700 | 40 | 0 | 6.055
0.43525 | 0 | 0.58695 | 700 | 40 | 0 | 3.525
0.41982 | 0 | 0.60314 | 700 | 40 | 0 | 1.982
0.41144 | 0 | 0.60726 | 700 | 40 | 0 | 1.144
0.40669 | 0 | 0.58587 | 700 | 40 | 0 | 0.669
0.41294 | 0 | 0.55854 | 700 | 40 | 0 | 1.294
0.42573 | 0 | 0.52828 | 700 | 40 | 0 | 2.573
0.46103 | 0 | 0.48922 | 700 | 40 | 0 | 6.103
0.49905 | 0.0003 | 0.44263 | 700 | 40 | 0.021 | 9.884
0.51746 | 0.0961 | 0.40708 | 700 | 40 | 6.727 | 5.019
0.52815 | 0.4882 | 0.38525 | 700 | 40 | 12.815 | 0
0.5316 | 0.6662 | 0.45596 | 700 | 40 | 13.16 | 0
0.52634 | 0.7378 | 0.49887 | 700 | 40 | 12.634 | 0
0.51647 | 0.736 | 0.40686 | 700 | 40 | 11.647 | 0
0.50571 | 0.7344 | 0.35516 | 700 | 40 | 10.571 | 0
0.49665 | 0.7402 | 0.31675 | 700 | 40 | 9.665 | 0
0.48658 | 0.6931 | 0.28622 | 700 | 40 | 8.658 | 0
0.48175 | 0.6593 | 0.23781 | 700 | 40 | 8.175 | 0
0.47799 | 0.5394 | 0.20148 | 700 | 40 | 7.799 | 0
0.48027 | 0.2849 | 0.16433 | 700 | 40 | 8.027 | 0
0.48404 | 0.0338 | 0.13571 | 699.3904 | 40 | 2.366 | 5.4284
0.50501 | 0 | 0.10947 | 693.2682 | 40 | 0 | 4.3788
0.50732 | 0 | 0.12116 | 687.3826 | 40 | 0 | 4.8464
0.49679 | 0 | 0.13618 | 683.1508 | 40 | 0 | 5.4472
0.48301 | 0 | 0.17043 | 681.667 | 40 | 0 | 6.8172
0.46124 | 0 | 0.18368 | 682.8902 | 40 | 0 | 7.3472
0.45021 | 0 | 0.18758 | 685.3724 | 40 | 0 | 7.5032
0.44233 | 0 | 0.20282 | 689.2522 | 40 | 0 | 8.1128
0.4427 | 0 | 0.19494 | 692.7798 | 40 | 0 | 7.7976
0.44702 | 0 | 0.18477 | 695.4686 | 40 | 0 | 7.3908
0.45649 | 0 | 0.17043 | 696.6368 | 40 | 0 | 6.8172
0.47465 | 0 | 0.18594 | 696.6094 | 40 | 0 | 7.4376
0.5012 | 0.0004 | 0.181 | 693.7574 | 40 | 0.028 | 7.24
0.52044 | 0.0683 | 0.19377 | 694.2452 | 40 | 4.781 | 7.7508
0.53004 | 0.2789 | 0.1826 | 700 | 40 | 18.7588 | 0
0.52507 | 0.4282 | 0.12466 | 700 | 40 | 12.507 | 0
0.5167 | 0.5253 | 0.12631 | 700 | 40 | 11.67 | 0
0.49868 | 0.572 | 0.12986 | 700 | 40 | 9.868 | 0
0.48274 | 0.5891 | 0.12847 | 700 | 40 | 8.274 | 0
0.47055 | 0.6187 | 0.11263 | 700 | 40 | 7.055 | 0
0.45887 | 0.5718 | 0.08327 | 700 | 40 | 5.887 | 0
0.45048 | 0.4826 | 0.06504 | 700 | 40 | 5.048 | 0
0.45131 | 0.5018 | 0.04928 | 700 | 40 | 5.131 | 0
0.45453 | 0.3943 | 0.03966 | 700 | 40 | 5.453 | 0
0.46125 | 0.0727 | 0.04534 | 700 | 40 | 5.089 | 1.036
0.48542 | 0 | 0.0782 | 694.586 | 40 | 0 | 3.128
0.48471 | 0 | 0.11657 | 690.7778 | 40 | 0 | 4.6628
0.47905 | 0 | 0.14056 | 688.4952 | 40 | 0 | 5.6224
0.46385 | 0 | 0.13843 | 687.6474 | 40 | 0 | 5.5372
0.44899 | 0 | 0.13311 | 688.0728 | 40 | 0 | 5.3244
0.43914 | 0 | 0.12207 | 689.0416 | 40 | 0 | 4.8828
0.43332 | 0 | 0.11492 | 690.3064 | 40 | 0 | 4.5968
0.43384 | 0 | 0.1057 | 691.1504 | 40 | 0 | 4.228
0.43322 | 0 | 0.09401 | 691.5888 | 40 | 0 | 3.7604
0.44249 | 0 | 0.08457 | 690.7226 | 40 | 0 | 3.3828
0.45877 | 0 | 0.08379 | 688.1972 | 40 | 0 | 3.3516
0.48171 | 0.0006 | 0.09375 | 683.8182 | 40 | 0.042 | 3.75
0.50089 | 0.1342 | 0.08478 | 686.5144 | 40 | 9.394 | 3.3912
0.50659 | 0.5216 | 0.06495 | 700 | 40 | 24.1446 | 0
0.49891 | 0.7114 | 0.03525 | 700 | 40 | 9.891 | 0
0.48494 | 0.7698 | 0.03867 | 700 | 40 | 8.494 | 0
0.47355 | 0.7891 | 0.02667 | 700 | 40 | 7.355 | 0
0.46078 | 0.8039 | 0.03507 | 700 | 40 | 6.078 | 0
0.45131 | 0.7958 | 0.0436 | 700 | 40 | 5.131 | 0
0.44538 | 0.7657 | 0.04317 | 700 | 40 | 4.538 | 0
0.44364 | 0.7403 | 0.0362 | 700 | 40 | 4.364 | 0
0.44478 | 0.6746 | 0.03226 | 700 | 40 | 4.478 | 0
0.45083 | 0.4459 | 0.03139 | 700 | 40 | 5.083 | 0
0.45735 | 0.0706 | 0.0297 | 700 | 40 | 4.942 | 0.793
0.4873 | 0 | 0.04802 | 693.1908 | 40 | 0 | 1.9208
0.48893 | 0 | 0.09522 | 688.1066 | 40 | 0 | 3.8088
0.47719 | 0 | 0.14705 | 686.2696 | 40 | 0 | 5.882
0.45237 | 0 | 0.20313 | 689.1578 | 40 | 0 | 8.1252
0.42802 | 0 | 0.24149 | 696.0154 | 40 | 0 | 9.6596
0.41898 | 0 | 0.2447 | 700 | 40 | 0 | 5.8826
0.4143 | 0 | 0.25539 | 700 | 40 | 0 | 1.43
0.41853 | 0 | 0.24058 | 700 | 40 | 0 | 1.853
0.4261 | 0 | 0.19763 | 700 | 40 | 0 | 2.61
0.44974 | 0 | 0.1752 | 700 | 40 | 0 | 4.974
0.50021 | 0 | 0.14294 | 695.6966 | 40 | 0 | 5.7176
0.55046 | 0.0006 | 0.08994 | 684.2902 | 40 | 0.042 | 3.5976
0.55749 | 0.0816 | 0.06456 | 676.8356 | 40 | 5.712 | 2.5824
0.54832 | 0.3542 | 0.04581 | 688.63 | 40 | 26.6264 | 0
0.53566 | 0.5881 | 0.02711 | 700 | 40 | 24.936 | 0
0.51903 | 0.6148 | 0.03191 | 700 | 40 | 11.903 | 0
0.5034 | 0.6785 | 0.03295 | 700 | 40 | 10.34 | 0
0.49267 | 0.6846 | 0.06941 | 700 | 40 | 9.267 | 0
0.48703 | 0.6491 | 0.1002 | 700 | 40 | 8.703 | 0
0.48038 | 0.5885 | 0.11445 | 700 | 40 | 8.038 | 0
0.4777 | 0.4381 | 0.12337 | 700 | 40 | 7.77 | 0
0.48124 | 0.3037 | 0.13068 | 700 | 40 | 8.124 | 0
0.48479 | 0.1096 | 0.14653 | 700 | 40 | 7.672 | 0.807
0.48706 | 0.0226 | 0.15597 | 699.1148 | 40 | 1.582 | 6.2388
0.50932 | 0 | 0.18139 | 695.4384 | 40 | 0 | 7.2556
0.50637 | 0 | 0.24249 | 694.501 | 40 | 0 | 9.6996
0.48391 | 0 | 0.3371 | 699.594 | 40 | 0 | 13.484
0.45065 | 0 | 0.35884 | 700 | 40 | 0 | 5.471
0.42197 | 0 | 0.37356 | 700 | 40 | 0 | 2.197
0.40941 | 0 | 0.41543 | 700 | 40 | 0 | 0.941
0.40305 | 0 | 0.43769 | 700 | 40 | 0 | 0.305
0.40411 | 0 | 0.43093 | 700 | 40 | 0 | 0.411
0.41098 | 0 | 0.44033 | 700 | 40 | 0 | 1.098
0.431 | 0 | 0.44761 | 700 | 40 | 0 | 3.1
0.47597 | 0 | 0.4525 | 700 | 40 | 0 | 7.597
0.52807 | 0.0007 | 0.49502 | 700 | 40 | 0.049 | 12.758
0.52799 | 0.132 | 0.48242 | 700 | 40 | 9.24 | 3.559
0.52026 | 0.552 | 0.42829 | 700 | 40 | 12.026 | 0
0.51111 | 0.6182 | 0.38395 | 700 | 40 | 11.111 | 0
0.50242 | 0.7258 | 0.4111 | 700 | 40 | 10.242 | 0
0.49439 | 0.7498 | 0.37473 | 700 | 40 | 9.439 | 0
0.48915 | 0.7463 | 0.29943 | 700 | 40 | 8.915 | 0
0.48473 | 0.7395 | 0.25188 | 700 | 40 | 8.473 | 0
0.48066 | 0.7137 | 0.21724 | 700 | 40 | 8.066 | 0
0.48094 | 0.6811 | 0.21464 | 700 | 40 | 8.094 | 0
0.48125 | 0.6332 | 0.22127 | 700 | 40 | 8.125 | 0
0.48369 | 0.4605 | 0.20373 | 700 | 40 | 8.369 | 0
0.48237 | 0.0844 | 0.21014 | 700 | 40 | 5.908 | 2.329
0.50574 | 0 | 0.22071 | 698.2544 | 40 | 0 | 8.8284
0.50229 | 0 | 0.31389 | 700 | 40 | 0 | 11.9746
0.47998 | 0 | 0.37685 | 700 | 40 | 0 | 7.998
0.44499 | 0 | 0.42613 | 700 | 40 | 0 | 4.499
0.41927 | 0 | 0.44016 | 700 | 40 | 0 | 1.927
0.40289 | 0 | 0.45042 | 700 | 40 | 0 | 0.289
0.39429 | 0 | 0.43474 | 700 | 39.429 | 0 | 0
0.3944 | 0 | 0.38733 | 700 | 39.44 | 0 | 0
0.40071 | 0 | 0.36819 | 700 | 40 | 0 | 0.071
0.41855 | 0 | 0.33212 | 700 | 40 | 0 | 1.855
0.458 | 0 | 0.28497 | 700 | 40 | 0 | 5.8
0.50881 | 0.0004 | 0.23915 | 698.713 | 40 | 0.028 | 9.566
0.5092 | 0.0414 | 0.24487 | 700 | 40 | 2.898 | 9.309
0.5018 | 0.1279 | 0.22924 | 700 | 40 | 8.953 | 1.227
0.49832 | 0.2015 | 0.2411 | 700 | 40 | 9.832 | 0
0.49449 | 0.2722 | 0.21707 | 700 | 40 | 9.449 | 0
0.48856 | 0.2766 | 0.18923 | 700 | 40 | 8.856 | 0
0.4886 | 0.3008 | 0.15601 | 700 | 40 | 8.86 | 0
0.48793 | 0.3183 | 0.13917 | 700 | 40 | 8.793 | 0
0.48498 | 0.3241 | 0.12185 | 700 | 40 | 8.498 | 0
0.48741 | 0.3294 | 0.0918 | 700 | 40 | 8.741 | 0
0.49016 | 0.3245 | 0.09453 | 700 | 40 | 9.016 | 0
0.49477 | 0.1868 | 0.0779 | 700 | 40 | 9.477 | 0
0.49217 | 0.0321 | 0.05213 | 695.1152 | 40 | 2.247 | 2.0852
0.51252 | 0 | 0.03698 | 685.3424 | 40 | 0 | 1.4792
0.50921 | 0 | 0.03386 | 675.7758 | 40 | 0 | 1.3544
0.4882 | 0 | 0.03252 | 668.2566 | 40 | 0 | 1.3008
0.45214 | 0 | 0.06019 | 665.4502 | 40 | 0 | 2.4076
0.42249 | 0 | 0.08478 | 666.5924 | 40 | 0 | 3.3912
0.40685 | 0 | 0.1083 | 670.2394 | 40 | 0 | 4.332
0.3962 | 0 | 0.12951 | 675.7998 | 40 | 5.1804 | 0
0.39738 | 0 | 0.15887 | 682.4166 | 40 | 6.3548 | -1.1369e-13
0.4002 | 0 | 0.16788 | 689.1118 | 40 | 0 | 6.7152
0.4171 | 0 | 0.16567 | 694.0286 | 40 | 0 | 6.6268
0.45944 | 0 | 0.17953 | 695.2658 | 40 | 0 | 7.1812
0.51168 | 0.0013 | 0.18187 | 691.4636 | 40 | 0.091 | 7.2748
0.51083 | 0.0841 | 0.19585 | 694.1016 | 40 | 5.887 | 7.834
0.50195 | 0.2795 | 0.16073 | 700 | 40 | 16.0934 | 0
0.49476 | 0.3643 | 0.07036 | 700 | 40 | 9.476 | 0
0.49106 | 0.4454 | 0.06101 | 700 | 40 | 9.106 | 0
0.48812 | 0.4993 | 0.0359 | 700 | 40 | 8.812 | 0
0.49071 | 0.5362 | 0.02009 | 700 | 40 | 9.071 | 0
0.49287 | 0.55 | 0.0307 | 700 | 40 | 9.287 | 0
0.49703 | 0.4949 | 0.05313 | 700 | 40 | 9.703 | 0
0.50673 | 0.5715 | 0.0701 | 700 | 40 | 10.673 | 0
0.50991 | 0.5166 | 0.08846 | 700 | 40 | 10.991 | 0
0.50679 | 0.4029 | 0.09998 | 700 | 40 | 10.679 | 0
0.50076 | 0.0585 | 0.11029 | 698.4306 | 40 | 4.095 | 4.4116
0.51327 | 0 | 0.12709 | 692.1872 | 40 | 0 | 5.0836
0.51138 | 0 | 0.20923 | 689.4184 | 40 | 0 | 8.3692
0.48215 | 0 | 0.29531 | 693.0158 | 40 | 0 | 11.8124
0.44134 | 0 | 0.33082 | 700 | 40 | 0 | 11.1182
0.41187 | 0 | 0.37274 | 700 | 40 | 0 | 1.187
0.39641 | 0 | 0.40223 | 700 | 39.641 | 0 | 0
0.38512 | 0 | 0.42349 | 700 | 38.512 | 0 | 0
0.37967 | 0 | 0.45393 | 700 | 37.967 | 0 | 0
0.38347 | 0 | 0.4932 | 700 | 38.347 | 0 | 0
0.39965 | 0 | 0.48636 | 700 | 39.965 | 0 | 0
0.43835 | 0 | 0.44726 | 700 | 40 | 0 | 3.835
0.49007 | 0.0011 | 0.45094 | 700 | 40 | 0.077 | 8.93
0.49072 | 0.0559 | 0.4276 | 700 | 40 | 3.913 | 5.159
0.4883 | 0.155 | 0.36949 | 700 | 40 | 8.83 | 0
0.49029 | 0.285 | 0.29713 | 700 | 40 | 9.029 | 0
0.49071 | 0.3616 | 0.43492 | 700 | 40 | 9.071 | 0
0.49196 | 0.4673 | 0.50615 | 700 | 40 | 9.196 | 0
0.49926 | 0.4296 | 0.62332 | 700 | 40 | 9.926 | 0
0.50333 | 0.4124 | 0.67208 | 700 | 40 | 10.333 | 0
0.50972 | 0.2977 | 0.65983 | 700 | 40 | 10.972 | 0
0.51189 | 0.2328 | 0.67732 | 700 | 40 | 11.189 | 0
0.5155 | 0.2079 | 0.67 | 700 | 40 | 11.55 | 0
0.51008 | 0.1364 | 0.67225 | 700 | 40 | 9.548 | 1.46
0.49695 | 0.0151 | 0.69092 | 700 | 40 | 1.057 | 8.638
0.50422 | 0 | 0.64372 | 700 | 40 | 0 | 10.422
0.49582 | 0 | 0.65757 | 700 | 40 | 0 | 9.582
0.47792 | 0 | 0.65593 | 700 | 40 | 0 | 7.792
0.44995 | 0 | 0.63224 | 700 | 40 | 0 | 4.995
0.42375 | 0 | 0.61206 | 700 | 40 | 0 | 2.375
0.39986 | 0 | 0.59587 | 700 | 39.986 | 0 | 0
0.38812 | 0 | 0.58253 | 700 | 38.812 | 0 | 0
0.37649 | 0 | 0.53836 | 700 | 37.649 | 0 | 0
0.37742 | 0 | 0.52403 | 700 | 37.742 | 0 | 0
0.37916 | 0 | 0.49554 | 700 | 37.916 | 0 | 0
0.39209 | 0 | 0.48428 | 700 | 39.209 | 0 | 0
0.40618 | 0.0004 | 0.44224 | 700 | 40 | 0.028 | 0.59
0.42335 | 0.1342 | 0.38066 | 700 | 40 | 2.335 | 0
0.44321 | 0.5135 | 0.34312 | 700 | 40 | 4.321 | 0
0.4583 | 0.6408 | 0.29501 | 700 | 40 | 5.83 | 0
0.4689 | 0.6379 | 0.34897 | 700 | 40 | 6.89 | 0
0.47358 | 0.6366 | 0.28592 | 700 | 40 | 7.358 | 0
0.47531 | 0.6266 | 0.25223 | 700 | 40 | 7.531 | 0
0.47245 | 0.6217 | 0.28579 | 700 | 40 | 7.245 | 0
0.47061 | 0.5738 | 0.35789 | 700 | 40 | 7.061 | 0
0.4719 | 0.5905 | 0.39924 | 700 | 40 | 7.19 | 0
0.4721 | 0.4771 | 0.3856 | 700 | 40 | 7.21 | 0
0.47119 | 0.308 | 0.35581 | 700 | 40 | 7.119 | 0
0.47136 | 0.0642 | 0.31653 | 700 | 40 | 4.494 | 2.642
0.48257 | 0 | 0.32225 | 700 | 40 | 0 | 8.257
0.47865 | 0 | 0.35559 | 700 | 40 | 0 | 7.865
0.46522 | 0 | 0.37235 | 700 | 40 | 0 | 6.522
0.44197 | 0 | 0.38555 | 700 | 40 | 0 | 4.197
0.41611 | 0 | 0.42175 | 700 | 40 | 0 | 1.611
0.39926 | 0 | 0.50585 | 700 | 39.926 | 0 | 0
0.38486 | 0 | 0.51871 | 700 | 38.486 | 0 | 0
0.37743 | 0 | 0.521 | 700 | 37.743 | 0 | 0
0.37392 | 0 | 0.51208 | 700 | 37.392 | 0 | 0
0.37306 | 0 | 0.48866 | 700 | 37.306 | 0 | 0
0.37872 | 0 | 0.4842 | 700 | 37.872 | 0 | 0
0.3905 | 0.001 | 0.42214 | 700 | 39.05 | 0 | 0
0.4019 | 0.1375 | 0.372 | 700 | 40 | 0.19 | 0
0.42692 | 0.4627 | 0.28172 | 700 | 40 | 2.692 | 0
0.44884 | 0.6194 | 0.27405 | 700 | 40 | 4.884 | 0
0.46238 | 0.6385 | 0.25093 | 700 | 40 | 6.238 | 0
0.47394 | 0.6571 | 0.19789 | 700 | 40 | 7.394 | 0
0.48525 | 0.6778 | 0.18884 | 700 | 40 | 8.525 | 0
0.49818 | 0.6826 | 0.18174 | 700 | 40 | 9.818 | 0
0.50741 | 0.6756 | 0.19395 | 700 | 40 | 10.741 | 0
0.52257 | 0.6665 | 0.1968 | 700 | 40 | 12.257 | 0
0.53304 | 0.6509 | 0.21369 | 700 | 40 | 13.304 | 0
0.53867 | 0.4992 | 0.21391 | 700 | 40 | 13.867 | 0
0.53267 | 0.0959 | 0.18897 | 700 | 40 | 6.713 | 6.554
0.54083 | 0 | 0.20352 | 694.0578 | 40 | 0 | 8.1408
0.54251 | 0 | 0.27752 | 690.9076 | 40 | 0 | 11.1008
0.5149 | 0 | 0.34208 | 693.1008 | 40 | 0 | 13.6832
0.4743 | 0 | 0.39547 | 700 | 40 | 0 | 14.3292
0.43736 | 0 | 0.39556 | 700 | 40 | 0 | 3.736
0.41053 | 0 | 0.33173 | 700 | 40 | 0 | 1.053
0.39445 | 0 | 0.27622 | 700 | 39.445 | 0 | 0
0.38626 | 0 | 0.19477 | 700 | 38.626 | 0 | 0
0.38509 | 0 | 0.15463 | 700 | 38.509 | 0 | 0
0.39845 | 0 | 0.20023 | 700 | 39.845 | 0 | 0
0.43536 | 0 | 0.22586 | 700 | 40 | 0 | 3.536
0.4829 | 0.0014 | 0.22729 | 700 | 40 | 0.098 | 8.192
0.48559 | 0.1703 | 0.21668 | 700 | 40 | 8.559 | 0
0.48867 | 0.5327 | 0.15008 | 700 | 40 | 8.867 | 0
0.49793 | 0.5983 | 0.1461 | 700 | 40 | 9.793 | 0
0.50784 | 0.6683 | 0.15324 | 700 | 40 | 10.784 | 0
0.51784 | 0.6955 | 0.13709 | 700 | 40 | 11.784 | 0
0.53004 | 0.7328 | 0.12622 | 700 | 40 | 13.004 | 0
0.54433 | 0.7362 | 0.12501 | 700 | 40 | 14.433 | 0
0.55741 | 0.7483 | 0.11709 | 700 | 40 | 15.741 | 0
0.56924 | 0.7313 | 0.12337 | 700 | 40 | 16.924 | 0
0.57458 | 0.6809 | 0.12787 | 700 | 40 | 17.458 | 0
0.57571 | 0.4274 | 0.14186 | 700 | 40 | 17.571 | 0
0.56311 | 0.0711 | 0.13332 | 693.9988 | 40 | 4.977 | 5.3328
0.56631 | 0 | 0.17048 | 684.187 | 40 | 0 | 6.8192
0.55416 | 0 | 0.27141 | 679.6274 | 40 | 0 | 10.8564
0.52049 | 0 | 0.3533 | 681.7104 | 40 | 0 | 14.132
0.47151 | 0 | 0.40396 | 690.7178 | 40 | 0 | 16.1584
0.43159 | 0 | 0.40456 | 700 | 40 | 0 | 12.4412
0.40692 | 0 | 0.39231 | 700 | 40 | 0 | 0.692
0.3884 | 0 | 0.37165 | 700 | 38.84 | 0 | 0
0.38272 | 0 | 0.35304 | 700 | 38.272 | 0 | 0
0.38274 | 0 | 0.31328 | 700 | 38.274 | 0 | 0
0.39425 | 0 | 0.28025 | 700 | 39.425 | 0 | 0
0.43281 | 0 | 0.2566 | 700 | 40 | 0 | 3.281
0.48073 | 0.0028 | 0.23106 | 700 | 40 | 0.196 | 7.877
0.47562 | 0.1216 | 0.21296 | 700 | 40 | 7.562 | 0
0.47772 | 0.3944 | 0.17217 | 700 | 40 | 7.772 | 0
0.48129 | 0.4826 | 0.15991 | 700 | 40 | 8.129 | 0
0.48513 | 0.5482 | 0.17113 | 700 | 40 | 8.513 | 0
0.48966 | 0.5957 | 0.20334 | 700 | 40 | 8.966 | 0
0.49702 | 0.5993 | 0.24106 | 700 | 40 | 9.702 | 0
0.50457 | 0.6117 | 0.26613 | 700 | 40 | 10.457 | 0
0.51441 | 0.6194 | 0.27444 | 700 | 40 | 11.441 | 0
0.52465 | 0.617 | 0.30588 | 700 | 40 | 12.465 | 0
0.53424 | 0.5624 | 0.34429 | 700 | 40 | 13.424 | 0
0.53406 | 0.3905 | 0.38984 | 700 | 40 | 13.406 | 0
0.52495 | 0.0736 | 0.44466 | 700 | 40 | 5.152 | 7.343
0.53573 | 0 | 0.43063 | 700 | 40 | 0 | 13.573
0.52766 | 0 | 0.51884 | 700 | 40 | 0 | 12.766
0.49836 | 0 | 0.61124 | 700 | 40 | 0 | 9.836
0.4559 | 0 | 0.65008 | 700 | 40 | 0 | 5.59
0.42171 | 0 | 0.62683 | 700 | 40 | 0 | 2.171
0.40091 | 0 | 0.65199 | 700 | 40 | 0 | 0.091
0.38883 | 0 | 0.62995 | 700 | 38.883 | 0 | 0
0.3825 | 0 | 0.61804 | 700 | 38.25 | 0 | 0
0.38462 | 0 | 0.61756 | 700 | 38.462 | 0 | 0
0.39771 | 0 | 0.61639 | 700 | 39.771 | 0 | 0
0.43958 | 0 | 0.66407 | 700 | 40 | 0 | 3.958
0.48616 | 0.0025 | 0.6493 | 700 | 40 | 0.175 | 8.441
0.4842 | 0.0731 | 0.65212 | 700 | 40 | 5.117 | 3.303
0.48322 | 0.2218 | 0.61354 | 700 | 40 | 8.322 | 0
0.48827 | 0.3934 | 0.67576 | 700 | 40 | 8.827 | 0
0.49131 | 0.3565 | 0.70048 | 700 | 40 | 9.131 | 0
0.49426 | 0.4699 | 0.68187 | 700 | 40 | 9.426 | 0
0.49876 | 0.5285 | 0.68775 | 700 | 40 | 9.876 | 0
0.50478 | 0.5437 | 0.70395 | 700 | 40 | 10.478 | 0
0.5146 | 0.5667 | 0.71027 | 700 | 40 | 11.46 | 0
0.52347 | 0.4549 | 0.71192 | 700 | 40 | 12.347 | 0
0.52994 | 0.3418 | 0.74296 | 700 | 40 | 12.994 | 0
0.53092 | 0.1839 | 0.74686 | 700 | 40 | 12.873 | 0.219
0.52016 | 0.0383 | 0.74599 | 700 | 40 | 2.681 | 9.335
0.53114 | 0 | 0.74851 | 700 | 40 | 0 | 13.114
0.527 | 0 | 0.75141 | 700 | 40 | 0 | 12.7
0.49809 | 0 | 0.7308 | 700 | 40 | 0 | 9.809
0.45712 | 0 | 0.70031 | 700 | 40 | 0 | 5.712
0.4199 | 0 | 0.67147 | 700 | 40 | 0 | 1.99
0.39974 | 0 | 0.64393 | 700 | 39.974 | 0 | 0
0.38685 | 0 | 0.61709 | 700 | 38.685 | 0 | 0
0.38033 | 0 | 0.60938 | 700 | 38.033 | 0 | 0
0.38014 | 0 | 0.6083 | 700 | 38.014 | 0 | 0
0.39421 | 0 | 0.62609 | 700 | 39.421 | 0 | 0
0.43076 | 0 | 0.63696 | 700 | 40 | 0 | 3.076
0.4805 | 0.0014 | 0.65099 | 700 | 40 | 0.098 | 7.952
0.47766 | 0.0752 | 0.63904 | 700 | 40 | 5.264 | 2.502
0.47971 | 0.3251 | 0.60505 | 700 | 40 | 7.971 | 0
0.48749 | 0.4469 | 0.66597 | 700 | 40 | 8.749 | 0
0.49173 | 0.5963 | 0.67424 | 700 | 40 | 9.173 | 0
0.49601 | 0.6841 | 0.64701 | 700 | 40 | 9.601 | 0
0.50379 | 0.6718 | 0.65801 | 700 | 40 | 10.379 | 0
0.51334 | 0.5897 | 0.65272 | 700 | 40 | 11.334 | 0
0.52052 | 0.5283 | 0.63246 | 700 | 40 | 12.052 | 0
0.53136 | 0.403 | 0.61674 | 700 | 40 | 13.136 | 0
0.5345 | 0.4508 | 0.62492 | 700 | 40 | 13.45 | 0
0.53318 | 0.2555 | 0.63588 | 700 | 40 | 13.318 | 0
0.5224 | 0.0751 | 0.65757 | 700 | 40 | 5.257 | 6.983
0.53439 | 0.0001 | 0.65181 | 700 | 40 | 0.007 | 13.432
0.53121 | 0 | 0.70884 | 700 | 40 | 0 | 13.121
0.50682 | 0 | 0.6988 | 700 | 40 | 0 | 10.682
0.466 | 0 | 0.6852 | 700 | 40 | 0 | 6.6
0.43073 | 0 | 0.67355 | 700 | 40 | 0 | 3.073
0.40684 | 0 | 0.65671 | 700 | 40 | 0 | 0.684
0.39326 | 0 | 0.62912 | 700 | 39.326 | 0 | 0
0.38541 | 0 | 0.60553 | 700 | 38.541 | 0 | 0
0.38753 | 0 | 0.59916 | 700 | 38.753 | 0 | 0
0.3982 | 0 | 0.6015 | 700 | 39.82 | 0 | 0
0.43136 | 0 | 0.63969 | 700 | 40 | 0 | 3.136
0.47587 | 0.0027 | 0.60557 | 700 | 40 | 0.189 | 7.398
0.47806 | 0.1245 | 0.5346 | 700 | 40 | 7.806 | 0
0.48316 | 0.5042 | 0.44388 | 700 | 40 | 8.316 | 0
0.49476 | 0.631 | 0.51351 | 700 | 40 | 9.476 | 0
0.50406 | 0.6572 | 0.47276 | 700 | 40 | 10.406 | 0
0.50697 | 0.6409 | 0.3972 | 700 | 40 | 10.697 | 0
0.51573 | 0.5898 | 0.33199 | 700 | 40 | 11.573 | 0
0.52291 | 0.6896 | 0.27873 | 700 | 40 | 12.291 | 0
0.52614 | 0.6973 | 0.23305 | 700 | 40 | 12.614 | 0
0.52998 | 0.7448 | 0.24729 | 700 | 40 | 12.998 | 0
0.5329 | 0.6972 | 0.29739 | 700 | 40 | 13.29 | 0
0.53081 | 0.5215 | 0.33927 | 700 | 40 | 13.081 | 0
0.52061 | 0.1321 | 0.39331 | 700 | 40 | 9.247 | 2.814
0.52299 | 0 | 0.44141 | 700 | 40 | 0 | 12.299
0.51609 | 0 | 0.48225 | 700 | 40 | 0 | 11.609
0.5018 | 0 | 0.53559 | 700 | 40 | 0 | 10.18
0.4743 | 0 | 0.64644 | 700 | 40 | 0 | 7.43
0.44284 | 0 | 0.66636 | 700 | 40 | 0 | 4.284
0.41405 | 0 | 0.63281 | 700 | 40 | 0 | 1.405
0.39918 | 0 | 0.62207 | 700 | 39.918 | 0 | 0
0.39097 | 0 | 0.60418 | 700 | 39.097 | 0 | 0
0.38698 | 0 | 0.60726 | 700 | 38.698 | 0 | 0
0.38801 | 0 | 0.59063 | 700 | 38.801 | 0 | 0
0.39896 | 0 | 0.58331 | 700 | 39.896 | 0 | 0
0.419 | 0.0015 | 0.61722 | 700 | 40 | 0.105 | 1.795
0.43356 | 0.1021 | 0.63614 | 700 | 40 | 3.356 | 0
0.45796 | 0.2198 | 0.59712 | 700 | 40 | 5.796 | 0
0.4792 | 0.2015 | 0.62899 | 700 | 40 | 7.92 | 0
0.49326 | 0.1924 | 0.62562 | 700 | 40 | 9.326 | 0
0.49644 | 0.2508 | 0.60483 | 700 | 40 | 9.644 | 0
0.49723 | 0.2678 | 0.58851 | 700 | 40 | 9.723 | 0
0.4946 | 0.31 | 0.59617 | 700 | 40 | 9.46 | 0
0.49386 | 0.3236 | 0.60518 | 700 | 40 | 9.386 | 0
0.48674 | 0.3099 | 0.63791 | 700 | 40 | 8.674 | 0
0.48042 | 0.2367 | 0.6403 | 700 | 40 | 8.042 | 0
0.47636 | 0.1381 | 0.65736 | 700 | 40 | 7.636 | 0
0.47713 | 0.0364 | 0.65952 | 700 | 40 | 2.548 | 5.165
0.49515 | 0 | 0.66199 | 700 | 40 | 0 | 9.515
0.49341 | 0 | 0.59145 | 700 | 40 | 0 | 9.341
0.481 | 0 | 0.55729 | 700 | 40 | 0 | 8.1
0.46048 | 0 | 0.52005 | 700 | 40 | 0 | 6.048
0.43913 | 0 | 0.50619 | 700 | 40 | 0 | 3.913
0.42515 | 0 | 0.51091 | 700 | 40 | 0 | 2.515
0.41725 | 0 | 0.49342 | 700 | 40 | 0 | 1.725
0.4129 | 0 | 0.44596 | 700 | 40 | 0 | 1.29
0.41302 | 0 | 0.44501 | 700 | 40 | 0 | 1.302
0.41969 | 0 | 0.44319 | 700 | 40 | 0 | 1.969
0.43524 | 0 | 0.40508 | 700 | 40 | 0 | 3.524
0.45908 | 0.0027 | 0.36183 | 700 | 40 | 0.189 | 5.719
0.48372 | 0.1245 | 0.32692 | 700 | 40 | 8.372 | 0
0.5081 | 0.501 | 0.3174 | 700 | 40 | 10.81 | 0
0.52191 | 0.6878 | 0.32788 | 700 | 40 | 12.191 | 0
0.52281 | 0.7183 | 0.31432 | 700 | 40 | 12.281 | 0
0.51515 | 0.7361 | 0.27436 | 700 | 40 | 11.515 | 0
0.50213 | 0.7716 | 0.21807 | 700 | 40 | 10.213 | 0
0.48714 | 0.7876 | 0.18247 | 700 | 40 | 8.714 | 0
0.47579 | 0.781 | 0.15684 | 700 | 40 | 7.579 | 0
0.46939 | 0.8003 | 0.11756 | 700 | 40 | 6.939 | 0
0.46704 | 0.7767 | 0.11522 | 700 | 40 | 6.704 | 0
0.47119 | 0.577 | 0.10721 | 700 | 40 | 7.119 | 0
0.47964 | 0.1378 | 0.11059 | 700 | 40 | 7.964 | 0
0.5089 | 0.0001 | 0.10877 | 693.4678 | 40 | 0.007 | 4.3508
0.52532 | 0 | 0.13428 | 686.307 | 40 | 0 | 5.3712
0.51069 | 0 | 0.14714 | 681.1236 | 40 | 0 | 5.8856
0.48686 | 0 | 0.12363 | 677.3828 | 40 | 0 | 4.9452
0.46227 | 0 | 0.08377 | 674.5066 | 40 | 0 | 3.3508
0.45037 | 0 | 0.06709 | 672.1532 | 40 | 0 | 2.6836
0.44883 | 0 | 0.06812 | 669.995 | 40 | 0 | 2.7248
0.45248 | 0 | 0.05381 | 666.8994 | 40 | 0 | 2.1524
0.46043 | 0 | 0.05747 | 663.1552 | 40 | 0 | 2.2988
0.48214 | 0 | 0.06295 | 657.4592 | 40 | 0 | 2.518
0.52813 | 0 | 0.0717 | 647.5142 | 40 | 0 | 2.868
0.58232 | 0.0026 | 0.07843 | 632.6014 | 40 | 0.182 | 3.1372
0.57729 | 0.2019 | 0.08274 | 632.315 | 40 | 14.133 | 3.3096
0.57193 | 0.6285 | 0.06674 | 661.7866 | 40 | 46.6646 | 0
0.56674 | 0.6921 | 0.0861 | 697.0036 | 40 | 51.891 | 0
0.55721 | 0.7287 | 0.11085 | 700 | 40 | 18.7174 | 0
0.54169 | 0.7485 | 0.12633 | 700 | 40 | 14.169 | 0
0.52312 | 0.7883 | 0.12339 | 700 | 40 | 12.312 | 0
0.50987 | 0.8029 | 0.12081 | 700 | 40 | 10.987 | 0
0.4973 | 0.8015 | 0.12171 | 700 | 40 | 9.73 | 0
0.49083 | 0.7645 | 0.10524 | 700 | 40 | 9.083 | 0
0.48965 | 0.7066 | 0.08998 | 700 | 40 | 8.965 | 0
0.49431 | 0.522 | 0.07502 | 700 | 40 | 9.431 | 0
0.49455 | 0.0997 | 0.07674 | 700 | 40 | 6.979 | 2.476
0.52334 | 0.0002 | 0.08679 | 691.1516 | 40 | 0.014 | 3.4716
0.52851 | 0 | 0.14349 | 684.0402 | 40 | 0 | 5.7396
0.50858 | 0 | 0.23946 | 682.7606 | 40 | 0 | 9.5784
0.4774 | 0 | 0.33944 | 688.5982 | 40 | 0 | 13.5776
0.45421 | 0 | 0.44063 | 700 | 40 | 0 | 16.8228
0.45072 | 0 | 0.52065 | 700 | 40 | 0 | 5.072
0.44762 | 0 | 0.52824 | 700 | 40 | 0 | 4.762
0.44985 | 0 | 0.55859 | 700 | 40 | 0 | 4.985
0.46161 | 0 | 0.58093 | 700 | 40 | 0 | 6.161
0.48481 | 0 | 0.56773 | 700 | 40 | 0 | 8.481
0.53784 | 0 | 0.56424 | 700 | 40 | 0 | 13.784
0.5973 | 0.009 | 0.56704 | 700 | 40 | 0.63 | 19.1
0.5835 | 0.2533 | 0.55618 | 700 | 40 | 17.731 | 0.619
0.5603 | 0.6888 | 0.48405 | 700 | 40 | 16.03 | 0
0.53874 | 0.7527 | 0.47831 | 700 | 40 | 13.874 | 0
0.5173 | 0.7646 | 0.4615 | 700 | 40 | 11.73 | 0
0.49901 | 0.7734 | 0.42731 | 700 | 40 | 9.901 | 0
0.48956 | 0.7697 | 0.43654 | 700 | 40 | 8.956 | 0
0.4847 | 0.7468 | 0.43666 | 700 | 40 | 8.47 | 0
0.47915 | 0.7264 | 0.43973 | 700 | 40 | 7.915 | 0
0.48231 | 0.7186 | 0.45163 | 700 | 40 | 8.231 | 0
0.48372 | 0.6224 | 0.48357 | 700 | 40 | 8.372 | 0
0.48463 | 0.3704 | 0.52755 | 700 | 40 | 8.463 | 0
0.48534 | 0.082 | 0.55963 | 700 | 40 | 5.74 | 2.794
0.50461 | 0.001 | 0.56394 | 700 | 40 | 0.07 | 10.391
0.50863 | 0 | 0.60861 | 700 | 40 | 0 | 10.863
0.48479 | 0 | 0.62098 | 700 | 40 | 0 | 8.479
0.44757 | 0 | 0.63206 | 700 | 40 | 0 | 4.757
0.41868 | 0 | 0.58009 | 700 | 40 | 0 | 1.868
0.40241 | 0 | 0.57214 | 700 | 40 | 0 | 0.241
0.39373 | 0 | 0.5834 | 700 | 39.373 | 0 | 0
0.39389 | 0 | 0.5797 | 700 | 39.389 | 0 | 0
0.39876 | 0 | 0.55947 | 700 | 39.876 | 0 | 0
0.41591 | 0 | 0.55839 | 700 | 40 | 0 | 1.591
0.45834 | 0 | 0.56797 | 700 | 40 | 0 | 5.834
0.50798 | 0.0025 | 0.61472 | 700 | 40 | 0.175 | 10.623
0.50457 | 0.1496 | 0.61378 | 700 | 40 | 10.457 | 0
0.49853 | 0.5335 | 0.56784 | 700 | 40 | 9.853 | 0
0.49757 | 0.599 | 0.55285 | 700 | 40 | 9.757 | 0
0.49897 | 0.6457 | 0.53162 | 700 | 40 | 9.897 | 0
0.49659 | 0.6541 | 0.53012 | 700 | 40 | 9.659 | 0
0.49296 | 0.6794 | 0.52221 | 700 | 40 | 9.296 | 0
0.49318 | 0.6749 | 0.54761 | 700 | 40 | 9.318 | 0
0.49197 | 0.602 | 0.56423 | 700 | 40 | 9.197 | 0
0.49322 | 0.5283 | 0.58701 | 700 | 40 | 9.322 | 0
0.49786 | 0.4874 | 0.58769 | 700 | 40 | 9.786 | 0
0.50036 | 0.3184 | 0.58318 | 700 | 40 | 10.036 | 0
0.50101 | 0.0732 | 0.65816 | 700 | 40 | 5.124 | 4.977
0.51641 | 0.0001 | 0.68063 | 700 | 40 | 0.007 | 11.634
0.51365 | 0 | 0.7187 | 700 | 40 | 0 | 11.365
0.49056 | 0 | 0.71513 | 700 | 40 | 0 | 9.056
0.45513 | 0 | 0.68841 | 700 | 40 | 0 | 5.513
0.42442 | 0 | 0.6457 | 700 | 40 | 0 | 2.442
0.40651 | 0 | 0.60823 | 700 | 40 | 0 | 0.651
0.39377 | 0 | 0.53803 | 700 | 39.377 | 0 | 0
0.387 | 0 | 0.47602 | 700 | 38.7 | 0 | 0
0.38678 | 0 | 0.43405 | 700 | 38.678 | 0 | 0
0.39981 | 0 | 0.42236 | 700 | 39.981 | 0 | 0
0.43784 | 0 | 0.44354 | 700 | 40 | 0 | 3.784
0.48423 | 0.0068 | 0.42438 | 700 | 40 | 0.476 | 7.947
0.4838 | 0.2652 | 0.35379 | 700 | 40 | 8.38 | 0
0.49122 | 0.6875 | 0.26093 | 700 | 40 | 9.122 | 0
0.50046 | 0.7786 | 0.22355 | 700 | 40 | 10.046 | 0
0.51067 | 0.8072 | 0.23159 | 700 | 40 | 11.067 | 0
0.51963 | 0.8442 | 0.19997 | 700 | 40 | 11.963 | 0
0.53222 | 0.8463 | 0.17681 | 700 | 40 | 13.222 | 0
0.54904 | 0.8365 | 0.13049 | 700 | 40 | 14.904 | 0
0.56106 | 0.8788 | 0.11115 | 700 | 40 | 16.106 | 0
0.57929 | 0.8538 | 0.07622 | 700 | 40 | 17.929 | 0
0.59201 | 0.696 | 0.05049 | 700 | 40 | 19.201 | 0
0.59625 | 0.4267 | 0.03841 | 700 | 40 | 19.625 | 0
0.58281 | 0.0842 | 0.03304 | 688.9346 | 40 | 5.894 | 1.3216
0.58483 | 0.0005 | 0.0632 | 673.0146 | 40 | 0.035 | 2.528
0.57677 | 0 | 0.15309 | 661.4612 | 40 | 0 | 6.1236
0.54169 | 0 | 0.24469 | 657.0798 | 40 | 0 | 9.7876
0.49528 | 0 | 0.33028 | 660.763 | 40 | 0 | 13.2112
0.45451 | 0 | 0.37577 | 670.3428 | 40 | 0 | 15.0308
0.4264 | 0 | 0.40018 | 683.71 | 40 | 0 | 16.0072
0.41267 | 0 | 0.42938 | 699.6182 | 40 | 0 | 17.1752
0.40088 | 0 | 0.4195 | 700 | 40 | 0 | 0.4698
0.40183 | 0 | 0.4224 | 700 | 40 | 0 | 0.183
0.41189 | 0 | 0.41597 | 700 | 40 | 0 | 1.189
0.44478 | 0 | 0.41072 | 700 | 40 | 0 | 4.478
0.48799 | 0.008 | 0.39476 | 700 | 40 | 0.56 | 8.239
0.48623 | 0.2097 | 0.36535 | 700 | 40 | 8.623 | 0
0.49249 | 0.5929 | 0.29216 | 700 | 40 | 9.249 | 0
0.50041 | 0.6124 | 0.25842 | 700 | 40 | 10.041 | 0
0.51369 | 0.6132 | 0.28699 | 700 | 40 | 11.369 | 0
0.52169 | 0.5602 | 0.32745 | 700 | 40 | 12.169 | 0
0.5336 | 0.6458 | 0.35497 | 700 | 40 | 13.36 | 0
0.54942 | 0.5767 | 0.35993 | 700 | 40 | 14.942 | 0
0.56238 | 0.5686 | 0.35732 | 700 | 40 | 16.238 | 0
0.57697 | 0.568 | 0.34531 | 700 | 40 | 17.697 | 0
0.58385 | 0.5041 | 0.34879 | 700 | 40 | 18.385 | 0
0.57711 | 0.4269 | 0.38114 | 700 | 40 | 17.711 | 0
0.55742 | 0.0911 | 0.37938 | 700 | 40 | 6.377 | 9.365
0.55371 | 0.0001 | 0.42068 | 700 | 40 | 0.007 | 15.364
0.54873 | 0 | 0.51559 | 700 | 40 | 0 | 14.873
0.52625 | 0 | 0.5705 | 700 | 40 | 0 | 12.625
0.49629 | 0 | 0.566 | 700 | 40 | 0 | 9.629
0.46313 | 0 | 0.60125 | 700 | 40 | 0 | 6.313
0.43905 | 0 | 0.5773 | 700 | 40 | 0 | 3.905
0.41994 | 0 | 0.52176 | 700 | 40 | 0 | 1.994
0.40708 | 0 | 0.3435 | 700 | 40 | 0 | 0.708
0.40081 | 0 | 0.29619 | 700 | 40 | 0 | 0.081
0.39872 | 0 | 0.2046 | 700 | 39.872 | 0 | 0
0.41062 | 0 | 0.22128 | 700 | 40 | 0 | 1.062
0.42904 | 0.0054 | 0.21914 | 700 | 40 | 0.378 | 2.526
0.44566 | 0.2229 | 0.1962 | 700 | 40 | 4.566 | 0
0.4677 | 0.5766 | 0.21998 | 700 | 40 | 6.77 | 0
0.48941 | 0.7223 | 0.15726 | 700 | 40 | 8.941 | 0
0.50006 | 0.7316 | 0.14373 | 700 | 40 | 10.006 | 0
0.50627 | 0.7609 | 0.18057 | 700 | 40 | 10.627 | 0
0.5124 | 0.7256 | 0.1962 | 700 | 40 | 11.24 | 0
0.51582 | 0.7032 | 0.19347 | 700 | 40 | 11.582 | 0
0.52366 | 0.6362 | 0.20208 | 700 | 40 | 12.366 | 0
0.53326 | 0.6347 | 0.19864 | 700 | 40 | 13.326 | 0
0.53513 | 0.4729 | 0.20162 | 700 | 40 | 13.513 | 0
0.53224 | 0.2929 | 0.20259 | 700 | 40 | 13.224 | 0
0.5215 | 0.1239 | 0.20322 | 700 | 40 | 8.673 | 3.477
0.52305 | 0.0007 | 0.25557 | 697.9668 | 40 | 0.049 | 10.2228
0.52051 | 0 | 0.36888 | 700 | 40 | 0 | 14.0842
0.50502 | 0 | 0.42366 | 700 | 40 | 0 | 10.502
0.48348 | 0 | 0.45349 | 700 | 40 | 0 | 8.348
0.45203 | 0 | 0.47799 | 700 | 40 | 0 | 5.203
0.42899 | 0 | 0.46261 | 700 | 40 | 0 | 2.899
0.41443 | 0 | 0.44774 | 700 | 40 | 0 | 1.443
0.40236 | 0 | 0.4061 | 700 | 40 | 0 | 0.236
0.39671 | 0 | 0.39728 | 700 | 39.671 | 0 | 0
0.39652 | 0 | 0.37888 | 700 | 39.652 | 0 | 0
0.3972 | 0 | 0.37438 | 700 | 39.72 | 0 | 0
0.40892 | 0.0046 | 0.31775 | 700 | 40 | 0.322 | 0.57
0.41837 | 0.0867 | 0.26867 | 700 | 40 | 1.837 | 0
0.44056 | 0.2809 | 0.30712 | 700 | 40 | 4.056 | 0
0.46058 | 0.5032 | 0.27615 | 700 | 40 | 6.058 | 0
0.46953 | 0.6797 | 0.23985 | 700 | 40 | 6.953 | 0
0.4774 | 0.7435 | 0.21213 | 700 | 40 | 7.74 | 0
0.47755 | 0.7275 | 0.17923 | 700 | 40 | 7.755 | 0
0.47611 | 0.7577 | 0.20582 | 700 | 40 | 7.611 | 0
0.47633 | 0.7473 | 0.2262 | 700 | 40 | 7.633 | 0
0.48234 | 0.6982 | 0.21082 | 700 | 40 | 8.234 | 0
0.48989 | 0.5692 | 0.1907 | 700 | 40 | 8.989 | 0
0.49794 | 0.4894 | 0.16394 | 700 | 40 | 9.794 | 0
0.49857 | 0.117 | 0.1352 | 700 | 40 | 8.19 | 1.667
0.50678 | 0.0006 | 0.12898 | 694.5232 | 40 | 0.042 | 5.1592
0.50608 | 0 | 0.16205 | 690.3972 | 40 | 0 | 6.482
0.48144 | 0 | 0.21259 | 690.7568 | 40 | 0 | 8.5036
0.44479 | 0 | 0.20284 | 694.3914 | 40 | 0 | 8.1136
0.41023 | 0 | 0.18083 | 700 | 40 | 0 | 6.6316
0.3906 | 0 | 0.17028 | 700 | 39.06 | 0 | 0
0.37744 | 0 | 0.13902 | 700 | 37.744 | 0 | 0
0.37127 | 0 | 0.10045 | 700 | 37.127 | 0 | 0
0.37232 | 0 | 0.08293 | 700 | 37.232 | 0 | 0
0.3871 | 0 | 0.07285 | 700 | 38.71 | 0 | 0
0.42198 | 0 | 0.07272 | 700 | 40 | 0 | 2.198
0.46906 | 0.0133 | 0.08277 | 697.3358 | 40 | 0.931 | 3.3108
0.47096 | 0.3352 | 0.08214 | 700 | 40 | 9.7602 | 0
0.47725 | 0.7913 | 0.05512 | 700 | 40 | 7.725 | 0
0.48952 | 0.8566 | 0.02983 | 700 | 40 | 8.952 | 0
0.50398 | 0.8813 | 0.0284 | 700 | 40 | 10.398 | 0
0.51726 | 0.8897 | 0.03227 | 700 | 40 | 11.726 | 0
0.53608 | 0.8892 | 0.04684 | 700 | 40 | 13.608 | 0
0.55846 | 0.8856 | 0.05004 | 700 | 40 | 15.846 | 0
0.57639 | 0.8804 | 0.0442 | 700 | 40 | 17.639 | 0
0.59473 | 0.8633 | 0.03806 | 700 | 40 | 19.473 | 0
0.60953 | 0.8287 | 0.04311 | 700 | 40 | 20.953 | 0
0.61519 | 0.6388 | 0.04748 | 700 | 40 | 21.519 | 0
0.60534 | 0.1661 | 0.05479 | 693.2846 | 40 | 11.627 | 2.1916
0.59496 | 0.0006 | 0.0884 | 677.3666 | 40 | 0.042 | 3.536
0.58062 | 0 | 0.18835 | 666.8386 | 40 | 0 | 7.534
0.53909 | 0 | 0.28628 | 664.3808 | 40 | 0 | 11.4512
0.48949 | 0 | 0.34106 | 669.0742 | 40 | 0 | 13.6424
0.4446 | 0 | 0.39098 | 680.2534 | 40 | 0 | 15.6392
0.41479 | 0 | 0.40253 | 694.8756 | 40 | 0 | 16.1012
0.39794 | 0 | 0.42017 | 700 | 40 | 4.9184 | 0
0.38717 | 0 | 0.4248 | 700 | 38.717 | 0 | 0
0.38822 | 0 | 0.42719 | 700 | 38.822 | 0 | 0
0.39641 | 0 | 0.41476 | 700 | 39.641 | 0 | 0
0.42975 | 0 | 0.39824 | 700 | 40 | 0 | 2.975
0.47173 | 0.0215 | 0.39182 | 700 | 40 | 1.505 | 5.668
0.46927 | 0.3821 | 0.39837 | 700 | 40 | 6.927 | 0
0.47715 | 0.8211 | 0.29699 | 700 | 40 | 7.715 | 0
0.50414 | 0.8634 | 0.22036 | 700 | 40 | 10.414 | 0
0.52729 | 0.8748 | 0.22746 | 700 | 40 | 12.729 | 0
0.55337 | 0.8891 | 0.23565 | 700 | 40 | 15.337 | 0
0.58274 | 0.8866 | 0.28103 | 700 | 40 | 18.274 | 0
0.61394 | 0.8747 | 0.31422 | 700 | 40 | 21.394 | 0
0.64091 | 0.8643 | 0.33312 | 700 | 40 | 24.091 | 0
0.66515 | 0.8392 | 0.35652 | 700 | 40 | 26.515 | 0
0.67878 | 0.7823 | 0.38001 | 700 | 40 | 27.878 | 0
0.67968 | 0.5551 | 0.39203 | 700 | 40 | 27.968 | 0
0.65748 | 0.1394 | 0.39829 | 699.9416 | 40 | 9.758 | 15.9316
0.63643 | 0.0005 | 0.50097 | 696.3724 | 40 | 0.035 | 20.0388
0.621 | 0 | 0.64541 | 700 | 40 | 0 | 25.7276
0.57751 | 0 | 0.7104 | 700 | 40 | 0 | 17.751
0.52367 | 0 | 0.73427 | 700 | 40 | 0 | 12.367
0.47527 | 0 | 0.72284 | 700 | 40 | 0 | 7.527
0.44355 | 0 | 0.71095 | 700 | 40 | 0 | 4.355
0.42463 | 0 | 0.68919 | 700 | 40 | 0 | 2.463
0.41199 | 0 | 0.64713 | 700 | 40 | 0 | 1.199
0.40878 | 0 | 0.64881 | 700 | 40 | 0 | 0.878
0.41815 | 0 | 0.65465 | 700 | 40 | 0 | 1.815
0.45083 | 0 | 0.70759 | 700 | 40 | 0 | 5.083
0.48819 | 0.0161 | 0.71225 | 700 | 40 | 1.127 | 7.692
0.48938 | 0.3636 | 0.702 | 700 | 40 | 8.938 | 0
0.50431 | 0.7969 | 0.62633 | 700 | 40 | 10.431 | 0
0.52814 | 0.8626 | 0.5555 | 700 | 40 | 12.814 | 0
0.55289 | 0.849 | 0.57571 | 700 | 40 | 15.289 | 0
0.58078 | 0.817 | 0.61911 | 700 | 40 | 18.078 | 0
0.61182 | 0.832 | 0.63881 | 700 | 40 | 21.182 | 0
0.63989 | 0.7869 | 0.64364 | 700 | 40 | 23.989 | 0
0.66271 | 0.6763 | 0.64369 | 700 | 40 | 26.271 | 0
0.68578 | 0.6991 | 0.62339 | 700 | 40 | 28.578 | 0
0.69523 | 0.6117 | 0.61793 | 700 | 40 | 29.523 | 0
0.69048 | 0.4664 | 0.62226 | 700 | 40 | 29.048 | 0
0.66479 | 0.0833 | 0.60726 | 700 | 40 | 5.831 | 20.648
0.64267 | 0.0001 | 0.66494 | 700 | 40 | 0.007 | 24.26
0.63309 | 0 | 0.68213 | 700 | 40 | 0 | 23.309
0.59123 | 0 | 0.71721 | 700 | 40 | 0 | 19.123
0.53701 | 0 | 0.69549 | 700 | 40 | 0 | 13.701
0.48548 | 0 | 0.67171 | 700 | 40 | 0 | 8.548
0.45447 | 0 | 0.62789 | 700 | 40 | 0 | 5.447
0.43174 | 0 | 0.61003 | 700 | 40 | 0 | 3.174
0.41798 | 0 | 0.60432 | 700 | 40 | 0 | 1.798
0.41411 | 0 | 0.56983 | 700 | 40 | 0 | 1.411
0.42171 | 0 | 0.58907 | 700 | 40 | 0 | 2.171
0.45498 | 0 | 0.58676 | 700 | 40 | 0 | 5.498
0.49385 | 0.0202 | 0.53357 | 700 | 40 | 1.414 | 7.971
0.4888 | 0.3649 | 0.45143 | 700 | 40 | 8.88 | 0
0.50163 | 0.7235 | 0.42929 | 700 | 40 | 10.163 | 0
0.51801 | 0.6351 | 0.48382 | 700 | 40 | 11.801 | 0
0.52855 | 0.7084 | 0.45009 | 700 | 40 | 12.855 | 0
0.53309 | 0.7665 | 0.3956 | 700 | 40 | 13.309 | 0
0.53871 | 0.799 | 0.36896 | 700 | 40 | 13.871 | 0
0.54142 | 0.8054 | 0.34144 | 700 | 40 | 14.142 | 0
0.54534 | 0.8045 | 0.33148 | 700 | 40 | 14.534 | 0
0.55596 | 0.7865 | 0.28678 | 700 | 40 | 15.596 | 0
0.56291 | 0.7253 | 0.2475 | 700 | 40 | 16.291 | 0
0.56038 | 0.5775 | 0.21721 | 700 | 40 | 16.038 | 0
0.54781 | 0.1615 | 0.19208 | 700 | 40 | 11.305 | 3.476
0.54899 | 0.0011 | 0.18515 | 692.584 | 40 | 0.077 | 7.406
0.54699 | 0 | 0.23149 | 687.1446 | 40 | 0 | 9.2596
0.51543 | 0 | 0.27082 | 686.4344 | 40 | 0 | 10.8328
0.47214 | 0 | 0.27338 | 690.1556 | 40 | 0 | 10.9352
0.43517 | 0 | 0.31128 | 699.0898 | 40 | 0 | 12.4512
0.40939 | 0 | 0.33317 | 700 | 40 | 0 | 1.8492
0.39417 | 0 | 0.32384 | 700 | 39.417 | 0 | 0
0.38759 | 0 | 0.29989 | 700 | 38.759 | 0 | 0
0.38583 | 0 | 0.33581 | 700 | 38.583 | 0 | 0
0.40073 | 0 | 0.35371 | 700 | 40 | 0 | 0.073
0.43691 | 0 | 0.36291 | 700 | 40 | 0 | 3.691
0.48717 | 0.0247 | 0.36543 | 700 | 40 | 1.729 | 6.988
0.48394 | 0.331 | 0.37581 | 700 | 40 | 8.394 | 0
0.48552 | 0.6797 | 0.29157 | 700 | 40 | 8.552 | 0
0.49 | 0.7233 | 0.28935 | 700 | 40 | 9 | 0
0.49237 | 0.7256 | 0.30493 | 700 | 40 | 9.237 | 0
0.49534 | 0.7551 | 0.29136 | 700 | 40 | 9.534 | 0
0.50052 | 0.7455 | 0.31363 | 700 | 40 | 10.052 | 0
0.50659 | 0.6855 | 0.31796 | 700 | 40 | 10.659 | 0
0.51433 | 0.5793 | 0.34329 | 700 | 40 | 11.433 | 0
0.52457 | 0.537 | 0.37039 | 700 | 40 | 12.457 | 0
0.52901 | 0.2801 | 0.37904 | 700 | 40 | 12.901 | 0
0.52426 | 0.1491 | 0.41173 | 700 | 40 | 10.437 | 1.989
0.51833 | 0.0307 | 0.4003 | 700 | 40 | 2.149 | 9.684
0.52375 | 0 | 0.41429 | 700 | 40 | 0 | 12.375
0.52461 | 0 | 0.47429 | 700 | 40 | 0 | 12.461
0.5072 | 0 | 0.57096 | 700 | 40 | 0 | 10.72
0.48269 | 0 | 0.60444 | 700 | 40 | 0 | 8.269
0.4517 | 0 | 0.60327 | 700 | 40 | 0 | 5.17
0.42806 | 0 | 0.59461 | 700 | 40 | 0 | 2.806
0.41261 | 0 | 0.58104 | 700 | 40 | 0 | 1.261
0.40154 | 0 | 0.54764 | 700 | 40 | 0 | 0.154
0.39889 | 0 | 0.53542 | 700 | 39.889 | 0 | 0
0.4005 | 0 | 0.52067 | 700 | 40 | 0 | 0.05
0.4107 | 0 | 0.48038 | 700 | 40 | 0 | 1.07
0.43005 | 0.0054 | 0.47282 | 700 | 40 | 0.378 | 2.627
0.44759 | 0.0642 | 0.47836 | 700 | 40 | 4.494 | 0.265
0.47585 | 0.1052 | 0.51038 | 700 | 40 | 7.364 | 0.221
0.50125 | 0.1812 | 0.5731 | 700 | 40 | 10.125 | 0
0.52057 | 0.1907 | 0.58764 | 700 | 40 | 12.057 | 0
0.52774 | 0.2835 | 0.62238 | 700 | 40 | 12.774 | 0
0.53361 | 0.4107 | 0.69356 | 700 | 40 | 13.361 | 0
0.53695 | 0.4106 | 0.71948 | 700 | 40 | 13.695 | 0
0.5299 | 0.4986 | 0.73435 | 700 | 40 | 12.99 | 0
0.51636 | 0.3861 | 0.72586 | 700 | 40 | 11.636 | 0
0.51675 | 0.3583 | 0.77233 | 700 | 40 | 11.675 | 0
0.51969 | 0.2301 | 0.74931 | 700 | 40 | 11.969 | 0
0.50729 | 0.0946 | 0.71729 | 700 | 40 | 6.622 | 4.107
0.50555 | 0.0009 | 0.65591 | 700 | 40 | 0.063 | 10.492
0.49919 | 0 | 0.57848 | 700 | 40 | 0 | 9.919
0.4836 | 0 | 0.52891 | 700 | 40 | 0 | 8.36
0.46259 | 0 | 0.47412 | 700 | 40 | 0 | 6.259
0.43992 | 0 | 0.41018 | 700 | 40 | 0 | 3.992
0.42441 | 0 | 0.33741 | 700 | 40 | 0 | 2.441
0.41321 | 0 | 0.30388 | 700 | 40 | 0 | 1.321
0.40595 | 0 | 0.25498 | 700 | 40 | 0 | 0.595
0.40419 | 0 | 0.26103 | 700 | 40 | 0 | 0.419
0.40808 | 0 | 0.27527 | 700 | 40 | 0 | 0.808
0.41789 | 0 | 0.28989 | 700 | 40 | 0 | 1.789
0.43332 | 0.0305 | 0.27578 | 700 | 40 | 2.135 | 1.197
0.45138 | 0.4236 | 0.27578 | 700 | 40 | 5.138 | 0
0.46429 | 0.8406 | 0.22956 | 700 | 40 | 6.429 | 0
0.46719 | 0.8732 | 0.19087 | 700 | 40 | 6.719 | 0
0.46152 | 0.8821 | 0.18503 | 700 | 40 | 6.152 | 0
0.45685 | 0.8875 | 0.19792 | 700 | 40 | 5.685 | 0
0.45257 | 0.8893 | 0.22565 | 700 | 40 | 5.257 | 0
0.44687 | 0.8854 | 0.25569 | 700 | 40 | 4.687 | 0
0.45151 | 0.8791 | 0.28019 | 700 | 40 | 5.151 | 0
0.45562 | 0.8717 | 0.29447 | 700 | 40 | 5.562 | 0
0.46648 | 0.8478 | 0.32766 | 700 | 40 | 6.648 | 0
0.4772 | 0.6941 | 0.33211 | 700 | 40 | 7.72 | 0
0.47935 | 0.2023 | 0.29371 | 700 | 40 | 7.935 | 0
0.48789 | 0.0009 | 0.32338 | 700 | 40 | 0.063 | 8.726
0.49402 | 0 | 0.46988 | 700 | 40 | 0 | 9.402
0.47884 | 0 | 0.63369 | 700 | 40 | 0 | 7.884
0.44479 | 0 | 0.68036 | 700 | 40 | 0 | 4.479
0.41262 | 0 | 0.62591 | 700 | 40 | 0 | 1.262
0.39263 | 0 | 0.5973 | 700 | 39.263 | 0 | 0
0.38344 | 0 | 0.57239 | 700 | 38.344 | 0 | 0
0.38202 | 0 | 0.57798 | 700 | 38.202 | 0 | 0
0.38551 | 0 | 0.58293 | 700 | 38.551 | 0 | 0
0.40222 | 0 | 0.62318 | 700 | 40 | 0 | 0.222
0.44522 | 0 | 0.69234 | 700 | 40 | 0 | 4.522
0.48875 | 0.0253 | 0.70288 | 700 | 40 | 1.771 | 7.104
0.48952 | 0.2979 | 0.64116 | 700 | 40 | 8.952 | 0
0.49084 | 0.6451 | 0.56289 | 700 | 40 | 9.084 | 0
0.49141 | 0.8008 | 0.58407 | 700 | 40 | 9.141 | 0
0.49585 | 0.7548 | 0.58138 | 700 | 40 | 9.585 | 0
0.50386 | 0.7057 | 0.60016 | 700 | 40 | 10.386 | 0
0.51091 | 0.727 | 0.59751 | 700 | 40 | 11.091 | 0
0.52209 | 0.7533 | 0.61146 | 700 | 40 | 12.209 | 0
0.53321 | 0.7169 | 0.62201 | 700 | 40 | 13.321 | 0
0.54693 | 0.7432 | 0.62587 | 700 | 40 | 14.693 | 0
0.55863 | 0.774 | 0.65095 | 700 | 40 | 15.863 | 0
0.56311 | 0.5919 | 0.66343 | 700 | 40 | 16.311 | 0
0.55508 | 0.12 | 0.6691 | 700 | 40 | 8.4 | 7.108
0.54998 | 0.0007 | 0.67213 | 700 | 40 | 0.049 | 14.949
0.55207 | 0 | 0.69805 | 700 | 40 | 0 | 15.207
0.52076 | 0 | 0.63785 | 700 | 40 | 0 | 12.076
0.47617 | 0 | 0.63734 | 700 | 40 | 0 | 7.617
0.43897 | 0 | 0.61054 | 700 | 40 | 0 | 3.897
0.41507 | 0 | 0.59587 | 700 | 40 | 0 | 1.507
0.40061 | 0 | 0.57483 | 700 | 40 | 0 | 0.061
0.39398 | 0 | 0.56995 | 700 | 39.398 | 0 | 0
0.39225 | 0 | 0.57445 | 700 | 39.225 | 0 | 0
0.4032 | 0 | 0.58688 | 700 | 40 | 0 | 0.32
0.43952 | 0 | 0.61789 | 700 | 40 | 0 | 3.952
0.48233 | 0.0116 | 0.67314 | 700 | 40 | 0.812 | 7.421
0.4852 | 0.0933 | 0.63524 | 700 | 40 | 6.531 | 1.989
0.49263 | 0.1833 | 0.62911 | 700 | 40 | 9.263 | 0
0.50752 | 0.3708 | 0.66322 | 700 | 40 | 10.752 | 0
0.51986 | 0.5193 | 0.65919 | 700 | 40 | 11.986 | 0
0.53003 | 0.6098 | 0.6523 | 700 | 40 | 13.003 | 0
0.54245 | 0.6743 | 0.64062 | 700 | 40 | 14.245 | 0
0.55895 | 0.6131 | 0.59894 | 700 | 40 | 15.895 | 0
0.56789 | 0.5936 | 0.62499 | 700 | 40 | 16.789 | 0
0.57625 | 0.5699 | 0.66973 | 700 | 40 | 17.625 | 0
0.57552 | 0.5007 | 0.67746 | 700 | 40 | 17.552 | 0
0.57238 | 0.32 | 0.70448 | 700 | 40 | 17.238 | 0
0.56404 | 0.1339 | 0.71091 | 700 | 40 | 9.373 | 7.031
0.57053 | 0.0029 | 0.72217 | 700 | 40 | 0.203 | 16.85
0.57311 | 0 | 0.74788 | 700 | 40 | 0 | 17.311
0.54421 | 0 | 0.7575 | 700 | 40 | 0 | 14.421
0.50288 | 0 | 0.75099 | 700 | 40 | 0 | 10.288
0.46493 | 0 | 0.75426 | 700 | 40 | 0 | 6.493
0.44143 | 0 | 0.72767 | 700 | 40 | 0 | 4.143
0.42593 | 0 | 0.69494 | 700 | 40 | 0 | 2.593
0.41811 | 0 | 0.67364 | 700 | 40 | 0 | 1.811
0.41545 | 0 | 0.65356 | 700 | 40 | 0 | 1.545
0.42915 | 0 | 0.65461 | 700 | 40 | 0 | 2.915
0.46421 | 0 | 0.6055 | 700 | 40 | 0 | 6.421
0.50858 | 0.0151 | 0.57928 | 700 | 40 | 1.057 | 9.801
0.50918 | 0.3314 | 0.57415 | 700 | 40 | 10.918 | 0
0.52201 | 0.6692 | 0.54769 | 700 | 40 | 12.201 | 0
0.53447 | 0.7204 | 0.56079 | 700 | 40 | 13.447 | 0
0.54535 | 0.7692 | 0.53529 | 700 | 40 | 14.535 | 0
0.55158 | 0.8051 | 0.4871 | 700 | 40 | 15.158 | 0
0.56106 | 0.8248 | 0.46626 | 700 | 40 | 16.106 | 0
0.57272 | 0.7836 | 0.44211 | 700 | 40 | 17.272 | 0
0.58161 | 0.7561 | 0.45316 | 700 | 40 | 18.161 | 0
0.59406 | 0.7472 | 0.47563 | 700 | 40 | 19.406 | 0
0.60522 | 0.6434 | 0.5287 | 700 | 40 | 20.522 | 0
0.60764 | 0.3534 | 0.57209 | 700 | 40 | 20.764 | 0
0.60101 | 0.0871 | 0.59398 | 700 | 40 | 6.097 | 14.004
0.59935 | 0.0014 | 0.60587 | 700 | 40 | 0.098 | 19.837
0.59756 | 0 | 0.62579 | 700 | 40 | 0 | 19.756
0.57012 | 0 | 0.62873 | 700 | 40 | 0 | 17.012
0.52686 | 0 | 0.61549 | 700 | 40 | 0 | 12.686
0.48157 | 0 | 0.52075 | 700 | 40 | 0 | 8.157
0.44227 | 0 | 0.39064 | 700 | 40 | 0 | 4.227
0.42134 | 0 | 0.40282 | 700 | 40 | 0 | 2.134
0.41216 | 0 | 0.46559 | 700 | 40 | 0 | 1.216
0.40673 | 0 | 0.53004 | 700 | 40 | 0 | 0.673
0.40803 | 0 | 0.49265 | 700 | 40 | 0 | 0.803
0.43788 | 0 | 0.58348 | 700 | 40 | 0 | 3.788
0.48108 | 0.0272 | 0.5831 | 700 | 40 | 1.904 | 6.204
0.48147 | 0.3398 | 0.54164 | 700 | 40 | 8.147 | 0
0.49078 | 0.5545 | 0.53668 | 700 | 40 | 9.078 | 0
0.50017 | 0.4507 | 0.55016 | 700 | 40 | 10.017 | 0
0.51014 | 0.6092 | 0.63163 | 700 | 40 | 11.014 | 0
0.51568 | 0.7401 | 0.68486 | 700 | 40 | 11.568 | 0
0.52057 | 0.8055 | 0.71717 | 700 | 40 | 12.057 | 0
0.52528 | 0.6958 | 0.707 | 700 | 40 | 12.528 | 0
0.5296 | 0.7479 | 0.69574 | 700 | 40 | 12.96 | 0
0.53444 | 0.7145 | 0.67986 | 700 | 40 | 13.444 | 0
0.53824 | 0.7402 | 0.68045 | 700 | 40 | 13.824 | 0
0.532 | 0.6489 | 0.65864 | 700 | 40 | 13.2 | 0
0.51896 | 0.2186 | 0.55861 | 700 | 40 | 11.896 | 0
0.5098 | 0.0024 | 0.42568 | 700 | 40 | 0.168 | 10.812
0.51496 | 0 | 0.38648 | 700 | 40 | 0 | 11.496
0.48909 | 0 | 0.45475 | 700 | 40 | 0 | 8.909
0.45533 | 0 | 0.4695 | 700 | 40 | 0 | 5.533
0.41953 | 0 | 0.42976 | 700 | 40 | 0 | 1.953
0.39785 | 0 | 0.43962 | 700 | 39.785 | 0 | 0
0.38273 | 0 | 0.4032 | 700 | 38.273 | 0 | 0
0.37621 | 0 | 0.34009 | 700 | 37.621 | 0 | 0
0.37577 | 0 | 0.33136 | 700 | 37.577 | 0 | 0
0.38559 | 0 | 0.32469 | 700 | 38.559 | 0 | 0
0.40666 | 0 | 0.34215 | 700 | 40 | 0 | 0.666
0.42818 | 0.0492 | 0.39074 | 700 | 40 | 2.818 | 0
0.44333 | 0.4843 | 0.34286 | 700 | 40 | 4.333 | 0
0.4596 | 0.8452 | 0.25436 | 700 | 40 | 5.96 | 0
0.46911 | 0.8839 | 0.31034 | 700 | 40 | 6.911 | 0
0.47465 | 0.8937 | 0.30719 | 700 | 40 | 7.465 | 0
0.47732 | 0.8976 | 0.27522 | 700 | 40 | 7.732 | 0
0.4774 | 0.8992 | 0.24719 | 700 | 40 | 7.74 | 0
0.48002 | 0.9009 | 0.208 | 700 | 40 | 8.002 | 0
0.48383 | 0.8973 | 0.18114 | 700 | 40 | 8.383 | 0
0.49055 | 0.8912 | 0.15227 | 700 | 40 | 9.055 | 0
0.49667 | 0.87 | 0.12106 | 700 | 40 | 9.667 | 0
0.49829 | 0.7246 | 0.08749 | 700 | 40 | 9.829 | 0
0.48812 | 0.2348 | 0.04066 | 700 | 40 | 8.812 | 0
0.48247 | 0.0026 | 0.02639 | 692.9906 | 40 | 0.182 | 1.0556
0.48332 | 0 | 0.05056 | 686.681 | 40 | 0 | 2.0224
0.4636 | 0 | 0.10284 | 684.4346 | 40 | 0 | 4.1136
0.43902 | 0 | 0.161 | 686.9726 | 40 | 0 | 6.44
0.41041 | 0 | 0.21723 | 694.6208 | 40 | 0 | 8.6892
0.3902 | 0 | 0.27669 | 700 | 40 | 4.3992 | 0
0.38007 | 0 | 0.33917 | 700 | 38.007 | 0 | 0
0.37288 | 0 | 0.38666 | 700 | 37.288 | 0 | 0
0.37102 | 0 | 0.40668 | 700 | 37.102 | 0 | 0
0.37693 | 0 | 0.44961 | 700 | 37.693 | 0 | 0
0.3886 | 0.0001 | 0.46354 | 700 | 38.86 | 0 | 0
0.40347 | 0.0544 | 0.49161 | 700 | 40 | 0.347 | 0
0.42331 | 0.4917 | 0.50881 | 700 | 40 | 2.331 | 0
0.44072 | 0.8046 | 0.40467 | 700 | 40 | 4.072 | 0
0.45359 | 0.8387 | 0.46119 | 700 | 40 | 5.359 | 0
0.45786 | 0.8592 | 0.45921 | 700 | 40 | 5.786 | 0
0.46505 | 0.8721 | 0.44382 | 700 | 40 | 6.505 | 0
0.47316 | 0.8723 | 0.48267 | 700 | 40 | 7.316 | 0
0.4858 | 0.8527 | 0.5506 | 700 | 40 | 8.58 | 0
0.49959 | 0.845 | 0.59987 | 700 | 40 | 9.959 | 0
0.51706 | 0.8237 | 0.62169 | 700 | 40 | 11.706 | 0
0.53007 | 0.7829 | 0.63784 | 700 | 40 | 13.007 | 0
0.53741 | 0.633 | 0.67988 | 700 | 40 | 13.741 | 0
0.53088 | 0.1838 | 0.69319 | 700 | 40 | 12.866 | 0.222
0.51325 | 0.0017 | 0.69516 | 700 | 40 | 0.119 | 11.206
0.51578 | 0 | 0.75923 | 700 | 40 | 0 | 11.578
0.4973 | 0 | 0.77782 | 700 | 40 | 0 | 9.73
0.46781 | 0 | 0.77077 | 700 | 40 | 0 | 6.781
0.43533 | 0 | 0.69616 | 700 | 40 | 0 | 3.533
0.41014 | 0 | 0.67086 | 700 | 40 | 0 | 1.014
0.38995 | 0 | 0.61824 | 700 | 38.995 | 0 | 0
0.37822 | 0 | 0.6028 | 700 | 37.822 | 0 | 0
0.37373 | 0 | 0.58921 | 700 | 37.373 | 0 | 0
0.37189 | 0 | 0.59021 | 700 | 37.189 | 0 | 0
0.37715 | 0.0001 | 0.60117 | 700 | 37.715 | 0 | 0
0.38632 | 0.0384 | 0.62911 | 700 | 38.632 | 0 | 0
0.40476 | 0.428 | 0.66436 | 700 | 40 | 0.476 | 0
0.43 | 0.7762 | 0.60029 | 700 | 40 | 3 | 0
0.45242 | 0.8299 | 0.60318 | 700 | 40 | 5.242 | 0
0.46738 | 0.8629 | 0.60133 | 700 | 40 | 6.738 | 0
0.48638 | 0.8821 | 0.60817 | 700 | 40 | 8.638 | 0
0.50289 | 0.886 | 0.56877 | 700 | 40 | 10.289 | 0
0.51772 | 0.8745 | 0.5394 | 700 | 40 | 11.772 | 0
0.5329 | 0.8609 | 0.54121 | 700 | 40 | 13.29 | 0
0.54573 | 0.8317 | 0.54519 | 700 | 40 | 14.573 | 0
0.55512 | 0.8168 | 0.58174 | 700 | 40 | 15.512 | 0
0.55708 | 0.6357 | 0.607 | 700 | 40 | 15.708 | 0
0.54864 | 0.1519 | 0.59932 | 700 | 40 | 10.633 | 4.231
0.54087 | 0.0015 | 0.58971 | 700 | 40 | 0.105 | 13.982
0.54244 | 0 | 0.64246 | 700 | 40 | 0 | 14.244
0.52175 | 0 | 0.69658 | 700 | 40 | 0 | 12.175
0.48442 | 0 | 0.70548 | 700 | 40 | 0 | 8.442
0.44664 | 0 | 0.69197 | 700 | 40 | 0 | 4.664
0.41858 | 0 | 0.65874 | 700 | 40 | 0 | 1.858
0.40524 | 0 | 0.65765 | 700 | 40 | 0 | 0.524
0.39645 | 0 | 0.65135 | 700 | 39.645 | 0 | 0
0.39606 | 0 | 0.63381 | 700 | 39.606 | 0 | 0
0.40493 | 0 | 0.61153 | 700 | 40 | 0 | 0.493
0.4367 | 0.0001 | 0.62219 | 700 | 40 | 0.007 | 3.663
0.46837 | 0.0125 | 0.60159 | 700 | 40 | 0.875 | 5.962
0.47978 | 0.0893 | 0.53311 | 700 | 40 | 6.251 | 1.727
0.49373 | 0.1834 | 0.50269 | 700 | 40 | 9.373 | 0
0.51601 | 0.3033 | 0.49794 | 700 | 40 | 11.601 | 0
0.53749 | 0.3911 | 0.38339 | 700 | 40 | 13.749 | 0
0.55536 | 0.4561 | 0.36753 | 700 | 40 | 15.536 | 0
0.57032 | 0.5456 | 0.34697 | 700 | 40 | 17.032 | 0
0.58713 | 0.5511 | 0.34647 | 700 | 40 | 18.713 | 0
0.59732 | 0.4479 | 0.35578 | 700 | 40 | 19.732 | 0
0.60418 | 0.2916 | 0.35926 | 700 | 40 | 20.412 | 0.006
0.60537 | 0.1775 | 0.34147 | 700 | 40 | 12.425 | 8.112
0.59903 | 0.1638 | 0.36778 | 700 | 40 | 11.466 | 8.437
0.58334 | 0.1001 | 0.31978 | 700 | 40 | 7.007 | 11.327
0.58075 | 0.0079 | 0.32968 | 695.6652 | 40 | 0.553 | 13.1872
0.58082 | 0 | 0.31835 | 690.3172 | 40 | 0 | 12.734
0.54829 | 0 | 0.35452 | 689.669 | 40 | 0 | 14.1808
0.50353 | 0 | 0.36631 | 693.9684 | 40 | 0 | 14.6524
0.46243 | 0 | 0.38188 | 700 | 40 | 0 | 12.2746
0.43585 | 0 | 0.34982 | 700 | 40 | 0 | 3.585
0.41934 | 0 | 0.36568 | 700 | 40 | 0 | 1.934
0.41026 | 0 | 0.37366 | 700 | 40 | 0 | 1.026
0.40845 | 0 | 0.28479 | 700 | 40 | 0 | 0.845
0.41935 | 0 | 0.28143 | 700 | 40 | 0 | 1.935
0.45303 | 0 | 0.2312 | 700 | 40 | 0 | 5.303
0.488 | 0.0083 | 0.20758 | 700 | 40 | 0.581 | 8.219
0.49359 | 0.0635 | 0.21954 | 700 | 40 | 4.445 | 4.914
0.5028 | 0.1837 | 0.23972 | 700 | 40 | 10.28 | 0
0.5191 | 0.3272 | 0.26343 | 700 | 40 | 11.91 | 0
0.53302 | 0.3773 | 0.30186 | 700 | 40 | 13.302 | 0
0.54247 | 0.3854 | 0.28378 | 700 | 40 | 14.247 | 0
0.55068 | 0.5155 | 0.30153 | 700 | 40 | 15.068 | 0
0.56087 | 0.5977 | 0.25713 | 700 | 40 | 16.087 | 0
0.56323 | 0.5144 | 0.24564 | 700 | 40 | 16.323 | 0
0.56641 | 0.4544 | 0.27547 | 700 | 40 | 16.641 | 0
0.56609 | 0.3365 | 0.31021 | 700 | 40 | 16.609 | 0
0.56204 | 0.1289 | 0.35566 | 700 | 40 | 9.023 | 7.181
0.55654 | 0.0676 | 0.39359 | 700 | 40 | 4.732 | 10.922
0.55889 | 0.0005 | 0.35708 | 698.4292 | 40 | 0.035 | 14.2832
0.55781 | 0 | 0.38285 | 697.9622 | 40 | 0 | 15.314
0.52822 | 0 | 0.38134 | 700 | 40 | 0 | 14.8598
0.48368 | 0 | 0.32507 | 700 | 40 | 0 | 8.368
0.44668 | 0 | 0.3343 | 700 | 40 | 0 | 4.668
0.4217 | 0 | 0.30258 | 700 | 40 | 0 | 2.17
0.40839 | 0 | 0.29456 | 700 | 40 | 0 | 0.839
0.40354 | 0 | 0.26041 | 700 | 40 | 0 | 0.354
0.40234 | 0 | 0.21005 | 700 | 40 | 0 | 0.234
0.4124 | 0 | 0.18144 | 700 | 40 | 0 | 1.24
0.43914 | 0 | 0.16234 | 700 | 40 | 0 | 3.914
0.47791 | 0.0023 | 0.16402 | 698.9308 | 40 | 0.161 | 6.5608
0.48215 | 0.0158 | 0.12118 | 696.669 | 40 | 1.106 | 4.8472
0.49739 | 0.0176 | 0.14846 | 694.1004 | 40 | 1.232 | 5.9384
0.51075 | 0.0397 | 0.13985 | 691.3984 | 40 | 2.779 | 5.594
0.51966 | 0.1189 | 0.17229 | 694.647 | 40 | 8.323 | 6.8916
0.5235 | 0.2495 | 0.19365 | 700 | 40 | 17.703 | 0
0.52803 | 0.3539 | 0.18492 | 700 | 40 | 12.803 | 0
0.53278 | 0.4362 | 0.18307 | 700 | 40 | 13.278 | 0
0.53858 | 0.4044 | 0.16927 | 700 | 40 | 13.858 | 0
0.54418 | 0.2551 | 0.12836 | 700 | 40 | 14.418 | 0
0.54549 | 0.2897 | 0.10255 | 700 | 40 | 14.549 | 0
0.54488 | 0.3502 | 0.11996 | 700 | 40 | 14.488 | 0
0.53843 | 0.1598 | 0.10486 | 700 | 40 | 11.186 | 2.657
0.54165 | 0.0037 | 0.08942 | 689.6708 | 40 | 0.259 | 3.5768
0.53966 | 0 | 0.10662 | 679.9696 | 40 | 0 | 4.2648
0.51354 | 0 | 0.11678 | 673.2868 | 40 | 0 | 4.6712
0.47149 | 0 | 0.13461 | 671.5222 | 40 | 0 | 5.3844
0.43762 | 0 | 0.15727 | 674.051 | 40 | 0 | 6.2908
0.41758 | 0 | 0.20607 | 680.5358 | 40 | 0 | 8.2428
0.40355 | 0 | 0.26309 | 690.7044 | 40 | 0 | 10.5236
0.39486 | 0 | 0.27899 | 700 | 40 | 8.7816 | 0
0.39276 | 0 | 0.26439 | 700 | 39.276 | 0 | 0
0.40313 | 0 | 0.26129 | 700 | 40 | 0 | 0.313
0.43638 | 0 | 0.26225 | 700 | 40 | 0 | 3.638
0.47334 | 0.0663 | 0.27602 | 700 | 40 | 4.641 | 2.693
0.47676 | 0.4888 | 0.24211 | 700 | 40 | 7.676 | 0
0.48636 | 0.8124 | 0.15601 | 700 | 40 | 8.636 | 0
0.50418 | 0.873 | 0.12152 | 700 | 40 | 10.418 | 0
0.52041 | 0.888 | 0.13364 | 700 | 40 | 12.041 | 0
0.53599 | 0.8935 | 0.10402 | 700 | 40 | 13.599 | 0
0.55447 | 0.8932 | 0.15622 | 700 | 40 | 15.447 | 0
0.57721 | 0.8857 | 0.15886 | 700 | 40 | 17.721 | 0
0.59846 | 0.8787 | 0.18278 | 700 | 40 | 19.846 | 0
0.62016 | 0.8644 | 0.19612 | 700 | 40 | 22.016 | 0
0.63624 | 0.8388 | 0.21173 | 700 | 40 | 23.624 | 0
0.63829 | 0.702 | 0.22558 | 700 | 40 | 23.829 | 0
0.62394 | 0.2443 | 0.23246 | 700 | 40 | 17.101 | 5.293
0.60196 | 0.0039 | 0.22453 | 689.0582 | 40 | 0.273 | 8.9812
0.59617 | 0 | 0.29511 | 681.2456 | 40 | 0 | 11.8044
0.55995 | 0 | 0.29498 | 677.0498 | 40 | 0 | 11.7992
0.50912 | 0 | 0.32003 | 678.939 | 40 | 0 | 12.8012
0.46592 | 0 | 0.29595 | 684.185 | 40 | 0 | 11.838
0.43404 | 0 | 0.29565 | 692.607 | 40 | 0 | 11.826
0.41259 | 0 | 0.2753 | 700 | 40 | 0 | 8.652
0.40336 | 0 | 0.29473 | 700 | 40 | 0 | 0.336
0.39649 | 0 | 0.31433 | 700 | 39.649 | 0 | 0
0.407 | 0 | 0.27841 | 700 | 40 | 0 | 0.7
0.43654 | 0.0001 | 0.36413 | 700 | 40 | 0.007 | 3.647
0.46774 | 0.0568 | 0.334 | 700 | 40 | 3.976 | 2.798
0.47589 | 0.464 | 0.28051 | 700 | 40 | 7.589 | 0
0.49122 | 0.7888 | 0.28432 | 700 | 40 | 9.122 | 0
0.51158 | 0.82 | 0.28617 | 700 | 40 | 11.158 | 0
0.5301 | 0.8232 | 0.28336 | 700 | 40 | 13.01 | 0
0.55061 | 0.8359 | 0.28432 | 700 | 40 | 15.061 | 0
0.57225 | 0.8606 | 0.29087 | 700 | 40 | 17.225 | 0
0.59417 | 0.8654 | 0.28038 | 700 | 40 | 19.417 | 0
0.61309 | 0.8487 | 0.2855 | 700 | 40 | 21.309 | 0
0.63032 | 0.7911 | 0.30337 | 700 | 40 | 23.032 | 0
0.63796 | 0.7154 | 0.34559 | 700 | 40 | 23.796 | 0
0.63163 | 0.5053 | 0.41365 | 700 | 40 | 23.163 | 0
0.60957 | 0.1908 | 0.46471 | 700 | 40 | 13.356 | 7.601
0.58297 | 0.0038 | 0.47667 | 700 | 40 | 0.266 | 18.031
0.57566 | 0 | 0.57276 | 700 | 40 | 0 | 17.566
0.54633 | 0 | 0.64082 | 700 | 40 | 0 | 14.633
0.51007 | 0 | 0.65282 | 700 | 40 | 0 | 11.007
0.47136 | 0 | 0.64988 | 700 | 40 | 0 | 7.136
0.43685 | 0 | 0.58048 | 700 | 40 | 0 | 3.685
0.41717 | 0 | 0.55228 | 700 | 40 | 0 | 1.717
0.40342 | 0 | 0.44692 | 700 | 40 | 0 | 0.342
0.3958 | 0 | 0.43983 | 700 | 39.58 | 0 | 0
0.39898 | 0 | 0.52853 | 700 | 39.898 | 0 | 0
0.40875 | 0.0001 | 0.59084 | 700 | 40 | 0.007 | 0.868
0.41548 | 0.0539 | 0.56668 | 700 | 40 | 1.548 | 0
0.44119 | 0.3846 | 0.59147 | 700 | 40 | 4.119 | 0
0.47136 | 0.5307 | 0.58921 | 700 | 40 | 7.136 | 0
0.50105 | 0.647 | 0.59873 | 700 | 40 | 10.105 | 0
0.52287 | 0.7971 | 0.55274 | 700 | 40 | 12.287 | 0
0.54319 | 0.8435 | 0.50726 | 700 | 40 | 14.319 | 0
0.56187 | 0.8363 | 0.44428 | 700 | 40 | 16.187 | 0
0.57803 | 0.8397 | 0.39061 | 700 | 40 | 17.803 | 0
0.59881 | 0.846 | 0.31026 | 700 | 40 | 19.881 | 0
0.61649 | 0.8086 | 0.32402 | 700 | 40 | 21.649 | 0
0.6313 | 0.7638 | 0.30501 | 700 | 40 | 23.13 | 0
0.62689 | 0.5859 | 0.34945 | 700 | 40 | 22.689 | 0
0.60677 | 0.2151 | 0.40206 | 700 | 40 | 15.057 | 5.62
0.58428 | 0.0039 | 0.44352 | 699.5858 | 40 | 0.273 | 17.7408
0.57582 | 0 | 0.53693 | 700 | 40 | 0 | 17.9962
0.54848 | 0 | 0.54813 | 700 | 40 | 0 | 14.848
0.51314 | 0 | 0.50164 | 700 | 40 | 0 | 11.314
0.47715 | 0 | 0.47856 | 700 | 40 | 0 | 7.715
0.44777 | 0 | 0.53139 | 700 | 40 | 0 | 4.777
0.42633 | 0 | 0.548 | 700 | 40 | 0 | 2.633
0.41032 | 0 | 0.5026 | 700 | 40 | 0 | 1.032
0.40291 | 0 | 0.52971 | 700 | 40 | 0 | 0.291
0.39809 | 0 | 0.48695 | 700 | 39.809 | 0 | 0
0.39845 | 0.0001 | 0.36451 | 700 | 39.845 | 0 | 0
0.40391 | 0.0451 | 0.35247 | 700 | 40 | 0.391 | 0
0.42134 | 0.359 | 0.34613 | 700 | 40 | 2.134 | 0
0.45244 | 0.6648 | 0.32998 | 700 | 40 | 5.244 | 0
0.48465 | 0.7926 | 0.4097 | 700 | 40 | 8.465 | 0
0.51217 | 0.8304 | 0.46152 | 700 | 40 | 11.217 | 0
0.53847 | 0.8339 | 0.50407 | 700 | 40 | 13.847 | 0
0.56849 | 0.8257 | 0.52304 | 700 | 40 | 16.849 | 0
0.5926 | 0.7279 | 0.57691 | 700 | 40 | 19.26 | 0
0.61597 | 0.5409 | 0.63499 | 700 | 40 | 21.597 | 0
0.63553 | 0.4821 | 0.69721 | 700 | 40 | 23.553 | 0
0.64259 | 0.3918 | 0.70678 | 700 | 40 | 24.259 | 0
0.64464 | 0.2531 | 0.72759 | 700 | 40 | 17.717 | 6.747
0.62764 | 0.1031 | 0.73397 | 700 | 40 | 7.217 | 15.547
0.60681 | 0.0019 | 0.70577 | 700 | 40 | 0.133 | 20.548
0.6012 | 0 | 0.70892 | 700 | 40 | 0 | 20.12
0.56967 | 0 | 0.7205 | 700 | 40 | 0 | 16.967
0.52534 | 0 | 0.71769 | 700 | 40 | 0 | 12.534
0.48281 | 0 | 0.70619 | 700 | 40 | 0 | 8.281
0.45068 | 0 | 0.6623 | 700 | 40 | 0 | 5.068
0.43111 | 0 | 0.62869 | 700 | 40 | 0 | 3.111
0.42234 | 0 | 0.62106 | 700 | 40 | 0 | 2.234
0.42041 | 0 | 0.62227 | 700 | 40 | 0 | 2.041
0.43431 | 0 | 0.60297 | 700 | 40 | 0 | 3.431
0.47131 | 0.0001 | 0.5749 | 700 | 40 | 0.007 | 7.124
0.50887 | 0.0407 | 0.5736 | 700 | 40 | 2.849 | 8.038
0.51645 | 0.3448 | 0.53936 | 700 | 40 | 11.645 | 0
0.53255 | 0.6179 | 0.53185 | 700 | 40 | 13.255 | 0
0.55323 | 0.6768 | 0.51901 | 700 | 40 | 15.323 | 0
0.57595 | 0.7096 | 0.45615 | 700 | 40 | 17.595 | 0
0.59406 | 0.7222 | 0.40911 | 700 | 40 | 19.406 | 0
0.61189 | 0.6925 | 0.35159 | 700 | 40 | 21.189 | 0
0.63366 | 0.6662 | 0.3651 | 700 | 40 | 23.366 | 0
0.64522 | 0.472 | 0.38725 | 700 | 40 | 24.522 | 0
0.65852 | 0.3449 | 0.39888 | 700 | 40 | 24.143 | 1.709
0.66431 | 0.304 | 0.41436 | 700 | 40 | 21.28 | 5.151
0.66074 | 0.2348 | 0.41478 | 700 | 40 | 16.436 | 9.638
0.64289 | 0.0894 | 0.40731 | 698.2614 | 40 | 6.258 | 16.2924
0.63701 | 0.0038 | 0.3823 | 690.1184 | 40 | 0.266 | 15.292
0.63446 | 0 | 0.36313 | 681.1976 | 40 | 0 | 14.5252
0.59915 | 0 | 0.33698 | 674.7618 | 40 | 0 | 13.4792
0.55549 | 0 | 0.29708 | 671.096 | 40 | 0 | 11.8832
0.51432 | 0 | 0.28512 | 671.0688 | 40 | 0 | 11.4048
0.48675 | 0 | 0.28541 | 673.8102 | 40 | 0 | 11.4164
0.46992 | 0 | 0.29372 | 678.567 | 40 | 0 | 11.7488
0.46246 | 0 | 0.31529 | 684.9326 | 40 | 0 | 12.6116
0.45827 | 0 | 0.33115 | 692.3516 | 40 | 0 | 13.246
0.46895 | 0 | 0.35146 | 699.515 | 40 | 0 | 14.0584
0.50379 | 0 | 0.33942 | 700 | 40 | 0 | 10.864
0.53957 | 0.0118 | 0.32935 | 700 | 40 | 0.826 | 13.131
0.54986 | 0.1133 | 0.35448 | 700 | 40 | 7.931 | 7.055
0.56278 | 0.2649 | 0.37689 | 700 | 40 | 16.278 | 0
0.57821 | 0.4341 | 0.38855 | 700 | 40 | 17.821 | 0
0.59815 | 0.5508 | 0.39846 | 700 | 40 | 19.815 | 0
0.61322 | 0.6276 | 0.43307 | 700 | 40 | 21.322 | 0
0.63503 | 0.5897 | 0.47671 | 700 | 40 | 23.503 | 0
0.64945 | 0.4761 | 0.4564 | 700 | 40 | 24.945 | 0
0.65006 | 0.4491 | 0.42602 | 700 | 40 | 25.006 | 0
0.65337 | 0.6008 | 0.42548 | 700 | 40 | 25.337 | 0
0.65034 | 0.6252 | 0.42846 | 700 | 40 | 25.034 | 0
0.6399 | 0.5414 | 0.44025 | 700 | 40 | 23.99 | 0
0.62905 | 0.2195 | 0.46551 | 700 | 40 | 15.365 | 7.54
0.63053 | 0.0052 | 0.43521 | 694.7194 | 40 | 0.364 | 17.4084
0.62688 | 0 | 0.4066 | 688.2954 | 40 | 0 | 16.264
0.59832 | 0 | 0.43744 | 685.961 | 40 | 0 | 17.4976
0.5558 | 0 | 0.43618 | 687.8282 | 40 | 0 | 17.4472
0.51844 | 0 | 0.46635 | 694.6382 | 40 | 0 | 18.654
0.49206 | 0 | 0.45976 | 700 | 40 | 0 | 14.5678
0.47222 | 0 | 0.44797 | 700 | 40 | 0 | 7.222
0.46275 | 0 | 0.43018 | 700 | 40 | 0 | 6.275
0.46014 | 0 | 0.39296 | 700 | 40 | 0 | 6.014
0.47024 | 0 | 0.37366 | 700 | 40 | 0 | 7.024
0.50139 | 0 | 0.34613 | 700 | 40 | 0 | 10.139
0.53715 | 0.0458 | 0.31714 | 700 | 40 | 3.206 | 10.509
0.54404 | 0.3169 | 0.25936 | 700 | 40 | 14.404 | 0
0.55887 | 0.5655 | 0.25004 | 700 | 40 | 15.887 | 0
0.58537 | 0.6969 | 0.28537 | 700 | 40 | 18.537 | 0
0.60764 | 0.7307 | 0.29397 | 700 | 40 | 20.764 | 0
0.62564 | 0.7419 | 0.2782 | 700 | 40 | 22.564 | 0
0.64438 | 0.7261 | 0.27786 | 700 | 40 | 24.438 | 0
0.65756 | 0.6876 | 0.30207 | 700 | 40 | 25.756 | 0
0.66181 | 0.6728 | 0.32389 | 700 | 40 | 26.181 | 0
0.66201 | 0.6854 | 0.3481 | 700 | 40 | 26.201 | 0
0.65709 | 0.5926 | 0.40626 | 700 | 40 | 25.709 | 0
0.65263 | 0.2997 | 0.4478 | 700 | 40 | 20.979 | 4.284
0.64259 | 0.1364 | 0.45498 | 700 | 40 | 9.548 | 14.711
0.63617 | 0.0038 | 0.43798 | 694.1682 | 40 | 0.266 | 17.5192
0.62627 | 0 | 0.51561 | 692.1656 | 40 | 0 | 20.6244
0.59579 | 0 | 0.51918 | 693.3538 | 40 | 0 | 20.7672
0.54793 | 0 | 0.5394 | 700 | 40 | 0 | 21.4392
0.50579 | 0 | 0.54016 | 700 | 40 | 0 | 10.579
0.47736 | 0 | 0.59194 | 700 | 40 | 0 | 7.736
0.45996 | 0 | 0.61774 | 700 | 40 | 0 | 5.996
0.44722 | 0 | 0.58896 | 700 | 40 | 0 | 4.722
0.43991 | 0 | 0.56793 | 700 | 40 | 0 | 3.991
0.44837 | 0 | 0.51221 | 700 | 40 | 0 | 4.837
0.48003 | 0 | 0.49404 | 700 | 40 | 0 | 8.003
0.51492 | 0.0423 | 0.4614 | 700 | 40 | 2.961 | 8.531
0.51436 | 0.3173 | 0.34911 | 700 | 40 | 11.436 | 0
0.52277 | 0.5276 | 0.38809 | 700 | 40 | 12.277 | 0
0.54143 | 0.5794 | 0.4499 | 700 | 40 | 14.143 | 0
0.56003 | 0.5423 | 0.37202 | 700 | 40 | 16.003 | 0
0.58093 | 0.542 | 0.33996 | 700 | 40 | 18.093 | 0
0.59935 | 0.5918 | 0.28776 | 700 | 40 | 19.935 | 0
0.61711 | 0.611 | 0.27837 | 700 | 40 | 21.711 | 0
0.62532 | 0.5921 | 0.2993 | 700 | 40 | 22.532 | 0
0.62866 | 0.4188 | 0.35037 | 700 | 40 | 22.866 | 0
0.62045 | 0.3227 | 0.28458 | 700 | 40 | 22.045 | 0
0.60414 | 0.1946 | 0.26569 | 700 | 40 | 13.622 | 6.792
0.5871 | 0.0829 | 0.24291 | 696.8094 | 40 | 5.803 | 9.7164
0.57735 | 0.0035 | 0.22189 | 688.195 | 40 | 0.245 | 8.8756
0.57202 | 0 | 0.23452 | 680.3738 | 40 | 0 | 9.3808
0.54302 | 0 | 0.24303 | 675.793 | 40 | 0 | 9.7212
0.50143 | 0 | 0.2255 | 674.67 | 40 | 0 | 9.02
0.46301 | 0 | 0.25491 | 678.5654 | 40 | 0 | 10.1964
0.43643 | 0 | 0.29263 | 686.6276 | 40 | 0 | 11.7052
0.42349 | 0 | 0.26762 | 694.9834 | 40 | 0 | 10.7048
0.41494 | 0 | 0.28239 | 700 | 40 | 0 | 6.5106
0.41519 | 0 | 0.28504 | 700 | 40 | 0 | 1.519
0.42713 | 0 | 0.27702 | 700 | 40 | 0 | 2.713
0.45843 | 0 | 0.27602 | 700 | 40 | 0 | 5.843
0.49634 | 0.0109 | 0.24396 | 700 | 40 | 0.763 | 8.871
0.5032 | 0.0645 | 0.16478 | 700 | 40 | 4.515 | 5.805
0.5144 | 0.1429 | 0.10624 | 700 | 40 | 10.003 | 1.437
0.52817 | 0.3021 | 0.1203 | 700 | 40 | 12.817 | 0
0.53903 | 0.4446 | 0.18102 | 700 | 40 | 13.903 | 0
0.54964 | 0.5084 | 0.21144 | 700 | 40 | 14.964 | 0
0.56262 | 0.5561 | 0.197 | 700 | 40 | 16.262 | 0
0.57425 | 0.485 | 0.20586 | 700 | 40 | 17.425 | 0
0.57814 | 0.5439 | 0.21467 | 700 | 40 | 17.814 | 0
0.58564 | 0.5208 | 0.20896 | 700 | 40 | 18.564 | 0
0.58584 | 0.3943 | 0.24631 | 700 | 40 | 18.584 | 0
0.57465 | 0.1723 | 0.20103 | 700 | 40 | 12.061 | 5.404
0.56352 | 0.1634 | 0.24522 | 700 | 40 | 11.438 | 4.914
0.55575 | 0.008 | 0.26313 | 695.5102 | 40 | 0.56 | 10.5252
0.54963 | 0 | 0.26498 | 691.1464 | 40 | 0 | 10.5992
0.53132 | 0 | 0.29364 | 689.76 | 40 | 0 | 11.7456
0.49982 | 0 | 0.24324 | 689.5076 | 40 | 0 | 9.7296
0.46652 | 0 | 0.19541 | 690.672 | 40 | 0 | 7.8164
0.43999 | 0 | 0.19789 | 694.5886 | 40 | 0 | 7.9156
0.42165 | 0 | 0.1626 | 698.9276 | 40 | 0 | 6.504
0.403 | 0 | 0.13771 | 700 | 40 | 0 | 1.3724
0.39378 | 0 | 0.12521 | 700 | 39.378 | 0 | 0
0.3957 | 0 | 0.09001 | 700 | 39.57 | 0 | 0
0.40327 | 0.0001 | 0.07834 | 700 | 40 | 0.007 | 0.32
0.41187 | 0.0263 | 0.0791 | 700 | 40 | 1.187 | 0
0.43619 | 0.2031 | 0.07599 | 700 | 40 | 3.619 | 0
0.46696 | 0.3885 | 0.05782 | 700 | 40 | 6.696 | 0
0.49181 | 0.536 | 0.05543 | 700 | 40 | 9.181 | 0
0.51589 | 0.6197 | 0.03831 | 700 | 40 | 11.589 | 0
0.5389 | 0.6798 | 0.03315 | 700 | 40 | 13.89 | 0
0.55956 | 0.6925 | 0.03462 | 700 | 40 | 15.956 | 0
0.57984 | 0.6934 | 0.04376 | 700 | 40 | 17.984 | 0
0.59755 | 0.7528 | 0.0595 | 700 | 40 | 19.755 | 0
0.61271 | 0.5458 | 0.09009 | 700 | 40 | 21.271 | 0
0.61888 | 0.4029 | 0.12315 | 700 | 40 | 21.888 | 0
0.61527 | 0.3833 | 0.15987 | 700 | 40 | 21.527 | 0
0.59802 | 0.2025 | 0.2007 | 700 | 40 | 14.175 | 5.627
0.5725 | 0.0087 | 0.20829 | 691.6906 | 40 | 0.609 | 8.3316
0.56712 | 0 | 0.24199 | 684.6582 | 40 | 0 | 9.6796
0.53986 | 0 | 0.30149 | 682.7318 | 40 | 0 | 12.0596
0.5073 | 0 | 0.29586 | 683.8362 | 40 | 0 | 11.8344
0.4697 | 0 | 0.33589 | 690.3018 | 40 | 0 | 13.4356
0.44087 | 0 | 0.36182 | 700 | 40 | 0 | 13.7852
0.41892 | 0 | 0.32729 | 700 | 40 | 0 | 1.892
0.4061 | 0 | 0.27035 | 700 | 40 | 0 | 0.61
0.39629 | 0 | 0.27618 | 700 | 39.629 | 0 | 0
0.3929 | 0 | 0.26951 | 700 | 39.29 | 0 | 0
0.39609 | 0.0003 | 0.29079 | 700 | 39.609 | 0 | 0
0.39857 | 0.0504 | 0.30845 | 700 | 39.857 | 0 | 0
0.42004 | 0.29 | 0.25537 | 700 | 40 | 2.004 | 0
0.45442 | 0.4715 | 0.23477 | 700 | 40 | 5.442 | 0
0.4898 | 0.6619 | 0.25986 | 700 | 40 | 8.98 | 0
0.52461 | 0.7857 | 0.32591 | 700 | 40 | 12.461 | 0
0.55877 | 0.7357 | 0.33887 | 700 | 40 | 15.877 | 0
0.58434 | 0.5485 | 0.32775 | 700 | 40 | 18.434 | 0
0.6138 | 0.5085 | 0.34521 | 700 | 40 | 21.38 | 0
0.63825 | 0.2768 | 0.40064 | 700 | 40 | 19.376 | 4.449
0.65474 | 0.2483 | 0.41172 | 700 | 40 | 17.381 | 8.093
0.6662 | 0.1795 | 0.46509 | 700 | 40 | 12.565 | 14.055
0.66557 | 0.0988 | 0.5081 | 700 | 40 | 6.916 | 19.641
0.64687 | 0.0253 | 0.50252 | 697.1848 | 40 | 1.771 | 20.1008
0.62457 | 0.0016 | 0.48653 | 694.301 | 40 | 0.112 | 19.4612
0.61787 | 0 | 0.54305 | 694.236 | 40 | 0 | 21.722
0.58416 | 0 | 0.53038 | 697.0352 | 40 | 0 | 21.2152
0.53474 | 0 | 0.46165 | 700 | 40 | 0 | 16.4388
0.48722 | 0 | 0.47797 | 700 | 40 | 0 | 8.722
0.45364 | 0 | 0.45775 | 700 | 40 | 0 | 5.364
0.43424 | 0 | 0.44478 | 700 | 40 | 0 | 3.424
0.42554 | 0 | 0.38839 | 700 | 40 | 0 | 2.554
0.42095 | 0 | 0.41927 | 700 | 40 | 0 | 2.095
0.43293 | 0 | 0.43383 | 700 | 40 | 0 | 3.293
0.46802 | 0.0003 | 0.43035 | 700 | 40 | 0.021 | 6.781
0.50248 | 0.0296 | 0.38943 | 700 | 40 | 2.072 | 8.176
0.51101 | 0.2746 | 0.36006 | 700 | 40 | 11.101 | 0
0.53101 | 0.6618 | 0.29947 | 700 | 40 | 13.101 | 0
0.55504 | 0.7587 | 0.29389 | 700 | 40 | 15.504 | 0
0.57717 | 0.7693 | 0.25562 | 700 | 40 | 17.717 | 0
0.59616 | 0.7674 | 0.29758 | 700 | 40 | 19.616 | 0
0.61451 | 0.7732 | 0.35834 | 700 | 40 | 21.451 | 0
0.63655 | 0.7706 | 0.38343 | 700 | 40 | 23.655 | 0
0.64555 | 0.7544 | 0.42833 | 700 | 40 | 24.555 | 0
0.65736 | 0.4573 | 0.47268 | 700 | 40 | 25.736 | 0
0.65796 | 0.2701 | 0.50348 | 700 | 40 | 18.907 | 6.889
0.6508 | 0.1825 | 0.53739 | 700 | 40 | 12.775 | 12.305
0.63597 | 0.0705 | 0.54574 | 700 | 40 | 4.935 | 18.662
0.62968 | 0.001 | 0.53961 | 698.6864 | 40 | 0.07 | 21.5844
0.6278 | 0 | 0.52513 | 696.9116 | 40 | 0 | 21.0052
0.59664 | 0 | 0.57393 | 700 | 40 | 0 | 22.7524
0.54538 | 0 | 0.60167 | 700 | 40 | 0 | 14.538
0.50162 | 0 | 0.61073 | 700 | 40 | 0 | 10.162
0.47025 | 0 | 0.56785 | 700 | 40 | 0 | 7.025
0.44971 | 0 | 0.53092 | 700 | 40 | 0 | 4.971
0.43871 | 0 | 0.48024 | 700 | 40 | 0 | 3.871
0.43725 | 0 | 0.44801 | 700 | 40 | 0 | 3.725
0.44959 | 0 | 0.42829 | 700 | 40 | 0 | 4.959
0.48289 | 0.0001 | 0.40744 | 700 | 40 | 0.007 | 8.282
0.5178 | 0.0196 | 0.32729 | 700 | 40 | 1.372 | 10.408
0.52649 | 0.1561 | 0.29158 | 700 | 40 | 10.927 | 1.722
0.54506 | 0.3972 | 0.28017 | 700 | 40 | 14.506 | 0
0.57024 | 0.6428 | 0.32322 | 700 | 40 | 17.024 | 0
0.59159 | 0.6715 | 0.38142 | 700 | 40 | 19.159 | 0
0.61105 | 0.6712 | 0.43223 | 700 | 40 | 21.105 | 0
0.62615 | 0.6518 | 0.49207 | 700 | 40 | 22.615 | 0
0.64375 | 0.4507 | 0.50785 | 700 | 40 | 24.375 | 0
0.65608 | 0.4439 | 0.51007 | 700 | 40 | 25.608 | 0
0.66655 | 0.2963 | 0.51997 | 700 | 40 | 20.741 | 5.914
0.67331 | 0.1569 | 0.54905 | 700 | 40 | 10.983 | 16.348
0.66651 | 0.1004 | 0.56177 | 700 | 40 | 7.028 | 19.623
0.64379 | 0.0522 | 0.47205 | 698.157 | 40 | 3.654 | 18.882
0.62249 | 0.0067 | 0.43878 | 693.9282 | 40 | 0.469 | 17.5512
0.61711 | 0 | 0.50063 | 692.2424 | 40 | 0 | 20.0252
0.58341 | 0 | 0.5436 | 695.6454 | 40 | 0 | 21.744
0.53511 | 0 | 0.53181 | 700 | 40 | 0 | 17.8656
0.49355 | 0 | 0.57824 | 700 | 40 | 0 | 9.355
0.46782 | 0 | 0.5427 | 700 | 40 | 0 | 6.782
0.45211 | 0 | 0.51154 | 700 | 40 | 0 | 5.211
0.44125 | 0 | 0.46912 | 700 | 40 | 0 | 4.125
0.43548 | 0 | 0.47219 | 700 | 40 | 0 | 3.548
0.44166 | 0 | 0.38703 | 700 | 40 | 0 | 4.166
0.47516 | 0 | 0.39626 | 700 | 40 | 0 | 7.516
0.51291 | 0.0479 | 0.34114 | 700 | 40 | 3.353 | 7.938
0.52104 | 0.3976 | 0.309 | 700 | 40 | 12.104 | 0
0.5351 | 0.6032 | 0.30745 | 700 | 40 | 13.51 | 0
0.55221 | 0.6227 | 0.31026 | 700 | 40 | 15.221 | 0
0.56455 | 0.6576 | 0.2905 | 700 | 40 | 16.455 | 0
0.57796 | 0.646 | 0.31282 | 700 | 40 | 17.796 | 0
0.58357 | 0.5569 | 0.27016 | 700 | 40 | 18.357 | 0
0.58604 | 0.7023 | 0.22812 | 700 | 40 | 18.604 | 0
0.59049 | 0.7561 | 0.19427 | 700 | 40 | 19.049 | 0
0.59677 | 0.7566 | 0.20627 | 700 | 40 | 19.677 | 0
0.60623 | 0.7413 | 0.23106 | 700 | 40 | 20.623 | 0
0.61196 | 0.6589 | 0.25321 | 700 | 40 | 21.196 | 0
0.60485 | 0.2811 | 0.2686 | 700 | 40 | 19.677 | 0.808
0.5994 | 0.0068 | 0.31475 | 693.126 | 40 | 0.476 | 12.59
0.60162 | 0 | 0.39382 | 688.7168 | 40 | 0 | 15.7528
0.57431 | 0 | 0.44588 | 689.121 | 40 | 0 | 17.8352
0.53406 | 0 | 0.46715 | 694.401 | 40 | 0 | 18.686
0.49286 | 0 | 0.45394 | 700 | 40 | 0 | 14.885
0.46951 | 0 | 0.49656 | 700 | 40 | 0 | 6.951
0.45617 | 0 | 0.49891 | 700 | 40 | 0 | 5.617
0.44604 | 0 | 0.45335 | 700 | 40 | 0 | 4.604
0.44374 | 0 | 0.42843 | 700 | 40 | 0 | 4.374
0.45461 | 0 | 0.37797 | 700 | 40 | 0 | 5.461
0.48839 | 0.0001 | 0.35964 | 700 | 40 | 0.007 | 8.832
0.52517 | 0.0742 | 0.3262 | 700 | 40 | 5.194 | 7.323
0.53214 | 0.4211 | 0.3416 | 700 | 40 | 13.214 | 0
0.54903 | 0.563 | 0.36828 | 700 | 40 | 14.903 | 0
0.5669 | 0.6796 | 0.36538 | 700 | 40 | 16.69 | 0
0.5915 | 0.6522 | 0.37868 | 700 | 40 | 19.15 | 0
0.613 | 0.3464 | 0.39588 | 700 | 40 | 21.3 | 0
0.63612 | 0.3292 | 0.41484 | 700 | 40 | 23.044 | 0.568
0.65589 | 0.6933 | 0.43141 | 700 | 40 | 25.589 | 0
0.66066 | 0.7218 | 0.45675 | 700 | 40 | 26.066 | 0
0.65984 | 0.6662 | 0.47143 | 700 | 40 | 25.984 | 0
0.65206 | 0.5574 | 0.47995 | 700 | 40 | 25.206 | 0
0.63344 | 0.4986 | 0.50289 | 700 | 40 | 23.344 | 0
0.61192 | 0.2133 | 0.51288 | 700 | 40 | 14.931 | 6.261
0.59833 | 0.0064 | 0.44614 | 698.4606 | 40 | 0.448 | 17.8456
0.58408 | 0 | 0.4453 | 697.8646 | 40 | 0 | 17.812
0.54311 | 0 | 0.41425 | 700 | 40 | 0 | 16.4464
0.49692 | 0 | 0.4505 | 700 | 40 | 0 | 9.692
0.45022 | 0 | 0.43723 | 700 | 40 | 0 | 5.022
0.42471 | 0 | 0.44797 | 700 | 40 | 0 | 2.471
0.41122 | 0 | 0.42649 | 700 | 40 | 0 | 1.122
0.40144 | 0 | 0.44696 | 700 | 40 | 0 | 0.144
0.399 | 0 | 0.45116 | 700 | 39.9 | 0 | 0
0.40854 | 0 | 0.48447 | 700 | 40 | 0 | 0.854
0.43607 | 0.0001 | 0.47059 | 700 | 40 | 0.007 | 3.6
0.47465 | 0.0095 | 0.46538 | 700 | 40 | 0.665 | 6.8
0.48066 | 0.0382 | 0.4118 | 700 | 40 | 2.674 | 5.392
0.49095 | 0.0978 | 0.41524 | 700 | 40 | 6.846 | 2.249
0.50446 | 0.1147 | 0.38045 | 700 | 40 | 8.029 | 2.417
0.5067 | 0.1369 | 0.3304 | 700 | 40 | 9.583 | 1.087
0.50824 | 0.2097 | 0.21433 | 700 | 40 | 10.824 | 0
0.50854 | 0.2107 | 0.13981 | 700 | 40 | 10.854 | 0
0.51056 | 0.2103 | 0.13138 | 700 | 40 | 11.056 | 0
0.51055 | 0.2173 | 0.18236 | 700 | 40 | 11.055 | 0
0.51191 | 0.1542 | 0.18886 | 700 | 40 | 10.794 | 0.397
0.51337 | 0.0714 | 0.21341 | 700 | 40 | 4.998 | 6.339
0.51472 | 0.0259 | 0.18614 | 697.7866 | 40 | 1.813 | 7.4456
0.50662 | 0.0093 | 0.18341 | 695.112 | 40 | 0.651 | 7.3364
0.50481 | 0.0003 | 0.14384 | 690.4056 | 40 | 0.021 | 5.7536
0.50985 | 0 | 0.12441 | 684.397 | 40 | 0 | 4.9764
0.49103 | 0 | 0.10314 | 679.4196 | 40 | 0 | 4.1256
0.46666 | 0 | 0.07049 | 675.5732 | 40 | 0 | 2.8196
0.43866 | 0 | 0.05165 | 673.7732 | 40 | 0 | 2.066
0.41647 | 0 | 0.04779 | 674.0378 | 40 | 0 | 1.9116
0.40287 | 0 | 0.03344 | 675.0884 | 40 | 0 | 1.3376
0.39531 | 0 | 0.06999 | 678.357 | 40 | 2.7996 | 0
0.39141 | 0 | 0.08014 | 682.4216 | 40 | 3.2056 | 0
0.3918 | 0 | 0.08518 | 686.6488 | 40 | 3.4072 | 0
0.40363 | 0 | 0.11497 | 690.8846 | 40 | 0 | 4.5988
0.41678 | 0.0341 | 0.09177 | 695.2644 | 40 | 6.0578 | 0
0.43514 | 0.1364 | 0.10402 | 700 | 40 | 8.2496 | 0
0.45815 | 0.2278 | 0.08833 | 700 | 40 | 5.815 | 0
0.47701 | 0.279 | 0.10742 | 700 | 40 | 7.701 | 0
0.48726 | 0.3655 | 0.08933 | 700 | 40 | 8.726 | 0
0.49205 | 0.5074 | 0.06466 | 700 | 40 | 9.205 | 0
0.48909 | 0.7052 | 0.05312 | 700 | 40 | 8.909 | 0
0.48297 | 0.7417 | 0.04842 | 700 | 40 | 8.297 | 0
0.47788 | 0.7137 | 0.04783 | 700 | 40 | 7.788 | 0
0.47676 | 0.6847 | 0.03881 | 700 | 40 | 7.676 | 0
0.47701 | 0.678 | 0.03877 | 700 | 40 | 7.701 | 0
0.47846 | 0.5842 | 0.0261 | 700 | 40 | 7.846 | 0
0.47445 | 0.2711 | 0.02669 | 700 | 40 | 7.445 | 0
0.48008 | 0.0118 | 0.02064 | 693.6436 | 40 | 0.826 | 0.8256
0.48834 | 0 | 0.03709 | 686.2932 | 40 | 0 | 1.4836
0.47593 | 0 | 0.06412 | 681.265 | 40 | 0 | 2.5648
0.45451 | 0 | 0.07884 | 678.9676 | 40 | 0 | 3.1536
0.43156 | 0 | 0.08755 | 679.3136 | 40 | 0 | 3.502
0.40926 | 0 | 0.09103 | 682.0288 | 40 | 0 | 3.6412
0.39445 | 0 | 0.09502 | 686.3846 | 40 | 3.8008 | 0
0.38616 | 0 | 0.08768 | 691.2758 | 40 | 3.5072 | 0
0.38019 | 0 | 0.10785 | 697.5708 | 40 | 4.314 | 0
0.37958 | 0 | 0.13076 | 700 | 40 | 0.3872 | 0
0.38602 | 0.0004 | 0.14875 | 700 | 38.602 | 0 | 0
0.38877 | 0.0803 | 0.13575 | 700 | 38.877 | 0 | 0
0.40672 | 0.429 | 0.1105 | 700 | 40 | 0.672 | 0
0.43308 | 0.4935 | 0.04438 | 700 | 40 | 3.308 | 0
0.45189 | 0.5146 | 0.03423 | 700 | 40 | 5.189 | 0
0.46483 | 0.6594 | 0.01963 | 700 | 40 | 6.483 | 0
0.47661 | 0.7349 | 0.01296 | 700 | 40 | 7.661 | 0
0.48835 | 0.7242 | 0.01275 | 700 | 40 | 8.835 | 0
0.49818 | 0.6237 | 0.01812 | 700 | 40 | 9.818 | 0
0.51672 | 0.4653 | 0.01867 | 700 | 40 | 11.672 | 0
0.53287 | 0.3966 | 0.01594 | 700 | 40 | 13.287 | 0
0.54695 | 0.3601 | 0.01808 | 700 | 40 | 14.695 | 0
0.5538 | 0.2988 | 0.0245 | 700 | 40 | 15.38 | 0
0.55129 | 0.0998 | 0.03184 | 693.1306 | 40 | 6.986 | 1.2736
0.54256 | 0.0076 | 0.04648 | 681.2658 | 40 | 0.532 | 1.8592
0.54025 | 0 | 0.08679 | 670.7124 | 40 | 0 | 3.4716
0.52014 | 0 | 0.15576 | 664.9288 | 40 | 0 | 6.2304
0.47912 | 0 | 0.21575 | 665.6468 | 40 | 0 | 8.63
0.44161 | 0 | 0.26873 | 672.235 | 40 | 0 | 10.7492
0.41256 | 0 | 0.3098 | 683.371 | 40 | 0 | 12.392
0.39719 | 0 | 0.30116 | 695.6984 | 40 | 12.0464 | 0
0.38748 | 0 | 0.29906 | 700 | 40 | 3.0496 | 0
0.38614 | 0 | 0.27544 | 700 | 38.614 | 0 | 0
0.39754 | 0 | 0.2436 | 700 | 39.754 | 0 | 0
0.42935 | 0.0008 | 0.29797 | 700 | 40 | 0.056 | 2.879
0.4655 | 0.0567 | 0.30552 | 700 | 40 | 3.969 | 2.581
0.47461 | 0.2456 | 0.25942 | 700 | 40 | 7.461 | 0
0.4899 | 0.4674 | 0.15324 | 700 | 40 | 8.99 | 0
0.51474 | 0.5805 | 0.1342 | 700 | 40 | 11.474 | 0
0.5345 | 0.5321 | 0.10513 | 700 | 40 | 13.45 | 0
0.55323 | 0.5502 | 0.08365 | 700 | 40 | 15.323 | 0
0.57543 | 0.4426 | 0.08465 | 700 | 40 | 17.543 | 0
0.59306 | 0.4167 | 0.10026 | 700 | 40 | 19.306 | 0
0.61207 | 0.34 | 0.13499 | 700 | 40 | 21.207 | 0
0.63436 | 0.2772 | 0.17434 | 700 | 40 | 19.404 | 4.032
0.64709 | 0.3143 | 0.22359 | 700 | 40 | 22.001 | 2.708
0.64575 | 0.293 | 0.2634 | 700 | 40 | 20.51 | 4.065
0.63341 | 0.1339 | 0.31991 | 698.8284 | 40 | 9.373 | 12.7964
0.6127 | 0.0091 | 0.33065 | 691.4214 | 40 | 0.637 | 13.226
0.60469 | 0 | 0.33312 | 684.2772 | 40 | 0 | 13.3248
0.56623 | 0 | 0.3421 | 681.3382 | 40 | 0 | 13.684
0.5129 | 0 | 0.31014 | 682.4538 | 40 | 0 | 12.4056
0.46903 | 0 | 0.26516 | 686.1572 | 40 | 0 | 10.6064
0.44233 | 0 | 0.22569 | 690.9518 | 40 | 0 | 9.0276
0.41938 | 0 | 0.21936 | 697.7882 | 40 | 0 | 8.7744
0.40901 | 0 | 0.23051 | 700 | 40 | 0 | 3.1128
0.406 | 0 | 0.20551 | 700 | 40 | 0 | 0.6
0.41227 | 0 | 0.18357 | 700 | 40 | 0 | 1.227
0.44778 | 0.0007 | 0.16902 | 700 | 40 | 0.049 | 4.729
0.47982 | 0.1182 | 0.15345 | 700 | 40 | 7.982 | 0
0.49029 | 0.569 | 0.11557 | 700 | 40 | 9.029 | 0
0.51381 | 0.7932 | 0.0709 | 700 | 40 | 11.381 | 0
0.54063 | 0.8305 | 0.09321 | 700 | 40 | 14.063 | 0
0.57101 | 0.8306 | 0.07534 | 700 | 40 | 17.101 | 0
0.59782 | 0.8205 | 0.07157 | 700 | 40 | 19.782 | 0
0.61787 | 0.8212 | 0.06834 | 700 | 40 | 21.787 | 0
0.63935 | 0.8192 | 0.07316 | 700 | 40 | 23.935 | 0
0.65643 | 0.8346 | 0.07001 | 700 | 40 | 25.643 | 0
0.67061 | 0.8297 | 0.07593 | 700 | 40 | 27.061 | 0
0.67861 | 0.7851 | 0.09116 | 700 | 40 | 27.861 | 0
0.67608 | 0.6996 | 0.12602 | 700 | 40 | 27.608 | 0
0.65597 | 0.3198 | 0.14364 | 700 | 40 | 22.386 | 3.211
0.63491 | 0.0175 | 0.18034 | 684.9476 | 40 | 1.225 | 7.2136
0.62749 | 0 | 0.25564 | 672.4242 | 40 | 0 | 10.2256
0.5867 | 0 | 0.32998 | 666.9534 | 40 | 0 | 13.1992
0.53149 | 0 | 0.34407 | 667.5672 | 40 | 0 | 13.7628
0.48363 | 0 | 0.33761 | 672.7086 | 40 | 0 | 13.5044
0.45079 | 0 | 0.33157 | 680.8924 | 40 | 0 | 13.2628
0.43155 | 0 | 0.35737 | 692.0322 | 40 | 0 | 14.2948
0.41809 | 0 | 0.37486 | 700 | 40 | 0 | 9.7768
0.4143 | 0 | 0.35905 | 700 | 40 | 0 | 1.43
0.42279 | 0 | 0.31584 | 700 | 40 | 0 | 2.279
0.45097 | 0.0008 | 0.29583 | 700 | 40 | 0.056 | 5.041
0.48347 | 0.1072 | 0.27871 | 700 | 40 | 7.504 | 0.843
0.49763 | 0.4526 | 0.21877 | 700 | 40 | 9.763 | 0
0.52366 | 0.5917 | 0.13332 | 700 | 40 | 12.366 | 0
0.55565 | 0.68 | 0.12711 | 700 | 40 | 15.565 | 0
0.58654 | 0.7981 | 0.08658 | 700 | 40 | 18.654 | 0
0.61698 | 0.8154 | 0.0649 | 700 | 40 | 21.698 | 0
0.64614 | 0.8164 | 0.09149 | 700 | 40 | 24.614 | 0
0.67241 | 0.8473 | 0.10072 | 700 | 40 | 27.241 | 0
0.69351 | 0.8349 | 0.11343 | 700 | 40 | 29.351 | 0
0.71334 | 0.851 | 0.14368 | 700 | 40 | 31.334 | 0
0.7232 | 0.8256 | 0.16574 | 700 | 40 | 32.32 | 0
0.71857 | 0.6166 | 0.18718 | 700 | 40 | 31.857 | 0
0.69362 | 0.2418 | 0.22561 | 696.5884 | 40 | 16.926 | 9.0244
0.66475 | 0.0139 | 0.27678 | 682.1576 | 40 | 0.973 | 11.0712
0.65269 | 0 | 0.3489 | 670.8446 | 40 | 0 | 13.956
0.61221 | 0 | 0.4252 | 666.6316 | 40 | 0 | 17.008
0.5554 | 0 | 0.46392 | 669.6484 | 40 | 0 | 18.5568
0.50331 | 0 | 0.49912 | 679.2822 | 40 | 0 | 19.9648
0.46856 | 0 | 0.5078 | 692.7382 | 40 | 0 | 20.312
0.4444 | 0 | 0.48226 | 700 | 40 | 0 | 11.7018
0.43033 | 0 | 0.45671 | 700 | 40 | 0 | 3.033
0.42402 | 0 | 0.44333 | 700 | 40 | 0 | 2.402
0.43049 | 0 | 0.43431 | 700 | 40 | 0 | 3.049
0.46391 | 0.0008 | 0.42273 | 700 | 40 | 0.056 | 6.335
0.49546 | 0.0589 | 0.40998 | 700 | 40 | 4.123 | 5.423
0.50952 | 0.2657 | 0.33535 | 700 | 40 | 10.952 | 0
0.53695 | 0.3698 | 0.33971 | 700 | 40 | 13.695 | 0
0.56887 | 0.6342 | 0.35603 | 700 | 40 | 16.887 | 0
0.60001 | 0.7961 | 0.35569 | 700 | 40 | 20.001 | 0
0.63193 | 0.8244 | 0.32687 | 700 | 40 | 23.193 | 0
0.6644 | 0.837 | 0.34139 | 700 | 40 | 26.44 | 0
0.6922 | 0.839 | 0.37373 | 700 | 40 | 29.22 | 0
0.71074 | 0.8363 | 0.41342 | 700 | 40 | 31.074 | 0
0.7298 | 0.7989 | 0.44702 | 700 | 40 | 32.98 | 0
0.73661 | 0.7358 | 0.4771 | 700 | 40 | 33.661 | 0
0.72737 | 0.592 | 0.53197 | 700 | 40 | 32.737 | 0
0.70349 | 0.2023 | 0.54984 | 700 | 40 | 14.161 | 16.188
0.67364 | 0.0078 | 0.52341 | 694.1184 | 40 | 0.546 | 20.9364
0.66468 | 0 | 0.55756 | 689.9528 | 40 | 0 | 22.3024
0.62764 | 0 | 0.63105 | 692.4308 | 40 | 0 | 25.242
0.5734 | 0 | 0.66612 | 700 | 40 | 0 | 24.9092
0.52512 | 0 | 0.68429 | 700 | 40 | 0 | 12.512
0.49371 | 0 | 0.67237 | 700 | 40 | 0 | 9.371
0.46973 | 0 | 0.65249 | 700 | 40 | 0 | 6.973
0.45422 | 0 | 0.63831 | 700 | 40 | 0 | 5.422
0.44857 | 0 | 0.62694 | 700 | 40 | 0 | 4.857
0.45843 | 0 | 0.63458 | 700 | 40 | 0 | 5.843
0.48803 | 0.0006 | 0.62405 | 700 | 40 | 0.042 | 8.761
0.52174 | 0.0632 | 0.59414 | 700 | 40 | 4.424 | 7.75
0.5332 | 0.3511 | 0.57383 | 700 | 40 | 13.32 | 0
0.55592 | 0.4442 | 0.63567 | 700 | 40 | 15.592 | 0
0.58358 | 0.6362 | 0.67308 | 700 | 40 | 18.358 | 0
0.61592 | 0.6333 | 0.67799 | 700 | 40 | 21.592 | 0
0.64312 | 0.2695 | 0.63579 | 700 | 40 | 18.865 | 5.447
0.67024 | 0.3845 | 0.62329 | 700 | 40 | 26.915 | 0.109
0.7016 | 0.5714 | 0.61385 | 700 | 40 | 30.16 | 0
0.7223 | 0.7387 | 0.60953 | 700 | 40 | 32.23 | 0
0.73518 | 0.4497 | 0.60542 | 700 | 40 | 31.479 | 2.039
0.74186 | 0.4645 | 0.63134 | 700 | 40 | 32.515 | 1.671
0.73067 | 0.4392 | 0.66423 | 700 | 40 | 30.744 | 2.323
0.69947 | 0.2005 | 0.65056 | 700 | 40 | 14.035 | 15.912
0.67548 | 0.0207 | 0.6553 | 700 | 40 | 1.449 | 26.099
0.67285 | 0 | 0.70635 | 700 | 40 | 0 | 27.285
0.6463 | 0 | 0.74197 | 700 | 40 | 0 | 24.63
0.61043 | 0 | 0.74184 | 700 | 40 | 0 | 21.043
0.56943 | 0 | 0.72264 | 700 | 40 | 0 | 16.943
0.53799 | 0 | 0.69394 | 700 | 40 | 0 | 13.799
0.51412 | 0 | 0.67049 | 700 | 40 | 0 | 11.412
0.5004 | 0 | 0.62185 | 700 | 40 | 0 | 10.04
0.48827 | 0 | 0.60293 | 700 | 40 | 0 | 8.827
0.48561 | 0 | 0.51641 | 700 | 40 | 0 | 8.561
0.48946 | 0.0001 | 0.47096 | 700 | 40 | 0.007 | 8.939
0.49849 | 0.0629 | 0.43752 | 700 | 40 | 4.403 | 5.446
0.51943 | 0.2619 | 0.36841 | 700 | 40 | 11.943 | 0
0.54783 | 0.4782 | 0.3507 | 700 | 40 | 14.783 | 0
0.57744 | 0.6167 | 0.37001 | 700 | 40 | 17.744 | 0
0.59748 | 0.6801 | 0.40983 | 700 | 40 | 19.748 | 0
0.61237 | 0.7518 | 0.42325 | 700 | 40 | 21.237 | 0
0.61526 | 0.7812 | 0.45347 | 700 | 40 | 21.526 | 0
0.6117 | 0.7691 | 0.47688 | 700 | 40 | 21.17 | 0
0.60812 | 0.5431 | 0.4953 | 700 | 40 | 20.812 | 0
0.61212 | 0.4358 | 0.52186 | 700 | 40 | 21.212 | 0
0.61303 | 0.4284 | 0.5227 | 700 | 40 | 21.303 | 0
0.6067 | 0.5997 | 0.55065 | 700 | 40 | 20.67 | 0
0.60149 | 0.2977 | 0.49241 | 700 | 40 | 20.149 | 0
0.59622 | 0.0215 | 0.47998 | 700 | 40 | 1.505 | 18.117
0.59887 | 0 | 0.48531 | 699.5254 | 40 | 0 | 19.4124
0.58165 | 0 | 0.47088 | 700 | 40 | 0 | 18.6396
0.55653 | 0 | 0.41717 | 700 | 40 | 0 | 15.653
0.52521 | 0 | 0.36237 | 700 | 40 | 0 | 12.521
0.49947 | 0 | 0.33153 | 700 | 40 | 0 | 9.947
0.48051 | 0 | 0.26548 | 700 | 40 | 0 | 8.051
0.46963 | 0 | 0.25428 | 700 | 40 | 0 | 6.963
0.46112 | 0 | 0.2813 | 700 | 40 | 0 | 6.112
0.4581 | 0 | 0.25848 | 700 | 40 | 0 | 5.81
0.45904 | 0.0009 | 0.25806 | 700 | 40 | 0.063 | 5.841
0.45824 | 0.1459 | 0.20921 | 700 | 40 | 5.824 | 0
0.48105 | 0.5855 | 0.16952 | 700 | 40 | 8.105 | 0
0.51859 | 0.7568 | 0.16159 | 700 | 40 | 11.859 | 0
0.55906 | 0.8003 | 0.13734 | 700 | 40 | 15.906 | 0
0.5931 | 0.8388 | 0.10612 | 700 | 40 | 19.31 | 0
0.63039 | 0.8622 | 0.12273 | 700 | 40 | 23.039 | 0
0.66186 | 0.8828 | 0.15542 | 700 | 40 | 26.186 | 0
0.6878 | 0.8735 | 0.14304 | 700 | 40 | 28.78 | 0
0.71323 | 0.846 | 0.15932 | 700 | 40 | 31.323 | 0
0.73111 | 0.8365 | 0.19583 | 700 | 40 | 33.111 | 0
0.74181 | 0.7395 | 0.27585 | 700 | 40 | 34.181 | 0
0.74004 | 0.4234 | 0.3484 | 700 | 40 | 29.638 | 4.366
0.72241 | 0.2 | 0.3935 | 697.499 | 40 | 14 | 15.74
0.69853 | 0.0192 | 0.42246 | 685.8884 | 40 | 1.344 | 16.8984
0.68454 | 0 | 0.47575 | 676.4644 | 40 | 0 | 19.03
0.65251 | 0 | 0.5467 | 673.0814 | 40 | 0 | 21.868
0.60598 | 0 | 0.5864 | 675.9394 | 40 | 0 | 23.456
0.55816 | 0 | 0.61694 | 684.801 | 40 | 0 | 24.6776
0.52444 | 0 | 0.63306 | 697.6794 | 40 | 0 | 25.3224
0.50258 | 0 | 0.64246 | 700 | 40 | 0 | 12.5786
0.49429 | 0 | 0.65588 | 700 | 40 | 0 | 9.429
0.49276 | 0 | 0.64153 | 700 | 40 | 0 | 9.276
0.50399 | 0 | 0.63486 | 700 | 40 | 0 | 10.399
0.54168 | 0.0001 | 0.65777 | 700 | 40 | 0.007 | 14.161
0.57623 | 0.0446 | 0.66465 | 700 | 40 | 3.122 | 14.501
0.58592 | 0.1576 | 0.66998 | 700 | 40 | 11.032 | 7.56
0.61241 | 0.3051 | 0.69398 | 700 | 40 | 21.241 | 0
0.64374 | 0.3498 | 0.71769 | 700 | 40 | 24.374 | 0
0.67461 | 0.3917 | 0.73586 | 700 | 40 | 27.419 | 0.042
0.7007 | 0.3895 | 0.74299 | 700 | 40 | 27.265 | 2.805
0.72704 | 0.4047 | 0.76334 | 700 | 40 | 28.329 | 4.375
0.75482 | 0.4209 | 0.73959 | 700 | 40 | 29.463 | 6.019
0.7696 | 0.3412 | 0.75831 | 700 | 40 | 23.884 | 13.076
0.78342 | 0.3104 | 0.75587 | 700 | 40 | 21.728 | 16.614
0.78969 | 0.276 | 0.75818 | 700 | 40 | 19.32 | 19.649
0.7771 | 0.249 | 0.71467 | 700 | 40 | 17.43 | 20.28
0.74975 | 0.0876 | 0.68651 | 698.6174 | 40 | 6.132 | 27.4604
0.72245 | 0.0061 | 0.63297 | 692.1182 | 40 | 0.427 | 25.3188
0.71591 | 0 | 0.57343 | 683.4644 | 40 | 0 | 22.9372
0.67792 | 0 | 0.56882 | 678.4252 | 40 | 0 | 22.7528
0.62594 | 0 | 0.57683 | 678.9044 | 40 | 0 | 23.0732
0.57787 | 0 | 0.57016 | 683.9238 | 40 | 0 | 22.8064
0.54601 | 0 | 0.53558 | 690.746 | 40 | 0 | 21.4232
0.52429 | 0 | 0.60683 | 700 | 40 | 0 | 21.683
0.51268 | 0 | 0.61589 | 700 | 40 | 0 | 11.268
0.50885 | 0 | 0.52711 | 700 | 40 | 0 | 10.885
0.51534 | 0 | 0.53168 | 700 | 40 | 0 | 11.534
0.54302 | 0.0003 | 0.5483 | 700 | 40 | 0.021 | 14.281
0.57087 | 0.0775 | 0.56798 | 700 | 40 | 5.425 | 11.662
0.57254 | 0.3636 | 0.53088 | 700 | 40 | 17.254 | 0
0.5796 | 0.6589 | 0.51657 | 700 | 40 | 17.96 | 0
0.59656 | 0.5396 | 0.60251 | 700 | 40 | 19.656 | 0
0.61109 | 0.4488 | 0.60045 | 700 | 40 | 21.109 | 0
0.62342 | 0.581 | 0.59156 | 700 | 40 | 22.342 | 0
0.64287 | 0.7348 | 0.60125 | 700 | 40 | 24.287 | 0
0.66958 | 0.8006 | 0.58812 | 700 | 40 | 26.958 | 0
0.68717 | 0.7965 | 0.57398 | 700 | 40 | 28.717 | 0
0.7122 | 0.8234 | 0.57767 | 700 | 40 | 31.22 | 0
0.7245 | 0.8066 | 0.57637 | 700 | 40 | 32.45 | 0
0.72744 | 0.6799 | 0.58807 | 700 | 40 | 32.744 | 0
0.70664 | 0.2907 | 0.54486 | 700 | 40 | 20.349 | 10.315
0.67745 | 0.0185 | 0.51796 | 694.2684 | 40 | 1.295 | 20.7184
0.66746 | 0 | 0.52497 | 688.5212 | 40 | 0 | 20.9988
0.63046 | 0 | 0.53797 | 686.994 | 40 | 0 | 21.5188
0.58125 | 0 | 0.5496 | 690.853 | 40 | 0 | 21.984
0.53672 | 0 | 0.55333 | 699.3142 | 40 | 0 | 22.1332
0.50847 | 0 | 0.59554 | 700 | 40 | 0 | 11.5328
0.48715 | 0 | 0.60922 | 700 | 40 | 0 | 8.715
0.47693 | 0 | 0.63008 | 700 | 40 | 0 | 7.693
0.47634 | 0 | 0.64728 | 700 | 40 | 0 | 7.634
0.49092 | 0 | 0.62802 | 700 | 40 | 0 | 9.092
0.52559 | 0.0003 | 0.62471 | 700 | 40 | 0.021 | 12.538
0.56063 | 0.1259 | 0.59999 | 700 | 40 | 8.813 | 7.25
0.57376 | 0.5359 | 0.5334 | 700 | 40 | 17.376 | 0
0.59809 | 0.7132 | 0.47843 | 700 | 40 | 19.809 | 0
0.63303 | 0.7476 | 0.47113 | 700 | 40 | 23.303 | 0
0.67129 | 0.7833 | 0.47222 | 700 | 40 | 27.129 | 0
0.70902 | 0.8046 | 0.46261 | 700 | 40 | 30.902 | 0
0.73907 | 0.8127 | 0.43165 | 700 | 40 | 33.907 | 0
0.76707 | 0.8193 | 0.43072 | 700 | 40 | 36.707 | 0
0.78572 | 0.8158 | 0.44465 | 700 | 40 | 38.572 | 0
0.80086 | 0.8022 | 0.47533 | 700 | 40 | 40.086 | 0
0.80389 | 0.7604 | 0.5462 | 700 | 40 | 40.389 | 0
0.7946 | 0.6589 | 0.6023 | 700 | 40 | 39.46 | 0
0.77203 | 0.2991 | 0.61871 | 700 | 40 | 20.937 | 16.266
0.74772 | 0.0172 | 0.64313 | 692.1572 | 40 | 1.204 | 25.7252
0.74064 | 0 | 0.6558 | 684.3252 | 40 | 0 | 26.232
0.70778 | 0 | 0.69931 | 681.5196 | 40 | 0 | 27.9724
0.65508 | 0 | 0.71446 | 684.59 | 40 | 0 | 28.5784
0.6087 | 0 | 0.71484 | 692.3136 | 40 | 0 | 28.5936
0.57749 | 0 | 0.72117 | 700 | 40 | 0 | 25.4354
0.55577 | 0 | 0.72726 | 700 | 40 | 0 | 15.577
0.53929 | 0 | 0.71853 | 700 | 40 | 0 | 13.929
0.53037 | 0 | 0.70854 | 700 | 40 | 0 | 13.037
0.53718 | 0 | 0.70254 | 700 | 40 | 0 | 13.718
0.56299 | 0.0003 | 0.64246 | 700 | 40 | 0.021 | 16.278
0.59244 | 0.0504 | 0.6208 | 700 | 40 | 3.528 | 15.716
0.60211 | 0.2601 | 0.61833 | 700 | 40 | 18.207 | 2.004
0.63132 | 0.484 | 0.66776 | 700 | 40 | 23.132 | 0
0.66021 | 0.5711 | 0.70313 | 700 | 40 | 26.021 | 0
0.69497 | 0.6483 | 0.72067 | 700 | 40 | 29.497 | 0
0.72371 | 0.676 | 0.74056 | 700 | 40 | 32.371 | 0
0.75147 | 0.7365 | 0.74954 | 700 | 40 | 35.147 | 0
0.7793 | 0.7863 | 0.75516 | 700 | 40 | 37.93 | 0
0.79814 | 0.8 | 0.76074 | 700 | 40 | 39.814 | 0
0.81308 | 0.7842 | 0.76015 | 700 | 40 | 41.308 | 0
0.81607 | 0.7275 | 0.76888 | 700 | 40 | 41.607 | 0
0.80306 | 0.5772 | 0.75831 | 700 | 40 | 40.306 | 0
0.7764 | 0.2457 | 0.74081 | 700 | 40 | 17.199 | 20.441
0.74901 | 0.0159 | 0.72654 | 695.2736 | 40 | 1.113 | 29.0616
0.74126 | 0 | 0.72235 | 690.0416 | 40 | 0 | 28.894
0.70848 | 0 | 0.73359 | 688.5372 | 40 | 0 | 29.3436
0.65972 | 0 | 0.69877 | 690.516 | 40 | 0 | 27.9508
0.61111 | 0 | 0.69612 | 697.2498 | 40 | 0 | 27.8448
0.57686 | 0 | 0.70707 | 700 | 40 | 0 | 20.4362
0.55018 | 0 | 0.64023 | 700 | 40 | 0 | 15.018
0.53243 | 0 | 0.59756 | 700 | 40 | 0 | 13.243
0.52524 | 0 | 0.5488 | 700 | 40 | 0 | 12.524
0.52873 | 0 | 0.49866 | 700 | 40 | 0 | 12.873
0.55344 | 0.0004 | 0.46119 | 700 | 40 | 0.028 | 15.316
0.57629 | 0.0297 | 0.39053 | 700 | 40 | 2.079 | 15.55
0.59472 | 0.2166 | 0.3711 | 700 | 40 | 15.162 | 4.31
0.62218 | 0.455 | 0.42082 | 700 | 40 | 22.218 | 0
0.66161 | 0.5639 | 0.49018 | 700 | 40 | 26.161 | 0
0.6972 | 0.5416 | 0.54867 | 700 | 40 | 29.72 | 0
0.72839 | 0.6703 | 0.59194 | 700 | 40 | 32.839 | 0
0.75679 | 0.5261 | 0.60826 | 700 | 40 | 35.679 | 0
0.77937 | 0.4308 | 0.62328 | 700 | 40 | 30.156 | 7.781
0.79425 | 0.4052 | 0.63801 | 700 | 40 | 28.364 | 11.061
0.8046 | 0.3928 | 0.64367 | 700 | 40 | 27.496 | 12.964
0.80257 | 0.3343 | 0.62223 | 700 | 40 | 23.401 | 16.856
0.78283 | 0.2523 | 0.62148 | 700 | 40 | 17.661 | 20.622
0.75039 | 0.1329 | 0.63113 | 699.5092 | 40 | 9.303 | 25.2452
0.71312 | 0.0192 | 0.60163 | 693.6064 | 40 | 1.344 | 24.0652
0.69962 | 0 | 0.60033 | 687.6576 | 40 | 0 | 24.0132
0.66735 | 0 | 0.5971 | 684.8066 | 40 | 0 | 23.884
0.62905 | 0 | 0.62592 | 686.9384 | 40 | 0 | 25.0368
0.58513 | 0 | 0.59328 | 692.1566 | 40 | 0 | 23.7312
0.54774 | 0 | 0.54758 | 699.2858 | 40 | 0 | 21.9032
0.52228 | 0 | 0.54469 | 700 | 40 | 0 | 12.9422
0.50645 | 0 | 0.57213 | 700 | 40 | 0 | 10.645
0.4959 | 0 | 0.57821 | 700 | 40 | 0 | 9.59
0.4928 | 0 | 0.56374 | 700 | 40 | 0 | 9.28
0.49621 | 0.0007 | 0.54569 | 700 | 40 | 0.049 | 9.572
0.49814 | 0.0403 | 0.5313 | 700 | 40 | 2.821 | 6.993
0.53008 | 0.1538 | 0.53483 | 700 | 40 | 10.766 | 2.242
0.5706 | 0.2909 | 0.60205 | 700 | 40 | 17.06 | 0
0.61362 | 0.383 | 0.64497 | 700 | 40 | 21.362 | 0
0.65371 | 0.4687 | 0.6798 | 700 | 40 | 25.371 | 0
0.68684 | 0.5952 | 0.68744 | 700 | 40 | 28.684 | 0
0.71747 | 0.6338 | 0.70334 | 700 | 40 | 31.747 | 0
0.73932 | 0.6024 | 0.71177 | 700 | 40 | 33.932 | 0
0.75742 | 0.4855 | 0.74811 | 700 | 40 | 33.985 | 1.757
0.76571 | 0.3393 | 0.69 | 700 | 40 | 23.751 | 12.82
0.76799 | 0.335 | 0.60968 | 700 | 40 | 23.45 | 13.349
0.75922 | 0.2608 | 0.63742 | 700 | 40 | 18.256 | 17.666
0.73145 | 0.1413 | 0.67779 | 700 | 40 | 9.891 | 23.254
0.69449 | 0.025 | 0.67254 | 699.2026 | 40 | 1.75 | 26.9016
0.68425 | 0 | 0.65282 | 696.8904 | 40 | 0 | 26.1128
0.65459 | 0 | 0.67875 | 698.5814 | 40 | 0 | 27.15
0.61832 | 0 | 0.6944 | 700 | 40 | 0 | 23.2506
0.57747 | 0 | 0.7114 | 700 | 40 | 0 | 17.747
0.54182 | 0 | 0.71089 | 700 | 40 | 0 | 14.182
0.51675 | 0 | 0.68643 | 700 | 40 | 0 | 11.675
0.49897 | 0 | 0.6618 | 700 | 40 | 0 | 9.897
0.48391 | 0 | 0.63511 | 700 | 40 | 0 | 8.391
0.47825 | 0 | 0.62584 | 700 | 40 | 0 | 7.825
0.47878 | 0.0006 | 0.61027 | 700 | 40 | 0.042 | 7.836
0.47555 | 0.0358 | 0.5921 | 700 | 40 | 2.506 | 5.049
0.50182 | 0.2076 | 0.58703 | 700 | 40 | 10.182 | 0
0.54493 | 0.2684 | 0.65299 | 700 | 40 | 14.493 | 0
0.58805 | 0.3098 | 0.68022 | 700 | 40 | 18.805 | 0
0.62576 | 0.3957 | 0.68156 | 700 | 40 | 22.576 | 0
0.65834 | 0.598 | 0.69898 | 700 | 40 | 25.834 | 0
0.68933 | 0.6247 | 0.68756 | 700 | 40 | 28.933 | 0
0.7164 | 0.4988 | 0.71156 | 700 | 40 | 31.64 | 0
0.73568 | 0.4594 | 0.70506 | 700 | 40 | 32.158 | 1.41
0.74978 | 0.357 | 0.69982 | 700 | 40 | 24.99 | 9.988
0.75139 | 0.2491 | 0.69109 | 700 | 40 | 17.437 | 17.702
0.74203 | 0.1657 | 0.69453 | 700 | 40 | 11.599 | 22.604
0.71785 | 0.1999 | 0.67749 | 700 | 40 | 13.993 | 17.792
0.68589 | 0.0285 | 0.69478 | 700 | 40 | 1.995 | 26.594
0.67273 | 0 | 0.72252 | 700 | 40 | 0 | 27.273
0.64361 | 0 | 0.72105 | 700 | 40 | 0 | 24.361
0.60599 | 0 | 0.67925 | 700 | 40 | 0 | 20.599
0.56518 | 0 | 0.67649 | 700 | 40 | 0 | 16.518
0.53239 | 0 | 0.67573 | 700 | 40 | 0 | 13.239
0.50963 | 0 | 0.66805 | 700 | 40 | 0 | 10.963
0.49472 | 0 | 0.68198 | 700 | 40 | 0 | 9.472
0.48497 | 0 | 0.64581 | 700 | 40 | 0 | 8.497
0.48241 | 0 | 0.58971 | 700 | 40 | 0 | 8.241
0.48867 | 0.0004 | 0.57356 | 700 | 40 | 0.028 | 8.839
0.48447 | 0.0771 | 0.56848 | 700 | 40 | 5.397 | 3.05
0.50741 | 0.3657 | 0.55304 | 700 | 40 | 10.741 | 0
0.54852 | 0.6323 | 0.61631 | 700 | 40 | 14.852 | 0
0.59782 | 0.798 | 0.65651 | 700 | 40 | 19.782 | 0
0.63911 | 0.8248 | 0.60851 | 700 | 40 | 23.911 | 0
0.67434 | 0.8434 | 0.5668 | 700 | 40 | 27.434 | 0
0.70804 | 0.8486 | 0.52652 | 700 | 40 | 30.804 | 0
0.73192 | 0.8449 | 0.51146 | 700 | 40 | 33.192 | 0
0.75189 | 0.8262 | 0.54645 | 700 | 40 | 35.189 | 0
0.76947 | 0.7963 | 0.6135 | 700 | 40 | 36.947 | 0
0.77689 | 0.7338 | 0.69029 | 700 | 40 | 37.689 | 0
0.76964 | 0.6157 | 0.72902 | 700 | 40 | 36.964 | 0
0.74874 | 0.2932 | 0.75881 | 700 | 40 | 20.524 | 14.35
0.71628 | 0.023 | 0.74769 | 699.8896 | 40 | 1.61 | 29.9076
0.70887 | 0 | 0.7466 | 698.8666 | 40 | 0 | 29.864
0.67423 | 0 | 0.76527 | 700 | 40 | 0 | 28.5564
0.62363 | 0 | 0.76897 | 700 | 40 | 0 | 22.363
0.57661 | 0 | 0.77027 | 700 | 40 | 0 | 17.661
0.54008 | 0 | 0.75533 | 700 | 40 | 0 | 14.008
0.51494 | 0 | 0.72784 | 700 | 40 | 0 | 11.494
0.50046 | 0 | 0.69738 | 700 | 40 | 0 | 10.046
0.49589 | 0 | 0.68572 | 700 | 40 | 0 | 9.589
0.50384 | 0 | 0.65777 | 700 | 40 | 0 | 10.384
0.53552 | 0.0004 | 0.62374 | 700 | 40 | 0.028 | 13.524
0.56433 | 0.1167 | 0.59147 | 700 | 40 | 8.169 | 8.264
0.58137 | 0.5116 | 0.52471 | 700 | 40 | 18.137 | 0
0.61156 | 0.7172 | 0.55866 | 700 | 40 | 21.156 | 0
0.64697 | 0.7508 | 0.56965 | 700 | 40 | 24.697 | 0
0.68499 | 0.7837 | 0.52484 | 700 | 40 | 28.499 | 0
0.71196 | 0.8029 | 0.46849 | 700 | 40 | 31.196 | 0
0.73801 | 0.8206 | 0.45183 | 700 | 40 | 33.801 | 0
0.75558 | 0.7949 | 0.44851 | 700 | 40 | 35.558 | 0
0.76457 | 0.7725 | 0.44696 | 700 | 40 | 36.457 | 0
0.78079 | 0.7913 | 0.44663 | 700 | 40 | 38.079 | 0
0.78388 | 0.7245 | 0.45829 | 700 | 40 | 38.388 | 0
0.77724 | 0.6445 | 0.47868 | 700 | 40 | 37.724 | 0
0.75544 | 0.3568 | 0.45309 | 700 | 40 | 24.976 | 10.568
0.73494 | 0.0305 | 0.399 | 684.601 | 40 | 2.135 | 15.96
0.72784 | 0 | 0.40609 | 668.0606 | 40 | 0 | 16.2436
0.69438 | 0 | 0.46752 | 657.3234 | 40 | 0 | 18.7008
0.6472 | 0 | 0.50894 | 652.961 | 40 | 0 | 20.3576
0.59845 | 0 | 0.50583 | 653.3492 | 40 | 0 | 20.2332
0.56495 | 0 | 0.48305 | 656.1762 | 40 | 0 | 19.322
0.54196 | 0 | 0.50239 | 662.0758 | 40 | 0 | 20.0956
0.52849 | 0 | 0.50629 | 669.4784 | 40 | 0 | 20.2516
0.52572 | 0 | 0.50612 | 677.1512 | 40 | 0 | 20.2448
0.53479 | 0 | 0.4523 | 681.7642 | 40 | 0 | 18.092
0.56217 | 0.0005 | 0.42797 | 682.701 | 40 | 0.035 | 17.1188
0.58521 | 0.0396 | 0.47131 | 685.8044 | 40 | 2.772 | 18.8524
0.60463 | 0.169 | 0.44903 | 695.1326 | 40 | 11.83 | 17.9612
0.62537 | 0.2632 | 0.43322 | 700 | 40 | 18.424 | 8.9804
0.65529 | 0.464 | 0.40637 | 700 | 40 | 25.529 | 0
0.68281 | 0.6135 | 0.38879 | 700 | 40 | 28.281 | 0
0.70029 | 0.6743 | 0.34592 | 700 | 40 | 30.029 | 0
0.7236 | 0.7921 | 0.32377 | 700 | 40 | 32.36 | 0
0.73291 | 0.8006 | 0.302 | 700 | 40 | 33.291 | 0
0.73684 | 0.8131 | 0.30565 | 700 | 40 | 33.684 | 0
0.74442 | 0.7921 | 0.28715 | 700 | 40 | 34.442 | 0
0.74452 | 0.7216 | 0.29054 | 700 | 40 | 34.452 | 0
0.73228 | 0.6623 | 0.28807 | 700 | 40 | 33.228 | 0
0.70931 | 0.3539 | 0.27955 | 700 | 40 | 24.773 | 6.158
0.68476 | 0.033 | 0.27981 | 685.0264 | 40 | 2.31 | 11.1924
0.67725 | 0 | 0.29369 | 669.049 | 40 | 0 | 11.7476
0.64791 | 0 | 0.3145 | 656.838 | 40 | 0 | 12.58
0.59675 | 0 | 0.31471 | 649.7514 | 40 | 0 | 12.5884
0.55243 | 0 | 0.31484 | 647.102 | 40 | 0 | 12.5936
0.51827 | 0 | 0.30913 | 647.6402 | 40 | 0 | 12.3652
0.49691 | 0 | 0.35227 | 652.04 | 40 | 0 | 14.0908
0.48412 | 0 | 0.33422 | 656.9968 | 40 | 0 | 13.3688
0.48023 | 0 | 0.29076 | 660.6042 | 40 | 0 | 11.6304
0.4917 | 0 | 0.22329 | 660.3658 | 40 | 0 | 8.9316
0.5221 | 0.0007 | 0.17207 | 655.0876 | 40 | 0.049 | 6.8828
0.55049 | 0.0378 | 0.15194 | 648.7622 | 40 | 2.646 | 6.0776
0.5605 | 0.1295 | 0.10743 | 646.0744 | 40 | 9.065 | 4.2972
0.57862 | 0.2243 | 0.13652 | 649.3742 | 40 | 15.701 | 5.4608
0.60505 | 0.2935 | 0.17811 | 656.5386 | 40 | 27.6694 | 0
0.64135 | 0.3393 | 0.17724 | 663.2442 | 40 | 23.751 | 7.0896
0.67843 | 0.5311 | 0.16599 | 679.2178 | 40 | 43.8166 | 0
0.70567 | 0.6337 | 0.16949 | 699.7894 | 40 | 51.1386 | 0
0.73219 | 0.4351 | 0.18082 | 700 | 40 | 30.457 | 2.9726
0.7437 | 0.4869 | 0.18691 | 700 | 40 | 34.083 | 0.287
0.7602 | 0.5394 | 0.21358 | 700 | 40 | 36.02 | 0
0.76661 | 0.4838 | 0.21774 | 700 | 40 | 33.866 | 2.795
0.75422 | 0.2869 | 0.21991 | 693.4574 | 40 | 20.083 | 8.7964
0.72827 | 0.1692 | 0.21908 | 681.2376 | 40 | 11.844 | 8.7632
0.70501 | 0.0207 | 0.20816 | 660.512 | 40 | 1.449 | 8.3264
0.69132 | 0 | 0.2127 | 639.888 | 40 | 0 | 8.508
0.65591 | 0 | 0.25329 | 624.4286 | 40 | 0 | 10.1316
0.60567 | 0 | 0.23687 | 613.3364 | 40 | 0 | 9.4748
0.55477 | 0 | 0.23183 | 607.1326 | 40 | 0 | 9.2732
0.52265 | 0 | 0.21783 | 603.5808 | 40 | 0 | 8.7132
0.49691 | 0 | 0.19753 | 601.791 | 40 | 0 | 7.9012
0.47943 | 0 | 0.19853 | 601.7892 | 40 | 0 | 7.9412
0.47269 | 0 | 0.14544 | 600.3378 | 40 | 0 | 5.8176
0.48196 | 0 | 0.17028 | 598.953 | 40 | 0 | 6.8112
0.5058 | 0.0011 | 0.15798 | 594.7692 | 40 | 0.077 | 6.3192
0.53006 | 0.0452 | 0.12748 | 590.0264 | 40 | 3.164 | 5.0992
0.55572 | 0.2044 | 0.15323 | 594.8916 | 40 | 14.308 | 6.1292
0.58063 | 0.314 | 0.12869 | 603.9562 | 40 | 27.1276 | 0
0.60776 | 0.3097 | 0.0961 | 608.7032 | 40 | 25.523 | 0
0.63938 | 0.406 | 0.07105 | 616.0272 | 40 | 31.262 | 0
0.67072 | 0.5664 | 0.06714 | 631.2888 | 40 | 42.3336 | 0
0.69935 | 0.5963 | 0.08418 | 646.462 | 40 | 45.1082 | 1.1369e-13
0.72776 | 0.6077 | 0.09622 | 660.0738 | 40 | 46.3878 | 0
0.74813 | 0.6334 | 0.10181 | 673.6712 | 40 | 48.4104 | 0
0.75905 | 0.5688 | 0.12277 | 682.493 | 40 | 44.7268 | 0
0.75921 | 0.4186 | 0.16365 | 682.42 | 40 | 29.302 | 6.546
0.74728 | 0.241 | 0.1774 | 671.658 | 40 | 16.87 | 7.096
0.724 | 0.0771 | 0.18361 | 651.9994 | 40 | 5.397 | 7.3444
0.69312 | 0.0066 | 0.2087 | 631.4974 | 40 | 0.462 | 8.348
0.67726 | 0 | 0.26404 | 614.333 | 40 | 0 | 10.5616
0.64434 | 0 | 0.34189 | 603.5746 | 40 | 0 | 13.6756
0.6051 | 0 | 0.35585 | 597.2986 | 40 | 0 | 14.234
0.56023 | 0 | 0.37923 | 596.4448 | 40 | 0 | 15.1692
0.52313 | 0 | 0.38836 | 599.6662 | 40 | 0 | 15.5344
0.49614 | 0 | 0.34506 | 603.8546 | 40 | 0 | 13.8024
0.4759 | 0 | 0.30468 | 608.4518 | 40 | 0 | 12.1872
0.46521 | 0 | 0.3088 | 614.2828 | 40 | 0 | 12.352
0.46255 | 0 | 0.28121 | 619.2762 | 40 | 0 | 11.2484
0.46839 | 0.0014 | 0.25671 | 622.8036 | 40 | 0.098 | 10.2684
0.47053 | 0.1053 | 0.23483 | 632.5148 | 40 | 16.7642 | 0
0.5058 | 0.4754 | 0.16444 | 661.7904 | 40 | 39.8556 | 0
0.55402 | 0.5713 | 0.14702 | 692.2602 | 40 | 45.8718 | 0
0.60835 | 0.6171 | 0.18082 | 700 | 40 | 28.5748 | 0
0.65981 | 0.7318 | 0.17515 | 700 | 40 | 25.981 | 0
0.70505 | 0.8449 | 0.15782 | 700 | 40 | 30.505 | 0
0.74335 | 0.8364 | 0.16128 | 700 | 40 | 34.335 | 0
0.77414 | 0.8305 | 0.16382 | 700 | 40 | 37.414 | 0
0.79485 | 0.8127 | 0.22595 | 700 | 40 | 39.485 | 0
0.80405 | 0.7551 | 0.30409 | 700 | 40 | 40.405 | 0
0.80409 | 0.6513 | 0.3681 | 700 | 40 | 40.409 | 0
0.77948 | 0.2399 | 0.4119 | 695.321 | 40 | 16.793 | 16.476
0.7412 | 0.1055 | 0.43616 | 686.0324 | 40 | 7.385 | 17.4464
0.70377 | 0.0176 | 0.41936 | 673.6618 | 40 | 1.232 | 16.7744
0.68674 | 0 | 0.4727 | 663.8958 | 40 | 0 | 18.908
0.65265 | 0 | 0.48971 | 658.2192 | 40 | 0 | 19.5884
0.61488 | 0 | 0.48629 | 656.1828 | 40 | 0 | 19.4516
0.5715 | 0 | 0.49146 | 658.6912 | 40 | 0 | 19.6584
0.53541 | 0 | 0.43728 | 662.6414 | 40 | 0 | 17.4912
0.50881 | 0 | 0.39523 | 667.5696 | 40 | 0 | 15.8092
0.4849 | 0 | 0.3466 | 672.9436 | 40 | 0 | 13.864
0.47865 | 0 | 0.34722 | 678.9674 | 40 | 0 | 13.8888
0.47108 | 0 | 0.26192 | 682.3362 | 40 | 0 | 10.4768
0.47246 | 0.0006 | 0.28196 | 686.4106 | 40 | 0.042 | 11.2784
0.46951 | 0.0674 | 0.272 | 695.0576 | 40 | 4.718 | 10.88
0.49443 | 0.2795 | 0.228 | 700 | 40 | 14.3854 | 0
0.53139 | 0.341 | 0.19816 | 700 | 40 | 13.139 | 0
0.57158 | 0.3879 | 0.20928 | 700 | 40 | 17.158 | 0
0.61526 | 0.5461 | 0.2285 | 700 | 40 | 21.526 | 0
0.65588 | 0.5906 | 0.22212 | 700 | 40 | 25.588 | 0
0.68918 | 0.6322 | 0.24512 | 700 | 40 | 28.918 | 0
0.72175 | 0.7254 | 0.18724 | 700 | 40 | 32.175 | 0
0.74995 | 0.6825 | 0.16415 | 700 | 40 | 34.995 | 0
0.7708 | 0.6027 | 0.19162 | 700 | 40 | 37.08 | 0
0.78072 | 0.4632 | 0.21129 | 700 | 40 | 32.424 | 5.648
0.78074 | 0.2624 | 0.25638 | 690.5492 | 40 | 18.368 | 10.2552
0.76692 | 0.0803 | 0.28721 | 670.9666 | 40 | 5.621 | 11.4884
0.73691 | 0.0034 | 0.28926 | 649.084 | 40 | 0.238 | 11.5704
0.72544 | 0 | 0.32276 | 629.4504 | 40 | 0 | 12.9104
0.69151 | 0 | 0.29547 | 612.1182 | 40 | 0 | 11.8188
0.64009 | 0 | 0.29422 | 599.878 | 40 | 0 | 11.7688
0.58964 | 0 | 0.27221 | 591.8024 | 40 | 0 | 10.8884
0.55233 | 0 | 0.34342 | 590.3062 | 40 | 0 | 13.7368
0.52603 | 0 | 0.38449 | 593.0828 | 40 | 0 | 15.3796
0.50788 | 0 | 0.3438 | 596.0468 | 40 | 0 | 13.752
0.49936 | 0 | 0.2517 | 596.1788 | 40 | 0 | 10.068
0.50355 | 0 | 0.12618 | 590.871 | 40 | 0 | 5.0472
0.52979 | 0.0011 | 0.12134 | 582.8226 | 40 | 0.077 | 4.8536
0.55205 | 0.037 | 0.10831 | 574.54 | 40 | 2.59 | 4.3324
0.58085 | 0.1895 | 0.10678 | 573.9912 | 40 | 13.265 | 4.2712
0.61814 | 0.413 | 0.09516 | 584.8936 | 40 | 32.7164 | 0
0.66492 | 0.5413 | 0.09433 | 600.0658 | 40 | 41.6642 | 0
0.71714 | 0.7114 | 0.11609 | 622.7934 | 40 | 54.4416 | 0
0.75901 | 0.7937 | 0.16671 | 649.1198 | 40 | 62.2274 | 0
0.7949 | 0.7491 | 0.23681 | 671.5392 | 40 | 61.9094 | 0
0.82516 | 0.7286 | 0.28304 | 691.3468 | 40 | 62.3236 | 0
0.84583 | 0.7006 | 0.30897 | 700 | 40 | 53.2362 | 0
0.85955 | 0.7279 | 0.35955 | 700 | 40 | 45.955 | 0
0.85847 | 0.6274 | 0.38395 | 700 | 40 | 43.918 | 1.929
0.84317 | 0.4006 | 0.36712 | 698.4098 | 40 | 28.042 | 14.6848
0.81204 | 0.1466 | 0.35931 | 681.8402 | 40 | 10.262 | 14.3724
0.77555 | 0.0116 | 0.35124 | 659.1468 | 40 | 0.812 | 14.0496
0.76031 | 0 | 0.384 | 638.4758 | 40 | 0 | 15.36
0.71939 | 0 | 0.46208 | 625.02 | 40 | 0 | 18.4832
0.65905 | 0 | 0.44926 | 617.0854 | 40 | 0 | 17.9704
0.60773 | 0 | 0.4517 | 614.3804 | 40 | 0 | 18.068
0.56729 | 0 | 0.41787 | 614.3662 | 40 | 0 | 16.7148
0.54011 | 0 | 0.34595 | 614.1932 | 40 | 0 | 13.838
0.51848 | 0 | 0.26104 | 612.7868 | 40 | 0 | 10.4416
0.50808 | 0 | 0.17696 | 609.0572 | 40 | 0 | 7.0784
0.51369 | 0 | 0.14719 | 603.5758 | 40 | 0 | 5.8876
0.5353 | 0.0009 | 0.17556 | 597.1312 | 40 | 0.063 | 7.0224
0.55598 | 0.0541 | 0.22825 | 594.4502 | 40 | 3.787 | 9.13
0.58554 | 0.2012 | 0.17787 | 597.095 | 40 | 14.084 | 7.1148
0.61912 | 0.3657 | 0.18937 | 608.3568 | 40 | 33.1738 | 0
0.65934 | 0.4992 | 0.22643 | 626.424 | 40 | 44.0012 | 0
0.69872 | 0.6451 | 0.27519 | 652.7166 | 40 | 56.1646 | 0
0.72961 | 0.7126 | 0.27179 | 680.5092 | 40 | 60.7536 | 0
0.75813 | 0.7783 | 0.23557 | 700 | 40 | 55.3038 | 0
0.77273 | 0.7709 | 0.23784 | 700 | 40 | 37.273 | 0
0.77368 | 0.7494 | 0.25715 | 700 | 40 | 37.368 | 0
0.76735 | 0.7331 | 0.23962 | 700 | 40 | 36.735 | 0
0.74865 | 0.6386 | 0.22043 | 700 | 40 | 34.865 | 0
0.7318 | 0.3906 | 0.28916 | 700 | 40 | 27.342 | 5.838
0.70976 | 0.104 | 0.33648 | 689.7632 | 40 | 7.28 | 13.4592
0.68518 | 0.0073 | 0.33362 | 675.101 | 40 | 0.511 | 13.3448
0.67815 | 0 | 0.36022 | 661.6948 | 40 | 0 | 14.4088
0.64711 | 0 | 0.39392 | 652.7406 | 40 | 0 | 15.7568
0.6047 | 0 | 0.41137 | 648.7254 | 40 | 0 | 16.4548
0.56098 | 0 | 0.36725 | 647.3174 | 40 | 0 | 14.69
0.53254 | 0 | 0.34553 | 647.8846 | 40 | 0 | 13.8212
0.51283 | 0 | 0.31712 | 649.2864 | 40 | 0 | 12.6848
0.50077 | 0 | 0.25418 | 649.3766 | 40 | 0 | 10.1672
0.49858 | 0 | 0.16989 | 646.3142 | 40 | 0 | 6.7956
0.50612 | 0 | 0.19074 | 643.3318 | 40 | 0 | 7.6296
0.52936 | 0.0006 | 0.17064 | 637.2634 | 40 | 0.042 | 6.8256
0.55239 | 0.0793 | 0.07796 | 630.6938 | 40 | 5.551 | 3.1184
0.57093 | 0.5285 | 0.08784 | 654.1094 | 40 | 40.5086 | 0
0.5906 | 0.7232 | 0.07829 | 688.805 | 40 | 53.7556 | 0
0.61373 | 0.7671 | 0.05959 | 700 | 40 | 32.568 | 0
0.63671 | 0.8117 | 0.04392 | 700 | 40 | 23.671 | 0
0.65233 | 0.8378 | 0.03602 | 700 | 40 | 25.233 | 0
0.67096 | 0.8335 | 0.02341 | 700 | 40 | 27.096 | 0
0.69126 | 0.8048 | 0.02055 | 700 | 40 | 29.126 | 0
0.71232 | 0.749 | 0.02684 | 700 | 40 | 31.232 | 0
0.72425 | 0.7437 | 0.0653 | 700 | 40 | 32.425 | 0
0.73183 | 0.5831 | 0.04553 | 700 | 40 | 33.183 | 0
0.72642 | 0.2628 | 0.08681 | 689.2264 | 40 | 18.396 | 3.4724
0.7073 | 0.0866 | 0.16232 | 671.0512 | 40 | 6.062 | 6.4928
0.68645 | 0.007 | 0.26998 | 653.6954 | 40 | 0.49 | 10.7992
0.67633 | 0 | 0.283 | 637.3824 | 40 | 0 | 11.32
0.64362 | 0 | 0.30161 | 625.0848 | 40 | 0 | 12.0644
0.60013 | 0 | 0.23296 | 614.3902 | 40 | 0 | 9.3184
0.55367 | 0 | 0.20241 | 607.1196 | 40 | 0 | 8.0964
0.52104 | 0 | 0.16001 | 601.416 | 40 | 0 | 6.4004
0.50045 | 0 | 0.12075 | 596.201 | 40 | 0 | 4.83
0.48159 | 0 | 0.09171 | 591.7104 | 40 | 0 | 3.6684
0.4717 | 0 | 0.07707 | 587.6232 | 40 | 0 | 3.0828
0.47546 | 0 | 0.07682 | 583.15 | 40 | 0 | 3.0728
0.49875 | 0.0012 | 0.10176 | 577.4294 | 40 | 0.084 | 4.0704
0.51739 | 0.1545 | 0.11517 | 581.1122 | 40 | 10.815 | 4.6068
0.54135 | 0.6084 | 0.12236 | 614.4596 | 40 | 47.4824 | 0
0.57427 | 0.7826 | 0.07793 | 654.9318 | 40 | 57.8992 | 0
0.617 | 0.8353 | 0.07359 | 694.6464 | 40 | 61.4146 | 0
0.66483 | 0.8553 | 0.07053 | 700 | 40 | 31.8366 | 0
0.71029 | 0.859 | 0.06457 | 700 | 40 | 31.029 | 0
0.75734 | 0.8631 | 0.081 | 700 | 40 | 35.734 | 0
0.79583 | 0.8537 | 0.11876 | 700 | 40 | 39.583 | 0
0.82379 | 0.8359 | 0.15285 | 700 | 40 | 42.379 | 0
0.83652 | 0.8205 | 0.17126 | 700 | 40 | 43.652 | 0
0.834 | 0.7781 | 0.21974 | 700 | 40 | 43.4 | 0
0.80113 | 0.6867 | 0.22135 | 700 | 40 | 40.113 | 0
0.76807 | 0.3868 | 0.19777 | 698.1798 | 40 | 27.076 | 7.9108
0.72611 | 0.0454 | 0.16365 | 675.2928 | 40 | 3.178 | 6.546
0.69974 | 0 | 0.15318 | 651.446 | 40 | 0 | 6.1272
0.66087 | 0 | 0.16476 | 631.9494 | 40 | 0 | 6.5904
0.60649 | 0 | 0.12621 | 616.3488 | 40 | 0 | 5.0484
0.55551 | 0 | 0.12188 | 605.673 | 40 | 0 | 4.8752
0.51631 | 0 | 0.13751 | 599.5424 | 40 | 0 | 5.5004
0.49087 | 0 | 0.10947 | 594.8342 | 40 | 0 | 4.3788
0.47691 | 0 | 0.09686 | 591.0176 | 40 | 0 | 3.8744
0.46962 | 0 | 0.10666 | 588.322 | 40 | 0 | 4.2664
0.47644 | 0 | 0.09777 | 584.5888 | 40 | 0 | 3.9108
0.49628 | 0.0015 | 0.09107 | 578.7086 | 40 | 0.105 | 3.6428
0.51298 | 0.1702 | 0.0823 | 582.6166 | 40 | 15.206 | 0
0.54498 | 0.6037 | 0.05376 | 612.528 | 40 | 44.4094 | 0
0.58568 | 0.7627 | 0.04322 | 649.0778 | 40 | 55.1178 | 0
0.63244 | 0.8211 | 0.05707 | 685.5936 | 40 | 59.7598 | 0
0.67496 | 0.8506 | 0.04979 | 700 | 40 | 41.9024 | 0
0.71511 | 0.8623 | 0.05298 | 700 | 40 | 31.511 | 0
0.75384 | 0.8616 | 0.04574 | 700 | 40 | 35.384 | 0
0.78741 | 0.8333 | 0.03912 | 700 | 40 | 38.741 | 0
0.80467 | 0.7701 | 0.04098 | 700 | 40 | 40.467 | 0
0.82262 | 0.7613 | 0.06175 | 700 | 40 | 42.262 | 0
0.8253 | 0.7559 | 0.07936 | 700 | 40 | 42.53 | 0
0.81587 | 0.6676 | 0.05918 | 700 | 40 | 41.587 | 0
0.79495 | 0.3762 | 0.08147 | 690.0978 | 40 | 26.334 | 3.2588
0.75833 | 0.0389 | 0.09549 | 660.8074 | 40 | 2.723 | 3.8196
0.73334 | 0 | 0.14442 | 633.2502 | 40 | 0 | 5.7768
0.69524 | 0 | 0.18941 | 611.3026 | 40 | 0 | 7.5764
0.64731 | 0 | 0.25653 | 596.8328 | 40 | 0 | 10.2612
0.59586 | 0 | 0.29032 | 588.8596 | 40 | 0 | 11.6128
0.55261 | 0 | 0.30323 | 585.7278 | 40 | 0 | 12.1292
0.52038 | 0 | 0.27585 | 584.7238 | 40 | 0 | 11.034
0.49786 | 0 | 0.27039 | 585.7534 | 40 | 0 | 10.8156
0.4792 | 0 | 0.22295 | 586.7514 | 40 | 0 | 8.918
0.47323 | 0 | 0.19227 | 587.1192 | 40 | 0 | 7.6908
0.47661 | 0.002 | 0.18825 | 587.1282 | 40 | 0.14 | 7.53
0.48055 | 0.1591 | 0.18205 | 597.4922 | 40 | 18.419 | 0
0.51914 | 0.56 | 0.15997 | 631.177 | 40 | 45.5988 | 0
0.56782 | 0.7073 | 0.14438 | 669.6812 | 40 | 55.2862 | 0
0.6224 | 0.7551 | 0.19206 | 700 | 40 | 52.5588 | 0
0.68081 | 0.778 | 0.18441 | 700 | 40 | 28.081 | 0
0.7265 | 0.7894 | 0.18102 | 700 | 40 | 32.65 | 0
0.7674 | 0.7895 | 0.18557 | 700 | 40 | 36.74 | 0
0.79847 | 0.7828 | 0.17878 | 700 | 40 | 39.847 | 0
0.82395 | 0.7856 | 0.16212 | 700 | 40 | 42.395 | 0
0.84461 | 0.7701 | 0.15443 | 700 | 40 | 44.461 | 0
0.8544 | 0.7293 | 0.17771 | 700 | 40 | 45.44 | 0
0.84909 | 0.5997 | 0.20579 | 700 | 40 | 41.979 | 2.93
0.83153 | 0.266 | 0.26158 | 685.9302 | 40 | 18.62 | 10.4632
0.79109 | 0.0317 | 0.32333 | 661.9734 | 40 | 2.219 | 12.9332
0.76448 | 0 | 0.37911 | 640.6898 | 40 | 0 | 15.1644
0.72606 | 0 | 0.46948 | 626.863 | 40 | 0 | 18.7792
0.67629 | 0 | 0.51133 | 619.6872 | 40 | 0 | 20.4532
0.62701 | 0 | 0.52663 | 618.0514 | 40 | 0 | 21.0652
0.58534 | 0 | 0.54529 | 621.329 | 40 | 0 | 21.8116
0.55125 | 0 | 0.51427 | 626.7748 | 40 | 0 | 20.5708
0.52633 | 0 | 0.45074 | 632.1714 | 40 | 0 | 18.0296
0.50894 | 0 | 0.41592 | 637.9142 | 40 | 0 | 16.6368
0.50127 | 0 | 0.3873 | 643.2792 | 40 | 0 | 15.492
0.49991 | 0.0016 | 0.39942 | 649.377 | 40 | 0.112 | 15.9768
0.49536 | 0.1396 | 0.40703 | 665.8942 | 40 | 26.0532 | -1.1369e-13
0.52955 | 0.5626 | 0.36423 | 700 | 40 | 47.0608 | 0
0.58529 | 0.7187 | 0.31249 | 700 | 40 | 18.529 | 0
0.64383 | 0.7545 | 0.31261 | 700 | 40 | 24.383 | 0
0.70457 | 0.7447 | 0.29967 | 700 | 40 | 30.457 | 0
0.75709 | 0.7521 | 0.37328 | 700 | 40 | 35.709 | 0
0.79484 | 0.7265 | 0.42556 | 700 | 40 | 39.484 | 0
0.77265 | 0.7193 | 0.46299 | 700 | 40 | 37.265 | 0
0.7796 | 0.6593 | 0.47945 | 700 | 40 | 37.96 | 0
0.79413 | 0.6143 | 0.4787 | 700 | 40 | 39.413 | 0
0.79563 | 0.4896 | 0.53135 | 700 | 40 | 34.272 | 5.291
0.79103 | 0.3351 | 0.5878 | 700 | 40 | 23.457 | 15.646
0.76756 | 0.192 | 0.63706 | 700 | 40 | 13.44 | 23.316
0.7382 | 0.0236 | 0.62932 | 693.0048 | 40 | 1.652 | 25.1728
0.71797 | 0 | 0.63916 | 686.7742 | 40 | 0 | 25.5664
0.68758 | 0 | 0.64884 | 683.9698 | 40 | 0 | 25.9536
0.6384 | 0 | 0.60261 | 684.2342 | 40 | 0 | 24.1044
0.59016 | 0 | 0.58288 | 688.5334 | 40 | 0 | 23.3152
0.55734 | 0 | 0.55227 | 694.8902 | 40 | 0 | 22.0908
0.53259 | 0 | 0.48999 | 700 | 40 | 0 | 18.3688
0.51419 | 0 | 0.48027 | 700 | 40 | 0 | 11.419
0.50777 | 0 | 0.4873 | 700 | 40 | 0 | 10.777
0.51032 | 0 | 0.46811 | 700 | 40 | 0 | 11.032
0.52898 | 0.0011 | 0.45397 | 700 | 40 | 0.077 | 12.821
0.54237 | 0.0211 | 0.41543 | 700 | 40 | 1.477 | 12.76
0.56246 | 0.0777 | 0.38553 | 700 | 40 | 5.439 | 10.807
0.58766 | 0.1392 | 0.3866 | 700 | 40 | 9.744 | 9.022
0.62327 | 0.1977 | 0.37779 | 700 | 40 | 13.839 | 8.488
0.65391 | 0.2954 | 0.33085 | 700 | 40 | 20.678 | 4.713
0.68006 | 0.3754 | 0.30165 | 700 | 40 | 26.278 | 1.728
0.70187 | 0.3391 | 0.25025 | 700 | 40 | 23.737 | 6.45
0.72623 | 0.3508 | 0.23176 | 700 | 40 | 24.556 | 8.067
0.74381 | 0.3552 | 0.1988 | 698.435 | 40 | 24.864 | 7.952
0.75542 | 0.3972 | 0.16195 | 697.175 | 40 | 27.804 | 6.478
0.7538 | 0.2861 | 0.13362 | 687.1668 | 40 | 20.027 | 5.3448
0.73747 | 0.2335 | 0.11646 | 674.4232 | 40 | 16.345 | 4.6584
0.71036 | 0.1095 | 0.10236 | 655.1466 | 40 | 7.665 | 4.0944
0.68368 | 0.0129 | 0.08511 | 631.086 | 40 | 0.903 | 3.4044
0.67347 | 0 | 0.09007 | 607.3418 | 40 | 0 | 3.6028
0.64063 | 0 | 0.09657 | 587.1416 | 40 | 0 | 3.8628
0.59473 | 0 | 0.11931 | 572.441 | 40 | 0 | 4.7724
0.54416 | 0 | 0.14152 | 563.6858 | 40 | 0 | 5.6608
0.50828 | 0 | 0.14094 | 558.4954 | 40 | 0 | 5.6376
0.48545 | 0 | 0.13697 | 555.4292 | 40 | 0 | 5.4788
0.46963 | 0 | 0.13978 | 554.0574 | 40 | 0 | 5.5912
0.46189 | 0 | 0.13813 | 553.3936 | 40 | 0 | 5.5252
0.4686 | 0 | 0.13528 | 551.9448 | 40 | 0 | 5.4112
0.49087 | 0.0006 | 0.14628 | 548.751 | 40 | 0.042 | 5.8512
0.50921 | 0.0343 | 0.16381 | 546.7834 | 40 | 2.401 | 6.5524
0.52669 | 0.1805 | 0.15256 | 552.8518 | 40 | 12.635 | 6.1024
0.54473 | 0.3357 | 0.15687 | 568.1526 | 40 | 29.7738 | 0
0.57211 | 0.3775 | 0.18019 | 584.5742 | 40 | 33.6326 | 0
0.60117 | 0.5284 | 0.17709 | 608.5288 | 40 | 44.0716 | 0
0.62783 | 0.6722 | 0.15868 | 639.147 | 40 | 53.4012 | 0
0.65445 | 0.6907 | 0.15819 | 668.3786 | 40 | 54.6766 | 0
0.67422 | 0.7298 | 0.16245 | 698.5406 | 40 | 57.584 | 0
0.68515 | 0.744 | 0.17742 | 700 | 40 | 29.9744 | 0
0.68902 | 0.7365 | 0.16844 | 700 | 40 | 28.902 | 0
0.68458 | 0.7379 | 0.17812 | 700 | 40 | 28.458 | 0
0.67266 | 0.6677 | 0.20368 | 700 | 40 | 27.266 | 0
0.65265 | 0.3951 | 0.21356 | 700 | 40 | 25.265 | 0
0.63714 | 0.0524 | 0.23916 | 689.5204 | 40 | 3.668 | 9.5664
0.62912 | 0 | 0.30591 | 678.8448 | 40 | 0 | 12.2364
0.60347 | 0 | 0.38151 | 673.7582 | 40 | 0 | 15.2604
0.55653 | 0 | 0.41481 | 674.6976 | 40 | 0 | 16.5924
0.51175 | 0 | 0.41616 | 680.169 | 40 | 0 | 16.6464
0.48113 | 0 | 0.41835 | 688.79 | 40 | 0 | 16.734
0.46311 | 0 | 0.39727 | 698.3698 | 40 | 0 | 15.8908
0.45072 | 0 | 0.39426 | 700 | 40 | 0 | 6.7022
0.44708 | 0 | 0.39099 | 700 | 40 | 0 | 4.708
0.45277 | 0 | 0.35813 | 700 | 40 | 0 | 5.277
0.47817 | 0.0005 | 0.30457 | 700 | 40 | 0.035 | 7.782
0.49667 | 0.1151 | 0.2384 | 700 | 40 | 8.057 | 1.61
0.51594 | 0.4838 | 0.18855 | 700 | 40 | 11.594 | 0
0.54324 | 0.7155 | 0.2038 | 700 | 40 | 14.324 | 0
0.57877 | 0.7417 | 0.19868 | 700 | 40 | 17.877 | 0
0.61384 | 0.7768 | 0.20777 | 700 | 40 | 21.384 | 0
0.64866 | 0.8064 | 0.25307 | 700 | 40 | 24.866 | 0
0.68176 | 0.8413 | 0.24972 | 700 | 40 | 28.176 | 0
0.71724 | 0.8313 | 0.25646 | 700 | 40 | 31.724 | 0
0.74394 | 0.8447 | 0.24774 | 700 | 40 | 34.394 | 0
0.76933 | 0.8581 | 0.24381 | 700 | 40 | 36.933 | 0
0.77871 | 0.8 | 0.22302 | 700 | 40 | 37.871 | 0
0.77537 | 0.6426 | 0.19723 | 700 | 40 | 37.537 | 0
0.75455 | 0.3295 | 0.16694 | 694.2876 | 40 | 23.065 | 6.6776
0.72048 | 0.0387 | 0.14391 | 670.705 | 40 | 2.709 | 5.7564
0.69599 | 0 | 0.15536 | 647.3204 | 40 | 0 | 6.2144
0.65891 | 0 | 0.19268 | 629.1366 | 40 | 0 | 7.7072
0.60424 | 0 | 0.2019 | 616.7886 | 40 | 0 | 8.076
0.55139 | 0 | 0.20397 | 609.8084 | 40 | 0 | 8.1588
0.51177 | 0 | 0.20574 | 606.861 | 40 | 0 | 8.2296
0.4847 | 0 | 0.19959 | 606.3746 | 40 | 0 | 7.9836
0.46554 | 0 | 0.18454 | 607.2022 | 40 | 0 | 7.3816
0.45642 | 0 | 0.16528 | 608.1714 | 40 | 0 | 6.6112
0.46275 | 0 | 0.17016 | 608.7028 | 40 | 0 | 6.8064
0.48533 | 0.0024 | 0.16954 | 607.1194 | 40 | 0.168 | 6.7816
0.5039 | 0.1563 | 0.18905 | 615.2324 | 40 | 18.503 | 0
0.53426 | 0.5607 | 0.17615 | 648.1014 | 40 | 46.295 | 0
0.5691 | 0.7317 | 0.18934 | 689.984 | 40 | 58.7926 | 0
0.61225 | 0.7847 | 0.25133 | 700 | 40 | 31.241 | 0
0.65564 | 0.7742 | 0.25646 | 700 | 40 | 25.564 | 0
0.69379 | 0.8155 | 0.24212 | 700 | 40 | 29.379 | 0
0.73026 | 0.7941 | 0.22901 | 700 | 40 | 33.026 | 0
0.76235 | 0.7936 | 0.24604 | 700 | 40 | 36.235 | 0
0.78597 | 0.8122 | 0.27849 | 700 | 40 | 38.597 | 0
0.80285 | 0.813 | 0.30519 | 700 | 40 | 40.285 | 0
0.81166 | 0.801 | 0.3497 | 700 | 40 | 41.166 | 0
0.80613 | 0.6439 | 0.39698 | 700 | 40 | 40.613 | 0
0.77995 | 0.2566 | 0.46596 | 698.6054 | 40 | 17.962 | 18.6384
0.73891 | 0.0138 | 0.45964 | 684.066 | 40 | 0.966 | 18.3856
0.71518 | 0 | 0.5075 | 672.848 | 40 | 0 | 20.3
0.67493 | 0 | 0.6112 | 669.803 | 40 | 0 | 24.448
0.62441 | 0 | 0.63286 | 672.6764 | 40 | 0 | 25.3144
0.57276 | 0 | 0.62612 | 680.4452 | 40 | 0 | 25.0448
0.53431 | 0 | 0.62753 | 692.1154 | 40 | 0 | 25.1012
0.50567 | 0 | 0.60384 | 700 | 40 | 0 | 18.4516
0.48919 | 0 | 0.61124 | 700 | 40 | 0 | 8.919
0.48172 | 0 | 0.58086 | 700 | 40 | 0 | 8.172
0.48614 | 0 | 0.54515 | 700 | 40 | 0 | 8.614
0.50492 | 0.0008 | 0.51581 | 700 | 40 | 0.056 | 10.436
0.5197 | 0.0698 | 0.55797 | 700 | 40 | 4.886 | 7.084
0.54833 | 0.3454 | 0.54086 | 700 | 40 | 14.833 | 0
0.59017 | 0.5453 | 0.57524 | 700 | 40 | 19.017 | 0
0.63413 | 0.5517 | 0.64166 | 700 | 40 | 23.413 | 0
0.67869 | 0.6687 | 0.63145 | 700 | 40 | 27.869 | 0
0.71985 | 0.706 | 0.63881 | 700 | 40 | 31.985 | 0
0.75762 | 0.5185 | 0.62157 | 700 | 40 | 35.762 | 0
0.79013 | 0.6292 | 0.60992 | 700 | 40 | 39.013 | 0
0.8132 | 0.7241 | 0.63757 | 700 | 40 | 41.32 | 0
0.82686 | 0.557 | 0.66154 | 700 | 40 | 38.99 | 3.696
0.83243 | 0.3379 | 0.68692 | 700 | 40 | 23.653 | 19.59
0.82117 | 0.2914 | 0.72573 | 700 | 40 | 20.398 | 21.719
0.79328 | 0.0789 | 0.72656 | 695.2574 | 40 | 5.523 | 29.0624
0.75608 | 0.0121 | 0.70068 | 688.5236 | 40 | 0.847 | 28.0272
0.73507 | 0.0001 | 0.71581 | 683.656 | 40 | 0.007 | 28.6324
0.70365 | 0 | 0.72416 | 682.2574 | 40 | 0 | 28.9664
0.66097 | 0 | 0.72234 | 685.054 | 40 | 0 | 28.8936
0.61791 | 0 | 0.73623 | 692.7122 | 40 | 0 | 29.4492
0.58353 | 0 | 0.73139 | 700 | 40 | 0 | 25.6408
0.55678 | 0 | 0.72188 | 700 | 40 | 0 | 15.678
0.53966 | 0 | 0.72267 | 700 | 40 | 0 | 13.966
0.52438 | 0 | 0.70333 | 700 | 40 | 0 | 12.438
0.5228 | 0 | 0.70403 | 700 | 40 | 0 | 12.28
0.52782 | 0.0008 | 0.65877 | 700 | 40 | 0.056 | 12.726
0.5267 | 0.1426 | 0.60851 | 700 | 40 | 9.982 | 2.688
0.56121 | 0.5346 | 0.57313 | 700 | 40 | 16.121 | 0
0.60767 | 0.7373 | 0.62732 | 700 | 40 | 20.767 | 0
0.65516 | 0.8113 | 0.61695 | 700 | 40 | 25.516 | 0
0.69884 | 0.8478 | 0.55855 | 700 | 40 | 29.884 | 0
0.74114 | 0.8566 | 0.51089 | 700 | 40 | 34.114 | 0
0.77351 | 0.8548 | 0.45332 | 700 | 40 | 37.351 | 0
0.79627 | 0.8297 | 0.44104 | 700 | 40 | 39.627 | 0
0.81369 | 0.7913 | 0.4529 | 700 | 40 | 41.369 | 0
0.82769 | 0.5567 | 0.48717 | 700 | 40 | 38.969 | 3.8
0.83565 | 0.4246 | 0.55367 | 700 | 40 | 29.722 | 13.843
0.83252 | 0.5188 | 0.61004 | 700 | 40 | 36.316 | 6.936
0.80833 | 0.2845 | 0.6272 | 700 | 40 | 19.915 | 20.918
0.77434 | 0.0388 | 0.64286 | 690.9964 | 40 | 2.716 | 25.7144
0.75546 | 0 | 0.67208 | 682.3336 | 40 | 0 | 26.8832
0.72463 | 0 | 0.64303 | 675.5918 | 40 | 0 | 25.7212
0.68548 | 0 | 0.60711 | 671.3282 | 40 | 0 | 24.2844
0.64444 | 0 | 0.5683 | 669.6162 | 40 | 0 | 22.732
0.60333 | 0 | 0.52052 | 670.104 | 40 | 0 | 20.8208
0.5787 | 0 | 0.50713 | 672.5192 | 40 | 0 | 20.2852
0.55078 | 0 | 0.43931 | 675.0136 | 40 | 0 | 17.5724
0.52662 | 0 | 0.39252 | 678.0524 | 40 | 0 | 15.7008
0.51505 | 0 | 0.3113 | 678.9994 | 40 | 0 | 12.452
0.50913 | 0.0004 | 0.29254 | 679.816 | 40 | 0.028 | 11.7016
0.50858 | 0.083 | 0.25679 | 685.0396 | 40 | 5.81 | 10.2716
0.52631 | 0.4482 | 0.22058 | 700 | 40 | 27.5914 | 0
0.56433 | 0.6151 | 0.25555 | 700 | 40 | 16.433 | 0
0.60021 | 0.7513 | 0.25373 | 700 | 40 | 20.021 | 0
0.63113 | 0.7885 | 0.25179 | 700 | 40 | 23.113 | 0
0.66274 | 0.7376 | 0.23166 | 700 | 40 | 26.274 | 0
0.68281 | 0.7462 | 0.2136 | 700 | 40 | 28.281 | 0
0.69472 | 0.7946 | 0.21843 | 700 | 40 | 29.472 | 0
0.70104 | 0.8093 | 0.19789 | 700 | 40 | 30.104 | 0
0.68462 | 0.7969 | 0.20909 | 700 | 40 | 28.462 | 0
0.67706 | 0.7509 | 0.19388 | 700 | 40 | 27.706 | 0
0.66651 | 0.6493 | 0.22071 | 700 | 40 | 26.651 | 0
0.66039 | 0.3745 | 0.24885 | 700 | 40 | 26.039 | 0
0.64433 | 0.0518 | 0.2517 | 689.261 | 40 | 3.626 | 10.068
0.63679 | 0 | 0.29828 | 677.5132 | 40 | 0 | 11.9312
0.60852 | 0 | 0.34296 | 670.3796 | 40 | 0 | 13.7184
0.56945 | 0 | 0.29919 | 665.4022 | 40 | 0 | 11.9676
0.52338 | 0 | 0.28126 | 664.3146 | 40 | 0 | 11.2504
0.48553 | 0 | 0.26993 | 666.5588 | 40 | 0 | 10.7972
0.46497 | 0 | 0.22906 | 669.2242 | 40 | 0 | 9.1624
0.45179 | 0 | 0.20302 | 672.166 | 40 | 0 | 8.1208
0.44652 | 0 | 0.15615 | 673.76 | 40 | 0 | 6.246
0.45706 | 0 | 0.16053 | 674.4752 | 40 | 0 | 6.4212
0.48427 | 0.0009 | 0.11936 | 670.8856 | 40 | 0.063 | 4.7744
0.50286 | 0.0855 | 0.11982 | 671.3774 | 40 | 5.985 | 4.7928
0.52421 | 0.3691 | 0.12614 | 689.839 | 40 | 30.8826 | -1.1369e-13
0.54789 | 0.4928 | 0.11936 | 700 | 40 | 24.95 | 0
0.57226 | 0.6124 | 0.11085 | 700 | 40 | 17.226 | 0
0.60066 | 0.7472 | 0.11473 | 700 | 40 | 20.066 | 0
0.62623 | 0.8287 | 0.10225 | 700 | 40 | 22.623 | 0
0.66001 | 0.7424 | 0.09304 | 700 | 40 | 26.001 | 0
0.70169 | 0.485 | 0.09415 | 700 | 40 | 30.169 | 0
0.73941 | 0.4316 | 0.10453 | 700 | 40 | 30.212 | 3.729
0.77367 | 0.3406 | 0.1044 | 690.651 | 40 | 23.842 | 4.176
0.79151 | 0.3019 | 0.12689 | 677.7086 | 40 | 21.133 | 5.0756
0.79637 | 0.2586 | 0.15334 | 662.3072 | 40 | 18.102 | 6.1336
0.77906 | 0.1099 | 0.19347 | 639.833 | 40 | 7.693 | 7.7388
0.74598 | 0.0177 | 0.24009 | 616.0776 | 40 | 1.239 | 9.6036
0.72666 | 0 | 0.29023 | 595.0208 | 40 | 0 | 11.6092
0.68773 | 0 | 0.28431 | 577.6202 | 40 | 0 | 11.3724
0.63281 | 0 | 0.28431 | 565.7116 | 40 | 0 | 11.3724
0.58294 | 0 | 0.30957 | 559.8004 | 40 | 0 | 12.3828
0.54056 | 0 | 0.31548 | 558.3636 | 40 | 0 | 12.6192
0.5138 | 0 | 0.33937 | 560.5584 | 40 | 0 | 13.5748
0.49535 | 0 | 0.28456 | 562.4058 | 40 | 0 | 11.3824
0.48663 | 0 | 0.2944 | 565.5188 | 40 | 0 | 11.776
0.49189 | 0 | 0.30114 | 568.3754 | 40 | 0 | 12.0456
0.51342 | 0.0012 | 0.2906 | 568.7414 | 40 | 0.084 | 11.624
0.53443 | 0.1253 | 0.29436 | 575.8438 | 40 | 8.771 | 11.7744
0.56405 | 0.4082 | 0.23406 | 597.3752 | 40 | 37.9364 | 0
0.60061 | 0.7188 | 0.21261 | 636.1346 | 40 | 58.8204 | 0
0.64277 | 0.8025 | 0.2205 | 676.8526 | 40 | 64.995 | 0
0.68772 | 0.8178 | 0.24662 | 700 | 40 | 51.9194 | 0
0.72984 | 0.8459 | 0.27055 | 700 | 40 | 32.984 | 0
0.77213 | 0.8428 | 0.28386 | 700 | 40 | 37.213 | 0
0.80874 | 0.5712 | 0.29217 | 700 | 40 | 39.984 | 0.89
0.8384 | 0.35 | 0.26667 | 691.3268 | 40 | 24.5 | 10.6668
0.86342 | 0.2932 | 0.22327 | 674.4396 | 40 | 20.524 | 8.9308
0.87199 | 0.2661 | 0.23877 | 655.4184 | 40 | 18.627 | 9.5508
0.86809 | 0.3218 | 0.27539 | 642.151 | 40 | 22.526 | 11.0156
0.84837 | 0.2732 | 0.33056 | 629.6604 | 40 | 19.124 | 13.2224
0.8115 | 0.049 | 0.37359 | 606.884 | 40 | 3.43 | 14.9436
0.7921 | 0 | 0.42897 | 584.8328 | 40 | 0 | 17.1588
0.75051 | 0 | 0.45836 | 568.1162 | 40 | 0 | 18.3344
0.69328 | 0 | 0.42881 | 555.9406 | 40 | 0 | 17.1524
0.64102 | 0 | 0.40446 | 548.017 | 40 | 0 | 16.1784
0.59717 | 0 | 0.43802 | 545.8208 | 40 | 0 | 17.5208
0.56769 | 0 | 0.3411 | 542.6958 | 40 | 0 | 13.644
0.5477 | 0 | 0.22914 | 537.0914 | 40 | 0 | 9.1656
0.53371 | 0 | 0.22434 | 532.694 | 40 | 0 | 8.9736
0.53367 | 0 | 0.27981 | 530.5194 | 40 | 0 | 11.1924
0.55294 | 0.0007 | 0.3273 | 528.3664 | 40 | 0.049 | 13.092
0.56517 | 0.1396 | 0.28423 | 532.9906 | 40 | 9.772 | 11.3692
0.59302 | 0.5318 | 0.27783 | 562.0278 | 40 | 48.3392 | 0
0.63243 | 0.7411 | 0.25237 | 600.7566 | 40 | 61.9718 | 0
0.68181 | 0.8056 | 0.25559 | 639.1912 | 40 | 66.6156 | 0
0.73364 | 0.8308 | 0.2415 | 673.6432 | 40 | 67.816 | 0
0.78514 | 0.8365 | 0.21029 | 700 | 40 | 64.8708 | 0
0.83465 | 0.8265 | 0.16665 | 700 | 40 | 43.465 | 0
0.87396 | 0.7987 | 0.16193 | 700 | 40 | 47.396 | 0
0.89744 | 0.7653 | 0.16743 | 700 | 40 | 49.744 | 0
0.91072 | 0.7491 | 0.18227 | 700 | 40 | 51.072 | 0
0.91413 | 0.6567 | 0.20455 | 700 | 40 | 45.969 | 5.444
0.91083 | 0.4026 | 0.23207 | 686.3818 | 40 | 28.182 | 9.2828
0.88852 | 0.2207 | 0.22996 | 662.1772 | 40 | 15.449 | 9.1984
0.84806 | 0.0374 | 0.23306 | 629.3116 | 40 | 2.618 | 9.3224
0.82679 | 0 | 0.267 | 597.3126 | 40 | 0 | 10.68
0.78494 | 0 | 0.31205 | 571.3006 | 40 | 0 | 12.482
0.72164 | 0 | 0.3676 | 553.8406 | 40 | 0 | 14.704
0.66101 | 0 | 0.39335 | 543.4736 | 40 | 0 | 15.734
0.61452 | 0 | 0.40794 | 538.3392 | 40 | 0 | 16.3176
0.5822 | 0 | 0.45071 | 538.1476 | 40 | 0 | 18.0284
0.55822 | 0 | 0.46229 | 540.8172 | 40 | 0 | 18.4916
0.54684 | 0 | 0.45778 | 544.4444 | 40 | 0 | 18.3112
0.54901 | 0 | 0.45943 | 547.9206 | 40 | 0 | 18.3772
0.56978 | 0.0009 | 0.47803 | 550.1268 | 40 | 0.063 | 19.1212
0.58785 | 0.1501 | 0.48031 | 561.0612 | 40 | 10.507 | 19.2124
0.61038 | 0.5459 | 0.41372 | 594.785 | 40 | 54.7618 | 0
0.64893 | 0.7259 | 0.36305 | 635.227 | 40 | 65.335 | 0
0.69597 | 0.7815 | 0.33705 | 673.817 | 40 | 68.187 | 0
0.7441 | 0.8138 | 0.32622 | 700 | 40 | 60.593 | 0
0.79218 | 0.8311 | 0.32478 | 700 | 40 | 39.218 | 0
0.83926 | 0.8332 | 0.3311 | 700 | 40 | 43.926 | 0
0.87898 | 0.8229 | 0.35445 | 700 | 40 | 47.898 | 0
0.90459 | 0.8123 | 0.35573 | 700 | 40 | 50.459 | 0
0.90868 | 0.7279 | 0.38843 | 700 | 40 | 50.868 | 0
0.9113 | 0.6711 | 0.4174 | 700 | 40 | 46.977 | 4.153
0.91067 | 0.5816 | 0.44236 | 700 | 40 | 40.712 | 10.355
0.89162 | 0.34 | 0.47101 | 693.4784 | 40 | 23.8 | 18.8404
0.85892 | 0.0444 | 0.50998 | 671.0936 | 40 | 3.108 | 20.3992
0.83859 | 0 | 0.6007 | 651.2626 | 40 | 0 | 24.028
0.8075 | 0 | 0.69068 | 638.1398 | 40 | 0 | 27.6272
0.75329 | 0 | 0.69209 | 630.4944 | 40 | 0 | 27.6836
0.70002 | 0 | 0.68134 | 627.746 | 40 | 0 | 27.2536
0.65532 | 0 | 0.65976 | 628.6044 | 40 | 0 | 26.3904
0.62708 | 0 | 0.67812 | 633.0212 | 40 | 0 | 27.1248
0.60839 | 0 | 0.67865 | 639.3282 | 40 | 0 | 27.146
0.59958 | 0 | 0.68713 | 646.8554 | 40 | 0 | 27.4852
0.60077 | 0 | 0.67973 | 653.9676 | 40 | 0 | 27.1892
0.62356 | 0.0006 | 0.68022 | 658.8624 | 40 | 0.042 | 27.2088
0.63305 | 0.111 | 0.65245 | 669.4254 | 40 | 7.77 | 26.098
0.6561 | 0.4449 | 0.61161 | 699.4228 | 40 | 55.6074 | 0
0.69004 | 0.6697 | 0.63488 | 700 | 40 | 29.5812 | 0
0.73636 | 0.7507 | 0.64712 | 700 | 40 | 33.636 | 0
0.78341 | 0.7841 | 0.63348 | 700 | 40 | 38.341 | 0
0.82033 | 0.8147 | 0.60169 | 700 | 40 | 42.033 | 0
0.85448 | 0.8194 | 0.57301 | 700 | 40 | 45.448 | 0
0.88468 | 0.7469 | 0.56954 | 700 | 40 | 48.468 | 0
0.90309 | 0.604 | 0.60616 | 700 | 40 | 42.28 | 8.029
0.90688 | 0.6272 | 0.65232 | 700 | 40 | 43.904 | 6.784
0.90623 | 0.5295 | 0.68374 | 700 | 40 | 37.065 | 13.558
0.89925 | 0.4116 | 0.67812 | 700 | 40 | 28.812 | 21.113
0.87313 | 0.1241 | 0.68374 | 688.7236 | 40 | 8.687 | 27.3496
0.83326 | 0.0243 | 0.70043 | 675.1158 | 40 | 1.701 | 28.0172
0.81692 | 0.0004 | 0.73445 | 662.8298 | 40 | 0.028 | 29.378
0.78389 | 0 | 0.69465 | 652.2268 | 40 | 0 | 27.786
0.74069 | 0 | 0.67679 | 645.2294 | 40 | 0 | 27.0716
0.69429 | 0 | 0.68076 | 643.0308 | 40 | 0 | 27.2304
0.65391 | 0 | 0.68436 | 645.0142 | 40 | 0 | 27.3744
0.62521 | 0 | 0.62831 | 647.6256 | 40 | 0 | 25.1324
0.59972 | 0 | 0.59202 | 651.3344 | 40 | 0 | 23.6808
0.58438 | 0 | 0.55168 | 654.9636 | 40 | 0 | 22.0672
0.57312 | 0 | 0.50581 | 657.884 | 40 | 0 | 20.2324
0.57493 | 0.0004 | 0.47307 | 659.3418 | 40 | 0.028 | 18.9228
0.57328 | 0.0541 | 0.50729 | 666.0924 | 40 | 3.787 | 20.2916
0.59797 | 0.4151 | 0.55561 | 697.5768 | 40 | 51.2814 | 0
0.6431 | 0.6343 | 0.58529 | 700 | 40 | 26.7332 | 0
0.68497 | 0.6833 | 0.62265 | 700 | 40 | 28.497 | 0
0.72925 | 0.693 | 0.60715 | 700 | 40 | 32.925 | 0
0.76468 | 0.7569 | 0.58624 | 700 | 40 | 36.468 | 0
0.79108 | 0.7658 | 0.53197 | 700 | 40 | 39.108 | 0
0.80821 | 0.7724 | 0.49196 | 700 | 40 | 40.821 | 0
0.81064 | 0.7756 | 0.47902 | 700 | 40 | 41.064 | 0
0.80624 | 0.7535 | 0.48551 | 700 | 40 | 40.624 | 0
0.80655 | 0.6284 | 0.52693 | 700 | 40 | 40.655 | 0
0.80553 | 0.5079 | 0.59252 | 700 | 40 | 35.553 | 5
0.79159 | 0.2358 | 0.65898 | 700 | 40 | 16.506 | 22.653
0.76755 | 0.0217 | 0.66555 | 691.386 | 40 | 1.519 | 26.622
0.75907 | 0 | 0.67344 | 682.4166 | 40 | 0 | 26.9376
0.73864 | 0 | 0.73416 | 677.919 | 40 | 0 | 29.3664
0.70329 | 0 | 0.74553 | 677.4112 | 40 | 0 | 29.8212
0.66605 | 0 | 0.74639 | 680.6618 | 40 | 0 | 29.8556
0.63641 | 0 | 0.73614 | 686.4664 | 40 | 0 | 29.4456
0.61385 | 0 | 0.70386 | 693.2358 | 40 | 0 | 28.1544
0.59594 | 0 | 0.68878 | 700 | 40 | 0 | 26.3582
0.58506 | 0 | 0.69266 | 700 | 40 | 0 | 18.506
0.58045 | 0 | 0.69118 | 700 | 40 | 0 | 18.045
0.57731 | 0.0004 | 0.66361 | 700 | 40 | 0.028 | 17.703
0.57158 | 0.0937 | 0.60269 | 700 | 40 | 6.559 | 10.599
0.59451 | 0.448 | 0.55813 | 700 | 40 | 19.451 | 0
0.63667 | 0.6275 | 0.59814 | 700 | 40 | 23.667 | 0
0.67863 | 0.7196 | 0.56284 | 700 | 40 | 27.863 | 0
0.71001 | 0.7504 | 0.4758 | 700 | 40 | 31.001 | 0
0.7433 | 0.7624 | 0.41467 | 700 | 40 | 34.33 | 0
0.77215 | 0.7997 | 0.35268 | 700 | 40 | 37.215 | 0
0.79827 | 0.807 | 0.28832 | 700 | 40 | 39.827 | 0
0.81522 | 0.7878 | 0.27927 | 700 | 40 | 41.522 | 0
0.83266 | 0.764 | 0.29093 | 700 | 40 | 43.266 | 0
0.84745 | 0.6932 | 0.30362 | 700 | 40 | 44.745 | 0
0.85077 | 0.5905 | 0.41128 | 700 | 40 | 41.335 | 3.742
0.8289 | 0.3735 | 0.38648 | 698.7142 | 40 | 26.145 | 15.4592
0.79807 | 0.0586 | 0.33949 | 676.5888 | 40 | 4.102 | 13.5796
0.77152 | 0 | 0.32775 | 652.5468 | 40 | 0 | 13.11
0.71963 | 0 | 0.35363 | 634.729 | 40 | 0 | 14.1452
0.67576 | 0 | 0.37871 | 622.3014 | 40 | 0 | 15.1484
0.62749 | 0 | 0.37144 | 614.41 | 40 | 0 | 14.8576
0.58977 | 0 | 0.36813 | 610.1582 | 40 | 0 | 14.7252
0.56543 | 0 | 0.31118 | 606.0624 | 40 | 0 | 12.4472
0.54959 | 0 | 0.30779 | 603.415 | 40 | 0 | 12.3116
0.53968 | 0 | 0.28369 | 600.7946 | 40 | 0 | 11.3476
0.54127 | 0 | 0.26348 | 597.2068 | 40 | 0 | 10.5392
0.54441 | 0.0005 | 0.26142 | 593.2576 | 40 | 0.035 | 10.4568
0.55513 | 0.1186 | 0.25724 | 596.3362 | 40 | 8.302 | 10.2896
0.56716 | 0.4882 | 0.23104 | 623.0358 | 40 | 43.4156 | 0
0.58108 | 0.6523 | 0.21905 | 659.3508 | 40 | 54.423 | 1.1369e-13
0.60403 | 0.7278 | 0.21339 | 698.4294 | 40 | 59.4816 | 0
0.62523 | 0.7493 | 0.18413 | 700 | 40 | 24.0936 | 0
0.65305 | 0.7629 | 0.1814 | 700 | 40 | 25.305 | 0
0.67779 | 0.7614 | 0.17669 | 700 | 40 | 27.779 | 0
0.70411 | 0.7446 | 0.18987 | 700 | 40 | 30.411 | 0
0.71648 | 0.7239 | 0.20657 | 700 | 40 | 31.648 | 0
0.72941 | 0.7219 | 0.23368 | 700 | 40 | 32.941 | 0
0.73793 | 0.6579 | 0.31469 | 700 | 40 | 33.793 | 0
0.73833 | 0.5859 | 0.37855 | 700 | 40 | 33.833 | 0
0.7159 | 0.3592 | 0.43079 | 700 | 40 | 25.144 | 6.446
0.68565 | 0.0475 | 0.45778 | 693.0712 | 40 | 3.325 | 18.3112
0.6738 | 0 | 0.52131 | 686.5436 | 40 | 0 | 20.8524
0.64528 | 0 | 0.57942 | 685.1924 | 40 | 0 | 23.1768
0.59827 | 0 | 0.6119 | 689.8414 | 40 | 0 | 24.476
0.5509 | 0 | 0.48378 | 694.1026 | 40 | 0 | 19.3512
0.51521 | 0 | 0.49064 | 700 | 40 | 0 | 17.4184
0.4939 | 0 | 0.45501 | 700 | 40 | 0 | 9.39
0.48086 | 0 | 0.4274 | 700 | 40 | 0 | 8.086
0.47705 | 0 | 0.35821 | 700 | 40 | 0 | 7.705
0.48538 | 0 | 0.33085 | 700 | 40 | 0 | 8.538
0.51097 | 0.0009 | 0.35032 | 700 | 40 | 0.063 | 11.034
0.529 | 0.0986 | 0.3094 | 700 | 40 | 6.902 | 5.998
0.54947 | 0.478 | 0.26092 | 700 | 40 | 14.947 | 0
0.57682 | 0.7051 | 0.22195 | 700 | 40 | 17.682 | 0
0.61024 | 0.8015 | 0.21331 | 700 | 40 | 21.024 | 0
0.64884 | 0.8256 | 0.12895 | 700 | 40 | 24.884 | 0
0.68919 | 0.8206 | 0.09981 | 700 | 40 | 28.919 | 0
0.72162 | 0.8127 | 0.1018 | 700 | 40 | 32.162 | 0
0.74931 | 0.7789 | 0.14974 | 700 | 40 | 34.931 | 0
0.77223 | 0.6643 | 0.19616 | 700 | 40 | 37.223 | 0
0.7849 | 0.4838 | 0.23505 | 700 | 40 | 33.866 | 4.624
0.78223 | 0.5181 | 0.29986 | 700 | 40 | 36.267 | 1.956
0.76974 | 0.4314 | 0.39843 | 700 | 40 | 30.198 | 6.776
0.74733 | 0.2001 | 0.47522 | 698.2828 | 40 | 14.007 | 19.0088
0.71463 | 0.047 | 0.49324 | 689.8394 | 40 | 3.29 | 19.7296
0.69586 | 0 | 0.45187 | 678.3282 | 40 | 0 | 18.0748
0.66673 | 0 | 0.46567 | 670.282 | 40 | 0 | 18.6268
0.61681 | 0 | 0.45935 | 666.975 | 40 | 0 | 18.374
0.56843 | 0 | 0.45766 | 668.4384 | 40 | 0 | 18.3064
0.53383 | 0 | 0.4615 | 673.5154 | 40 | 0 | 18.46
0.50912 | 0 | 0.42968 | 679.7906 | 40 | 0 | 17.1872
0.49286 | 0 | 0.43902 | 688.0654 | 40 | 0 | 17.5608
0.48587 | 0 | 0.45534 | 697.692 | 40 | 0 | 18.2136
0.4962 | 0 | 0.43964 | 700 | 40 | 0 | 11.928
0.52185 | 0.001 | 0.40335 | 700 | 40 | 0.07 | 12.115
0.54256 | 0.0832 | 0.3533 | 700 | 40 | 5.824 | 8.432
0.5655 | 0.3337 | 0.25038 | 700 | 40 | 16.55 | 0
0.59653 | 0.4663 | 0.27956 | 700 | 40 | 19.653 | 0
0.63644 | 0.6337 | 0.28981 | 700 | 40 | 23.644 | 0
0.67908 | 0.7578 | 0.31895 | 700 | 40 | 27.908 | 0
0.72573 | 0.8247 | 0.37814 | 700 | 40 | 32.573 | 0
0.76139 | 0.816 | 0.4136 | 700 | 40 | 36.139 | 0
0.78137 | 0.8042 | 0.41587 | 700 | 40 | 38.137 | 0
0.79731 | 0.799 | 0.42968 | 700 | 40 | 39.731 | 0
0.81048 | 0.7953 | 0.41471 | 700 | 40 | 41.048 | 0
0.80658 | 0.7452 | 0.41922 | 700 | 40 | 40.658 | 0
0.79378 | 0.6062 | 0.43228 | 700 | 40 | 39.378 | 0
0.77351 | 0.3686 | 0.42736 | 700 | 40 | 25.802 | 11.549
0.74407 | 0.0364 | 0.41389 | 684.6966 | 40 | 2.548 | 16.5556
0.72437 | 0 | 0.37181 | 667.132 | 40 | 0 | 14.8724
0.69222 | 0 | 0.44451 | 655.6904 | 40 | 0 | 17.7804
0.64087 | 0 | 0.45724 | 649.893 | 40 | 0 | 18.2896
0.59275 | 0 | 0.50333 | 650.7512 | 40 | 0 | 20.1332
0.55383 | 0 | 0.5192 | 656.1362 | 40 | 0 | 20.768
0.52937 | 0 | 0.48246 | 662.4976 | 40 | 0 | 19.2984
0.51322 | 0 | 0.4477 | 669.0836 | 40 | 0 | 17.908
0.50641 | 0 | 0.3838 | 673.7946 | 40 | 0 | 15.352
0.51686 | 0 | 0.34892 | 676.0654 | 40 | 0 | 13.9568
0.54256 | 0.0007 | 0.34458 | 675.6416 | 40 | 0.049 | 13.7832
0.5637 | 0.0744 | 0.31924 | 677.2492 | 40 | 5.208 | 12.7696
0.58793 | 0.2157 | 0.29109 | 685.1988 | 40 | 15.099 | 11.6436
0.62115 | 0.3988 | 0.36309 | 700 | 40 | 36.9162 | 0
0.66453 | 0.5386 | 0.40079 | 700 | 40 | 26.453 | 0
0.71185 | 0.6534 | 0.3483 | 700 | 40 | 31.185 | 0
0.75546 | 0.7244 | 0.28274 | 700 | 40 | 35.546 | 0
0.78813 | 0.7206 | 0.30312 | 700 | 40 | 38.813 | 0
0.80364 | 0.7392 | 0.33474 | 700 | 40 | 40.364 | 0
0.81001 | 0.7365 | 0.33118 | 700 | 40 | 41.001 | 0
0.81075 | 0.752 | 0.33222 | 700 | 40 | 41.075 | 0
0.81253 | 0.7133 | 0.33771 | 700 | 40 | 41.253 | 0
0.79621 | 0.564 | 0.34024 | 700 | 40 | 39.48 | 0.141
0.77404 | 0.322 | 0.38475 | 700 | 40 | 22.54 | 14.864
0.74481 | 0.031 | 0.38942 | 683.2658 | 40 | 2.17 | 15.5768
0.73278 | 0 | 0.41852 | 666.7286 | 40 | 0 | 16.7408
0.69677 | 0 | 0.44546 | 654.87 | 40 | 0 | 17.8184
0.64476 | 0 | 0.43745 | 647.892 | 40 | 0 | 17.498
0.59473 | 0 | 0.42567 | 645.4458 | 40 | 0 | 17.0268
0.55606 | 0 | 0.41715 | 646.5258 | 40 | 0 | 16.686
0.53204 | 0 | 0.42711 | 650.4062 | 40 | 0 | 17.0844
0.5142 | 0 | 0.41124 | 655.4358 | 40 | 0 | 16.4496
0.50626 | 0 | 0.40058 | 660.833 | 40 | 0 | 16.0232
0.50996 | 0 | 0.39273 | 665.5462 | 40 | 0 | 15.7092
0.53094 | 0.0007 | 0.38066 | 667.7276 | 40 | 0.049 | 15.2264
0.5461 | 0.0695 | 0.33614 | 671.4282 | 40 | 4.865 | 13.4456
0.57406 | 0.3966 | 0.27936 | 692.9586 | 40 | 38.9364 | 0
0.61672 | 0.5996 | 0.34693 | 700 | 40 | 28.7134 | 0
0.66546 | 0.7636 | 0.33168 | 700 | 40 | 26.546 | 0
0.71652 | 0.8211 | 0.2956 | 700 | 40 | 31.652 | 0
0.75949 | 0.8344 | 0.24315 | 700 | 40 | 35.949 | 0
0.8065 | 0.828 | 0.22455 | 700 | 40 | 40.65 | 0
0.83749 | 0.8195 | 0.22162 | 700 | 40 | 43.749 | 0
0.85851 | 0.812 | 0.20752 | 700 | 40 | 45.851 | 0
0.8626 | 0.7965 | 0.22699 | 700 | 40 | 46.26 | 0
0.85358 | 0.7658 | 0.24083 | 700 | 40 | 45.358 | 0
0.83535 | 0.6607 | 0.25212 | 700 | 40 | 43.535 | 0
0.80801 | 0.3806 | 0.26005 | 696.243 | 40 | 26.642 | 10.402
0.76708 | 0.0509 | 0.26993 | 673.8952 | 40 | 3.563 | 10.7972
0.74195 | 0 | 0.32379 | 652.6518 | 40 | 0 | 12.9516
0.70489 | 0 | 0.42372 | 639.1116 | 40 | 0 | 16.9488
0.66092 | 0 | 0.4727 | 631.9276 | 40 | 0 | 18.908
0.61311 | 0 | 0.46162 | 629.0814 | 40 | 0 | 18.4648
0.57281 | 0 | 0.44336 | 629.5348 | 40 | 0 | 17.7344
0.54268 | 0 | 0.4174 | 631.9628 | 40 | 0 | 16.696
0.52154 | 0 | 0.41538 | 636.424 | 40 | 0 | 16.6152
0.50831 | 0 | 0.39182 | 641.2658 | 40 | 0 | 15.6728
0.50148 | 0 | 0.35809 | 645.4414 | 40 | 0 | 14.3236
0.50685 | 0.0006 | 0.3292 | 647.9664 | 40 | 0.042 | 13.168
0.50524 | 0.1338 | 0.29969 | 658.796 | 40 | 9.366 | 11.9876
0.53707 | 0.5412 | 0.22112 | 691.8178 | 40 | 46.7288 | 0
0.58662 | 0.7553 | 0.17954 | 700 | 40 | 26.8442 | 0
0.64245 | 0.8205 | 0.16503 | 700 | 40 | 24.245 | 0
0.6956 | 0.8529 | 0.10787 | 700 | 40 | 29.56 | 0
0.74139 | 0.8546 | 0.05059 | 700 | 40 | 34.139 | 0
0.78208 | 0.837 | 0.05737 | 700 | 40 | 38.208 | 0
0.79649 | 0.8257 | 0.06931 | 700 | 40 | 39.649 | 0
0.79613 | 0.8144 | 0.09113 | 700 | 40 | 39.613 | 0
0.7985 | 0.8081 | 0.09518 | 700 | 40 | 39.85 | 0
0.79979 | 0.7853 | 0.10791 | 700 | 40 | 39.979 | 0
0.78229 | 0.6855 | 0.11721 | 700 | 40 | 38.229 | 0
0.74032 | 0.4068 | 0.11833 | 699.1772 | 40 | 28.476 | 4.7332
0.70113 | 0.0606 | 0.14036 | 678.9206 | 40 | 4.242 | 5.6144
0.67855 | 0 | 0.19326 | 658.796 | 40 | 0 | 7.7304
0.64583 | 0 | 0.26377 | 644.7638 | 40 | 0 | 10.5508
0.60611 | 0 | 0.3421 | 637.8368 | 40 | 0 | 13.684
0.56534 | 0 | 0.36842 | 636.0396 | 40 | 0 | 14.7368
0.53214 | 0 | 0.37905 | 637.9876 | 40 | 0 | 15.162
0.50611 | 0 | 0.38566 | 642.803 | 40 | 0 | 15.4264
0.48534 | 0 | 0.35454 | 648.4506 | 40 | 0 | 14.1816
0.47055 | 0 | 0.33052 | 654.6164 | 40 | 0 | 13.2208
0.46059 | 0 | 0.27183 | 659.4306 | 40 | 0 | 10.8732
0.46337 | 0.0007 | 0.22286 | 662.057 | 40 | 0.049 | 8.9144
0.46341 | 0.1174 | 0.21885 | 672.688 | 40 | 16.972 | 0
0.48247 | 0.4837 | 0.17946 | 700 | 40 | 35.559 | 0
0.51668 | 0.6752 | 0.11304 | 700 | 40 | 11.668 | 0
0.55152 | 0.7423 | 0.11548 | 700 | 40 | 15.152 | 0
0.58503 | 0.7822 | 0.0858 | 700 | 40 | 18.503 | 0
0.62599 | 0.8111 | 0.07138 | 700 | 40 | 22.599 | 0
0.66337 | 0.7911 | 0.0722 | 700 | 40 | 26.337 | 0
0.69008 | 0.7996 | 0.07386 | 700 | 40 | 29.008 | 0
0.71621 | 0.7467 | 0.0989 | 700 | 40 | 31.621 | 0
0.73609 | 0.6566 | 0.13995 | 700 | 40 | 33.609 | 0
0.74956 | 0.4905 | 0.20711 | 700 | 40 | 34.335 | 0.621
0.74939 | 0.3059 | 0.23017 | 695.6808 | 40 | 21.413 | 9.2068
0.73553 | 0.1215 | 0.27915 | 681.7988 | 40 | 8.505 | 11.166
0.71016 | 0.0316 | 0.32594 | 666.0324 | 40 | 2.212 | 13.0376
0.69582 | 0.0002 | 0.35284 | 650.578 | 40 | 0.014 | 14.1136
0.66744 | 0 | 0.39454 | 639.6156 | 40 | 0 | 15.7816
0.62025 | 0 | 0.42033 | 634.4038 | 40 | 0 | 16.8132
0.57409 | 0 | 0.4336 | 634.3388 | 40 | 0 | 17.344
0.53699 | 0 | 0.42224 | 637.5294 | 40 | 0 | 16.8896
0.51474 | 0 | 0.39054 | 641.677 | 40 | 0 | 15.6216
0.49535 | 0 | 0.3769 | 647.218 | 40 | 0 | 15.076
0.49105 | 0 | 0.37421 | 653.0814 | 40 | 0 | 14.9684
0.49775 | 0 | 0.35392 | 657.4632 | 40 | 0 | 14.1568
0.52165 | 0.0006 | 0.33643 | 658.7974 | 40 | 0.042 | 13.4572
0.53694 | 0.118 | 0.31407 | 665.9262 | 40 | 8.26 | 12.5628
0.56702 | 0.5224 | 0.24646 | 695.6506 | 40 | 46.4264 | 0
0.60949 | 0.746 | 0.24621 | 700 | 40 | 25.2984 | 0
0.65733 | 0.8136 | 0.25505 | 700 | 40 | 25.733 | 0
0.70709 | 0.8441 | 0.20083 | 700 | 40 | 30.709 | 0
0.7527 | 0.8614 | 0.16987 | 700 | 40 | 35.27 | 0
0.78994 | 0.8485 | 0.16714 | 700 | 40 | 38.994 | 0
0.81783 | 0.8357 | 0.20364 | 700 | 40 | 41.783 | 0
0.83833 | 0.8286 | 0.23302 | 700 | 40 | 43.833 | 0
0.85125 | 0.8007 | 0.26712 | 700 | 40 | 45.125 | 0
0.85404 | 0.7477 | 0.31011 | 700 | 40 | 45.404 | 0
0.83951 | 0.6841 | 0.38611 | 700 | 40 | 43.951 | 0
0.80954 | 0.3941 | 0.47692 | 700 | 40 | 27.587 | 13.367
0.77178 | 0.0566 | 0.52647 | 687.8428 | 40 | 3.962 | 21.0588
0.75376 | 0 | 0.5347 | 673.8548 | 40 | 0 | 21.388
0.7197 | 0 | 0.56437 | 664.4596 | 40 | 0 | 22.5748
0.66779 | 0 | 0.59591 | 661.517 | 40 | 0 | 23.8364
0.6159 | 0 | 0.60045 | 663.945 | 40 | 0 | 24.018
0.57696 | 0 | 0.57595 | 669.287 | 40 | 0 | 23.038
0.55057 | 0 | 0.5242 | 675.198 | 40 | 0 | 20.968
0.5355 | 0 | 0.50312 | 681.7728 | 40 | 0 | 20.1248
0.52693 | 0 | 0.4293 | 686.2518 | 40 | 0 | 17.172
0.52967 | 0 | 0.43373 | 690.634 | 40 | 0 | 17.3492
0.55213 | 0.0008 | 0.42546 | 692.4954 | 40 | 0.056 | 17.0184
0.56507 | 0.071 | 0.39934 | 696.932 | 40 | 4.97 | 15.9736
0.58988 | 0.3014 | 0.33379 | 700 | 40 | 22.056 | -1.1369e-13
0.63219 | 0.5547 | 0.3523 | 700 | 40 | 23.219 | 0
0.67891 | 0.6201 | 0.33151 | 700 | 40 | 27.891 | 0
0.72904 | 0.6754 | 0.26088 | 700 | 40 | 32.904 | 0
0.76868 | 0.7152 | 0.2086 | 700 | 40 | 36.868 | 0
0.79273 | 0.7368 | 0.16739 | 700 | 40 | 39.273 | 0
0.81339 | 0.6448 | 0.19297 | 700 | 40 | 41.339 | 0
0.82736 | 0.4693 | 0.20918 | 698.4822 | 40 | 32.851 | 8.3672
0.83469 | 0.6021 | 0.23931 | 700 | 40 | 42.147 | 2.8398
0.83864 | 0.6756 | 0.26067 | 700 | 40 | 43.864 | 0
0.82449 | 0.6595 | 0.28407 | 700 | 40 | 42.449 | 0
0.79763 | 0.3599 | 0.33114 | 698.6756 | 40 | 25.193 | 13.2456
0.76379 | 0.0485 | 0.41352 | 682.2324 | 40 | 3.395 | 16.5408
0.74362 | 0 | 0.44154 | 665.532 | 40 | 0 | 17.6616
0.70564 | 0 | 0.46886 | 653.7224 | 40 | 0 | 18.7544
0.65296 | 0 | 0.54358 | 650.1696 | 40 | 0 | 21.7432
0.60153 | 0 | 0.55292 | 652.1334 | 40 | 0 | 22.1168
0.56674 | 0 | 0.59306 | 659.1818 | 40 | 0 | 23.7224
0.54142 | 0 | 0.59983 | 669.033 | 40 | 0 | 23.9932
0.52234 | 0 | 0.55863 | 679.1442 | 40 | 0 | 22.3452
0.51538 | 0 | 0.53759 | 689.1098 | 40 | 0 | 21.5036
0.52021 | 0 | 0.48998 | 696.688 | 40 | 0 | 19.5992
0.54096 | 0.0005 | 0.44972 | 700 | 40 | 0.035 | 17.373
0.55686 | 0.0909 | 0.43397 | 700 | 40 | 6.363 | 9.323
0.58258 | 0.3894 | 0.39277 | 700 | 40 | 18.258 | 0
0.62049 | 0.6549 | 0.42455 | 700 | 40 | 22.049 | 0
0.65949 | 0.7586 | 0.38347 | 700 | 40 | 25.949 | 0
0.69585 | 0.7785 | 0.3323 | 700 | 40 | 29.585 | 0
0.72337 | 0.8009 | 0.33495 | 700 | 40 | 32.337 | 0
0.74808 | 0.8167 | 0.35995 | 700 | 40 | 34.808 | 0
0.77278 | 0.8252 | 0.38376 | 700 | 40 | 37.278 | 0
0.79704 | 0.7729 | 0.3962 | 700 | 40 | 39.704 | 0
0.81849 | 0.7131 | 0.415 | 700 | 40 | 41.849 | 0
0.81842 | 0.7183 | 0.42517 | 700 | 40 | 41.842 | 0
0.80191 | 0.5844 | 0.45476 | 700 | 40 | 40.191 | 0
0.77183 | 0.338 | 0.53317 | 700 | 40 | 23.66 | 13.523
0.73831 | 0.0374 | 0.55731 | 691.0794 | 40 | 2.618 | 22.2924
0.71879 | 0 | 0.53875 | 680.7504 | 40 | 0 | 21.55
0.68845 | 0 | 0.54879 | 673.857 | 40 | 0 | 21.9516
0.64473 | 0 | 0.51023 | 669.7932 | 40 | 0 | 20.4092
0.59959 | 0 | 0.5423 | 671.5262 | 40 | 0 | 21.692
0.56627 | 0 | 0.62281 | 679.8116 | 40 | 0 | 24.9124
0.54366 | 0 | 0.58504 | 688.8472 | 40 | 0 | 23.4016
0.52864 | 0 | 0.55689 | 698.2588 | 40 | 0 | 22.2756
0.5178 | 0 | 0.5497 | 700 | 40 | 0 | 13.5212
0.5146 | 0 | 0.51759 | 700 | 40 | 0 | 11.46
0.52126 | 0.0003 | 0.50829 | 700 | 40 | 0.021 | 12.105
0.51835 | 0.0603 | 0.43517 | 700 | 40 | 4.221 | 7.614
0.53863 | 0.271 | 0.35148 | 700 | 40 | 13.863 | 0
0.57668 | 0.6055 | 0.33065 | 700 | 40 | 17.668 | 0
0.62803 | 0.7738 | 0.36652 | 700 | 40 | 22.803 | 0
0.67721 | 0.8187 | 0.36065 | 700 | 40 | 27.721 | 0
0.72056 | 0.8502 | 0.34656 | 700 | 40 | 32.056 | 0
0.76098 | 0.8581 | 0.36371 | 700 | 40 | 36.098 | 0
0.79202 | 0.8318 | 0.39343 | 700 | 40 | 39.202 | 0
0.81323 | 0.8165 | 0.4324 | 700 | 40 | 41.323 | 0
0.82657 | 0.7681 | 0.45906 | 700 | 40 | 42.657 | 0
0.82584 | 0.7419 | 0.46869 | 700 | 40 | 42.584 | 0
0.81405 | 0.6982 | 0.51077 | 700 | 40 | 41.405 | 0
0.78708 | 0.3802 | 0.55929 | 700 | 40 | 26.614 | 12.094
0.74705 | 0.0394 | 0.55648 | 690.3122 | 40 | 2.758 | 22.2592
0.72155 | 0 | 0.53635 | 679.6112 | 40 | 0 | 21.454
0.68942 | 0 | 0.55049 | 672.6888 | 40 | 0 | 22.0196
0.66486 | 0 | 0.58082 | 669.4356 | 40 | 0 | 23.2328
0.62941 | 0 | 0.6231 | 671.4186 | 40 | 0 | 24.924
0.59361 | 0 | 0.61612 | 676.7024 | 40 | 0 | 24.6448
0.56543 | 0 | 0.56871 | 682.9078 | 40 | 0 | 22.7484
0.54665 | 0 | 0.54776 | 690.1532 | 40 | 0 | 21.9104
0.53599 | 0 | 0.52234 | 697.4478 | 40 | 0 | 20.8936
0.53837 | 0 | 0.50027 | 700 | 40 | 0 | 16.3892
0.55419 | 0.0006 | 0.49539 | 700 | 40 | 0.042 | 15.377
0.55976 | 0.0973 | 0.48741 | 700 | 40 | 6.811 | 9.165
0.58497 | 0.35 | 0.44641 | 700 | 40 | 18.497 | 0
0.62771 | 0.5739 | 0.53709 | 700 | 40 | 22.771 | 0
0.67421 | 0.7526 | 0.5018 | 700 | 40 | 27.421 | 0
0.72364 | 0.8383 | 0.44869 | 700 | 40 | 32.364 | 0
0.7674 | 0.8631 | 0.40806 | 700 | 40 | 36.74 | 0
0.80458 | 0.8593 | 0.37243 | 700 | 40 | 40.458 | 0
0.83766 | 0.8538 | 0.36714 | 700 | 40 | 43.766 | 0
0.85954 | 0.8337 | 0.39388 | 700 | 40 | 45.954 | 0
0.87934 | 0.8207 | 0.42352 | 700 | 40 | 47.934 | 0
0.88362 | 0.7686 | 0.44695 | 700 | 40 | 48.362 | 0
0.87447 | 0.604 | 0.46968 | 700 | 40 | 42.28 | 5.167
0.8461 | 0.3131 | 0.49023 | 696.9162 | 40 | 21.917 | 19.6092
0.80367 | 0.0293 | 0.45993 | 676.9974 | 40 | 2.051 | 18.3972
0.77657 | 0 | 0.42157 | 656.2032 | 40 | 0 | 16.8628
0.74134 | 0 | 0.48576 | 641.4996 | 40 | 0 | 19.4304
0.69717 | 0 | 0.51945 | 632.5606 | 40 | 0 | 20.778
0.64641 | 0 | 0.50275 | 628.0296 | 40 | 0 | 20.11
0.6065 | 0 | 0.47741 | 626.476 | 40 | 0 | 19.0964
0.57719 | 0 | 0.46286 | 627.2714 | 40 | 0 | 18.5144
0.55415 | 0 | 0.43778 | 629.3676 | 40 | 0 | 17.5112
0.5386 | 0 | 0.41223 | 631.9968 | 40 | 0 | 16.4892
0.52893 | 0 | 0.42612 | 636.1486 | 40 | 0 | 17.0448
0.52837 | 0.0006 | 0.36706 | 638.036 | 40 | 0.042 | 14.6824
0.52299 | 0.0774 | 0.32594 | 644.1926 | 40 | 5.418 | 13.0376
0.55001 | 0.3812 | 0.2515 | 665.9356 | 40 | 36.744 | 0
0.59779 | 0.6213 | 0.21042 | 698.0644 | 40 | 51.9078 | 0
0.6492 | 0.7217 | 0.15635 | 700 | 40 | 26.8556 | 0
0.70163 | 0.8078 | 0.14627 | 700 | 40 | 30.163 | 0
0.74872 | 0.803 | 0.13672 | 700 | 40 | 34.872 | 0
0.79107 | 0.82 | 0.12548 | 700 | 40 | 39.107 | 0
0.8245 | 0.7562 | 0.16607 | 700 | 40 | 42.45 | 0
0.84768 | 0.6478 | 0.19864 | 700 | 40 | 44.768 | 0
0.85859 | 0.5141 | 0.20913 | 698.4932 | 40 | 35.987 | 8.3652
0.86546 | 0.3315 | 0.21591 | 683.7886 | 40 | 23.205 | 8.6364
0.84452 | 0.226 | 0.27204 | 666.0382 | 40 | 15.82 | 10.8816
0.80183 | 0.1454 | 0.30977 | 648.424 | 40 | 10.178 | 12.3908
0.7591 | 0.0238 | 0.32279 | 627.0916 | 40 | 1.666 | 12.9116
0.73629 | 0 | 0.25857 | 603.8054 | 40 | 0 | 10.3428
0.70012 | 0 | 0.23811 | 583.3178 | 40 | 0 | 9.5244
0.65796 | 0 | 0.22616 | 566.5682 | 40 | 0 | 9.0464
0.61508 | 0 | 0.21013 | 553.4654 | 40 | 0 | 8.4052
0.57823 | 0 | 0.20769 | 543.95 | 40 | 0 | 8.3076
0.54951 | 0 | 0.1802 | 536.207 | 40 | 0 | 7.208
0.53073 | 0 | 0.19694 | 531.0116 | 40 | 0 | 7.8776
0.51585 | 0 | 0.2205 | 528.2466 | 40 | 0 | 8.82
0.50685 | 0 | 0.22385 | 526.5156 | 40 | 0 | 8.954
0.50584 | 0.0004 | 0.19888 | 523.9148 | 40 | 0.028 | 7.9552
0.5028 | 0.0315 | 0.16313 | 522.365 | 40 | 2.205 | 6.5252
0.52955 | 0.1606 | 0.12866 | 525.7984 | 40 | 11.242 | 5.1464
0.58106 | 0.2707 | 0.10899 | 531.001 | 40 | 23.3086 | 0
0.63612 | 0.5703 | 0.1061 | 551.554 | 40 | 44.165 | 0
0.69245 | 0.7975 | 0.09002 | 581.7348 | 40 | 59.4258 | 0
0.74233 | 0.7775 | 0.06419 | 604.4944 | 40 | 56.9926 | 0
0.78232 | 0.5847 | 0.07258 | 610.0946 | 40 | 43.8322 | 0
0.82242 | 0.502 | 0.10928 | 607.3638 | 40 | 35.14 | 4.3712
0.84957 | 0.4379 | 0.14015 | 598.6658 | 40 | 30.653 | 5.606
0.86833 | 0.3083 | 0.24823 | 583.343 | 40 | 21.581 | 9.9292
0.87757 | 0.2595 | 0.30775 | 566.061 | 40 | 18.165 | 12.31
0.87037 | 0.2356 | 0.3411 | 549.16 | 40 | 16.492 | 13.644
0.85026 | 0.1232 | 0.37309 | 527.6816 | 40 | 8.624 | 14.9236
0.81217 | 0.0281 | 0.37338 | 503.3668 | 40 | 1.967 | 14.9352
0.79059 | 0 | 0.27121 | 475.1562 | 40 | 0 | 10.8484
0.75177 | 0 | 0.28444 | 451.3568 | 40 | 0 | 11.3776
0.70112 | 0 | 0.22583 | 430.278 | 40 | 0 | 9.0332
0.65061 | 0 | 0.21922 | 413.9858 | 40 | 0 | 8.7688
0.6083 | 0 | 0.23079 | 402.3874 | 40 | 0 | 9.2316
0.57705 | 0 | 0.25071 | 394.7108 | 40 | 0 | 10.0284
0.55577 | 0 | 0.28448 | 390.513 | 40 | 0 | 11.3792
0.54668 | 0 | 0.28857 | 387.3878 | 40 | 0 | 11.5428
0.5498 | 0 | 0.28667 | 383.8746 | 40 | 0 | 11.4668
0.56781 | 0.0004 | 0.29031 | 378.734 | 40 | 0.028 | 11.6124
0.58226 | 0.0965 | 0.25431 | 377.4354 | 40 | 6.755 | 10.1724
0.61239 | 0.4743 | 0.20554 | 397.619 | 40 | 41.4226 | 0
0.65534 | 0.6898 | 0.20293 | 428.4882 | 40 | 56.4032 | 0
0.7093 | 0.7533 | 0.22257 | 459.192 | 40 | 61.6338 | 0
0.76269 | 0.7473 | 0.20508 | 483.4372 | 40 | 60.5142 | 0
0.811 | 0.7398 | 0.19132 | 501.776 | 40 | 59.4388 | 0
0.85307 | 0.6478 | 0.21248 | 510.3142 | 40 | 53.8452 | 0
0.88606 | 0.6376 | 0.22968 | 515.5274 | 40 | 44.632 | 9.1872
0.90499 | 0.6225 | 0.27357 | 519.5462 | 40 | 43.575 | 10.9428
0.9053 | 0.5265 | 0.34007 | 519.474 | 40 | 36.855 | 13.6028
0.89301 | 0.491 | 0.37942 | 519.7198 | 40 | 34.37 | 15.1768
0.86135 | 0.4733 | 0.40889 | 523.0714 | 40 | 33.131 | 16.3556
0.83055 | 0.2905 | 0.47502 | 519.3522 | 40 | 20.335 | 19.0008
0.79457 | 0.0426 | 0.3981 | 498.8012 | 40 | 2.982 | 15.924
0.77372 | 0 | 0.44274 | 479.1388 | 40 | 0 | 17.7096
0.73707 | 0 | 0.52589 | 466.4674 | 40 | 0 | 21.0356
0.68675 | 0 | 0.57004 | 460.594 | 40 | 0 | 22.8016
0.63723 | 0 | 0.61137 | 461.3258 | 40 | 0 | 24.4548
0.59942 | 0 | 0.63265 | 466.6898 | 40 | 0 | 25.306
0.57224 | 0 | 0.62298 | 474.385 | 40 | 0 | 24.9192
0.55253 | 0 | 0.5764 | 482.188 | 40 | 0 | 23.056
0.54803 | 0 | 0.55991 | 489.7814 | 40 | 0 | 22.3964
0.55298 | 0 | 0.56458 | 497.0666 | 40 | 0 | 22.5832
0.57598 | 0.0004 | 0.55681 | 501.769 | 40 | 0.028 | 22.2724
0.58907 | 0.0954 | 0.53288 | 510.8552 | 40 | 6.678 | 21.3152
0.6142 | 0.4911 | 0.46088 | 542.2474 | 40 | 52.8122 | 5.6843e-14
0.65262 | 0.7087 | 0.43811 | 584.1188 | 40 | 67.1334 | 0
0.70259 | 0.7936 | 0.37442 | 624.3886 | 40 | 70.5288 | 0
0.7527 | 0.8338 | 0.26241 | 657.981 | 40 | 68.8624 | 0
0.79964 | 0.8546 | 0.16863 | 684.5842 | 40 | 66.5672 | 0
0.84543 | 0.8217 | 0.11391 | 700 | 40 | 59.9588 | 0
0.88606 | 0.8092 | 0.11044 | 700 | 40 | 48.606 | 0
0.91179 | 0.7633 | 0.13189 | 700 | 40 | 51.179 | 0
0.92125 | 0.6125 | 0.16458 | 697.3332 | 40 | 42.875 | 6.5832
0.92499 | 0.5234 | 0.19917 | 689.439 | 40 | 36.638 | 7.9668
0.9202 | 0.5681 | 0.24641 | 687.0424 | 40 | 39.767 | 9.8564
0.9035 | 0.3189 | 0.313 | 671.5354 | 40 | 22.323 | 12.52
0.86876 | 0.0555 | 0.36665 | 643.2104 | 40 | 3.885 | 14.666
0.84351 | 0 | 0.40413 | 615.0246 | 40 | 0 | 16.1652
0.80075 | 0 | 0.43993 | 592.5468 | 40 | 0 | 17.5972
0.74089 | 0 | 0.46931 | 577.2302 | 40 | 0 | 18.7724
0.68448 | 0 | 0.45166 | 566.8486 | 40 | 0 | 18.0664
0.63953 | 0 | 0.43517 | 560.3024 | 40 | 0 | 17.4068
0.60572 | 0 | 0.38454 | 555.112 | 40 | 0 | 15.3816
0.5827 | 0 | 0.35536 | 551.0564 | 40 | 0 | 14.2144
0.56926 | 0 | 0.35755 | 548.4324 | 40 | 0 | 14.302
0.57002 | 0 | 0.36441 | 546.0068 | 40 | 0 | 14.5764
0.58718 | 0.0005 | 0.35681 | 541.5962 | 40 | 0.035 | 14.2724
0.59484 | 0.1252 | 0.32771 | 543.9846 | 40 | 8.764 | 13.1084
0.62528 | 0.562 | 0.25968 | 571.1838 | 40 | 49.7272 | 0
0.67058 | 0.7903 | 0.18925 | 607.0168 | 40 | 62.891 | 0
0.72722 | 0.8503 | 0.13437 | 639.1906 | 40 | 64.8958 | 0
0.78506 | 0.864 | 0.09014 | 664.7702 | 40 | 64.0856 | 0
0.84148 | 0.8639 | 0.09184 | 684.7688 | 40 | 64.1466 | 0
0.88989 | 0.8535 | 0.08452 | 698.9056 | 40 | 63.1258 | 0
0.9218 | 0.8501 | 0.12428 | 700 | 40 | 53.2744 | 0
0.94003 | 0.8089 | 0.16611 | 700 | 40 | 54.003 | 0
0.94753 | 0.7565 | 0.1759 | 700 | 40 | 52.955 | 1.798
0.94286 | 0.7415 | 0.17169 | 700 | 40 | 51.905 | 2.381
0.92474 | 0.6368 | 0.18586 | 699.5364 | 40 | 44.576 | 7.4344
0.873 | 0.3484 | 0.23331 | 685.9568 | 40 | 24.388 | 9.3324
0.83194 | 0.0482 | 0.27568 | 657.164 | 40 | 3.374 | 11.0272
0.80357 | 0 | 0.28849 | 628.3466 | 40 | 0 | 11.5396
0.75494 | 0 | 0.2813 | 604.1046 | 40 | 0 | 11.252
0.69699 | 0 | 0.282 | 585.6856 | 40 | 0 | 11.28
0.64261 | 0 | 0.29779 | 573.3362 | 40 | 0 | 11.9116
0.60015 | 0 | 0.27018 | 564.1284 | 40 | 0 | 10.8072
0.56749 | 0 | 0.26782 | 558.0922 | 40 | 0 | 10.7128
0.54595 | 0 | 0.20748 | 551.7964 | 40 | 0 | 8.2992
0.53479 | 0 | 0.16644 | 544.975 | 40 | 0 | 6.6576
0.53738 | 0 | 0.19975 | 539.227 | 40 | 0 | 7.99
0.55392 | 0.0005 | 0.17677 | 530.9408 | 40 | 0.035 | 7.0708
0.56613 | 0.0859 | 0.15578 | 526.572 | 40 | 6.013 | 6.2312
0.58735 | 0.4778 | 0.16991 | 548.0794 | 40 | 40.2424 | 0
0.61906 | 0.7034 | 0.12122 | 580.2602 | 40 | 54.0868 | 0
0.67062 | 0.7845 | 0.09093 | 611.7504 | 40 | 58.5522 | 0
0.72926 | 0.8414 | 0.06047 | 640.1412 | 40 | 61.3168 | 0
0.78319 | 0.853 | 0.04096 | 663.1706 | 40 | 61.3484 | 0
0.83255 | 0.8494 | 0.03381 | 680.726 | 40 | 60.8104 | 0
0.87222 | 0.8338 | 0.04042 | 693.4868 | 40 | 59.9828 | 0
0.8998 | 0.7935 | 0.07605 | 700 | 40 | 56.4932 | 0
0.91446 | 0.7263 | 0.11486 | 700 | 40 | 50.841 | 0.605
0.91928 | 0.6758 | 0.12924 | 700 | 40 | 47.306 | 4.622
0.91268 | 0.6104 | 0.13168 | 696.7272 | 40 | 42.728 | 5.2672
0.88648 | 0.291 | 0.1297 | 673.6372 | 40 | 20.37 | 5.188
0.84853 | 0.013 | 0.10626 | 633.9446 | 40 | 0.91 | 4.2504
0.82364 | 0 | 0.11044 | 595.9982 | 40 | 0 | 4.4176
0.78224 | 0 | 0.11589 | 562.4098 | 40 | 0 | 4.6356
0.72341 | 0 | 0.10874 | 534.4184 | 40 | 0 | 4.3496
0.66789 | 0 | 0.08324 | 510.959 | 40 | 0 | 3.3296
0.6234 | 0 | 0.07803 | 491.7402 | 40 | 0 | 3.1212
0.58965 | 0 | 0.0589 | 475.1312 | 40 | 0 | 2.356
0.56293 | 0 | 0.05803 | 461.1594 | 40 | 0 | 2.3212
0.55009 | 0 | 0.0584 | 448.4864 | 40 | 0 | 2.336
0.54887 | 0 | 0.06832 | 436.3322 | 40 | 0 | 2.7328
0.56343 | 0.0006 | 0.07878 | 423.1824 | 40 | 0.042 | 3.1512
0.57422 | 0.1052 | 0.07564 | 416.15 | 40 | 7.364 | 3.0256
0.60117 | 0.5129 | 0.05728 | 434.2272 | 40 | 38.1942 | 0
0.64568 | 0.7539 | 0.02203 | 463.3134 | 40 | 53.6542 | 0
0.70031 | 0.8255 | 0.0179 | 491.7834 | 40 | 58.501 | 0
0.75489 | 0.8372 | 0.01352 | 515.4392 | 40 | 59.1448 | -5.6843e-14
0.79812 | 0.8123 | 0.015 | 533.0882 | 40 | 57.461 | 0
0.8364 | 0.7157 | 0.03604 | 540.9888 | 40 | 51.5406 | 0
0.86725 | 0.7119 | 0.06158 | 546.56 | 40 | 52.2962 | 0
0.88712 | 0.6928 | 0.10399 | 550.5036 | 40 | 48.496 | 4.1596
0.89772 | 0.5766 | 0.11192 | 545.5704 | 40 | 40.362 | 4.4768
0.89536 | 0.4224 | 0.14024 | 531.212 | 40 | 29.568 | 5.6096
0.88295 | 0.2717 | 0.1323 | 507.228 | 40 | 19.019 | 5.292
0.8496 | 0.1643 | 0.11746 | 478.4674 | 40 | 11.501 | 4.6984
0.81118 | 0.025 | 0.10721 | 443.3878 | 40 | 1.75 | 4.2884
0.7837 | 0 | 0.12279 | 409.9294 | 40 | 0 | 4.9116
0.745 | 0 | 0.15507 | 381.6322 | 40 | 0 | 6.2028
0.6945 | 0 | 0.16933 | 358.9554 | 40 | 0 | 6.7732
0.64006 | 0 | 0.19397 | 342.7082 | 40 | 0 | 7.7588
0.59931 | 0 | 0.18272 | 330.086 | 40 | 0 | 7.3088
0.56639 | 0 | 0.1728 | 320.359 | 40 | 0 | 6.912
0.54016 | 0 | 0.15929 | 312.7146 | 40 | 0 | 6.3716
0.52677 | 0 | 0.12792 | 305.1544 | 40 | 0 | 5.1168
0.52151 | 0 | 0.09547 | 296.8222 | 40 | 0 | 3.8188
0.52393 | 0.0006 | 0.07142 | 287.328 | 40 | 0.042 | 2.8568
0.52472 | 0.0881 | 0.04881 | 282.9754 | 40 | 6.167 | 1.9524
0.55447 | 0.345 | 0.03786 | 293.1928 | 40 | 25.6644 | 0
0.60606 | 0.6007 | 0.01306 | 315.1582 | 40 | 42.5714 | 0
0.66502 | 0.7538 | 0.01083 | 341.8554 | 40 | 53.1992 | 0
0.72014 | 0.777 | 0.01835 | 364.9654 | 40 | 55.124 | 0
0.76379 | 0.7691 | 0.06034 | 384.837 | 40 | 56.2506 | 0
0.79814 | 0.7762 | 0.09692 | 403.2338 | 40 | 58.2108 | 0
0.81468 | 0.7478 | 0.13614 | 419.5574 | 40 | 57.7916 | 0
0.826 | 0.6887 | 0.14362 | 430.9112 | 40 | 53.9538 | 0
0.83755 | 0.6986 | 0.16255 | 442.5602 | 40 | 55.404 | 0
0.84384 | 0.6536 | 0.16962 | 450.713 | 40 | 52.5368 | 0
0.83204 | 0.5299 | 0.15656 | 450.8644 | 40 | 37.093 | 6.2624
0.81135 | 0.2366 | 0.14788 | 432.2066 | 40 | 16.562 | 5.9152
0.778 | 0.0206 | 0.15106 | 401.891 | 40 | 1.442 | 6.0424
0.75828 | 0 | 0.169 | 372.823 | 40 | 0 | 6.76
0.72991 | 0 | 0.19074 | 347.4616 | 40 | 0 | 7.6296
0.68904 | 0 | 0.19595 | 326.3956 | 40 | 0 | 7.838
0.64442 | 0 | 0.17285 | 308.8676 | 40 | 0 | 6.914
0.60451 | 0 | 0.14602 | 294.2574 | 40 | 0 | 5.8408
0.57331 | 0 | 0.13309 | 282.25 | 40 | 0 | 5.3236
0.55029 | 0 | 0.12131 | 272.0734 | 40 | 0 | 4.8524
0.53556 | 0 | 0.10432 | 262.6902 | 40 | 0 | 4.1728
0.5274 | 0 | 0.08022 | 253.159 | 40 | 0 | 3.2088
0.52633 | 0.0003 | 0.06439 | 243.1226 | 40 | 0.021 | 2.5756
0.52089 | 0.1112 | 0.04629 | 240.6692 | 40 | 7.784 | 1.8516
0.5431 | 0.5472 | 0.03968 | 266.2504 | 40 | 39.8912 | 0
0.58415 | 0.7794 | 0.03021 | 303.6018 | 40 | 55.7664 | 0
0.63197 | 0.8252 | 0.03488 | 339.564 | 40 | 59.1592 | 0
0.67629 | 0.7946 | 0.04207 | 369.2398 | 40 | 57.3048 | -5.6843e-14
0.71382 | 0.8397 | 0.04823 | 398.566 | 40 | 60.7082 | 0
0.74548 | 0.8523 | 0.05154 | 425.7406 | 40 | 61.7226 | 0
0.77237 | 0.8604 | 0.07626 | 451.782 | 40 | 63.2784 | 5.6843e-14
0.79429 | 0.8519 | 0.11122 | 476.4348 | 40 | 64.0818 | 0
0.80859 | 0.8322 | 0.14156 | 499.4922 | 40 | 63.9164 | 0
0.81171 | 0.7946 | 0.15499 | 520.1428 | 40 | 61.8216 | -5.6843e-14
0.81087 | 0.6956 | 0.17834 | 534.8814 | 40 | 55.8256 | 0
0.79698 | 0.4113 | 0.19562 | 531.7992 | 40 | 28.791 | 7.8248
0.76685 | 0.0577 | 0.19149 | 506.8128 | 40 | 4.039 | 7.6596
0.74898 | 0 | 0.18537 | 479.3296 | 40 | 0 | 7.4148
0.71901 | 0 | 0.18049 | 454.6482 | 40 | 0 | 7.2196
0.66943 | 0 | 0.18702 | 435.186 | 40 | 0 | 7.4808
0.61806 | 0 | 0.18566 | 420.8064 | 40 | 0 | 7.4264
0.58243 | 0 | 0.20946 | 410.9418 | 40 | 0 | 8.3784
0.55588 | 0 | 0.22496 | 404.3522 | 40 | 0 | 8.9984
0.54127 | 0 | 0.20818 | 398.5524 | 40 | 0 | 8.3272
0.53368 | 0 | 0.16933 | 391.9576 | 40 | 0 | 6.7732
0.54159 | 0 | 0.15082 | 383.8314 | 40 | 0 | 6.0328
0.56317 | 0.0005 | 0.1247 | 372.5374 | 40 | 0.035 | 4.988
0.57873 | 0.106 | 0.11804 | 366.806 | 40 | 7.42 | 4.7216
0.60538 | 0.5169 | 0.09237 | 386.1458 | 40 | 39.8778 | 0
0.64623 | 0.7503 | 0.08481 | 417.4362 | 40 | 55.9134 | 0
0.69727 | 0.8468 | 0.09456 | 450.7676 | 40 | 63.0584 | 0
0.75134 | 0.8437 | 0.07704 | 477.7742 | 40 | 62.1406 | 0
0.79871 | 0.827 | 0.06968 | 498.5804 | 40 | 60.6772 | 0
0.83427 | 0.8429 | 0.08431 | 517.5288 | 40 | 62.3754 | 0
0.86534 | 0.8484 | 0.1051 | 534.5868 | 40 | 63.592 | 0
0.88677 | 0.8094 | 0.11821 | 547.2962 | 40 | 61.3864 | 0
0.90152 | 0.8127 | 0.13982 | 559.626 | 40 | 62.4818 | 0
0.90511 | 0.7851 | 0.15793 | 570.3892 | 40 | 61.2742 | 0
0.89313 | 0.6978 | 0.17471 | 576.9106 | 40 | 48.846 | 6.9884
0.87784 | 0.4076 | 0.20062 | 565.6834 | 40 | 28.532 | 8.0248
0.84394 | 0.0451 | 0.26394 | 535.004 | 40 | 3.157 | 10.5576
0.81982 | 0 | 0.32656 | 506.0844 | 40 | 0 | 13.0624
0.78118 | 0 | 0.40128 | 484.0176 | 40 | 0 | 16.0512
0.72607 | 0 | 0.44861 | 469.355 | 40 | 0 | 17.9444
0.67497 | 0 | 0.4732 | 460.786 | 40 | 0 | 18.928
0.63652 | 0 | 0.47481 | 456.1264 | 40 | 0 | 18.9924
0.60807 | 0 | 0.45675 | 453.5894 | 40 | 0 | 18.27
0.58654 | 0 | 0.42996 | 452.1338 | 40 | 0 | 17.1984
0.57857 | 0 | 0.45162 | 452.3416 | 40 | 0 | 18.0648
0.58507 | 0 | 0.46348 | 452.3738 | 40 | 0 | 18.5392
0.60742 | 0.0002 | 0.46146 | 450.1042 | 40 | 0.014 | 18.4584
0.62034 | 0.0978 | 0.4653 | 453.5282 | 40 | 6.846 | 18.612
0.64672 | 0.4864 | 0.40029 | 478.9158 | 40 | 50.0596 | 0
0.68788 | 0.7364 | 0.42038 | 518.491 | 40 | 68.3632 | 0
0.73914 | 0.8265 | 0.43691 | 559.9084 | 40 | 75.3314 | 0
0.79307 | 0.8475 | 0.37128 | 594.7776 | 40 | 74.1762 | 0
0.84229 | 0.8429 | 0.32689 | 622.6272 | 40 | 72.0786 | 0
0.88168 | 0.8544 | 0.30672 | 646.536 | 40 | 72.0768 | 0
0.91705 | 0.8538 | 0.33354 | 667.9386 | 40 | 73.1076 | 0
0.9382 | 0.8117 | 0.36995 | 685.7356 | 40 | 71.617 | 0
0.94246 | 0.7757 | 0.40244 | 700 | 40 | 68.5104 | 0
0.93866 | 0.7084 | 0.43629 | 700 | 40 | 49.588 | 4.278
0.92581 | 0.5779 | 0.46849 | 700 | 40 | 40.453 | 12.128
0.90109 | 0.3549 | 0.48022 | 693.9428 | 40 | 24.843 | 19.2088
0.8668 | 0.03 | 0.49618 | 669.21 | 40 | 2.1 | 19.8472
0.84065 | 0 | 0.47857 | 644.2878 | 40 | 0 | 19.1428
0.79702 | 0 | 0.53428 | 625.957 | 40 | 0 | 21.3712
0.73993 | 0 | 0.55722 | 614.2528 | 40 | 0 | 22.2888
0.68837 | 0 | 0.58595 | 608.8538 | 40 | 0 | 23.438
0.64787 | 0 | 0.58863 | 607.612 | 40 | 0 | 23.5452
0.61773 | 0 | 0.59438 | 609.6142 | 40 | 0 | 23.7752
0.5986 | 0 | 0.59868 | 613.7014 | 40 | 0 | 23.9472
0.58953 | 0 | 0.60434 | 618.922 | 40 | 0 | 24.1736
0.59032 | 0 | 0.59277 | 623.6008 | 40 | 0 | 23.7108
0.60793 | 0.0005 | 0.56565 | 625.4688 | 40 | 0.035 | 22.626
0.61935 | 0.0864 | 0.54342 | 631.3186 | 40 | 6.048 | 21.7368
0.64461 | 0.4521 | 0.49064 | 658.1302 | 40 | 51.2726 | 0
0.68317 | 0.6597 | 0.58467 | 699.379 | 40 | 69.5658 | 0
0.73401 | 0.767 | 0.61484 | 700 | 40 | 34.022 | -1.1369e-13
0.78625 | 0.8319 | 0.55553 | 700 | 40 | 38.625 | 0
0.83217 | 0.8379 | 0.52635 | 700 | 40 | 43.217 | 0
0.87365 | 0.8496 | 0.53391 | 700 | 40 | 47.365 | 0
0.90114 | 0.8466 | 0.55015 | 700 | 40 | 50.114 | 0
0.92043 | 0.727 | 0.55739 | 700 | 40 | 50.89 | 1.153
0.9322 | 0.6765 | 0.59037 | 700 | 40 | 47.355 | 5.865
0.93512 | 0.6225 | 0.63096 | 700 | 40 | 43.575 | 9.937
0.92668 | 0.4906 | 0.65418 | 700 | 40 | 34.342 | 18.326
0.90318 | 0.2379 | 0.67902 | 693.4958 | 40 | 16.653 | 27.1608
0.86208 | 0.0177 | 0.65724 | 674.8164 | 40 | 1.239 | 26.2896
0.83585 | 0 | 0.60244 | 655.329 | 40 | 0 | 24.0976
0.79446 | 0 | 0.62596 | 640.9214 | 40 | 0 | 25.0384
0.73994 | 0 | 0.6534 | 633.0634 | 40 | 0 | 26.136
0.68674 | 0 | 0.65048 | 630.4086 | 40 | 0 | 26.0192
0.64758 | 0 | 0.67322 | 632.5794 | 40 | 0 | 26.9288
0.61763 | 0 | 0.71936 | 639.5908 | 40 | 0 | 28.7744
0.59314 | 0 | 0.70883 | 648.63 | 40 | 0 | 28.3532
0.58024 | 0 | 0.69076 | 658.2364 | 40 | 0 | 27.6304
0.58501 | 0 | 0.66884 | 666.489 | 40 | 0 | 26.7536
0.6034 | 0.0004 | 0.64602 | 672.0178 | 40 | 0.028 | 25.8408
0.61114 | 0.0949 | 0.62868 | 682.694 | 40 | 6.643 | 25.1472
0.63997 | 0.4881 | 0.59049 | 700 | 40 | 41.303 | 0
0.68248 | 0.6678 | 0.66716 | 700 | 40 | 28.248 | 0
0.73026 | 0.7818 | 0.66613 | 700 | 40 | 33.026 | 0
0.77682 | 0.8481 | 0.63122 | 700 | 40 | 37.682 | 0
0.8253 | 0.8842 | 0.6127 | 700 | 40 | 42.53 | 0
0.86607 | 0.9017 | 0.59025 | 700 | 40 | 46.607 | 0
0.90306 | 0.8889 | 0.59045 | 700 | 40 | 50.306 | 0
0.92777 | 0.8771 | 0.59787 | 700 | 40 | 52.777 | 0
0.94056 | 0.8615 | 0.60586 | 700 | 40 | 54.056 | 0
0.93763 | 0.8246 | 0.60053 | 700 | 40 | 53.763 | 0
0.92746 | 0.7136 | 0.6277 | 700 | 40 | 49.952 | 2.794
0.90564 | 0.3822 | 0.66171 | 700 | 40 | 26.754 | 23.81
0.86642 | 0.0427 | 0.66347 | 682.8858 | 40 | 2.989 | 26.5388
0.84061 | 0 | 0.65573 | 665.054 | 40 | 0 | 26.2292
0.80329 | 0 | 0.696 | 652.565 | 40 | 0 | 27.84
0.74633 | 0 | 0.71805 | 646.654 | 40 | 0 | 28.722
0.69315 | 0 | 0.72079 | 646.1706 | 40 | 0 | 28.8316
0.65274 | 0 | 0.71149 | 649.3562 | 40 | 0 | 28.4596
0.61931 | 0 | 0.70776 | 655.7356 | 40 | 0 | 28.3104
0.59908 | 0 | 0.69392 | 663.5844 | 40 | 0 | 27.7568
0.58431 | 0 | 0.68338 | 672.4886 | 40 | 0 | 27.3352
0.58341 | 0 | 0.65708 | 680.4308 | 40 | 0 | 26.2832
0.59795 | 0.0004 | 0.64536 | 686.4782 | 40 | 0.028 | 25.8144
0.60575 | 0.0929 | 0.62266 | 697.3126 | 40 | 6.503 | 24.9064
0.63302 | 0.4905 | 0.58164 | 700 | 40 | 25.9894 | 0
0.67767 | 0.7319 | 0.64897 | 700 | 40 | 27.767 | 0
0.72922 | 0.813 | 0.66306 | 700 | 40 | 32.922 | 0
0.77838 | 0.866 | 0.63971 | 700 | 40 | 37.838 | 0
0.82377 | 0.8874 | 0.62176 | 700 | 40 | 42.377 | 0
0.86649 | 0.9027 | 0.60815 | 700 | 40 | 46.649 | 0
0.90216 | 0.8876 | 0.59287 | 700 | 40 | 50.216 | 0
0.92383 | 0.8744 | 0.5755 | 700 | 40 | 52.383 | 0
0.93787 | 0.8587 | 0.57628 | 700 | 40 | 53.787 | 0
0.9331 | 0.8404 | 0.58972 | 700 | 40 | 53.31 | 0
0.9255 | 0.7544 | 0.63884 | 700 | 40 | 52.55 | 0
0.89709 | 0.4352 | 0.65864 | 700 | 40 | 30.464 | 19.245
0.85726 | 0.0519 | 0.64507 | 683.7098 | 40 | 3.633 | 25.8028
0.82846 | 0 | 0.61078 | 665.295 | 40 | 0 | 24.4312
0.79124 | 0 | 0.6547 | 652.359 | 40 | 0 | 26.188
0.74287 | 0 | 0.69752 | 645.9728 | 40 | 0 | 27.9008
0.69374 | 0 | 0.72682 | 645.6716 | 40 | 0 | 29.0728
0.65308 | 0 | 0.72325 | 649.2936 | 40 | 0 | 28.93
0.62258 | 0 | 0.71817 | 655.7624 | 40 | 0 | 28.7268
0.59936 | 0 | 0.70826 | 664.1568 | 40 | 0 | 28.3304
0.5825 | 0 | 0.68752 | 673.4076 | 40 | 0 | 27.5008
0.57162 | 0 | 0.66765 | 682.9516 | 40 | 0 | 26.706
0.57343 | 0.0004 | 0.6411 | 691.2806 | 40 | 0.028 | 25.644
0.56707 | 0.0871 | 0.60033 | 700 | 40 | 6.097 | 19.3294
0.593 | 0.5044 | 0.53628 | 700 | 40 | 19.3 | 0
0.64597 | 0.7743 | 0.58771 | 700 | 40 | 24.597 | 0
0.69901 | 0.8774 | 0.58763 | 700 | 40 | 29.901 | 0
0.7511 | 0.8991 | 0.55058 | 700 | 40 | 35.11 | 0
0.80206 | 0.9056 | 0.5489 | 700 | 40 | 40.206 | 0
0.84007 | 0.8869 | 0.55657 | 700 | 40 | 44.007 | 0
0.87002 | 0.8695 | 0.53383 | 700 | 40 | 47.002 | 0
0.89111 | 0.8548 | 0.52637 | 700 | 40 | 49.111 | 0
0.90645 | 0.8543 | 0.53067 | 700 | 40 | 50.645 | 0
0.90704 | 0.7805 | 0.51981 | 700 | 40 | 50.704 | 0
0.89881 | 0.6162 | 0.54931 | 700 | 40 | 43.134 | 6.747
0.87282 | 0.3405 | 0.59316 | 700 | 40 | 23.835 | 23.447
0.83429 | 0.0408 | 0.60684 | 683.7006 | 40 | 2.856 | 24.2736
0.80994 | 0 | 0.63815 | 668.2326 | 40 | 0 | 25.526
0.77217 | 0 | 0.68814 | 658.5412 | 40 | 0 | 27.5256
0.72615 | 0 | 0.73124 | 655.1758 | 40 | 0 | 29.2496
0.67881 | 0 | 0.70912 | 655.6596 | 40 | 0 | 28.3648
0.64028 | 0 | 0.67793 | 658.7488 | 40 | 0 | 27.1172
0.61068 | 0 | 0.66683 | 664.354 | 40 | 0 | 26.6732
0.58513 | 0 | 0.63327 | 671.1718 | 40 | 0 | 25.3308
0.56636 | 0 | 0.62651 | 679.5962 | 40 | 0 | 25.0604
0.55096 | 0 | 0.58275 | 687.8102 | 40 | 0 | 23.31
0.54582 | 0.0003 | 0.50785 | 693.5632 | 40 | 0.021 | 20.314
0.53643 | 0.0764 | 0.4647 | 700 | 40 | 5.348 | 14.7318
0.55887 | 0.4475 | 0.4236 | 700 | 40 | 15.887 | 0
0.60862 | 0.6942 | 0.4329 | 700 | 40 | 20.862 | 0
0.66362 | 0.8082 | 0.44434 | 700 | 40 | 26.362 | 0
0.71715 | 0.8071 | 0.40139 | 700 | 40 | 31.715 | 0
0.76997 | 0.8386 | 0.326 | 700 | 40 | 36.997 | 0
0.81593 | 0.8645 | 0.29035 | 700 | 40 | 41.593 | 0
0.84348 | 0.8804 | 0.28736 | 700 | 40 | 44.348 | 0
0.86407 | 0.8727 | 0.30527 | 700 | 40 | 46.407 | 0
0.87832 | 0.836 | 0.3151 | 700 | 40 | 47.832 | 0
0.88092 | 0.7809 | 0.32579 | 700 | 40 | 48.092 | 0
0.8775 | 0.682 | 0.30904 | 700 | 40 | 47.74 | 0.01
0.85726 | 0.3798 | 0.33075 | 694.09 | 40 | 26.586 | 13.23
0.82537 | 0.0413 | 0.33235 | 667.738 | 40 | 2.891 | 13.294
0.80674 | 0 | 0.35599 | 641.3036 | 40 | 0 | 14.2396
0.76778 | 0 | 0.42065 | 621.3516 | 40 | 0 | 16.826
0.71424 | 0 | 0.44856 | 607.87 | 40 | 0 | 17.9424
0.66366 | 0 | 0.43106 | 598.7464 | 40 | 0 | 17.2424
0.62025 | 0 | 0.40029 | 592.733 | 40 | 0 | 16.0116
0.59127 | 0 | 0.40205 | 589.688 | 40 | 0 | 16.082
0.57143 | 0 | 0.37611 | 587.5894 | 40 | 0 | 15.0444
0.564 | 0 | 0.32215 | 584.0754 | 40 | 0 | 12.886
0.56714 | 0 | 0.28187 | 578.6362 | 40 | 0 | 11.2748
0.58609 | 0.0002 | 0.28736 | 571.5356 | 40 | 0.014 | 11.4944
0.60297 | 0.0689 | 0.26462 | 566.6464 | 40 | 4.823 | 10.5848
0.62646 | 0.4278 | 0.22311 | 582.8708 | 40 | 38.8704 | 0
0.66561 | 0.6618 | 0.21553 | 611.257 | 40 | 54.9472 | 0
0.71139 | 0.7299 | 0.22413 | 640.1762 | 40 | 60.0582 | 0
0.7596 | 0.8046 | 0.21684 | 669.2118 | 40 | 64.9956 | 0
0.80439 | 0.7147 | 0.25638 | 689.057 | 40 | 60.2842 | 0
0.84148 | 0.6969 | 0.32407 | 700 | 40 | 55.091 | 0
0.86296 | 0.5951 | 0.34526 | 700 | 40 | 41.657 | 4.639
0.87914 | 0.6491 | 0.3623 | 700 | 40 | 45.437 | 2.477
0.88381 | 0.633 | 0.3453 | 700 | 40 | 44.31 | 4.071
0.8775 | 0.5236 | 0.41639 | 700 | 40 | 36.652 | 11.098
0.86527 | 0.4951 | 0.46232 | 700 | 40 | 34.657 | 11.87
0.84261 | 0.217 | 0.46699 | 689.6086 | 40 | 15.19 | 18.6796
0.80625 | 0.0115 | 0.44134 | 667.4422 | 40 | 0.805 | 17.6536
0.78631 | 0 | 0.33251 | 642.1116 | 40 | 0 | 13.3004
0.74049 | 0 | 0.2781 | 619.1866 | 40 | 0 | 11.124
0.68666 | 0 | 0.2781 | 601.6446 | 40 | 0 | 11.124
0.63303 | 0 | 0.2756 | 589.3656 | 40 | 0 | 11.024
0.59404 | 0 | 0.25167 | 580.0284 | 40 | 0 | 10.0668
0.569 | 0 | 0.23827 | 572.6592 | 40 | 0 | 9.5308
0.5505 | 0 | 0.21946 | 566.3876 | 40 | 0 | 8.7784
0.54037 | 0 | 0.20406 | 560.513 | 40 | 0 | 8.1624
0.54072 | 0 | 0.17263 | 553.3462 | 40 | 0 | 6.9052
0.56077 | 0.0003 | 0.14026 | 542.9006 | 40 | 0.021 | 5.6104
0.57237 | 0.0575 | 0.13411 | 535.053 | 40 | 4.025 | 5.3644
0.59213 | 0.432 | 0.11379 | 550.6316 | 40 | 34.7916 | 0
0.62159 | 0.6597 | 0.12051 | 579.472 | 40 | 50.9994 | 0
0.656 | 0.6777 | 0.13505 | 606.713 | 40 | 52.841 | 0
0.69098 | 0.7518 | 0.14202 | 635.9218 | 40 | 58.3068 | 0
0.72131 | 0.7936 | 0.15284 | 665.4564 | 40 | 61.6656 | 0
0.7494 | 0.7817 | 0.16325 | 691.7654 | 40 | 61.249 | -1.1369e-13
0.77065 | 0.8235 | 0.18549 | 700 | 40 | 45.2996 | 0
0.79034 | 0.8423 | 0.21135 | 700 | 40 | 39.034 | 0
0.80922 | 0.821 | 0.24696 | 700 | 40 | 40.922 | 0
0.81379 | 0.8017 | 0.24905 | 700 | 40 | 41.379 | 0
0.80475 | 0.7026 | 0.22762 | 700 | 40 | 40.475 | 0
0.78275 | 0.3604 | 0.21217 | 695.4398 | 40 | 25.228 | 8.4868
0.74737 | 0.041 | 0.17595 | 670.6108 | 40 | 2.87 | 7.038
0.72573 | 0 | 0.15358 | 644.181 | 40 | 0 | 6.1432
0.68538 | 0 | 0.17119 | 622.4906 | 40 | 0 | 6.8476
0.63184 | 0 | 0.19402 | 607.0674 | 40 | 0 | 7.7608
0.58247 | 0 | 0.20557 | 597.0432 | 40 | 0 | 8.2228
0.5395 | 0 | 0.19094 | 590.7308 | 40 | 0 | 7.6376
0.51686 | 0 | 0.18226 | 586.3352 | 40 | 0 | 7.2904
0.49779 | 0 | 0.15976 | 582.9466 | 40 | 0 | 6.3904
0.48787 | 0 | 0.14657 | 580.0224 | 40 | 0 | 5.8628
0.49123 | 0 | 0.11969 | 575.687 | 40 | 0 | 4.7876
0.50889 | 0.0003 | 0.11862 | 569.5638 | 40 | 0.021 | 4.7448
0.52169 | 0.0908 | 0.11125 | 568.2008 | 40 | 6.356 | 4.45
0.54111 | 0.5187 | 0.09621 | 594.2472 | 40 | 40.1574 | 0
0.57627 | 0.7963 | 0.06548 | 634.9804 | 40 | 58.3602 | 0
0.61463 | 0.87 | 0.08961 | 678.0018 | 40 | 64.4844 | 0
0.65277 | 0.8834 | 0.07912 | 700 | 40 | 47.2752 | 0
0.68984 | 0.8929 | 0.07167 | 700 | 40 | 28.984 | 0
0.72497 | 0.9094 | 0.06634 | 700 | 40 | 32.497 | 0
0.75533 | 0.909 | 0.0833 | 700 | 40 | 35.533 | 0
0.782 | 0.9026 | 0.10018 | 700 | 40 | 38.2 | 0
0.80513 | 0.8896 | 0.09379 | 700 | 40 | 40.513 | 0
0.81414 | 0.8619 | 0.08912 | 700 | 40 | 41.414 | 0
0.80647 | 0.7643 | 0.09351 | 700 | 40 | 40.647 | 0
0.78123 | 0.4216 | 0.11563 | 696.0142 | 40 | 29.512 | 4.6252
0.73856 | 0.0449 | 0.13604 | 670.7428 | 40 | 3.143 | 5.4416
0.71194 | 0 | 0.21123 | 647.998 | 40 | 0 | 8.4492
0.66781 | 0 | 0.2956 | 633.041 | 40 | 0 | 11.824
0.61043 | 0 | 0.3587 | 626.346 | 40 | 0 | 14.348
0.55861 | 0 | 0.39918 | 626.4522 | 40 | 0 | 15.9672
0.52056 | 0 | 0.41578 | 631.0274 | 40 | 0 | 16.6312
0.49193 | 0 | 0.42561 | 638.8588 | 40 | 0 | 17.0244
0.4743 | 0 | 0.41303 | 647.95 | 40 | 0 | 16.5212
0.4638 | 0 | 0.38791 | 657.0864 | 40 | 0 | 15.5164
0.4671 | 0 | 0.40307 | 666.4992 | 40 | 0 | 16.1228
0.48559 | 0.0003 | 0.41156 | 674.4236 | 40 | 0.021 | 16.4624
0.50046 | 0.0822 | 0.3932 | 685.8596 | 40 | 5.754 | 15.728
0.52629 | 0.5086 | 0.32588 | 700 | 40 | 26.7694 | 0
0.55949 | 0.8227 | 0.24864 | 700 | 40 | 15.949 | 0
0.6023 | 0.8892 | 0.26114 | 700 | 40 | 20.23 | 0
0.63967 | 0.9103 | 0.19185 | 700 | 40 | 23.967 | 0
0.67933 | 0.9162 | 0.11748 | 700 | 40 | 27.933 | 0
0.71884 | 0.9175 | 0.07912 | 700 | 40 | 31.884 | 0
0.75501 | 0.9027 | 0.09215 | 700 | 40 | 35.501 | 0
0.78715 | 0.8868 | 0.10604 | 700 | 40 | 38.715 | 0
0.80876 | 0.8243 | 0.1337 | 700 | 40 | 40.876 | 0
0.8197 | 0.8137 | 0.16898 | 700 | 40 | 41.97 | 0
0.81174 | 0.7619 | 0.20389 | 700 | 40 | 41.174 | 0
0.78628 | 0.4213 | 0.2472 | 700 | 40 | 29.491 | 9.137
0.74815 | 0.0457 | 0.27015 | 679.19 | 40 | 3.199 | 10.806
0.72144 | 0 | 0.31891 | 659.8024 | 40 | 0 | 12.7564
0.68259 | 0 | 0.42004 | 648.345 | 40 | 0 | 16.8016
0.62666 | 0 | 0.47318 | 644.6062 | 40 | 0 | 18.9272
0.57406 | 0 | 0.506 | 647.4402 | 40 | 0 | 20.24
0.53605 | 0 | 0.50559 | 654.0588 | 40 | 0 | 20.2236
0.5056 | 0 | 0.50871 | 663.8472 | 40 | 0 | 20.3484
0.48628 | 0 | 0.50994 | 675.6168 | 40 | 0 | 20.3976
0.47909 | 0 | 0.4774 | 686.8038 | 40 | 0 | 19.096
0.47928 | 0 | 0.43245 | 696.1738 | 40 | 0 | 17.298
0.49846 | 0.0003 | 0.41196 | 700 | 40 | 0.021 | 13.6512
0.5113 | 0.082 | 0.39783 | 700 | 40 | 5.74 | 5.39
0.53356 | 0.4739 | 0.34194 | 700 | 40 | 13.356 | 0
0.57367 | 0.8103 | 0.24405 | 700 | 40 | 17.367 | 0
0.62346 | 0.8834 | 0.29531 | 700 | 40 | 22.346 | 0
0.67356 | 0.8942 | 0.24044 | 700 | 40 | 27.356 | 0
0.71616 | 0.8891 | 0.15108 | 700 | 40 | 31.616 | 0
0.75357 | 0.8944 | 0.09297 | 700 | 40 | 35.357 | 0
0.78955 | 0.8642 | 0.1069 | 700 | 40 | 38.955 | 0
0.81567 | 0.8043 | 0.14395 | 700 | 40 | 41.567 | 0
0.82983 | 0.7969 | 0.1655 | 700 | 40 | 42.983 | 0
0.83735 | 0.7916 | 0.19959 | 700 | 40 | 43.735 | 0
0.82262 | 0.7068 | 0.23155 | 700 | 40 | 42.262 | 0
0.79606 | 0.3934 | 0.25962 | 698.3168 | 40 | 27.538 | 10.3848
0.75513 | 0.037 | 0.29096 | 677.0322 | 40 | 2.59 | 11.6384
0.73267 | 0 | 0.32321 | 656.6936 | 40 | 0 | 12.9284
0.69267 | 0 | 0.42598 | 644.4658 | 40 | 0 | 17.0392
0.64536 | 0 | 0.47617 | 638.9766 | 40 | 0 | 19.0468
0.6032 | 0 | 0.46708 | 637.3398 | 40 | 0 | 18.6832
0.56174 | 0 | 0.46949 | 639.9454 | 40 | 0 | 18.7796
0.53388 | 0 | 0.45933 | 644.9306 | 40 | 0 | 18.3732
0.51201 | 0 | 0.42229 | 650.6212 | 40 | 0 | 16.8916
0.49676 | 0 | 0.38783 | 656.4584 | 40 | 0 | 15.5132
0.49491 | 0 | 0.348 | 660.8874 | 40 | 0 | 13.92
0.49803 | 0.0002 | 0.3153 | 663.7104 | 40 | 0.014 | 12.612
0.49938 | 0.0795 | 0.35095 | 673.3754 | 40 | 5.565 | 14.038
0.52795 | 0.5107 | 0.33292 | 700 | 40 | 39.4196 | 0
0.57998 | 0.5817 | 0.28847 | 700 | 40 | 17.998 | 0
0.63844 | 0.6962 | 0.38238 | 700 | 40 | 23.844 | 0
0.69623 | 0.8834 | 0.34354 | 700 | 40 | 29.623 | 0
0.74478 | 0.8867 | 0.24798 | 700 | 40 | 34.478 | 0
0.78254 | 0.8898 | 0.21303 | 700 | 40 | 38.254 | 0
0.81349 | 0.8773 | 0.21291 | 700 | 40 | 41.349 | 0
0.83055 | 0.8745 | 0.25216 | 700 | 40 | 43.055 | 0
0.84665 | 0.8432 | 0.27097 | 700 | 40 | 44.665 | 0
0.85356 | 0.8131 | 0.32284 | 700 | 40 | 45.356 | 0
0.84992 | 0.6952 | 0.37124 | 700 | 40 | 44.992 | 0
0.83042 | 0.3844 | 0.40295 | 699.984 | 40 | 26.908 | 16.118
0.79262 | 0.0382 | 0.39705 | 679.278 | 40 | 2.674 | 15.882
0.77019 | 0 | 0.41373 | 658.8082 | 40 | 0 | 16.5492
0.73523 | 0 | 0.48425 | 644.6552 | 40 | 0 | 19.37
0.6902 | 0 | 0.54415 | 637.4012 | 40 | 0 | 21.766
0.64751 | 0 | 0.55095 | 634.6882 | 40 | 0 | 22.038
0.60661 | 0 | 0.53255 | 635.3292 | 40 | 0 | 21.302
0.57724 | 0 | 0.52727 | 638.696 | 40 | 0 | 21.0908
0.55525 | 0 | 0.50633 | 643.4242 | 40 | 0 | 20.2532
0.53929 | 0 | 0.51301 | 650.0156 | 40 | 0 | 20.5204
0.53114 | 0 | 0.50375 | 657.0516 | 40 | 0 | 20.15
0.53239 | 0.0001 | 0.49621 | 663.668 | 40 | 0.007 | 19.8484
0.52764 | 0.0581 | 0.51223 | 675.4602 | 40 | 4.067 | 20.4892
0.55257 | 0.374 | 0.4824 | 700 | 40 | 39.7968 | 0
0.60746 | 0.6386 | 0.51596 | 700 | 40 | 20.746 | 0
0.66482 | 0.7903 | 0.59668 | 700 | 40 | 26.482 | 0
0.71664 | 0.8344 | 0.60824 | 700 | 40 | 31.664 | 0
0.75774 | 0.8512 | 0.55935 | 700 | 40 | 35.774 | 0
0.78838 | 0.8657 | 0.51416 | 700 | 40 | 38.838 | 0
0.80456 | 0.8423 | 0.49273 | 700 | 40 | 40.456 | 0
0.8212 | 0.8519 | 0.44978 | 700 | 40 | 42.12 | 0
0.83716 | 0.8244 | 0.40352 | 700 | 40 | 43.716 | 0
0.8524 | 0.7003 | 0.38885 | 700 | 40 | 45.24 | 0
0.85595 | 0.5703 | 0.39967 | 700 | 40 | 39.921 | 5.674
0.84104 | 0.2853 | 0.42233 | 692.7602 | 40 | 19.971 | 16.8932
0.81014 | 0.0284 | 0.42971 | 670.9226 | 40 | 1.988 | 17.1884
0.79715 | 0 | 0.42917 | 648.3744 | 40 | 0 | 17.1668
0.76088 | 0 | 0.47273 | 631.1956 | 40 | 0 | 18.9092
0.71292 | 0 | 0.4849 | 619.2996 | 40 | 0 | 19.396
0.6598 | 0 | 0.47101 | 612.16 | 40 | 0 | 18.8404
0.62077 | 0 | 0.49883 | 610.0362 | 40 | 0 | 19.9532
0.5919 | 0 | 0.50539 | 611.0618 | 40 | 0 | 20.2156
0.57552 | 0 | 0.51072 | 613.9386 | 40 | 0 | 20.4288
0.56711 | 0 | 0.49121 | 616.876 | 40 | 0 | 19.6484
0.57096 | 0 | 0.43585 | 617.214 | 40 | 0 | 17.434
0.59146 | 0.0002 | 0.39193 | 613.7592 | 40 | 0.014 | 15.6772
0.60589 | 0.0478 | 0.36394 | 611.0738 | 40 | 3.346 | 14.5576
0.62945 | 0.3301 | 0.30338 | 623.371 | 40 | 35.2422 | 0
0.67309 | 0.5857 | 0.30641 | 649.3174 | 40 | 53.2554 | 0
0.72465 | 0.6786 | 0.33296 | 677.6728 | 40 | 60.8204 | 0
0.77231 | 0.7934 | 0.30211 | 700 | 40 | 59.5582 | 0
0.80662 | 0.8306 | 0.26261 | 700 | 40 | 40.662 | 0
0.84433 | 0.8055 | 0.23823 | 700 | 40 | 44.433 | 0
0.86955 | 0.7112 | 0.22508 | 700 | 40 | 46.955 | 0
0.88223 | 0.6789 | 0.2352 | 700 | 40 | 47.523 | 0.7
0.88535 | 0.7158 | 0.27351 | 700 | 40 | 48.535 | 0
0.8833 | 0.6856 | 0.31375 | 700 | 40 | 47.992 | 0.338
0.86995 | 0.4722 | 0.30088 | 698.0942 | 40 | 33.054 | 12.0352
0.84938 | 0.2398 | 0.30334 | 682.0758 | 40 | 16.786 | 12.1336
0.81833 | 0.0225 | 0.30088 | 653.853 | 40 | 1.575 | 12.0352
0.80588 | 0 | 0.28322 | 624.5938 | 40 | 0 | 11.3288
0.76668 | 0 | 0.29736 | 599.8202 | 40 | 0 | 11.8944
0.70984 | 0 | 0.31317 | 581.363 | 40 | 0 | 12.5268
0.6578 | 0 | 0.32026 | 568.3934 | 40 | 0 | 12.8104
0.61751 | 0 | 0.30666 | 558.9088 | 40 | 0 | 12.2664
0.58831 | 0 | 0.27961 | 551.2622 | 40 | 0 | 11.1844
0.56875 | 0 | 0.25757 | 544.69 | 40 | 0 | 10.3028
0.56113 | 0 | 0.23131 | 537.8294 | 40 | 0 | 9.2524
0.56534 | 0 | 0.21397 | 529.8542 | 40 | 0 | 8.5588
0.58407 | 0.0001 | 0.19701 | 519.3346 | 40 | 0.007 | 7.8804
0.60163 | 0.046 | 0.1775 | 509.4916 | 40 | 3.22 | 7.1
0.62438 | 0.3794 | 0.14788 | 519.5268 | 40 | 32.4732 | 0
0.66751 | 0.689 | 0.13919 | 546.5734 | 40 | 53.7976 | 0
0.72261 | 0.7907 | 0.15042 | 575.6782 | 40 | 61.3658 | 0
0.78178 | 0.8636 | 0.1153 | 602.5642 | 40 | 65.064 | 0
0.83592 | 0.8288 | 0.07548 | 620.0074 | 40 | 61.0352 | 0
0.8848 | 0.803 | 0.08011 | 630.9418 | 40 | 59.4144 | 0
0.91705 | 0.789 | 0.10379 | 638.6184 | 40 | 59.3816 | 0
0.94368 | 0.7517 | 0.13497 | 642.2682 | 40 | 52.619 | 5.3988
0.9513 | 0.7616 | 0.14665 | 646.3162 | 40 | 53.312 | 5.866
0.94176 | 0.7475 | 0.16869 | 651.2128 | 40 | 52.325 | 6.7476
0.92419 | 0.6292 | 0.22065 | 651.6638 | 40 | 44.044 | 8.826
0.88952 | 0.3126 | 0.2665 | 635.2538 | 40 | 21.882 | 10.66
0.84397 | 0.0311 | 0.29019 | 604.6414 | 40 | 2.177 | 11.6076
0.82094 | 0 | 0.33665 | 576.0134 | 40 | 0 | 13.466
0.77563 | 0 | 0.41299 | 554.97 | 40 | 0 | 16.5196
0.71432 | 0 | 0.46634 | 542.1916 | 40 | 0 | 18.6536
0.65838 | 0 | 0.46482 | 534.9464 | 40 | 0 | 18.5928
0.61592 | 0 | 0.42475 | 530.3444 | 40 | 0 | 16.99
0.58336 | 0 | 0.37074 | 526.838 | 40 | 0 | 14.8296
0.55945 | 0 | 0.32776 | 524.0034 | 40 | 0 | 13.1104
0.54866 | 0 | 0.30023 | 521.1466 | 40 | 0 | 12.0092
0.54994 | 0 | 0.27138 | 517.0078 | 40 | 0 | 10.8552
0.56914 | 0.0002 | 0.252 | 510.1878 | 40 | 0.014 | 10.08
0.58192 | 0.0605 | 0.2463 | 506.0828 | 40 | 4.235 | 9.852
0.60541 | 0.4404 | 0.22569 | 525.3974 | 40 | 39.8556 | 5.6843e-14
0.64721 | 0.7351 | 0.1494 | 558.1094 | 40 | 57.433 | 0
0.70364 | 0.8374 | 0.14845 | 592.3014 | 40 | 64.556 | 0
0.76275 | 0.8698 | 0.10674 | 621.182 | 40 | 65.1556 | 0
0.81925 | 0.8756 | 0.06409 | 643.1126 | 40 | 63.8556 | 0
0.86842 | 0.8846 | 0.06359 | 660.7362 | 40 | 64.4656 | 0
0.90863 | 0.8734 | 0.09183 | 674.6844 | 40 | 64.8112 | 0
0.93157 | 0.8338 | 0.12739 | 684.989 | 40 | 63.4616 | 0
0.94041 | 0.8236 | 0.1646 | 695.184 | 40 | 64.236 | 0
0.94229 | 0.7789 | 0.18578 | 700 | 40 | 59.045 | 0
0.93742 | 0.6712 | 0.24806 | 700 | 40 | 46.984 | 6.758
0.91179 | 0.3273 | 0.26179 | 682.2036 | 40 | 22.911 | 10.4716
0.87238 | 0.0279 | 0.3178 | 649.6306 | 40 | 1.953 | 12.712
0.84572 | 0 | 0.38308 | 620.3818 | 40 | 0 | 15.3232
0.79626 | 0 | 0.48367 | 600.1026 | 40 | 0 | 19.3468
0.73509 | 0 | 0.54095 | 588.2316 | 40 | 0 | 21.638
0.67871 | 0 | 0.53133 | 581.6138 | 40 | 0 | 21.2532
0.63258 | 0 | 0.52502 | 579.3566 | 40 | 0 | 21.0008
0.59723 | 0 | 0.5001 | 579.6376 | 40 | 0 | 20.004
0.57346 | 0 | 0.45286 | 580.406 | 40 | 0 | 18.1144
0.55893 | 0 | 0.422 | 581.393 | 40 | 0 | 16.88
0.56105 | 0 | 0.38992 | 580.8848 | 40 | 0 | 15.5968
0.57822 | 0.0001 | 0.37841 | 578.2062 | 40 | 0.007 | 15.1364
0.59241 | 0.0525 | 0.36714 | 577.3258 | 40 | 3.675 | 14.6856
0.61357 | 0.4294 | 0.31924 | 598.7964 | 40 | 42.8276 | 0
0.65326 | 0.7486 | 0.20262 | 633.9772 | 40 | 60.5068 | 0
0.70608 | 0.838 | 0.23794 | 671.5468 | 40 | 68.1776 | 0
0.76126 | 0.8565 | 0.19152 | 700 | 40 | 64.5792 | 0
0.81063 | 0.8553 | 0.10957 | 700 | 40 | 41.063 | 0
0.857 | 0.8626 | 0.06863 | 700 | 40 | 45.7 | 0
0.89861 | 0.8606 | 0.11276 | 700 | 40 | 49.861 | 0
0.92 | 0.8334 | 0.15411 | 700 | 40 | 52 | 0
0.93129 | 0.8028 | 0.20643 | 700 | 40 | 53.129 | 0
0.93013 | 0.7574 | 0.25237 | 700 | 40 | 53.013 | 0
0.91649 | 0.6592 | 0.28048 | 700 | 40 | 46.144 | 5.505
0.89241 | 0.2457 | 0.34743 | 681.8552 | 40 | 17.199 | 13.8972
0.85456 | 0.0227 | 0.35747 | 652.287 | 40 | 1.589 | 14.2988
0.83062 | 0 | 0.37722 | 624.3138 | 40 | 0 | 15.0888
0.78569 | 0 | 0.45761 | 604.0492 | 40 | 0 | 18.3044
0.72665 | 0 | 0.47658 | 590.4474 | 40 | 0 | 19.0632
0.67351 | 0 | 0.48429 | 582.468 | 40 | 0 | 19.3716
0.63102 | 0 | 0.48761 | 578.8704 | 40 | 0 | 19.5044
0.59845 | 0 | 0.49031 | 578.6378 | 40 | 0 | 19.6124
0.57427 | 0 | 0.46048 | 579.63 | 40 | 0 | 18.4192
0.56148 | 0 | 0.45183 | 581.5552 | 40 | 0 | 18.0732
0.56313 | 0 | 0.44647 | 583.101 | 40 | 0 | 17.8588
0.58156 | 0.0001 | 0.44729 | 582.8436 | 40 | 0.007 | 17.8916
0.59397 | 0.0626 | 0.40754 | 584.1302 | 40 | 4.382 | 16.3016
0.61907 | 0.4649 | 0.35099 | 608.8058 | 40 | 46.5826 | 0
0.66156 | 0.7585 | 0.24757 | 645.6476 | 40 | 62.9978 | 0
0.7162 | 0.8328 | 0.2588 | 682.6756 | 40 | 68.648 | 0
0.77493 | 0.8522 | 0.20107 | 700 | 40 | 54.8174 | 0
0.82501 | 0.8676 | 0.14907 | 700 | 40 | 42.501 | 0
0.86823 | 0.8684 | 0.11026 | 700 | 40 | 46.823 | 0
0.9042 | 0.868 | 0.09982 | 700 | 40 | 50.42 | 0
0.92406 | 0.8609 | 0.10072 | 700 | 40 | 52.406 | 0
0.93178 | 0.8116 | 0.10531 | 700 | 40 | 53.178 | 0
0.92835 | 0.7787 | 0.12198 | 700 | 40 | 52.835 | 0
0.91931 | 0.6582 | 0.16173 | 700 | 40 | 46.074 | 5.857
0.88908 | 0.3155 | 0.20565 | 681.403 | 40 | 22.085 | 8.226
0.84866 | 0.0199 | 0.26036 | 648.3444 | 40 | 1.393 | 10.4144
0.82368 | 0 | 0.34915 | 619.9424 | 40 | 0 | 13.966
0.78377 | 0 | 0.39045 | 597.1834 | 40 | 0 | 15.618
0.73619 | 0 | 0.45036 | 581.5788 | 40 | 0 | 18.0144
0.6893 | 0 | 0.46404 | 571.2104 | 40 | 0 | 18.5616
0.64798 | 0 | 0.48703 | 565.8936 | 40 | 0 | 19.4812
0.61554 | 0 | 0.4561 | 562.5836 | 40 | 0 | 18.244
0.59221 | 0 | 0.42372 | 560.3114 | 40 | 0 | 16.9488
0.57481 | 0 | 0.37996 | 558.0288 | 40 | 0 | 15.1984
0.56797 | 0 | 0.35419 | 555.3994 | 40 | 0 | 14.1676
0.5686 | 0 | 0.32342 | 551.4762 | 40 | 0 | 12.9368
0.56665 | 0.0437 | 0.32817 | 550.997 | 40 | 3.059 | 13.1268
0.58157 | 0.375 | 0.2749 | 570.086 | 40 | 37.246 | 0
0.61374 | 0.6272 | 0.21299 | 601.1356 | 40 | 52.4236 | 0
0.64622 | 0.6882 | 0.17464 | 631.6732 | 40 | 55.1596 | 0
0.68577 | 0.7255 | 0.1378 | 659.3932 | 40 | 56.297 | 0
0.7234 | 0.7827 | 0.14829 | 687.7738 | 40 | 60.7206 | 0
0.7521 | 0.7731 | 0.13604 | 700 | 40 | 47.4362 | 0
0.77584 | 0.7668 | 0.1344 | 700 | 40 | 37.584 | 0
0.79564 | 0.7478 | 0.15288 | 700 | 40 | 39.564 | 0
0.81332 | 0.7724 | 0.16165 | 700 | 40 | 41.332 | 0
0.82027 | 0.6182 | 0.1478 | 700 | 40 | 42.027 | 0
0.80794 | 0.3171 | 0.1564 | 687.659 | 40 | 22.197 | 6.256
0.78683 | 0.1099 | 0.19197 | 664.3478 | 40 | 7.693 | 7.6788
0.76143 | 0.0064 | 0.20529 | 636.8644 | 40 | 0.448 | 8.2116
0.74843 | 0 | 0.22069 | 610.849 | 40 | 0 | 8.8276
0.71712 | 0 | 0.24532 | 588.9498 | 40 | 0 | 9.8128
0.68003 | 0 | 0.26753 | 571.648 | 40 | 0 | 10.7012
0.63719 | 0 | 0.24839 | 557.8646 | 40 | 0 | 9.9356
0.60356 | 0 | 0.22676 | 546.579 | 40 | 0 | 9.0704
0.57948 | 0 | 0.17541 | 535.6474 | 40 | 0 | 7.0164
0.56141 | 0 | 0.13768 | 525.0136 | 40 | 0 | 5.5072
0.54613 | 0 | 0.11895 | 515.1586 | 40 | 0 | 4.758
0.53938 | 0 | 0.10211 | 505.305 | 40 | 0 | 4.0844
0.5389 | 0 | 0.10707 | 495.6978 | 40 | 0 | 4.2828
0.53583 | 0.0255 | 0.08203 | 487.181 | 40 | 1.785 | 3.2812
0.54994 | 0.2149 | 0.06253 | 489.7312 | 40 | 17.5442 | -5.6843e-14
0.58612 | 0.4139 | 0.04266 | 501.7986 | 40 | 30.6794 | 0
0.62356 | 0.5621 | 0.05036 | 520.804 | 40 | 41.3614 | 0
0.66326 | 0.6404 | 0.05544 | 541.5236 | 40 | 47.0456 | 0
0.7047 | 0.7813 | 0.06568 | 568.3718 | 40 | 57.3182 | 0
0.74225 | 0.8025 | 0.069 | 593.0818 | 40 | 58.935 | 0
0.77539 | 0.824 | 0.09273 | 616.932 | 40 | 61.3892 | 0
0.80026 | 0.7965 | 0.11875 | 637.411 | 40 | 60.505 | 0
0.82427 | 0.6923 | 0.12366 | 648.3914 | 40 | 53.4074 | 0
0.8373 | 0.6998 | 0.13038 | 658.8626 | 40 | 54.2012 | 0
0.84146 | 0.636 | 0.15009 | 665.2402 | 40 | 50.5236 | 0
0.82815 | 0.2815 | 0.16259 | 648.6338 | 40 | 19.705 | 6.5036
0.79902 | 0.0172 | 0.18267 | 617.2426 | 40 | 1.204 | 7.3068
0.78204 | 0 | 0.21065 | 587.4646 | 40 | 0 | 8.426
0.74285 | 0 | 0.25523 | 563.3888 | 40 | 0 | 10.2092
0.68914 | 0 | 0.29641 | 546.3312 | 40 | 0 | 11.8564
0.64111 | 0 | 0.32588 | 535.2554 | 40 | 0 | 13.0352
0.60072 | 0 | 0.30899 | 527.543 | 40 | 0 | 12.3596
0.57594 | 0 | 0.27531 | 520.9614 | 40 | 0 | 11.0124
0.55721 | 0 | 0.24733 | 515.1336 | 40 | 0 | 9.8932
0.55105 | 0 | 0.22422 | 508.9974 | 40 | 0 | 8.9688
0.55679 | 0 | 0.21201 | 501.7988 | 40 | 0 | 8.4804
0.57736 | 0.0001 | 0.19451 | 491.8502 | 40 | 0.007 | 7.7804
0.59527 | 0.0592 | 0.16476 | 483.0576 | 40 | 4.144 | 6.5904
0.61935 | 0.4363 | 0.111 | 496.1036 | 40 | 34.981 | 0
0.66943 | 0.7295 | 0.07683 | 523.2988 | 40 | 54.1382 | 0
0.72599 | 0.8161 | 0.06986 | 550.6212 | 40 | 59.9214 | 0
0.78055 | 0.849 | 0.04765 | 573.9022 | 40 | 61.336 | 0
0.82957 | 0.8191 | 0.02672 | 589.351 | 40 | 58.4058 | 0
0.87304 | 0.8235 | 0.02385 | 600.646 | 40 | 58.599 | 0
0.90403 | 0.8217 | 0.04614 | 609.6076 | 40 | 59.3646 | 0
0.9234 | 0.8077 | 0.05183 | 615.8798 | 40 | 58.6122 | 0
0.93559 | 0.7688 | 0.07699 | 619.2164 | 40 | 56.8956 | 0
0.93563 | 0.7178 | 0.09314 | 619.625 | 40 | 50.246 | 3.7256
0.9308 | 0.606 | 0.13673 | 614.4342 | 40 | 42.42 | 5.4692
0.90928 | 0.3285 | 0.21393 | 595.0584 | 40 | 22.995 | 8.5572
0.87108 | 0.0256 | 0.26183 | 560.2156 | 40 | 1.792 | 10.4732
0.8518 | 0 | 0.30363 | 527.1808 | 40 | 0 | 12.1452
0.8036 | 0 | 0.39012 | 502.4256 | 40 | 0 | 15.6048
0.74343 | 0 | 0.40664 | 484.3482 | 40 | 0 | 16.2656
0.68573 | 0 | 0.40988 | 472.1704 | 40 | 0 | 16.3952
0.64441 | 0 | 0.41451 | 464.3098 | 40 | 0 | 16.5804
0.61223 | 0 | 0.39611 | 458.9312 | 40 | 0 | 15.8444
0.5907 | 0 | 0.35812 | 454.186 | 40 | 0 | 14.3248
0.57927 | 0 | 0.33358 | 449.6022 | 40 | 0 | 13.3432
0.58295 | 0 | 0.29703 | 443.1884 | 40 | 0 | 11.8812
0.60278 | 0.0001 | 0.26585 | 433.5514 | 40 | 0.007 | 10.634
0.61763 | 0.0486 | 0.24548 | 425.0096 | 40 | 3.402 | 9.8192
0.63855 | 0.3844 | 0.17853 | 435.2038 | 40 | 34.0492 | 0
0.68208 | 0.6938 | 0.12534 | 460.5754 | 40 | 53.5796 | 5.6843e-14
0.7414 | 0.7929 | 0.12149 | 486.798 | 40 | 60.3626 | 0
0.7999 | 0.8159 | 0.10166 | 507.9874 | 40 | 61.1794 | 0
0.85621 | 0.8188 | 0.09121 | 523.3308 | 40 | 60.9644 | 0
0.90098 | 0.7111 | 0.08683 | 526.483 | 40 | 49.777 | 3.4732
0.92823 | 0.7913 | 0.1017 | 533.119 | 40 | 59.459 | 0
0.94787 | 0.7604 | 0.13059 | 536.7836 | 40 | 53.228 | 5.2236
0.95415 | 0.7959 | 0.14538 | 542.8968 | 40 | 61.5282 | 0
0.95183 | 0.7125 | 0.15747 | 543.8876 | 40 | 49.875 | 6.2988
0.94512 | 0.6045 | 0.18918 | 539.2578 | 40 | 42.315 | 7.5672
0.9197 | 0.2732 | 0.25888 | 516.767 | 40 | 19.124 | 10.3552
0.88233 | 0.0189 | 0.29367 | 481.6038 | 40 | 1.323 | 11.7468
0.86182 | 0 | 0.32698 | 448.501 | 40 | 0 | 13.0792
0.81542 | 0 | 0.37931 | 422.1314 | 40 | 0 | 15.1724
0.75487 | 0 | 0.4195 | 403.4244 | 40 | 0 | 16.78
0.70069 | 0 | 0.4755 | 392.3754 | 40 | 0 | 19.02
0.65855 | 0 | 0.48959 | 386.104 | 40 | 0 | 19.5836
0.62749 | 0 | 0.46185 | 381.829 | 40 | 0 | 18.474
0.60635 | 0 | 0.45447 | 379.3728 | 40 | 0 | 18.1788
0.59809 | 0 | 0.47451 | 378.5442 | 40 | 0 | 18.9804
0.6009 | 0 | 0.46103 | 376.8954 | 40 | 0 | 18.4412
0.62135 | 0.0001 | 0.44091 | 372.4038 | 40 | 0.007 | 17.6364
0.63582 | 0.0498 | 0.42612 | 369.3526 | 40 | 3.486 | 17.0448
0.65258 | 0.3967 | 0.35937 | 386.2384 | 40 | 42.1438 | 0
0.69367 | 0.7173 | 0.33253 | 420.3836 | 40 | 63.5122 | 0
0.75156 | 0.8209 | 0.3574 | 456.9866 | 40 | 71.759 | 0
0.80972 | 0.8683 | 0.27287 | 487.7104 | 40 | 71.6958 | 0
0.86399 | 0.8662 | 0.20632 | 510.1982 | 40 | 68.8868 | 0
0.91386 | 0.8548 | 0.20341 | 526.7846 | 40 | 67.9724 | 0
0.95354 | 0.8506 | 0.20632 | 539.2254 | 40 | 67.7948 | 0
0.9758 | 0.8152 | 0.2425 | 548.4094 | 40 | 57.064 | 9.7
0.98072 | 0.7461 | 0.29553 | 554.3856 | 40 | 52.227 | 11.8212
0.98021 | 0.7293 | 0.28254 | 558.7172 | 40 | 51.051 | 11.3016
0.9742 | 0.5958 | 0.32691 | 556.0796 | 40 | 41.706 | 13.0764
0.95223 | 0.2937 | 0.35691 | 535.692 | 40 | 20.559 | 14.2764
0.91123 | 0.0169 | 0.4228 | 502.664 | 40 | 1.183 | 16.912
0.88597 | 0 | 0.47701 | 473.1474 | 40 | 0 | 19.0804
0.8359 | 0 | 0.54229 | 451.249 | 40 | 0 | 21.6916
0.77689 | 0 | 0.57589 | 436.5956 | 40 | 0 | 23.0356
0.71814 | 0 | 0.59474 | 428.5712 | 40 | 0 | 23.7896
0.67158 | 0 | 0.56806 | 424.1356 | 40 | 0 | 22.7224
0.63966 | 0 | 0.54409 | 421.9332 | 40 | 0 | 21.7636
0.61778 | 0 | 0.5552 | 422.3632 | 40 | 0 | 22.208
0.60791 | 0 | 0.58072 | 424.801 | 40 | 0 | 23.2288
0.61135 | 0 | 0.55475 | 425.856 | 40 | 0 | 22.19
0.62811 | 0 | 0.48808 | 422.5682 | 40 | 0 | 19.5232
0.64124 | 0.0383 | 0.43251 | 418.4256 | 40 | 2.681 | 17.3004
0.65571 | 0.3179 | 0.38432 | 430.4804 | 40 | 22.253 | 15.3728
0.69715 | 0.6301 | 0.35982 | 459.2652 | 40 | 58.4998 | 0
0.74877 | 0.7968 | 0.35929 | 494.5358 | 40 | 70.1476 | 0
0.80341 | 0.8532 | 0.30979 | 526.3104 | 40 | 72.1156 | 0
0.85592 | 0.8591 | 0.27282 | 551.7682 | 40 | 71.0498 | 0
0.90428 | 0.8399 | 0.28553 | 571.5544 | 40 | 70.2142 | 0
0.94309 | 0.8723 | 0.28717 | 589.7932 | 40 | 72.5478 | 0
0.9619 | 0.86 | 0.30483 | 605.9964 | 40 | 72.3932 | 0
0.96935 | 0.8365 | 0.32433 | 620.5896 | 40 | 71.5282 | 0
0.96901 | 0.7861 | 0.3522 | 632.8036 | 40 | 55.027 | 14.088
0.95641 | 0.6406 | 0.37129 | 636.8562 | 40 | 44.842 | 14.8516
0.93088 | 0.2928 | 0.43022 | 621.473 | 40 | 20.496 | 17.2088
0.89492 | 0.0169 | 0.4503 | 591.176 | 40 | 1.183 | 18.012
0.87274 | 0 | 0.48467 | 563.2888 | 40 | 0 | 19.3868
0.82789 | 0 | 0.53176 | 541.7702 | 40 | 0 | 21.2704
0.76983 | 0 | 0.5672 | 527.4752 | 40 | 0 | 22.688
0.71735 | 0 | 0.56376 | 518.2906 | 40 | 0 | 22.5504
0.67341 | 0 | 0.54753 | 512.8508 | 40 | 0 | 21.9012
0.64128 | 0 | 0.51787 | 509.4376 | 40 | 0 | 20.7148
0.61952 | 0 | 0.48525 | 506.8956 | 40 | 0 | 19.41
0.60862 | 0 | 0.463 | 504.5536 | 40 | 0 | 18.52
0.613 | 0 | 0.43612 | 500.6984 | 40 | 0 | 17.4448
0.63266 | 0 | 0.40239 | 493.528 | 40 | 0 | 16.0956
0.64509 | 0.0378 | 0.40448 | 487.8442 | 40 | 2.646 | 16.1792
0.66154 | 0.3615 | 0.35552 | 501.216 | 40 | 25.305 | 14.2208
0.70306 | 0.6995 | 0.3052 | 532.083 | 40 | 61.173 | -5.6843e-14
0.75652 | 0.8463 | 0.28999 | 567.2716 | 40 | 70.8406 | 0
0.81344 | 0.8852 | 0.24672 | 597.7604 | 40 | 71.8328 | 0
0.86637 | 0.8898 | 0.24451 | 623.1898 | 40 | 72.0664 | 0
0.91387 | 0.8821 | 0.24475 | 643.3398 | 40 | 71.537 | 0
0.94696 | 0.8799 | 0.27028 | 661.048 | 40 | 72.4042 | 0
0.97176 | 0.8678 | 0.30274 | 676.7276 | 40 | 72.8556 | 0
0.98005 | 0.8295 | 0.32667 | 689.8544 | 40 | 71.1318 | 0
0.97855 | 0.7486 | 0.39891 | 700 | 40 | 52.402 | 15.5986
0.96642 | 0.5757 | 0.40973 | 700 | 40 | 40.299 | 16.343
0.93422 | 0.2016 | 0.42403 | 677.6512 | 40 | 14.112 | 16.9612
0.88947 | 0.0054 | 0.4219 | 645.9582 | 40 | 0.378 | 16.876
0.86566 | 0 | 0.4285 | 616.5322 | 40 | 0 | 17.14
0.82352 | 0 | 0.50287 | 594.295 | 40 | 0 | 20.1148
0.77064 | 0 | 0.54692 | 579.1078 | 40 | 0 | 21.8768
0.72332 | 0 | 0.62441 | 571.7522 | 40 | 0 | 24.9764
0.67849 | 0 | 0.60777 | 568.214 | 40 | 0 | 24.3108
0.64243 | 0 | 0.58974 | 567.5606 | 40 | 0 | 23.5896
0.61868 | 0 | 0.56843 | 568.4298 | 40 | 0 | 22.7372
0.5994 | 0 | 0.52979 | 569.6814 | 40 | 0 | 21.1916
0.58986 | 0 | 0.48095 | 569.9334 | 40 | 0 | 19.238
0.59019 | 0 | 0.42218 | 567.8016 | 40 | 0 | 16.8872
0.59016 | 0.0408 | 0.36084 | 566.0752 | 40 | 2.856 | 14.4336
0.60906 | 0.3687 | 0.3106 | 583.4022 | 40 | 38.233 | 0
0.66204 | 0.6838 | 0.34445 | 618.8422 | 40 | 61.644 | 0
0.71997 | 0.824 | 0.3581 | 658.8492 | 40 | 72.004 | 0
0.77975 | 0.8831 | 0.32044 | 695.5088 | 40 | 74.6346 | 0
0.83341 | 0.9044 | 0.28327 | 700 | 40 | 47.8322 | 0
0.87691 | 0.8995 | 0.2543 | 700 | 40 | 47.691 | 0
0.91221 | 0.8934 | 0.24902 | 700 | 40 | 51.221 | 0
0.93964 | 0.8733 | 0.27881 | 700 | 40 | 53.964 | 0
0.95739 | 0.7688 | 0.30163 | 700 | 40 | 53.816 | 1.923
0.96295 | 0.6741 | 0.32331 | 700 | 40 | 47.187 | 9.108
0.95313 | 0.5328 | 0.3572 | 696.271 | 40 | 37.296 | 14.288
0.92693 | 0.1402 | 0.38973 | 668.9812 | 40 | 9.814 | 15.5892
0.88528 | 0.0029 | 0.40395 | 636.8142 | 40 | 0.203 | 16.158
0.86155 | 0 | 0.47472 | 609.648 | 40 | 0 | 18.9888
0.81872 | 0 | 0.58912 | 591.3408 | 40 | 0 | 23.5648
0.77162 | 0 | 0.64428 | 579.95 | 40 | 0 | 25.7712
0.72171 | 0 | 0.64174 | 573.4486 | 40 | 0 | 25.6696
0.67494 | 0 | 0.57282 | 568.8674 | 40 | 0 | 22.9128
0.64318 | 0 | 0.574 | 567.5094 | 40 | 0 | 22.96
0.61755 | 0 | 0.58052 | 568.9752 | 40 | 0 | 23.2208
0.60215 | 0 | 0.58253 | 572.0614 | 40 | 0 | 23.3012
0.58854 | 0 | 0.56343 | 575.7446 | 40 | 0 | 22.5372
0.5807 | 0.0001 | 0.53213 | 578.9668 | 40 | 0.007 | 21.2852
0.57434 | 0.0456 | 0.51766 | 585.4312 | 40 | 3.192 | 20.7064
0.59561 | 0.402 | 0.4548 | 612.2022 | 40 | 46.332 | 0
0.64585 | 0.7606 | 0.43944 | 658.4368 | 40 | 70.8196 | 0
0.70422 | 0.8341 | 0.48549 | 700 | 40 | 71.9852 | 0
0.76139 | 0.8792 | 0.40133 | 700 | 40 | 36.139 | 0
0.81904 | 0.887 | 0.30155 | 700 | 40 | 41.904 | 0
0.86692 | 0.8878 | 0.26549 | 700 | 40 | 46.692 | 0
0.90655 | 0.8931 | 0.27418 | 700 | 40 | 50.655 | 0
0.9354 | 0.8837 | 0.30352 | 700 | 40 | 53.54 | 0
0.95369 | 0.8465 | 0.31446 | 700 | 40 | 55.369 | 0
0.9646 | 0.7878 | 0.35228 | 700 | 40 | 55.146 | 1.314
0.96036 | 0.6603 | 0.38514 | 700 | 40 | 46.221 | 9.815
0.93494 | 0.2629 | 0.4587 | 683.257 | 40 | 18.403 | 18.348
0.90047 | 0.0064 | 0.4873 | 653.15 | 40 | 0.448 | 19.492
0.87789 | 0 | 0.52676 | 626.4314 | 40 | 0 | 21.0704
0.83628 | 0 | 0.58908 | 606.3666 | 40 | 0 | 23.5632
0.77518 | 0 | 0.5799 | 592.0446 | 40 | 0 | 23.196
0.72061 | 0 | 0.53389 | 581.3392 | 40 | 0 | 21.3556
0.67571 | 0 | 0.51385 | 574.3222 | 40 | 0 | 20.554
0.64084 | 0 | 0.47128 | 569.0894 | 40 | 0 | 18.8512
0.62026 | 0 | 0.44915 | 565.0294 | 40 | 0 | 17.966
0.60995 | 0 | 0.44792 | 561.9512 | 40 | 0 | 17.9168
0.61291 | 0 | 0.44993 | 558.6574 | 40 | 0 | 17.9972
0.6344 | 0 | 0.43927 | 552.7882 | 40 | 0 | 17.5708
0.64996 | 0.0463 | 0.4319 | 548.3092 | 40 | 3.241 | 17.276
0.66734 | 0.4123 | 0.39141 | 566.0926 | 40 | 44.5174 | 0
0.71516 | 0.7514 | 0.37527 | 602.1854 | 40 | 67.6088 | 0
0.77007 | 0.8398 | 0.42354 | 640.906 | 40 | 75.7276 | 0
0.83103 | 0.8804 | 0.34896 | 673.3894 | 40 | 75.5864 | 0
0.88508 | 0.898 | 0.23947 | 697.3202 | 40 | 72.4388 | 0
0.93154 | 0.894 | 0.20185 | 700 | 40 | 55.8338 | 0
0.96732 | 0.8772 | 0.22681 | 700 | 40 | 56.732 | 0
0.99109 | 0.8293 | 0.24537 | 700 | 40 | 58.051 | 1.058
0.9998 | 0.7925 | 0.29081 | 700 | 40 | 55.475 | 4.505
1 | 0.7502 | 0.31675 | 700 | 40 | 52.514 | 7.486
0.99539 | 0.6445 | 0.33462 | 698.9608 | 40 | 45.115 | 13.3848
0.97994 | 0.278 | 0.39149 | 676.0864 | 40 | 19.46 | 15.6596
0.93942 | 0.0142 | 0.44026 | 640.7488 | 40 | 0.994 | 17.6104
0.91277 | 0 | 0.50955 | 609.8538 | 40 | 0 | 20.382
0.85919 | 0 | 0.59269 | 587.6424 | 40 | 0 | 23.7076
0.79685 | 0 | 0.63203 | 573.2386 | 40 | 0 | 25.2812
0.74085 | 0 | 0.6635 | 565.6936 | 40 | 0 | 26.54
0.6931 | 0 | 0.63998 | 561.9828 | 40 | 0 | 25.5992
0.65879 | 0 | 0.62404 | 561.0654 | 40 | 0 | 24.9616
0.63287 | 0 | 0.5454 | 559.5944 | 40 | 0 | 21.816
0.61707 | 0 | 0.48361 | 557.2318 | 40 | 0 | 19.3444
0.61708 | 0 | 0.42956 | 552.7062 | 40 | 0 | 17.1824
0.63545 | 0 | 0.35105 | 543.2032 | 40 | 0 | 14.042
0.64813 | 0.046 | 0.27856 | 532.7526 | 40 | 3.22 | 11.1424
0.66604 | 0.403 | 0.19087 | 541.9934 | 40 | 35.8448 | 0
0.70985 | 0.7876 | 0.16628 | 572.7916 | 40 | 61.7832 | 0
0.76732 | 0.8678 | 0.16161 | 603.27 | 40 | 67.2104 | 0
0.82797 | 0.8717 | 0.12137 | 626.3468 | 40 | 65.8738 | 0
0.88173 | 0.8757 | 0.11109 | 643.9164 | 40 | 65.7426 | 0
0.93515 | 0.8896 | 0.13801 | 658.1938 | 40 | 67.7924 | 0
0.9705 | 0.8842 | 0.1567 | 669.3058 | 40 | 68.162 | 0
0.99341 | 0.7434 | 0.17743 | 669.1 | 40 | 52.038 | 7.0972
0.99352 | 0.5986 | 0.2007 | 659.678 | 40 | 41.902 | 8.028
0.99588 | 0.6019 | 0.24475 | 652.013 | 40 | 42.133 | 9.79
0.9894 | 0.4766 | 0.29639 | 638.2906 | 40 | 33.362 | 11.8556
0.9663 | 0.1665 | 0.32638 | 606.3708 | 40 | 11.655 | 13.0552
0.92915 | 0.0032 | 0.35638 | 567.935 | 40 | 0.224 | 14.2552
0.9051 | 0 | 0.33531 | 530.8374 | 40 | 0 | 13.4124
0.85239 | 0 | 0.33966 | 499.1848 | 40 | 0 | 13.5864
0.7881 | 0 | 0.34126 | 474.0252 | 40 | 0 | 13.6504
0.72906 | 0 | 0.32445 | 454.0972 | 40 | 0 | 12.978
0.68623 | 0 | 0.33089 | 438.7098 | 40 | 0 | 13.2356
0.65255 | 0 | 0.30192 | 425.5316 | 40 | 0 | 12.0768
0.62772 | 0 | 0.29557 | 414.5824 | 40 | 0 | 11.8228
0.61895 | 0 | 0.27528 | 403.6986 | 40 | 0 | 11.0112
0.6162 | 0 | 0.27991 | 393.275 | 40 | 0 | 11.1964
0.63189 | 0 | 0.28835 | 381.62 | 40 | 0 | 11.534
0.64892 | 0.0287 | 0.2718 | 369.609 | 40 | 2.009 | 10.872
0.65383 | 0.3152 | 0.26541 | 376.9064 | 40 | 22.064 | 10.6164
0.68475 | 0.5318 | 0.23521 | 395.0658 | 40 | 46.6344 | 0
0.73055 | 0.6042 | 0.24267 | 414.0116 | 40 | 52.0008 | 0
0.78549 | 0.6932 | 0.22681 | 433.059 | 40 | 57.5964 | 0
0.83633 | 0.7701 | 0.19128 | 450.9842 | 40 | 61.5582 | 0
0.87958 | 0.7617 | 0.14342 | 462.082 | 40 | 59.0558 | 5.6843e-14
0.91442 | 0.8103 | 0.1587 | 473.709 | 40 | 63.069 | 0
0.94056 | 0.6695 | 0.18587 | 473.9528 | 40 | 46.865 | 7.4348
0.9599 | 0.5834 | 0.20103 | 466.842 | 40 | 40.838 | 8.0412
0.9611 | 0.4302 | 0.19919 | 448.8136 | 40 | 30.114 | 7.9676
0.94549 | 0.3615 | 0.15329 | 425.7012 | 40 | 25.305 | 6.1316
0.90589 | 0.1192 | 0.15288 | 389.5714 | 40 | 8.344 | 6.1152
0.86433 | 0.0036 | 0.18829 | 350.922 | 40 | 0.252 | 7.5316
0.83802 | 0 | 0.19566 | 314.9464 | 40 | 0 | 7.8264
0.78557 | 0 | 0.22849 | 285.529 | 40 | 0 | 9.1396
0.72417 | 0 | 0.25836 | 263.4464 | 40 | 0 | 10.3344
0.67151 | 0 | 0.26192 | 246.7722 | 40 | 0 | 10.4768
0.63097 | 0 | 0.24803 | 233.5964 | 40 | 0 | 9.9212
0.59986 | 0 | 0.2232 | 222.5384 | 40 | 0 | 8.928
0.57866 | 0 | 0.2048 | 212.8644 | 40 | 0 | 8.192
0.57042 | 0 | 0.1821 | 203.1064 | 40 | 0 | 7.284
0.57257 | 0 | 0.11146 | 190.3078 | 40 | 0 | 4.4584
0.59661 | 0 | 0.07175 | 173.5168 | 40 | 0 | 2.87
0.61577 | 0.0378 | 0.06618 | 157.233 | 40 | 2.646 | 2.6472
0.62933 | 0.3495 | 0.05098 | 160.8042 | 40 | 26.5042 | 0
0.67198 | 0.7589 | 0.06134 | 189.1828 | 40 | 55.5766 | 0
0.72733 | 0.8572 | 0.05745 | 218.7518 | 40 | 62.302 | 0
0.78877 | 0.8736 | 0.03635 | 242.4808 | 40 | 62.606 | 0
0.84563 | 0.8789 | 0.06519 | 262.0484 | 40 | 64.1306 | 0
0.89209 | 0.8534 | 0.08568 | 276.0046 | 40 | 63.1652 | 0
0.923 | 0.8546 | 0.09175 | 287.1966 | 40 | 63.492 | 0
0.9465 | 0.7679 | 0.08417 | 289.6664 | 40 | 53.753 | 3.3668
0.95197 | 0.6887 | 0.09613 | 286.5236 | 40 | 48.209 | 3.8452
0.94912 | 0.6408 | 0.12932 | 281.6404 | 40 | 44.856 | 5.1728
0.94104 | 0.4326 | 0.15432 | 263.9912 | 40 | 30.282 | 6.1728
0.9205 | 0.2045 | 0.18108 | 233.4994 | 40 | 14.315 | 7.2432
0.88477 | 0.0084 | 0.2532 | 195.7384 | 40 | 0.588 | 10.128
0.85934 | 0 | 0.33535 | 163.2184 | 40 | 0 | 13.414
0.80898 | 0 | 0.42608 | 139.3636 | 40 | 0 | 17.0432
0.74963 | 0 | 0.44886 | 122.355 | 40 | 0 | 17.9544
0.69202 | 0 | 0.48013 | 112.3582 | 40 | 0 | 19.2052
0.65329 | 0 | 0.55216 | 109.1156 | 40 | 0 | 22.0864
0.62148 | 0 | 0.53917 | 108.5344 | 40 | 0 | 21.5668
0.60219 | 0 | 0.51725 | 109.0054 | 40 | 0 | 20.69
0.59174 | 0 | 0.47718 | 108.9186 | 40 | 0 | 19.0872
0.59324 | 0 | 0.47132 | 108.4474 | 40 | 0 | 18.8528
0.61534 | 0 | 0.42296 | 103.8318 | 40 | 0 | 16.9184
0.63265 | 0.0427 | 0.37854 | 98.6974 | 40 | 2.989 | 15.1416
0.64644 | 0.4162 | 0.35523 | 117.3966 | 40 | 43.3432 | 0
0.69021 | 0.7672 | 0.25799 | 152.3992 | 40 | 64.0236 | -1.4211e-14
0.75285 | 0.874 | 0.29212 | 189.979 | 40 | 72.8648 | 0
0.81108 | 0.9053 | 0.26688 | 222.9172 | 40 | 74.0462 | 0
0.86503 | 0.9124 | 0.2071 | 248.5662 | 40 | 72.152 | 0
0.91203 | 0.8877 | 0.16395 | 266.0602 | 40 | 68.697 | 2.8422e-14
0.95075 | 0.8128 | 0.16129 | 274.3328 | 40 | 63.3476 | 0
0.96782 | 0.7309 | 0.20198 | 276.793 | 40 | 51.163 | 8.0792
0.97715 | 0.7758 | 0.22963 | 282.5692 | 40 | 54.306 | 9.1852
0.97385 | 0.7268 | 0.27631 | 287.1126 | 40 | 50.876 | 11.0524
0.96289 | 0.467 | 0.35363 | 277.6588 | 40 | 32.69 | 14.1452
0.92887 | 0.2057 | 0.4355 | 256.5908 | 40 | 14.399 | 17.42
0.89115 | 0.0064 | 0.50352 | 228.0646 | 40 | 0.448 | 20.1408
0.86687 | 0 | 0.52807 | 202.5004 | 40 | 0 | 21.1228
0.82151 | 0 | 0.60896 | 184.7078 | 40 | 0 | 24.3584
0.76837 | 0 | 0.59716 | 171.7572 | 40 | 0 | 23.8864
0.72213 | 0 | 0.58437 | 162.919 | 40 | 0 | 23.3748
0.68154 | 0 | 0.61445 | 159.343 | 40 | 0 | 24.578
0.64998 | 0 | 0.60785 | 158.659 | 40 | 0 | 24.314
0.62543 | 0 | 0.56339 | 158.6516 | 40 | 0 | 22.5356
0.60895 | 0 | 0.54303 | 159.4778 | 40 | 0 | 21.7212
0.59936 | 0 | 0.5175 | 160.2418 | 40 | 0 | 20.7
0.59974 | 0 | 0.54438 | 162.043 | 40 | 0 | 21.7752
0.60057 | 0.0375 | 0.54434 | 166.3846 | 40 | 2.625 | 21.7736
0.61932 | 0.3741 | 0.49934 | 190.6132 | 40 | 46.1606 | 0
0.67116 | 0.7804 | 0.48787 | 237.64 | 40 | 74.1428 | 0
0.73423 | 0.8965 | 0.57904 | 290.1336 | 40 | 85.9166 | 0
0.7895 | 0.918 | 0.5452 | 337.2516 | 40 | 86.068 | 0
0.83907 | 0.89 | 0.47841 | 374.781 | 40 | 81.4364 | 0
0.8828 | 0.8617 | 0.41395 | 403.378 | 40 | 76.877 | 0
0.91236 | 0.8104 | 0.37596 | 423.9084 | 40 | 71.7664 | 0
0.93604 | 0.7027 | 0.37199 | 434.373 | 40 | 49.189 | 14.8796
0.94718 | 0.602 | 0.37023 | 436.6042 | 40 | 42.14 | 14.8092
0.94831 | 0.443 | 0.40887 | 429.138 | 40 | 31.01 | 16.3548
0.93928 | 0.3193 | 0.42882 | 414.7138 | 40 | 22.351 | 17.1528
0.91362 | 0.1389 | 0.53151 | 394.3352 | 40 | 9.723 | 21.2604
0.87086 | 0.0065 | 0.47857 | 366.847 | 40 | 0.455 | 19.1428
0.8516 | 0 | 0.53794 | 343.2046 | 40 | 0 | 21.5176
0.81001 | 0 | 0.60252 | 326.3044 | 40 | 0 | 24.1008
0.76421 | 0 | 0.61338 | 314.4186 | 40 | 0 | 24.5352
0.71711 | 0 | 0.60531 | 306.92 | 40 | 0 | 24.2124
0.67824 | 0 | 0.59748 | 302.9952 | 40 | 0 | 23.8992
0.64724 | 0 | 0.61375 | 302.8212 | 40 | 0 | 24.55
0.62295 | 0 | 0.62482 | 305.519 | 40 | 0 | 24.9928
0.60788 | 0 | 0.60883 | 309.0842 | 40 | 0 | 24.3532
0.59555 | 0 | 0.60478 | 313.7204 | 40 | 0 | 24.1912
0.59383 | 0 | 0.59699 | 318.217 | 40 | 0 | 23.8796
0.58913 | 0.0265 | 0.58658 | 324.6222 | 40 | 1.855 | 23.4632
0.60536 | 0.3293 | 0.58425 | 350.5072 | 40 | 46.421 | 0
0.65905 | 0.7155 | 0.62244 | 399.5848 | 40 | 74.9826 | 0
0.71862 | 0.8105 | 0.67673 | 451.527 | 40 | 83.8042 | 0
0.76821 | 0.8714 | 0.58286 | 499.0184 | 40 | 84.3124 | -5.6843e-14
0.81615 | 0.9167 | 0.46927 | 540.3432 | 40 | 82.9398 | 0
0.85513 | 0.9148 | 0.3558 | 573.0982 | 40 | 78.268 | 0
0.89544 | 0.8964 | 0.32269 | 599.2098 | 40 | 75.6556 | 0
0.9255 | 0.853 | 0.29118 | 618.017 | 40 | 71.3572 | 0
0.94905 | 0.7686 | 0.28127 | 628.1648 | 40 | 53.802 | 11.2508
0.95696 | 0.6434 | 0.30114 | 629.5524 | 40 | 45.038 | 12.0456
0.9536 | 0.5055 | 0.33863 | 623.1226 | 40 | 35.385 | 13.5452
0.92937 | 0.165 | 0.40731 | 598.028 | 40 | 11.55 | 16.2924
0.89536 | 0.0061 | 0.49377 | 568.6698 | 40 | 0.427 | 19.7508
0.87337 | 0 | 0.51869 | 542.0804 | 40 | 0 | 20.7476
0.82541 | 0 | 0.55749 | 521.839 | 40 | 0 | 22.2996
0.76713 | 0 | 0.59294 | 508.8436 | 40 | 0 | 23.7176
0.71209 | 0 | 0.58437 | 501.0094 | 40 | 0 | 23.3748
0.67358 | 0 | 0.59392 | 497.4082 | 40 | 0 | 23.7568
0.64391 | 0 | 0.59335 | 496.7512 | 40 | 0 | 23.734
0.62521 | 0 | 0.53483 | 495.6234 | 40 | 0 | 21.3932
0.6168 | 0 | 0.50266 | 494.0498 | 40 | 0 | 20.1064
0.62313 | 0 | 0.47607 | 490.7796 | 40 | 0 | 19.0428
0.64307 | 0 | 0.47209 | 485.3562 | 40 | 0 | 18.8836
0.66169 | 0.0321 | 0.44821 | 479.3626 | 40 | 2.247 | 17.9284
0.67402 | 0.2301 | 0.40563 | 484.2928 | 40 | 16.107 | 16.2252
0.71275 | 0.5642 | 0.36805 | 507.2338 | 40 | 54.216 | 5.6843e-14
0.76538 | 0.7965 | 0.41813 | 543.176 | 40 | 72.4802 | 0
0.81483 | 0.8468 | 0.3186 | 573.713 | 40 | 72.02 | 0
0.86648 | 0.8733 | 0.26438 | 598.7712 | 40 | 71.7062 | 0
0.91454 | 0.8801 | 0.2727 | 619.8322 | 40 | 72.515 | 0
0.95737 | 0.8923 | 0.29475 | 638.3462 | 40 | 74.251 | 0
0.98346 | 0.9017 | 0.32568 | 656.1464 | 40 | 76.1462 | 0
0.99094 | 0.8833 | 0.34978 | 672.8746 | 40 | 75.8222 | 0
0.98853 | 0.8456 | 0.37777 | 688.3244 | 40 | 74.3028 | 0
0.98051 | 0.6641 | 0.37686 | 691.8348 | 40 | 46.487 | 15.0744
0.95251 | 0.2149 | 0.38703 | 667.108 | 40 | 15.043 | 15.4812
0.91563 | 0.0041 | 0.37072 | 630.6608 | 40 | 0.287 | 14.8288
0.89574 | 0 | 0.4353 | 598.4988 | 40 | 0 | 17.412
0.83954 | 0 | 0.48996 | 574.1432 | 40 | 0 | 19.5984
0.7765 | 0 | 0.53487 | 557.888 | 40 | 0 | 21.3948
0.72058 | 0 | 0.579 | 548.99 | 40 | 0 | 23.16
0.67665 | 0 | 0.58113 | 544.5702 | 40 | 0 | 23.2452
0.64489 | 0 | 0.55798 | 542.4004 | 40 | 0 | 22.3192
0.62254 | 0 | 0.52172 | 541.0152 | 40 | 0 | 20.8688
0.61339 | 0 | 0.47673 | 538.7454 | 40 | 0 | 19.0692
0.61351 | 0 | 0.43509 | 534.798 | 40 | 0 | 17.4036
0.63493 | 0 | 0.37572 | 526.3338 | 40 | 0 | 15.0288
0.65473 | 0.0345 | 0.33294 | 516.5934 | 40 | 2.415 | 13.3176
0.66078 | 0.4067 | 0.26319 | 529.512 | 40 | 38.9966 | 0
0.70065 | 0.7954 | 0.19153 | 562.7862 | 40 | 63.3392 | -1.1369e-13
0.75621 | 0.892 | 0.22349 | 598.5448 | 40 | 71.3796 | 0
0.81244 | 0.8801 | 0.20747 | 627.2066 | 40 | 69.9058 | 0
0.86283 | 0.8842 | 0.17091 | 649.654 | 40 | 68.7304 | 0
0.89476 | 0.8779 | 0.17518 | 668.6382 | 40 | 68.4602 | 0
0.91354 | 0.8979 | 0.18354 | 687.4788 | 40 | 70.1946 | 0
0.93253 | 0.8798 | 0.20181 | 700 | 40 | 65.7742 | 0
0.95024 | 0.8293 | 0.22857 | 700 | 40 | 55.024 | 0
0.9564 | 0.7982 | 0.2795 | 700 | 40 | 55.64 | 0
0.94843 | 0.6434 | 0.30643 | 700 | 40 | 45.038 | 9.805
0.92133 | 0.2228 | 0.36306 | 677.9854 | 40 | 15.596 | 14.5224
0.88659 | 0.0053 | 0.35306 | 643.8198 | 40 | 0.371 | 14.1224
0.86263 | 0 | 0.35695 | 611.8348 | 40 | 0 | 14.278
0.81064 | 0 | 0.40756 | 587.0732 | 40 | 0 | 16.3024
0.74513 | 0 | 0.44956 | 570.5426 | 40 | 0 | 17.9824
0.69132 | 0 | 0.46403 | 559.9718 | 40 | 0 | 18.5612
0.65152 | 0 | 0.44824 | 552.7494 | 40 | 0 | 17.9296
0.61813 | 0 | 0.43006 | 548.1388 | 40 | 0 | 17.2024
0.59671 | 0 | 0.42283 | 545.381 | 40 | 0 | 16.9132
0.58659 | 0 | 0.41968 | 543.5092 | 40 | 0 | 16.7872
0.59057 | 0 | 0.4196 | 541.2362 | 40 | 0 | 16.784
0.6147 | 0 | 0.41257 | 536.269 | 40 | 0 | 16.5028
0.63656 | 0.0323 | 0.36378 | 529.4252 | 40 | 2.261 | 14.5512
0.64272 | 0.3963 | 0.29228 | 544.5854 | 40 | 39.4322 | 0
0.68075 | 0.7852 | 0.21016 | 579.8808 | 40 | 63.3704 | 0
0.73526 | 0.8677 | 0.26223 | 617.583 | 40 | 71.2282 | 0
0.79033 | 0.9151 | 0.20782 | 650.9198 | 40 | 72.3698 | 0
0.84088 | 0.8991 | 0.14053 | 675.39 | 40 | 68.5582 | 0
0.88596 | 0.8763 | 0.14218 | 693.8222 | 40 | 67.0282 | 0
0.92412 | 0.8584 | 0.1503 | 700 | 40 | 58.5898 | 0
0.94476 | 0.8356 | 0.16714 | 700 | 40 | 54.476 | 0
0.95661 | 0.8155 | 0.1831 | 700 | 40 | 55.661 | 0
0.96295 | 0.7924 | 0.24021 | 700 | 40 | 55.468 | 0.827
0.9516 | 0.6522 | 0.31353 | 700 | 40 | 45.654 | 9.506
0.92309 | 0.2552 | 0.39908 | 681.5182 | 40 | 17.864 | 15.9632
0.88377 | 0.005 | 0.4305 | 650.7112 | 40 | 0.35 | 17.22
0.86021 | 0 | 0.43576 | 622.1206 | 40 | 0 | 17.4304
0.80734 | 0 | 0.47671 | 600.455 | 40 | 0 | 19.0684
0.74458 | 0 | 0.498 | 585.917 | 40 | 0 | 19.92
0.68843 | 0 | 0.4984 | 577.01 | 40 | 0 | 19.936
0.64578 | 0 | 0.48011 | 571.6364 | 40 | 0 | 19.2044
0.61543 | 0 | 0.4242 | 567.0614 | 40 | 0 | 16.968
0.59287 | 0 | 0.3721 | 562.6584 | 40 | 0 | 14.884
0.58216 | 0 | 0.34568 | 558.2696 | 40 | 0 | 13.8272
0.58507 | 0 | 0.28723 | 551.2518 | 40 | 0 | 11.4892
0.61085 | 0 | 0.23771 | 539.6752 | 40 | 0 | 9.5084
0.63332 | 0.0307 | 0.2186 | 527.2362 | 40 | 2.149 | 8.744
0.64112 | 0.3535 | 0.17817 | 534.996 | 40 | 31.8718 | 0
0.68183 | 0.7725 | 0.14582 | 566.7208 | 40 | 59.9078 | 0
0.73242 | 0.8638 | 0.16719 | 600.6324 | 40 | 67.1536 | 0
0.78252 | 0.8983 | 0.11645 | 629.9194 | 40 | 67.539 | 0
0.82761 | 0.8633 | 0.08466 | 650.9758 | 40 | 63.8174 | 0
0.87343 | 0.8391 | 0.07065 | 665.1958 | 40 | 61.563 | 0
0.91319 | 0.7692 | 0.11152 | 672.1816 | 40 | 58.3048 | 0
0.9371 | 0.6865 | 0.15907 | 672.8894 | 40 | 48.055 | 6.3628
0.9502 | 0.5579 | 0.17942 | 664.0992 | 40 | 39.053 | 7.1768
0.95255 | 0.4028 | 0.22071 | 645.8686 | 40 | 28.196 | 8.8284
0.94005 | 0.3779 | 0.32872 | 631.4654 | 40 | 26.453 | 13.1488
0.90992 | 0.0786 | 0.36567 | 600.6022 | 40 | 5.502 | 14.6268
0.87065 | 0.0007 | 0.36862 | 568.331 | 40 | 0.049 | 14.7448
0.84693 | 0 | 0.39863 | 539.5832 | 40 | 0 | 15.9452
0.79802 | 0 | 0.44238 | 517.4764 | 40 | 0 | 17.6952
0.73832 | 0 | 0.44618 | 501.4916 | 40 | 0 | 17.8472
0.68497 | 0 | 0.41475 | 489.5846 | 40 | 0 | 16.59
0.64546 | 0 | 0.46003 | 483.4398 | 40 | 0 | 18.4012
0.6182 | 0 | 0.4999 | 481.6158 | 40 | 0 | 19.996
0.5966 | 0 | 0.38543 | 477.373 | 40 | 0 | 15.4172
0.58682 | 0 | 0.29107 | 470.3338 | 40 | 0 | 11.6428
0.59075 | 0 | 0.23254 | 460.5604 | 40 | 0 | 9.3016
0.61341 | 0 | 0.24131 | 448.8718 | 40 | 0 | 9.6524
0.63546 | 0.0199 | 0.18391 | 434.0752 | 40 | 1.393 | 7.3564
0.64236 | 0.3157 | 0.13503 | 437.3394 | 40 | 22.099 | 5.4012
0.68208 | 0.713 | 0.0683 | 461.7734 | 40 | 52.642 | 5.6843e-14
0.72791 | 0.8247 | 0.08628 | 490.1626 | 40 | 61.1802 | 0
0.7792 | 0.8491 | 0.05449 | 513.8592 | 40 | 61.6166 | 5.6843e-14
0.82253 | 0.8817 | 0.02403 | 534.2864 | 40 | 62.6802 | 0
0.85427 | 0.8706 | 0.03732 | 551.2942 | 40 | 62.4348 | 0
0.87412 | 0.7946 | 0.07145 | 562.3622 | 40 | 58.48 | 0
0.88232 | 0.6842 | 0.15083 | 568.0574 | 40 | 47.894 | 6.0332
0.88512 | 0.6689 | 0.24874 | 576.318 | 40 | 46.823 | 9.9496
0.87391 | 0.5294 | 0.34443 | 579.7622 | 40 | 37.058 | 13.7772
0.84602 | 0.3525 | 0.42768 | 576.9424 | 40 | 24.675 | 17.1072
0.80927 | 0.0775 | 0.45999 | 559.84 | 40 | 5.425 | 18.3996
0.7816 | 0.0006 | 0.41754 | 538.4236 | 40 | 0.042 | 16.7016
0.76554 | 0 | 0.46738 | 520.5648 | 40 | 0 | 18.6952
0.72988 | 0 | 0.44371 | 505.3252 | 40 | 0 | 17.7484
0.68548 | 0 | 0.42618 | 493.8244 | 40 | 0 | 17.0472
0.64103 | 0 | 0.30933 | 482.0946 | 40 | 0 | 12.3732
0.60644 | 0 | 0.27293 | 472.3678 | 40 | 0 | 10.9172
0.58019 | 0 | 0.20071 | 462.3772 | 40 | 0 | 8.0284
0.56077 | 0 | 0.17559 | 453.3238 | 40 | 0 | 7.0236
0.54896 | 0 | 0.14566 | 444.2542 | 40 | 0 | 5.8264
0.54397 | 0 | 0.11201 | 434.3376 | 40 | 0 | 4.4804
0.5498 | 0 | 0.12231 | 424.25 | 40 | 0 | 4.8924
0.55753 | 0.0263 | 0.103 | 414.458 | 40 | 1.841 | 4.12
0.57417 | 0.3444 | 0.05429 | 423.3206 | 40 | 26.2796 | 0
0.61606 | 0.7067 | 0.0231 | 452.1076 | 40 | 50.393 | 0
0.66127 | 0.7963 | 0.03163 | 482.9868 | 40 | 57.0062 | 0
0.71402 | 0.838 | 0.02904 | 511.4064 | 40 | 59.8216 | 0
0.76396 | 0.8618 | 0.01709 | 536.02 | 40 | 61.0096 | 5.6843e-14
0.80242 | 0.8492 | 0.03046 | 556.4404 | 40 | 60.6624 | 0
0.84022 | 0.8022 | 0.05938 | 570.9476 | 40 | 58.5292 | 1.1369e-13
0.86296 | 0.7986 | 0.1276 | 585.6576 | 40 | 61.006 | 0
0.87182 | 0.7476 | 0.16521 | 597.416 | 40 | 58.9404 | 0
0.85996 | 0.7121 | 0.19598 | 609.1062 | 40 | 57.6862 | 0
0.83771 | 0.5492 | 0.26094 | 614.2168 | 40 | 38.444 | 10.4376
0.80151 | 0.1863 | 0.28743 | 598.604 | 40 | 13.041 | 11.4972
0.77756 | 0.0034 | 0.35073 | 575.1152 | 40 | 0.238 | 14.0292
0.75703 | 0 | 0.37004 | 554.2138 | 40 | 0 | 14.8016
0.72202 | 0 | 0.41297 | 538.5306 | 40 | 0 | 16.5188
0.68098 | 0 | 0.40962 | 526.8174 | 40 | 0 | 16.3848
0.63848 | 0 | 0.43765 | 520.4754 | 40 | 0 | 17.506
0.6056 | 0 | 0.41346 | 516.4538 | 40 | 0 | 16.5384
0.57889 | 0 | 0.39132 | 514.2176 | 40 | 0 | 15.6528
0.56023 | 0 | 0.37105 | 513.0366 | 40 | 0 | 14.842
0.5459 | 0 | 0.36333 | 512.9798 | 40 | 0 | 14.5332
0.54158 | 0 | 0.33914 | 512.3874 | 40 | 0 | 13.5656
0.5415 | 0 | 0.29899 | 510.197 | 40 | 0 | 11.9596
0.54225 | 0.0267 | 0.29967 | 509.8278 | 40 | 1.869 | 11.9868
0.55976 | 0.374 | 0.2741 | 530.9958 | 40 | 37.144 | 0
0.60486 | 0.7834 | 0.18888 | 572.903 | 40 | 62.3932 | 0
0.66152 | 0.8831 | 0.19687 | 616.4428 | 40 | 69.6918 | 0
0.72074 | 0.9061 | 0.18956 | 655.3782 | 40 | 71.0094 | 0
0.77761 | 0.9173 | 0.18799 | 689.3478 | 40 | 71.7306 | 0
0.81479 | 0.9024 | 0.22676 | 700 | 40 | 52.1312 | 0
0.83633 | 0.8838 | 0.23189 | 700 | 40 | 43.633 | 0
0.85517 | 0.867 | 0.26296 | 700 | 40 | 45.517 | 0
0.87153 | 0.8568 | 0.23622 | 700 | 40 | 47.153 | 0
0.88221 | 0.828 | 0.20713 | 700 | 40 | 48.221 | 0
0.87832 | 0.6601 | 0.20584 | 700 | 40 | 46.207 | 1.625
0.86601 | 0.2145 | 0.26982 | 679.2068 | 40 | 15.015 | 10.7928
0.83805 | 0.003 | 0.33958 | 649.195 | 40 | 0.21 | 13.5832
0.82175 | 0 | 0.46124 | 625.4696 | 40 | 0 | 18.4496
0.77797 | 0 | 0.55427 | 609.8434 | 40 | 0 | 22.1708
0.7229 | 0 | 0.5781 | 600.6774 | 40 | 0 | 23.124
0.67392 | 0 | 0.57382 | 596.2382 | 40 | 0 | 22.9528
0.6406 | 0 | 0.58723 | 595.6674 | 40 | 0 | 23.4892
0.61577 | 0 | 0.59038 | 597.7056 | 40 | 0 | 23.6152
0.6018 | 0 | 0.58331 | 600.858 | 40 | 0 | 23.3324
0.59581 | 0 | 0.57515 | 604.283 | 40 | 0 | 23.006
0.60458 | 0 | 0.57236 | 606.7194 | 40 | 0 | 22.8944
0.63611 | 0 | 0.55124 | 605.158 | 40 | 0 | 22.0496
0.66202 | 0.0263 | 0.52531 | 601.8094 | 40 | 1.841 | 21.0124
0.66341 | 0.3958 | 0.48608 | 622.6176 | 40 | 47.1492 | 0
0.70188 | 0.8235 | 0.41172 | 666.5434 | 40 | 74.1138 | 0
0.75655 | 0.9109 | 0.44343 | 700 | 40 | 69.1116 | 0
0.81536 | 0.9331 | 0.42554 | 700 | 40 | 41.536 | 0
0.87063 | 0.929 | 0.37824 | 700 | 40 | 47.063 | 0
0.92015 | 0.9118 | 0.33534 | 700 | 40 | 52.015 | 0
0.96014 | 0.8941 | 0.33344 | 700 | 40 | 56.014 | 0
0.98962 | 0.8487 | 0.36382 | 700 | 40 | 58.962 | 0
0.99599 | 0.8319 | 0.37379 | 700 | 40 | 58.233 | 1.366
0.9962 | 0.8307 | 0.37561 | 700 | 40 | 58.149 | 1.471
0.99502 | 0.6501 | 0.42154 | 700 | 40 | 45.507 | 13.995
0.97106 | 0.1963 | 0.47982 | 675.8278 | 40 | 13.741 | 19.1928
0.9352 | 0.0024 | 0.5495 | 644.4558 | 40 | 0.168 | 21.98
0.91331 | 0 | 0.65153 | 619.186 | 40 | 0 | 26.0612
0.85894 | 0 | 0.67944 | 600.4696 | 40 | 0 | 27.1776
0.7957 | 0 | 0.68494 | 588.2972 | 40 | 0 | 27.3976
0.73943 | 0 | 0.65331 | 580.4866 | 40 | 0 | 26.1324
0.70081 | 0 | 0.64269 | 576.1132 | 40 | 0 | 25.7076
0.66983 | 0 | 0.61465 | 573.7162 | 40 | 0 | 24.586
0.64642 | 0 | 0.58444 | 572.4518 | 40 | 0 | 23.3776
0.63584 | 0 | 0.52838 | 570.003 | 40 | 0 | 21.1352
0.63707 | 0 | 0.5264 | 567.352 | 40 | 0 | 21.056
0.65618 | 0 | 0.50709 | 562.0176 | 40 | 0 | 20.2836
0.67069 | 0.0114 | 0.46746 | 554.445 | 40 | 0.798 | 18.6984
0.66302 | 0.1493 | 0.44161 | 556.2584 | 40 | 10.451 | 17.6644
0.68183 | 0.4577 | 0.43773 | 577.6236 | 40 | 49.5482 | 0
0.71062 | 0.7117 | 0.48188 | 615.6558 | 40 | 69.0942 | 0
0.73753 | 0.7916 | 0.46787 | 656.0296 | 40 | 74.1268 | 0
0.76496 | 0.8013 | 0.48471 | 695.013 | 40 | 75.4794 | 0
0.7948 | 0.7813 | 0.47833 | 700 | 40 | 44.467 | 0
0.81785 | 0.7483 | 0.45401 | 700 | 40 | 41.785 | 0
0.81974 | 0.7396 | 0.45535 | 700 | 40 | 41.974 | 0
0.81964 | 0.6663 | 0.436 | 700 | 40 | 41.964 | 0
0.82056 | 0.5849 | 0.40837 | 700 | 40 | 40.943 | 1.113
0.80768 | 0.3869 | 0.4156 | 700 | 40 | 27.083 | 13.685
0.78853 | 0.0783 | 0.40183 | 682.7012 | 40 | 5.481 | 16.0732
0.77411 | 0.0003 | 0.35146 | 659.3696 | 40 | 0.021 | 14.0584
0.76055 | 0 | 0.29386 | 635.069 | 40 | 0 | 11.7544
0.71811 | 0 | 0.29281 | 614.9704 | 40 | 0 | 11.7124
0.66605 | 0 | 0.2794 | 599.5414 | 40 | 0 | 11.176
0.6193 | 0 | 0.27923 | 588.7806 | 40 | 0 | 11.1692
0.58715 | 0 | 0.26174 | 580.5352 | 40 | 0 | 10.4696
0.56415 | 0 | 0.22842 | 573.257 | 40 | 0 | 9.1368
0.54799 | 0 | 0.18335 | 565.792 | 40 | 0 | 7.334
0.54261 | 0 | 0.1571 | 557.815 | 40 | 0 | 6.284
0.54944 | 0 | 0.13194 | 548.1486 | 40 | 0 | 5.2776
0.58059 | 0 | 0.12625 | 535.1396 | 40 | 0 | 5.05
0.6109 | 0.0073 | 0.09887 | 518.5154 | 40 | 0.511 | 3.9548
0.61698 | 0.1144 | 0.09531 | 508.6378 | 40 | 8.008 | 3.8124
0.6521 | 0.4536 | 0.08566 | 518.6062 | 40 | 35.1784 | 0
0.69275 | 0.6965 | 0.10626 | 542.3366 | 40 | 53.0054 | 0
0.74026 | 0.6641 | 0.08505 | 558.1996 | 40 | 49.889 | 0
0.78483 | 0.7107 | 0.05117 | 571.5124 | 40 | 51.7958 | 0
0.82816 | 0.7818 | 0.06474 | 586.012 | 40 | 57.3156 | 0
0.86022 | 0.8091 | 0.09834 | 600.5606 | 40 | 60.5706 | 1.1369e-13
0.885 | 0.8408 | 0.138 | 616.4366 | 40 | 64.376 | 0
0.90078 | 0.7749 | 0.13715 | 626.0876 | 40 | 59.729 | 0
0.89894 | 0.7332 | 0.17935 | 634.6916 | 40 | 58.498 | 0
0.87561 | 0.5457 | 0.25169 | 635.3972 | 40 | 38.199 | 10.0676
0.84484 | 0.1478 | 0.26695 | 611.9372 | 40 | 10.346 | 10.678
0.81629 | 0.0004 | 0.27071 | 581.1646 | 40 | 0.028 | 10.8284
0.79402 | 0 | 0.30782 | 554.0754 | 40 | 0 | 12.3128
0.74253 | 0 | 0.33678 | 533.2936 | 40 | 0 | 13.4712
0.6836 | 0 | 0.36695 | 519.6116 | 40 | 0 | 14.678
0.6327 | 0 | 0.39578 | 512.1728 | 40 | 0 | 15.8312
0.59717 | 0 | 0.42175 | 509.3258 | 40 | 0 | 16.87
0.57142 | 0 | 0.41985 | 508.9778 | 40 | 0 | 16.794
0.55543 | 0 | 0.38645 | 508.8928 | 40 | 0 | 15.458
0.54656 | 0 | 0.36885 | 508.9908 | 40 | 0 | 14.754
0.55327 | 0 | 0.37321 | 508.5922 | 40 | 0 | 14.9284
0.58419 | 0 | 0.37293 | 505.0904 | 40 | 0 | 14.9172
0.60929 | 0.0217 | 0.39461 | 501.4648 | 40 | 1.519 | 15.7844
0.61539 | 0.3481 | 0.36909 | 519.0564 | 40 | 39.1306 | 0
0.65202 | 0.7679 | 0.26118 | 558.0546 | 40 | 64.2002 | 0
0.70399 | 0.8937 | 0.26388 | 600.7698 | 40 | 73.1142 | 0
0.76072 | 0.9203 | 0.2966 | 640.9828 | 40 | 76.285 | 0
0.81467 | 0.9329 | 0.25758 | 675.122 | 40 | 75.6062 | 0
0.86307 | 0.9327 | 0.20306 | 700 | 40 | 71.185 | 0
0.90556 | 0.9211 | 0.21328 | 700 | 40 | 50.556 | 0
0.93386 | 0.8993 | 0.2443 | 700 | 40 | 53.386 | 0
0.95111 | 0.8833 | 0.2548 | 700 | 40 | 55.111 | 0
0.95128 | 0.8144 | 0.28593 | 700 | 40 | 55.128 | 0
0.93751 | 0.568 | 0.33347 | 699.3478 | 40 | 39.76 | 13.3388
0.90552 | 0.1475 | 0.38456 | 674.5032 | 40 | 10.325 | 15.3824
0.86968 | 0.0003 | 0.39849 | 643.4958 | 40 | 0.021 | 15.9396
0.84547 | 0 | 0.47373 | 617.898 | 40 | 0 | 18.9492
0.79356 | 0 | 0.5146 | 599.126 | 40 | 0 | 20.584
0.73287 | 0 | 0.5314 | 587.095 | 40 | 0 | 21.256
0.68204 | 0 | 0.55248 | 580.9902 | 40 | 0 | 22.0992
0.63966 | 0 | 0.54396 | 578.7826 | 40 | 0 | 21.7584
0.60997 | 0 | 0.50567 | 578.0124 | 40 | 0 | 20.2268
0.58895 | 0 | 0.46638 | 577.7726 | 40 | 0 | 18.6552
0.57407 | 0 | 0.40883 | 576.7188 | 40 | 0 | 16.3532
0.57944 | 0 | 0.37777 | 573.8856 | 40 | 0 | 15.1108
0.60442 | 0 | 0.34684 | 567.3172 | 40 | 0 | 13.8736
0.6294 | 0.0148 | 0.33262 | 558.718 | 40 | 1.036 | 13.3048
0.63211 | 0.2958 | 0.32054 | 569.0346 | 40 | 20.706 | 12.8216
0.66789 | 0.7491 | 0.25847 | 605.0214 | 40 | 62.7758 | 0
0.71467 | 0.869 | 0.22539 | 643.4 | 40 | 69.8456 | 0
0.76448 | 0.8908 | 0.21417 | 677.8748 | 40 | 70.9228 | 0
0.81343 | 0.8594 | 0.19228 | 700 | 40 | 63.4682 | 0
0.85631 | 0.8507 | 0.20815 | 700 | 40 | 45.631 | 0
0.87444 | 0.7777 | 0.23234 | 700 | 40 | 47.444 | 0
0.85844 | 0.7731 | 0.28202 | 700 | 40 | 45.844 | 0
0.84937 | 0.5741 | 0.30261 | 700 | 40 | 40.187 | 4.75
0.833 | 0.4548 | 0.31255 | 700 | 40 | 31.836 | 11.464
0.80674 | 0.2377 | 0.36242 | 690.4618 | 40 | 16.639 | 14.4968
0.77145 | 0.075 | 0.39033 | 674.18 | 40 | 5.25 | 15.6132
0.7474 | 0.001 | 0.39284 | 655.2236 | 40 | 0.07 | 15.7136
0.72826 | 0 | 0.41537 | 639.0124 | 40 | 0 | 16.6148
0.69209 | 0 | 0.45168 | 627.8706 | 40 | 0 | 18.0672
0.65333 | 0 | 0.46509 | 621.1412 | 40 | 0 | 18.6036
0.61158 | 0 | 0.46795 | 618.7012 | 40 | 0 | 18.718
0.57666 | 0 | 0.41372 | 617.584 | 40 | 0 | 16.5488
0.5495 | 0 | 0.34417 | 616.4008 | 40 | 0 | 13.7668
0.52996 | 0 | 0.27503 | 614.406 | 40 | 0 | 11.0012
0.51712 | 0 | 0.22709 | 611.7776 | 40 | 0 | 9.0836
0.51177 | 0 | 0.2006 | 608.6246 | 40 | 0 | 8.024
0.51582 | 0 | 0.16994 | 603.8402 | 40 | 0 | 6.7976
0.52171 | 0.0208 | 0.14818 | 599.0524 | 40 | 1.456 | 5.9272
0.53821 | 0.3585 | 0.11308 | 614.8496 | 40 | 29.6182 | 0
0.57965 | 0.7702 | 0.05929 | 653.1702 | 40 | 56.2856 | 0
0.62625 | 0.8769 | 0.06732 | 694.621 | 40 | 64.0758 | 0
0.67037 | 0.9128 | 0.05032 | 700 | 40 | 32.416 | 0
0.71345 | 0.8768 | 0.04665 | 700 | 40 | 31.345 | 0
0.74771 | 0.8753 | 0.0456 | 700 | 40 | 34.771 | 0
0.77478 | 0.8115 | 0.04842 | 700 | 40 | 37.478 | 0
0.79465 | 0.7613 | 0.07379 | 700 | 40 | 39.465 | 0
0.80557 | 0.735 | 0.121 | 700 | 40 | 40.557 | 0
0.80599 | 0.6231 | 0.13493 | 700 | 40 | 40.599 | 0
0.79567 | 0.4392 | 0.18824 | 698.7066 | 40 | 30.744 | 7.5296
0.77144 | 0.1092 | 0.23448 | 678.5858 | 40 | 7.644 | 9.3792
0.74144 | 0.0007 | 0.24531 | 654.3032 | 40 | 0.049 | 9.8124
0.72103 | 0 | 0.25851 | 632.5406 | 40 | 0 | 10.3404
0.68213 | 0 | 0.28553 | 615.7488 | 40 | 0 | 11.4212
0.64103 | 0 | 0.31647 | 604.3046 | 40 | 0 | 12.6588
0.60117 | 0 | 0.29159 | 595.8512 | 40 | 0 | 11.6636
0.56572 | 0 | 0.30528 | 591.4904 | 40 | 0 | 12.2112
0.54075 | 0 | 0.27757 | 588.5182 | 40 | 0 | 11.1028
0.51987 | 0 | 0.25148 | 586.5904 | 40 | 0 | 10.0592
0.50653 | 0 | 0.20015 | 583.9434 | 40 | 0 | 8.006
0.50023 | 0 | 0.17822 | 581.0492 | 40 | 0 | 7.1288
0.50074 | 0 | 0.14325 | 576.7052 | 40 | 0 | 5.73
0.49879 | 0.0148 | 0.09454 | 571.6438 | 40 | 1.036 | 3.7816
0.51549 | 0.3255 | 0.05876 | 585.2302 | 40 | 25.1354 | 0
0.56585 | 0.7365 | 0.01918 | 620.9674 | 40 | 52.3222 | 0
0.6292 | 0.8375 | 0.0088 | 657.0244 | 40 | 58.977 | 0
0.68649 | 0.8943 | 0.01115 | 691.4224 | 40 | 63.047 | 0
0.73943 | 0.8921 | 0.01268 | 700 | 40 | 42.5206 | 0
0.78537 | 0.8188 | 0.02948 | 700 | 40 | 38.537 | 0
0.81992 | 0.7356 | 0.03998 | 700 | 40 | 41.992 | 0
0.84724 | 0.6656 | 0.05981 | 700 | 40 | 44.724 | 0
0.85899 | 0.6585 | 0.09648 | 700 | 40 | 45.899 | 0
0.86204 | 0.591 | 0.15314 | 700 | 40 | 41.37 | 4.834
0.84831 | 0.2205 | 0.18852 | 678.1448 | 40 | 15.435 | 7.5408
0.81818 | 0.0513 | 0.23513 | 649.323 | 40 | 3.591 | 9.4052
0.78173 | 0.0006 | 0.21223 | 619.6812 | 40 | 0.042 | 8.4892
0.75191 | 0 | 0.25039 | 594.5058 | 40 | 0 | 10.0156
0.70945 | 0 | 0.31263 | 576.066 | 40 | 0 | 12.5052
0.6644 | 0 | 0.30972 | 562.0148 | 40 | 0 | 12.3888
0.61946 | 0 | 0.27248 | 550.968 | 40 | 0 | 10.8992
0.58341 | 0 | 0.23028 | 541.8382 | 40 | 0 | 9.2112
0.55501 | 0 | 0.21166 | 534.8036 | 40 | 0 | 8.4664
0.53495 | 0 | 0.17935 | 528.4826 | 40 | 0 | 7.174
0.52393 | 0 | 0.16259 | 522.5932 | 40 | 0 | 6.5036
0.51853 | 0 | 0.14596 | 516.5786 | 40 | 0 | 5.8384
0.52072 | 0 | 0.1323 | 509.7986 | 40 | 0 | 5.292
0.51951 | 0.0232 | 0.11946 | 504.25 | 40 | 1.624 | 4.7784
0.52939 | 0.3785 | 0.10262 | 521.9108 | 40 | 30.5998 | 5.6843e-14
0.57929 | 0.8153 | 0.05052 | 563.0736 | 40 | 59.0918 | 0
0.64458 | 0.897 | 0.04511 | 603.21 | 40 | 64.5944 | 0
0.71343 | 0.902 | 0.05109 | 637.0506 | 40 | 65.1836 | 0
0.77255 | 0.8963 | 0.05933 | 664.9098 | 40 | 65.1142 | 0
0.81856 | 0.8962 | 0.07605 | 688.8298 | 40 | 65.776 | 0
0.85028 | 0.8627 | 0.09503 | 700 | 40 | 56.1982 | 0
0.87473 | 0.8639 | 0.12883 | 700 | 40 | 47.473 | 0
0.88946 | 0.8374 | 0.13295 | 700 | 40 | 48.946 | 0
0.89578 | 0.8148 | 0.15339 | 700 | 40 | 49.578 | 0
0.88349 | 0.6116 | 0.18174 | 700 | 40 | 42.812 | 5.537
0.85149 | 0.1527 | 0.2411 | 675.184 | 40 | 10.689 | 9.644
0.82101 | 0.0003 | 0.25104 | 643.1456 | 40 | 0.021 | 10.0416
0.78771 | 0 | 0.29292 | 616.0914 | 40 | 0 | 11.7168
0.73437 | 0 | 0.33751 | 596.1548 | 40 | 0 | 13.5004
0.67261 | 0 | 0.35976 | 583.2842 | 40 | 0 | 14.3904
0.6181 | 0 | 0.36142 | 575.931 | 40 | 0 | 14.4568
0.57902 | 0 | 0.33617 | 571.4758 | 40 | 0 | 13.4468
0.55084 | 0 | 0.31008 | 568.795 | 40 | 0 | 12.4032
0.53164 | 0 | 0.29042 | 567.2478 | 40 | 0 | 11.6168
0.52441 | 0 | 0.27664 | 565.8724 | 40 | 0 | 11.0656
0.53192 | 0 | 0.2745 | 563.6604 | 40 | 0 | 10.98
0.55929 | 0 | 0.25839 | 558.067 | 40 | 0 | 10.3356
0.58957 | 0.022 | 0.25686 | 550.9244 | 40 | 1.54 | 10.2744
0.59597 | 0.3634 | 0.23783 | 566.2786 | 40 | 34.9512 | 0
0.63405 | 0.8108 | 0.14103 | 605.2708 | 40 | 62.3972 | 0
0.69008 | 0.9084 | 0.13469 | 645.2384 | 40 | 68.9756 | 0
0.74759 | 0.9208 | 0.14353 | 680.6766 | 40 | 70.1972 | 0
0.79752 | 0.9023 | 0.10941 | 700 | 40 | 59.0754 | 0
0.84368 | 0.8726 | 0.10488 | 700 | 40 | 44.368 | 0
0.88252 | 0.8376 | 0.10601 | 700 | 40 | 48.252 | 0
0.90317 | 0.7977 | 0.09971 | 700 | 40 | 50.317 | 0
0.91678 | 0.7563 | 0.09398 | 700 | 40 | 51.678 | 0
0.91897 | 0.7596 | 0.12112 | 700 | 40 | 51.897 | 0
0.90632 | 0.5592 | 0.14632 | 694.3648 | 40 | 39.144 | 5.8528
0.87314 | 0.1476 | 0.17572 | 664.4116 | 40 | 10.332 | 7.0288
0.84323 | 0.0001 | 0.22103 | 628.9368 | 40 | 0.007 | 8.8412
0.81312 | 0 | 0.31416 | 600.1912 | 40 | 0 | 12.5664
0.75656 | 0 | 0.38823 | 580.0644 | 40 | 0 | 15.5292
0.69513 | 0 | 0.4161 | 567.1954 | 40 | 0 | 16.644
0.64112 | 0 | 0.42002 | 559.8842 | 40 | 0 | 16.8008
0.60141 | 0 | 0.38789 | 555.2588 | 40 | 0 | 15.5156
0.57422 | 0 | 0.34951 | 551.8172 | 40 | 0 | 13.9804
0.55622 | 0 | 0.31284 | 548.7088 | 40 | 0 | 12.5136
0.54487 | 0 | 0.26799 | 544.9414 | 40 | 0 | 10.7196
0.55225 | 0 | 0.24412 | 539.4812 | 40 | 0 | 9.7648
0.5776 | 0 | 0.22026 | 530.5316 | 40 | 0 | 8.8104
0.60553 | 0.0192 | 0.20502 | 519.5234 | 40 | 1.344 | 8.2008
0.6097 | 0.3501 | 0.17342 | 529.9972 | 40 | 31.4438 | 0
0.65186 | 0.7941 | 0.1407 | 566.0262 | 40 | 61.215 | 0
0.70906 | 0.905 | 0.13934 | 604.0438 | 40 | 68.9236 | 1.1369e-13
0.76412 | 0.8805 | 0.16603 | 635.908 | 40 | 68.2762 | 0
0.81135 | 0.766 | 0.17832 | 655.5258 | 40 | 60.7528 | 0
0.85044 | 0.8091 | 0.21978 | 675.91 | 40 | 65.4282 | 0
0.88726 | 0.7277 | 0.23163 | 687.3882 | 40 | 60.2042 | 0
0.90361 | 0.7743 | 0.24073 | 700 | 40 | 62.9728 | 0
0.91762 | 0.7443 | 0.22525 | 700 | 40 | 51.762 | 0
0.91737 | 0.668 | 0.22996 | 700 | 40 | 46.76 | 4.977
0.90725 | 0.4412 | 0.22306 | 689.0814 | 40 | 30.884 | 8.9224
0.87348 | 0.106 | 0.23247 | 658.4522 | 40 | 7.42 | 9.2988
0.84529 | 0.0001 | 0.26906 | 624.6926 | 40 | 0.007 | 10.7624
0.81049 | 0 | 0.30657 | 595.9064 | 40 | 0 | 12.2628
0.75332 | 0 | 0.34843 | 574.5116 | 40 | 0 | 13.9372
0.68797 | 0 | 0.3766 | 560.7786 | 40 | 0 | 15.064
0.63345 | 0 | 0.36708 | 552.1168 | 40 | 0 | 14.6832
0.59189 | 0 | 0.36197 | 547.4066 | 40 | 0 | 14.4788
0.56538 | 0 | 0.349 | 544.8286 | 40 | 0 | 13.96
0.54408 | 0 | 0.30467 | 542.6074 | 40 | 0 | 12.1868
0.53357 | 0 | 0.26983 | 540.0436 | 40 | 0 | 10.7932
0.53721 | 0 | 0.27155 | 537.1846 | 40 | 0 | 10.862
0.56523 | 0 | 0.26245 | 531.1596 | 40 | 0 | 10.498
0.59326 | 0.0184 | 0.23879 | 522.6732 | 40 | 1.288 | 9.5516
0.59548 | 0.3392 | 0.2071 | 535.1532 | 40 | 32.028 | 0
0.63443 | 0.7693 | 0.13057 | 570.784 | 40 | 59.0738 | 0
0.68989 | 0.8556 | 0.15168 | 607.7542 | 40 | 65.9592 | 0
0.75015 | 0.8772 | 0.1751 | 641.1472 | 40 | 68.408 | 0
0.80303 | 0.8041 | 0.1257 | 662.1592 | 40 | 61.315 | 0
0.84574 | 0.7714 | 0.09605 | 675.4252 | 40 | 57.84 | 0
0.88035 | 0.8174 | 0.10164 | 688.6738 | 40 | 61.2836 | 0
0.89967 | 0.8563 | 0.09142 | 700 | 40 | 61.2932 | 0
0.91088 | 0.786 | 0.09709 | 700 | 40 | 51.088 | 0
0.9134 | 0.7433 | 0.07817 | 700 | 40 | 51.34 | 0
0.90337 | 0.5305 | 0.10263 | 690.9032 | 40 | 37.135 | 4.1052
0.87377 | 0.1261 | 0.10215 | 656.4392 | 40 | 8.827 | 4.086
0.84405 | 0 | 0.13152 | 617.295 | 40 | 0 | 5.2608
0.80863 | 0 | 0.18827 | 583.9628 | 40 | 0 | 7.5308
0.75596 | 0 | 0.25399 | 558.5264 | 40 | 0 | 10.1596
0.69292 | 0 | 0.29374 | 540.984 | 40 | 0 | 11.7496
0.63935 | 0 | 0.30475 | 529.239 | 40 | 0 | 12.19
0.5986 | 0 | 0.31097 | 521.8178 | 40 | 0 | 12.4388
0.56934 | 0 | 0.31193 | 517.361 | 40 | 0 | 12.4772
0.54888 | 0 | 0.27861 | 513.6174 | 40 | 0 | 11.1444
0.54035 | 0 | 0.23156 | 508.8448 | 40 | 0 | 9.2624
0.54342 | 0 | 0.19705 | 502.3848 | 40 | 0 | 7.882
0.5714 | 0 | 0.18396 | 492.6032 | 40 | 0 | 7.3584
0.59803 | 0.018 | 0.16656 | 480.7226 | 40 | 1.26 | 6.6624
0.59979 | 0.2822 | 0.15742 | 486.7944 | 40 | 19.754 | 6.2968
0.64107 | 0.6746 | 0.10806 | 514.2318 | 40 | 51.5444 | 5.6843e-14
0.69983 | 0.7748 | 0.09988 | 542.48 | 40 | 58.2312 | 0
0.76138 | 0.8963 | 0.08875 | 572.633 | 40 | 66.291 | 0
0.81884 | 0.7776 | 0.06061 | 587.6054 | 40 | 56.8564 | 0
0.86477 | 0.7859 | 0.0413 | 597.7934 | 40 | 56.665 | 0
0.90164 | 0.7247 | 0.04912 | 600.3232 | 40 | 52.6938 | 0
0.91779 | 0.7882 | 0.04769 | 605.6258 | 40 | 57.0816 | 0
0.92122 | 0.7888 | 0.05387 | 610.8746 | 40 | 57.3708 | 0
0.92328 | 0.6787 | 0.07087 | 608.8904 | 40 | 47.509 | 2.8348
0.91406 | 0.4812 | 0.07622 | 594.2172 | 40 | 33.684 | 3.0488
0.87989 | 0.1081 | 0.09609 | 557.6388 | 40 | 7.567 | 3.8436
0.84438 | 0 | 0.13887 | 518.7556 | 40 | 0 | 5.5548
0.80392 | 0 | 0.19517 | 486.1704 | 40 | 0 | 7.8068
0.75399 | 0 | 0.25658 | 461.0346 | 40 | 0 | 10.2632
0.70369 | 0 | 0.29892 | 442.6224 | 40 | 0 | 11.9568
0.65128 | 0 | 0.31959 | 430.278 | 40 | 0 | 12.7836
0.61486 | 0 | 0.32211 | 421.6764 | 40 | 0 | 12.8844
0.5824 | 0 | 0.30343 | 415.5736 | 40 | 0 | 12.1372
0.55718 | 0 | 0.27638 | 410.9108 | 40 | 0 | 11.0552
0.5406 | 0 | 0.24278 | 406.562 | 40 | 0 | 9.7112
0.53218 | 0 | 0.23037 | 402.5588 | 40 | 0 | 9.2148
0.53401 | 0 | 0.21716 | 397.8442 | 40 | 0 | 8.6864
0.53957 | 0.0163 | 0.20978 | 393.4194 | 40 | 1.141 | 8.3912
0.5538 | 0.3434 | 0.1929 | 409.7934 | 40 | 31.754 | 0
0.60461 | 0.784 | 0.12506 | 449.2148 | 40 | 59.8824 | 0
0.66958 | 0.8317 | 0.15371 | 486.6242 | 40 | 64.3674 | 5.6843e-14
0.73318 | 0.8973 | 0.14557 | 521.94 | 40 | 68.6338 | 0
0.79134 | 0.8685 | 0.1328 | 548.913 | 40 | 66.107 | 0
0.84222 | 0.8797 | 0.14785 | 572.184 | 40 | 67.493 | 0
0.87804 | 0.8241 | 0.16955 | 588.849 | 40 | 64.469 | 0
0.90336 | 0.8044 | 0.19058 | 602.4442 | 40 | 63.9312 | 0
0.91733 | 0.7837 | 0.20571 | 613.7986 | 40 | 63.0874 | 1.1369e-13
0.91564 | 0.7235 | 0.22302 | 621.8004 | 40 | 50.645 | 8.9208
0.90114 | 0.497 | 0.25722 | 616.7652 | 40 | 34.79 | 10.2888
0.8672 | 0.0851 | 0.28045 | 587.2202 | 40 | 5.957 | 11.218
0.83074 | 0 | 0.31508 | 556.7494 | 40 | 0 | 12.6032
0.79181 | 0 | 0.3897 | 533.1564 | 40 | 0 | 15.588
0.74723 | 0 | 0.42869 | 515.581 | 40 | 0 | 17.1476
0.70045 | 0 | 0.47957 | 504.7188 | 40 | 0 | 19.1828
0.65006 | 0 | 0.49374 | 499.4624 | 40 | 0 | 19.7496
0.60816 | 0 | 0.5148 | 499.2384 | 40 | 0 | 20.592
0.57778 | 0 | 0.50439 | 501.636 | 40 | 0 | 20.1756
0.55278 | 0 | 0.49018 | 505.9652 | 40 | 0 | 19.6072
0.53597 | 0 | 0.47917 | 511.535 | 40 | 0 | 19.1668
0.52878 | 0 | 0.46632 | 517.3098 | 40 | 0 | 18.6528
0.52413 | 0 | 0.44549 | 522.7164 | 40 | 0 | 17.8196
0.52288 | 0.0101 | 0.43587 | 528.5702 | 40 | 0.707 | 17.4348
0.53434 | 0.248 | 0.39916 | 548.4626 | 40 | 33.3264 | 0
0.58219 | 0.6357 | 0.31572 | 587.3714 | 40 | 57.1278 | 0
0.64607 | 0.8319 | 0.38591 | 636.4338 | 40 | 73.6694 | 0
0.70211 | 0.8504 | 0.39745 | 681.6488 | 40 | 75.426 | 0
0.76002 | 0.8871 | 0.37075 | 700 | 40 | 54.3532 | 1.1369e-13
0.81516 | 0.896 | 0.40251 | 700 | 40 | 41.516 | 0
0.85623 | 0.8468 | 0.40926 | 700 | 40 | 45.623 | 0
0.8839 | 0.8126 | 0.42175 | 700 | 40 | 48.39 | 0
0.90235 | 0.7482 | 0.46872 | 700 | 40 | 50.235 | 0
0.90747 | 0.6795 | 0.50279 | 700 | 40 | 47.565 | 3.182
0.89088 | 0.2838 | 0.52793 | 691.8952 | 40 | 19.866 | 21.1172
0.86162 | 0.03 | 0.55658 | 670.0964 | 40 | 2.1 | 22.2632
0.83196 | 0 | 0.52131 | 647.7528 | 40 | 0 | 20.8524
0.79873 | 0 | 0.57873 | 631.029 | 40 | 0 | 23.1492
0.7466 | 0 | 0.58687 | 619.8438 | 40 | 0 | 23.4748
0.68639 | 0 | 0.59218 | 614.892 | 40 | 0 | 23.6872
0.63003 | 0 | 0.55331 | 614.0214 | 40 | 0 | 22.1324
0.59585 | 0 | 0.50507 | 614.6392 | 40 | 0 | 20.2028
0.5716 | 0 | 0.485 | 616.8792 | 40 | 0 | 19.4
0.5528 | 0 | 0.49625 | 621.4492 | 40 | 0 | 19.85
0.54599 | 0 | 0.48795 | 626.3682 | 40 | 0 | 19.518
0.55513 | 0 | 0.44198 | 628.5344 | 40 | 0 | 17.6792
0.58062 | 0 | 0.39577 | 626.3032 | 40 | 0 | 15.8308
0.61067 | 0.0121 | 0.37949 | 621.2628 | 40 | 0.847 | 15.1796
0.60983 | 0.166 | 0.35016 | 625.9062 | 40 | 11.62 | 14.0064
0.63989 | 0.3028 | 0.40607 | 639.356 | 40 | 21.196 | 16.2428
0.68671 | 0.4519 | 0.49812 | 662.2428 | 40 | 51.5578 | 0
0.74142 | 0.5706 | 0.52813 | 689.168 | 40 | 61.0672 | 0
0.78926 | 0.6578 | 0.54868 | 700 | 40 | 49.758 | 0
0.83625 | 0.5635 | 0.56225 | 700 | 40 | 39.445 | 4.18
0.87216 | 0.5474 | 0.55886 | 700 | 40 | 38.318 | 8.898
0.89485 | 0.5688 | 0.55467 | 700 | 40 | 39.816 | 9.669
0.90927 | 0.4351 | 0.55714 | 700 | 40 | 30.457 | 20.47
0.90307 | 0.2927 | 0.53204 | 691.4636 | 40 | 20.489 | 21.2816
0.883 | 0.1344 | 0.50192 | 672.6484 | 40 | 9.408 | 20.0768
0.84993 | 0.023 | 0.49529 | 649.077 | 40 | 1.61 | 19.8116
0.8283 | 0 | 0.43204 | 623.5286 | 40 | 0 | 17.2816
0.79575 | 0 | 0.49322 | 603.6824 | 40 | 0 | 19.7288
0.74448 | 0 | 0.50375 | 589.3844 | 40 | 0 | 20.15
0.6829 | 0 | 0.49433 | 580.8676 | 40 | 0 | 19.7732
0.63326 | 0 | 0.4852 | 576.9496 | 40 | 0 | 19.408
0.597 | 0 | 0.48252 | 576.5504 | 40 | 0 | 19.3008
0.57222 | 0 | 0.46975 | 578.1184 | 40 | 0 | 18.79
0.55241 | 0 | 0.4411 | 580.5214 | 40 | 0 | 17.644
0.54515 | 0 | 0.4186 | 582.7504 | 40 | 0 | 16.744
0.55069 | 0 | 0.40076 | 583.7118 | 40 | 0 | 16.0304
0.57941 | 0 | 0.37378 | 580.722 | 40 | 0 | 14.9512
0.61134 | 0.0079 | 0.37606 | 575.1834 | 40 | 0.553 | 15.0424
0.6115 | 0.1196 | 0.37502 | 577.4062 | 40 | 8.372 | 15.0008
0.6456 | 0.314 | 0.43312 | 592.151 | 40 | 21.98 | 17.3248
0.69968 | 0.4128 | 0.58384 | 614.4326 | 40 | 28.896 | 23.3536
0.74975 | 0.4949 | 0.59246 | 637.799 | 40 | 34.643 | 23.6984
0.79277 | 0.6483 | 0.58312 | 667.2278 | 40 | 68.7058 | 0
0.82997 | 0.683 | 0.57662 | 695.1056 | 40 | 70.8748 | 0
0.85228 | 0.7244 | 0.57107 | 700 | 40 | 50.1224 | 0
0.86221 | 0.6572 | 0.51836 | 700 | 40 | 46.004 | 0.217
0.87375 | 0.6294 | 0.48711 | 700 | 40 | 44.058 | 3.317
0.86559 | 0.4533 | 0.47251 | 700 | 40 | 31.731 | 14.828
0.8383 | 0.2069 | 0.52007 | 691.4558 | 40 | 14.483 | 20.8028
0.80215 | 0.0392 | 0.5089 | 674.3408 | 40 | 2.744 | 20.356
0.78201 | 0 | 0.46939 | 654.9154 | 40 | 0 | 18.7756
0.75651 | 0 | 0.52502 | 640.2652 | 40 | 0 | 21.0008
0.7086 | 0 | 0.57514 | 632.4108 | 40 | 0 | 23.0056
0.65728 | 0 | 0.61129 | 631.1344 | 40 | 0 | 24.4516
0.60796 | 0 | 0.5759 | 633.3744 | 40 | 0 | 23.036
0.57379 | 0 | 0.52167 | 636.8622 | 40 | 0 | 20.8668
0.54866 | 0 | 0.51899 | 642.7558 | 40 | 0 | 20.7596
0.53518 | 0 | 0.49884 | 649.1914 | 40 | 0 | 19.9536
0.5308 | 0 | 0.51724 | 656.801 | 40 | 0 | 20.6896
0.53813 | 0 | 0.51724 | 663.6776 | 40 | 0 | 20.6896
0.56951 | 0 | 0.4832 | 666.0546 | 40 | 0 | 19.328
0.60137 | 0.0059 | 0.47426 | 665.301 | 40 | 0.413 | 18.9704
0.59928 | 0.182 | 0.44258 | 675.8162 | 40 | 12.74 | 17.7032
0.616 | 0.4718 | 0.42542 | 700 | 40 | 45.7838 | 0
0.65039 | 0.6045 | 0.48974 | 700 | 40 | 25.039 | 0
0.69484 | 0.7312 | 0.52789 | 700 | 40 | 29.484 | 0
0.74126 | 0.8383 | 0.53396 | 700 | 40 | 34.126 | 0
0.79236 | 0.8178 | 0.54884 | 700 | 40 | 39.236 | 0
0.83406 | 0.6185 | 0.551 | 700 | 40 | 43.295 | 0.111
0.85436 | 0.5939 | 0.57514 | 700 | 40 | 41.573 | 3.863
0.85451 | 0.3068 | 0.53432 | 697.3978 | 40 | 21.476 | 21.3728
0.84615 | 0.1902 | 0.51181 | 686.5692 | 40 | 13.314 | 20.4724
0.82734 | 0.1015 | 0.48655 | 670.4022 | 40 | 7.105 | 19.462
0.78832 | 0.0158 | 0.4336 | 650.0202 | 40 | 1.106 | 17.344
0.77214 | 0 | 0.37362 | 627.751 | 40 | 0 | 14.9448
0.74395 | 0 | 0.41269 | 609.8636 | 40 | 0 | 16.5076
0.69827 | 0 | 0.48603 | 599.4778 | 40 | 0 | 19.4412
0.6437 | 0 | 0.54397 | 596.8666 | 40 | 0 | 21.7588
0.59476 | 0 | 0.54884 | 599.3442 | 40 | 0 | 21.9536
0.55944 | 0 | 0.5518 | 605.4722 | 40 | 0 | 22.072
0.53479 | 0 | 0.50978 | 612.3844 | 40 | 0 | 20.3912
0.51829 | 0 | 0.47638 | 619.6106 | 40 | 0 | 19.0552
0.51313 | 0 | 0.45391 | 626.454 | 40 | 0 | 18.1564
0.51902 | 0 | 0.43089 | 631.7876 | 40 | 0 | 17.2356
0.55115 | 0 | 0.41281 | 633.185 | 40 | 0 | 16.5124
0.58435 | 0.0129 | 0.40898 | 632.0122 | 40 | 0.903 | 16.3592
0.58639 | 0.2577 | 0.41508 | 648.0154 | 40 | 18.039 | 16.6032
0.61877 | 0.6677 | 0.39785 | 688.7914 | 40 | 62.653 | 0
0.66585 | 0.7456 | 0.45096 | 700 | 40 | 37.7936 | 0
0.71271 | 0.8143 | 0.43328 | 700 | 40 | 31.271 | 0
0.75423 | 0.8708 | 0.40599 | 700 | 40 | 35.423 | 0
0.79837 | 0.8724 | 0.36205 | 700 | 40 | 39.837 | 0
0.8371 | 0.8627 | 0.3097 | 700 | 40 | 43.71 | 0
0.86233 | 0.7996 | 0.28085 | 700 | 40 | 46.233 | 0
0.88147 | 0.7008 | 0.29266 | 700 | 40 | 48.147 | 0
0.88307 | 0.4902 | 0.27805 | 697.129 | 40 | 34.314 | 11.122
0.86674 | 0.2247 | 0.28859 | 677.7276 | 40 | 15.729 | 11.5436
0.83209 | 0.0377 | 0.2905 | 648.7776 | 40 | 2.639 | 11.62
0.80907 | 0 | 0.27163 | 618.7358 | 40 | 0 | 10.8652
0.77768 | 0 | 0.36816 | 595.6942 | 40 | 0 | 14.7264
0.73177 | 0 | 0.45982 | 580.91 | 40 | 0 | 18.3928
0.67138 | 0 | 0.46081 | 572.2044 | 40 | 0 | 18.4324
0.61965 | 0 | 0.37913 | 565.4046 | 40 | 0 | 15.1652
0.58185 | 0 | 0.29066 | 558.846 | 40 | 0 | 11.6264
0.55628 | 0 | 0.25686 | 553.4924 | 40 | 0 | 10.2744
0.53734 | 0 | 0.27462 | 550.7432 | 40 | 0 | 10.9848
0.52865 | 0 | 0.2767 | 548.9462 | 40 | 0 | 11.068
0.5341 | 0 | 0.22546 | 544.5546 | 40 | 0 | 9.0184
0.56443 | 0 | 0.16516 | 534.718 | 40 | 0 | 6.6064
0.59429 | 0.0073 | 0.13643 | 521.2572 | 40 | 0.511 | 5.4572
0.59485 | 0.152 | 0.13053 | 517.6334 | 40 | 10.64 | 5.2212
0.62882 | 0.5717 | 0.0836 | 538.1144 | 40 | 43.363 | -1.1369e-13
0.67748 | 0.7362 | 0.04445 | 563.6784 | 40 | 53.312 | 0
0.72749 | 0.7845 | 0.04673 | 587.7136 | 40 | 56.7842 | 0
0.77243 | 0.7495 | 0.05998 | 605.3348 | 40 | 54.8642 | 1.1369e-13
0.81445 | 0.7807 | 0.07271 | 621.4472 | 40 | 57.5574 | 0
0.84998 | 0.7724 | 0.11337 | 635.052 | 40 | 58.6028 | 0
0.86693 | 0.7941 | 0.15227 | 650.0368 | 40 | 61.6778 | 0
0.87557 | 0.6501 | 0.1599 | 654.3828 | 40 | 45.507 | 6.396
0.87156 | 0.512 | 0.18033 | 650.28 | 40 | 35.84 | 7.2132
0.84553 | 0.361 | 0.17785 | 638.111 | 40 | 25.27 | 7.114
0.80794 | 0.04 | 0.1753 | 607.129 | 40 | 2.8 | 7.012
0.78176 | 0 | 0.17275 | 575.863 | 40 | 0 | 6.91
0.74529 | 0 | 0.2257 | 550.362 | 40 | 0 | 9.028
0.70008 | 0 | 0.27143 | 531.2112 | 40 | 0 | 10.8572
0.65461 | 0 | 0.26325 | 516.2802 | 40 | 0 | 10.53
0.60881 | 0 | 0.24996 | 505.3976 | 40 | 0 | 9.9984
0.57296 | 0 | 0.26038 | 498.5168 | 40 | 0 | 10.4152
0.54194 | 0 | 0.25188 | 494.398 | 40 | 0 | 10.0752
0.52131 | 0 | 0.24294 | 491.9846 | 40 | 0 | 9.7176
0.50709 | 0 | 0.24485 | 491.0696 | 40 | 0 | 9.794
0.50269 | 0 | 0.24848 | 490.7398 | 40 | 0 | 9.9392
0.50706 | 0 | 0.24773 | 489.943 | 40 | 0 | 9.9092
0.51596 | 0.0117 | 0.2251 | 488.17 | 40 | 0.819 | 9.004
0.52767 | 0.3189 | 0.19182 | 505.3988 | 40 | 29.9958 | 0
0.57618 | 0.7992 | 0.11369 | 548.2724 | 40 | 60.4916 | -5.6843e-14
0.63573 | 0.9033 | 0.11417 | 592.4972 | 40 | 67.7978 | 0
0.70214 | 0.9199 | 0.1567 | 632.9442 | 40 | 70.661 | 0
0.76045 | 0.8966 | 0.19457 | 667.444 | 40 | 70.5448 | 0
0.80827 | 0.857 | 0.17155 | 693.469 | 40 | 66.852 | 0
0.83808 | 0.78 | 0.14226 | 700 | 40 | 50.339 | 0
0.85612 | 0.7745 | 0.13408 | 700 | 40 | 45.612 | 0
0.86798 | 0.8 | 0.15275 | 700 | 40 | 46.798 | 0
0.86237 | 0.7038 | 0.18097 | 700 | 40 | 46.237 | 0
0.84325 | 0.4554 | 0.20176 | 695.6234 | 40 | 31.878 | 8.0704
0.81001 | 0.0589 | 0.21879 | 667.497 | 40 | 4.123 | 8.7516
0.77949 | 0 | 0.19294 | 637.2656 | 40 | 0 | 7.7176
0.74216 | 0 | 0.24537 | 612.8644 | 40 | 0 | 9.8148
0.70023 | 0 | 0.28583 | 594.2746 | 40 | 0 | 11.4332
0.6562 | 0 | 0.31959 | 581.4382 | 40 | 0 | 12.7836
0.61184 | 0 | 0.31125 | 572.7042 | 40 | 0 | 12.45
0.57446 | 0 | 0.30698 | 567.5374 | 40 | 0 | 12.2792
0.54685 | 0 | 0.31169 | 565.32 | 40 | 0 | 12.4676
0.52566 | 0 | 0.30088 | 564.7892 | 40 | 0 | 12.0352
0.51095 | 0 | 0.27283 | 564.6074 | 40 | 0 | 10.9132
0.50054 | 0 | 0.23787 | 564.0682 | 40 | 0 | 9.5148
0.49876 | 0 | 0.22733 | 563.2854 | 40 | 0 | 9.0932
0.50062 | 0.0106 | 0.19876 | 561.9158 | 40 | 0.742 | 7.9504
0.51266 | 0.3046 | 0.16875 | 578.7218 | 40 | 28.072 | 0
0.56043 | 0.7857 | 0.09314 | 621.4034 | 40 | 58.7246 | 0
0.62339 | 0.9023 | 0.06321 | 664.7538 | 40 | 65.6894 | 1.1369e-13
0.68468 | 0.9178 | 0.09693 | 700 | 40 | 63.7142 | 0
0.74246 | 0.9099 | 0.12733 | 700 | 40 | 34.246 | 0
0.78809 | 0.8726 | 0.11468 | 700 | 40 | 38.809 | 0
0.82565 | 0.82 | 0.13879 | 700 | 40 | 42.565 | 0
0.85167 | 0.8379 | 0.15591 | 700 | 40 | 45.167 | 0
0.8687 | 0.7905 | 0.20367 | 700 | 40 | 46.87 | 0
0.87 | 0.7118 | 0.20495 | 700 | 40 | 47 | 0
0.85863 | 0.4412 | 0.25391 | 695.1774 | 40 | 30.884 | 10.1564
0.82846 | 0.0558 | 0.24098 | 665.8766 | 40 | 3.906 | 9.6392
0.80934 | 0 | 0.21496 | 633.541 | 40 | 0 | 8.5984
0.77005 | 0 | 0.26528 | 607.1472 | 40 | 0 | 10.6112
0.72128 | 0 | 0.32877 | 588.17 | 40 | 0 | 13.1508
0.66604 | 0 | 0.36389 | 576.1216 | 40 | 0 | 14.5556
0.61239 | 0 | 0.39034 | 570.4962 | 40 | 0 | 15.6136
0.57316 | 0 | 0.39828 | 569.1114 | 40 | 0 | 15.9312
0.54935 | 0 | 0.38536 | 569.5908 | 40 | 0 | 15.4144
0.5341 | 0 | 0.35447 | 570.3596 | 40 | 0 | 14.1788
0.52908 | 0 | 0.33791 | 570.968 | 40 | 0 | 13.5164
0.53603 | 0 | 0.3087 | 569.713 | 40 | 0 | 12.348
0.5668 | 0 | 0.28807 | 564.5558 | 40 | 0 | 11.5228
0.59711 | 0.0128 | 0.26644 | 556.3984 | 40 | 0.896 | 10.6576
0.59727 | 0.3015 | 0.2352 | 567.1844 | 40 | 30.513 | 0
0.63452 | 0.7956 | 0.12941 | 604.6008 | 40 | 60.8684 | 0
0.68703 | 0.7523 | 0.13037 | 633.7736 | 40 | 57.8758 | 0
0.74146 | 0.8708 | 0.13675 | 666.0536 | 40 | 66.426 | 0
0.78529 | 0.8334 | 0.1158 | 690.4946 | 40 | 62.97 | 0
0.82262 | 0.7952 | 0.11664 | 700 | 40 | 51.7674 | 0
0.84855 | 0.7463 | 0.12853 | 700 | 40 | 44.855 | 0
0.86236 | 0.6697 | 0.15231 | 700 | 40 | 46.236 | 0
0.87387 | 0.5448 | 0.17905 | 697.911 | 40 | 38.136 | 7.162
0.87062 | 0.5325 | 0.21273 | 696.6332 | 40 | 37.275 | 8.5092
0.85239 | 0.4211 | 0.22239 | 689.7668 | 40 | 29.477 | 8.8956
0.82013 | 0.0717 | 0.22921 | 661.9412 | 40 | 5.019 | 9.1684
0.80224 | 0 | 0.22223 | 630.6064 | 40 | 0 | 8.8892
0.76972 | 0 | 0.2674 | 604.3304 | 40 | 0 | 10.696
0.71761 | 0 | 0.32602 | 585.6102 | 40 | 0 | 13.0408
0.65902 | 0 | 0.34785 | 573.6222 | 40 | 0 | 13.914
0.60834 | 0 | 0.36584 | 567.4218 | 40 | 0 | 14.6336
0.5706 | 0 | 0.37227 | 565.2526 | 40 | 0 | 14.8908
0.54707 | 0 | 0.36604 | 565.1872 | 40 | 0 | 14.6416
0.52894 | 0 | 0.35407 | 566.456 | 40 | 0 | 14.1628
0.52075 | 0 | 0.33915 | 567.947 | 40 | 0 | 13.566
0.52893 | 0 | 0.31568 | 567.6812 | 40 | 0 | 12.6272
0.55728 | 0 | 0.2921 | 563.6372 | 40 | 0 | 11.684
0.59079 | 0.0095 | 0.25559 | 555.4468 | 40 | 0.665 | 10.2236
0.58955 | 0.3017 | 0.21887 | 566.3656 | 40 | 29.8738 | 0
0.61117 | 0.7871 | 0.12127 | 605.1964 | 40 | 59.9478 | 0
0.64821 | 0.8925 | 0.11955 | 647.6324 | 40 | 67.257 | 0
0.68904 | 0.9017 | 0.15267 | 687.9542 | 40 | 69.2258 | 0
0.72506 | 0.892 | 0.15698 | 700 | 40 | 44.5518 | 0
0.76115 | 0.8826 | 0.1316 | 700 | 40 | 36.115 | 0
0.79402 | 0.838 | 0.117 | 700 | 40 | 39.402 | 0
0.80898 | 0.762 | 0.12785 | 700 | 40 | 40.898 | 0
0.82002 | 0.6822 | 0.1437 | 700 | 40 | 42.002 | 0
0.82053 | 0.7131 | 0.16173 | 700 | 40 | 42.053 | 0
0.80756 | 0.4566 | 0.1905 | 698.826 | 40 | 31.962 | 7.62
0.78047 | 0.0612 | 0.22694 | 674.1406 | 40 | 4.284 | 9.0776
0.76781 | 0 | 0.24737 | 647.2544 | 40 | 0 | 9.8948
0.7428 | 0 | 0.32191 | 625.8508 | 40 | 0 | 12.8764
0.69767 | 0 | 0.39824 | 612.0134 | 40 | 0 | 15.9296
0.64374 | 0 | 0.44258 | 605.3426 | 40 | 0 | 17.7032
0.59833 | 0 | 0.4664 | 604.1656 | 40 | 0 | 18.656
0.56875 | 0 | 0.46664 | 605.9562 | 40 | 0 | 18.6656
0.54425 | 0 | 0.46568 | 610.1584 | 40 | 0 | 18.6272
0.52994 | 0 | 0.43675 | 614.6344 | 40 | 0 | 17.47
0.52114 | 0 | 0.39856 | 618.4628 | 40 | 0 | 15.9424
0.52795 | 0 | 0.36564 | 620.2934 | 40 | 0 | 14.6256
0.55728 | 0 | 0.33256 | 617.8678 | 40 | 0 | 13.3024
0.59371 | 0.0079 | 0.28779 | 610.5614 | 40 | 0.553 | 11.5116
0.58797 | 0.2957 | 0.23292 | 621.7802 | 40 | 30.0158 | 0
0.61311 | 0.7691 | 0.13037 | 659.521 | 40 | 59.0518 | 0
0.64642 | 0.8486 | 0.13635 | 699.735 | 40 | 64.856 | -1.1369e-13
0.68616 | 0.8636 | 0.12079 | 700 | 40 | 28.881 | 0
0.72497 | 0.8515 | 0.08671 | 700 | 40 | 32.497 | 0
0.76609 | 0.8566 | 0.06808 | 700 | 40 | 36.609 | 0
0.80055 | 0.8408 | 0.05583 | 700 | 40 | 40.055 | 0
0.8282 | 0.7394 | 0.06856 | 700 | 40 | 42.82 | 0
0.84217 | 0.743 | 0.09848 | 700 | 40 | 44.217 | 0
0.85183 | 0.613 | 0.14669 | 700 | 40 | 42.91 | 2.273
0.84024 | 0.2825 | 0.18867 | 683.2978 | 40 | 19.775 | 7.5468
0.81037 | 0.0217 | 0.2097 | 652.1678 | 40 | 1.519 | 8.388
0.79279 | 0 | 0.24753 | 622.79 | 40 | 0 | 9.9012
0.76017 | 0 | 0.33236 | 600.0674 | 40 | 0 | 13.2944
0.71467 | 0 | 0.39824 | 584.53 | 40 | 0 | 15.9296
0.65918 | 0 | 0.41173 | 575.0812 | 40 | 0 | 16.4692
0.61433 | 0 | 0.42614 | 570.6938 | 40 | 0 | 17.0456
0.58313 | 0 | 0.43089 | 569.6164 | 40 | 0 | 17.2356
0.56038 | 0 | 0.42291 | 570.4948 | 40 | 0 | 16.9164
0.54579 | 0 | 0.38196 | 571.1942 | 40 | 0 | 15.2784
0.53839 | 0 | 0.33819 | 570.8828 | 40 | 0 | 13.5276
0.5497 | 0 | 0.28775 | 567.4228 | 40 | 0 | 11.51
0.58161 | 0 | 0.24944 | 559.2394 | 40 | 0 | 9.9776
0.61966 | 0.0063 | 0.22083 | 546.5476 | 40 | 0.441 | 8.8332
0.61787 | 0.1787 | 0.18615 | 544.7156 | 40 | 12.509 | 7.446
0.63475 | 0.5535 | 0.1405 | 565.6056 | 40 | 44.365 | 0
0.658 | 0.7435 | 0.15459 | 598.0342 | 40 | 58.2286 | 0
0.67745 | 0.7914 | 0.14657 | 631.55 | 40 | 61.2608 | 0
0.69654 | 0.7651 | 0.13444 | 660.8306 | 40 | 58.9346 | 0
0.71758 | 0.7558 | 0.1247 | 686.9666 | 40 | 57.894 | 0
0.73513 | 0.6796 | 0.13727 | 700 | 40 | 46.5464 | 0
0.74147 | 0.572 | 0.1814 | 700 | 40 | 34.147 | 0
0.74076 | 0.3219 | 0.25291 | 698.5734 | 40 | 22.533 | 10.1164
0.73738 | 0.2455 | 0.28396 | 693.3788 | 40 | 17.185 | 11.3584
0.72842 | 0.1698 | 0.34074 | 686.0524 | 40 | 11.886 | 13.6296
0.71051 | 0.0319 | 0.36548 | 671.8536 | 40 | 2.233 | 14.6192
0.70768 | 0 | 0.37737 | 656.1804 | 40 | 0 | 15.0948
0.68696 | 0 | 0.41189 | 643.96 | 40 | 0 | 16.4756
0.65058 | 0 | 0.4259 | 635.938 | 40 | 0 | 17.036
0.60914 | 0 | 0.45128 | 633.0752 | 40 | 0 | 18.0512
0.57075 | 0 | 0.43935 | 633.5742 | 40 | 0 | 17.574
0.54975 | 0 | 0.44058 | 636.2224 | 40 | 0 | 17.6232
0.53418 | 0 | 0.41955 | 639.5864 | 40 | 0 | 16.782
0.52623 | 0 | 0.39346 | 642.7018 | 40 | 0 | 15.7384
0.52366 | 0 | 0.34769 | 644.2434 | 40 | 0 | 13.9076
0.53289 | 0 | 0.30726 | 643.2448 | 40 | 0 | 12.2904
0.56492 | 0 | 0.2854 | 638.1688 | 40 | 0 | 11.416
0.60234 | 0.0031 | 0.29274 | 629.8614 | 40 | 0.217 | 11.7096
0.60691 | 0.1829 | 0.30575 | 634.2034 | 40 | 12.803 | 12.23
0.63715 | 0.5059 | 0.31185 | 658.3754 | 40 | 47.887 | 0
0.67759 | 0.6266 | 0.40942 | 690.8552 | 40 | 60.2388 | 0
0.71455 | 0.7611 | 0.42191 | 700 | 40 | 40.5998 | 0
0.75203 | 0.8242 | 0.42155 | 700 | 40 | 35.203 | 0
0.78342 | 0.818 | 0.43647 | 700 | 40 | 38.342 | 0
0.80709 | 0.7707 | 0.48045 | 700 | 40 | 40.709 | 0
0.82873 | 0.6544 | 0.50918 | 700 | 40 | 42.873 | 0
0.8362 | 0.3549 | 0.49777 | 700 | 40 | 24.843 | 18.777
0.82847 | 0.1551 | 0.49844 | 687.9476 | 40 | 10.857 | 19.9376
0.79933 | 0.0845 | 0.49238 | 673.6248 | 40 | 5.915 | 19.6952
0.76104 | 0.0136 | 0.49605 | 658.3148 | 40 | 0.952 | 19.842
0.74595 | 0 | 0.42706 | 640.8022 | 40 | 0 | 17.0824
0.72579 | 0 | 0.418 | 624.9432 | 40 | 0 | 16.72
0.69055 | 0 | 0.45782 | 614.201 | 40 | 0 | 18.3128
0.65528 | 0 | 0.48559 | 608.0966 | 40 | 0 | 19.4236
0.61605 | 0 | 0.52087 | 607.3264 | 40 | 0 | 20.8348
0.58176 | 0 | 0.57829 | 612.282 | 40 | 0 | 23.1316
0.55857 | 0 | 0.59122 | 620.0738 | 40 | 0 | 23.6488
0.5441 | 0 | 0.60395 | 629.8218 | 40 | 0 | 24.158
0.53312 | 0 | 0.56217 | 638.9966 | 40 | 0 | 22.4868
0.5305 | 0 | 0.52945 | 647.1246 | 40 | 0 | 21.178
0.53458 | 0 | 0.51105 | 654.1086 | 40 | 0 | 20.442
0.54695 | 0.0024 | 0.47709 | 658.6652 | 40 | 0.168 | 19.0836
0.5587 | 0.0607 | 0.47027 | 665.855 | 40 | 4.249 | 18.8108
0.60117 | 0.1208 | 0.52402 | 675.1548 | 40 | 8.456 | 20.9608
0.6478 | 0.2362 | 0.6249 | 691.9048 | 40 | 16.534 | 24.996
0.69123 | 0.388 | 0.62171 | 700 | 40 | 27.16 | 10.0582
0.72908 | 0.4419 | 0.59765 | 700 | 40 | 30.933 | 1.975
0.76514 | 0.4026 | 0.58863 | 700 | 40 | 28.182 | 8.332
0.79127 | 0.4151 | 0.56105 | 700 | 40 | 29.057 | 10.07
0.81082 | 0.4322 | 0.54569 | 700 | 40 | 30.254 | 10.828
0.82133 | 0.3573 | 0.54581 | 700 | 40 | 25.011 | 17.122
0.81743 | 0.2393 | 0.535 | 696.408 | 40 | 16.751 | 21.4
0.79991 | 0.0733 | 0.51724 | 682.2376 | 40 | 5.131 | 20.6896
0.76347 | 0.0017 | 0.49425 | 665.7796 | 40 | 0.119 | 19.77
0.74488 | 0 | 0.44717 | 649.1784 | 40 | 0 | 17.8868
0.71673 | 0 | 0.4563 | 635.7574 | 40 | 0 | 18.252
0.6837 | 0 | 0.45052 | 625.4082 | 40 | 0 | 18.0208
0.64802 | 0 | 0.41596 | 617.2446 | 40 | 0 | 16.6384
0.60919 | 0 | 0.43791 | 613.842 | 40 | 0 | 17.5164
0.57596 | 0 | 0.42578 | 613.2772 | 40 | 0 | 17.0312
0.55294 | 0 | 0.46875 | 616.7332 | 40 | 0 | 18.75
0.53481 | 0 | 0.46544 | 621.8698 | 40 | 0 | 18.6176
0.51977 | 0 | 0.41245 | 626.3908 | 40 | 0 | 16.498
0.51293 | 0 | 0.46081 | 633.5302 | 40 | 0 | 18.4324
0.51425 | 0 | 0.45128 | 640.1564 | 40 | 0 | 18.0512
0.51928 | 0.0033 | 0.41253 | 644.9606 | 40 | 0.231 | 16.5012
0.52779 | 0.0919 | 0.35738 | 652.9098 | 40 | 6.433 | 14.2952
0.57436 | 0.285 | 0.3255 | 668.4438 | 40 | 32.97 | 0
0.626 | 0.5262 | 0.37594 | 697.7154 | 40 | 51.8716 | 0
0.6758 | 0.6571 | 0.40132 | 700 | 40 | 29.8646 | 0
0.7214 | 0.6049 | 0.35 | 700 | 40 | 32.14 | 0
0.75761 | 0.7248 | 0.25084 | 700 | 40 | 35.761 | 0
0.78855 | 0.7652 | 0.19433 | 700 | 40 | 38.855 | 0
0.80955 | 0.6733 | 0.14433 | 700 | 40 | 40.955 | 0
0.81473 | 0.523 | 0.1079 | 699.453 | 40 | 36.61 | 4.316
0.81776 | 0.4536 | 0.0836 | 692.773 | 40 | 31.752 | 3.344
0.80886 | 0.3118 | 0.09964 | 677.6986 | 40 | 21.826 | 3.9856
0.78944 | 0.0225 | 0.13332 | 645.6624 | 40 | 1.575 | 5.3328
0.78009 | 0 | 0.13871 | 613.2018 | 40 | 0 | 5.5484
0.7538 | 0 | 0.17259 | 584.7254 | 40 | 0 | 6.9036
0.70859 | 0 | 0.19824 | 561.796 | 40 | 0 | 7.9296
0.65989 | 0 | 0.21221 | 544.2954 | 40 | 0 | 8.4884
0.61412 | 0 | 0.1937 | 530.6314 | 40 | 0 | 7.748
0.57694 | 0 | 0.18927 | 520.5082 | 40 | 0 | 7.5708
0.55838 | 0 | 0.18559 | 512.0938 | 40 | 0 | 7.4236
0.54632 | 0 | 0.1986 | 505.4058 | 40 | 0 | 7.944
0.54253 | 0 | 0.19338 | 498.888 | 40 | 0 | 7.7352
0.54838 | 0 | 0.18831 | 491.5824 | 40 | 0 | 7.5324
0.58116 | 0 | 0.16213 | 479.9516 | 40 | 0 | 6.4852
0.61581 | 0.0052 | 0.15451 | 464.915 | 40 | 0.364 | 6.1804
0.61079 | 0.2078 | 0.13703 | 463.8632 | 40 | 14.546 | 5.4812
0.64277 | 0.5599 | 0.09613 | 482.6244 | 40 | 43.0382 | 0
0.68262 | 0.5775 | 0.0759 | 497.8234 | 40 | 43.461 | 0
0.73219 | 0.6748 | 0.07606 | 514.8828 | 40 | 50.2784 | -5.6843e-14
0.78275 | 0.7138 | 0.07394 | 529.5314 | 40 | 52.9236 | 0
0.82035 | 0.8396 | 0.06883 | 549.0216 | 40 | 61.5252 | 0
0.85016 | 0.7246 | 0.07147 | 557.5864 | 40 | 53.5808 | 0
0.86237 | 0.5123 | 0.11061 | 551.6348 | 40 | 35.861 | 4.4244
0.86763 | 0.4253 | 0.16536 | 541.2572 | 40 | 29.771 | 6.6144
0.86658 | 0.3149 | 0.20894 | 524.9998 | 40 | 22.043 | 8.3576
0.85597 | 0.1757 | 0.24721 | 501.5902 | 40 | 12.299 | 9.8884
0.82569 | 0.0263 | 0.26221 | 471.3506 | 40 | 1.841 | 10.4884
0.81001 | 0 | 0.30914 | 442.7152 | 40 | 0 | 12.3656
0.77501 | 0 | 0.28739 | 416.7098 | 40 | 0 | 11.4956
0.72738 | 0 | 0.31257 | 396.4746 | 40 | 0 | 12.5028
0.67132 | 0 | 0.31899 | 382.1022 | 40 | 0 | 12.7596
0.62468 | 0 | 0.34206 | 373.3166 | 40 | 0 | 13.6824
0.58678 | 0 | 0.31823 | 367.3678 | 40 | 0 | 12.7292
0.5658 | 0 | 0.31272 | 363.2966 | 40 | 0 | 12.5088
0.54824 | 0 | 0.29341 | 360.209 | 40 | 0 | 11.7364
0.54119 | 0 | 0.27872 | 357.2388 | 40 | 0 | 11.1488
0.54679 | 0 | 0.26902 | 353.3206 | 40 | 0 | 10.7608
0.57564 | 0 | 0.25828 | 346.0878 | 40 | 0 | 10.3312
0.61025 | 0.0035 | 0.25178 | 335.379 | 40 | 0.245 | 10.0712
0.60712 | 0.2107 | 0.24423 | 339.1852 | 40 | 14.749 | 9.7692
0.63566 | 0.6694 | 0.22954 | 371.6588 | 40 | 56.0396 | -5.6843e-14
0.67831 | 0.8274 | 0.24886 | 411.7002 | 40 | 67.8724 | 0
0.72588 | 0.8801 | 0.26702 | 451.4 | 40 | 72.2878 | 5.6843e-14
0.76856 | 0.8722 | 0.29416 | 487.3644 | 40 | 72.8204 | 0
0.81173 | 0.8751 | 0.27193 | 518.3256 | 40 | 72.1342 | 0
0.84598 | 0.8205 | 0.21781 | 539.875 | 40 | 66.1474 | 0
0.86705 | 0.783 | 0.2135 | 556.52 | 40 | 63.35 | 0
0.87901 | 0.5657 | 0.21673 | 556.8872 | 40 | 39.599 | 8.6692
0.87548 | 0.434 | 0.22196 | 548.5976 | 40 | 30.38 | 8.8784
0.85798 | 0.2872 | 0.23142 | 532.1604 | 40 | 20.104 | 9.2568
0.81983 | 0.0157 | 0.25365 | 501.4224 | 40 | 1.099 | 10.146
0.79968 | 0 | 0.30989 | 473.85 | 40 | 0 | 12.3956
0.76481 | 0 | 0.38481 | 452.7614 | 40 | 0 | 15.3924
0.71471 | 0 | 0.43051 | 438.5108 | 40 | 0 | 17.2204
0.66275 | 0 | 0.47845 | 431.3738 | 40 | 0 | 19.138
0.61402 | 0 | 0.49325 | 429.7018 | 40 | 0 | 19.73
0.57925 | 0 | 0.52411 | 432.7412 | 40 | 0 | 20.9644
0.5508 | 0 | 0.52379 | 438.6128 | 40 | 0 | 20.9516
0.53444 | 0 | 0.4988 | 445.1208 | 40 | 0 | 19.952
0.52645 | 0 | 0.46883 | 451.229 | 40 | 0 | 18.7532
0.53334 | 0 | 0.46025 | 456.305 | 40 | 0 | 18.41
0.56091 | 0 | 0.44596 | 458.0524 | 40 | 0 | 17.8384
0.59786 | 0.0059 | 0.4533 | 456.8114 | 40 | 0.413 | 18.132
0.59471 | 0.185 | 0.41818 | 467.0176 | 40 | 12.95 | 16.7272
0.62303 | 0.5596 | 0.33959 | 497.4702 | 40 | 52.7556 | 0
0.66841 | 0.8418 | 0.31336 | 542.0896 | 40 | 71.4604 | 0
0.71511 | 0.8932 | 0.26487 | 583.6974 | 40 | 73.1188 | 0
0.75819 | 0.9015 | 0.22076 | 619.8138 | 40 | 71.9354 | 0
0.80946 | 0.8901 | 0.17219 | 648.0624 | 40 | 69.1946 | 0
0.85434 | 0.8577 | 0.16133 | 669.1206 | 40 | 66.4922 | 0
0.88569 | 0.8607 | 0.19546 | 688.619 | 40 | 68.0674 | 0
0.90091 | 0.8019 | 0.21106 | 700 | 40 | 61.472 | 0
0.90346 | 0.6116 | 0.21909 | 700 | 40 | 42.812 | 7.534
0.88723 | 0.365 | 0.22679 | 685.8986 | 40 | 25.55 | 9.0716
0.84686 | 0.0367 | 0.23401 | 653.142 | 40 | 2.569 | 9.3604
0.82284 | 0 | 0.27704 | 621.9396 | 40 | 0 | 11.0816
0.78235 | 0 | 0.32961 | 596.889 | 40 | 0 | 13.1844
0.73114 | 0 | 0.37008 | 578.5782 | 40 | 0 | 14.8032
0.67528 | 0 | 0.42021 | 567.8586 | 40 | 0 | 16.8084
0.6234 | 0 | 0.46261 | 564.023 | 40 | 0 | 18.5044
0.58576 | 0 | 0.52283 | 566.3602 | 40 | 0 | 20.9132
0.5582 | 0 | 0.49585 | 570.3742 | 40 | 0 | 19.834
0.54126 | 0 | 0.48927 | 575.819 | 40 | 0 | 19.5708
0.53114 | 0 | 0.45124 | 580.7546 | 40 | 0 | 18.0496
0.53269 | 0 | 0.39445 | 583.2636 | 40 | 0 | 15.778
0.56074 | 0 | 0.37785 | 582.3036 | 40 | 0 | 15.114
0.59432 | 0.005 | 0.33117 | 576.4684 | 40 | 0.35 | 13.2468
0.59017 | 0.2723 | 0.28966 | 588.0988 | 40 | 30.6474 | -1.1369e-13
0.61959 | 0.7815 | 0.20172 | 628.9136 | 40 | 62.7738 | 0
0.6635 | 0.8689 | 0.18659 | 670.8502 | 40 | 68.2866 | 0
0.70848 | 0.898 | 0.13476 | 700 | 40 | 59.9978 | 0
0.75544 | 0.8953 | 0.08332 | 700 | 40 | 35.544 | 0
0.80173 | 0.8841 | 0.07538 | 700 | 40 | 40.173 | 0
0.84725 | 0.8713 | 0.11496 | 700 | 40 | 44.725 | 0
0.87235 | 0.8838 | 0.14002 | 700 | 40 | 47.235 | 0
0.88841 | 0.819 | 0.16233 | 700 | 40 | 48.841 | 0
0.89053 | 0.6624 | 0.19769 | 700 | 40 | 46.368 | 2.685
0.87141 | 0.4062 | 0.24122 | 690.9418 | 40 | 28.434 | 9.6488
0.82771 | 0.0304 | 0.28033 | 661.512 | 40 | 2.128 | 11.2132
0.80859 | 0 | 0.37306 | 635.5754 | 40 | 0 | 14.9224
0.77066 | 0 | 0.49792 | 618.4262 | 40 | 0 | 19.9168
0.72018 | 0 | 0.56616 | 609.0546 | 40 | 0 | 22.6464
0.6674 | 0 | 0.56213 | 604.7998 | 40 | 0 | 22.4852
0.61483 | 0 | 0.57526 | 606.3272 | 40 | 0 | 23.0104
0.57721 | 0 | 0.56357 | 611.149 | 40 | 0 | 22.5428
0.55041 | 0 | 0.56508 | 618.7112 | 40 | 0 | 22.6032
0.5336 | 0 | 0.55263 | 627.4564 | 40 | 0 | 22.1052
0.52538 | 0 | 0.55387 | 637.0732 | 40 | 0 | 22.1548
0.53207 | 0 | 0.54976 | 645.8566 | 40 | 0 | 21.9904
0.56054 | 0 | 0.54202 | 651.4834 | 40 | 0 | 21.6808
0.59265 | 0.0044 | 0.52115 | 653.3724 | 40 | 0.308 | 20.846
0.59137 | 0.2629 | 0.48332 | 671.9712 | 40 | 18.403 | 19.3328
0.61488 | 0.7261 | 0.39362 | 700 | 40 | 49.5168 | -1.1369e-13
0.65872 | 0.8459 | 0.38364 | 700 | 40 | 25.872 | 0
0.70365 | 0.9185 | 0.33871 | 700 | 40 | 30.365 | 0
0.74316 | 0.9131 | 0.26333 | 700 | 40 | 34.316 | 0
0.78117 | 0.9049 | 0.23164 | 700 | 40 | 38.117 | 0
0.81017 | 0.8963 | 0.24214 | 700 | 40 | 41.017 | 0
0.82925 | 0.8852 | 0.27618 | 700 | 40 | 42.925 | 0
0.84764 | 0.8198 | 0.2984 | 700 | 40 | 44.764 | 0
0.84888 | 0.754 | 0.33256 | 700 | 40 | 44.888 | 0
0.82997 | 0.3502 | 0.36241 | 696.0134 | 40 | 24.514 | 14.4964
0.7917 | 0.0225 | 0.38037 | 673.6332 | 40 | 1.575 | 15.2148
0.77026 | 0 | 0.46325 | 655.1372 | 40 | 0 | 18.53
0.74297 | 0 | 0.54593 | 642.6774 | 40 | 0 | 21.8372
0.71227 | 0 | 0.60938 | 635.8256 | 40 | 0 | 24.3752
0.67269 | 0 | 0.65311 | 634.681 | 40 | 0 | 26.1244
0.63569 | 0 | 0.64262 | 636.8168 | 40 | 0 | 25.7048
0.60191 | 0 | 0.62618 | 641.673 | 40 | 0 | 25.0472
0.57727 | 0 | 0.61349 | 648.4856 | 40 | 0 | 24.5396
0.55997 | 0 | 0.58532 | 655.9014 | 40 | 0 | 23.4128
0.54735 | 0 | 0.58308 | 664.4896 | 40 | 0 | 23.3232
0.54241 | 0 | 0.5512 | 672.2966 | 40 | 0 | 22.048
0.54477 | 0 | 0.46337 | 676.3544 | 40 | 0 | 18.5348
0.55531 | 0.0027 | 0.3249 | 674.0084 | 40 | 0.189 | 12.996
0.56712 | 0.1781 | 0.25208 | 679.8466 | 40 | 12.467 | 10.0832
0.60957 | 0.4591 | 0.18747 | 698.5254 | 40 | 39.6358 | 0
0.6563 | 0.6401 | 0.22901 | 700 | 40 | 27.1046 | 0
0.70616 | 0.7738 | 0.25798 | 700 | 40 | 30.616 | 0
0.75012 | 0.7455 | 0.3397 | 700 | 40 | 35.012 | 0
0.78715 | 0.6951 | 0.4073 | 700 | 40 | 38.715 | 0
0.81432 | 0.5196 | 0.48747 | 700 | 40 | 36.372 | 5.06
0.82855 | 0.4869 | 0.54206 | 700 | 40 | 34.083 | 8.772
0.83876 | 0.4549 | 0.59972 | 700 | 40 | 31.843 | 12.033
0.83444 | 0.4872 | 0.59094 | 700 | 40 | 34.104 | 9.34
0.81268 | 0.2443 | 0.62151 | 700 | 40 | 17.101 | 24.167
0.77451 | 0.0138 | 0.59282 | 687.2278 | 40 | 0.966 | 23.7128
0.7586 | 0 | 0.54964 | 673.3534 | 40 | 0 | 21.9856
0.73289 | 0 | 0.56991 | 662.8608 | 40 | 0 | 22.7964
0.70176 | 0 | 0.61034 | 657.0984 | 40 | 0 | 24.4136
0.67062 | 0 | 0.64489 | 655.832 | 40 | 0 | 25.7956
0.63415 | 0 | 0.67382 | 659.3698 | 40 | 0 | 26.9528
0.60514 | 0 | 0.69553 | 666.677 | 40 | 0 | 27.8212
0.58148 | 0 | 0.67618 | 675.5762 | 40 | 0 | 27.0472
0.56625 | 0 | 0.65918 | 685.3184 | 40 | 0 | 26.3672
0.5525 | 0 | 0.63603 | 695.5096 | 40 | 0 | 25.4412
0.54369 | 0 | 0.61061 | 700 | 40 | 0 | 18.8594
0.54448 | 0 | 0.59852 | 700 | 40 | 0 | 14.448
0.54982 | 0.0014 | 0.58532 | 700 | 40 | 0.098 | 14.884
0.55565 | 0.0853 | 0.57913 | 700 | 40 | 5.971 | 9.594
0.59872 | 0.227 | 0.61269 | 700 | 40 | 15.89 | 3.982
0.65098 | 0.2758 | 0.69046 | 700 | 40 | 19.306 | 5.792
0.69527 | 0.3163 | 0.68839 | 700 | 40 | 22.141 | 7.386
0.73715 | 0.3466 | 0.63164 | 700 | 40 | 24.262 | 9.453
0.77746 | 0.3564 | 0.62207 | 700 | 40 | 24.948 | 12.798
0.80868 | 0.4058 | 0.63316 | 700 | 40 | 28.406 | 12.462
0.82985 | 0.4391 | 0.65279 | 700 | 40 | 30.737 | 12.248
0.84159 | 0.3763 | 0.63476 | 700 | 40 | 26.341 | 17.818
0.84315 | 0.2772 | 0.66512 | 700 | 40 | 19.404 | 24.911
0.82728 | 0.1297 | 0.66716 | 693.0374 | 40 | 9.079 | 26.6864
0.79415 | 0.0073 | 0.59517 | 677.9402 | 40 | 0.511 | 23.8068
0.78123 | 0 | 0.57873 | 662.9664 | 40 | 0 | 23.1492
0.74747 | 0 | 0.61476 | 652.8098 | 40 | 0 | 24.5904
0.7023 | 0 | 0.62773 | 647.689 | 40 | 0 | 25.1092
0.65785 | 0 | 0.61053 | 646.3252 | 40 | 0 | 24.4212
0.6109 | 0 | 0.60615 | 649.4812 | 40 | 0 | 24.246
0.5802 | 0 | 0.56049 | 653.8808 | 40 | 0 | 22.4196
0.55756 | 0 | 0.54629 | 659.9764 | 40 | 0 | 21.8516
0.54668 | 0 | 0.57402 | 668.2692 | 40 | 0 | 22.9608
0.5429 | 0 | 0.5996 | 677.9632 | 40 | 0 | 23.984
0.55708 | 0 | 0.5854 | 685.6712 | 40 | 0 | 23.416
0.58811 | 0 | 0.58444 | 690.2378 | 40 | 0 | 23.3776
0.62123 | 0.0016 | 0.57458 | 691.21 | 40 | 0.112 | 22.9832
0.62368 | 0.0735 | 0.54904 | 695.9486 | 40 | 5.145 | 21.9616
0.65241 | 0.2059 | 0.54126 | 700 | 40 | 14.413 | 14.8794
0.69055 | 0.2019 | 0.59988 | 700 | 40 | 14.133 | 14.922
0.73207 | 0.2476 | 0.61856 | 700 | 40 | 17.332 | 15.875
0.77163 | 0.3305 | 0.63093 | 700 | 40 | 23.135 | 14.028
0.80817 | 0.4407 | 0.63392 | 700 | 40 | 30.849 | 9.968
0.8371 | 0.4075 | 0.61692 | 700 | 40 | 28.525 | 15.185
0.8546 | 0.4487 | 0.63328 | 700 | 40 | 31.409 | 14.051
0.86457 | 0.3707 | 0.61093 | 700 | 40 | 25.949 | 20.508
0.87051 | 0.2727 | 0.59561 | 695.8624 | 40 | 19.089 | 23.8244
0.85458 | 0.1363 | 0.59541 | 683.7618 | 40 | 9.541 | 23.8164
0.82443 | 0.0074 | 0.5423 | 663.5288 | 40 | 0.518 | 21.692
0.81346 | 0 | 0.49429 | 641.9544 | 40 | 0 | 19.7716
0.77946 | 0 | 0.53496 | 625.4068 | 40 | 0 | 21.3984
0.73751 | 0 | 0.59298 | 615.375 | 40 | 0 | 23.7192
0.67971 | 0 | 0.59417 | 611.1708 | 40 | 0 | 23.7668
0.63315 | 0 | 0.59453 | 611.637 | 40 | 0 | 23.7812
0.60152 | 0 | 0.5998 | 615.477 | 40 | 0 | 23.992
0.57594 | 0 | 0.60854 | 622.2246 | 40 | 0 | 24.3416
0.56286 | 0 | 0.62011 | 630.743 | 40 | 0 | 24.8044
0.55548 | 0 | 0.60658 | 639.4582 | 40 | 0 | 24.2632
0.56125 | 0 | 0.61065 | 647.7592 | 40 | 0 | 24.426
0.58686 | 0 | 0.59701 | 652.9536 | 40 | 0 | 23.8804
0.61747 | 0.0025 | 0.55048 | 653.4008 | 40 | 0.175 | 22.0192
0.61267 | 0.1095 | 0.53671 | 661.2672 | 40 | 7.665 | 21.4684
0.63998 | 0.2606 | 0.56121 | 677.9596 | 40 | 18.242 | 22.4484
0.67846 | 0.3223 | 0.60662 | 696.9394 | 40 | 22.561 | 24.2648
0.72139 | 0.351 | 0.60986 | 700 | 40 | 24.57 | 10.6296
0.76059 | 0.4219 | 0.60219 | 700 | 40 | 29.533 | 6.526
0.80038 | 0.4769 | 0.59529 | 700 | 40 | 33.383 | 6.655
0.83366 | 0.4617 | 0.57749 | 700 | 40 | 32.319 | 11.047
0.85766 | 0.4882 | 0.56616 | 700 | 40 | 34.174 | 11.592
0.8677 | 0.5031 | 0.54569 | 700 | 40 | 35.217 | 11.553
0.86467 | 0.4094 | 0.51034 | 700 | 40 | 28.658 | 17.809
0.84286 | 0.1619 | 0.4905 | 686.667 | 40 | 11.333 | 19.62
0.80809 | 0.0019 | 0.43168 | 663.2582 | 40 | 0.133 | 17.2672
0.79639 | 0 | 0.41516 | 640.2256 | 40 | 0 | 16.6064
0.76413 | 0 | 0.47949 | 622.9922 | 40 | 0 | 19.1796
0.71692 | 0 | 0.548 | 613.2202 | 40 | 0 | 21.92
0.66198 | 0 | 0.57179 | 609.8938 | 40 | 0 | 22.8716
0.61475 | 0 | 0.56868 | 611.166 | 40 | 0 | 22.7472
0.58133 | 0 | 0.54653 | 614.8942 | 40 | 0 | 21.8612
0.55861 | 0 | 0.52869 | 620.1808 | 40 | 0 | 21.1476
0.54007 | 0 | 0.49681 | 626.0462 | 40 | 0 | 19.8724
0.53279 | 0 | 0.46891 | 631.5236 | 40 | 0 | 18.7564
0.53817 | 0 | 0.47698 | 636.7858 | 40 | 0 | 19.0792
0.56696 | 0 | 0.45998 | 638.489 | 40 | 0 | 18.3992
0.60235 | 0.002 | 0.43631 | 635.8464 | 40 | 0.14 | 17.4524
0.59496 | 0.0989 | 0.3901 | 638.8774 | 40 | 6.923 | 15.604
0.62194 | 0.2988 | 0.35658 | 651.8626 | 40 | 20.916 | 14.2632
0.66676 | 0.3706 | 0.47107 | 669.9714 | 40 | 25.942 | 18.8428
0.71322 | 0.5724 | 0.45271 | 696.8258 | 40 | 58.1764 | 0
0.75801 | 0.761 | 0.4186 | 700 | 40 | 38.9752 | 0
0.79959 | 0.7996 | 0.36053 | 700 | 40 | 39.959 | 0
0.83691 | 0.767 | 0.32139 | 700 | 40 | 43.691 | 0
0.8577 | 0.7317 | 0.26907 | 700 | 40 | 45.77 | 0
0.87375 | 0.6654 | 0.22761 | 700 | 40 | 46.578 | 0.797
0.87011 | 0.4102 | 0.20786 | 690.0174 | 40 | 28.714 | 8.3144
0.85396 | 0.0997 | 0.22462 | 660.5852 | 40 | 6.979 | 8.9848
0.81446 | 0.0008 | 0.2164 | 627.8512 | 40 | 0.056 | 8.656
0.79715 | 0 | 0.23919 | 597.7038 | 40 | 0 | 9.5676
0.76206 | 0 | 0.28611 | 572.9422 | 40 | 0 | 11.4444
0.7137 | 0 | 0.35443 | 555.7494 | 40 | 0 | 14.1772
0.65454 | 0 | 0.39469 | 546.083 | 40 | 0 | 15.7876
0.60667 | 0 | 0.40255 | 541.518 | 40 | 0 | 16.102
0.57201 | 0 | 0.4077 | 540.625 | 40 | 0 | 16.308
0.54609 | 0 | 0.34222 | 539.7048 | 40 | 0 | 13.6888
0.52959 | 0 | 0.32478 | 539.737 | 40 | 0 | 12.9912
0.52202 | 0 | 0.31668 | 540.2022 | 40 | 0 | 12.6672
0.53047 | 0 | 0.35359 | 541.2988 | 40 | 0 | 14.1436
0.55921 | 0 | 0.36341 | 539.9142 | 40 | 0 | 14.5364
0.5901 | 0.0031 | 0.34477 | 534.912 | 40 | 0.217 | 13.7908
0.58621 | 0.2094 | 0.30603 | 543.1902 | 40 | 14.658 | 12.2412
0.61608 | 0.6765 | 0.22678 | 578.0084 | 40 | 56.4262 | 0
0.66306 | 0.7791 | 0.2002 | 614.2474 | 40 | 62.545 | 0
0.71003 | 0.8658 | 0.15275 | 649.9604 | 40 | 66.716 | 0
0.75879 | 0.814 | 0.12969 | 676.249 | 40 | 62.1676 | 0
0.79935 | 0.7885 | 0.15463 | 697.6942 | 40 | 61.3802 | 0
0.83038 | 0.7494 | 0.17418 | 700 | 40 | 45.3438 | 0
0.85318 | 0.7786 | 0.22789 | 700 | 40 | 45.318 | 0
0.86193 | 0.6487 | 0.26652 | 700 | 40 | 45.409 | 0.784
0.85326 | 0.5098 | 0.3073 | 700 | 40 | 35.686 | 9.64
0.82813 | 0.2976 | 0.31576 | 690.6494 | 40 | 20.832 | 12.6304
0.79505 | 0.0069 | 0.30575 | 663.8574 | 40 | 0.483 | 12.23
0.77196 | 0 | 0.32725 | 639.7514 | 40 | 0 | 13.09
0.74426 | 0 | 0.34302 | 619.0462 | 40 | 0 | 13.7208
0.69681 | 0 | 0.34038 | 602.9804 | 40 | 0 | 13.6152
0.6444 | 0 | 0.32195 | 591.4184 | 40 | 0 | 12.878
0.59306 | 0 | 0.25172 | 582.1812 | 40 | 0 | 10.0688
0.55651 | 0 | 0.2158 | 575.1622 | 40 | 0 | 8.632
0.53183 | 0 | 0.19214 | 569.6648 | 40 | 0 | 7.6856
0.51212 | 0 | 0.14968 | 564.44 | 40 | 0 | 5.9872
0.50304 | 0 | 0.11812 | 558.8608 | 40 | 0 | 4.7248
0.51011 | 0 | 0.1063 | 552.1018 | 40 | 0 | 4.252
0.54035 | 0 | 0.08432 | 541.4396 | 40 | 0 | 3.3728
0.57272 | 0.0022 | 0.06664 | 526.9872 | 40 | 0.154 | 2.6656
0.56734 | 0.1893 | 0.04381 | 525.2566 | 40 | 13.251 | 1.7524
0.59157 | 0.6324 | 0.02602 | 551.4084 | 40 | 45.3088 | 0
0.6261 | 0.7737 | 0.02558 | 583.9806 | 40 | 55.1822 | 0
0.66983 | 0.819 | 0.04665 | 616.1936 | 40 | 59.196 | 0
0.71094 | 0.8276 | 0.07662 | 646.0964 | 40 | 60.9968 | 0
0.75501 | 0.8547 | 0.09565 | 674.2504 | 40 | 63.655 | 0
0.79209 | 0.8576 | 0.10571 | 699.3018 | 40 | 64.2604 | -1.1369e-13
0.81789 | 0.8357 | 0.12231 | 700 | 40 | 42.4872 | 0
0.83853 | 0.795 | 0.13735 | 700 | 40 | 43.853 | 0
0.83743 | 0.6947 | 0.17426 | 700 | 40 | 43.743 | 0
0.81241 | 0.2916 | 0.16883 | 685.9242 | 40 | 20.412 | 6.7532
0.76641 | 0.0109 | 0.15858 | 656.3894 | 40 | 0.763 | 6.3432
0.74334 | 0 | 0.20331 | 630.1878 | 40 | 0 | 8.1324
0.71149 | 0 | 0.25834 | 609.3724 | 40 | 0 | 10.3336
0.67368 | 0 | 0.29258 | 593.7076 | 40 | 0 | 11.7032
0.63262 | 0 | 0.35072 | 584.4744 | 40 | 0 | 14.0288
0.58607 | 0 | 0.37642 | 580.9242 | 40 | 0 | 15.0568
0.55341 | 0 | 0.42869 | 582.7308 | 40 | 0 | 17.1476
0.52414 | 0 | 0.42522 | 587.3256 | 40 | 0 | 17.0088
0.50689 | 0 | 0.43863 | 594.1818 | 40 | 0 | 17.5452
0.49322 | 0 | 0.42015 | 601.6658 | 40 | 0 | 16.806
0.48741 | 0 | 0.40567 | 609.1516 | 40 | 0 | 16.2268
0.49111 | 0 | 0.40092 | 616.0774 | 40 | 0 | 16.0368
0.50021 | 0.0028 | 0.39489 | 622.048 | 40 | 0.196 | 15.7956
0.5089 | 0.2065 | 0.36285 | 640.127 | 40 | 28.969 | 0
0.54966 | 0.6423 | 0.26313 | 680.6472 | 40 | 55.4862 | 0
0.5987 | 0.8167 | 0.24685 | 700 | 40 | 39.2228 | 0
0.65305 | 0.8886 | 0.2919 | 700 | 40 | 25.305 | 0
0.70533 | 0.8822 | 0.22606 | 700 | 40 | 30.533 | 0
0.75363 | 0.8804 | 0.14042 | 700 | 40 | 35.363 | 0
0.78588 | 0.846 | 0.08699 | 700 | 40 | 38.588 | 0
0.80655 | 0.8076 | 0.06512 | 700 | 40 | 40.655 | 0
0.81935 | 0.7595 | 0.05802 | 700 | 40 | 41.935 | 0
0.81947 | 0.7036 | 0.05914 | 700 | 40 | 41.947 | 0
0.80603 | 0.3028 | 0.07107 | 683.4358 | 40 | 21.196 | 2.8428
0.76603 | 0.0098 | 0.09202 | 651.1996 | 40 | 0.686 | 3.6808
0.74309 | 0 | 0.16293 | 623.4078 | 40 | 0 | 6.5172
0.70732 | 0 | 0.27294 | 603.5934 | 40 | 0 | 10.9176
0.66932 | 0 | 0.32801 | 589.7818 | 40 | 0 | 13.1204
0.62788 | 0 | 0.33164 | 580.2594 | 40 | 0 | 13.2656
0.58651 | 0 | 0.32925 | 574.7784 | 40 | 0 | 13.17
0.55548 | 0 | 0.32618 | 572.2776 | 40 | 0 | 13.0472
0.52759 | 0 | 0.31026 | 571.929 | 40 | 0 | 12.4104
0.50587 | 0 | 0.29066 | 572.9684 | 40 | 0 | 11.6264
0.49361 | 0 | 0.24733 | 573.5006 | 40 | 0 | 9.8932
0.48627 | 0 | 0.19984 | 572.8672 | 40 | 0 | 7.9936
0.48482 | 0 | 0.19074 | 572.0148 | 40 | 0 | 7.6296
0.48899 | 0.0022 | 0.18779 | 570.7814 | 40 | 0.154 | 7.5116
0.49398 | 0.2044 | 0.1929 | 583.4074 | 40 | 22.024 | 0
0.53807 | 0.7098 | 0.13244 | 624.584 | 40 | 54.9836 | 0
0.59504 | 0.8641 | 0.12741 | 670.6634 | 40 | 65.5834 | 0
0.64935 | 0.8888 | 0.10084 | 700 | 40 | 54.2716 | 1.1369e-13
0.70587 | 0.8955 | 0.08025 | 700 | 40 | 30.587 | 0
0.75342 | 0.8864 | 0.09274 | 700 | 40 | 35.342 | 0
0.79505 | 0.8725 | 0.13583 | 700 | 40 | 39.505 | 0
0.81915 | 0.8649 | 0.16963 | 700 | 40 | 41.915 | 0
0.83887 | 0.8416 | 0.22243 | 700 | 40 | 43.887 | 0
0.83511 | 0.707 | 0.37211 | 700 | 40 | 43.511 | 0
0.80848 | 0.2731 | 0.44661 | 696.1334 | 40 | 19.117 | 17.8644
0.77116 | 0.0094 | 0.49589 | 679.511 | 40 | 0.658 | 19.8356
0.75442 | 0 | 0.51704 | 664.7506 | 40 | 0 | 20.6816
0.71459 | 0 | 0.56109 | 655.7352 | 40 | 0 | 22.4436
0.66098 | 0 | 0.53867 | 651.184 | 40 | 0 | 21.5468
0.60486 | 0 | 0.516 | 651.338 | 40 | 0 | 20.64
0.5539 | 0 | 0.49262 | 655.6528 | 40 | 0 | 19.7048
0.5206 | 0 | 0.48452 | 662.9736 | 40 | 0 | 19.3808
0.49787 | 0 | 0.45794 | 671.5042 | 40 | 0 | 18.3176
0.48364 | 0 | 0.42578 | 680.1714 | 40 | 0 | 17.0312
0.47505 | 0 | 0.39892 | 688.6232 | 40 | 0 | 15.9568
0.48026 | 0 | 0.38595 | 696.0352 | 40 | 0 | 15.438
0.50862 | 0 | 0.35451 | 699.3536 | 40 | 0 | 14.1804
0.54244 | 0.0015 | 0.3512 | 699.2626 | 40 | 0.105 | 14.048
0.53558 | 0.0763 | 0.33715 | 700 | 40 | 5.341 | 8.9544
0.55315 | 0.2661 | 0.283 | 700 | 40 | 15.315 | 0
0.57481 | 0.4216 | 0.33073 | 700 | 40 | 17.481 | 0
0.59799 | 0.6488 | 0.35383 | 700 | 40 | 19.799 | 0
0.61309 | 0.7401 | 0.27538 | 700 | 40 | 21.309 | 0
0.64032 | 0.8543 | 0.23045 | 700 | 40 | 24.032 | 0
0.66011 | 0.8836 | 0.19577 | 700 | 40 | 26.011 | 0
0.68034 | 0.9032 | 0.15966 | 700 | 40 | 28.034 | 0
0.69052 | 0.9085 | 0.14046 | 700 | 40 | 29.052 | 0
0.68627 | 0.7699 | 0.12805 | 700 | 40 | 28.627 | 0
0.67135 | 0.312 | 0.12446 | 699.6834 | 40 | 21.84 | 4.9784
0.64948 | 0.0082 | 0.12334 | 680.243 | 40 | 0.574 | 4.9336
0.64373 | 0 | 0.15619 | 662.1176 | 40 | 0 | 6.2476
0.61573 | 0 | 0.21257 | 649.0474 | 40 | 0 | 8.5028
0.57507 | 0 | 0.22901 | 640.7008 | 40 | 0 | 9.1604
0.523 | 0 | 0.24226 | 638.0912 | 40 | 0 | 9.6904
0.48283 | 0 | 0.2415 | 639.4682 | 40 | 0 | 9.66
0.4558 | 0 | 0.25136 | 643.9426 | 40 | 0 | 10.0544
0.43667 | 0 | 0.29294 | 651.9932 | 40 | 0 | 11.7176
0.42819 | 0 | 0.33811 | 662.6986 | 40 | 0 | 13.5244
0.42437 | 0 | 0.36967 | 675.0484 | 40 | 0 | 14.7868
0.43348 | 0 | 0.37035 | 686.5144 | 40 | 0 | 14.814
0.4667 | 0 | 0.38121 | 695.0928 | 40 | 0 | 15.2484
0.49959 | 0.0026 | 0.40303 | 700 | 40 | 0.182 | 14.6842
0.49437 | 0.218 | 0.39657 | 700 | 40 | 9.437 | 0
0.50725 | 0.727 | 0.3435 | 700 | 40 | 10.725 | 0
0.52686 | 0.6971 | 0.35036 | 700 | 40 | 12.686 | 0
0.55044 | 0.7828 | 0.34605 | 700 | 40 | 15.044 | 0
0.57296 | 0.8536 | 0.32067 | 700 | 40 | 17.296 | 0
0.59948 | 0.8595 | 0.29884 | 700 | 40 | 19.948 | 0
0.62854 | 0.9091 | 0.27753 | 700 | 40 | 22.854 | 0
0.65164 | 0.8976 | 0.27598 | 700 | 40 | 25.164 | 0
0.67539 | 0.8807 | 0.30666 | 700 | 40 | 27.539 | 0
0.68566 | 0.6249 | 0.35363 | 700 | 40 | 28.566 | 0
0.67721 | 0.2814 | 0.39002 | 700 | 40 | 19.698 | 8.023
0.64948 | 0.0042 | 0.40766 | 691.6524 | 40 | 0.294 | 16.3064
0.64162 | 0 | 0.48851 | 687.0308 | 40 | 0 | 19.5404
0.61366 | 0 | 0.52797 | 686.7836 | 40 | 0 | 21.1188
0.57228 | 0 | 0.52674 | 690.6252 | 40 | 0 | 21.0696
0.52316 | 0 | 0.52019 | 699.1168 | 40 | 0 | 20.8076
0.48102 | 0 | 0.49481 | 700 | 40 | 0 | 8.9852
0.45837 | 0 | 0.51712 | 700 | 40 | 0 | 5.837
0.4417 | 0 | 0.50722 | 700 | 40 | 0 | 4.17
0.43312 | 0 | 0.51883 | 700 | 40 | 0 | 3.312
0.4314 | 0 | 0.52338 | 700 | 40 | 0 | 3.14
0.44479 | 0 | 0.52338 | 700 | 40 | 0 | 4.479
0.47845 | 0 | 0.53328 | 700 | 40 | 0 | 7.845
0.51561 | 0.0012 | 0.53077 | 700 | 40 | 0.084 | 11.477
0.51656 | 0.1187 | 0.5318 | 700 | 40 | 8.309 | 3.347
0.53469 | 0.4501 | 0.52107 | 700 | 40 | 13.469 | 0
0.56652 | 0.4843 | 0.58304 | 700 | 40 | 16.652 | 0
0.60139 | 0.4561 | 0.61006 | 700 | 40 | 20.139 | 0
0.63668 | 0.5044 | 0.61373 | 700 | 40 | 23.668 | 0
0.67549 | 0.6058 | 0.62594 | 700 | 40 | 27.549 | 0
0.71563 | 0.6654 | 0.61923 | 700 | 40 | 31.563 | 0
0.7448 | 0.7259 | 0.62757 | 700 | 40 | 34.48 | 0
0.77121 | 0.6148 | 0.62813 | 700 | 40 | 37.121 | 0
0.77981 | 0.5288 | 0.65507 | 700 | 40 | 37.016 | 0.965
0.76754 | 0.2144 | 0.67195 | 700 | 40 | 15.008 | 21.746
0.74136 | 0.005 | 0.65319 | 692.3416 | 40 | 0.35 | 26.1276
0.73659 | 0 | 0.64808 | 684.6058 | 40 | 0 | 25.9232
0.70795 | 0 | 0.67239 | 680.7064 | 40 | 0 | 26.8956
0.67014 | 0 | 0.68587 | 681.1272 | 40 | 0 | 27.4348
0.61926 | 0 | 0.67318 | 686.1284 | 40 | 0 | 26.9272
0.57563 | 0 | 0.64868 | 694.5126 | 40 | 0 | 25.9472
0.54982 | 0 | 0.64785 | 700 | 40 | 0 | 20.4694
0.5311 | 0 | 0.62418 | 700 | 40 | 0 | 13.11
0.52163 | 0 | 0.62546 | 700 | 40 | 0 | 12.163
0.52034 | 0 | 0.61927 | 700 | 40 | 0 | 12.034
0.53006 | 0 | 0.62674 | 700 | 40 | 0 | 13.006
0.56314 | 0 | 0.63093 | 700 | 40 | 0 | 16.314
0.6003 | 0.0007 | 0.63304 | 700 | 40 | 0.049 | 19.981
0.59997 | 0.1659 | 0.62139 | 700 | 40 | 11.613 | 8.384
0.62136 | 0.4474 | 0.58998 | 700 | 40 | 22.136 | 0
0.6554 | 0.3424 | 0.63384 | 700 | 40 | 23.968 | 1.572
0.69087 | 0.5195 | 0.62275 | 700 | 40 | 29.087 | 0
0.72359 | 0.6864 | 0.56652 | 700 | 40 | 32.359 | 0
0.7624 | 0.7902 | 0.49613 | 700 | 40 | 36.24 | 0
0.79304 | 0.866 | 0.4429 | 700 | 40 | 39.304 | 0
0.81531 | 0.8855 | 0.42937 | 700 | 40 | 41.531 | 0
0.83409 | 0.8735 | 0.4492 | 700 | 40 | 43.409 | 0
0.83227 | 0.7313 | 0.49705 | 700 | 40 | 43.227 | 0
0.8145 | 0.2911 | 0.54908 | 700 | 40 | 20.377 | 21.073
0.78297 | 0.0057 | 0.57023 | 684.9112 | 40 | 0.399 | 22.8092
0.76597 | 0 | 0.59653 | 672.1754 | 40 | 0 | 23.8612
0.72759 | 0 | 0.59641 | 663.2728 | 40 | 0 | 23.8564
0.671 | 0 | 0.599 | 660.1328 | 40 | 0 | 23.96
0.6161 | 0 | 0.61895 | 663.2808 | 40 | 0 | 24.758
0.56451 | 0 | 0.63232 | 672.1226 | 40 | 0 | 25.2928
0.53207 | 0 | 0.6235 | 683.8556 | 40 | 0 | 24.94
0.50729 | 0 | 0.60894 | 697.4842 | 40 | 0 | 24.3576
0.49176 | 0 | 0.58867 | 700 | 40 | 0 | 11.6918
0.4794 | 0 | 0.56664 | 700 | 40 | 0 | 7.94
0.47925 | 0 | 0.54792 | 700 | 40 | 0 | 7.925
0.5001 | 0 | 0.54972 | 700 | 40 | 0 | 10.01
0.52658 | 0.0006 | 0.57394 | 700 | 40 | 0.042 | 12.616
0.52597 | 0.0867 | 0.57917 | 700 | 40 | 6.069 | 6.528
0.53694 | 0.2165 | 0.56624 | 700 | 40 | 13.694 | 0
0.53918 | 0.4198 | 0.55539 | 700 | 40 | 13.918 | 0
0.53972 | 0.6069 | 0.54222 | 700 | 40 | 13.972 | 0
0.52605 | 0.6817 | 0.5095 | 700 | 40 | 12.605 | 0
0.51731 | 0.7161 | 0.50591 | 700 | 40 | 11.731 | 0
0.5145 | 0.8172 | 0.50515 | 700 | 40 | 11.45 | 0
0.50743 | 0.8622 | 0.46341 | 700 | 40 | 10.743 | 0
0.50002 | 0.8318 | 0.39266 | 700 | 40 | 10.002 | 0
0.48655 | 0.6962 | 0.33073 | 700 | 40 | 8.655 | 0
0.48792 | 0.2746 | 0.27231 | 700 | 40 | 8.792 | 0
0.48737 | 0.005 | 0.22362 | 700 | 40 | 0.35 | 8.387
0.49388 | 0 | 0.22534 | 699.6256 | 40 | 0 | 9.0136
0.4825 | 0 | 0.23807 | 700 | 40 | 0 | 8.6244
0.46757 | 0 | 0.22941 | 700 | 40 | 0 | 6.757
0.44511 | 0 | 0.22334 | 700 | 40 | 0 | 4.511
0.42314 | 0 | 0.218 | 700 | 40 | 0 | 2.314
0.40917 | 0 | 0.20583 | 700 | 40 | 0 | 0.917
0.39558 | 0 | 0.2172 | 700 | 39.558 | 0 | 0
0.39176 | 0 | 0.22885 | 700 | 39.176 | 0 | 0
0.395 | 0 | 0.24082 | 700 | 39.5 | 0 | 0
0.39911 | 0 | 0.23516 | 700 | 39.911 | 0 | 0
0.41049 | 0 | 0.23823 | 700 | 40 | 0 | 1.049
0.43 | 0.0011 | 0.25802 | 700 | 40 | 0.077 | 2.923
0.4486 | 0.0815 | 0.26891 | 700 | 40 | 4.86 | 0
0.46383 | 0.2749 | 0.24769 | 700 | 40 | 6.383 | 0
0.47083 | 0.4557 | 0.2103 | 700 | 40 | 7.083 | 0
0.47178 | 0.6062 | 0.24541 | 700 | 40 | 7.178 | 0
0.46648 | 0.7005 | 0.26856 | 700 | 40 | 6.648 | 0
0.46028 | 0.7918 | 0.26393 | 700 | 40 | 6.028 | 0
0.45761 | 0.8726 | 0.25798 | 700 | 40 | 5.761 | 0
0.45794 | 0.7936 | 0.24996 | 700 | 40 | 5.794 | 0
0.46095 | 0.8 | 0.24769 | 700 | 40 | 6.095 | 0
0.46597 | 0.6612 | 0.25271 | 700 | 40 | 6.597 | 0
0.46474 | 0.2257 | 0.26089 | 700 | 40 | 6.474 | 0
0.468 | 0.0041 | 0.23911 | 700 | 40 | 0.287 | 6.513
0.47555 | 0 | 0.32063 | 700 | 40 | 0 | 7.555
0.47009 | 0 | 0.40176 | 700 | 40 | 0 | 7.009
0.45395 | 0 | 0.4591 | 700 | 40 | 0 | 5.395
0.43745 | 0 | 0.46453 | 700 | 40 | 0 | 3.745
0.41629 | 0 | 0.44162 | 700 | 40 | 0 | 1.629
0.40057 | 0 | 0.4502 | 700 | 40 | 0 | 0.057
0.39063 | 0 | 0.44493 | 700 | 39.063 | 0 | 0
0.38328 | 0 | 0.42825 | 700 | 38.328 | 0 | 0
0.38116 | 0 | 0.41939 | 700 | 38.116 | 0 | 0
0.3809 | 0 | 0.41381 | 700 | 38.09 | 0 | 0
0.38859 | 0 | 0.40998 | 700 | 38.859 | 0 | 0
0.3977 | 0.0007 | 0.38958 | 700 | 39.77 | 0 | 0
0.4083 | 0.1747 | 0.36213 | 700 | 40 | 0.83 | 0
0.42785 | 0.5516 | 0.27534 | 700 | 40 | 2.785 | 0
0.44 | 0.6584 | 0.16891 | 700 | 40 | 4 | 0
0.45299 | 0.7208 | 0.11927 | 700 | 40 | 5.299 | 0
0.46454 | 0.7367 | 0.08188 | 700 | 40 | 6.454 | 0
0.47799 | 0.7561 | 0.07167 | 700 | 40 | 7.799 | 0
0.49137 | 0.7646 | 0.06748 | 700 | 40 | 9.137 | 0
0.51083 | 0.6853 | 0.08388 | 700 | 40 | 11.083 | 0
0.52767 | 0.5008 | 0.10479 | 700 | 40 | 12.767 | 0
0.54134 | 0.2226 | 0.11528 | 700 | 40 | 14.134 | 0
0.54056 | 0.0544 | 0.13336 | 695.0864 | 40 | 3.808 | 5.3344
0.54673 | 0.0001 | 0.17275 | 687.3304 | 40 | 0.007 | 6.91
0.55308 | 0 | 0.25866 | 682.3688 | 40 | 0 | 10.3464
0.53742 | 0 | 0.32103 | 681.468 | 40 | 0 | 12.8412
0.51643 | 0 | 0.34206 | 683.5074 | 40 | 0 | 13.6824
0.48455 | 0 | 0.33871 | 688.6008 | 40 | 0 | 13.5484
0.45317 | 0 | 0.33563 | 696.709 | 40 | 0 | 13.4252
0.43137 | 0 | 0.34198 | 700 | 40 | 0 | 6.428
0.41694 | 0 | 0.30862 | 700 | 40 | 0 | 1.694
0.4131 | 0 | 0.3018 | 700 | 40 | 0 | 1.31
0.41337 | 0 | 0.30407 | 700 | 40 | 0 | 1.337
0.42272 | 0 | 0.32107 | 700 | 40 | 0 | 2.272
0.45065 | 0 | 0.32662 | 700 | 40 | 0 | 5.065
0.48351 | 0.0003 | 0.31026 | 700 | 40 | 0.021 | 8.33
0.49284 | 0.0233 | 0.32446 | 700 | 40 | 1.631 | 7.653
0.51221 | 0.0798 | 0.32809 | 700 | 40 | 5.586 | 5.635
0.54009 | 0.1366 | 0.25674 | 700 | 40 | 9.562 | 4.447
0.56476 | 0.2427 | 0.22394 | 700 | 40 | 16.476 | 0
0.59302 | 0.3249 | 0.20012 | 700 | 40 | 19.302 | 0
0.61943 | 0.3362 | 0.17614 | 700 | 40 | 21.943 | 0
0.63742 | 0.4134 | 0.18504 | 700 | 40 | 23.742 | 0
0.65563 | 0.3898 | 0.21879 | 700 | 40 | 25.563 | 0
0.66696 | 0.2712 | 0.26209 | 700 | 40 | 18.984 | 7.712
0.66854 | 0.2341 | 0.27989 | 700 | 40 | 16.387 | 10.467
0.66244 | 0.1018 | 0.32598 | 693.9212 | 40 | 7.126 | 13.0392
0.65938 | 0.0013 | 0.32063 | 680.8994 | 40 | 0.091 | 12.8252
0.65703 | 0 | 0.35439 | 669.372 | 40 | 0 | 14.1756
0.63328 | 0 | 0.4595 | 664.424 | 40 | 0 | 18.38
0.59885 | 0 | 0.50734 | 664.8326 | 40 | 0 | 20.2936
0.55787 | 0 | 0.5233 | 669.9776 | 40 | 0 | 20.932
0.52146 | 0 | 0.51369 | 678.3792 | 40 | 0 | 20.5476
0.49896 | 0 | 0.51313 | 689.0084 | 40 | 0 | 20.5252
0.48381 | 0 | 0.50379 | 700 | 40 | 0 | 19.3726
0.47387 | 0 | 0.45778 | 700 | 40 | 0 | 7.387
0.47343 | 0 | 0.43847 | 700 | 40 | 0 | 7.343
0.48651 | 0 | 0.41061 | 700 | 40 | 0 | 8.651
0.52099 | 0 | 0.37801 | 700 | 40 | 0 | 12.099
0.56111 | 0.0005 | 0.35323 | 698.0532 | 40 | 0.035 | 14.1292
0.56372 | 0.0424 | 0.34306 | 698.3716 | 40 | 2.968 | 13.7224
0.57905 | 0.2542 | 0.33252 | 700 | 40 | 17.794 | 1.7394
0.60518 | 0.4172 | 0.31457 | 700 | 40 | 20.518 | 0
0.63646 | 0.506 | 0.31169 | 700 | 40 | 23.646 | 0
0.66734 | 0.4989 | 0.31277 | 700 | 40 | 26.734 | 0
0.69625 | 0.5674 | 0.2844 | 700 | 40 | 29.625 | 0
0.71943 | 0.5065 | 0.28563 | 700 | 40 | 31.943 | 0
0.73875 | 0.4759 | 0.28328 | 700 | 40 | 33.313 | 0.562
0.75968 | 0.5535 | 0.31636 | 700 | 40 | 35.968 | 0
0.7651 | 0.4406 | 0.37889 | 700 | 40 | 30.842 | 5.668
0.74756 | 0.1123 | 0.48751 | 692.6054 | 40 | 7.861 | 19.5004
0.72005 | 0.002 | 0.50986 | 681.1348 | 40 | 0.14 | 20.3944
0.70709 | 0 | 0.51453 | 671.007 | 40 | 0 | 20.5812
0.67936 | 0 | 0.54441 | 664.8474 | 40 | 0 | 21.7764
0.63285 | 0 | 0.54166 | 663.2288 | 40 | 0 | 21.6664
0.58239 | 0 | 0.5269 | 666.0658 | 40 | 0 | 21.076
0.53373 | 0 | 0.50176 | 672.7632 | 40 | 0 | 20.0704
0.49967 | 0 | 0.52614 | 683.8418 | 40 | 0 | 21.0456
0.47658 | 0 | 0.52259 | 697.0874 | 40 | 0 | 20.9036
0.46195 | 0 | 0.49749 | 700 | 40 | 0 | 9.1076
0.45498 | 0 | 0.46911 | 700 | 40 | 0 | 5.498
0.46043 | 0 | 0.39828 | 700 | 40 | 0 | 6.043
0.48734 | 0 | 0.36205 | 700 | 40 | 0 | 8.734
0.5168 | 0.0003 | 0.3417 | 700 | 40 | 0.021 | 11.659
0.51558 | 0.0862 | 0.31437 | 700 | 40 | 6.034 | 5.524
0.51722 | 0.3502 | 0.23316 | 700 | 40 | 11.722 | 0
0.52252 | 0.5182 | 0.19597 | 700 | 40 | 12.252 | 0
0.52849 | 0.602 | 0.21457 | 700 | 40 | 12.849 | 0
0.52792 | 0.6668 | 0.20479 | 700 | 40 | 12.792 | 0
0.52576 | 0.6935 | 0.21006 | 700 | 40 | 12.576 | 0
0.52422 | 0.7367 | 0.2087 | 700 | 40 | 12.422 | 0
0.52144 | 0.7336 | 0.20387 | 700 | 40 | 12.144 | 0
0.52197 | 0.7165 | 0.20259 | 700 | 40 | 12.197 | 0
0.52033 | 0.5981 | 0.19972 | 700 | 40 | 12.033 | 0
0.5149 | 0.2104 | 0.1753 | 700 | 40 | 11.49 | 0
0.52092 | 0.0028 | 0.183 | 695.424 | 40 | 0.196 | 7.32
0.52552 | 0 | 0.23077 | 692.1028 | 40 | 0 | 9.2308
0.51176 | 0 | 0.23416 | 690.2932 | 40 | 0 | 9.3664
0.4847 | 0 | 0.25283 | 691.9364 | 40 | 0 | 10.1132
0.44808 | 0 | 0.25726 | 697.4188 | 40 | 0 | 10.2904
0.41827 | 0 | 0.28224 | 700 | 40 | 0 | 4.4082
0.39957 | 0 | 0.29864 | 700 | 39.957 | 0 | 0
0.38899 | 0 | 0.31656 | 700 | 38.899 | 0 | 0
0.38277 | 0 | 0.36281 | 700 | 38.277 | 0 | 0
0.38412 | 0 | 0.37171 | 700 | 38.412 | 0 | 0
0.39686 | 0 | 0.3652 | 700 | 39.686 | 0 | 0
0.43229 | 0 | 0.32502 | 700 | 40 | 0 | 3.229
0.47312 | 0.0003 | 0.31919 | 700 | 40 | 0.021 | 7.291
0.47566 | 0.1424 | 0.28715 | 700 | 40 | 7.566 | 0
0.47826 | 0.5975 | 0.26556 | 700 | 40 | 7.826 | 0
0.48301 | 0.7826 | 0.18061 | 700 | 40 | 8.301 | 0
0.48349 | 0.8216 | 0.17023 | 700 | 40 | 8.349 | 0
0.48591 | 0.8109 | 0.1492 | 700 | 40 | 8.591 | 0
0.49121 | 0.807 | 0.151 | 700 | 40 | 9.121 | 0
0.4968 | 0.8054 | 0.16129 | 700 | 40 | 9.68 | 0
0.50528 | 0.8093 | 0.17829 | 700 | 40 | 10.528 | 0
0.51067 | 0.807 | 0.21796 | 700 | 40 | 11.067 | 0
0.51376 | 0.6642 | 0.25491 | 700 | 40 | 11.376 | 0
0.51376 | 0.2293 | 0.28412 | 700 | 40 | 11.376 | 0
0.51753 | 0.004 | 0.34322 | 700 | 40 | 0.28 | 11.473
0.52566 | 0 | 0.48647 | 700 | 40 | 0 | 12.566
0.51235 | 0 | 0.51093 | 700 | 40 | 0 | 11.235
0.48595 | 0 | 0.47338 | 700 | 40 | 0 | 8.595
0.45048 | 0 | 0.47434 | 700 | 40 | 0 | 5.048
0.42244 | 0 | 0.46197 | 700 | 40 | 0 | 2.244
0.40583 | 0 | 0.46688 | 700 | 40 | 0 | 0.583
0.39635 | 0 | 0.45619 | 700 | 39.635 | 0 | 0
0.39001 | 0 | 0.45116 | 700 | 39.001 | 0 | 0
0.39009 | 0 | 0.4565 | 700 | 39.009 | 0 | 0
0.40486 | 0 | 0.46089 | 700 | 40 | 0 | 0.486
0.43737 | 0 | 0.48424 | 700 | 40 | 0 | 3.737
0.47693 | 0.001 | 0.50455 | 700 | 40 | 0.07 | 7.623
0.4787 | 0.1689 | 0.49473 | 700 | 40 | 7.87 | 0
0.48357 | 0.6645 | 0.42845 | 700 | 40 | 8.357 | 0
0.4924 | 0.8037 | 0.36616 | 700 | 40 | 9.24 | 0
0.50238 | 0.8355 | 0.32757 | 700 | 40 | 10.238 | 0
0.51323 | 0.8319 | 0.31768 | 700 | 40 | 11.323 | 0
0.52868 | 0.8199 | 0.3565 | 700 | 40 | 12.868 | 0
0.54589 | 0.7592 | 0.36057 | 700 | 40 | 14.589 | 0
0.56107 | 0.6274 | 0.38635 | 700 | 40 | 16.107 | 0
0.57886 | 0.6792 | 0.42127 | 700 | 40 | 17.886 | 0
0.58756 | 0.5589 | 0.45483 | 700 | 40 | 18.756 | 0
0.58065 | 0.1796 | 0.47797 | 700 | 40 | 12.572 | 5.493
0.56447 | 0.0003 | 0.47518 | 700 | 40 | 0.021 | 16.426
0.55882 | 0 | 0.52578 | 700 | 40 | 0 | 15.882
0.54053 | 0 | 0.52458 | 700 | 40 | 0 | 14.053
0.52013 | 0 | 0.52047 | 700 | 40 | 0 | 12.013
0.48852 | 0 | 0.46213 | 700 | 40 | 0 | 8.852
0.4603 | 0 | 0.47829 | 700 | 40 | 0 | 6.03
0.43734 | 0 | 0.47199 | 700 | 40 | 0 | 3.734
0.42131 | 0 | 0.46856 | 700 | 40 | 0 | 2.131
0.41336 | 0 | 0.4492 | 700 | 40 | 0 | 1.336
0.40904 | 0 | 0.45894 | 700 | 40 | 0 | 0.904
0.41043 | 0 | 0.47598 | 700 | 40 | 0 | 1.043
0.42189 | 0 | 0.48974 | 700 | 40 | 0 | 2.189
0.43779 | 0.0006 | 0.4911 | 700 | 40 | 0.042 | 3.737
0.45168 | 0.1561 | 0.47594 | 700 | 40 | 5.168 | 0
0.47987 | 0.6307 | 0.36752 | 700 | 40 | 7.987 | 0
0.50983 | 0.7953 | 0.32953 | 700 | 40 | 10.983 | 0
0.54178 | 0.8149 | 0.29561 | 700 | 40 | 14.178 | 0
0.57291 | 0.8399 | 0.24553 | 700 | 40 | 17.291 | 0
0.60675 | 0.8307 | 0.18448 | 700 | 40 | 20.675 | 0
0.63188 | 0.8358 | 0.13144 | 700 | 40 | 23.188 | 0
0.65856 | 0.8419 | 0.10495 | 700 | 40 | 25.856 | 0
0.67662 | 0.8199 | 0.09162 | 700 | 40 | 27.662 | 0
0.68133 | 0.6438 | 0.09637 | 700 | 40 | 28.133 | 0
0.66471 | 0.1957 | 0.08699 | 690.7076 | 40 | 13.699 | 3.4796
0.63931 | 0.0008 | 0.08707 | 670.3154 | 40 | 0.056 | 3.4828
0.62206 | 0 | 0.10998 | 652.5086 | 40 | 0 | 4.3992
0.59563 | 0 | 0.15431 | 639.118 | 40 | 0 | 6.1724
0.56698 | 0 | 0.2081 | 630.744 | 40 | 0 | 8.324
0.53172 | 0 | 0.24948 | 627.5512 | 40 | 0 | 9.9792
0.50193 | 0 | 0.31656 | 630.0206 | 40 | 0 | 12.6624
0.47499 | 0 | 0.36445 | 637.0996 | 40 | 0 | 14.578
0.45528 | 0 | 0.38867 | 647.1184 | 40 | 0 | 15.5468
0.4416 | 0 | 0.42003 | 659.7596 | 40 | 0 | 16.8012
0.43439 | 0 | 0.45499 | 674.5202 | 40 | 0 | 18.1996
0.43143 | 0 | 0.4583 | 689.7092 | 40 | 0 | 18.332
0.43351 | 0 | 0.45982 | 700 | 40 | 0 | 13.6418
0.44264 | 0.0005 | 0.47346 | 700 | 40 | 0.035 | 4.229
0.4524 | 0.0784 | 0.47801 | 700 | 40 | 5.24 | 0
0.4785 | 0.4943 | 0.47298 | 700 | 40 | 7.85 | 0
0.51484 | 0.7167 | 0.44513 | 700 | 40 | 11.484 | 0
0.54633 | 0.7436 | 0.46987 | 700 | 40 | 14.633 | 0
0.58177 | 0.6904 | 0.49932 | 700 | 40 | 18.177 | 0
0.61384 | 0.6305 | 0.52761 | 700 | 40 | 21.384 | 0
0.64905 | 0.6854 | 0.55271 | 700 | 40 | 24.905 | 0
0.67847 | 0.5861 | 0.56081 | 700 | 40 | 27.847 | 0
0.69792 | 0.5729 | 0.57698 | 700 | 40 | 29.792 | 0
0.70681 | 0.4733 | 0.58911 | 700 | 40 | 30.681 | 0
0.69893 | 0.1766 | 0.58695 | 700 | 40 | 12.362 | 17.531
0.69332 | 0.0006 | 0.52913 | 691.8752 | 40 | 0.042 | 21.1652
0.68619 | 0 | 0.51121 | 683.7046 | 40 | 0 | 20.4484
0.65969 | 0 | 0.53412 | 679.1004 | 40 | 0 | 21.3648
0.61551 | 0 | 0.56073 | 679.9786 | 40 | 0 | 22.4292
0.579 | 0 | 0.56644 | 684.7362 | 40 | 0 | 22.6576
0.54775 | 0 | 0.57267 | 692.868 | 40 | 0 | 22.9068
0.51502 | 0 | 0.56572 | 700 | 40 | 0 | 18.634
0.49453 | 0 | 0.51189 | 700 | 40 | 0 | 9.453
0.47931 | 0 | 0.43555 | 700 | 40 | 0 | 7.931
0.46605 | 0 | 0.35862 | 700 | 40 | 0 | 6.605
0.46698 | 0 | 0.27003 | 700 | 40 | 0 | 6.698
0.49083 | 0 | 0.23172 | 700 | 40 | 0 | 9.083
0.51989 | 0.0001 | 0.19717 | 695.9048 | 40 | 0.007 | 7.8868
0.512 | 0.1512 | 0.17302 | 700 | 40 | 10.584 | 4.7112
0.51796 | 0.6665 | 0.12821 | 700 | 40 | 11.796 | 0
0.52444 | 0.8168 | 0.08132 | 700 | 40 | 12.444 | 0
0.53624 | 0.8233 | 0.10531 | 700 | 40 | 13.624 | 0
0.54591 | 0.8218 | 0.09054 | 700 | 40 | 14.591 | 0
0.55846 | 0.8158 | 0.09824 | 700 | 40 | 15.846 | 0
0.57407 | 0.8303 | 0.12741 | 700 | 40 | 17.407 | 0
0.59043 | 0.844 | 0.14701 | 700 | 40 | 19.043 | 0
0.60384 | 0.8286 | 0.18049 | 700 | 40 | 20.384 | 0
0.60699 | 0.6661 | 0.18264 | 700 | 40 | 20.699 | 0
0.59451 | 0.1984 | 0.17007 | 700 | 40 | 13.888 | 5.563
0.57845 | 0.0005 | 0.10838 | 686.5252 | 40 | 0.035 | 4.3352
0.56801 | 0 | 0.16468 | 676.3114 | 40 | 0 | 6.5872
0.54106 | 0 | 0.20455 | 670.3874 | 40 | 0 | 8.182
0.50472 | 0 | 0.21832 | 668.6482 | 40 | 0 | 8.7328
0.46279 | 0 | 0.24306 | 672.0916 | 40 | 0 | 9.7224
0.42805 | 0 | 0.25654 | 679.5482 | 40 | 0 | 10.2616
0.40588 | 0 | 0.27051 | 689.7806 | 40 | 0 | 10.8204
0.39228 | 0 | 0.25387 | 700 | 40 | 9.4474 | 0
0.3859 | 0 | 0.24972 | 700 | 38.59 | 0 | 0
0.38636 | 0 | 0.23803 | 700 | 38.636 | 0 | 0
0.39931 | 0 | 0.2166 | 700 | 39.931 | 0 | 0
0.43194 | 0 | 0.20375 | 700 | 40 | 0 | 3.194
0.47661 | 0.0007 | 0.17817 | 699.5148 | 40 | 0.049 | 7.1268
0.47527 | 0.1589 | 0.151 | 700 | 40 | 8.0122 | 0
0.47633 | 0.6823 | 0.1352 | 700 | 40 | 7.633 | 0
0.48434 | 0.8287 | 0.10088 | 700 | 40 | 8.434 | 0
0.49506 | 0.8396 | 0.15611 | 700 | 40 | 9.506 | 0
0.50378 | 0.8336 | 0.17111 | 700 | 40 | 10.378 | 0
0.5151 | 0.7918 | 0.16696 | 700 | 40 | 11.51 | 0
0.52725 | 0.7937 | 0.16065 | 700 | 40 | 12.725 | 0
0.53997 | 0.801 | 0.16672 | 700 | 40 | 13.997 | 0
0.55247 | 0.816 | 0.18583 | 700 | 40 | 15.247 | 0
0.55954 | 0.6494 | 0.19964 | 700 | 40 | 15.954 | 0
0.55348 | 0.1875 | 0.20599 | 700 | 40 | 13.125 | 2.223
0.54899 | 0.0003 | 0.21297 | 693.6408 | 40 | 0.021 | 8.5188
0.54422 | 0 | 0.32901 | 692.3792 | 40 | 0 | 13.1604
0.52589 | 0 | 0.4494 | 697.7662 | 40 | 0 | 17.976
0.49333 | 0 | 0.49868 | 700 | 40 | 0 | 11.5668
0.45351 | 0 | 0.49848 | 700 | 40 | 0 | 5.351
0.42272 | 0 | 0.48344 | 700 | 40 | 0 | 2.272
0.40016 | 0 | 0.50443 | 700 | 40 | 0 | 0.016
0.39126 | 0 | 0.49397 | 700 | 39.126 | 0 | 0
0.3849 | 0 | 0.49186 | 700 | 38.49 | 0 | 0
0.38575 | 0 | 0.50299 | 700 | 38.575 | 0 | 0
0.40206 | 0 | 0.5241 | 700 | 40 | 0 | 0.206
0.43659 | 0 | 0.55363 | 700 | 40 | 0 | 3.659
0.47986 | 0.0006 | 0.59717 | 700 | 40 | 0.042 | 7.944
0.47748 | 0.1081 | 0.58204 | 700 | 40 | 7.567 | 0.181
0.48227 | 0.4829 | 0.54425 | 700 | 40 | 8.227 | 0
0.49381 | 0.6188 | 0.54976 | 700 | 40 | 9.381 | 0
0.51036 | 0.69 | 0.57534 | 700 | 40 | 11.036 | 0
0.52418 | 0.7905 | 0.56552 | 700 | 40 | 12.418 | 0
0.53958 | 0.791 | 0.54872 | 700 | 40 | 13.958 | 0
0.55584 | 0.7983 | 0.49541 | 700 | 40 | 15.584 | 0
0.5695 | 0.8075 | 0.46468 | 700 | 40 | 16.95 | 0
0.58836 | 0.7753 | 0.43224 | 700 | 40 | 18.836 | 0
0.59646 | 0.6021 | 0.40152 | 700 | 40 | 19.646 | 0
0.59023 | 0.1665 | 0.40315 | 700 | 40 | 11.655 | 7.368
0.58454 | 0.0002 | 0.37402 | 696.5208 | 40 | 0.014 | 14.9608
0.58236 | 0 | 0.45842 | 696.6216 | 40 | 0 | 18.3368
0.56491 | 0 | 0.55192 | 700 | 40 | 0 | 19.8694
0.53414 | 0 | 0.57398 | 700 | 40 | 0 | 13.414
0.49315 | 0 | 0.53476 | 700 | 40 | 0 | 9.315
0.45871 | 0 | 0.50016 | 700 | 40 | 0 | 5.871
0.43466 | 0 | 0.50347 | 700 | 40 | 0 | 3.466
0.41911 | 0 | 0.48735 | 700 | 40 | 0 | 1.911
0.41117 | 0 | 0.47662 | 700 | 40 | 0 | 1.117
0.40957 | 0 | 0.46233 | 700 | 40 | 0 | 0.957
0.42072 | 0 | 0.44002 | 700 | 40 | 0 | 2.072
0.45383 | 0 | 0.45682 | 700 | 40 | 0 | 5.383
0.4939 | 0.0003 | 0.47961 | 700 | 40 | 0.021 | 9.369
0.49647 | 0.0628 | 0.51656 | 700 | 40 | 4.396 | 5.251
0.50582 | 0.1677 | 0.50064 | 700 | 40 | 10.582 | 0
0.52444 | 0.2473 | 0.54733 | 700 | 40 | 12.444 | 0
0.5439 | 0.325 | 0.57314 | 700 | 40 | 14.39 | 0
0.56498 | 0.234 | 0.62546 | 700 | 40 | 16.38 | 0.118
0.58118 | 0.1515 | 0.62187 | 700 | 40 | 10.605 | 7.513
0.59477 | 0.1452 | 0.60319 | 700 | 40 | 10.164 | 9.313
0.59832 | 0.1381 | 0.56313 | 700 | 40 | 9.667 | 10.165
0.60327 | 0.1371 | 0.56189 | 700 | 40 | 9.597 | 10.73
0.60412 | 0.0695 | 0.62267 | 700 | 40 | 4.865 | 15.547
0.59662 | 0.0191 | 0.65854 | 700 | 40 | 1.337 | 18.325
0.59302 | 0.0001 | 0.67179 | 700 | 40 | 0.007 | 19.295
0.58587 | 0 | 0.6575 | 700 | 40 | 0 | 18.587
0.56093 | 0 | 0.65814 | 700 | 40 | 0 | 16.093
0.52842 | 0 | 0.6328 | 700 | 40 | 0 | 12.842
0.48734 | 0 | 0.59457 | 700 | 40 | 0 | 8.734
0.45468 | 0 | 0.58328 | 700 | 40 | 0 | 5.468
0.43392 | 0 | 0.60487 | 700 | 40 | 0 | 3.392
0.41707 | 0 | 0.59717 | 700 | 40 | 0 | 1.707
0.40826 | 0 | 0.57917 | 700 | 40 | 0 | 0.826
0.40575 | 0 | 0.5593 | 700 | 40 | 0 | 0.575
0.4132 | 0 | 0.57279 | 700 | 40 | 0 | 1.32
0.4507 | 0 | 0.62039 | 700 | 40 | 0 | 5.07
0.49546 | 0 | 0.68156 | 700 | 40 | 0 | 9.546
0.50932 | 0.1142 | 0.68404 | 700 | 40 | 7.994 | 2.938
0.51393 | 0.5311 | 0.66341 | 700 | 40 | 11.393 | 0
0.51985 | 0.6958 | 0.65471 | 700 | 40 | 11.985 | 0
0.52005 | 0.7142 | 0.65148 | 700 | 40 | 12.005 | 0
0.51641 | 0.7119 | 0.64529 | 700 | 40 | 11.641 | 0
0.51208 | 0.7036 | 0.63879 | 700 | 40 | 11.208 | 0
0.5078 | 0.7197 | 0.63089 | 700 | 40 | 10.78 | 0
0.50502 | 0.7023 | 0.63468 | 700 | 40 | 10.502 | 0
0.504 | 0.6978 | 0.61061 | 700 | 40 | 10.4 | 0
0.504 | 0.5738 | 0.58775 | 700 | 40 | 10.4 | 0
0.50736 | 0.1707 | 0.53472 | 700 | 40 | 10.736 | 0
0.51553 | 0.0035 | 0.39796 | 700 | 40 | 0.245 | 11.308
0.51467 | 0 | 0.36676 | 700 | 40 | 0 | 11.467
0.5062 | 0 | 0.36692 | 700 | 40 | 0 | 10.62
0.49263 | 0 | 0.3324 | 700 | 40 | 0 | 9.263
0.46975 | 0 | 0.30056 | 700 | 40 | 0 | 6.975
0.44751 | 0 | 0.24186 | 700 | 40 | 0 | 4.751
0.43018 | 0 | 0.22897 | 700 | 40 | 0 | 3.018
0.42092 | 0 | 0.23248 | 700 | 40 | 0 | 2.092
0.41509 | 0 | 0.24661 | 700 | 40 | 0 | 1.509
0.41389 | 0 | 0.27518 | 700 | 40 | 0 | 1.389
0.4213 | 0 | 0.30311 | 700 | 40 | 0 | 2.13
0.43544 | 0 | 0.29561 | 700 | 40 | 0 | 3.544
0.45665 | 0.0003 | 0.28029 | 700 | 40 | 0.021 | 5.644
0.47705 | 0.1478 | 0.27123 | 700 | 40 | 7.705 | 0
0.48752 | 0.6777 | 0.21149 | 700 | 40 | 8.752 | 0
0.4898 | 0.8455 | 0.13444 | 700 | 40 | 8.98 | 0
0.48006 | 0.858 | 0.12721 | 700 | 40 | 8.006 | 0
0.46837 | 0.8482 | 0.14848 | 700 | 40 | 6.837 | 0
0.46218 | 0.8397 | 0.17382 | 700 | 40 | 6.218 | 0
0.45578 | 0.8416 | 0.22566 | 700 | 40 | 5.578 | 0
0.45374 | 0.8407 | 0.24777 | 700 | 40 | 5.374 | 0
0.45582 | 0.7632 | 0.26425 | 700 | 40 | 5.582 | 0
0.45964 | 0.5872 | 0.28376 | 700 | 40 | 5.964 | 0
0.45955 | 0.1664 | 0.27406 | 700 | 40 | 5.955 | 0
0.47131 | 0.0001 | 0.31053 | 700 | 40 | 0.007 | 7.124
0.47181 | 0 | 0.46141 | 700 | 40 | 0 | 7.181
0.46801 | 0 | 0.5241 | 700 | 40 | 0 | 6.801
0.45401 | 0 | 0.52522 | 700 | 40 | 0 | 5.401
0.43812 | 0 | 0.51353 | 700 | 40 | 0 | 3.812
0.41727 | 0 | 0.51006 | 700 | 40 | 0 | 1.727
0.40425 | 0 | 0.53033 | 700 | 40 | 0 | 0.425
0.39659 | 0 | 0.54246 | 700 | 39.659 | 0 | 0
0.39153 | 0 | 0.5405 | 700 | 39.153 | 0 | 0
0.39236 | 0 | 0.53966 | 700 | 39.236 | 0 | 0
0.39519 | 0 | 0.52713 | 700 | 39.519 | 0 | 0
0.40611 | 0 | 0.53033 | 700 | 40 | 0 | 0.611
0.42495 | 0.0006 | 0.52526 | 700 | 40 | 0.042 | 2.453
0.44027 | 0.1196 | 0.55196 | 700 | 40 | 4.027 | 0
0.45458 | 0.6468 | 0.54785 | 700 | 40 | 5.458 | 0
0.45714 | 0.8222 | 0.41041 | 700 | 40 | 5.714 | 0
0.45858 | 0.8431 | 0.38807 | 700 | 40 | 5.858 | 0
0.46059 | 0.827 | 0.35451 | 700 | 40 | 6.059 | 0
0.46275 | 0.825 | 0.31592 | 700 | 40 | 6.275 | 0
0.46808 | 0.8314 | 0.25786 | 700 | 40 | 6.808 | 0
0.47661 | 0.8358 | 0.23851 | 700 | 40 | 7.661 | 0
0.48872 | 0.7956 | 0.26113 | 700 | 40 | 8.872 | 0
0.49695 | 0.6019 | 0.31245 | 700 | 40 | 9.695 | 0
0.50201 | 0.1481 | 0.37263 | 700 | 40 | 10.201 | 0
0.51293 | 0.0001 | 0.43982 | 700 | 40 | 0.007 | 11.286
0.51564 | 0 | 0.51652 | 700 | 40 | 0 | 11.564
0.50478 | 0 | 0.5415 | 700 | 40 | 0 | 10.478
0.4809 | 0 | 0.56772 | 700 | 40 | 0 | 8.09
0.45076 | 0 | 0.56305 | 700 | 40 | 0 | 5.076
0.4178 | 0 | 0.54134 | 700 | 40 | 0 | 1.78
0.3993 | 0 | 0.49816 | 700 | 39.93 | 0 | 0
0.38828 | 0 | 0.47662 | 700 | 38.828 | 0 | 0
0.38543 | 0 | 0.48695 | 700 | 38.543 | 0 | 0
0.38922 | 0 | 0.48919 | 700 | 38.922 | 0 | 0
0.40261 | 0 | 0.46341 | 700 | 40 | 0 | 0.261
0.44055 | 0 | 0.42869 | 700 | 40 | 0 | 4.055
0.48436 | 0.0002 | 0.39872 | 700 | 40 | 0.014 | 8.422
0.48713 | 0.0554 | 0.34585 | 700 | 40 | 3.878 | 4.835
0.4902 | 0.1968 | 0.27522 | 700 | 40 | 9.02 | 0
0.50194 | 0.3098 | 0.20706 | 700 | 40 | 10.194 | 0
0.51291 | 0.5022 | 0.168 | 700 | 40 | 11.291 | 0
0.51793 | 0.6323 | 0.12698 | 700 | 40 | 11.793 | 0
0.52733 | 0.6836 | 0.11273 | 700 | 40 | 12.733 | 0
0.53595 | 0.6851 | 0.12518 | 700 | 40 | 13.595 | 0
0.54053 | 0.7257 | 0.12358 | 700 | 40 | 14.053 | 0
0.54661 | 0.7083 | 0.12702 | 700 | 40 | 14.661 | 0
0.5506 | 0.5466 | 0.15315 | 700 | 40 | 15.06 | 0
0.55249 | 0.1318 | 0.20527 | 700 | 40 | 9.226 | 6.023
0.56233 | 0 | 0.2506 | 693.791 | 40 | 0 | 10.024
0.55867 | 0 | 0.33448 | 691.3032 | 40 | 0 | 13.3792
0.54701 | 0 | 0.36512 | 691.207 | 40 | 0 | 14.6048
0.51843 | 0 | 0.36692 | 694.0408 | 40 | 0 | 14.6768
0.48219 | 0 | 0.35898 | 700 | 40 | 0 | 14.1782
0.44946 | 0 | 0.32654 | 700 | 40 | 0 | 4.946
0.43234 | 0 | 0.32306 | 700 | 40 | 0 | 3.234
0.42185 | 0 | 0.30096 | 700 | 40 | 0 | 2.185
0.4186 | 0 | 0.30443 | 700 | 40 | 0 | 1.86
0.42001 | 0 | 0.27422 | 700 | 40 | 0 | 2.001
0.43643 | 0 | 0.22211 | 700 | 40 | 0 | 3.643
0.47424 | 0 | 0.19122 | 700 | 40 | 0 | 7.424
0.51723 | 0.0001 | 0.17203 | 695.1652 | 40 | 0.007 | 6.8812
0.52271 | 0.0049 | 0.13328 | 688.5684 | 40 | 0.343 | 5.3312
0.52804 | 0.0498 | 0.1152 | 683.8584 | 40 | 3.486 | 4.608
0.53888 | 0.1195 | 0.1156 | 682.9594 | 40 | 8.365 | 4.624
0.54614 | 0.2076 | 0.10646 | 687.1358 | 40 | 14.532 | 4.2584
0.54954 | 0.306 | 0.11069 | 698.0294 | 40 | 25.8476 | 0
0.55337 | 0.4007 | 0.13879 | 700 | 40 | 17.3076 | 0
0.55304 | 0.4185 | 0.15196 | 700 | 40 | 15.304 | 0
0.55221 | 0.4412 | 0.18196 | 700 | 40 | 15.221 | 0
0.55433 | 0.3802 | 0.20551 | 700 | 40 | 15.433 | 0
0.56064 | 0.2588 | 0.24258 | 700 | 40 | 16.064 | 0
0.56703 | 0.0762 | 0.27494 | 699.6286 | 40 | 5.334 | 10.9976
0.58046 | 0 | 0.30215 | 693.6686 | 40 | 0 | 12.086
0.57807 | 0 | 0.30419 | 688.0292 | 40 | 0 | 12.1676
0.56576 | 0 | 0.31117 | 683.9 | 40 | 0 | 12.4468
0.53745 | 0 | 0.30822 | 682.4838 | 40 | 0 | 12.3288
0.50765 | 0 | 0.31185 | 684.1928 | 40 | 0 | 12.474
0.47595 | 0 | 0.3257 | 689.6258 | 40 | 0 | 13.028
0.4614 | 0 | 0.33962 | 697.0706 | 40 | 0 | 13.5848
0.45261 | 0 | 0.32674 | 700 | 40 | 0 | 8.1904
0.44581 | 0 | 0.31748 | 700 | 40 | 0 | 4.581
0.45037 | 0 | 0.31995 | 700 | 40 | 0 | 5.037
0.46569 | 0 | 0.31844 | 700 | 40 | 0 | 6.569
0.50607 | 0 | 0.28743 | 700 | 40 | 0 | 10.607
0.54385 | 0 | 0.26421 | 696.1834 | 40 | 0 | 10.5684
0.55375 | 0.0088 | 0.25247 | 691.5232 | 40 | 0.616 | 10.0988
0.5585 | 0.0704 | 0.23699 | 690.0808 | 40 | 4.928 | 9.4796
0.56515 | 0.1155 | 0.27043 | 692.468 | 40 | 8.085 | 10.8172
0.5701 | 0.1986 | 0.32602 | 700 | 40 | 13.902 | 10.64
0.56885 | 0.238 | 0.37171 | 700 | 40 | 16.66 | 0.225
0.57075 | 0.2502 | 0.43595 | 700 | 40 | 17.075 | 0
0.56899 | 0.2328 | 0.52083 | 700 | 40 | 16.296 | 0.603
0.56864 | 0.2018 | 0.57227 | 700 | 40 | 14.126 | 2.738
0.5741 | 0.2054 | 0.62829 | 700 | 40 | 14.378 | 3.032
0.58403 | 0.202 | 0.65267 | 700 | 40 | 14.14 | 4.263
0.59658 | 0.0669 | 0.66457 | 700 | 40 | 4.683 | 14.975
0.614 | 0 | 0.66536 | 700 | 40 | 0 | 21.4
0.61016 | 0 | 0.62562 | 700 | 40 | 0 | 21.016
0.60143 | 0 | 0.60511 | 700 | 40 | 0 | 20.143
0.57976 | 0 | 0.59114 | 700 | 40 | 0 | 17.976
0.5516 | 0 | 0.58986 | 700 | 40 | 0 | 15.16
0.52672 | 0 | 0.52394 | 700 | 40 | 0 | 12.672
0.51289 | 0 | 0.48783 | 700 | 40 | 0 | 11.289
0.5147 | 0 | 0.50882 | 700 | 40 | 0 | 11.47
0.51711 | 0 | 0.50219 | 700 | 40 | 0 | 11.711
0.5248 | 0 | 0.50052 | 700 | 40 | 0 | 12.48
0.54979 | 0 | 0.45834 | 700 | 40 | 0 | 14.979
0.60015 | 0 | 0.42011 | 696.7894 | 40 | 0 | 16.8044
0.65742 | 0.0003 | 0.38567 | 686.4952 | 40 | 0.021 | 15.4268
0.65679 | 0.1238 | 0.33775 | 682.9922 | 40 | 8.666 | 13.51
0.64209 | 0.6713 | 0.29314 | 700 | 40 | 41.2168 | -1.1369e-13
0.62401 | 0.884 | 0.21413 | 700 | 40 | 22.401 | 0
0.60768 | 0.8918 | 0.17618 | 700 | 40 | 20.768 | 0
0.58349 | 0.8761 | 0.15367 | 700 | 40 | 18.349 | 0
0.56004 | 0.8671 | 0.13551 | 700 | 40 | 16.004 | 0
0.54118 | 0.8728 | 0.12191 | 700 | 40 | 14.118 | 0
0.5232 | 0.8847 | 0.11002 | 700 | 40 | 12.32 | 0
0.51412 | 0.8617 | 0.10806 | 700 | 40 | 11.412 | 0
0.51285 | 0.6428 | 0.12099 | 700 | 40 | 11.285 | 0
0.51955 | 0.1438 | 0.12239 | 700 | 40 | 10.066 | 1.889
0.54551 | 0 | 0.15403 | 691.6102 | 40 | 0 | 6.1612
0.55858 | 0 | 0.22203 | 684.6334 | 40 | 0 | 8.8812
0.5761 | 0 | 0.27087 | 677.8582 | 40 | 0 | 10.8348
0.573 | 0 | 0.34773 | 674.4674 | 40 | 0 | 13.9092
0.54975 | 0 | 0.40467 | 675.6792 | 40 | 0 | 16.1868
0.53458 | 0 | 0.45746 | 680.5196 | 40 | 0 | 18.2984
0.52477 | 0 | 0.51656 | 688.705 | 40 | 0 | 20.6624
0.52764 | 0 | 0.55938 | 698.3162 | 40 | 0 | 22.3752
0.53305 | 0 | 0.57099 | 700 | 40 | 0 | 14.9888
0.54379 | 0 | 0.58372 | 700 | 40 | 0 | 14.379
0.56578 | 0 | 0.57267 | 700 | 40 | 0 | 16.578
0.61343 | 0 | 0.58883 | 700 | 40 | 0 | 21.343
0.66017 | 0.0003 | 0.59102 | 697.6448 | 40 | 0.021 | 23.6408
0.66287 | 0.1225 | 0.59074 | 700 | 40 | 8.575 | 20.0672
0.6366 | 0.6589 | 0.55507 | 700 | 40 | 23.66 | 0
0.60673 | 0.856 | 0.44346 | 700 | 40 | 20.673 | 0
0.57631 | 0.8285 | 0.41792 | 700 | 40 | 17.631 | 0
0.54997 | 0.8347 | 0.42314 | 700 | 40 | 14.997 | 0
0.52799 | 0.8375 | 0.38248 | 700 | 40 | 12.799 | 0
0.5104 | 0.8428 | 0.33184 | 700 | 40 | 11.04 | 0
0.49714 | 0.8503 | 0.26205 | 700 | 40 | 9.714 | 0
0.48858 | 0.8246 | 0.2065 | 700 | 40 | 8.858 | 0
0.48724 | 0.623 | 0.19553 | 700 | 40 | 8.724 | 0
0.49248 | 0.127 | 0.20611 | 700 | 40 | 8.89 | 0.358
0.51474 | 0 | 0.28603 | 699.9672 | 40 | 0 | 11.4412
0.51849 | 0 | 0.38368 | 700 | 40 | 0 | 11.8818
0.51942 | 0 | 0.49362 | 700 | 40 | 0 | 11.942
0.50642 | 0 | 0.52051 | 700 | 40 | 0 | 10.642
0.49119 | 0 | 0.50882 | 700 | 40 | 0 | 9.119
0.4735 | 0 | 0.49042 | 700 | 40 | 0 | 7.35
0.46607 | 0 | 0.50674 | 700 | 40 | 0 | 6.607
0.46263 | 0 | 0.51552 | 700 | 40 | 0 | 6.263
0.46275 | 0 | 0.49086 | 700 | 40 | 0 | 6.275
0.46809 | 0 | 0.48148 | 700 | 40 | 0 | 6.809
0.47814 | 0 | 0.4516 | 700 | 40 | 0 | 7.814
0.49793 | 0 | 0.41417 | 700 | 40 | 0 | 9.793
0.52476 | 0.0003 | 0.35826 | 700 | 40 | 0.021 | 12.455
0.54591 | 0.1125 | 0.32127 | 700 | 40 | 7.875 | 6.716
0.54789 | 0.6625 | 0.2259 | 700 | 40 | 14.789 | 0
0.53333 | 0.926 | 0.14098 | 700 | 40 | 13.333 | 0
0.51467 | 0.9388 | 0.1765 | 700 | 40 | 11.467 | 0
0.49555 | 0.9222 | 0.12749 | 700 | 40 | 9.555 | 0
0.47889 | 0.9082 | 0.09026 | 700 | 40 | 7.889 | 0
0.46624 | 0.9113 | 0.09134 | 700 | 40 | 6.624 | 0
0.45918 | 0.9119 | 0.10104 | 700 | 40 | 5.918 | 0
0.4558 | 0.8811 | 0.09924 | 700 | 40 | 5.58 | 0
0.45727 | 0.6367 | 0.11073 | 700 | 40 | 5.727 | 0
0.46181 | 0.1119 | 0.11045 | 700 | 40 | 6.181 | 0
0.48098 | 0 | 0.12147 | 696.7608 | 40 | 0 | 4.8588
0.48565 | 0 | 0.17777 | 695.3066 | 40 | 0 | 7.1108
0.48265 | 0 | 0.21632 | 695.6944 | 40 | 0 | 8.6528
0.47618 | 0 | 0.25279 | 698.188 | 40 | 0 | 10.1116
0.46416 | 0 | 0.29661 | 700 | 40 | 0 | 8.228
0.45154 | 0 | 0.38492 | 700 | 40 | 0 | 5.154
0.44547 | 0 | 0.49417 | 700 | 40 | 0 | 4.547
0.44626 | 0 | 0.45463 | 700 | 40 | 0 | 4.626
0.44671 | 0 | 0.51177 | 700 | 40 | 0 | 4.671
0.44918 | 0 | 0.51433 | 700 | 40 | 0 | 4.918
0.45517 | 0 | 0.53579 | 700 | 40 | 0 | 5.517
0.46809 | 0 | 0.54693 | 700 | 40 | 0 | 6.809
0.48494 | 0.0003 | 0.56413 | 700 | 40 | 0.021 | 8.473
0.50504 | 0.0614 | 0.58755 | 700 | 40 | 4.298 | 6.206
0.5162 | 0.4561 | 0.57729 | 700 | 40 | 11.62 | 0
0.51019 | 0.747 | 0.50196 | 700 | 40 | 11.019 | 0
0.4963 | 0.7929 | 0.52666 | 700 | 40 | 9.63 | 0
0.47994 | 0.811 | 0.4915 | 700 | 40 | 7.994 | 0
0.47018 | 0.8352 | 0.45479 | 700 | 40 | 7.018 | 0
0.46204 | 0.8497 | 0.43057 | 700 | 40 | 6.204 | 0
0.46058 | 0.825 | 0.40048 | 700 | 40 | 6.058 | 0
0.4611 | 0.6702 | 0.38492 | 700 | 40 | 6.11 | 0
0.46168 | 0.3644 | 0.39385 | 700 | 40 | 6.168 | 0
0.47049 | 0.0519 | 0.35874 | 700 | 40 | 3.633 | 3.416
0.49946 | 0 | 0.3982 | 700 | 40 | 0 | 9.946
0.50654 | 0 | 0.52167 | 700 | 40 | 0 | 10.654
0.50183 | 0 | 0.58827 | 700 | 40 | 0 | 10.183
0.48879 | 0 | 0.61808 | 700 | 40 | 0 | 8.879
0.46544 | 0 | 0.61604 | 700 | 40 | 0 | 6.544
0.4374 | 0 | 0.59086 | 700 | 40 | 0 | 3.74
0.41756 | 0 | 0.57857 | 700 | 40 | 0 | 1.756
0.40708 | 0 | 0.56903 | 700 | 40 | 0 | 0.708
0.40013 | 0 | 0.55706 | 700 | 40 | 0 | 0.013
0.39938 | 0 | 0.5498 | 700 | 39.938 | 0 | 0
0.40706 | 0 | 0.54641 | 700 | 40 | 0 | 0.706
0.4298 | 0 | 0.52103 | 700 | 40 | 0 | 2.98
0.47055 | 0.0001 | 0.50267 | 700 | 40 | 0.007 | 7.048
0.5083 | 0.0842 | 0.46776 | 700 | 40 | 5.894 | 4.936
0.50422 | 0.4769 | 0.35662 | 700 | 40 | 10.422 | 0
0.50025 | 0.7731 | 0.21772 | 700 | 40 | 10.025 | 0
0.50399 | 0.8761 | 0.17414 | 700 | 40 | 10.399 | 0
0.50773 | 0.8308 | 0.13164 | 700 | 40 | 10.773 | 0
0.51384 | 0.824 | 0.11652 | 700 | 40 | 11.384 | 0
0.51932 | 0.8297 | 0.10986 | 700 | 40 | 11.932 | 0
0.52619 | 0.8091 | 0.11229 | 700 | 40 | 12.619 | 0
0.52853 | 0.7342 | 0.12223 | 700 | 40 | 12.853 | 0
0.53725 | 0.5129 | 0.12885 | 700 | 40 | 13.725 | 0
0.53729 | 0.0801 | 0.13895 | 697.436 | 40 | 5.607 | 5.558
0.5537 | 0 | 0.2069 | 690.342 | 40 | 0 | 8.276
0.5541 | 0 | 0.38504 | 690.3336 | 40 | 0 | 15.4016
0.54028 | 0 | 0.45547 | 694.5244 | 40 | 0 | 18.2188
0.52511 | 0 | 0.49952 | 700 | 40 | 0 | 17.9866
0.49266 | 0 | 0.50658 | 700 | 40 | 0 | 9.266
0.45823 | 0 | 0.4927 | 700 | 40 | 0 | 5.823
0.42783 | 0 | 0.43661 | 700 | 40 | 0 | 2.783
0.4103 | 0 | 0.36797 | 700 | 40 | 0 | 1.03
0.40069 | 0 | 0.33983 | 700 | 40 | 0 | 0.069
0.39792 | 0 | 0.33633 | 700 | 39.792 | 0 | 0
0.40012 | 0 | 0.32874 | 700 | 40 | 0 | 0.012
0.41497 | 0 | 0.30068 | 700 | 40 | 0 | 1.497
0.45211 | 0 | 0.27099 | 700 | 40 | 0 | 5.211
0.48978 | 0.0647 | 0.25254 | 700 | 40 | 4.529 | 4.449
0.49223 | 0.4912 | 0.1942 | 700 | 40 | 9.223 | 0
0.50684 | 0.7351 | 0.10811 | 700 | 40 | 10.684 | 0
0.52382 | 0.7586 | 0.07921 | 700 | 40 | 12.382 | 0
0.53605 | 0.7495 | 0.0525 | 700 | 40 | 13.605 | 0
0.545 | 0.7494 | 0.04734 | 700 | 40 | 14.5 | 0
0.55096 | 0.7636 | 0.04861 | 700 | 40 | 15.096 | 0
0.56046 | 0.7412 | 0.05855 | 700 | 40 | 16.046 | 0
0.56381 | 0.7443 | 0.07043 | 700 | 40 | 16.381 | 0
0.56584 | 0.4829 | 0.08275 | 700 | 40 | 16.584 | 0
0.56235 | 0.0768 | 0.11292 | 693.6578 | 40 | 5.376 | 4.5168
0.57283 | 0 | 0.15068 | 682.402 | 40 | 0 | 6.0272
0.57328 | 0 | 0.21149 | 673.5336 | 40 | 0 | 8.4596
0.56034 | 0 | 0.21641 | 666.156 | 40 | 0 | 8.6564
0.54087 | 0 | 0.23359 | 661.4126 | 40 | 0 | 9.3436
0.50918 | 0 | 0.26002 | 660.8954 | 40 | 0 | 10.4008
0.47218 | 0 | 0.28975 | 665.2674 | 40 | 0 | 11.59
0.44088 | 0 | 0.34328 | 674.9106 | 40 | 0 | 13.7312
0.42382 | 0 | 0.34213 | 686.2138 | 40 | 0 | 13.6852
0.41153 | 0 | 0.37607 | 700 | 40 | 0 | 14.9392
0.40818 | 0 | 0.38362 | 700 | 40 | 0 | 0.818
0.40965 | 0 | 0.36848 | 700 | 40 | 0 | 0.965
0.42336 | 0 | 0.33021 | 700 | 40 | 0 | 2.336
0.45937 | 0.0001 | 0.30874 | 700 | 40 | 0.007 | 5.93
0.49294 | 0.0181 | 0.24766 | 700 | 40 | 1.267 | 8.027
0.4992 | 0.1327 | 0.25481 | 700 | 40 | 9.289 | 0.631
0.51166 | 0.2316 | 0.26832 | 700 | 40 | 11.166 | 0
0.52668 | 0.3299 | 0.34555 | 700 | 40 | 12.668 | 0
0.54323 | 0.3497 | 0.38752 | 700 | 40 | 14.323 | 0
0.55441 | 0.4121 | 0.38935 | 700 | 40 | 15.441 | 0
0.56537 | 0.3891 | 0.37357 | 700 | 40 | 16.537 | 0
0.57474 | 0.3244 | 0.35195 | 700 | 40 | 17.474 | 0
0.57664 | 0.2705 | 0.35501 | 700 | 40 | 17.664 | 0
0.57328 | 0.1776 | 0.32893 | 700 | 40 | 12.432 | 4.896
0.56747 | 0.042 | 0.33156 | 699.4554 | 40 | 2.94 | 13.2624
0.58055 | 0 | 0.32528 | 694.4116 | 40 | 0 | 13.0112
0.57591 | 0 | 0.33517 | 690.2274 | 40 | 0 | 13.4068
0.55025 | 0 | 0.24889 | 685.158 | 40 | 0 | 9.9556
0.5373 | 0 | 0.25934 | 681.8016 | 40 | 0 | 10.3736
0.50812 | 0 | 0.2996 | 682.9736 | 40 | 0 | 11.984
0.47056 | 0 | 0.2907 | 687.5456 | 40 | 0 | 11.628
0.43826 | 0 | 0.29849 | 695.6592 | 40 | 0 | 11.9396
0.41798 | 0 | 0.2777 | 700 | 40 | 0 | 6.1388
0.40673 | 0 | 0.28605 | 700 | 40 | 0 | 0.673
0.40406 | 0 | 0.2996 | 700 | 40 | 0 | 0.406
0.40672 | 0 | 0.35513 | 700 | 40 | 0 | 0.672
0.42197 | 0 | 0.46936 | 700 | 40 | 0 | 2.197
0.45784 | 0 | 0.52929 | 700 | 40 | 0 | 5.784
0.49927 | 0.0019 | 0.5527 | 700 | 40 | 0.133 | 9.794
0.50417 | 0.0109 | 0.56085 | 700 | 40 | 0.763 | 9.654
0.51721 | 0.0349 | 0.57198 | 700 | 40 | 2.443 | 9.278
0.53321 | 0.0728 | 0.56959 | 700 | 40 | 5.096 | 8.225
0.54461 | 0.1024 | 0.55207 | 700 | 40 | 7.168 | 7.293
0.55129 | 0.1141 | 0.54825 | 700 | 40 | 7.987 | 7.142
0.55406 | 0.1101 | 0.51451 | 700 | 40 | 7.707 | 7.699
0.55745 | 0.0761 | 0.49662 | 700 | 40 | 5.327 | 10.418
0.55394 | 0.0489 | 0.46248 | 700 | 40 | 3.423 | 11.971
0.56044 | 0.0244 | 0.43998 | 700 | 40 | 1.708 | 14.336
0.56951 | 0.0022 | 0.43831 | 700 | 40 | 0.154 | 16.797
0.58914 | 0 | 0.3837 | 696.434 | 40 | 0 | 15.348
0.58776 | 0 | 0.3816 | 692.922 | 40 | 0 | 15.264
0.57664 | 0 | 0.3752 | 690.266 | 40 | 0 | 15.008
0.56303 | 0 | 0.34857 | 687.9058 | 40 | 0 | 13.9428
0.53599 | 0 | 0.32774 | 687.4164 | 40 | 0 | 13.1096
0.50502 | 0 | 0.29523 | 688.7236 | 40 | 0 | 11.8092
0.47956 | 0 | 0.26021 | 691.176 | 40 | 0 | 10.4084
0.4682 | 0 | 0.23386 | 693.7104 | 40 | 0 | 9.3544
0.45989 | 0 | 0.2188 | 696.4734 | 40 | 0 | 8.752
0.4591 | 0 | 0.19205 | 698.2454 | 40 | 0 | 7.682
0.46329 | 0 | 0.18152 | 699.1772 | 40 | 0 | 7.2608
0.48207 | 0 | 0.17961 | 698.1546 | 40 | 0 | 7.1844
0.52642 | 0 | 0.17015 | 692.3186 | 40 | 0 | 6.806
0.56993 | 0.0055 | 0.14785 | 681.6246 | 40 | 0.385 | 5.914
0.57194 | 0.0487 | 0.13223 | 673.1288 | 40 | 3.409 | 5.2892
0.57914 | 0.1125 | 0.11033 | 667.503 | 40 | 7.875 | 4.4132
0.57493 | 0.2148 | 0.10827 | 669.3768 | 40 | 15.036 | 4.3308
0.56459 | 0.3109 | 0.10707 | 678.9636 | 40 | 26.0458 | 0
0.55213 | 0.3673 | 0.13247 | 694.7604 | 40 | 31.0098 | 0
0.54504 | 0.3748 | 0.12929 | 700 | 40 | 19.7436 | 0
0.5387 | 0.3479 | 0.12619 | 700 | 40 | 13.87 | 0
0.52978 | 0.2707 | 0.11208 | 700 | 40 | 12.978 | 0
0.52735 | 0.1368 | 0.09944 | 700 | 40 | 9.576 | 3.159
0.53758 | 0.0197 | 0.08828 | 691.1522 | 40 | 1.379 | 3.5312
0.55961 | 0 | 0.09686 | 679.0656 | 40 | 0 | 3.8744
0.5631 | 0 | 0.11975 | 667.5456 | 40 | 0 | 4.79
0.55423 | 0 | 0.13331 | 657.455 | 40 | 0 | 5.3324
0.54778 | 0 | 0.14825 | 648.607 | 40 | 0 | 5.93
0.53548 | 0 | 0.1682 | 641.787 | 40 | 0 | 6.728
0.51476 | 0 | 0.17373 | 637.2602 | 40 | 0 | 6.9492
0.49431 | 0 | 0.18951 | 635.4096 | 40 | 0 | 7.5804
0.48286 | 0 | 0.20127 | 635.1744 | 40 | 0 | 8.0508
0.47471 | 0 | 0.2188 | 636.4554 | 40 | 0 | 8.752
0.4743 | 0 | 0.21832 | 637.7582 | 40 | 0 | 8.7328
0.4774 | 0 | 0.20187 | 638.093 | 40 | 0 | 8.0748
0.4904 | 0 | 0.19006 | 636.6554 | 40 | 0 | 7.6024
0.50764 | 0.0001 | 0.1849 | 633.2944 | 40 | 0.007 | 7.396
0.52939 | 0.0734 | 0.16836 | 632.2278 | 40 | 5.138 | 6.7344
0.5388 | 0.5206 | 0.15489 | 660.9854 | 40 | 42.6376 | 0
0.53232 | 0.8179 | 0.09062 | 700 | 40 | 52.2466 | 0
0.51694 | 0.8608 | 0.05779 | 700 | 40 | 11.694 | 0
0.4986 | 0.8596 | 0.05167 | 700 | 40 | 9.86 | 0
0.48442 | 0.863 | 0.06272 | 700 | 40 | 8.442 | 0
0.47322 | 0.88 | 0.08299 | 700 | 40 | 7.322 | 0
0.46452 | 0.8768 | 0.07798 | 700 | 40 | 6.452 | 0
0.46152 | 0.7856 | 0.07492 | 700 | 40 | 6.152 | 0
0.46087 | 0.5208 | 0.06952 | 700 | 40 | 6.087 | 0
0.46333 | 0.0541 | 0.0847 | 700 | 40 | 3.787 | 2.546
0.48785 | 0 | 0.15878 | 697.5662 | 40 | 0 | 6.3512
0.48765 | 0 | 0.27333 | 699.7344 | 40 | 0 | 10.9332
0.48334 | 0 | 0.33756 | 700 | 40 | 0 | 8.5996
0.4783 | 0 | 0.39229 | 700 | 40 | 0 | 7.83
0.4668 | 0 | 0.42866 | 700 | 40 | 0 | 6.68
0.44987 | 0 | 0.48688 | 700 | 40 | 0 | 4.987
0.4329 | 0 | 0.49205 | 700 | 40 | 0 | 3.29
0.42358 | 0 | 0.49491 | 700 | 40 | 0 | 2.358
0.41831 | 0 | 0.47834 | 700 | 40 | 0 | 1.831
0.41554 | 0 | 0.46912 | 700 | 40 | 0 | 1.554
0.4188 | 0 | 0.46987 | 700 | 40 | 0 | 1.88
0.42602 | 0 | 0.47846 | 700 | 40 | 0 | 2.602
0.43946 | 0.0001 | 0.46085 | 700 | 40 | 0.007 | 3.939
0.45291 | 0.0456 | 0.45922 | 700 | 40 | 3.192 | 2.099
0.4682 | 0.3812 | 0.44587 | 700 | 40 | 6.82 | 0
0.46789 | 0.6116 | 0.36447 | 700 | 40 | 6.789 | 0
0.46608 | 0.6714 | 0.30676 | 700 | 40 | 6.608 | 0
0.46393 | 0.6451 | 0.28812 | 700 | 40 | 6.393 | 0
0.46497 | 0.6758 | 0.2744 | 700 | 40 | 6.497 | 0
0.46776 | 0.6638 | 0.30668 | 700 | 40 | 6.776 | 0
0.4715 | 0.7067 | 0.36638 | 700 | 40 | 7.15 | 0
0.47167 | 0.5626 | 0.39928 | 700 | 40 | 7.167 | 0
0.47603 | 0.2873 | 0.39726 | 700 | 40 | 7.603 | 0
0.48013 | 0.0303 | 0.35378 | 700 | 40 | 2.121 | 5.892
0.50849 | 0 | 0.3963 | 700 | 40 | 0 | 10.849
0.51141 | 0 | 0.46526 | 700 | 40 | 0 | 11.141
0.50339 | 0 | 0.52019 | 700 | 40 | 0 | 10.339
0.49338 | 0 | 0.55827 | 700 | 40 | 0 | 9.338
0.47039 | 0 | 0.5847 | 700 | 40 | 0 | 7.039
0.4457 | 0 | 0.58291 | 700 | 40 | 0 | 4.57
0.41832 | 0 | 0.55145 | 700 | 40 | 0 | 1.832
0.40312 | 0 | 0.53319 | 700 | 40 | 0 | 0.312
0.3935 | 0 | 0.5071 | 700 | 39.35 | 0 | 0
0.39247 | 0 | 0.49436 | 700 | 39.247 | 0 | 0
0.39217 | 0 | 0.47126 | 700 | 39.217 | 0 | 0
0.40845 | 0 | 0.43779 | 700 | 40 | 0 | 0.845
0.44111 | 0 | 0.40038 | 700 | 40 | 0 | 4.111
0.48227 | 0.0049 | 0.46184 | 700 | 40 | 0.343 | 7.884
0.49052 | 0.0581 | 0.54727 | 700 | 40 | 4.067 | 4.985
0.50549 | 0.1278 | 0.58042 | 700 | 40 | 8.946 | 1.603
0.52299 | 0.2245 | 0.63644 | 700 | 40 | 12.299 | 0
0.53646 | 0.1934 | 0.62052 | 700 | 40 | 13.538 | 0.108
0.54889 | 0.147 | 0.61184 | 700 | 40 | 10.29 | 4.599
0.5631 | 0.1268 | 0.60029 | 700 | 40 | 8.876 | 7.434
0.57336 | 0.0684 | 0.5844 | 700 | 40 | 4.788 | 12.548
0.58105 | 0.0416 | 0.57928 | 700 | 40 | 2.912 | 15.193
0.59782 | 0.0189 | 0.58149 | 700 | 40 | 1.323 | 18.459
0.62108 | 0.0013 | 0.58291 | 700 | 40 | 0.091 | 22.017
0.66087 | 0 | 0.64429 | 699.6846 | 40 | 0 | 25.7716
0.66926 | 0 | 0.66297 | 699.2774 | 40 | 0 | 26.5188
0.66955 | 0 | 0.65485 | 698.5164 | 40 | 0 | 26.194
0.66318 | 0 | 0.68773 | 699.7076 | 40 | 0 | 27.5092
0.64047 | 0 | 0.69514 | 700 | 40 | 0 | 24.3394
0.61635 | 0 | 0.6588 | 700 | 40 | 0 | 21.635
0.60348 | 0 | 0.62395 | 700 | 40 | 0 | 20.348
0.5987 | 0 | 0.59091 | 700 | 40 | 0 | 19.87
0.60052 | 0 | 0.55957 | 700 | 40 | 0 | 20.052
0.60973 | 0 | 0.51735 | 699.721 | 40 | 0 | 20.694
0.62375 | 0 | 0.48987 | 696.9408 | 40 | 0 | 19.5948
0.65302 | 0 | 0.47209 | 690.5224 | 40 | 0 | 18.8836
0.70642 | 0 | 0.41031 | 676.2928 | 40 | 0 | 16.4124
0.75734 | 0.0272 | 0.35287 | 656.5776 | 40 | 1.904 | 14.1148
0.7496 | 0.3074 | 0.29567 | 654.9624 | 40 | 21.518 | 11.8268
0.74374 | 0.6142 | 0.25097 | 673.6212 | 40 | 53.0328 | 0
0.72918 | 0.6466 | 0.21761 | 694.6696 | 40 | 53.9664 | 0
0.70994 | 0.6487 | 0.18509 | 700 | 40 | 36.3244 | 0
0.68643 | 0.6813 | 0.17184 | 700 | 40 | 28.643 | 0
0.66217 | 0.6904 | 0.16999 | 700 | 40 | 26.217 | 0
0.64251 | 0.5894 | 0.18907 | 700 | 40 | 24.251 | 0
0.63079 | 0.4018 | 0.20551 | 700 | 40 | 23.079 | 0
0.63757 | 0.1547 | 0.20512 | 695.2768 | 40 | 10.829 | 8.2048
0.66326 | 0.0195 | 0.2046 | 678.4998 | 40 | 1.365 | 8.184
0.71491 | 0 | 0.20378 | 655.16 | 40 | 0 | 8.1512
0.72751 | 0 | 0.21824 | 631.1386 | 40 | 0 | 8.7296
0.72913 | 0 | 0.22388 | 607.1808 | 40 | 0 | 8.9552
0.72052 | 0 | 0.22353 | 584.07 | 40 | 0 | 8.9412
0.69401 | 0 | 0.2255 | 563.689 | 40 | 0 | 9.02
0.66385 | 0 | 0.246 | 547.144 | 40 | 0 | 9.84
0.64711 | 0 | 0.30959 | 534.8166 | 40 | 0 | 12.3836
0.63882 | 0 | 0.35812 | 525.2594 | 40 | 0 | 14.3248
0.63815 | 0 | 0.44189 | 519.12 | 40 | 0 | 17.6756
0.64157 | 0 | 0.50765 | 515.269 | 40 | 0 | 20.306
0.65203 | 0 | 0.51545 | 510.684 | 40 | 0 | 20.618
0.6743 | 0 | 0.51356 | 503.7964 | 40 | 0 | 20.5424
0.72439 | 0 | 0.51096 | 491.7958 | 40 | 0 | 20.4384
0.76163 | 0.0205 | 0.52704 | 478.1494 | 40 | 1.435 | 21.0816
0.7401 | 0.204 | 0.53197 | 479.6982 | 40 | 14.28 | 21.2788
0.71416 | 0.3119 | 0.4847 | 489.5032 | 40 | 21.833 | 19.388
0.69193 | 0.4176 | 0.48088 | 508.7774 | 40 | 48.4672 | 0
0.67099 | 0.4682 | 0.47189 | 533.328 | 40 | 51.6496 | -5.6843e-14
0.6514 | 0.4104 | 0.43677 | 554.3868 | 40 | 46.1988 | 0
0.63722 | 0.4741 | 0.40609 | 580.0954 | 40 | 49.4306 | 0
0.62478 | 0.5133 | 0.41449 | 610.128 | 40 | 52.5106 | 0
0.62119 | 0.3643 | 0.43913 | 631.0752 | 40 | 43.0662 | 0
0.62841 | 0.161 | 0.37617 | 634.551 | 40 | 11.27 | 15.0468
0.64723 | 0.0255 | 0.28412 | 622.9778 | 40 | 1.785 | 11.3648
0.68048 | 0 | 0.26007 | 605.3326 | 40 | 0 | 10.4028
0.68014 | 0 | 0.27411 | 588.283 | 40 | 0 | 10.9644
0.67002 | 0 | 0.25408 | 571.4442 | 40 | 0 | 10.1632
0.65316 | 0 | 0.23792 | 555.645 | 40 | 0 | 9.5168
0.61868 | 0 | 0.20338 | 541.9122 | 40 | 0 | 8.1352
0.58003 | 0 | 0.18115 | 531.1552 | 40 | 0 | 7.246
0.55223 | 0 | 0.14669 | 521.7998 | 40 | 0 | 5.8676
0.53832 | 0 | 0.14011 | 513.5722 | 40 | 0 | 5.6044
0.53034 | 0 | 0.15182 | 506.611 | 40 | 0 | 6.0728
0.53106 | 0 | 0.18 | 500.705 | 40 | 0 | 7.2
0.53754 | 0 | 0.24434 | 496.7246 | 40 | 0 | 9.7736
0.55756 | 0 | 0.26808 | 491.6918 | 40 | 0 | 10.7232
0.60306 | 0 | 0.30103 | 483.427 | 40 | 0 | 12.0412
0.64567 | 0.0352 | 0.32618 | 474.3712 | 40 | 2.464 | 13.0472
0.63459 | 0.3636 | 0.32126 | 489.2146 | 40 | 38.3024 | 0
0.62486 | 0.696 | 0.29737 | 527.3434 | 40 | 60.6148 | 0
0.61763 | 0.7563 | 0.358 | 572.8414 | 40 | 67.261 | 0
0.60826 | 0.7668 | 0.39084 | 621.325 | 40 | 69.3096 | 0
0.59501 | 0.7821 | 0.37397 | 671.5298 | 40 | 69.7058 | 0
0.5869 | 0.7941 | 0.37192 | 700 | 40 | 47.1602 | -1.1369e-13
0.57914 | 0.815 | 0.36502 | 700 | 40 | 17.914 | 0
0.57032 | 0.7892 | 0.35145 | 700 | 40 | 17.032 | 0
0.56656 | 0.5352 | 0.33714 | 700 | 40 | 16.656 | 0
0.57651 | 0.0705 | 0.27742 | 698.3808 | 40 | 4.935 | 11.0968
0.61127 | 0 | 0.20949 | 685.6334 | 40 | 0 | 8.3796
0.61577 | 0 | 0.21304 | 672.578 | 40 | 0 | 8.5216
0.61189 | 0 | 0.18249 | 658.6886 | 40 | 0 | 7.2996
0.6063 | 0 | 0.16163 | 644.5238 | 40 | 0 | 6.4652
0.5844 | 0 | 0.15635 | 632.3378 | 40 | 0 | 6.254
0.55916 | 0 | 0.15351 | 622.5622 | 40 | 0 | 6.1404
0.53927 | 0 | 0.16248 | 615.1344 | 40 | 0 | 6.4992
0.53165 | 0 | 0.16511 | 608.5738 | 40 | 0 | 6.6044
0.53239 | 0 | 0.17671 | 602.4032 | 40 | 0 | 7.0684
0.53607 | 0 | 0.18196 | 596.0746 | 40 | 0 | 7.2784
0.54936 | 0 | 0.17898 | 588.2978 | 40 | 0 | 7.1592
0.57757 | 0 | 0.17118 | 577.388 | 40 | 0 | 6.8472
0.63273 | 0 | 0.17925 | 561.285 | 40 | 0 | 7.17
0.67095 | 0.0627 | 0.18427 | 545.9498 | 40 | 4.389 | 7.3708
0.64858 | 0.5706 | 0.17435 | 568.0078 | 40 | 46.916 | 0
0.6114 | 0.9032 | 0.14731 | 615.9842 | 40 | 69.1164 | 0
0.58222 | 0.9184 | 0.14563 | 667.8754 | 40 | 70.1132 | 0
0.55324 | 0.8961 | 0.16757 | 700 | 40 | 47.4486 | 0
0.52673 | 0.8851 | 0.16436 | 700 | 40 | 12.673 | 0
0.50941 | 0.896 | 0.15699 | 700 | 40 | 10.941 | 0
0.49771 | 0.915 | 0.15887 | 700 | 40 | 9.771 | 0
0.48911 | 0.8872 | 0.15758 | 700 | 40 | 8.911 | 0
0.48764 | 0.5866 | 0.16142 | 700 | 40 | 8.764 | 0
0.49436 | 0.0763 | 0.16322 | 700 | 40 | 5.341 | 4.095
0.53282 | 0 | 0.20335 | 694.852 | 40 | 0 | 8.134
0.53615 | 0 | 0.27656 | 692.2994 | 40 | 0 | 11.0624
0.53844 | 0 | 0.34001 | 692.0558 | 40 | 0 | 13.6004
0.54385 | 0 | 0.40851 | 694.0112 | 40 | 0 | 16.3404
0.53682 | 0 | 0.47372 | 699.278 | 40 | 0 | 18.9488
0.53041 | 0 | 0.51519 | 700 | 40 | 0 | 13.763
0.51602 | 0 | 0.51554 | 700 | 40 | 0 | 11.602
0.51209 | 0 | 0.51236 | 700 | 40 | 0 | 11.209
0.51306 | 0 | 0.50805 | 700 | 40 | 0 | 11.306
0.51798 | 0 | 0.48999 | 700 | 40 | 0 | 11.798
0.52658 | 0 | 0.47815 | 700 | 40 | 0 | 12.658
0.54118 | 0 | 0.47702 | 700 | 40 | 0 | 14.118
0.56746 | 0.0001 | 0.46973 | 700 | 40 | 0.007 | 16.739
0.59315 | 0.0504 | 0.47529 | 700 | 40 | 3.528 | 15.787
0.59823 | 0.3252 | 0.48607 | 700 | 40 | 19.823 | 0
0.57486 | 0.5994 | 0.40459 | 700 | 40 | 17.486 | 0
0.54978 | 0.7964 | 0.3502 | 700 | 40 | 14.978 | 0
0.5233 | 0.8056 | 0.3241 | 700 | 40 | 12.33 | 0
0.49897 | 0.7639 | 0.29843 | 700 | 40 | 9.897 | 0
0.48234 | 0.6725 | 0.30294 | 700 | 40 | 8.234 | 0
0.46843 | 0.5571 | 0.33076 | 700 | 40 | 6.843 | 0
0.46409 | 0.4172 | 0.3489 | 700 | 40 | 6.409 | 0
0.4646 | 0.2359 | 0.3634 | 700 | 40 | 6.46 | 0
0.47246 | 0.0379 | 0.35541 | 700 | 40 | 2.653 | 4.593
0.50427 | 0 | 0.41568 | 700 | 40 | 0 | 10.427
0.5083 | 0 | 0.51197 | 700 | 40 | 0 | 10.83
0.50953 | 0 | 0.5927 | 700 | 40 | 0 | 10.953
0.50885 | 0 | 0.60219 | 700 | 40 | 0 | 10.885
0.49877 | 0 | 0.59807 | 700 | 40 | 0 | 9.877
0.48538 | 0 | 0.5697 | 700 | 40 | 0 | 8.538
0.47158 | 0 | 0.52444 | 700 | 40 | 0 | 7.158
0.46431 | 0 | 0.52561 | 700 | 40 | 0 | 6.431
0.45885 | 0 | 0.48191 | 700 | 40 | 0 | 5.885
0.45795 | 0 | 0.4693 | 700 | 40 | 0 | 5.795
0.46467 | 0 | 0.44705 | 700 | 40 | 0 | 6.467
0.47568 | 0 | 0.41787 | 700 | 40 | 0 | 7.568
0.49133 | 0 | 0.38823 | 700 | 40 | 0 | 9.133
0.50964 | 0.0418 | 0.3672 | 700 | 40 | 2.926 | 8.038
0.5222 | 0.3933 | 0.41458 | 700 | 40 | 12.22 | 0
0.52063 | 0.5481 | 0.45003 | 700 | 40 | 12.063 | 0
0.50553 | 0.6088 | 0.50427 | 700 | 40 | 10.553 | 0
0.4874 | 0.6983 | 0.47012 | 700 | 40 | 8.74 | 0
0.4752 | 0.6968 | 0.37436 | 700 | 40 | 7.52 | 0
0.46558 | 0.7448 | 0.29451 | 700 | 40 | 6.558 | 0
0.46023 | 0.7892 | 0.26999 | 700 | 40 | 6.023 | 0
0.45662 | 0.7719 | 0.24963 | 700 | 40 | 5.662 | 0
0.46035 | 0.4771 | 0.17381 | 700 | 40 | 6.035 | 0
0.47123 | 0.0563 | 0.09481 | 700 | 40 | 3.941 | 3.182
0.5019 | 0 | 0.07206 | 692.6924 | 40 | 0 | 2.8824
0.51012 | 0 | 0.07136 | 684.5348 | 40 | 0 | 2.8544
0.50647 | 0 | 0.05753 | 676.189 | 40 | 0 | 2.3012
0.49742 | 0 | 0.04723 | 668.3362 | 40 | 0 | 1.8892
0.4777 | 0 | 0.05773 | 662.8754 | 40 | 0 | 2.3092
0.45268 | 0 | 0.07472 | 660.5962 | 40 | 0 | 2.9888
0.43384 | 0 | 0.10523 | 661.4214 | 40 | 0 | 4.2092
0.42562 | 0 | 0.12857 | 664.0022 | 40 | 0 | 5.1428
0.42296 | 0 | 0.15415 | 667.8722 | 40 | 0 | 6.166
0.42614 | 0 | 0.17291 | 672.1746 | 40 | 0 | 6.9164
0.43812 | 0 | 0.2107 | 676.7906 | 40 | 0 | 8.428
0.46857 | 0 | 0.24602 | 679.7744 | 40 | 0 | 9.8408
0.51576 | 0 | 0.27454 | 679.18 | 40 | 0 | 10.9816
0.56385 | 0.053 | 0.26522 | 677.1138 | 40 | 3.71 | 10.6088
0.55378 | 0.5324 | 0.27309 | 700 | 40 | 38.2642 | 0
0.53226 | 0.85 | 0.19539 | 700 | 40 | 13.226 | 0
0.51674 | 0.8634 | 0.11416 | 700 | 40 | 11.674 | 0
0.50824 | 0.8205 | 0.11397 | 700 | 40 | 10.824 | 0
0.50129 | 0.8055 | 0.06795 | 700 | 40 | 10.129 | 0
0.49877 | 0.8149 | 0.05111 | 700 | 40 | 9.877 | 0
0.49904 | 0.8284 | 0.05291 | 700 | 40 | 9.904 | 0
0.49743 | 0.7914 | 0.05538 | 700 | 40 | 9.743 | 0
0.50064 | 0.5106 | 0.04324 | 700 | 40 | 10.064 | 0
0.50484 | 0.0628 | 0.03513 | 695.3172 | 40 | 4.396 | 1.4052
0.52763 | 0 | 0.0582 | 684.8822 | 40 | 0 | 2.328
0.53014 | 0 | 0.08898 | 675.4274 | 40 | 0 | 3.5592
0.52158 | 0 | 0.10229 | 667.361 | 40 | 0 | 4.0916
0.50773 | 0 | 0.14306 | 662.3104 | 40 | 0 | 5.7224
0.4812 | 0 | 0.16742 | 660.8872 | 40 | 0 | 6.6968
0.45069 | 0 | 0.20212 | 663.903 | 40 | 0 | 8.0848
0.42838 | 0 | 0.22448 | 670.0442 | 40 | 0 | 8.9792
0.4166 | 0 | 0.25446 | 678.5626 | 40 | 0 | 10.1784
0.41325 | 0 | 0.24803 | 687.1588 | 40 | 0 | 9.9212
0.41545 | 0 | 0.24658 | 695.477 | 40 | 0 | 9.8632
0.42306 | 0 | 0.23639 | 700 | 40 | 0 | 6.829
0.4455 | 0 | 0.22001 | 700 | 40 | 0 | 4.55
0.49471 | 0 | 0.23674 | 699.9986 | 40 | 0 | 9.4696
0.53672 | 0.0345 | 0.25998 | 699.1408 | 40 | 2.415 | 10.3992
0.52543 | 0.3971 | 0.27429 | 700 | 40 | 13.4022 | 0
0.51934 | 0.7109 | 0.25113 | 700 | 40 | 11.934 | 0
0.5036 | 0.8042 | 0.19881 | 700 | 40 | 10.36 | 0
0.49942 | 0.8221 | 0.23765 | 700 | 40 | 9.942 | 0
0.499 | 0.8173 | 0.27021 | 700 | 40 | 9.9 | 0
0.50594 | 0.8319 | 0.37316 | 700 | 40 | 10.594 | 0
0.51294 | 0.8095 | 0.41031 | 700 | 40 | 11.294 | 0
0.51293 | 0.6935 | 0.42595 | 700 | 40 | 11.293 | 0
0.51678 | 0.3403 | 0.45711 | 700 | 40 | 11.678 | 0
0.51443 | 0.0374 | 0.43641 | 700 | 40 | 2.618 | 8.825
0.53588 | 0 | 0.52757 | 700 | 40 | 0 | 13.588
0.53816 | 0 | 0.61743 | 700 | 40 | 0 | 13.816
0.52681 | 0 | 0.67147 | 700 | 40 | 0 | 12.681
0.51208 | 0 | 0.6701 | 700 | 40 | 0 | 11.208
0.48481 | 0 | 0.67821 | 700 | 40 | 0 | 8.481
0.44951 | 0 | 0.66716 | 700 | 40 | 0 | 4.951
0.4232 | 0 | 0.65519 | 700 | 40 | 0 | 2.32
0.40684 | 0 | 0.61981 | 700 | 40 | 0 | 0.684
0.39792 | 0 | 0.59527 | 700 | 39.792 | 0 | 0
0.39412 | 0 | 0.60675 | 700 | 39.412 | 0 | 0
0.39529 | 0 | 0.61226 | 700 | 39.529 | 0 | 0
0.40999 | 0 | 0.62043 | 700 | 40 | 0 | 0.999
0.44795 | 0 | 0.66085 | 700 | 40 | 0 | 4.795
0.49031 | 0.0098 | 0.6853 | 700 | 40 | 0.686 | 8.345
0.49237 | 0.0945 | 0.70496 | 700 | 40 | 6.615 | 2.622
0.50127 | 0.1978 | 0.67763 | 700 | 40 | 10.127 | 0
0.51181 | 0.2367 | 0.73043 | 700 | 40 | 11.181 | 0
0.51853 | 0.3224 | 0.72296 | 700 | 40 | 11.853 | 0
0.52473 | 0.2942 | 0.72988 | 700 | 40 | 12.473 | 0
0.53345 | 0.3091 | 0.71042 | 700 | 40 | 13.345 | 0
0.53797 | 0.3524 | 0.68892 | 700 | 40 | 13.797 | 0
0.53883 | 0.3356 | 0.65436 | 700 | 40 | 13.883 | 0
0.54035 | 0.2544 | 0.64846 | 700 | 40 | 14.035 | 0
0.54009 | 0.0279 | 0.6158 | 700 | 40 | 1.953 | 12.056
0.56271 | 0 | 0.59036 | 700 | 40 | 0 | 16.271
0.56126 | 0 | 0.63077 | 700 | 40 | 0 | 16.126
0.54925 | 0 | 0.65648 | 700 | 40 | 0 | 14.925
0.53833 | 0 | 0.6119 | 700 | 40 | 0 | 13.833
0.5115 | 0 | 0.55518 | 700 | 40 | 0 | 11.15
0.47767 | 0 | 0.54377 | 700 | 40 | 0 | 7.767
0.44566 | 0 | 0.52793 | 700 | 40 | 0 | 4.566
0.42351 | 0 | 0.45237 | 700 | 40 | 0 | 2.351
0.41258 | 0 | 0.40437 | 700 | 40 | 0 | 1.258
0.40488 | 0 | 0.39002 | 700 | 40 | 0 | 0.488
0.40615 | 0 | 0.40476 | 700 | 40 | 0 | 0.615
0.42012 | 0 | 0.39207 | 700 | 40 | 0 | 2.012
0.45583 | 0 | 0.39435 | 700 | 40 | 0 | 5.583
0.49934 | 0.014 | 0.4083 | 700 | 40 | 0.98 | 8.954
0.49997 | 0.248 | 0.40359 | 700 | 40 | 9.997 | 0
0.51505 | 0.4532 | 0.42277 | 700 | 40 | 11.505 | 0
0.52959 | 0.6065 | 0.42977 | 700 | 40 | 12.959 | 0
0.54194 | 0.642 | 0.43071 | 700 | 40 | 14.194 | 0
0.54802 | 0.6439 | 0.40661 | 700 | 40 | 14.802 | 0
0.5509 | 0.6327 | 0.36514 | 700 | 40 | 15.09 | 0
0.55461 | 0.6224 | 0.38609 | 700 | 40 | 15.461 | 0
0.55302 | 0.5821 | 0.40162 | 700 | 40 | 15.302 | 0
0.55545 | 0.3826 | 0.44561 | 700 | 40 | 15.545 | 0
0.55874 | 0.0492 | 0.46778 | 700 | 40 | 3.444 | 12.43
0.57668 | 0 | 0.4725 | 700 | 40 | 0 | 17.668
0.57193 | 0 | 0.45052 | 700 | 40 | 0 | 17.193
0.56075 | 0 | 0.4817 | 700 | 40 | 0 | 16.075
0.54551 | 0 | 0.46841 | 700 | 40 | 0 | 14.551
0.51998 | 0 | 0.41951 | 700 | 40 | 0 | 11.998
0.4875 | 0 | 0.44412 | 700 | 40 | 0 | 8.75
0.45458 | 0 | 0.48146 | 700 | 40 | 0 | 5.458
0.43538 | 0 | 0.50686 | 700 | 40 | 0 | 3.538
0.42315 | 0 | 0.49605 | 700 | 40 | 0 | 2.315
0.41467 | 0 | 0.40748 | 700 | 40 | 0 | 1.467
0.41749 | 0 | 0.34403 | 700 | 40 | 0 | 1.749
0.43237 | 0 | 0.26748 | 700 | 40 | 0 | 3.237
0.46874 | 0 | 0.26815 | 700 | 40 | 0 | 6.874
0.5113 | 0.014 | 0.28203 | 700 | 40 | 0.98 | 10.15
0.52081 | 0.1721 | 0.23026 | 700 | 40 | 12.047 | 0.034
0.53293 | 0.2423 | 0.2071 | 700 | 40 | 13.293 | 0
0.54614 | 0.3115 | 0.16614 | 700 | 40 | 14.614 | 0
0.55366 | 0.4347 | 0.1315 | 700 | 40 | 15.366 | 0
0.54781 | 0.5672 | 0.12203 | 700 | 40 | 14.781 | 0
0.5428 | 0.6257 | 0.11688 | 700 | 40 | 14.28 | 0
0.53947 | 0.6878 | 0.11515 | 700 | 40 | 13.947 | 0
0.53286 | 0.6928 | 0.09616 | 700 | 40 | 13.286 | 0
0.5292 | 0.4534 | 0.11703 | 700 | 40 | 12.92 | 0
0.53741 | 0.0457 | 0.10772 | 693.7668 | 40 | 3.199 | 4.3088
0.55561 | 0 | 0.11314 | 682.7314 | 40 | 0 | 4.5256
0.55497 | 0 | 0.13744 | 672.732 | 40 | 0 | 5.4976
0.54708 | 0 | 0.14314 | 663.7496 | 40 | 0 | 5.7256
0.53705 | 0 | 0.14341 | 655.781 | 40 | 0 | 5.7364
0.5215 | 0 | 0.12686 | 648.7054 | 40 | 0 | 5.0744
0.50124 | 0 | 0.10835 | 642.9154 | 40 | 0 | 4.334
0.47885 | 0 | 0.0993 | 639.0024 | 40 | 0 | 3.972
0.46719 | 0 | 0.12148 | 637.1426 | 40 | 0 | 4.8592
0.45965 | 0 | 0.12737 | 636.2724 | 40 | 0 | 5.0948
0.45866 | 0 | 0.15033 | 636.4196 | 40 | 0 | 6.0132
0.46002 | 0 | 0.16983 | 637.2108 | 40 | 0 | 6.7932
0.47197 | 0 | 0.2047 | 638.2018 | 40 | 0 | 8.188
0.49315 | 0 | 0.21457 | 637.4696 | 40 | 0 | 8.5828
0.51615 | 0.034 | 0.25223 | 638.3238 | 40 | 2.38 | 10.0892
0.53701 | 0.4405 | 0.2643 | 666.0298 | 40 | 41.407 | 0
0.53664 | 0.8032 | 0.23187 | 700 | 40 | 47.6342 | 0
0.53228 | 0.8391 | 0.21355 | 700 | 40 | 13.228 | 0
0.51809 | 0.8416 | 0.24755 | 700 | 40 | 11.809 | 0
0.50298 | 0.8493 | 0.25302 | 700 | 40 | 10.298 | 0
0.48891 | 0.8607 | 0.2623 | 700 | 40 | 8.891 | 0
0.47737 | 0.8789 | 0.25089 | 700 | 40 | 7.737 | 0
0.47035 | 0.8382 | 0.20832 | 700 | 40 | 7.035 | 0
0.47107 | 0.5206 | 0.16181 | 700 | 40 | 7.107 | 0
0.48199 | 0.0627 | 0.09754 | 700 | 40 | 4.389 | 3.81
0.51118 | 0.0047 | 0.07642 | 692.2678 | 40 | 0.329 | 3.0568
0.51429 | 0 | 0.07061 | 683.6632 | 40 | 0 | 2.8244
0.5118 | 0 | 0.06671 | 675.1516 | 40 | 0 | 2.6684
0.50828 | 0 | 0.06703 | 667.0048 | 40 | 0 | 2.6812
0.4986 | 0 | 0.07025 | 659.9548 | 40 | 0 | 2.81
0.48545 | 0 | 0.06239 | 653.9054 | 40 | 0 | 2.4956
0.47162 | 0 | 0.06899 | 649.503 | 40 | 0 | 2.7596
0.46243 | 0 | 0.10587 | 647.4948 | 40 | 0 | 4.2348
0.45834 | 0 | 0.12281 | 646.5732 | 40 | 0 | 4.9124
0.45767 | 0 | 0.12266 | 645.7126 | 40 | 0 | 4.9064
0.46108 | 0 | 0.12195 | 644.4826 | 40 | 0 | 4.878
0.4721 | 0 | 0.14577 | 643.1034 | 40 | 0 | 5.8308
0.4885 | 0 | 0.15301 | 640.3738 | 40 | 0 | 6.1204
0.50748 | 0.0355 | 0.165 | 638.7108 | 40 | 2.485 | 6.6
0.52335 | 0.4294 | 0.2139 | 664.9898 | 40 | 38.614 | 0
0.51602 | 0.7273 | 0.19743 | 700 | 40 | 46.6122 | 0
0.49989 | 0.7545 | 0.11778 | 700 | 40 | 9.989 | 0
0.48479 | 0.7789 | 0.1521 | 700 | 40 | 8.479 | 0
0.4756 | 0.7723 | 0.24166 | 700 | 40 | 7.56 | 0
0.47073 | 0.6936 | 0.29567 | 700 | 40 | 7.073 | 0
0.46812 | 0.6592 | 0.32657 | 700 | 40 | 6.812 | 0
0.46844 | 0.6733 | 0.31678 | 700 | 40 | 6.844 | 0
0.46798 | 0.3765 | 0.30153 | 700 | 40 | 6.798 | 0
0.47453 | 0.0436 | 0.29264 | 700 | 40 | 3.052 | 4.401
0.50037 | 0.0035 | 0.37662 | 700 | 40 | 0.245 | 9.792
0.50598 | 0 | 0.50265 | 700 | 40 | 0 | 10.598
0.50187 | 0 | 0.62201 | 700 | 40 | 0 | 10.187
0.49388 | 0 | 0.65589 | 700 | 40 | 0 | 9.388
0.47784 | 0 | 0.65393 | 700 | 40 | 0 | 7.784
0.45531 | 0 | 0.65094 | 700 | 40 | 0 | 5.531
0.4329 | 0 | 0.60782 | 700 | 40 | 0 | 3.29
0.42193 | 0 | 0.6158 | 700 | 40 | 0 | 2.193
0.41578 | 0 | 0.6145 | 700 | 40 | 0 | 1.578
0.41768 | 0 | 0.62755 | 700 | 40 | 0 | 1.768
0.4228 | 0 | 0.6237 | 700 | 40 | 0 | 2.28
0.4404 | 0 | 0.59932 | 700 | 40 | 0 | 4.04
0.47407 | 0 | 0.61462 | 700 | 40 | 0 | 7.407
0.50595 | 0.0295 | 0.64544 | 700 | 40 | 2.065 | 8.53
0.51588 | 0.3242 | 0.59288 | 700 | 40 | 11.588 | 0
0.5135 | 0.4468 | 0.46774 | 700 | 40 | 11.35 | 0
0.51259 | 0.5115 | 0.34324 | 700 | 40 | 11.259 | 0
0.51454 | 0.5373 | 0.34933 | 700 | 40 | 11.454 | 0
0.51597 | 0.5761 | 0.32001 | 700 | 40 | 11.597 | 0
0.51943 | 0.4282 | 0.26316 | 700 | 40 | 11.943 | 0
0.5257 | 0.3242 | 0.21976 | 700 | 40 | 12.57 | 0
0.53055 | 0.2469 | 0.19554 | 700 | 40 | 13.055 | 0
0.53312 | 0.1092 | 0.20852 | 700 | 40 | 7.644 | 5.668
0.53216 | 0.0086 | 0.20462 | 695.5708 | 40 | 0.602 | 8.1848
0.556 | 0 | 0.26257 | 690.4736 | 40 | 0 | 10.5028
0.54891 | 0 | 0.35087 | 689.6174 | 40 | 0 | 14.0348
0.53746 | 0 | 0.45068 | 693.8986 | 40 | 0 | 18.0272
0.52578 | 0 | 0.53178 | 700 | 40 | 0 | 18.6794
0.5048 | 0 | 0.62936 | 700 | 40 | 0 | 10.48
0.47703 | 0 | 0.67999 | 700 | 40 | 0 | 7.703
0.45236 | 0 | 0.70795 | 700 | 40 | 0 | 5.236
0.43446 | 0 | 0.70173 | 700 | 40 | 0 | 3.446
0.42555 | 0 | 0.71518 | 700 | 40 | 0 | 2.555
0.41929 | 0 | 0.69576 | 700 | 40 | 0 | 1.929
0.42158 | 0 | 0.7127 | 700 | 40 | 0 | 2.158
0.43221 | 0 | 0.71773 | 700 | 40 | 0 | 3.221
0.45951 | 0 | 0.72626 | 700 | 40 | 0 | 5.951
0.48734 | 0.0095 | 0.75488 | 700 | 40 | 0.665 | 8.069
0.50383 | 0.1021 | 0.74903 | 700 | 40 | 7.147 | 3.236
0.52057 | 0.2601 | 0.67673 | 700 | 40 | 12.057 | 0
0.53471 | 0.3643 | 0.62193 | 700 | 40 | 13.471 | 0
0.54557 | 0.4506 | 0.6441 | 700 | 40 | 14.557 | 0
0.5476 | 0.5345 | 0.59527 | 700 | 40 | 14.76 | 0
0.55022 | 0.6116 | 0.52164 | 700 | 40 | 15.022 | 0
0.54931 | 0.5883 | 0.52223 | 700 | 40 | 14.931 | 0
0.55325 | 0.4319 | 0.58596 | 700 | 40 | 15.325 | 0
0.55104 | 0.2363 | 0.58773 | 700 | 40 | 15.104 | 0
0.553 | 0.0197 | 0.62865 | 700 | 40 | 1.379 | 13.921
0.57244 | 0 | 0.64351 | 700 | 40 | 0 | 17.244
0.56703 | 0 | 0.65943 | 700 | 40 | 0 | 16.703
0.55655 | 0 | 0.64524 | 700 | 40 | 0 | 15.655
0.54223 | 0 | 0.63435 | 700 | 40 | 0 | 14.223
0.51998 | 0 | 0.58226 | 700 | 40 | 0 | 11.998
0.49396 | 0 | 0.57416 | 700 | 40 | 0 | 9.396
0.46498 | 0 | 0.5249 | 700 | 40 | 0 | 6.498
0.44596 | 0 | 0.46342 | 700 | 40 | 0 | 4.596
0.43585 | 0 | 0.45284 | 700 | 40 | 0 | 3.585
0.42766 | 0 | 0.44958 | 700 | 40 | 0 | 2.766
0.42585 | 0 | 0.34953 | 700 | 40 | 0 | 2.585
0.4375 | 0 | 0.3305 | 700 | 40 | 0 | 3.75
0.46497 | 0 | 0.31293 | 700 | 40 | 0 | 6.497
0.49935 | 0.0091 | 0.27653 | 700 | 40 | 0.637 | 9.298
0.51735 | 0.1125 | 0.2735 | 700 | 40 | 7.875 | 3.86
0.53218 | 0.247 | 0.25927 | 700 | 40 | 13.218 | 0
0.53828 | 0.3335 | 0.26847 | 700 | 40 | 13.828 | 0
0.53803 | 0.3598 | 0.2746 | 700 | 40 | 13.803 | 0
0.53253 | 0.3003 | 0.25821 | 700 | 40 | 13.253 | 0
0.52814 | 0.2458 | 0.23521 | 700 | 40 | 12.814 | 0
0.52674 | 0.1466 | 0.24236 | 700 | 40 | 10.262 | 2.412
0.52258 | 0.0723 | 0.2345 | 700 | 40 | 5.061 | 7.197
0.52707 | 0.0251 | 0.19853 | 696.9912 | 40 | 1.757 | 7.9412
0.53953 | 0.0014 | 0.20738 | 691.4314 | 40 | 0.098 | 8.2952
0.56107 | 0 | 0.17628 | 682.3756 | 40 | 0 | 7.0512
0.556 | 0 | 0.19523 | 674.5848 | 40 | 0 | 7.8092
0.54736 | 0 | 0.21858 | 668.592 | 40 | 0 | 8.7432
0.53911 | 0 | 0.2242 | 663.649 | 40 | 0 | 8.968
0.52221 | 0 | 0.20903 | 659.7892 | 40 | 0 | 8.3612
0.49671 | 0 | 0.17486 | 657.1126 | 40 | 0 | 6.9944
0.47209 | 0 | 0.17467 | 656.8904 | 40 | 0 | 6.9868
0.4527 | 0.0003 | 0.16142 | 658.0982 | 40 | 0.021 | 6.4568
0.44038 | 0 | 0.13752 | 659.561 | 40 | 0 | 5.5008
0.43462 | 0 | 0.1409 | 661.735 | 40 | 0 | 5.636
0.43415 | 0.0014 | 0.15544 | 664.6356 | 40 | 0.098 | 6.2176
0.44219 | 0 | 0.15316 | 666.543 | 40 | 0 | 6.1264
0.45709 | 0 | 0.19173 | 668.5032 | 40 | 0 | 7.6692
0.47287 | 0.003 | 0.19314 | 669.1518 | 40 | 0.21 | 7.7256
0.4971 | 0.0807 | 0.17188 | 671.966 | 40 | 5.649 | 6.8752
0.52385 | 0.2297 | 0.13795 | 681.178 | 40 | 21.597 | 0
0.54287 | 0.3044 | 0.10984 | 692.5926 | 40 | 25.7016 | 0
0.55124 | 0.3635 | 0.08779 | 700 | 40 | 22.5314 | 0
0.5475 | 0.3956 | 0.07666 | 700 | 40 | 14.75 | 0
0.53118 | 0.4173 | 0.06892 | 700 | 40 | 13.118 | 0
0.51577 | 0.3606 | 0.06074 | 700 | 40 | 11.577 | 0
0.50545 | 0.2203 | 0.06129 | 700 | 40 | 10.545 | 0
0.49998 | 0.0962 | 0.06565 | 699.362 | 40 | 6.734 | 2.626
0.49881 | 0.0097 | 0.06911 | 692.9244 | 40 | 0.679 | 2.7644
0.51246 | 0 | 0.09093 | 685.3156 | 40 | 0 | 3.6372
0.50855 | 0 | 0.12946 | 679.639 | 40 | 0 | 5.1784
0.50472 | 0 | 0.12022 | 673.9758 | 40 | 0 | 4.8088
0.50178 | 0 | 0.08444 | 667.1754 | 40 | 0 | 3.3776
0.4922 | 0 | 0.07587 | 660.9902 | 40 | 0 | 3.0348
0.47947 | 0 | 0.07705 | 656.1252 | 40 | 0 | 3.082
0.4605 | 0 | 0.06517 | 652.682 | 40 | 0 | 2.6068
0.44798 | 0 | 0.06679 | 650.5556 | 40 | 0 | 2.6716
0.43944 | 0 | 0.08089 | 649.8472 | 40 | 0 | 3.2356
0.43447 | 0 | 0.10202 | 650.481 | 40 | 0 | 4.0808
0.43186 | 0 | 0.0693 | 650.067 | 40 | 0 | 2.772
0.44518 | 0 | 0.06829 | 648.2806 | 40 | 0 | 2.7316
0.45849 | 0 | 0.08649 | 645.8912 | 40 | 0 | 3.4596
0.47491 | 0.0063 | 0.12635 | 643.8952 | 40 | 0.441 | 5.054
0.48654 | 0.1613 | 0.16351 | 653.0726 | 40 | 17.8314 | 0
0.50166 | 0.3328 | 0.2157 | 674.8306 | 40 | 31.924 | 1.1369e-13
0.52017 | 0.3962 | 0.24876 | 700 | 40 | 37.1864 | 0
0.52744 | 0.4034 | 0.29373 | 700 | 40 | 12.744 | 0
0.53204 | 0.3971 | 0.38593 | 700 | 40 | 13.204 | 0
0.53094 | 0.3575 | 0.46048 | 700 | 40 | 13.094 | 0
0.52629 | 0.2888 | 0.50297 | 700 | 40 | 12.629 | 0
0.52312 | 0.1907 | 0.53631 | 700 | 40 | 12.312 | 0
0.52399 | 0.0927 | 0.56177 | 700 | 40 | 6.489 | 5.91
0.52896 | 0.0094 | 0.57544 | 700 | 40 | 0.658 | 12.238
0.54418 | 0 | 0.60487 | 700 | 40 | 0 | 14.418
0.53691 | 0 | 0.62361 | 700 | 40 | 0 | 13.691
0.52688 | 0 | 0.61109 | 700 | 40 | 0 | 12.688
0.51682 | 0 | 0.61928 | 700 | 40 | 0 | 11.682
0.50054 | 0 | 0.63852 | 700 | 40 | 0 | 10.054
0.48148 | 0 | 0.63871 | 700 | 40 | 0 | 8.148
0.45976 | 0 | 0.61921 | 700 | 40 | 0 | 5.976
0.44091 | 0 | 0.54913 | 700 | 40 | 0 | 4.091
0.42654 | 0 | 0.51669 | 700 | 40 | 0 | 2.654
0.41935 | 0 | 0.48524 | 700 | 40 | 0 | 1.935
0.41796 | 0 | 0.4499 | 700 | 40 | 0 | 1.796
0.41858 | 0 | 0.40208 | 700 | 40 | 0 | 1.858
0.43157 | 0 | 0.41985 | 700 | 40 | 0 | 3.157
0.44378 | 0.0129 | 0.42896 | 700 | 40 | 0.903 | 3.475
0.46196 | 0.319 | 0.44975 | 700 | 40 | 6.196 | 0
0.48356 | 0.69 | 0.43383 | 700 | 40 | 8.356 | 0
0.50675 | 0.7844 | 0.48049 | 700 | 40 | 10.675 | 0
0.52766 | 0.815 | 0.51943 | 700 | 40 | 12.766 | 0
0.53599 | 0.7668 | 0.50278 | 700 | 40 | 13.599 | 0
0.54299 | 0.6448 | 0.51476 | 700 | 40 | 14.299 | 0
0.54363 | 0.7034 | 0.55076 | 700 | 40 | 14.363 | 0
0.54695 | 0.5416 | 0.55864 | 700 | 40 | 14.695 | 0
0.54732 | 0.3201 | 0.57281 | 700 | 40 | 14.732 | 0
0.54145 | 0.0393 | 0.56551 | 700 | 40 | 2.751 | 11.394
0.55736 | 0 | 0.57081 | 700 | 40 | 0 | 15.736
0.55011 | 0 | 0.61507 | 700 | 40 | 0 | 15.011
0.5366 | 0 | 0.62948 | 700 | 40 | 0 | 13.66
0.52228 | 0 | 0.57308 | 700 | 40 | 0 | 12.228
0.50527 | 0 | 0.55578 | 700 | 40 | 0 | 10.527
0.48277 | 0 | 0.55215 | 700 | 40 | 0 | 8.277
0.45364 | 0 | 0.548 | 700 | 40 | 0 | 5.364
0.43677 | 0 | 0.55981 | 700 | 40 | 0 | 3.677
0.42453 | 0 | 0.56001 | 700 | 40 | 0 | 2.453
0.41629 | 0 | 0.53468 | 700 | 40 | 0 | 1.629
0.41601 | 0 | 0.52345 | 700 | 40 | 0 | 1.601
0.42206 | 0 | 0.51338 | 700 | 40 | 0 | 2.206
0.43166 | 0 | 0.46883 | 700 | 40 | 0 | 3.166
0.44905 | 0.0228 | 0.42139 | 700 | 40 | 1.596 | 3.309
0.4677 | 0.3997 | 0.36352 | 700 | 40 | 6.77 | 0
0.48159 | 0.8184 | 0.3192 | 700 | 40 | 8.159 | 0
0.48859 | 0.8614 | 0.3795 | 700 | 40 | 8.859 | 0
0.48846 | 0.8505 | 0.33476 | 700 | 40 | 8.846 | 0
0.48312 | 0.8419 | 0.23934 | 700 | 40 | 8.312 | 0
0.47983 | 0.8559 | 0.20313 | 700 | 40 | 7.983 | 0
0.47454 | 0.8697 | 0.1819 | 700 | 40 | 7.454 | 0
0.47238 | 0.829 | 0.16476 | 700 | 40 | 7.238 | 0
0.47505 | 0.5192 | 0.14349 | 700 | 40 | 7.505 | 0
0.48962 | 0.0576 | 0.10843 | 699.4072 | 40 | 4.032 | 4.3372
0.52756 | 0.0047 | 0.09705 | 690.8622 | 40 | 0.329 | 3.882
0.53994 | 0.002 | 0.11909 | 681.7718 | 40 | 0.14 | 4.7636
0.54142 | 0 | 0.12731 | 672.7222 | 40 | 0 | 5.0924
0.53595 | 0 | 0.13665 | 664.5932 | 40 | 0 | 5.466
0.51856 | 0 | 0.1399 | 658.3332 | 40 | 0 | 5.596
0.49524 | 0 | 0.13847 | 654.348 | 40 | 0 | 5.5388
0.4728 | 0 | 0.13439 | 652.4436 | 40 | 0 | 5.3756
0.46307 | 0 | 0.14339 | 651.8722 | 40 | 0 | 5.7356
0.46002 | 0 | 0.15057 | 651.893 | 40 | 0 | 6.0228
0.4627 | 0 | 0.16969 | 652.4106 | 40 | 0 | 6.7876
0.47354 | 0 | 0.17564 | 652.0822 | 40 | 0 | 7.0256
0.50032 | 0 | 0.17174 | 648.9198 | 40 | 0 | 6.8696
0.55253 | 0 | 0.17336 | 640.6012 | 40 | 0 | 6.9344
0.60818 | 0.0213 | 0.18858 | 628.8174 | 40 | 1.491 | 7.5432
0.60084 | 0.3589 | 0.19611 | 641.7008 | 40 | 32.9674 | -1.1369e-13
0.58092 | 0.8132 | 0.17425 | 687.5028 | 40 | 63.894 | 0
0.56466 | 0.8718 | 0.15509 | 700 | 40 | 28.9632 | 0
0.5485 | 0.8583 | 0.18047 | 700 | 40 | 14.85 | 0
0.53336 | 0.8404 | 0.19202 | 700 | 40 | 13.336 | 0
0.52092 | 0.8498 | 0.19758 | 700 | 40 | 12.092 | 0
0.51263 | 0.8718 | 0.20287 | 700 | 40 | 11.263 | 0
0.50519 | 0.8347 | 0.20569 | 700 | 40 | 10.519 | 0
0.50635 | 0.531 | 0.22215 | 700 | 40 | 10.635 | 0
0.51708 | 0.059 | 0.22184 | 700 | 40 | 4.13 | 7.578
0.5633 | 0.0012 | 0.27766 | 694.8604 | 40 | 0.084 | 11.1064
0.5714 | 0 | 0.38837 | 693.2552 | 40 | 0 | 15.5348
0.57445 | 0 | 0.48957 | 695.393 | 40 | 0 | 19.5828
0.57257 | 0 | 0.56235 | 700 | 40 | 0 | 21.864
0.55344 | 0 | 0.60213 | 700 | 40 | 0 | 15.344
0.52398 | 0 | 0.60692 | 700 | 40 | 0 | 12.398
0.50265 | 0 | 0.60542 | 700 | 40 | 0 | 10.265
0.49206 | 0 | 0.58962 | 700 | 40 | 0 | 9.206
0.49003 | 0 | 0.5788 | 700 | 40 | 0 | 9.003
0.49169 | 0 | 0.55848 | 700 | 40 | 0 | 9.169
0.50088 | 0 | 0.53446 | 700 | 40 | 0 | 10.088
0.52678 | 0 | 0.50579 | 700 | 40 | 0 | 12.678
0.57488 | 0 | 0.46995 | 700 | 40 | 0 | 17.488
0.62295 | 0.0209 | 0.45932 | 697.5408 | 40 | 1.463 | 18.3728
0.60763 | 0.3844 | 0.45693 | 700 | 40 | 23.2222 | 0
0.58041 | 0.8295 | 0.34549 | 700 | 40 | 18.041 | 0
0.55631 | 0.8632 | 0.24455 | 700 | 40 | 15.631 | 0
0.53514 | 0.8539 | 0.25587 | 700 | 40 | 13.514 | 0
0.52182 | 0.8197 | 0.21489 | 700 | 40 | 12.182 | 0
0.51177 | 0.8221 | 0.23679 | 700 | 40 | 11.177 | 0
0.50905 | 0.8526 | 0.23551 | 700 | 40 | 10.905 | 0
0.50335 | 0.8056 | 0.21095 | 700 | 40 | 10.335 | 0
0.50724 | 0.5145 | 0.18611 | 700 | 40 | 10.724 | 0
0.51403 | 0.0566 | 0.14339 | 698.2946 | 40 | 3.962 | 5.7356
0.54641 | 0.0023 | 0.14964 | 689.8002 | 40 | 0.161 | 5.9856
0.54881 | 0 | 0.17518 | 681.9264 | 40 | 0 | 7.0072
0.54687 | 0 | 0.18101 | 674.4798 | 40 | 0 | 7.2404
0.53897 | 0 | 0.1707 | 667.4108 | 40 | 0 | 6.828
0.51611 | 0 | 0.1547 | 661.9878 | 40 | 0 | 6.188
0.48536 | 0 | 0.17796 | 660.5702 | 40 | 0 | 7.1184
0.4611 | 0 | 0.1863 | 661.9122 | 40 | 0 | 7.452
0.45083 | 0 | 0.18538 | 664.2444 | 40 | 0 | 7.4152
0.4464 | 0 | 0.16923 | 666.3736 | 40 | 0 | 6.7692
0.44962 | 0 | 0.16069 | 667.8392 | 40 | 0 | 6.4276
0.45857 | 0 | 0.18151 | 669.2426 | 40 | 0 | 7.2604
0.48169 | 0 | 0.19013 | 668.6788 | 40 | 0 | 7.6052
0.52929 | 0 | 0.187 | 663.2298 | 40 | 0 | 7.48
0.5783 | 0.0153 | 0.20457 | 654.6536 | 40 | 1.071 | 8.1828
0.5661 | 0.2238 | 0.21261 | 662.214 | 40 | 15.666 | 8.5044
0.54783 | 0.4506 | 0.19917 | 686.9398 | 40 | 39.5088 | 0
0.53348 | 0.494 | 0.16328 | 700 | 40 | 26.4082 | 0
0.5191 | 0.548 | 0.17097 | 700 | 40 | 11.91 | 0
0.51259 | 0.5528 | 0.19059 | 700 | 40 | 11.259 | 0
0.51136 | 0.5062 | 0.18959 | 700 | 40 | 11.136 | 0
0.5135 | 0.4316 | 0.19855 | 700 | 40 | 11.35 | 0
0.51066 | 0.2777 | 0.18553 | 700 | 40 | 11.066 | 0
0.51192 | 0.1307 | 0.17112 | 700 | 40 | 9.149 | 2.043
0.51699 | 0.0135 | 0.17402 | 696.2068 | 40 | 0.945 | 6.9608
0.54884 | 0.0012 | 0.26479 | 691.9984 | 40 | 0.084 | 10.5916
0.5518 | 0 | 0.3942 | 692.5864 | 40 | 0 | 15.768
0.54557 | 0 | 0.48895 | 697.5874 | 40 | 0 | 19.558
0.53738 | 0 | 0.58556 | 700 | 40 | 0 | 16.1506
0.51264 | 0 | 0.57366 | 700 | 40 | 0 | 11.264
0.47982 | 0 | 0.56142 | 700 | 40 | 0 | 7.982
0.4499 | 0 | 0.51294 | 700 | 40 | 0 | 4.99
0.43775 | 0 | 0.51557 | 700 | 40 | 0 | 3.775
0.43269 | 0 | 0.52588 | 700 | 40 | 0 | 3.269
0.43041 | 0 | 0.51047 | 700 | 40 | 0 | 3.041
0.43475 | 0 | 0.49448 | 700 | 40 | 0 | 3.475
0.45325 | 0 | 0.47458 | 700 | 40 | 0 | 5.325
0.49755 | 0 | 0.44932 | 700 | 40 | 0 | 9.755
0.54201 | 0.0054 | 0.41363 | 700 | 40 | 0.378 | 13.823
0.53624 | 0.1297 | 0.4098 | 700 | 40 | 9.079 | 4.545
0.52916 | 0.37 | 0.35959 | 700 | 40 | 12.916 | 0
0.52367 | 0.4339 | 0.29612 | 700 | 40 | 12.367 | 0
0.51961 | 0.5185 | 0.32444 | 700 | 40 | 11.961 | 0
0.51877 | 0.576 | 0.36565 | 700 | 40 | 11.877 | 0
0.5203 | 0.7022 | 0.41904 | 700 | 40 | 12.03 | 0
0.52195 | 0.692 | 0.46025 | 700 | 40 | 12.195 | 0
0.5234 | 0.5811 | 0.47165 | 700 | 40 | 12.34 | 0
0.52346 | 0.3673 | 0.48119 | 700 | 40 | 12.346 | 0
0.52637 | 0.0379 | 0.46203 | 700 | 40 | 2.653 | 9.984
0.55363 | 0 | 0.41332 | 700 | 40 | 0 | 15.363
0.55187 | 0 | 0.47145 | 700 | 40 | 0 | 15.187
0.54621 | 0 | 0.5258 | 700 | 40 | 0 | 14.621
0.53575 | 0 | 0.56903 | 700 | 40 | 0 | 13.575
0.51011 | 0 | 0.59989 | 700 | 40 | 0 | 11.011
0.47869 | 0 | 0.62558 | 700 | 40 | 0 | 7.869
0.44533 | 0 | 0.57981 | 700 | 40 | 0 | 4.533
0.42893 | 0 | 0.57042 | 700 | 40 | 0 | 2.893
0.41756 | 0 | 0.56227 | 700 | 40 | 0 | 1.756
0.41297 | 0 | 0.55871 | 700 | 40 | 0 | 1.297
0.41769 | 0 | 0.53179 | 700 | 40 | 0 | 1.769
0.43258 | 0 | 0.48297 | 700 | 40 | 0 | 3.258
0.47256 | 0 | 0.45222 | 700 | 40 | 0 | 7.256
0.51774 | 0.0135 | 0.44422 | 700 | 40 | 0.945 | 10.829
0.51798 | 0.3451 | 0.43754 | 700 | 40 | 11.798 | 0
0.51958 | 0.8061 | 0.3604 | 700 | 40 | 11.958 | 0
0.52104 | 0.8548 | 0.30477 | 700 | 40 | 12.104 | 0
0.52162 | 0.8252 | 0.23165 | 700 | 40 | 12.162 | 0
0.51883 | 0.8042 | 0.1515 | 700 | 40 | 11.883 | 0
0.51798 | 0.8226 | 0.11148 | 700 | 40 | 11.798 | 0
0.51809 | 0.7872 | 0.09093 | 700 | 40 | 11.809 | 0
0.51615 | 0.7011 | 0.07853 | 700 | 40 | 11.615 | 0
0.51704 | 0.4714 | 0.0725 | 700 | 40 | 11.704 | 0
0.51812 | 0.0551 | 0.07756 | 695.1474 | 40 | 3.857 | 3.1024
0.54369 | 0 | 0.10252 | 684.8792 | 40 | 0 | 4.1008
0.53671 | 0 | 0.14192 | 676.885 | 40 | 0 | 5.6768
0.52944 | 0 | 0.18232 | 671.2338 | 40 | 0 | 7.2928
0.52162 | 0 | 0.20774 | 667.3814 | 40 | 0 | 8.3096
0.50722 | 0 | 0.22779 | 665.771 | 40 | 0 | 9.1116
0.48671 | 0 | 0.24297 | 666.8188 | 40 | 0 | 9.7188
0.46213 | 0 | 0.24726 | 670.4962 | 40 | 0 | 9.8904
0.44903 | 0 | 0.24142 | 675.25 | 40 | 0 | 9.6568
0.4409 | 0 | 0.23227 | 680.4508 | 40 | 0 | 9.2908
0.4389 | 0 | 0.22138 | 685.416 | 40 | 0 | 8.8552
0.44138 | 0 | 0.20542 | 689.4948 | 40 | 0 | 8.2168
0.4513 | 0 | 0.19816 | 692.2912 | 40 | 0 | 7.9264
0.47049 | 0 | 0.21299 | 693.7618 | 40 | 0 | 8.5196
0.50147 | 0.0147 | 0.22199 | 693.5234 | 40 | 1.029 | 8.8796
0.52253 | 0.3483 | 0.20195 | 700 | 40 | 18.7296 | 0
0.52571 | 0.7859 | 0.16973 | 700 | 40 | 12.571 | 0
0.52009 | 0.8225 | 0.14192 | 700 | 40 | 12.009 | 0
0.50921 | 0.8129 | 0.15486 | 700 | 40 | 10.921 | 0
0.50083 | 0.7864 | 0.16757 | 700 | 40 | 10.083 | 0
0.49555 | 0.7576 | 0.19283 | 700 | 40 | 9.555 | 0
0.48946 | 0.7434 | 0.22856 | 700 | 40 | 8.946 | 0
0.48596 | 0.5848 | 0.23679 | 700 | 40 | 8.596 | 0
0.48793 | 0.4249 | 0.24915 | 700 | 40 | 8.793 | 0
0.49155 | 0.0526 | 0.25556 | 700 | 40 | 3.682 | 5.473
0.51961 | 0 | 0.33575 | 700 | 40 | 0 | 11.961
0.519 | 0 | 0.48598 | 700 | 40 | 0 | 11.9
0.51448 | 0 | 0.59062 | 700 | 40 | 0 | 11.448
0.51055 | 0 | 0.62318 | 700 | 40 | 0 | 11.055
0.50032 | 0 | 0.61515 | 700 | 40 | 0 | 10.032
0.48202 | 0 | 0.60839 | 700 | 40 | 0 | 8.202
0.4633 | 0 | 0.60997 | 700 | 40 | 0 | 6.33
0.44912 | 0 | 0.59981 | 700 | 40 | 0 | 4.912
0.44023 | 0 | 0.59452 | 700 | 40 | 0 | 4.023
0.43626 | 0 | 0.59908 | 700 | 40 | 0 | 3.626
0.43475 | 0 | 0.56961 | 700 | 40 | 0 | 3.475
0.43761 | 0 | 0.56068 | 700 | 40 | 0 | 3.761
0.44797 | 0 | 0.52627 | 700 | 40 | 0 | 4.797
0.46778 | 0.0106 | 0.56582 | 700 | 40 | 0.742 | 6.036
0.48147 | 0.1915 | 0.56621 | 700 | 40 | 8.147 | 0
0.4927 | 0.4748 | 0.51313 | 700 | 40 | 9.27 | 0
0.49486 | 0.6074 | 0.44233 | 700 | 40 | 9.486 | 0
0.48839 | 0.6032 | 0.44372 | 700 | 40 | 8.839 | 0
0.48902 | 0.6368 | 0.46489 | 700 | 40 | 8.902 | 0
0.49094 | 0.6234 | 0.50637 | 700 | 40 | 9.094 | 0
0.49204 | 0.5621 | 0.56432 | 700 | 40 | 9.204 | 0
0.4922 | 0.3722 | 0.57057 | 700 | 40 | 9.22 | 0
0.49688 | 0.1726 | 0.54095 | 700 | 40 | 9.688 | 0
0.50578 | 0.024 | 0.48675 | 700 | 40 | 1.68 | 8.898
0.54354 | 0.0023 | 0.49884 | 700 | 40 | 0.161 | 14.193
0.54609 | 0 | 0.56192 | 700 | 40 | 0 | 14.609
0.5424 | 0 | 0.61998 | 700 | 40 | 0 | 14.24
0.53037 | 0 | 0.64061 | 700 | 40 | 0 | 13.037
0.50231 | 0 | 0.60769 | 700 | 40 | 0 | 10.231
0.47008 | 0 | 0.58714 | 700 | 40 | 0 | 7.008
0.43906 | 0 | 0.55315 | 700 | 40 | 0 | 3.906
0.41882 | 0 | 0.50858 | 700 | 40 | 0 | 1.882
0.40967 | 0 | 0.48891 | 700 | 40 | 0 | 0.967
0.40688 | 0 | 0.49506 | 700 | 40 | 0 | 0.688
0.40869 | 0 | 0.50494 | 700 | 40 | 0 | 0.869
0.42327 | 0 | 0.48721 | 700 | 40 | 0 | 2.327
0.46223 | 0 | 0.47636 | 700 | 40 | 0 | 6.223
0.50709 | 0.0014 | 0.4616 | 700 | 40 | 0.098 | 10.611
0.50781 | 0.0446 | 0.456 | 700 | 40 | 3.122 | 7.659
0.51762 | 0.0915 | 0.4151 | 700 | 40 | 6.405 | 5.357
0.52637 | 0.1394 | 0.41718 | 700 | 40 | 9.758 | 2.879
0.53764 | 0.3346 | 0.44662 | 700 | 40 | 13.764 | 0
0.54333 | 0.2823 | 0.4504 | 700 | 40 | 14.333 | 0
0.55176 | 0.2049 | 0.42649 | 700 | 40 | 14.343 | 0.833
0.55972 | 0.1673 | 0.40872 | 700 | 40 | 11.711 | 4.261
0.55839 | 0.0966 | 0.39976 | 700 | 40 | 6.762 | 9.077
0.56184 | 0.0393 | 0.39771 | 700 | 40 | 2.751 | 13.433
0.56837 | 0.0025 | 0.44291 | 700 | 40 | 0.175 | 16.662
0.59951 | 0 | 0.41135 | 696.503 | 40 | 0 | 16.454
0.60033 | 0 | 0.3558 | 690.702 | 40 | 0 | 14.232
0.59133 | 0 | 0.35897 | 685.9278 | 40 | 0 | 14.3588
0.57857 | 0 | 0.42162 | 684.9356 | 40 | 0 | 16.8648
0.55274 | 0 | 0.41815 | 686.3876 | 40 | 0 | 16.726
0.51659 | 0 | 0.42216 | 691.615 | 40 | 0 | 16.8864
0.48811 | 0 | 0.37805 | 697.926 | 40 | 0 | 15.122
0.47297 | 0 | 0.36612 | 700 | 40 | 0 | 9.371
0.4629 | 0 | 0.33066 | 700 | 40 | 0 | 6.29
0.4587 | 0 | 0.26143 | 700 | 40 | 0 | 5.87
0.466 | 0 | 0.23795 | 700 | 40 | 0 | 6.6
0.48764 | 0 | 0.23567 | 700 | 40 | 0 | 8.764
0.5318 | 0 | 0.24092 | 696.4568 | 40 | 0 | 9.6368
0.58388 | 0.0002 | 0.23169 | 687.3504 | 40 | 0.014 | 9.2676
0.5917 | 0.0216 | 0.23385 | 679.0464 | 40 | 1.512 | 9.354
0.59939 | 0.097 | 0.2206 | 674.7214 | 40 | 6.79 | 8.824
0.60606 | 0.1775 | 0.2099 | 674.9364 | 40 | 12.425 | 8.396
0.60922 | 0.3477 | 0.18735 | 685.8474 | 40 | 31.833 | 0
0.60658 | 0.4686 | 0.19403 | 700 | 40 | 34.8106 | 0
0.60053 | 0.5279 | 0.19237 | 700 | 40 | 20.053 | 0
0.59137 | 0.453 | 0.1892 | 700 | 40 | 19.137 | 0
0.5824 | 0.446 | 0.19488 | 700 | 40 | 18.24 | 0
0.58468 | 0.3284 | 0.19998 | 700 | 40 | 18.468 | 0
0.59876 | 0.0412 | 0.20751 | 691.3084 | 40 | 2.884 | 8.3004
0.64365 | 0 | 0.24239 | 676.639 | 40 | 0 | 9.6956
0.65254 | 0 | 0.27893 | 662.5422 | 40 | 0 | 11.1572
0.6481 | 0 | 0.28878 | 649.2834 | 40 | 0 | 11.5512
0.64055 | 0 | 0.30103 | 637.2696 | 40 | 0 | 12.0412
0.61566 | 0 | 0.29728 | 627.5948 | 40 | 0 | 11.8912
0.58405 | 0 | 0.31246 | 621.6882 | 40 | 0 | 12.4984
0.55761 | 0 | 0.31131 | 618.3796 | 40 | 0 | 12.4524
0.54716 | 0 | 0.32818 | 616.7908 | 40 | 0 | 13.1272
0.54438 | 0 | 0.33769 | 615.8604 | 40 | 0 | 13.5076
0.54563 | 0 | 0.33727 | 614.7882 | 40 | 0 | 13.4908
0.55506 | 0 | 0.35341 | 613.4186 | 40 | 0 | 14.1364
0.57924 | 0 | 0.34321 | 609.223 | 40 | 0 | 13.7284
0.62465 | 0 | 0.33248 | 600.0572 | 40 | 0 | 13.2992
0.67162 | 0.0048 | 0.32255 | 586.1332 | 40 | 0.336 | 12.902
0.65824 | 0.1102 | 0.31055 | 580.4452 | 40 | 7.714 | 12.422
0.64307 | 0.2479 | 0.27884 | 584.6448 | 40 | 17.353 | 11.1536
0.62626 | 0.3282 | 0.27727 | 596.0836 | 40 | 34.0648 | 0
0.6016 | 0.4211 | 0.27646 | 616.459 | 40 | 40.5354 | 0
0.57866 | 0.4739 | 0.30257 | 643.8688 | 40 | 45.2758 | 0
0.55834 | 0.5103 | 0.32657 | 676.8186 | 40 | 48.7838 | 0
0.54416 | 0.5097 | 0.35211 | 700 | 40 | 37.5974 | 0
0.53147 | 0.5614 | 0.36089 | 700 | 40 | 13.147 | 0
0.53312 | 0.3159 | 0.36457 | 700 | 40 | 13.312 | 0
0.54959 | 0.0219 | 0.34471 | 700 | 40 | 1.533 | 13.426
0.60581 | 0 | 0.38193 | 694.6962 | 40 | 0 | 15.2772
0.6216 | 0 | 0.47203 | 691.4174 | 40 | 0 | 18.8812
0.62749 | 0 | 0.56244 | 691.166 | 40 | 0 | 22.4976
0.62871 | 0 | 0.59084 | 691.9286 | 40 | 0 | 23.6336
0.61004 | 0 | 0.60453 | 695.1058 | 40 | 0 | 24.1812
0.57979 | 0 | 0.60108 | 700 | 40 | 0 | 22.8732
0.55745 | 0 | 0.59118 | 700 | 40 | 0 | 15.745
0.54783 | 0 | 0.59225 | 700 | 40 | 0 | 14.783
0.54495 | 0 | 0.58494 | 700 | 40 | 0 | 14.495
0.54421 | 0 | 0.53829 | 700 | 40 | 0 | 14.421
0.55203 | 0 | 0.5418 | 700 | 40 | 0 | 15.203
0.57598 | 0 | 0.54583 | 700 | 40 | 0 | 17.598
0.62855 | 0 | 0.49028 | 696.7562 | 40 | 0 | 19.6112
0.67592 | 0.0055 | 0.48069 | 688.7768 | 40 | 0.385 | 19.2276
0.66141 | 0.2567 | 0.43876 | 698.1552 | 40 | 17.969 | 17.5504
0.6373 | 0.6865 | 0.33238 | 700 | 40 | 25.5748 | 0
0.60619 | 0.7367 | 0.27352 | 700 | 40 | 20.619 | 0
0.57834 | 0.7728 | 0.23821 | 700 | 40 | 17.834 | 0
0.55332 | 0.7976 | 0.18662 | 700 | 40 | 15.332 | 0
0.53216 | 0.8149 | 0.13956 | 700 | 40 | 13.216 | 0
0.52029 | 0.7952 | 0.11684 | 700 | 40 | 12.029 | 0
0.51197 | 0.6972 | 0.09379 | 700 | 40 | 11.197 | 0
0.51291 | 0.4765 | 0.09382 | 700 | 40 | 11.291 | 0
0.52456 | 0.0662 | 0.08583 | 695.6112 | 40 | 4.634 | 3.4332
0.56979 | 0.0024 | 0.11315 | 683.3262 | 40 | 0.168 | 4.526
0.57833 | 0 | 0.19758 | 673.3964 | 40 | 0 | 7.9032
0.57968 | 0 | 0.23449 | 664.808 | 40 | 0 | 9.3796
0.57548 | 0 | 0.25313 | 657.3852 | 40 | 0 | 10.1252
0.55539 | 0 | 0.26447 | 652.425 | 40 | 0 | 10.5788
0.52457 | 0 | 0.2755 | 650.988 | 40 | 0 | 11.02
0.50115 | 0 | 0.27572 | 651.9018 | 40 | 0 | 11.0288
0.4885 | 0 | 0.28707 | 654.5346 | 40 | 0 | 11.4828
0.48106 | 0 | 0.28545 | 657.8466 | 40 | 0 | 11.418
0.48047 | 0 | 0.29097 | 661.4384 | 40 | 0 | 11.6388
0.48764 | 0 | 0.30416 | 664.8408 | 40 | 0 | 12.1664
0.51075 | 0 | 0.32114 | 666.6114 | 40 | 0 | 12.8456
0.55477 | 0 | 0.33639 | 664.59 | 40 | 0 | 13.4556
0.60186 | 0.0079 | 0.35776 | 659.2674 | 40 | 0.553 | 14.3104
0.59024 | 0.2995 | 0.39097 | 676.8472 | 40 | 36.6038 | 0
0.56943 | 0.7847 | 0.36948 | 700 | 40 | 40.0958 | 0
0.55206 | 0.8349 | 0.27238 | 700 | 40 | 15.206 | 0
0.53514 | 0.8241 | 0.248 | 700 | 40 | 13.514 | 0
0.52193 | 0.809 | 0.30679 | 700 | 40 | 12.193 | 0
0.51451 | 0.7847 | 0.31381 | 700 | 40 | 11.451 | 0
0.51466 | 0.6896 | 0.32294 | 700 | 40 | 11.466 | 0
0.51031 | 0.6666 | 0.33748 | 700 | 40 | 11.031 | 0
0.51106 | 0.4329 | 0.30904 | 700 | 40 | 11.106 | 0
0.51549 | 0.0633 | 0.21776 | 700 | 40 | 4.431 | 7.118
0.54508 | 0.0047 | 0.16911 | 692.5854 | 40 | 0.329 | 6.7644
0.53929 | 0 | 0.16885 | 685.4104 | 40 | 0 | 6.754
0.53489 | 0 | 0.18966 | 679.5078 | 40 | 0 | 7.5864
0.5279 | 0 | 0.22967 | 675.9046 | 40 | 0 | 9.1868
0.51466 | 0 | 0.23173 | 673.7078 | 40 | 0 | 9.2692
0.49475 | 0 | 0.2702 | 675.0408 | 40 | 0 | 10.808
0.47492 | 0 | 0.256 | 677.7888 | 40 | 0 | 10.24
0.46172 | 0 | 0.20976 | 680.0072 | 40 | 0 | 8.3904
0.45614 | 0 | 0.19552 | 682.214 | 40 | 0 | 7.8208
0.45525 | 0 | 0.15969 | 683.0766 | 40 | 0 | 6.3876
0.46317 | 0 | 0.13099 | 681.9992 | 40 | 0 | 5.2396
0.47705 | 0 | 0.13448 | 679.6734 | 40 | 0 | 5.3792
0.49565 | 0 | 0.14815 | 676.0344 | 40 | 0 | 5.926
0.52629 | 0.0085 | 0.17069 | 670.828 | 40 | 0.595 | 6.8276
0.54108 | 0.3163 | 0.17126 | 685.7114 | 40 | 28.9914 | 0
0.53883 | 0.7995 | 0.14755 | 700 | 40 | 28.1716 | 0
0.52328 | 0.8539 | 0.11337 | 700 | 40 | 12.328 | 0
0.51 | 0.8487 | 0.14519 | 700 | 40 | 11 | 0
0.49924 | 0.8365 | 0.1897 | 700 | 40 | 9.924 | 0
0.49319 | 0.8474 | 0.23324 | 700 | 40 | 9.319 | 0
0.49139 | 0.87 | 0.28583 | 700 | 40 | 9.139 | 0
0.49138 | 0.8233 | 0.26272 | 700 | 40 | 9.138 | 0
0.49261 | 0.5203 | 0.25521 | 700 | 40 | 9.261 | 0
0.49637 | 0.0662 | 0.23421 | 700 | 40 | 4.634 | 5.003
0.52559 | 0.0035 | 0.30476 | 699.8764 | 40 | 0.245 | 12.1904
0.52069 | 0 | 0.38736 | 700 | 40 | 0 | 12.1926
0.51539 | 0 | 0.45464 | 700 | 40 | 0 | 11.539
0.50996 | 0 | 0.49104 | 700 | 40 | 0 | 10.996
0.49873 | 0 | 0.52087 | 700 | 40 | 0 | 9.873
0.48175 | 0 | 0.53552 | 700 | 40 | 0 | 8.175
0.46236 | 0 | 0.52673 | 700 | 40 | 0 | 6.236
0.44766 | 0 | 0.52398 | 700 | 40 | 0 | 4.766
0.43934 | 0 | 0.51328 | 700 | 40 | 0 | 3.934
0.43288 | 0 | 0.50449 | 700 | 40 | 0 | 3.288
0.43128 | 0 | 0.47928 | 700 | 40 | 0 | 3.128
0.43622 | 0 | 0.49664 | 700 | 40 | 0 | 3.622
0.44781 | 0 | 0.47812 | 700 | 40 | 0 | 4.781
0.45906 | 0.0049 | 0.45885 | 700 | 40 | 0.343 | 5.563
0.47334 | 0.2726 | 0.45735 | 700 | 40 | 7.334 | 0
0.49039 | 0.7428 | 0.38909 | 700 | 40 | 9.039 | 0
0.49869 | 0.8124 | 0.34548 | 700 | 40 | 9.869 | 0
0.50154 | 0.8309 | 0.35134 | 700 | 40 | 10.154 | 0
0.5085 | 0.8198 | 0.43034 | 700 | 40 | 10.85 | 0
0.51454 | 0.8222 | 0.45795 | 700 | 40 | 11.454 | 0
0.51694 | 0.8333 | 0.42173 | 700 | 40 | 11.694 | 0
0.52348 | 0.7806 | 0.44739 | 700 | 40 | 12.348 | 0
0.52689 | 0.4968 | 0.48743 | 700 | 40 | 12.689 | 0
0.53069 | 0.0695 | 0.48807 | 700 | 40 | 4.865 | 8.204
0.56302 | 0.0047 | 0.51685 | 700 | 40 | 0.329 | 15.973
0.56825 | 0 | 0.53071 | 700 | 40 | 0 | 16.825
0.56388 | 0 | 0.51955 | 700 | 40 | 0 | 16.388
0.55378 | 0 | 0.53296 | 700 | 40 | 0 | 15.378
0.52885 | 0 | 0.50295 | 700 | 40 | 0 | 12.885
0.50087 | 0 | 0.44589 | 700 | 40 | 0 | 10.087
0.47193 | 0 | 0.44067 | 700 | 40 | 0 | 7.193
0.45535 | 0 | 0.43308 | 700 | 40 | 0 | 5.535
0.44735 | 0 | 0.41768 | 700 | 40 | 0 | 4.735
0.44612 | 0 | 0.40949 | 700 | 40 | 0 | 4.612
0.45257 | 0 | 0.4134 | 700 | 40 | 0 | 5.257
0.47433 | 0 | 0.41276 | 700 | 40 | 0 | 7.433
0.51773 | 0 | 0.41381 | 700 | 40 | 0 | 11.773
0.57045 | 0.0023 | 0.38413 | 698.4812 | 40 | 0.161 | 15.3652
0.57955 | 0.183 | 0.31982 | 700 | 40 | 12.81 | 6.6638
0.58933 | 0.5907 | 0.29875 | 700 | 40 | 18.933 | 0
0.59739 | 0.6944 | 0.33391 | 700 | 40 | 19.739 | 0
0.60434 | 0.7474 | 0.36208 | 700 | 40 | 20.434 | 0
0.60088 | 0.7669 | 0.39187 | 700 | 40 | 20.088 | 0
0.59035 | 0.7755 | 0.40885 | 700 | 40 | 19.035 | 0
0.5827 | 0.7751 | 0.48353 | 700 | 40 | 18.27 | 0
0.57692 | 0.7496 | 0.50385 | 700 | 40 | 17.692 | 0
0.5843 | 0.4897 | 0.54761 | 700 | 40 | 18.43 | 0
0.59923 | 0.0638 | 0.56305 | 700 | 40 | 4.466 | 15.457
0.64528 | 0 | 0.52147 | 696.3308 | 40 | 0 | 20.8588
0.65436 | 0 | 0.55881 | 693.2472 | 40 | 0 | 22.3524
0.65439 | 0 | 0.59938 | 691.7834 | 40 | 0 | 23.9752
0.64963 | 0 | 0.59126 | 690.4708 | 40 | 0 | 23.6504
0.62505 | 0 | 0.58875 | 691.5158 | 40 | 0 | 23.55
0.59229 | 0 | 0.56963 | 695.072 | 40 | 0 | 22.7852
0.56817 | 0 | 0.5573 | 700 | 40 | 0 | 21.745
0.55441 | 0 | 0.53845 | 700 | 40 | 0 | 15.441
0.55044 | 0 | 0.50678 | 700 | 40 | 0 | 15.044
0.55375 | 0 | 0.47357 | 700 | 40 | 0 | 15.375
0.566 | 0 | 0.46576 | 700 | 40 | 0 | 16.6
0.59567 | 0 | 0.4575 | 698.733 | 40 | 0 | 18.3
0.65055 | 0 | 0.41655 | 690.34 | 40 | 0 | 16.662
0.70668 | 0.0052 | 0.37339 | 674.9716 | 40 | 0.364 | 14.9356
0.702 | 0.2455 | 0.33842 | 675.4934 | 40 | 17.185 | 13.5368
0.68223 | 0.7165 | 0.28072 | 700 | 40 | 52.7296 | 0
0.65995 | 0.814 | 0.22137 | 700 | 40 | 25.995 | 0
0.63362 | 0.8151 | 0.21096 | 700 | 40 | 23.362 | 0
0.60646 | 0.7976 | 0.21817 | 700 | 40 | 20.646 | 0
0.5879 | 0.8192 | 0.22039 | 700 | 40 | 18.79 | 0
0.57116 | 0.849 | 0.23136 | 700 | 40 | 17.116 | 0
0.5592 | 0.8603 | 0.25559 | 700 | 40 | 15.92 | 0
0.55987 | 0.5849 | 0.25033 | 700 | 40 | 15.987 | 0
0.58321 | 0.0775 | 0.19274 | 694.8136 | 40 | 5.425 | 7.7096
0.6419 | 0 | 0.13268 | 675.9308 | 40 | 0 | 5.3072
0.65652 | 0 | 0.11465 | 654.8648 | 40 | 0 | 4.586
0.66841 | 0 | 0.12742 | 633.1206 | 40 | 0 | 5.0968
0.6708 | 0 | 0.14372 | 611.7894 | 40 | 0 | 5.7488
0.65395 | 0 | 0.15116 | 592.4408 | 40 | 0 | 6.0464
0.62657 | 0 | 0.16029 | 576.1954 | 40 | 0 | 6.4116
0.60583 | 0 | 0.19883 | 563.5656 | 40 | 0 | 7.9532
0.59814 | 0 | 0.2474 | 553.6476 | 40 | 0 | 9.896
0.59823 | 0 | 0.29139 | 545.4802 | 40 | 0 | 11.6556
0.60458 | 0 | 0.31948 | 537.8014 | 40 | 0 | 12.7792
0.61893 | 0 | 0.30998 | 528.3076 | 40 | 0 | 12.3992
0.64937 | 0 | 0.2906 | 514.9946 | 40 | 0 | 11.624
0.70243 | 0 | 0.27719 | 495.8392 | 40 | 0 | 11.0876
0.75459 | 0.0088 | 0.27264 | 471.9018 | 40 | 0.616 | 10.9056
0.73806 | 0.3452 | 0.26997 | 473.0586 | 40 | 24.164 | 10.7988
0.69284 | 0.909 | 0.18639 | 514.8602 | 40 | 71.0856 | 0
0.6485 | 0.9641 | 0.09804 | 561.4188 | 40 | 71.4086 | 0
0.61111 | 0.9693 | 0.09365 | 611.9048 | 40 | 71.597 | 0
0.57326 | 0.9606 | 0.10717 | 666.1076 | 40 | 71.5288 | 0
0.55005 | 0.9696 | 0.10063 | 700 | 40 | 48.8974 | 0
0.53389 | 1.002 | 0.09493 | 700 | 40 | 13.389 | 0
0.52398 | 0.9813 | 0.07532 | 700 | 40 | 12.398 | 0
0.52335 | 0.6585 | 0.05928 | 700 | 40 | 12.335 | 0
0.5397 | 0.0817 | 0.05875 | 694.099 | 40 | 5.719 | 2.35
0.59876 | 0 | 0.10251 | 678.3234 | 40 | 0 | 4.1004
0.62072 | 0 | 0.18489 | 663.647 | 40 | 0 | 7.3956
0.63302 | 0 | 0.2761 | 651.389 | 40 | 0 | 11.044
0.63717 | 0 | 0.32643 | 640.7292 | 40 | 0 | 13.0572
0.6283 | 0 | 0.39228 | 633.5904 | 40 | 0 | 15.6912
0.60682 | 0 | 0.42207 | 629.7912 | 40 | 0 | 16.8828
0.58752 | 0 | 0.46553 | 629.6604 | 40 | 0 | 18.6212
0.58357 | 0 | 0.49438 | 631.0786 | 40 | 0 | 19.7752
0.5822 | 0 | 0.48447 | 632.2374 | 40 | 0 | 19.3788
0.58831 | 0 | 0.47936 | 632.5808 | 40 | 0 | 19.1744
0.60266 | 0 | 0.4842 | 631.6828 | 40 | 0 | 19.368
0.63533 | 0 | 0.4726 | 627.0538 | 40 | 0 | 18.904
0.69039 | 0 | 0.47485 | 617.0088 | 40 | 0 | 18.994
0.74152 | 0.006 | 0.47879 | 602.4284 | 40 | 0.42 | 19.1516
0.72712 | 0.2035 | 0.48214 | 603.247 | 40 | 14.245 | 19.2856
0.68385 | 0.6292 | 0.43815 | 636.432 | 40 | 61.57 | 0
0.64385 | 0.796 | 0.39875 | 683.717 | 40 | 71.67 | 0
0.60602 | 0.7567 | 0.46069 | 700 | 40 | 36.885 | 0
0.57418 | 0.7506 | 0.53946 | 700 | 40 | 17.418 | 0
0.55539 | 0.759 | 0.55757 | 700 | 40 | 15.539 | 0
0.54176 | 0.6718 | 0.53424 | 700 | 40 | 14.176 | 0
0.5316 | 0.51 | 0.51989 | 700 | 40 | 13.16 | 0
0.53456 | 0.2398 | 0.52169 | 700 | 40 | 13.456 | 0
0.55163 | 0.0248 | 0.45119 | 700 | 40 | 1.736 | 13.427
0.60332 | 0 | 0.47556 | 698.6904 | 40 | 0 | 19.0224
0.61319 | 0 | 0.55836 | 699.7058 | 40 | 0 | 22.3344
0.61975 | 0 | 0.60817 | 700 | 40 | 0 | 22.2692
0.6175 | 0 | 0.63608 | 700 | 40 | 0 | 21.75
0.6005 | 0 | 0.63559 | 700 | 40 | 0 | 20.05
0.57026 | 0 | 0.60798 | 700 | 40 | 0 | 17.026
0.53994 | 0 | 0.58972 | 700 | 40 | 0 | 13.994
0.5268 | 0 | 0.54833 | 700 | 40 | 0 | 12.68
0.51816 | 0 | 0.51899 | 700 | 40 | 0 | 11.816
0.51224 | 0 | 0.48785 | 700 | 40 | 0 | 11.224
0.51611 | 0 | 0.45543 | 700 | 40 | 0 | 11.611
0.53381 | 0 | 0.41505 | 700 | 40 | 0 | 13.381
0.56845 | 0 | 0.38954 | 698.7366 | 40 | 0 | 15.5816
0.60823 | 0.0007 | 0.39657 | 693.8254 | 40 | 0.049 | 15.8628
0.6093 | 0.2269 | 0.40186 | 700 | 40 | 15.883 | 11.2216
0.60874 | 0.7189 | 0.37651 | 700 | 40 | 20.874 | 0
0.60956 | 0.823 | 0.32858 | 700 | 40 | 20.956 | 0
0.60615 | 0.8354 | 0.33462 | 700 | 40 | 20.615 | 0
0.59644 | 0.8221 | 0.32557 | 700 | 40 | 19.644 | 0
0.58856 | 0.8377 | 0.32369 | 700 | 40 | 18.856 | 0
0.58226 | 0.8631 | 0.33868 | 700 | 40 | 18.226 | 0
0.58081 | 0.8393 | 0.33661 | 700 | 40 | 18.081 | 0
0.58047 | 0.5771 | 0.3403 | 700 | 40 | 18.047 | 0
0.58654 | 0.0788 | 0.31791 | 699.5784 | 40 | 5.516 | 12.7164
0.61168 | 0 | 0.26581 | 689.0428 | 40 | 0 | 10.6324
0.60404 | 0 | 0.26911 | 679.4032 | 40 | 0 | 10.7644
0.59526 | 0 | 0.2344 | 669.2532 | 40 | 0 | 9.376
0.58401 | 0 | 0.20127 | 658.903 | 40 | 0 | 8.0508
0.5658 | 0 | 0.15676 | 648.5934 | 40 | 0 | 6.2704
0.5439 | 0 | 0.14507 | 640.0062 | 40 | 0 | 5.8028
0.51727 | 0 | 0.17794 | 635.3968 | 40 | 0 | 7.1176
0.49566 | 0 | 0.21085 | 634.2648 | 40 | 0 | 8.434
0.486 | 0 | 0.22576 | 634.6952 | 40 | 0 | 9.0304
0.47966 | 0 | 0.20724 | 635.0188 | 40 | 0 | 8.2896
0.48077 | 0 | 0.20931 | 635.3142 | 40 | 0 | 8.3724
0.48897 | 0 | 0.20243 | 634.5144 | 40 | 0 | 8.0972
0.50583 | 0 | 0.15533 | 630.1446 | 40 | 0 | 6.2132
0.52908 | 0.0018 | 0.12892 | 622.5194 | 40 | 0.126 | 5.1568
0.55261 | 0.2641 | 0.1113 | 630.1974 | 40 | 22.939 | 0
0.56574 | 0.7699 | 0.08279 | 670.828 | 40 | 57.2046 | 0
0.56643 | 0.8563 | 0.04091 | 700 | 40 | 45.815 | 0
0.5594 | 0.907 | 0.04192 | 700 | 40 | 15.94 | 0
0.54589 | 0.8926 | 0.05349 | 700 | 40 | 14.589 | 0
0.53085 | 0.921 | 0.05751 | 700 | 40 | 13.085 | 0
0.51712 | 0.9501 | 0.04504 | 700 | 40 | 11.712 | 0
0.51152 | 0.9264 | 0.03587 | 700 | 40 | 11.152 | 0
0.51164 | 0.6376 | 0.0204 | 700 | 40 | 11.164 | 0
0.52366 | 0.0909 | 0.0145 | 694.577 | 40 | 6.363 | 0.58
0.55674 | 0.0047 | 0.02325 | 680.162 | 40 | 0.329 | 0.93
0.56246 | 0 | 0.06724 | 666.6056 | 40 | 0 | 2.6896
0.5622 | 0 | 0.12471 | 655.374 | 40 | 0 | 4.9884
0.55942 | 0 | 0.1779 | 646.548 | 40 | 0 | 7.116
0.55359 | 0 | 0.19793 | 639.1062 | 40 | 0 | 7.9172
0.5388 | 0 | 0.21881 | 633.9786 | 40 | 0 | 8.7524
0.52378 | 0 | 0.25142 | 631.6574 | 40 | 0 | 10.0568
0.5137 | 0 | 0.24586 | 630.1218 | 40 | 0 | 9.8344
0.50898 | 0 | 0.22956 | 628.4062 | 40 | 0 | 9.1824
0.50941 | 0 | 0.21205 | 625.9472 | 40 | 0 | 8.482
0.51403 | 0 | 0.17178 | 621.4154 | 40 | 0 | 6.8712
0.52699 | 0 | 0.15428 | 614.8876 | 40 | 0 | 6.1712
0.54286 | 0.0001 | 0.11852 | 605.3494 | 40 | 0.007 | 4.7408
0.57033 | 0.0055 | 0.09631 | 592.5538 | 40 | 0.385 | 3.8524
0.5891 | 0.3115 | 0.07073 | 598.278 | 40 | 24.6342 | 0
0.58544 | 0.8957 | 0.05447 | 644.6118 | 40 | 64.8778 | 0
0.57053 | 0.9642 | 0.03107 | 696.2956 | 40 | 68.7368 | 0
0.54848 | 0.9527 | 0.01886 | 700 | 40 | 18.5524 | 0
0.52807 | 0.942 | 0.03125 | 700 | 40 | 12.807 | 0
0.50595 | 0.95 | 0.06803 | 700 | 40 | 10.595 | 0
0.48964 | 0.948 | 0.07111 | 700 | 40 | 8.964 | 0
0.47952 | 0.7916 | 0.07209 | 700 | 40 | 7.952 | 0
0.47678 | 0.3899 | 0.08166 | 700 | 40 | 7.678 | 0
0.49013 | 0.0361 | 0.08388 | 696.8692 | 40 | 2.527 | 3.3552
0.53371 | 0.0043 | 0.137 | 689.2792 | 40 | 0.301 | 5.48
0.55064 | 0 | 0.22636 | 683.2696 | 40 | 0 | 9.0544
0.55697 | 0 | 0.27963 | 678.7578 | 40 | 0 | 11.1852
0.56028 | 0 | 0.32133 | 675.583 | 40 | 0 | 12.8532
0.55697 | 0 | 0.37395 | 674.844 | 40 | 0 | 14.958
0.543 | 0 | 0.41621 | 677.1924 | 40 | 0 | 16.6484
0.52794 | 0 | 0.43068 | 681.6256 | 40 | 0 | 17.2272
0.52038 | 0 | 0.4238 | 686.5396 | 40 | 0 | 16.952
0.5192 | 0 | 0.4155 | 691.2396 | 40 | 0 | 16.62
0.52595 | 0 | 0.40476 | 694.835 | 40 | 0 | 16.1904
0.53795 | 0 | 0.38455 | 696.422 | 40 | 0 | 15.382
0.56187 | 0 | 0.36832 | 694.9678 | 40 | 0 | 14.7328
0.60132 | 0 | 0.33598 | 688.275 | 40 | 0 | 13.4392
0.63919 | 0.0055 | 0.31347 | 677.2798 | 40 | 0.385 | 12.5388
0.64901 | 0.2277 | 0.30495 | 680.5158 | 40 | 15.939 | 12.198
0.62917 | 0.684 | 0.29018 | 700 | 40 | 42.4012 | 0
0.5957 | 0.7734 | 0.19748 | 700 | 40 | 19.57 | 0
0.56443 | 0.8055 | 0.12054 | 700 | 40 | 16.443 | 0
0.53365 | 0.8293 | 0.11341 | 700 | 40 | 13.365 | 0
0.51617 | 0.8688 | 0.13779 | 700 | 40 | 11.617 | 0
0.50364 | 0.8357 | 0.16213 | 700 | 40 | 10.364 | 0
0.49642 | 0.7353 | 0.20165 | 700 | 40 | 9.642 | 0
0.49689 | 0.4938 | 0.19823 | 700 | 40 | 9.689 | 0
0.49981 | 0.066 | 0.1805 | 700 | 40 | 4.62 | 5.361
0.53537 | 0.0021 | 0.22704 | 695.6916 | 40 | 0.147 | 9.0816
0.53947 | 0 | 0.31847 | 694.4834 | 40 | 0 | 12.7388
0.54088 | 0 | 0.44033 | 698.0086 | 40 | 0 | 17.6132
0.54103 | 0 | 0.50851 | 700 | 40 | 0 | 16.0944
0.53326 | 0 | 0.55975 | 700 | 40 | 0 | 13.326
0.52098 | 0 | 0.60336 | 700 | 40 | 0 | 12.098
0.50284 | 0 | 0.62864 | 700 | 40 | 0 | 10.284
0.49102 | 0 | 0.62932 | 700 | 40 | 0 | 9.102
0.4885 | 0 | 0.63596 | 700 | 40 | 0 | 8.85
0.49001 | 0 | 0.6354 | 700 | 40 | 0 | 9.001
0.49826 | 0 | 0.61004 | 700 | 40 | 0 | 9.826
0.51648 | 0 | 0.5706 | 700 | 40 | 0 | 11.648
0.54561 | 0 | 0.52432 | 700 | 40 | 0 | 14.561
0.57371 | 0.0069 | 0.52748 | 700 | 40 | 0.483 | 16.888
0.58518 | 0.218 | 0.50994 | 700 | 40 | 15.26 | 3.258
0.57265 | 0.6729 | 0.46366 | 700 | 40 | 17.265 | 0
0.54841 | 0.7642 | 0.37403 | 700 | 40 | 14.841 | 0
0.52311 | 0.8063 | 0.35927 | 700 | 40 | 12.311 | 0
0.50461 | 0.8004 | 0.36757 | 700 | 40 | 10.461 | 0
0.49398 | 0.8068 | 0.3605 | 700 | 40 | 9.398 | 0
0.48797 | 0.6586 | 0.38549 | 700 | 40 | 8.797 | 0
0.48363 | 0.3975 | 0.40528 | 700 | 40 | 8.363 | 0
0.48191 | 0.1734 | 0.38383 | 700 | 40 | 8.191 | 0
0.48398 | 0.0245 | 0.36054 | 700 | 40 | 1.715 | 6.683
0.51247 | 0 | 0.45663 | 700 | 40 | 0 | 11.247
0.50629 | 0 | 0.62533 | 700 | 40 | 0 | 10.629
0.497 | 0 | 0.67601 | 700 | 40 | 0 | 9.7
0.4899 | 0 | 0.66756 | 700 | 40 | 0 | 8.99
0.48195 | 0 | 0.65467 | 700 | 40 | 0 | 8.195
0.46916 | 0 | 0.66241 | 700 | 40 | 0 | 6.916
0.45333 | 0 | 0.63104 | 700 | 40 | 0 | 5.333
0.44283 | 0 | 0.61703 | 700 | 40 | 0 | 4.283
0.4376 | 0 | 0.61883 | 700 | 40 | 0 | 3.76
0.43517 | 0 | 0.61102 | 700 | 40 | 0 | 3.517
0.43745 | 0 | 0.61429 | 700 | 40 | 0 | 3.745
0.44589 | 0 | 0.59945 | 700 | 40 | 0 | 4.589
0.45952 | 0 | 0.53567 | 700 | 40 | 0 | 5.952
0.47688 | 0.0033 | 0.55381 | 700 | 40 | 0.231 | 7.457
0.48745 | 0.2184 | 0.51354 | 700 | 40 | 8.745 | 0
0.48999 | 0.6355 | 0.39409 | 700 | 40 | 8.999 | 0
0.48577 | 0.6794 | 0.30145 | 700 | 40 | 8.577 | 0
0.47826 | 0.7845 | 0.30889 | 700 | 40 | 7.826 | 0
0.47241 | 0.8214 | 0.32467 | 700 | 40 | 7.241 | 0
0.46332 | 0.7688 | 0.31877 | 700 | 40 | 6.332 | 0
0.45696 | 0.713 | 0.31408 | 700 | 40 | 5.696 | 0
0.45384 | 0.4281 | 0.30142 | 700 | 40 | 5.384 | 0
0.45117 | 0.159 | 0.28583 | 700 | 40 | 5.117 | 0
0.45089 | 0.0188 | 0.24868 | 700 | 40 | 1.316 | 3.773
0.47707 | 0.0042 | 0.24849 | 700 | 40 | 0.294 | 7.413
0.47787 | 0 | 0.30634 | 700 | 40 | 0 | 7.787
0.47521 | 0 | 0.33098 | 700 | 40 | 0 | 7.521
0.47018 | 0 | 0.3232 | 700 | 40 | 0 | 7.018
0.45979 | 0 | 0.33308 | 700 | 40 | 0 | 5.979
0.44156 | 0 | 0.32891 | 700 | 40 | 0 | 4.156
0.4209 | 0 | 0.29725 | 700 | 40 | 0 | 2.09
0.40541 | 0 | 0.28842 | 700 | 40 | 0 | 0.541
0.39742 | 0 | 0.24759 | 700 | 39.742 | 0 | 0
0.39553 | 0 | 0.2021 | 700 | 39.553 | 0 | 0
0.39869 | 0 | 0.15957 | 700 | 39.869 | 0 | 0
0.41214 | 0 | 0.13715 | 700 | 40 | 0 | 1.214
0.4358 | 0 | 0.13722 | 700 | 40 | 0 | 3.58
0.46273 | 0.001 | 0.14924 | 699.7666 | 40 | 0.07 | 5.9696
0.47473 | 0.0434 | 0.14335 | 700 | 40 | 3.038 | 4.6684
0.48807 | 0.1161 | 0.11694 | 700 | 40 | 8.127 | 0.68
0.49985 | 0.1824 | 0.07355 | 700 | 40 | 9.985 | 0
0.50552 | 0.2793 | 0.06942 | 700 | 40 | 10.552 | 0
0.50678 | 0.3549 | 0.09376 | 700 | 40 | 10.678 | 0
0.50602 | 0.3077 | 0.09395 | 700 | 40 | 10.602 | 0
0.50395 | 0.3226 | 0.10011 | 700 | 40 | 10.395 | 0
0.50015 | 0.2644 | 0.09823 | 700 | 40 | 10.015 | 0
0.49983 | 0.1966 | 0.09301 | 700 | 40 | 9.983 | 0
0.50155 | 0.0527 | 0.10571 | 697.7624 | 40 | 3.689 | 4.2284
0.53151 | 0 | 0.13219 | 689.899 | 40 | 0 | 5.2876
0.52721 | 0 | 0.20416 | 685.3444 | 40 | 0 | 8.1664
0.5173 | 0 | 0.26573 | 684.2436 | 40 | 0 | 10.6292
0.50504 | 0 | 0.30236 | 685.834 | 40 | 0 | 12.0944
0.48718 | 0 | 0.34484 | 690.9096 | 40 | 0 | 13.7936
0.4626 | 0 | 0.33391 | 698.006 | 40 | 0 | 13.3564
0.43705 | 0 | 0.32429 | 700 | 40 | 0 | 5.699
0.41903 | 0 | 0.31193 | 700 | 40 | 0 | 1.903
0.40611 | 0 | 0.3137 | 700 | 40 | 0 | 0.611
0.40313 | 0 | 0.29852 | 700 | 40 | 0 | 0.313
0.40413 | 0 | 0.29864 | 700 | 40 | 0 | 0.413
0.4142 | 0 | 0.28853 | 700 | 40 | 0 | 1.42
0.43733 | 0 | 0.3164 | 700 | 40 | 0 | 3.733
0.46401 | 0.0007 | 0.33579 | 700 | 40 | 0.049 | 6.352
0.47819 | 0.0441 | 0.3436 | 700 | 40 | 3.087 | 4.732
0.48714 | 0.1452 | 0.31419 | 700 | 40 | 8.714 | 0
0.49394 | 0.2931 | 0.33571 | 700 | 40 | 9.394 | 0
0.50088 | 0.4032 | 0.36539 | 700 | 40 | 10.088 | 0
0.49938 | 0.4357 | 0.38917 | 700 | 40 | 9.938 | 0
0.50061 | 0.3851 | 0.42436 | 700 | 40 | 10.061 | 0
0.50163 | 0.3265 | 0.48762 | 700 | 40 | 10.163 | 0
0.50221 | 0.2203 | 0.53439 | 700 | 40 | 10.221 | 0
0.49897 | 0.1593 | 0.56711 | 700 | 40 | 9.897 | 0
0.49777 | 0.0277 | 0.56012 | 700 | 40 | 1.939 | 7.838
0.52563 | 0 | 0.56301 | 700 | 40 | 0 | 12.563
0.52299 | 0 | 0.5898 | 700 | 40 | 0 | 12.299
0.51531 | 0 | 0.63394 | 700 | 40 | 0 | 11.531
0.50313 | 0 | 0.67394 | 700 | 40 | 0 | 10.313
0.48729 | 0 | 0.67909 | 700 | 40 | 0 | 8.729
0.46718 | 0 | 0.67312 | 700 | 40 | 0 | 6.718
0.44009 | 0 | 0.61846 | 700 | 40 | 0 | 4.009
0.42424 | 0 | 0.60843 | 700 | 40 | 0 | 2.424
0.40977 | 0 | 0.58033 | 700 | 40 | 0 | 0.977
0.40116 | 0 | 0.55971 | 700 | 40 | 0 | 0.116
0.3995 | 0 | 0.55832 | 700 | 39.95 | 0 | 0
0.40119 | 0 | 0.50937 | 700 | 40 | 0 | 0.119
0.41144 | 0 | 0.46794 | 700 | 40 | 0 | 1.144
0.42563 | 0.0004 | 0.47602 | 700 | 40 | 0.028 | 2.535
0.44172 | 0.0469 | 0.501 | 700 | 40 | 3.283 | 0.889
0.46322 | 0.3047 | 0.51944 | 700 | 40 | 6.322 | 0
0.48493 | 0.4967 | 0.51591 | 700 | 40 | 8.493 | 0
0.4974 | 0.618 | 0.47534 | 700 | 40 | 9.74 | 0
0.50285 | 0.5638 | 0.53687 | 700 | 40 | 10.285 | 0
0.5058 | 0.6536 | 0.57766 | 700 | 40 | 10.58 | 0
0.50242 | 0.6954 | 0.58552 | 700 | 40 | 10.242 | 0
0.50439 | 0.7086 | 0.60681 | 700 | 40 | 10.439 | 0
0.49759 | 0.5153 | 0.59847 | 700 | 40 | 9.759 | 0
0.50124 | 0.0877 | 0.56824 | 700 | 40 | 6.139 | 3.985
0.52285 | 0 | 0.51805 | 700 | 40 | 0 | 12.285
0.52342 | 0 | 0.51542 | 700 | 40 | 0 | 12.342
0.5168 | 0 | 0.52259 | 700 | 40 | 0 | 11.68
0.50832 | 0 | 0.53946 | 700 | 40 | 0 | 10.832
0.49448 | 0 | 0.51298 | 700 | 40 | 0 | 9.448
0.47339 | 0 | 0.51362 | 700 | 40 | 0 | 7.339
0.45586 | 0 | 0.51377 | 700 | 40 | 0 | 5.586
0.43698 | 0 | 0.50276 | 700 | 40 | 0 | 3.698
0.42854 | 0 | 0.47207 | 700 | 40 | 0 | 2.854
0.42166 | 0 | 0.44273 | 700 | 40 | 0 | 2.166
0.42119 | 0 | 0.42376 | 700 | 40 | 0 | 2.119
0.42202 | 0 | 0.38094 | 700 | 40 | 0 | 2.202
0.43276 | 0 | 0.35656 | 700 | 40 | 0 | 3.276
0.44633 | 0.001 | 0.33162 | 700 | 40 | 0.07 | 4.563
0.46527 | 0.1699 | 0.35536 | 700 | 40 | 6.527 | 0
0.48306 | 0.6114 | 0.35476 | 700 | 40 | 8.306 | 0
0.49589 | 0.6809 | 0.3933 | 700 | 40 | 9.589 | 0
0.50115 | 0.7672 | 0.47023 | 700 | 40 | 10.115 | 0
0.50072 | 0.8046 | 0.50085 | 700 | 40 | 10.072 | 0
0.49257 | 0.8098 | 0.52541 | 700 | 40 | 9.257 | 0
0.48732 | 0.8203 | 0.53871 | 700 | 40 | 8.732 | 0
0.48101 | 0.7187 | 0.51918 | 700 | 40 | 8.101 | 0
0.4807 | 0.5776 | 0.4673 | 700 | 40 | 8.07 | 0
0.4891 | 0.0996 | 0.37561 | 700 | 40 | 6.972 | 1.938
0.52795 | 0.0037 | 0.26351 | 698.0044 | 40 | 0.259 | 10.5404
0.54048 | 0 | 0.23478 | 693.3476 | 40 | 0 | 9.3912
0.54397 | 0 | 0.22614 | 687.9962 | 40 | 0 | 9.0456
0.53935 | 0 | 0.21149 | 682.5208 | 40 | 0 | 8.4596
0.53104 | 0 | 0.20649 | 677.6764 | 40 | 0 | 8.2596
0.51175 | 0 | 0.20101 | 674.5418 | 40 | 0 | 8.0404
0.49483 | 0 | 0.24459 | 674.8424 | 40 | 0 | 9.7836
0.48556 | 0 | 0.30528 | 678.4976 | 40 | 0 | 12.2112
0.48628 | 0 | 0.35887 | 684.2244 | 40 | 0 | 14.3548
0.48974 | 0 | 0.38175 | 690.5204 | 40 | 0 | 15.27
0.50239 | 0 | 0.33999 | 693.881 | 40 | 0 | 13.5996
0.52405 | 0 | 0.30476 | 693.6664 | 40 | 0 | 12.1904
0.56047 | 0 | 0.27775 | 688.7294 | 40 | 0 | 11.11
0.60243 | 0.0038 | 0.28425 | 680.1224 | 40 | 0.266 | 11.37
0.61592 | 0.2482 | 0.27786 | 687.0188 | 40 | 17.374 | 11.1144
0.59895 | 0.796 | 0.2134 | 700 | 40 | 32.8762 | 0
0.58011 | 0.8846 | 0.18509 | 700 | 40 | 18.011 | 0
0.56012 | 0.8552 | 0.17212 | 700 | 40 | 16.012 | 0
0.54235 | 0.833 | 0.12625 | 700 | 40 | 14.235 | 0
0.52479 | 0.8398 | 0.11661 | 700 | 40 | 12.479 | 0
0.51232 | 0.8753 | 0.12396 | 700 | 40 | 11.232 | 0
0.50312 | 0.8651 | 0.12518 | 700 | 40 | 10.312 | 0
0.5015 | 0.6231 | 0.11147 | 700 | 40 | 10.15 | 0
0.51166 | 0.1002 | 0.09225 | 699.538 | 40 | 7.014 | 3.69
0.55802 | 0 | 0.0829 | 687.052 | 40 | 0 | 3.316
0.57083 | 0 | 0.08878 | 673.5202 | 40 | 0 | 3.5512
0.57515 | 0 | 0.0877 | 659.5132 | 40 | 0 | 3.508
0.57438 | 0 | 0.07991 | 645.2716 | 40 | 0 | 3.1964
0.56417 | 0 | 0.0758 | 631.8866 | 40 | 0 | 3.032
0.54708 | 0 | 0.08308 | 620.5018 | 40 | 0 | 3.3232
0.53049 | 0 | 0.09009 | 611.0564 | 40 | 0 | 3.6036
0.51946 | 0 | 0.09723 | 602.9996 | 40 | 0 | 3.8892
0.51832 | 0 | 0.09397 | 594.9264 | 40 | 0 | 3.7588
0.5195 | 0 | 0.10085 | 587.0104 | 40 | 0 | 4.034
0.53129 | 0 | 0.09815 | 577.8074 | 40 | 0 | 3.926
0.5549 | 0 | 0.1078 | 566.6294 | 40 | 0 | 4.312
0.58931 | 0 | 0.13084 | 552.932 | 40 | 0 | 5.2336
0.62281 | 0.0033 | 0.12999 | 536.0816 | 40 | 0.231 | 5.1996
0.6331 | 0.2229 | 0.1405 | 533.9946 | 40 | 15.603 | 5.62
0.6136 | 0.6938 | 0.1426 | 566.9046 | 40 | 54.27 | 0
0.58811 | 0.7896 | 0.11568 | 607.9928 | 40 | 59.8992 | 0
0.56243 | 0.794 | 0.14575 | 653.1598 | 40 | 61.41 | 0
0.53835 | 0.7307 | 0.1963 | 698.3258 | 40 | 59.001 | 0
0.51974 | 0.7508 | 0.20507 | 700 | 40 | 13.6482 | 0
0.50989 | 0.7304 | 0.21098 | 700 | 40 | 10.989 | 0
0.50108 | 0.5792 | 0.2078 | 700 | 40 | 10.108 | 0
0.50368 | 0.3556 | 0.20717 | 700 | 40 | 10.368 | 0
0.51598 | 0.0523 | 0.16694 | 698.7406 | 40 | 3.661 | 6.6776
0.55745 | 0 | 0.16143 | 689.4528 | 40 | 0 | 6.4572
0.55579 | 0 | 0.22041 | 682.6902 | 40 | 0 | 8.8164
0.54279 | 0 | 0.31546 | 681.0296 | 40 | 0 | 12.6184
0.53034 | 0 | 0.37696 | 683.074 | 40 | 0 | 15.0784
0.51852 | 0 | 0.4051 | 687.426 | 40 | 0 | 16.204
0.50743 | 0 | 0.43499 | 694.0826 | 40 | 0 | 17.3996